37568 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-12-05 07:00 | 2000-12-05 09:36 | 2000-12-05 | LOSS OF POWER TO 'B' RPS BUS DUE TO TRIP OF EPA BREAKER B-D "On December 5, 2000 at 07:00, Susquehanna Unit 2 was operating at 100% power. Power was lost to the 'B' RPS Bus as a result of an unexpected Undervoltage Trip of EPA breaker B-D. This resulted in an initiation of the Standby Gas Treatment and CREOASS Systems as well as Division 1 and 2 containment isolation signals to various systems (e.g., Reactor Water Cleanup, Main Steam Line Drains, H2O2 Analyzers, Reactor Building Chilled Water to Recirc Pumps, Reactor Building HVAC Zones II and Ill, Drywell Floor Drain Sumps, Drywell Equipment Drain Tank, Containment Radiation Monitors, Reactor Coolant Sample valves, Containment Instrument Gas to Vacuum Breakers and TIP Purge, Containment Atmosphere Control Valves, and TIP and RHR Shutdown Cooling Valves). All containment isolations associated with a loss of 'B' RPS Bus actuated and went to completion. Operators responded by transferring the 'B' RPS Bus to the alternate power supply and restoring the affected valves/systems. There were no significant impacts to plant operation. "This event is an unplanned Actuation of an Engineered Safety Feature and, therefore, requires a four hour ENS Notification under 10 CFR 50.72(b)(2)(ii)." The licensee is investigating the cause of the trip. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37567 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2000-12-04 20:25 | 2000-12-04 20:51 | 2000-12-04 | BORON FOUND ON REACTOR HEAD THERMOCOUPLE NOZZLE. On November 25, 2000, at approximately 1500 hours, during a routine visual inspection, engineering identified a small amount (about 1 cup) of boron accumulation at the interface between the outside of the reactor vessel head and an unused reactor head thermocouple nozzle. The source of the boron could not be concluded. Unit 1 has eight unused thermocouple nozzles that were used during original startup. Oconee Units 2 and 3 do not have these nozzles. On December 4, 2000, at 2025 hours, a preliminary review of the eddy current test results from the subject unused thermocouple nozzle indicated that the source of the observed boron was most likely from a degraded pressure boundary associated with this thermocouple nozzle. In addition, a video inspection of the reactor head revealed trace amounts of boron around three (3) additional thermocouple nozzles and one (1) control rod drive nozzle. Leakage of this magnitude would not typically be detectable during operation. A failure investigation team has been formed to evaluate this condition. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37566 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-11-19 22:00 | 2000-12-04 20:43 | 2000-12-04 | STOLEN CPN GAUGE RECOVERED An authorized user was working at a temporary job site on Saturday, November 18 and stayed overnight at a local motel to continue work the next day. The authorized user secured a CPN model MC-1 portable gauge, serial number MD81104670, containing 10 millicuries of cesium-137 and 50 millicuries of americium-241/beryllium into its locked case. The locked case was then chained and locked into the canopy covered bed of a 1988 Toyota four-wheel drive pick-up. The pick-up was last seen at 10 PM on Saturday night. At 9 AM Sunday, November 19, the authorized user discovered that the pick-up had been stolen. The theft was reported to the Centralia police, the licensee and the Department emergency line (206 Nuclear). On November 27, the pick-up truck was found abandoned in an apartment complex in Puyallup, WA. The canopy was gone, the rear slider window was broken and the stereo and speakers had been removed along with the portable gauge. A pipe bomb was discovered under the front seat and destroyed by the Washington State Patrol bomb squad. On December 3, in response to complaints from neighbors, police in Bonney Lake, WA investigated a suspected meth lab in a trailer park. While there, officers spotted a bright orange carrying case in one of several junk piles and noted the labels indicating it contained radioactive material. The Department's emergency line was called. Staff from the Department retrieved the CPN gauge on December 4 and determined that it was intact and still in its locked carrying case. The gauge is being held by the Department until the licensee picks it up. What is the notification or reporting criteria involved? WAC 246-221-240 See Event #37538. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37565 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2000-12-01 10:00 | 2000-12-04 17:06 | 2000-12-04 | BARE UNMARKED 8 MILLICURIE CESIUM-137 SOURCE FOUND IN SCRAPYARD. On December 01, 2000, around 1000 CT the Illinois Department of Nuclear Safety was notified by Joseph Behr Metals, Inc., that a bare 8 millicurie Cesium-137 source had been discovered after their truck portal monitor had alarmed. Illinois Department of Nuclear Safety immediately sent personnel to the site. The area around the Cesium-137 was secured and the source was leak tested, doubled bagged, labeled, and locked in a secure facility at the site by Illinois Department of Nuclear Safety personnel. Joseph Behr Metals, Inc., will have the source properly disposed of in the very near future. The source is unmarked and it looks like it has been through a shredder and nobody came in contact with or was exposed to the source. The source appears to have belonged to a Moisture Density gauge. The Illinois Department of Nuclear Safety has placed the 8 millicurie Cesium-137 on their orphan source list. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0
37564 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2000-12-03 14:16 | 2000-12-03 18:08 | 2000-12-21 | ESF ACTUATION Today, 12/03/2000, at 1416 hours, 121 Spent Fuel Special & In-Service Purge System tripped due to high radiation on IR-22, the Shield Building Stack gas radiation monitor. This ventilation system operated for approximately 1-2 minutes prior to the high radiation trip signal. Other diverse indications aligned to the Shield Building Stack include 1R-11 and 1R-12, which showed no increase in radiation. A gas sample taken in containment (concurrent to the vent system startup) also revealed no activity above the normal background level (.05 DAC). A post-trip gas sample taken on IR-22 also revealed no elevated activity. The licensee notified the NRC resident inspector. ***** UPDATE AT 1233 EST ON 12/21/00 FROM BRAD ELLISON TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "The event reported on 12/03/2000 (121 Spent Fuel Special & In-Service Purge System tripped due to high radiation on 1R-22, Shield Building Stack gas radiation monitor) is hereby retracted. Investigation and sampling as part of our Condition Reporting process has determined that the signal from 1R-22 was due to a spike and not actual gaseous activity. Thus, the trip of the 121 Spent Fuel Special & In-Service Purge System was not a valid ESF actuation." The licensee plans to notify the NRC resident inspector. The NRC operations center notified the R3DO (Kozak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37563 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2000-12-01 14:50 | 2000-12-01 15:46 | 2000-12-01 | UNESCORTED ACCESS GRANTED INAPPROPRIATELY TO A CONTRACTOR. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. The NRC Resident Inspector was notified of this event by the licensee. See HOO Log Book for further details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) |  |  |  | 0
37562 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2000-12-01 11:10 | 2000-12-01 14:34 | 2000-12-01 | AUTOMATIC REACTOR SCRAM OF DUE TO HIGH REACTOR VESSEL WATER LEVEL. High reactor vessel water level occurred during feedwater manipulations to place "2B" Turbine Driven Reactor Feedwater Pump online. The abnormally high reactor vessel water level (level 8) initiated trips of the Main Generator and all online feedwater pumps, resulting in a reactor scram. All rods fully inserted into the core. Reactor vessel water level has been restored to a normal level of 36 inches using their Motor Driven Reactor Feedwater Pump. All equipment responded as expected. There were no ESF actuations because of this event. Conditions are stable. An investigation has been initiated to determine the cause of the abnormally high reactor vessel water level. The licensee was coming out of a refueling outage when the reactor scrammed from 30% reactor power due to the valid high reactor vessel water level signal. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37561 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-12-01 10:15 | 2000-12-01 12:46 | 2000-12-01 | DISCOVERED THAT SHUTDOWN COOLING SYSTEM COULD NOT BE PLACED IN SERVICE. Logic for Shutdown Cooling System would have prevented placing Shutdown Cooling in service (not currently required to be in service because Shutdown cooling is above its cut in permissive temperature of 350 degrees F). A component had high resistance simulating a high temperature condition (thermocouples failed high). Maintenance is troubleshooting the problem at this time. At the this time rods are being pulled to go critical. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
37560 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2000-12-01 05:40 | 2000-12-01 07:30 | 2000-12-01 | PLANT SHUTDOWN REQUIRED DUE TO TECHNICAL SPECIFICATIONS The licensee reported that the unit has commenced a shutdown in accordance with Technical Specification 2.1.4 due to an approximately 1 gpm reactor coolant system (RCS) leak. The licensee stated that the leakage, as measured by containment sump level, began suddenly this morning and increased to the TS 2.1.4 threshold of 1 gpm. (The criterion for declaration of an Unusual Event is 10 gpm.) The licensee is preparing to make a containment entry in order to identify the location of the leak. The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE ON 12/01/00 AT 1540 ET BY ERICK MATZKE TAKEN BY MACKINNON * * * The leak has been identified and isolated, CVCS system isolated. The leak is located on a socket weld to the CVCS Regenerative Heat Exchanger. The crack on the socket weld is approximately 1.24" in length. The licensee has an alternate charging path to the reactor coolant system. Technical Specification 2.1.4 was exited at 0830 CST and the shutdown of the plant was secured at about 0900 CST. Reactor power is about 86%. Options for repair of the leak are being investigated at this time. R4DO (Kriss Kennedy) notified. The NRC Resident Inspector was notified of this event update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37559 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-11-30 17:00 | 2000-11-30 20:55 | 2000-12-27 | SERVICE WATER ACCUMULATOR LEVEL HIGH OUT OF SPECIFICATION At 1700 on 11/30/00, it was identified that the 11B service water accumulator level was higher than that allowed by technical specifications. This was identified following a level device calibration. The service water accumulators support containment integrity by ensuring the containment fan coils remain properly filled during a design basis accident. Tech Spec 3.6.1.1 and 3.6.2.3 were entered for containment integrity and the inoperability of 11 and 12 containment fan coil units. Actions were taken within the one hour time requirement to comply with the containment integrity LCO. The service water accumulator was subsequently drained to within specification at 1742. Tech Spec 3.6.11 was exited at this time. The 11 and 12 containment fan coils were restored to operable at 1745 and Tech Spec 3.6.2.3 was exited. Actions are underway to calibrate the redundant instrumentation and to investigate the cause of the instrument drift. All power plant parameters remained stable throughout this event and no other safety systems were affected. The licensee notified the NRC resident inspector. * * * RETRACTION ON 12/27/00 AT 1053ET BY BASHORE TAKEN BY MACKINNON * * * A review of the actual service water accumulator parameters that existed when the 11 service water accumulator level was high out of specification was performed. Based on the actual service water accumulator pressure, level and temperature and the service water inlet temperature that existed, engineering has determined that the 11 service water accumulator would have been able to perform its design basis function if called upon to do so during the time that the accumulator level was high out of specification. Since the 11 service water accumulator was capable of performing its design basis function, the above report is being retracted. NRC R1DO (L. Doerflein) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37558 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-11-30 15:50 | 2000-11-30 17:42 | 2000-11-30 | LOAD REJECT - REACTOR SCRAM The reactor scrammed at 1550 due to generator load reject. The main generator ouput circuit breaker 2-7 was being closed after maintenance when a bus to phase differential trip was received causing both output circuit breakers 2-3 and 2-7 to open. With both output circuit breakers open, the reactor scrammed due to load reject. The response to the reactor scram was normal, all rods inserted. Steam is being dumped to the main condenser for decay heat removal. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37557 | -1 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-11-30 08:44 | 2000-11-30 12:03 | 2000-12-06 | LOSS OF SAFETY FUNCTION OF THE NUCLEAR SERVICES SEA WATER SYSTEM At 0843 on November 30, 2000, RWP-2B. Nuclear Services Sea Water Pump, was started and observed to develop low discharge pressure, rendering the pump INOPERABLE. This condition was caused by diversion of flow via a failed open check valve upon shutdown of pump, RWP-1 which shares a common discharge header with pump RWP-2B. RWP-2A, Nuclear Services Sea Water Pump, discharge is also common to RWP-2B. Consequently, RWP--2A would likely not have developed adequate discharge pressure, and therefore, adequate flow could not have been provided by either Nuclear Services Sea Water Pump. Although allowed by design, this single failure defeats the safety function of the Nuclear Services Sea Water System. The licensee notified the NRC resident inspector. * * * RETRACTION ON 12/06/00 AT 1920 ET BY BILL BANDHAUER TAKEN BY MACKINNON * * * On December 6, 2000, FPC performed further evaluation of the required safety function and the pertinent plant conditions observed during this event. Even with the partially stuck open check valve, sufficient capacity of system pumps and heat exchangers remained to remove design basis heat loads. FPC has concluded that the Nuclear Services Sea Water System would have performed the required heat removal safety function, if called upon. Additionally, FPC considered the impact of increased electrical loading on the Emergency Diesel Generators caused by increased pump flow rate. FPC concluded that the electrical diesel generators remained capable of supporting the required electrical loads. Based upon these additional evaluations, FPC determined that this condition in not reportable and therefore, retracts this event. R2DO (Paul Fredrickson) notified. The NRC Resident Inspector will be notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37556 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-11-29 11:35 | 2000-11-29 17:11 | 2000-11-29 | REPORT INVOLVING ACTUATION OF A SAFETY SYSTEM "AT 1135 HOURS ON 11/29/00 AUTOCLAVE #3 IN THE X-343, EXPERIENCED A HIGH CONDENSATE LEVEL SHUTOFF ACTUATION WHEN BOTH PROBES IN THE CONDENSATE DRAIN LINE FIRED. THIS ACTUATION OCCURRED DURING MODE II OPERATIONS (HEATING), RESULTING IN THE SHUTTING OF THE STEAM ISOLATION VALVE AND SHUTTING DOWN OF THE AUTOCLAVE. OPERATORS FOLLOWING APPROVED RESPONSE PROCEDURES VERIFIED THE CYLINDERS STRUCTURAL INTEGRITY. APPROXIMATELY TEN MINUTES AFTER THE STEAM VALVE SHUT THE HIGH CONDENSATE PROBE ALARMS CLEARED BASED ON THE ACTUATION OF BOTH CONDENSATE LEVEL PROBES. THIS IS BEING REPORTED AS A SAFETY SYSTEM ACTUATION. THE AUTOCLAVE WAS DECLARED INOPERABLE AND ENGINEERING IS EVALUATING THIS SYSTEM ACTUATION. THERE WAS NO RELEASE OF RADIOACTIVE MATERIAL FROM THIS EVENT." OPERATIONS PERSONNEL INFORMED BOTH THE DOE SITE REPRESENTATIVE AND THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37555 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-28 16:25 | 2000-11-28 17:16 | 2000-11-29 | BOTH UNITS OUTSIDE OF DESIGN BASIS DUE TO MOMENTARY LOSS OF BOTH TRAINS OF CONTROL ROOM VENTILATION "Presently, 'A' Control Room Ventilation out of service for maintenance. 'B' Control Room Ventilation (VC/YC) inadvertently deenergized causing both trains of VC/YC to be inoperable. 'B' VC/YC restarted with no further complications. Deenergized from 1625 until 1643 which places both units one and two outside design basis. With VC/YC inoperable for 'A' and 'B' trains, entered [TS] 3.0.3 momentarily." The problem occurred when the technician performing maintenance on the "A" train went to the operating "B" train. The "B" train Chiller was tripped in error. The licensee informed the NRC resident inspector. * * * * UPDATE 1159EST ON 11/29/00 FROM JOHN JENKINS TO S. SANDIN * * * * The licensee is retracting this report based on the following: "On November 29, 2000, the above notification was made to the NRC under the requirements of 10 CFR 50.72 (b) (1) (ii) (B). Upon further evaluation, it has been determined that this condition did not place the plant outside of design basis. "The ability to pressurize the Main Control Room was not affected in this condition. The pressurization fans would start and run if needed during an accident. The pressurization function mitigates dose to the control operators. "During the 18 minutes that the chiller was out of service the temperature in the Control Room increased from 70 degrees to approximately 72 ½ degrees. The temperature rise was evaluated by the System Engineer. The temperature limit for the control room is listed as a maximum of 90 degrees in the Selected Licensee Commitments. This temperature is based on a continuous duty rating for equipment and instrumentation and for habitability of the Control Room. Annunciator alarms would alert the Operators of the increasing temperature and existing procedures would direct actions to be taken to limit the temperature affects. The Engineering evaluation determined that the chiller would need to be out of service for 2 hours before this limit was challenged. "This occurrence did not increase the probability of barrier failure or radiation releases. Remote shutdown capability outside the control room was not affected. For these reasons the plant remained within its design basis." The licensee will inform the NRC resident inspector. Notified R2DO(Belisle). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37554 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-11-28 15:13 | 2000-11-28 16:50 | 2001-01-12 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE DUE TO INSTRUMENTATION FAILURE "The HPCI System was taken out of service for surveillance testing earlier in the day. The surveillance's were completed and HPCI was placed back in service in standby lineup. At this time, the high flow isolation instrumentation was found to be reading well beyond the limits of the normal in service band (+10 to -10). At that time, HPCI was removed from service (availability) and isolated. The proper LCO was entered and troubleshooting is underway." The licensee informed the NRC resident inspector. * * * UPDATE 1415EST ON 1/12/01 FROM OLSON TO MacKINNON * * * The licensee is retracting this report based on the following: "This is a retraction of event no. 37554 made on November 28, 2000 at 1651 in accordance with 10CFR50.72(b)(2)(iii)(D). "An Engineer had noted a flow switch that provides a high steam flow to the HPCI system reading -17 inches of water while the other indicated -2 inches of water. The Primary Containment Isolation capability of the HPCI isolation valves was declared inoperable and the valves de-energized in the isolated condition. HPCI was declared inoperable and a 14 day cold shutdown LCO entered. Subsequent testing of the differential pressure switches found the trip setpoints to be correct. The face plate had not been 'zeroed' during previous calibration. This had no effect on switch operation, therefore could not have prevented fulfillment of safety function." The licensee informed the NRC resident inspector. Notified R1DO(Lew). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37553 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-25 20:07 | 2000-11-26 10:43 | 2000-11-26 | FITNESS-FOR-DUTY ISSUE A fitness-for-duty issue occurred at 2007 on 11/25/00. A contract engineering supervisor tested positive for THC (marijuana) during a followup test. The individual's access to the plant has been terminated. The licensee plans to perform a review of the individual's work. The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0
37552 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2000-11-26 01:54 | 2000-11-26 06:13 | 2000-12-14 | DISCOVERY OF LOOSE SERVICE WATER PUMP FOUNDATION BOLTS The following text is a portion of a facsimile received from the licensee: "At 0154 [CST] on 11/26/00, a station operator noticed that 2 foundation bolts on service water pump (SWP) C were loose and 3 foundation bolts on [SWP] D were loose. Both service water loops were declared inoperable, and [limiting condition for operation (LCO)] 3.7.2, condition A, was entered twice and condition B once. This required placing the plant in Mode 3 within 12 hours and Mode 4 within 36 hours. Personnel were called to the site, and all foundation bolts on all 4 [SWPs] were torqued. No loose bolts were found on SWP A, 4 loose bolts were found on SWP B, and 5 loose bolts were found on SWPs C [and] D. An operability determination was written to justify operability of the service water system, and all LCOs were exited at 0428 [CST]. Engineering [personnel are] evaluation the condition." The licensee notified the NRC resident inspector. * * * RETRACTED AT 1244 EST ON 12/14/00 BY STEVEN JOBE TO FANGIE JONES * * * "Subsequent evaluation has determined that all Service Water Pumps were operable at all times and this event is not reportable under either 10 CFR 50.72(b)(2)(iii)(B) or 10 CFR 50.72(b)(2)(iii)(D). "Engineering evaluation has determined that a Service Water Pump is operable with one or more pedestal nuts (foundation bolts) having less than installation torque provided a minimum finger tight torque exists. That justification is based on evaluation of loading stress and the impact of not having a preload stress applied to the nut. The determination is that the finger tight nut is an acceptable condition for pump operability. This evaluation has considered the effects of various loading conditions including seismic, barge impact and normal operational loads." The licensee has notified the NRC Resident Inspector. The R4DO (Chuck Cain) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(D) |  |  | 0
37551 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-11-26 01:53 | 2000-11-26 03:34 | 2000-11-26 | OFFSITE NOTIFICATION OF A DIESEL FUEL OIL SPILL While flushing diesel generator lube oil to a skid outdoors, one of the hoses came loose, and approximately 500 gallons of diesel lube oil spilled. The spill is now isolated and contained. Some of the oil entered a storm drain, but it is currently believed that none of the oil discharged to the ocean. The spill was reported to the control room at 0153 on 11/26/00. The licensee notified the New Hampshire State Police, the U.S. Coast Guard, and the National Response Center. The licensee plans to notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37550 | 0 | LAW ENVIRONMENTAL |  |  |  |  | 2000-11-24 14:45 | 2000-11-24 18:59 | 2000-11-24 | OVEREXPOSURE TO EXTREMITIES (HANDS/FINGERS) Radiation Safety Officer (RSO) for Law Environmental located in Dorado, Puerto Rico reported the following event which occurred today, 11/24/00, around 1445 hours ET. The RSO and another individual were performing a source exchange on a Sentinel Technology model number 660B Iridium-192 (Ir-192) Radiography camera. They were performing a source exchange, replacing their old Ir-192 source with a new Ir-192 source without realizing that the old source had not been retracted. One person had his hand on the guide tube and the other person unplugged the guide tube. The RSO said that their fingers were approximately 0.25" (material between fingers and source) from the Ir-192 6.3 (or 6.03) -curie source for about 30 seconds. The combined calculated total extremity dose to both person hands (fingers) is 628 Rems. The RSO had not calculated the whole body dose to himself and the other person at the time of the event notification. The original source strength of the radiography camera was 115 curies as of January or February of this year. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 2 | PR | MAT |  | 20.2202(a)(1) |  |  |  | 0
37549 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2000-11-24 13:30 | 2000-11-24 14:32 | 2000-11-24 | SYNCOR TRUCK CARRYING TECHNETIUM-99M INVOLVED IN ACCIDENT. At approximately 1300 hours ET time today, 11/24/00, a SYNCOR Radiopharmaceutical truck was involved in a one vehicle accident near Harpersfield, Ohio, which is located in Ashtabula County. The truck hit an icy patch on the road and the truck flipped over. The SYNCOR truck was carrying two ammo boxes containing Technetium-99m. One ammo box contained 158 millicuries of Tc-99m and the other ammo box contained 441 millicuries of Tc-99m. The driver of the truck was not injured but was transported to an area hospital as a precaution. The local fire department on scene determined that the boxes were not damaged and their surveys around the outside of the truck did not show any abnormal radiation readings. SYNCOR Corporation Pharmacy out of Oakwood Village, Ohio, dispatched personnel to the scene. When they arrived they performed contamination surveys of the ammo boxes and the vehicle and determined that the packages were not damaged. The ammo boxes were labeled "Radioactive White 1" Ohio State report number assigned to this event is 00-044. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0
37548 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-11-24 12:32 | 2000-11-24 14:19 | 2000-11-24 | TORUS TO DRYWELL VACUUM BREAKER OPENED FOR APPROXIMATELY 4 MINUTES. At 1232 CT on 11-24-00, Reactor Building Closed Cooling Water (RBCCW) temperature control valve failed open due to the feedback arm vibrating off of the controller. RBCCW temperature dropped from 70 degrees to 50 degrees and caused drywell temperature and pressure to lower. Drywell temperature decreased from 136 to 132 degrees and drywell pressure decreased from 15 to 10.5" of water column. Drywell pressure lowering caused T2300F400C (Torus to Drywell vacuum breaker) to open for approximately 4 minutes. After pressure stabilized, the vacuum breaker closed. This event only altered containment parameters, and the reactor was not affected. The feedback arm was reinstalled. RBCCW temperature and containment parameters were restored to normal. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37547 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2000-11-23 03:15 | 2000-11-23 04:25 | 2000-11-23 | SPDS OUT OF SERVICE FOR PLANNED MAINTENANCE The safety parameter display system (SPDS) was deenergized for planned maintenance. The system is expected to be down for 2 to 3 hours. The licensee notified the NRC Resident Inspector and intends to notify the state authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37546 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2000-11-21 | 2000-11-22 17:23 | 2000-11-22 | AGREEMENT STATE REPORT The licensee contacted the State of Illinois to request assistance in locating a 20 mCi Cs-137 source. The source was mounted in an Omart model SH-F1 holder, and was licensed under a general license. Representatives of the state surveyed warehouses and other buildings throughout the licensee's facility and other licensee locations, but were unable to locate the source. The licensee is currently investigating whether the source may have been sent to a licensee facility in Colorado; however, the source may have been discarded during renovations to the warehouse in which it had been located. In this instance, the source may have been deposited in a landfill in Wisconsin. The state is continuing its investigation of this matter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0
37545 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-11-22 03:40 | 2000-11-22 14:50 | 2000-11-22 | SAFETY SYSTEM ACTUATION "At 0340 on 11/22/00, the PSS office was notified that a primary condensate alarm was received on the C-333A position 3 South autoclave Water Inventory Control System (WICS). The WICS system is required to be operable while heating in mode 5 according to TSR 2.2.4.2. The autoclave was checked according to the alarm response procedure, removed from service and the Water Inventory Control System was declared inoperable by the Plant Shift Superintendent. The WICS actuation has been determined to be a valid actuation by the System Engineer. "This safety system actuation is reportable to the NRC as required by Safety Analysis Report, section 6.9, table 1 criteria J.2, Safety System actuation due to a valid signal as a 24-hour event notification." The NRC Senior Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37544 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-11-21 13:08 | 2000-11-21 16:12 | 2000-11-21 | BOTH TRAINS OF CONTROL ROOM EMERGENCY FILTRATION INOPERABLE SIMULTANEOUSLY "At 1308 hours, the 'B' Control Room Chiller tripped on an apparent high bearing oil temperature condition, rendering the 'B' Control Room Emergency Filtration (CREF) train inoperable. At the time that the 'B' CREF train tripped, the 'A' CREF train was out of service for scheduled maintenance. With both trains of CREF inoperable, Technical Specification 3.0.3 was entered. Preparations were made to commence plant shutdown in parallel with restoration of the 'A' train from maintenance. The 'A' CREF train was returned to operable status at 1402 hours and Technical Specification 3.0.3 was exited. A seven-day action statement remains in effect for the inoperability of the 'B' CREF train. "The Control Room Ventilation System provides heating, cooling, ventilation, and environmental control for the control room and adjacent areas. Under accident conditions, the Control Room Emergency Filtration Unit ensures that the control room will remain habitable during and following all design basis accidents. Because the CREF system is required to automatically respond in the event of a design basis accident, having both trains of CREF inoperable at the same time impacted the ability to mitigate the consequences of an accident. Therefore, this event is being reported in accordance with 10CFR50.72(b)(2)(iii)(D). "All other safety related equipment is operable with the exception of the 'C' Main Steam Line Radiation Monitor, which is in the tripped condition due to a surveillance test failure. A root cause investigation team has been assembled to determine required corrective actions." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37543 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 1999-12-23 | 2000-11-21 15:36 | 2000-11-21 | AGREEMENT STATE REPORT - ABANDONED WELL LOGGING SOURCE "Date of Occurrence: 12-23-99. "Description of Source: Am241Be sealed source Gulf Nuclear model: 712A, serial number: 635B, physical form: Solid, quantity: 20Ci. "Well Operator: Colorado Energy Minerals, Inc. "Well Name: UPRC Baur 17-1 "Surface Location: NW NE 600' FNL 2000' EEL Sec-17, Twp-9N, Rge-64W. "Results of efforts to seal and immobilize the source: The source is at the bottom of the hole with 100' of red cement above. A used drill bit has been cemented in as a deflector in one of the uphole plugs. "Description of attempted recovery: It was discovered the source was in the hole without the protection of the pad carrier. It was verified with a gamma ray to be on the bottom of the hole. Fishing was attempted via the wireline with a magnet since the holder was magnetic. These attempts were hampered by steadily deteriorating hole conditions and fill on top of the source. Fishing attempts involving use of the drilling rig and pipe were ruled out due to the possibility of source rupture from the extreme weight of the drill string. When the fishing attempts proved unsuccessful it was determined to cement the source in the hole. A final gamma ray was ran to assure the source was at the bottom of the hole and the well was plugged as outlined above. Note: The well was a dry hole and the well was plugged with cement plugs at various depths and the deflector cemented in one of these plugs. "Depth of the source: 4420'" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0
37542 | 0 | BEST INDUSTRIES |  |  |  |  | 2000-11-21 10:00 | 2000-11-21 12:02 | 2000-11-21 | 10 CFR PART 20.1906(d) REPORT One of three Type A shipping packages received from Baylor University exceeded the limit for surface radiation readings (200 mR/hr). The licensee reported that the package was reading 2.7 R/hr at the surface of the package, and 65 mR/hr at 1 meter. The package has been placed in safe storage. The licensee will contact Baylor University and the shipper (FedEx). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | [10 empty] | NON EMERGENCY | 2 | VA | MAT | [5 empty] | 0
37541 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2000-11-21 09:50 | 2000-11-21 11:29 | 2000-11-21 | LOSS OF POWER TO THE EMERGENCY OPERATIONS FACILITY (EOF) The licensee reported that power was lost to the EOF at 0950 and was restored at 1045. This facility serves both the NMP units as well as Fitzpatrick. The licensee notified the NRC resident inspector. (Refer to event number 37540 for a related event at Fitzpatrick.) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37540 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-11-21 10:22 | 2000-11-21 11:03 | 2000-11-21 | LOSS OF POWER TO THE EMERGENCY OPERATIONS FACILITY (EOF) The loss of power to the EOF impairs the ability of the licensee to carry out the plant's emergency plan. A snow storm is being blamed for the loss of power. The licensee notified the NRC resident inspector. (Refer to event number 37541 for a related event at Nine Mile Point.) | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37539 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-11-20 23:10 | 2000-11-21 01:12 | 2000-11-21 | HPCI INOPERABLE - TURBINE EXHAUST LINE FLOODED HPCI turbine exhaust drain pot level switch has malfunctioned. This has potentially led to a condition where exhaust line from the turbine is flooded. GE SIL 580 recognizes that a slug of water can create a momentary high pressure and rupture both exhaust line rupture diaphragms if HPCI should initiate. HPCI system has been declared inoperable and the licensee entered a 7 day LCO. The NRC resident inspector has been notified. | 72 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(D) |  |  | 0
37538 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-11-19 | 2000-11-20 14:07 | 2000-11-20 | AGREEMENT STATE REPORT "This is notification of an event in Washington state as reported to the WA Department of Health, Division of Radiation Protection. "STATUS: new "Licensee: Zipper Zeman Associates City and state: Lynnwood, WA License number: WN-I-507-1 Type of license: Portable Gauge "Date of event: November 19, 2000 Location of Event: Centralia, WA "ABSTRACT: An authorized user was working at a temporary job site on Saturday, November 18 and stayed overnight at a local motel to continue work the next day. The authorized user secured a CPN model MC-1 portable gauge, serial number MD81104670, containing 10 millicuries of cesium 137 and 50 millicuries of americium 241/beryllium into its locked case. The locked case was then chained and locked into the canopy covered bed of a 1988 Toyota four-wheel drive pick-up. The pick-up was last seen at 10 PM on Saturday night. At 9 AM on Sunday, November 19, the authorized user discovered that the pick-up had been stolen. The theft was reported to the Centralia police, the licensee and the Department's emergency line (206 NUCLEAR). As of this report (11 AM, November 20), the vehicle and gauge are still missing. "What is the notification or reporting criteria involved? WAC 246-221-240 (Reports of stolen, lost or missing radiation sources.)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37537 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-11-20 10:15 | 2000-11-20 14:03 | 2000-11-20 | 4-HOUR NRC BULLETIN 91-01 REPORT "At 1015 hours on 11/20/00, Nuclear Criticality Safety (NCS) personnel determined that NCSA-0705-076 was deficient in that it had not adequately considered conditions created by a 1 1/2" dike installed in several areas of the X-705 decontamination building. Holes in some dry active waste (DAW) containers may allow spilled solution to be absorbed into the containers and exceed the 1 1/2" favorable thickness allowed by the NCSA. DAW containers were removed from the areas in question to establish compliance with the double contingency principle. "SAFETY SIGNIFICANCE OF EVENTS: "The safety significance of this event is low because no leak of uranium bearing solution has occurred. However the potential existed for absorbent materials to collect an unsafe amount of material in the event of a leak within a diked area. The contingency of unprotected absorbent materials was analyzed to be subcritical in NCSE-0705-076 provided that a spill of an unsafe amount of fissile solution does not occur. Elevating absorbent materials to the wrong height represents a loss of one double contingency control. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: "For a criticality to occur, the following chain of events would be required. First, a leak of an unsafe concentration or unsafe mass of uranium bearing solution must occur in an Inadvertent Container Area. Secondly, the area must have a dike and the solution must collect in the area to a height greater than one inch (dikes are typically 1 1/2"). Third, absorbent materials which are required to be covered and elevated (e.g. a DAW barrel) must be present in same diked area. Fourth, the solution must absorb into the materials in an amount greater than the minimum critical mass. "CONTROLLED PARAMETERS: "The controlled parameter related to this event is geometry. Control #6 of NCSA-0705-076 requires that absorbent materials protected by covering be elevated above the floor by one inch. This height is insufficient if dikes are present in the area. NCSA-0705-076 is deficient because it fails to consider diked areas when establishing the required elevation height. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: "No leak or spill of uranium bearing material has occurred. There is no estimate of how much material could have spilled in the event of a leak. NCSAs for the X-705 building approve the processing of up to 100% enriched material. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "NCSA-0705-076 fails to establish the correct height for elevating absorbing materials such as DAW barrels in Inadvertent Container Areas. Storage of absorbent materials in accordance with control #6 will be placed on hold until NCSA-0705-076 can be revised. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At 1230 hours, barrels were removed from the areas in question and compliance established." The NRC resident inspector has been informed of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37536 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-11-20 10:28 | 2000-11-20 14:00 | 2000-11-20 | OFFSITE NOTIFICATION DUE TO DOWNED TRANSMISSION LINE ACROSS OHIO RIVER "At 1028 hours on 11/20/2000, with both Beaver Valley units at full power, several alarms were received at both units and control room lights flickered. There were no actuations of components or electrical protection devices at the site. Reports were received that an electrical power line, which crosses the Ohio river, was down in the river and draped over the auxiliary intake structure. This structure is located outside the Beaver Valley protected area and contains emergency backup river water systems for both units. There were no fires near the auxiliary intake structure. There were no injuries to plant personnel. The control room also received reports of a small brush fire which was caused by the downed line on the opposite side of the Ohio river, which is outside the owner controlled property. "Operators were dispatched, and reported that the downed line is a static wire from the top of a high tension tower. The static wire contacted scaffolding being built at the auxiliary intake structure, causing some sparking. The high voltage line has been deenergized. "Control room shift supervisors contacted the Beaver county Emergency Management Agency to report the downed line and the fire across the river. This report is submitted as a courtesy as the local emergency management agency was notified. The downed line does not affect the operation to either Beaver Valley unit. Offsite power sources are fully available." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37535 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-11-20 03:52 | 2000-11-20 07:45 | 2000-11-20 | REACTOR TRIP - SPURIOUS RATE TRIP A reactor trip signal was generated from the power range neutron flux rate signal. With one power range NI out of service, personnel performing incore flux maps operated a test meter on another power range NI. A spurious rate trip signal was generated, resulting in a 2 of 4 coincidence causing a reactor trip. All equipment functioned as designed. All three Auxiliary feedwater pumps started on low S/G level. All control and shutdown bank control rods fully inserted. The licensee will inform the NRC resident inspector and the local sheriff's office. | 0 | 0 | 0 | 46 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37534 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-19 06:20 | 2000-11-19 13:15 | 2000-11-19 | LICENSED EMPLOYEE DETERMINED POSITIVE FOR FAILURE TO PROVIDE A FOR-CAUSE TEST SAMPLE A licensed employee was determined to be under the influence of alcohol after refusing to provide a sample during a for-cause test. The employee's left the site and access to the plant has been terminated. The licensee informed the NRC resident inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0
37533 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2000-11-18 11:47 | 2000-11-18 17:36 | 2000-11-18 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP FOLLOWING A REACTOR POWER CUTBACK "On November 18, 2000, at approximately 1147 MST, Palo Verde Unit 2 experienced an automatic reactor trip (RPS actuation) from approximately 45% rated thermal power. Unit 2 is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to the fission product barrier. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "Prior to the reactor trip, at approximately 1008 MST, Unit 2 was at 100 percent power and normal operating temperature and pressure, when testing began to validate various parts of the electrical generator and exciter model parameters. At approximately 1059 MST, Unit 2 experienced a generator/turbine trip. Steam bypass control valves opened and a reactor power cutback was initiated. "Operations personnel were in the process of plant stabilization after the reactor power cutback, when at approximately 1147 MST, the reactor tripped. All control element assemblies (CEAs) inserted as required and the trip was classified as uncomplicated with respect to the emergency plan. The primary plant is now stabilized in Mode 3 in forced circulation with both steam generators being used for heat removal, "The cause of the reactor trip has not been determined and is under investigation at this time. APS [Arizona Public Service] will supplement this report if information is developed which significantly alters this information." The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37532 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-17 20:10 | 2000-11-17 20:41 | 2000-12-18 | UNIT 2 ENTERED TS 3.0.3 AFTER DECLARING BOTH LOOPS ECCS INOPERABLE "Tech Spec 3.5.2 requires two independent Emergency Core Cooling System (ECCS) loops, each capable of taking suction from the Refueling Water Storage Tank (RWST) and being transferred to the containment recirculation sump. This spec applies in modes 1 - 3. Following evaluation of recent modifications to the containment recirc sump ECCS suction isolation valves, it has been determined that neither of the two isolation valves (2-ICM-305 and 2-ICM-306) could be relied upon to open when transfer of ECCS suction is required. This is attributed to a lack of assurance that between seat relief valves on 2-ICM-305 and 2-ICM-306 would lift and preclude thermal hydraulic locking of the valves in the closed position. Since neither ECCS loop recirc sump suction is operable, the action statement of TS 3.5.2 is not valid. This led to the Shift Manager declaring entry into TS 3.0.3 with a requirement to place the unit in a mode for which TS 3.5.2 does not apply. A unit shutdown at 2% per hour has been initiated. Plans are to implement compensatory actions or have the unit in hot standby within 6 hours." The licensee anticipates exiting TS 3.0.3 after bleeding the fluid trapped between the double disk valves in approximately two hours. The licensee informed the NRC resident inspector. * * * UPDATE 0310 11/18/2000 FROM RICHARDSON TAKEN BY STRANSKY * * * The united exited the shutdown LCO at 2315. Reactor power had been reduced from 100% to 90%. The licensee removed approximately 4.5 gallons of water from the body of each valve in order to prevent thermal locking. The NRC resident inspector will be informed. Notified R3DO (Jorgensen). ***** UPDATE AT 1834 ON 12/18/00 FROM BRENDA L'ROURKE TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "The Donald C. Cook Nuclear Plant is withdrawing [its] 1-hour Non-Emergency notification made to the NRC at 2041 hours on [11/17/00] (Event # 37532). At that time, it was reported that Unit 2 entered TS 3.0.3 after declaring both ECCS loops inoperable. Both loops were declared inoperable because neither of the two containment recirculation sump ECCS suction isolation valves (2-ICM-305 and 2-ICM-306), could be relied upon to open when transfer of ECCS suction is required. This was attributed to a lack of assurance that the thermal relief valves (2-SV-344 East and West) installed between the seats of 2-ICM-305 and 2-ICM-306, would lift at the required 20 psid design pressure to preclude thermal hydraulic locking of the normally closed ECCS suction valves. These relief valves were installed prior to Unit 2 entering Mode 4. On [11/18/00] at 2315 hours, Unit 2 exited the TS-required shutdown after 2-ICM-305 and 2-ICM-306 were declared operable after approximately 4.5 gallons of water was drained from each valve." "Further Engineering evaluation concluded that both ECCS loops are and have been operable because 2-ICM-305 and 2-ICM-306 were determined not to be in a 'water solid' condition and, therefore, not susceptible to thermal hydraulic locking. This conclusion was confirmed by draining the volume of fluid present between the ECCS suction valve seats and comparing the total amount of fluid drained to the free space available inside each valve. It was determined, by calculation, that of the 30 gallons of free space available inside each valve, only 2 gallons of free space are needed to ensure the valves will open when transfer of ECCS suction is required. Both valves were drained on three separate occasions between 11/17/00 and 11/22/00. A total of 6.74 gallons was drained from 2-ICM-305, and a total of 8.25 gallons was drained from 2-ICM-306. Based on the total amount of fluid drained from each valve, both 2-ICM-305 and 2-ICM-306 have been operable during all periods when the ECCS is required to be operable." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Kozak). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37531 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-11-16 15:54 | 2000-11-17 15:21 | 2000-11-17 | SITE ACCESS INAPPROPRIATELY GRANTED TO UTILITY EMPLOYEE During a QA Audit it was determined that one (1) utility employee may have been granted access inappropriately following offsite drug testing conducted on 9/99. The employee was recalled to the site today for retesting. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0
37530 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-17 08:42 | 2000-11-17 10:41 | 2000-11-17 | PLANT HAD A REACTOR TRIP FROM 53% POWER DUE TO A TURBINE TRIP A "Turbine Trip/Reactor Trip" occurred at 53% reactor power due to a sudden pressure relay actuation on C phase Main Bank transformer which sent signal to the generator resulting in the turbine trip. Motor Driven Auxiliary Feedwater pumps started as required when level decreased to less than 10% in one Steam Generator and the Turbine Driven Auxiliary Feedwater pump started as required on less than 10% in two steam generators. Preliminary walkdown of the transformer showed no visible exterior damage or degradation. Investigation is in progress to determine the cause of this event. The Unit is stable and operating in accordance with Plant General Operating procedures. All rods fully inserted, there were no ECCS actuations and no safety relief valves lifted. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 53 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37529 | 0 | USAF RADIOISOTOPE COMMITTEE |  |  |  |  | 2000-11-16 17:20 | 2000-11-16 21:32 | 2000-11-16 | LOSS OF TWO AMERICIUM-241 SOURCES (4 MICROCURIES EACH) DUE TO THE CRASH OF AN F-16 NEAR SARASOTA, FLORIDA An F-16 crashed near Sarasota, Florida which may have been carrying two (2) Am-241 sources used in the LANTIRN (Low Altitude Navigation Targeting Infrared for Night) pod. The Air Force will followup to determine whether the sources were onboard and, if so, attempt recovery from the crash scene. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | FL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37528 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2000-11-16 12:15 | 2000-11-16 13:06 | 2000-11-16 | UNIT 1 PRESSURIZER LEVEL INSTRUMENTATION MAY NOT MEET CABLE SEPARATION CRITERIA "During development of a cable separation modification package for the upcoming 2001 Unit 1 Outage SL1-17, a re-evaluation of the Unit 1 Containment Shutdown Safety Assessment was performed. The re-evaluation identified a separation issue with the cables for pressurizer level instruments LT-1110X and LT-1110Y in the annulus area. At certain locations, these cables are not separated as required by 10 CFR Part 50 Appendix R, Section lll.G.2 as required by the plant design basis as delineated in the FSAR. "Fire protection for nuclear plants is based on the defense in depth concept with three primary barriers - prevention, detection and control, and protection of safe shutdown capabilities. The above concern is considered a degradation of the protection of safe shutdown capability. The affect of this concern on the fire protection program does not eliminate the ability to achieve safe shutdown. The remaining two 'defense in depth' barriers remain intact - (prevention of fires and prompt detection and control of fires that due occur). In an area such as containment (large volume, high ceilings, minimal ignition sources, limited combustibles, limited access, etc.) the potential for a fire of consequence during operation is highly unlikely. In the particular area described, the potential for a fire is even more remote since the combustible loading is negligible. The location where the separation issue exists (at the end of the annulus area near the pipe chase) does not contain significant equipment, significant exposed combustible materials or significant ignition sources. The cable trays routed in this area (between radius lines 1 and 3) are relatively lightly loaded since most cables have previously exited the tray enroute to their respective equipment (e.g., only one tray continues past radius line 2 to radius line 1). "The probability of a fire in Containment is very low. The probability of a fire causing significant damage such that required function is impaired is very low. Therefore, the equipment and system affected by this condition is considered degraded but operable. Based on the guidance provided in GL 91-18 a reasonable assurance of safety is provided." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37527 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-11-16 03:23 | 2000-11-16 05:10 | 2000-11-16 | AUTOMATIC REACTOR TRIP ON HIGH-HIGH STEAM GENERATOR WATER LEVEL FOLLOWING A MASTER STEAM GENERATOR FEEDWATER PUMP CONTROLLER FAILURE AND SLUGGISH CONTROLS AFTER SWITCHING TO MANUAL The master steam generator feedwater pump controller failed low and caused feedwater pump speeds to slow down. (Both pumps dropped to 3,200 rpm.) In an attempt to regain feedwater pump speed and steam generator water level in manual, a high-high level was reached in the 2A steam generator. This caused a turbine trip and subsequent reactor trip. All control rods fully inserted. Auxiliary feedwater actuation and feedwater isolation occurred as expected. All systems functioned as required. It was reported that the controller was sluggish after manual control was taken and that operators were not able to terminate the rising level in the 2A steam generator before the high-high level trip setpoint was reached. The lowest steam generator water level attained was approximately 27%. The low level trip occurs at 25%. The cause of the controller failure is currently under investigation. The unit is currently stable in Hot Standby. Pressurizer heaters and sprays, normal charging and letdown, and the reactor coolant pumps are currently being utilized for primary system pressure, level, and transport control. Secondary steam is being dumped to the main condenser, and auxiliary feedwater is supplying water to the steam generators. All containment parameters are normal. The licensee plans to notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37526 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-11-15 19:30 | 2000-11-15 20:30 | 2000-11-15 | LOSS OF PRIMARY METEOROLOGICAL TOWER INDICATIONS The licensee suffered a loss of all indications from the primary meteorological tower and loss of backup meteorological tower delta temperature in the control room and safety parameter display system. The backup meteorological tower indications available are wind speed and direction. This reduces the ability to perform prompt offsite dose assessment. The cause is unknown and is being investigated. There were no operations or work ongoing at the time. The licensee intends to notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37525 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-11-15 17:50 | 2000-11-15 19:04 | 2000-11-16 | AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL The plant received a low water level reactor scram during turbine manipulation after 2 turbine bypass valves opened. All systems functioned as designed. The actual cause is not fully understood and is under investigation. The licensee notified the NRC Resident Inspector. * * * UPDATE 1513EST ON 11/16/00 FROM STEVE FULLER TO S. SANDIN * * * The following information was received as an update: "On 11/15/00 at 1748 EST, Oyster Creek Nuclear Generating Station automatically scrammed on reactor low water level (as described on Event Number 37525). The station was in the process of restarting from the plant from the recent 1 SR refueling outage. The operators were in the process of securing High Pressure Turbine warm-up and preparing to perform Steam Chest warm-up. As they transitioned between these activities, the turbine bypass valves opened. As a result of the bypass valves opening, reactor water level increased. The operators responded to the reactor water level transient but failed to recognize the pressure reduction. The loss of inventory resulted in a low water level reactor scram. "The station has conducted a transient assessment of this incident. The preliminary root cause was identified as a procedural deficiency. The Turbine System Operating Procedure did not provide the appropriate guidance for preventing the bypass valves from opening. Additionally, the operators demonstrated a lack of integrated system knowledge and response regarding the turbine controls system. "Subsequent reviews of the plant data revealed that the cool down rate exceeded the plant's Technical Specification limit of 100 degrees per hour. This occurred because of the low initial power level coupled with the bypass valves not being closed in a timely manner. Engineering has assessed this condition and determined that the plant response was within our design bases. Additionally, the Post Transient Review Group (PTRG) identified a potential concern regarding the operation of the reactor low water level transmitters. One of the four reactor low water level scram switches did not actuate. Even though the PTRG suspected this switch didn't actuate because the decrease in reactor water level wasn't sufficient due to the low initial power level, this switch was subsequently tested and operated appropriately. "Following completion of the required restart activities, the plant commenced startup activities at 2:57 EST on 11/16/00. In accordance with 10CFR50.73 a Licensee Event Report will be submitted to describe this incident, the root cause, and associated corrective actions." The licensee will inform the NRC resident inspector. Notified R1DO(Barkley). | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37524 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-15 14:22 | 2000-11-15 15:49 | 2000-11-16 | MANUAL REACTOR TRIP DUE TO FAILURE OF TURBINE RUNBACK ACTUATION CIRCUITS Unit 2 experienced a turbine runback at 1410 EST. The control room operators noticed all status lights for overpower and overtemperature delta T runback were illuminated. The operators decided to manually trip the reactor from about 23 % rated thermal power. The reactor trip resulted in a turbine trip as expected. Auxiliary feedwater pumps started due to low-low steam generator levels. The unit is stable in Mode 3. The runback bistables are locked in without having the logic bistables tripped that feed the trip circuit. The licensee is troubleshooting the problem and the cause is unknown at this time. The plant will remain in Mode 3 until the problem is corrected. The licensee notified the NRC Resident Inspector. * * * UPDATE 1345EST FROM TIM HEADNON TO BOB STRANSKY * * * The licensee is updating their report to include the following information: "On November 15, 2000, McGuire Unit 2 experienced a turbine runback which ultimately resulted in plant operators manually tripping the reactor (RPS Actuation). Following the trip, the Unit 2 Auxiliary Feedwater Pumps started due to low-low steam generator levels (ESF Actuation) "Further investigation has determined that the turbine runback was caused by actuation of all four channels of over power delta temperature (OPDT) and over temperature delta temperature (OTDT) runback logic following a trip of an electrical breaker which supplies power to the logic circuitry. The turbine runback was a result of the breaker trip and was not initiated by a valid OPDT or OTDT condition. Subsequent to the turbine runback, a decision was made to manually trip the reactor. Plant equipment necessary to safely shutdown the unit operated correctly and the Unit is stable and in Mode 3. The Unit 2 Auxiliary Feedwater Pumps have been secured. Actions needed to restart Unit 2 are in progress." The licensee informed the NRC resident inspector. Notified R2DO(Ernstes). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37523 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-11-14 16:45 | 2000-11-14 17:35 | 2000-11-14 | OFFSITE NOTIFICATION DUE TO A DEAD GREEN SEA TURTLE FOUND IN THE PLANT INTAKE "A dead green sea turtle was discovered caught in the barrier net located in the plant's intake canal. Initial indications are that the turtle may have become caught in the net and drowned. The Florida Fish and Wildlife Conservation Commission was notified at 1645 hours on 11/14/00. In addition to the requirements of 10 CFR 50.72 (b) (2) (vi), this event is being reported under Section 4.1 of the plant's Environmental Protection Plan Appendix B Part II of the plant's Technical Specifications, which requires notification of a significant environmental impact causally related to station operation within 72 hours via the ENS." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | NON CFR REPORT REQMNT |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37522 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-11-14 15:30 | 2000-11-14 15:43 | 2000-11-14 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY The licensee determined that the Emergency Response Data System (ERDS) was unavailable as of 0937 EST on 11/8/00. The system was restored as of 1544 EST today, 11/14/00. The cause of the problem is being investigated and is unknown at this time. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37521 | 0 | BELLEFONTE NUCLEAR PLANT |  |  |  |  | 2000-11-14 | 2000-11-14 14:20 | 2000-11-14 | MISSING Co-60 CALIBRATION SOURCE The following is quoted from a facsimile: The purpose of this call is to report missing licensed byproduct material at BLN [Bellefonte] under TVA Byproduct Material License No. 41-08165-10. This report is being made under 10 CFR 20.2201. Event: Upon physical inventory at BLN of byproduct material being prepared for shipment to SQN [Sequoyah], it was discovered that a Co-60 source for a calibration unit was missing. The source is in solid form as cobalt chloride salt. The original source activity on May 11, 1979 was 350 µCi. The current activity for this source is estimated at about 21 µCi. On 10/15/00 the calibration unit was completely disassembled and a survey of the warehouse determined the source could not be located. Disposition: From preliminary evaluation of the documentation and circumstances, it appears the source was never included with the calibration unit at the time of initial receipt from the General Electric Co. (GE) on 2/3/82. GE has been contacted and is presently conducting an evaluation of their records. Background: The subject calibration unit was originally purchased for use at TVA's Hartsville Nuclear Plant (HNP). However, due to the deferral of HNP, the unit was shipped directly from GE to BLN for storage until needed. NRC amended TVA's Byproduct Material License No. 41-08165-10 to allow receipt of Co-60 at BLN on July 28, 1981. TVA's preliminary investigation of the documentation affecting this calibration unit determined that the wooden shipping crate was only physically opened one time since it was received at BLN. TVA's records indicate that TVA personnel opened the shipping crate on 8/25/87 for inventory and radiation survey purposes. Records indicate that the source was inaccessible because of an inoperable lever on the calibration unit. Therefore, surveys were limited to the external surfaces of the calibration unit. Based on preliminary evaluation of the readings recorded during the radiological survey that was performed on the exterior of the calibration unit on 8/25/87 as compared to the surveys performed for the Sequoyah transfer, it appears that the Co-60 source was not shipped with the calibration unit from GE in 1982. TVA has initiated a Problem Evaluation Report and is currently developing corrective actions to address this event. TVA is continuing to investigate this incident and will provide NRC a written report within 30 days of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | AL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37520 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2000-11-14 13:12 | 2000-11-14 14:00 | 2000-11-14 | OFFSITE NOTIFICATION DUE TO SPILL OF HAZARDOUS SUBSTANCE SPILLED TO WATER The licensee reported a spill of approximately 2 gallons of paint thinner (Reducer 54, R7 K54, ANSI 70 vinyl, P/C #7104) that was being used to clean paint brushes. Wind blew the tarp which in turn overturned the bucket of thinner which spilled into Lake Keowee. The Hazardous Materials Team was dispatched and the spill was cleaned up as of 12:55 PM on 11/14/00. The licensee notified the National Response Center, the South Carolina Warning point, the Oconee law enforcement center, and the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37519 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-11-14 12:45 | 2000-11-14 13:53 | 2000-11-14 | OFFSITE NOTIFICATION DUE TO FUEL OIL LEAK "Notifying NRC Operations Center per requirements of 10CFR50.72(b)(2)(vi). Any event related to protection of environment for which a notification to a government agency has been made. New Hampshire Department of Environmental Services was notified at 1245 on 11/14/00 regarding a fuel oil leak from the Auxiliary Boiler Fuel Oil Storage Tank. We have indications of discharge of #2 fuel oil into the ground for a buried supply or return fuel oil pipe. No known discharge to any navigable water ways. Currently excavation is continuing to identify source of leakage." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37518 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-11-13 09:15 | 2000-11-13 15:32 | 2000-11-13 | LICENSEE EMPLOYEE TESTED POSITIVE FOR ALCOHOL DURING A RANDOM FITNESS-FOR-DUTY TEST (24-HOUR REPORT PER 10 CFR 26.73.a(2)(ii)) A non-licensed employee tested positive for alcohol during a random fitness-for-duty test conducted on 06/07/00. The individual's access authorization has been suspended and badge deactivated. Plant safety has not been affected by this event. (Call the NRC operations officer for additional information.) The licensee notified the NRC resident inspector. * * * UPDATE by M. Shaffer on 11/14/00 at 0857ET taken by MacKinnon * * * Fitness-for-duty test was conducted on 11/13/00 instead of 06/07/00. R1DO (Eric Reber) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0
37517 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-11-13 11:00 | 2000-11-13 15:31 | 2000-11-13 | LICENSEE EMPLOYEE TESTED POSITIVE FOR ALCOHOL DURING A FOR-CAUSE FITNESS-FOR-DUTY TEST (24-HOUR REPORT PER 10 CFR 26.73.a(2)(ii)) A non-licensed employee tested positive for alcohol during a for-cause fitness-for-duty test conducted on 11/13/00. The individual's access authorization has been suspended and badge deactivated. Plant safety has not been affected by this event. (Call the NRC operations officer for additional information.) The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0
37516 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-11-11 11:19 | 2000-11-11 11:55 | 2000-11-11 | OFFSITE NOTIFICATION - DEAD GREEN SEA TURTLE AT 1119 ON 11/11/00, a notification was made to the Florida Fish and Wildlife Conservation Commission regarding a dead green sea turtle found in the plant's intake canal. The fatality is not believed to be related to plant operation. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37515 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-11-10 11:07 | 2000-11-10 14:31 | 2000-11-10 | ESF ACTUATION ESF actuation due to a invalid Train B Safety Injection signal. No ECCS system discharge to the Reactor Coolant System occurred. The event cause appears to be a procedure deficiency during scheduled calibration / testing of a Pressurizer Pressure instrument channel. The calibration procedure did not require adequate verification of other channel parameters prior to removing this channel from service, and did not veify blocks normally in place for this plant condition. One channel of Pressurizer Pressure was already in a tripped condition when this channel was removed from service. This satisfied the two out of four logic to initiate the Safety Injection signal. Only the Train B equipment was actuated. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37514 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-11-10 10:29 | 2000-11-10 13:33 | 2000-11-10 | ESF ACTUATION - EMERGENCY DIESEL GENERATOR STARTS During the performance of the procedure for protective relay calibration and testing on Unit 2 Safeguards Bus 2A06, an undervoltage signal was generated on bus 2A06. The undervoltage signal was generated when the technicians checked the continuity between two test points on bus 2A06 as specified in the procedure. On the undervoltage signal, the main feed breaker to bus 2A06 opened, bus 2A06 de-energized G-03 Emergency Diesel Generator (EDG) started, G-04 EDG started, and the G-04 EDG output breaker closed to re-energize bus 2A06. These actuations are as designed for an undervoltage condition on bus 2A06. Unit 2 is currently defueled in a refueling outage. Spent fuel pool cooling was not interrupted. Unit 1 is at 100% power. The appropriate Abnormal Operating Procedure was entered and completed. G-03 EDG, which was running unloaded, has been shutdown. After determining the cause of the undervoltage and verifying bus 2A06 condition was acceptable, we have re-established normal offsite power to bus 2A06. G-04 EDG has been shutdown. The licensee is investigating the cause of this event. The NRC resident inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37513 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-11-10 10:55 | 2000-11-10 11:29 | 2000-11-10 | UNUSUAL EVENT DECLARED DUE TO FIRE ONSITE The licensee declared an Unusual Event due to a small fire in the radwaste truck lock. Grinding was being performed as part of maintenance activities, igniting some material beneath the floor. The site fire brigade responded to the fire, but did not extinguish the fire within 10 minutes. The licensee believes that the fire has been extinguished, but there is still some smoke in the area. The licensee reported that the local fire department also responded to the site. No radiological release has occurred as a result of the fire. The NRC resident inspector will be informed of this event by the licensee. * * * UPDATE AT 1220 ON 11/10/00 BY COOLIDGE, RECEIVED BY WEAVER *** The licensee terminated the Unusual event at 1217. The fire is out, there was no extension and all air samples measured showed no airborne contamination. The resident inspector has been informed. The operations center notified the RDO (Evans); EO (Marsh) and Fema (Eches). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | MA | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37512 | -1 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2000-11-10 06:10 | 2000-11-10 09:52 | 2000-11-13 | OFFGAS ISOLATION VALVE FAILED TO CLOSE UPON DEMAND "At 0610 on November 10, 2000, the offgas isolation valve to the station ventilation stack (2N62-F057) failed to close when the main control room control switch for the valve was placed in the 'close' position. The valve subsequently closed approximately 20 minutes later without other action taken. The valve is air operated and is designed to close upon receipt of a high offgas release rate or via the control switch. There were no abnormal radiological releases occurring at the time of the failure. The unit was in the process of being shut down for a planned refueling outage. No other problems occurred during the event. All systems operated as designed except as described. A prompt investigation has been initiated to determine the cause of the valve failure. Corrective actions will be taken to address the cause." The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTED AT 1526 EST ON 11/13/00 BY DAN COVEYOU TO FANGIE JONES * * * This event has been retracted. "Further investigation has determined that this valve serves no safety function. The investigation has determined that while the design of this valve is to close upon a high radiation condition, this is not an accident mitigation function. The equipment is not safety related nor single failure proof; there are no safety design bases for this valve." The licensee has notified the NRC Resident Inspector. The R3DO (Bruce Jorgensen) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37511 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-11-10 02:17 | 2000-11-10 04:54 | 2000-11-10 | LOSS OF POWER TO 4kV ESF BUS DURING TESTING "A failure of a voltage regulator transformer on 1B diesel generator occurred during a planned ESF test, requiring an emergency shutdown of the diesel generator. This resulted in a loss of power to 4160V essential bus 1ETB. Systems required for the current mode of operation were unaffected as the B train components were removed from service for the test. Power has been restored to the bus from offsite power at this time." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37510 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2000-11-09 17:20 | 2000-11-09 21:59 | 2000-11-09 | FITNESS FOR DUTY A CONTRACT SUPERVISOR RECEIVED A CONFIRMED POSITIVE TEST RESULT. THE INDIVIDUAL WAS ESCORTED FROM THE PROTECTED AREA AND ACCESS WAS SUSPENDED. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0
37509 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-11-09 13:25 | 2000-11-09 15:01 | 2000-11-09 | OUTSIDE DESIGN BASIS - TRAVELING SCREEN COVERS NOT KEPT IN PLACE A review of USAR Section 2.6 identified an apparent discrepancy between plant design and current configuration. USAR and original plant Safety Evaluation identified modification to the plant to mitigate high lake level conditions to preclude flooding within safety related areas. Included in these features are closed and strengthened traveling water screen covers. KNPP has historically operated with these covers in the open position, which is contrary to the USAR. This is being considered as outside of design basis. Actions have been taken to close and brace the covers in the closed position. The licensee notified the NRC resident inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37508 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-11-09 10:24 | 2000-11-09 14:15 | 2000-11-09 | Offsite Notification of an oil spill. At 1024 hours, a report was made to the Unit 2 control room identifying a possible oil spill in progress from near the intake structure to the Ohio River. There was a sheen in front of the intake structure; it is not clear if Beaver Valley is the source of the discharge. The abnormal operating procedure for oil spills (1/2AOP-53C.4A.75.6) was entered to respond to the reports. On-site catch basins and oil separators were checked with no evidence of oil in the process streams. On-site equipment was checked for leakage that may have contributed to the spill; none was identified. A boom was placed in front of the apparent discharge point to stop any further release of oil into the Ohio River. Further observation indicated that the oil sheen also existed up river on th e water and on the shore. The source of the oil appears to be the Ohio River, not Beaver Valley Power Station. This report is being made due to the notification of other government agencies as directed by the plant procedure. The notifications began at 1149 hours. The licensee notified the National Response Center, Pennsylvania Department of Environmental Protection, Beaver County Emergency Management Agency and the Pennsylvania Emergency Management Agency. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37507 | 0 | SIEMENS POWER CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2000-11-08 08:35 | 2000-11-09 11:29 | 2000-11-09 | 24-HOUR NRC BULLETIN 91-01 REPORT Event Description: On 11/08/00 at about 8:35 a.m., while conducting an accountability audit of waste material transfers, a Siemens Power Corporation (SPC) process operator identified that a single 4-gallon container of uranium-containing waste material with a net weight of 10.73 kg had been transferred to a 30-gallon drum without first being sampled. Further investigation revealed that the 30-gallon drum contained 40 grams 235U exclusive of the material from the unanalyzed 4-gallon bucket, A high 235U value under normal conditions for a 4-gallon container of this waste weighing 10.73 kg would be 54 grams 235U (waste containing 10% U and assuming 5% 235U enrichment). Based on the highest U content observed in waste from this process (25 %U), the worst case 235U content in this 10.73 kg of waste material would be less than 135 grams. Safety Significance Of Event: The safety significance of this event is low. Assuming the material from the unanalyzed single 4-gallon container contained uranium at historic maximum levels from this process, the mass of 235U present in the 30-gallon waste drum would be less than 175 g (40g + 135g), which is less than 10% of a minimum critical mass. A safe mass of 235U (45% of minimum critical) is 792 grams, assuming 5 wt.% enriched material. If one assumes that all of the waste material in the unanalyzed 4-gallon container was UO2 (an unrealistic assumption), the mass of 235U present in the 30 gallon waste drum would still be less than 513 g assuming 5 wt.% enriched material. The material actually present is < 3.5 wt.% enriched. This waste drum had been stored in a two tier array. However, this type of waste drum is allowed to be stored in a 3 tier array. If this drum, as postulated above to contain 175g 235U, and two additional drums each at SPC's 100 g 235U waste disposal limit were present in a three tier stack, the total mass in the stack would have been approximately 375 g 235U. This is less than 22% of a minimum critical mass. Potential Criticality Pathways Involved: For criticality to occur in a single waste drum, a minimum of about 1760 g 235U is required. Current SOPs require that two independent individuals verify that waste container U contents have been determined by three independent means before the waste container contents are tabulated on a load list (as acceptable for incorporation into a single drum) and allowed to be transferred to a waste packaging area. Two independent individuals are then required to verify the selected buckets are on the load list before the individual bucket contents can be placed into a 30-gallon waste drum. At least 1 3 unanalyzed 4-gallon containers of this type of waste material (at historic high U levels from this process) would have to be placed into a drum before criticality is possible. Multiple additional failures would be required to reach conditions that approach a critical mass in a single drum or in an allowed 3 tier array of drums. Controlled Parameters: For waste drums the controlled criticality parameter mass/allowed surface density Estimated Amount, Enrichment, and Form Of Licensed Material: The licensed material is uranium bearing solid waste. The total 235U present in the waste drum in question was calculated at worst case historic process waste conditions to be <125 grams, with an actual enrichment of < 3.5 wt.% 235U. This is < 10% of the minimum critical mass of material enriched to 5 wt.% 235U. Nuclear Criticality Safety Control(s) Or Control Systems and a Description of the Failures Or Deficiencies: Nuclear criticality safety controls imposed on this waste generation, packaging, and storage process include: analysis of uranium content in the initial waste buckets by three independent means; second party verification of drum load lists for compliance with waste drum limits; second party verification that buckets actually received at the drum loading area match those called for by the drum load list. The control system failed when an operator selected a 4-gallon waste bucket not on the approved load list and the error was not caught by the waste handler tasked to verify that buckets received in the waste handling area matched those on the approved drum load list. A number of factors may have contributed to the failure, including but not limited to: 1 Human factors issues related to reading very similar alpha-numeric characters (in this case AA4072 vs. AC4072); 2 The practice of placing waste buckets inside plastic bags for the sake of contamination control, prior to their being stored in an unlit cargo container. This necessitates transcribing the container ID number to a piece of tape on the outside of the plastic bag, allowing for the possibility of transcription errors. 3 The practice of storing unanalyzed waste buckets destined for process recycle with buckets destined for placement into waste drums. A formal SPC Incident investigation Board (IIB) is investigating the incident. Corrective Actions To Restore Safety Systems and When Each Was Implemented: The process operators finding the infraction promptly notified Criticality Safety. Criticality Safety assembled a multi-disciplinary team to review the infraction and determined the safety significance of the incident to be low but that it met the NRC Bulletin 91-01 Criteria as a 24 hour reportable condition. This team also recommended the following immediate actions: 1 Stop loading waste drums with this type of material. (completed 2 Account for and label all unanalyzed waste buckets of this type of material to assure that no other buckets intended for process recycle have been, or will be, erroneously placed into waste drums. complete) The SPC IIB is formally evaluating incident cause(s) and potential corrective actions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 4 | WA | FUE | [5 empty] | 0
37506 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2000-11-08 | 2000-11-08 18:16 | 2000-11-08 | MOISTURE DENSITY GAUGE MISSING FROM QORE, INC., IN HUNTSVILLE, ALABAMA. The following text is a portion of a facsimile received from the Alabama Office of Radiation Control: "FROM: David Turberville, Radiation Physicist II" "SUBJECT: Alabama Incident File #00-30 - Lost Moisture Density Gauge." "On the morning of November 8, 2000, Shane Kirby, Radiation Safety Officer for Qore, Inc., of Huntsville, Alabama, notified the Alabama Office of Radiation Control stating that it appears that they have lost a CPN model MC-1 moisture density gauge, serial number M1310598? or M13105089? containing 10 millicuries of Cs-137 and 50 millicuries of Am-241/Be. Qore, Inc. is authorized to possess and use the device under Alabama Radioactive Material License No. 1022. The missing device is one of sixteen devices on the licensee's inventory." "Mr. Kirby stated that his records indicate that the device was last used in May of 1999 and was last leak tested on May 16, 1999. Mr. Kirby explained the reason the gauge had not been leak tested or inventoried since May of 1999 was because the file for this device was lost since that time and it did not come to his attention until the file was recently found. Mr. Kirby has no records of transfer since August of 1998." "The Agency last inspected this licensee on January 26, 2000 [...]." "The licensee continues to search the facilities, notify other branches and licensees, and review records of accountability in an effort to locate the device." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0
37505 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2000-11-07 | 2000-11-08 15:34 | 2000-11-08 | PRELIMINARY INCIDENT NOTIFICATION OF THE DISCOVERY OF A TN TECHNOLOGIES SOURCE HOLDER (WITH A 1-CURIE CESIUM-137 SOURCE AND THE SHUTTER LOCKED OPEN) NEAR HUEYTOWN, AL, AND POSSIBLE ILLEGAL TRANSPORT OF THE DEVICE FROM DESIGN FUELS CORPORATION IN McMURRY, PA, DURING THE EARLY 1990s The following text is a portion of a facsimile received from the State of Alabama Department of Public Health, Alabama Office of Radiation Control: "Subject: Preliminary Notification of a Found Source" "Members of the staff of the Alabama Office of Radiation Control (the Agency) traveled to Hueytown, AL, on November 7, 2000, to investigate the finding of a TN Technologies Model-5191 source holder containing 1,000 millicuries of Cs-137 (as of 1985)." "Circumstances of the Event" "Based on initial information, it appears that the general licensed device was illegally transported by Design Fuels Corporation from their facility in McMurry, PA, to Alabama in the early 1990s. During this transport, and until the time it was discovered, the device shutter was locked in the open position. The device was discovered in a wooded area away from personnel, on private property not accessible to the general public. It is believed the device had been in that location since early 1992." "The device shutter has subsequently been locked in the closed position, and the device [has been] moved to a secure storage location near Hueytown, AL, pending determination of final disposition. Maximum exposure readings with the shutter open were 2.6 rem/hr at near contact with the pipe opposite the source holder. After closing the shutter, maximum readings are 1.8 mrem/hr at contact with the pipe opposite the source holder, 0.5 mrem/hr at 30 cm, and 7.0 mrem/hr at contact with the source holder. The source was tested for leakage. Leak test results were negative." The Alabama Office of Radiation Control notified the NRC Region II office (Richard Woodruff). At this time, the NRC Region II office plans to clarify this information with the State, notify the Environmental Protection Agency, and issue a Preliminary Notification of Event or Unusual Occurrence. (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | AL | OTH | AGR |  |  |  |  | 0
37504 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2000-11-04 13:00 | 2000-11-08 14:10 | 2000-11-13 | TWO PATIENTS GIVEN INCORRECT DELIVERED DOSE The Radiation Safety Officer from Aultman Hospital, on November 4, 2000, at 1300 hours, notified the Ohio Department of Health, that two patients received brachytherapy doses involving Ir-192 temporary implants in excess of 20% of the prescribed dose. The misadministration were discovered during an internal audit of the licensee's Quality Management Program on November 3, 2000, by the Radiation Safety Officer and Radiation Protection Staff. One patient received two courses of brachytherapy treatments with Ir-192 temporary implants. On September 18, 2000, the delivered dose was 3330 cGy, while the prescribed dose was 2000 cGy. This represents a delivered dose discrepancy of 67%. On October 9, 2000, the prescribed dose was 2250 cGy, while the delivered dose was 3500 cGy. This represents a delivered dose discrepancy of 56%. The patient also had external beam therapy treatment from a linear accelerator that was not considered in this misadministration. Another patient received two courses of brachytherapy treatments, with only one brachytherapy treatment qualifying as a misadministration. On August 22, 2000, the delivered dose from Ir-192 was 3500 cGy, while the prescribed dose was 1980 cGy. This represents a delivered dose discrepancy of 78%. The patient also had external beam therapy treatment from a linear accelerator that was not considered in this misadministration. The primary notification from the licensee indicates that the misadministrations are due to operator error in data entry of the source strength in the treatment computer. The facility has recently acquired a new computer, and the operator mistakenly entered the source strengths into the computer as milligram-Radium equivalent (mg-Ra-eq) strengths instead of units of millicuries. The licensee does not anticipate any adverse effects to the patients as a result of the additional doses. One patient was notified of the misadministration on November 3, 2000. The other patient will be notified later this week by the radiation oncologist, as the referring physician was not immediately available. The Licensee shall submit a written report to the Ohio Department of Health, Bureau of Radiation Protection, within 15 days after discovery of the misadministration, as delineated in 10 CFR 35.33(2). * * * UPDATE AT 1430 EST ON 11/13/00 BY MARK LIGHT TO FANGIE JONES * * * After review of procedures performed by the hospital, two additional overexposures have been determined to have occurred on October 23, 2000 and October 30, 2000. The hospital notified the Ohio Department of Health, Bureau of Radiation Protection on November 13, 2000 at 0910 EST. The third patient received one course of brachytherapy treatment with Ir-192 temporary implants. On October 30, 2000, the delivered dose was 3240 cGy, while the prescribed dose was 1890 cGy. This represents a delivered dose discrepancy of 71%. The patient also had external beam therapy treatment from a linear accelerator that was not considered in this misadministration. The fourth patient received two courses of brachytherapy treatments with Ir-192 temporary implants. On October 23, 2000, the delivered dose was 3150 cGy, while the prescribed dose was 2025 cGy. This represents a delivered dose discrepancy of 56 %. On November 6, 2000, the second prescribed dose was 1400 cGy, which was delivered correctly. The patient also had external beam therapy treatment from a linear accelerator that was not considered in this misadministration. The notification of the third and fourth patient is pending. The licensee reports that the clinical treatment of all patients has not been affected by the misadministration. As soon as the licensee's management determined that a reportable event had occurred, the licensee took action to provide additional training to staff involved in brachytherapy procedures. The licensee is reviewing their current Quality Management Program. The Ohio Department of Health, Bureau of Radiation Protection will conduct an on-site investigation to review the procedures and finding of the licensee's Quality Management review and to confirm the adequacy of corrective actions to prevent reoccurrence. The R3DO (Bruce Jorgennsen) and the NMSS EO (Wayne Hodges) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0
37503 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-11-08 11:37 | 2000-11-08 12:10 | 2000-11-08 | OFFSITE NOTIFICATION REGARDING THE CAPTURE OF AN INJURED GREEN SEA TURTLE IN THE PLANT'S INTAKE NET The following text is a portion of a facsimile received from the licensee: "At 1137 on 11/08/00, a notification was made to the Florida Fish and Wildlife Conservation Commission regarding a live green sea turtle found in the plant's intake net. The turtle will be sent to an offsite rehabilitation facility. [...] The notification to a State Government Agency requires a notification to the NRC per 10CFR50.72(b)(2)(vi)." The licensee stated that the turtle was apparently injured by a boat propeller before entering the plant's intake. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37502 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-11-07 14:00 | 2000-11-07 18:18 | 2000-11-07 | OFFSITE NOTIFICATION REGARDING THE DISCOVERY OF A DEAD SEA TURTLE IN THE INTAKE The following text is a portion of a facsimile received from the licensee: "[The unit] was operating 100% with all [systems] normal for MODE 1. Maintenance was pulling an intake structure BAR rack in preparation for routine cleaning when the crew noticed a partially decomposed sea turtle floating to the surface. The dead sea turtle was retrieved and sent to the National Marine Fisheries Service (NMFS) for analysis." "NMFS has previously conducted an endangered species Act consultation with the NRC and FPC. This consultation resulted in the establishment of sea turtle protection criteria under a Biological Opinion and an Incidental Take Statement. This turtle discovery is within the sea turtle protection criteria established by the NMFS with FPC. A written report will be submitted to NMFS." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37501 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-07 15:01 | 2000-11-07 16:55 | 2000-11-07 | FEEDWATER ISOLATION DUE TO CYCLING OF A BOILER FEED (BF) VALVE AND THE SUBSEQUENT STEAM GENERATOR WATER LEVEL PERTURBATION The following text is a portion of a facsimile received from the licensee: "[The] 21 steam generator level rose to the high-high level trip setpoint of 67% narrow range level at which time a feedwater isolation signal was generated. This is an [engineered safety feature (ESF)] actuation. The plant is in Mode 4 at 332°F reactor coolant system temperature with [four] reactor coolant pumps in service. Steam generator levels were being maintained by intermittent feed with the main feed system and auxiliary feed system in standby. Temperature control is via steam dumps to [the] condenser. The 21 through 24BF13s and BF40s went closed. With the exception of [the] 21BF19, the 22 through 24BF19s were already closed. The 21BF19 went closed due to the high-high level. The condition was caused by cycling open of [the] 21BF19 during troubleshooting of position indication. [The] feedwater isolation is currently reset, and steam generator levels are being maintained with main feed as prior to the event. No other steam generator levels were effected, and 21 steam generator level is returned to the pre-event level of [approximately] 40% narrow range." The licensee stated that all systems functioned as required. The licensee plans to notify the NRC resident inspector and the Lower Alloways Creek Township. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37500 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-11-06 12:49 | 2000-11-07 12:23 | 2000-11-07 | POSITIVE FOR-CAUSE TEST FOR ALCOHOL REPORTED IN ACCORDANCE WITH 10 CFR 26.73.a(2)(ii) A contract supervisor was determined to be under the influence of alcohol during a for-cause test. The individual's site access was suspended, and the individual was subsequently terminated. (Contact the NRC operations officer for addition details.) The licensee notified the NRC resident inspector and plans to notify the NRC Region 3 office. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0
37499 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-11-07 05:10 | 2000-11-07 06:35 | 2000-11-07 | DEDICATED TELEPHONE SYSTEM FOR STATE NOTIFICATIONS INOPERABLE During testing of the Emergency Notification Network (ENN) to the states of Georgia and Alabama, the system failed producing a constant hum on the speaker in the control room. The licensee notified their Birmingham office to initiate repairs. There is currently no estimate available for restoration. The licensee informed the affected states via commercial telephone and will inform the NRC resident inspector. * * * UPDATE 0919EST ON 11/7/00 FROM ROBERT FUCICH TO S. SANDIN * * * The licensee returned the ENN system to service as of 0744EST and will inform the NRC resident inspector. Notified R2DO(Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37498 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-11-07 02:31 | 2000-11-07 05:30 | 2000-11-07 | HIGH PRESSURE COOLANT INJECTION (HPCI) ISOLATED AND INOPERABLE DUE TO FAILED STEAM LEAK DETECTION SYSTEM TEMPERATURE ELEMENT "On November 7, 2000 at 0231[EST] Limerick Generating Station received a High Pressure Coolant Injection (HPCI) System isolation due to a failed Steam Leak Detection System temperature element. Outboard isolation valves HV-055-2F003, HV-055-2F100, HV-055-2F041 and HV-055-2F042 received isolation commands. The system isolated as designed. Investigation [into] the cause of the failed temperature element is ongoing. The HPCI system remains isolated and inoperable." Unit 2 is in a 14-day LCO A/S. Other ECCS equipment has been verified operable. The licensee informed the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(iii)(D) |  |  | 0
37497 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-11-06 15:41 | 2000-11-06 17:07 | 2000-11-06 | GROUP II, PRIMARY CONTAINMENT ISOLATION VALVE (PCIV), ISOLATION FOLLOWING A PLANNED MANUAL REACTOR SCRAM The following text is a portion of a facsimile received from the licensee: "A Group II PCIV isolation (setpoint +3.0 inches) occurred at 15:41 on 11/06/00 following a planned manual reactor scram ([that occurred at] 1540 on 11/06/00)." "Prior to the scram, reactor water level had been increased to approximately 45 inches in anticipation of reactor water level decreasing following the scram." "The planned reactor scram was part of a forced outage." "All valves functioned as required." The licensee stated that reactor water level momentarily decreased to the Group II PCIV isolation setpoint following the reactor scram. The licensee also stated that all systems functioned as required and that there was nothing unusual or misunderstood. All rods fully inserted following the reactor scram. The Group II isolation has been reset, and the PCIV valves have been returned to their original positions. The NRC resident inspector was in the control room at the time of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37496 | 0 | MOUNTAINSIDE HOSPITAL |  |  |  |  | 2000-08-07 | 2000-11-06 15:58 | 2000-11-06 | MOUNTAINSIDE HOSPITAL 10 CFR PART 21 REPORT OF A DEFECTIVE TREATMENT HEAD OF A MICROSELECTRON HIGH DOSE RATE (HDR) UNIT MANUFACTURED BY NUCLETRON-OLD DELFT The following text is a portion of a facsimile received from Mountainside Hospital: "At the request Mr. David B. Everhart, who is conducting a field inspection of our facility today, we are filing a report following the criteria of 10 CFR [PART] 21, 'Reporting of Defects and Noncompliance.' " "3. The defective component was the treatment head of our Microselectron HDR Unit manufactured by Nucletron-Old Delft [...]." "4. The defect involved the failure of the treatment head to prevent the check source and the HDR source from driving past the optical interlock when no applicator was connected to the unit. The incident occurred during machine warmup. There were no injuries to either patients or staff." "5. The incident occurred on 8/7/00. A service call was placed to Nucletron [...]. Later that day, a service engineer from Nucletron visited our site. The problem could not be reproduced [...] nor has it occurred any time since." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21 |  |  |  | 0
37495 | 0 | MOUNTAINSIDE HOSPITAL |  |  |  |  | 1999-07-14 | 2000-11-06 15:58 | 2000-11-06 | MOUNTAINSIDE HOSPITAL 10 CFR PART 21 REPORT OF A DEFECTIVE TRANSFER TUBE THAT IS USED IN CONJUNCTION WITH A HIGH DOSE RATE BRACHYTHERAPY REMOTE AFTERLOADER MANUFACTURED BY NUCLETRON-OLD DELFT The following text is a portion of a facsimile received from Mountainside Hospital: "At the request Mr. David B. Everhart, who is conducting a field inspection of our facility today, we are filing a report following the criteria of 10 CFR [Part] 21, 'Reporting of Defects and Noncompliance.' " "3. The defective component was a transfer tube that is used in conjunction with our High Dose Rate brachytherapy remote afterloader manufactured by: Nucletron-Old Delft, [...]." "4. The defect involved separation of a metal connector end from the transfer tube itself. It is unclear whether or not this would create a safety hazard or simply prevent a treatment from being given. In our case, there was no injury to either patients or staff because the failure did not occur during patient treatment and the source was not in an exposed position. Also, the tube itself was intact until removal from the head of the unit was attempted." "5. The incident occurred on 7/14/99. A report of the defect was issued to the FDA on 7/14/99, and a copy of the report sent to Nucletron on 7/15/99 [...]." "6. The defective unit was immediately removed from service and sent to Nucletron for analysis. All other transfer tubes were immediately checked and found to be securely fastened to their connectors. Nucletron sent a replacement transfer tube, and no other problems have transpired with any of the transfer tubes since this incident." (Call the NRC operations officer for site contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21 |  |  |  | 0
37494 | 0 | WESTRONICS |  |  |  |  | 2000-11-03 12:00 | 2000-11-06 14:05 | 2000-11-06 | WESTRONICS CSVC VIDEOGRAPHIC RECORDERS On or about November 3, 2000, Westronics determined that Westronics Series CSVC "Smartview" Nuclear Safety Related videographic recorders, if utilized to measure thermocouple inputs, require hardware modification to ensure accurate measurement. The hardware modification requires installation of capacitors associated with the Dallas 1620 Temperature Compensation Chips. Instruments which would require the modification were shipped between July 16, 1998 and July 7, 2000. Nuclear Power Plants affected are Riverbend, Shearon Harris, and Brunswick. Westronics Corrective Action includes installation of the capacitors. Affected Customers will be notified in accordance with the requirements of 10CFR21. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0
37493 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2000-11-06 10:00 | 2000-11-06 12:29 | 2000-11-06 | ARIZONA RADIATION REGULATORY AGENCY REPORT REGARDING A SOURCE MISSING FROM PHELPS DODGE, BAGDAD, INC. IN BAGDAD, ARIZONA The following text is a portion of a facsimile received from the Arizona Radiation Regulatory Agency: "This First Notice constitutes EARLY notice of events of POSSIBLE safety or public interest significance. The information is as initially received WITHOUT verification or evaluation and is basically all that is known by the Agency Staff at this time." "Date: November 6, 2000 Time: 10:00 AM (MST) First Notice: 00-12 Arizona Licensee: Phelps Dodge, Bagdad, Inc. [...] License No. 13-005 [...]" "At approximately 11:30 AM, October 30, 2000, the Agency received a letter advising that a Cadmium-109 source was missing. This information was supplied by the Radiation Safety Officer. The information supplied indicated that the LICENSEE was unsure when the source disappeared. Agency inspection reports indicate that the last time that the LICENSEE reported seeing the source [was on a January 1998 inventory]. The missing source is a Texas Nuclear Model 696782, Serial Number LU-6484. The source [contained] 15 millicuries as of 6/89. Current estimated activity is approximately 40 microcuries of Cadmium-109." "The LICENSEE and the Agency continue to investigate this event." "The U.S. NRC and the U.S. FBI are being notified of this event." (Call the NRC Operations Officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0
37492 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-11-06 03:38 | 2000-11-06 05:29 | 2000-11-06 | 1-HOUR SECURITY REPORT SAFEGUARDS SYSTEM DEGRADATION RELATED TO PERIMETER MONITORING. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR ADDITIONAL DETAILS. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 0
37491 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-11-05 17:07 | 2000-11-05 20:44 | 2000-11-05 | MANUAL REACTOR TRIP ON ROD CONTROL PROBLEM "Reactor startup was in progress. Power was stabilized at 10E-8 amps in the intermediate range to take critical data. A rod control urgent failure was received when the last rod step was taken to stabilize power. Maintenance was called to investigate. After troubleshooting, a card was replaced in the logic cabinet. Rods were requested to be inserted 1 step after card replacement for post maintenance testing. Rods continued to move in with no demand. Rods inserted 2.5 steps until another urgent failure came in and stopped rod motion. The reactor trip breakers were opened at this time." All rods fully inserted and all other systems functioned as required. Troubleshooting will continue for the rod control system. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37490 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-11-05 14:07 | 2000-11-05 16:38 | 2000-11-05 | UNEXPECTED AUTOMATIC START OF THE G-03 EDG "During 2A06 Bus recovery work, from a scheduled bus maintenance outage, there was an automatic start of G-03 Emergency Diesel Generator (EDG). This was an inadvertent actuation and not part of the planned bus recovery work. G-03 EDG started and ran unloaded due to a 4160 Bus under voltage, that was caused by fuse replacement as part of the bus restoration procedure. The G-03 EDG output breaker 2A52-87 is currently out of service as part of the 2A06 bus outage, so the diesel could not have closed onto the dead bus. G-03 EDG was and is still lined up for normal operation to the 1A06 bus. Further investigation is continuing into the root cause of this actuation. "All buses remained energized and there were no other abnormal indications. Currently Unit 2 is in a refueling outage and is defueled at this time. Unit 1 is at 100% power normal operation." The sequence of actions taken were wrong in that the fuses were replaced when they should not have been. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37489 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-05 01:20 | 2000-11-05 04:39 | 2000-11-05 | UNUSUAL EVENT DECLARED DUE TO A POTENTIAL BOMB THREAT THE LICENSEE DECLARED AN UNUSUAL EVENT DUE TO A POTENTIAL BOMB THREAT. THE LICENSEE INFORMED STATE/LOCAL AUTHORITIES AND WILL INFORM THE NRC RESIDENT INSPECTOR. THE NRC WAS PLACED IN THE MONITORING PHASE OF THE NORMAL MODE OF OPERATION BY THE RIV RA ( MERSCHOFF) AT 0400CST FOLLOWING DISCUSSIONS WITH IRO (GIITTER) AND THE EO (RICHARDS) . REGION IV INCIDENT RESPONSE CENTER WAS OPERATIONAL AT 0456CST. NOTIFIED CHAIRMAN'S STAFF (TSCHILTZ) , EDO STAFF (SMITH), AND HEADQUARTERS PAO (GAGNER). * * * 0610EST ON 11/5/00 FROM DAVID PIERCE TO S. SANDIN * * * THE LICENSEE TERMINATED THE UNUSUAL EVENT AT 0237PST AFTER DETERMINING THAT THE BOMB THREAT WAS NOT CREDIBLE. THE LICENSEE INFORMED STATE/LOCAL AGENCIES AND THE NRC RESIDENT INSPECTOR. RIV IRC AND FEMA (SULLIVAN) NOTIFIED. * * * 0700EST ON 11/5/00 * * * COMMISSIONER'S ASSISTANTS BRIEFING CONDUCTED. * * * 1655 EST ON 11/4/00 * * * The NRC exited Monitoring Phase of the Normal Mode of Operation by NRC Region 4 Regional Administrator (Ellis Merschoff) following discussion with IRO (Joseph Giitter) and R4 DRP (Kenneth Brockman). Notifications made include EDO's office (Garrett Smith), Chairman's office (Alan Levin), PAO (Sue Gagner). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37488 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-05 00:30 | 2000-11-05 04:21 | 2000-11-05 | 1-HR SECURITY REPORT POTENTIAL BOMB THREAT. IMMEDIATE COMPENSATORY MEASURE TAKEN UPON DISCOVERY. LICENSEE HAS INFORMED STATE/LOCAL AGENCIES AND WILL INFORM THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR ADDITIONAL DETAILS. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 0
37487 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2000-11-04 08:22 | 2000-11-04 08:27 | 2000-11-07 | LOSS OF POWER TO THE EOF DUE TO PLANNED MAINTENANCE "LOSS OF POWER TO THE EMERGENCY OPERATIONS FACILITY. THIS IS A PREPLANNED MAINTENANCE ACTIVITY ON BREAKER H2110. THE REMOVAL OF THIS BREAKER CAUSES THE FACILITY (EOF) TO LOSE POWER AND IS, THEREFORE, 'POTENTIALLY' UNAVAILABLE FOR GREATER THAN 90 MINUTES. THE TOTAL ESTIMATED DURATION OF THE ACTIVITY IS 8 HOURS." THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. * * * UPDATE AT 1040EST ON 11/7/00 FROM BRUCE LUTHANEN TO S. SANDIN * * * The licensee is retracting this report based on the following: "Event Notification 37487 is hereby retracted, This notification reported the unavailability of the Emergency Operations Facility (EOF) due to an electrical maintenance activity that removed power from the EOF, as required by plant operating procedures. "The guidance for the one-hour call reporting criteria was obtained from a plant instruction which specifically stated that a one-hour-call to the NRC shall be made 'if, in the judgment of the Control Room Shift Supervisor, equipment failure or extensive maintenance activities have or will render one or more of the Perry onsite ERFs [Emergency Response Facilities] unavailable..' "10 CFR 50.72(b)(1)(v) requires one-hour, non-emergency notification for 'any event that results in a major loss of emergency assessment capability, offsite response capability, or communications capability (e.g. significant portion of control room indication, Emergency Notification System or offsite notification system.)' "The EOF electrical maintenance was a planned, scheduled activity. The Alternate Emergency Operations Facility was available during this time to provide redundancy of all required EOF features dealing with emergency assessment and offsite communication. This capacity was never lost or degraded, and so the criteria for reporting were not met. There is no corresponding section under 10 CFR 50.73, and so an LER is not required." The licensee informed the NRC resident inspector. Notified R3DO(Wright). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37486 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-11-02 14:30 | 2000-11-03 14:27 | 2000-11-22 | CRITICALITY ALARM HORNS AIR PRESSURE FOUND OUT OF SPECIFICATION DURING SURVEILLANCE "At 1330 on 11/2/00, the Plant Shift Superintendent was notified that the testing of the C-337 and C-337-A Criticality Accident Alarm System (CAAS) air horn regulators resulted in as found data which is outside of the optimum air pressure band allowed to insure desired horn sound quality. Twelve of the twenty-five CAAS horn regulators located in these two areas were discovered outside the desired pressure band. The effect of this as found condition is unknown at this time and is being evaluated by Engineering. This evaluation will require greater than the 24-hour reporting time limit allowed by 10 CFR 76.120.c.2. Due to the uncertainties and the length of time required to complete the engineering evaluation the condition is being conservatively reported. "Reasonable assurance of operability of CAAS horns in these and other buildings exists based on the successful completion of quarterly and annual TSR surveillances. In addition, all CAAS horn regulators found outside of established criteria during this and previous tests on other building CAAS systems were returned to acceptable values prior to returning the systems to service. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Senior Resident has been notified of this event." The DOE representative will be notified. * * * RETRACTION 1450 11/22/2000 FROM TOM WHITE TAKEN BY BOB STRANSKY * * * "On November 2, 2000, the PSS was notified that the testing of the C-337 and C-337A CAAS air horns had resulted in the discovery that the horn air regulator pressure was outside of the allowed optimum air pressure band used to ensure desired horn sound quality. This condition potentially affected the audibility of twelve of the twenty-five horns located in the C-337 and C-337A. The actual affect on the system was unknown at the time and could not be determined within the 24-hour reporting limit. Thus, the condition was conservatively reported to the NRC per 10CFR76.120(c)(2). Subsequently, System Engineering issued Engineering Notice EN-C-822-00-035 that transmitted the results of Operability Evaluation OE-C-822-00-005. This documented the results of additional CAAS horn testing at the air regulator pressure values noted on November 2, 2000 and testing data in other buildings. The evaluation concluded that although there is an expected amount of drift or variance in the settings of the air pressure regulators [for] the CAAS horns, in the as-found condition, could have performed their intended safety function and pass the audibility criteria described in the SAR." The NRC resident inspector has been informed of this retraction. Notified R3DO (Creed), NMSS (Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
37485 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-11-02 16:45 | 2000-11-03 11:29 | 2000-11-03 | 24 HOUR 91-01 BULLETIN At 1645 CST on 11-02-00, the Plant Shift Superintendent (PSS) was notified of a violation of NCSA GEN-15 Machining waste, defined in NCSE GPS-11 to be potentially fissile, was collected in a 55-gallon drum in the C-720 machine shop in violation of NCSA GEN-15. GEN-15 limits the containers used for accumulating fissile/potentially fissile waste to approved 5.5-gallon container. The purpose of this requirement is to ensure that fissile material will be accumulated in approved containers. SAFETY SIGNIFICANCE OF EVENTS; The mass of fissile material contained in the waste drum is less than what is required to achieve criticality. Therefore, no possibility exists for an inadvertent criticality. However, double contingency was not maintained. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, an additional violation would have to occur resulting in unsafe mass of fissile material accumulating in an unsafe geometry. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): Double contingency for this scenario is established by implementing one control on mass and one control on volume. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): A process limit of 22.3 kg. At 5.5 wt. % 235U would have to be exceeded for a criticality NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES; The two process conditions relied upon for double contingency for this scenario are mass and volume, The first leg of double contingency is based on limiting the mass of uranium accumulated. Analysis has shown that the machining waste from approximately 1490 machining operations would have to be accumulated before exceeding an unsafe mass. The waste would occupy more than eighteen 5.5-gallon containers, which exceeds the volume of the 55-gallon waste container (drum) in the machine shop. This control was not violated. The second leg of double contingency is based on the accumulation of fissile waste only in approved containers, limited to 5.5 gallons. This is controlled by limiting the volume of the containers used for accumulating fissile waste. Potentially fissile waste was placed In a container other than an approved 5.5 gallon container, violating this control. The machining waste exceeded the allowed volume of 5.5 gallons and resulted in a loss of the process condition. Since the volume process condition was lost, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Access to the area containing the 55 gallon drum has been controlled by ropes and signs. Remediation of violation will be made following development of a Remediation Guide. The NRC Resident Inspector was notified. The DOE Representative will be informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37484 | 0 | US ARMY |  |  |  |  | 2000-11-02 | 2000-11-02 16:31 | 2000-11-02 | STOLEN M43A1 CHEMICAL AGENT DETECTOR Council Bluff, Iowa Reserve Unit reported today, to Rock Island, that one M43A1 chemical agent detector, containing 250 µCi (microcurie) of Am-241, was stolen on 6/1/2000. The detector was reported stolen in Omaha, Nebraska to the Omaha police. The device has not been recovered. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0
37483 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2000-11-02 12:00 | 2000-11-02 16:08 | 2000-11-20 | INSTRUMENT AIR CONTAINMENT PENETRATION FAILED LEAKAGE TESTING "Currently Clinton is in RF-7. During performance of LLRTs of the Instrument Air penetration (1 MC-057), AOV 1IA005 (outboard isolation valve) would not close upon demand. The solenoid was later found to be sticking. Therefore, this valve was an as-found failure. Subsequently, the testing of the inboard containment isolation valve in this same penetration (1IA006), showed a leakage of 27,500 sccm at the air regulator assembly. When other known leakage pathways are combined with this leakage, the secondary bypass leakage criteria of 0.08 La (28,883 sccm) is violated (Tech Spec Section 3.6.1.3 SR 3.6.1.3.9), "These valves were repaired, and subsequently successfully passed their LLRTs. "Further analysis of these failures will be performed during the investigation of Condition Report 2-00-10-273." The licensee notified the NRC Resident Inspector. * * * RETRACTION 1815 11/20/2000 FROM JEFF NADEN TAKEN BY BOB STRANSKY * * * "Upon completion of further evaluation of the LLRT results for penetration 1MC-057, it was determined that the actual leakage through this penetration was approximately 751 sccm. This leakage in combination with other known leakage pathways does not exceed the secondary bypass leakage criteria of 0.08 La. As a result of this finding Clinton Power Station is retracting the 10CFR50.72 notification made on 11/2/00." The NRC resident inspector has been informed of this retraction. Notified R3DO (Creed). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37482 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-11-02 13:20 | 2000-11-02 13:33 | 2000-11-02 | OFFSITE NOTIFICATION DUE TO A DEAD TURTLE FOUND IN THE PLANT INTAKE The licensee made a call to the U. S. Fish and Wildlife Agency and the Florida Fish and Wildlife Conservation Commission to notify them of a dead loggerhead turtle (about 40 pounds) found in the plant intake. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37481 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2000-11-01 17:54 | 2000-11-01 19:51 | 2000-11-01 | PLANT SHUTDOWN PROCEDURE NOT IN ACCORDANCE WITH LTOP ASSUMPTIONS "During review of plant procedures associated with the conditions for Low Temperature Overpressurization Protection (LTOP) it was noted that the plant procedure associated with pressurizer cooldown did not appear to be in accordance with the assumptions in the LTOP analysis. An investigation was conducted to determine if this was the case and it has been determined that the analysis assumes that the plant is not operated in a water solid condition in the pressurizer at temperatures above 130 F. Plant procedures do allow water solid plant operation at temperatures below 200 F. A check with operations has determined that it is normal shutdown procedure to take the plant solid soon after temperature is below 200 F (about 180 F). The plant is currently in the process of starting up and heating up. Plant temperature is about 250 F with a bubble in the pressurizer. Current plant operation is in accordance with the LTOP analysis." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37480 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-11-01 14:20 | 2000-11-01 16:20 | 2000-11-01 | OFFSITE NOTIFICATION DUE TO OIL SPILL "A minor oil spill generated a small oil sheen on the Sequoyah Diffuser Pond. This was reported to the National Response Center at 1420 EST today. Based on reporting to another government agency this notification is being made. The oil spill is contained and cleanup in underway at this time." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Refueling |  | Cold Shutdown | Refueling |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37479 | -1 | SCHERING-PLOUGH |  |  |  |  | 2000-11-01 | 2000-11-01 16:08 | 2000-11-02 | MISSING SHIPMENT OF I-125 The licensee reported that a shipment of I-125 (10 vials, 100 µCi each) that was scheduled to arrive via FedEx on 10/31/00 cannot be located. When the package was not checked in to the RSO on 10/31/00, the licensee contacted the local FedEx office and attempted to locate the package. According to FedEx, the package was delivered on 10/26/00. The licensee stated that incoming FedEx packages are not invoiced and signed for individually; instead, a master list of packages is presented with the delivery (the packages are scanned when they are loaded onto the truck). The package has not been reported as misdelivered by any other FedEx customers. * * * RETRACTED AT 1515 EST ON 11/2/00 BY FRED JAEGER TO FANGIE JONES * * * The licensee is retracting the event notification because they received the shipment today from FedEx fully intact and complete, just late. They discussed this with NRC Region 1 (Eric Reber) who informed John Kinneman. The R1DO (Pete Eselgroth) and NMSS (Brian Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37478 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-11-01 13:40 | 2000-11-01 15:32 | 2000-11-01 | UNITS IN UNANALYZED CONDITION DUE TO INOPERABLE SAFEGUARDS COOLING WATER PUMPS "Due to a support system being unqualified (bearing lubrication water supply) the three safeguards cooling water (essential service water) pumps have been declared inoperable. This puts units outside their design basis. The pumps continue to be physically functional. "Compensatory measures are being implemented including provisions for standby replacement water supply and instructions for personnel for implementation. Preparations for an orderly plant two unit shutdown are in progress. A request for a NOED (Notice of Enforcement Discretion) has been initiated with NRR and Region III to allow continued operation until installation of a temporary modification is complete." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37477 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-10-31 17:15 | 2000-10-31 22:40 | 2000-10-31 | 24-HOUR NRC BULLETIN 91-01 REPORT "At 1715 CST on 10-31-00, the Plant Shift Superintendent (PSS) was notified of a violation of an NCSA In the C-400 building. A negative air machine (NAM) was operated in the C-400 Sear Disassembly Area with an expired calibration date on the magnehelic gauge in violation of NCSE GEN-09. The magnehelic gauge is a safety related item relied on to measure differential pressure across each filter bank to ensure that uranium is not excessively loaded onto filters and to prevent fissile material accumulating in the NAM in quantities grater than a maximum subcritical mass. "SAFETY SIGNIFICANCE OF EVENTS: "The NAM was operated with an expired calibration date on the magnehelic delta pressure gauge, The system design limits the ability to accumulate a critical mass, however, a control for double contingency was lost. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: "In order for a criticality to be possible, the NAM would have to be operated with a differential pressure above 20 In. WG. The filters would have to be fully loaded with fissile/potentially fissile material and dislodged from the filters more than two times, accumulating in the bottom of the NAM. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY CONCENTRATION ETC.): "Double contingency for this scenario is established by Implementing two controls on mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND %WORST CASE CRITICAL MASS): "The assay of any material is less than 2.75 wt. % U235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Double contingency for this scenario is established by implementing two controls on mass. "The first leg of double contingency is an administrative control to limit the delta pressure across the prefilter to a maximum of 12 in. WG or an increase across the HEPA filter to 2 in. WG by using calibrated instrumentation, This will limit the filter loading to less than a subcritical mass. Since the instrumentation was outside the calibration date, this control must be assumed to be violated. "The second leg of double contingency is a safety-related Item, which limits the ability of the NAM to exceed a differential pressure of 20 In. WG. This is accomplished by limiting the motor power rating. This prevents an accumulation of more than the subcritical mass. This control was not violated. "Since double contingency is based on two controls on mass and the differential pressure control was lost, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "Access to the area has been controlled by ropes and signs and the NAM unit has been tagged to prevent use. The NAM will not be operated until inspection, filter change, and replacement of the magnehelic gauge is performed." The NRC Senior Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37476 | 0 | CONSOLIDATED EDISON COMPANY |  |  |  |  | 2000-06-09 12:00 | 2000-10-31 10:30 | 2000-10-31 | PART 21 NOTIFICATION - Pursuant to 10 CFR 21.21(d)(3)(i), Consolidated Edison Company of New York, Inc., the licensee for Indian Point Unit No. 2 hereby provides initial notification of a defect determined to be reportable under 10 CFR Part 21. The reported condition involves a 2GN23 1800 Amp-hour battery produced by YUASA, Inc. These batteries are used in the 125V DC System, and provide a primary source of 125V DC power to safeguards equipment and logic circuitry at Indian Point. On June 9, 2000, during the performance of a battery load test (PT-R76B), 22 Battery failed its two-hour minimum voltage characteristic (110.2VDC). It also failed to satisfy its required amp-hour capacity (greater than 90%). Following initial troubleshooting activities, similar load capacity failures occurred on June 18 and July 18, 2000. Various load tests and destructive examinations of the battery cells were performed over the next several weeks. A visual examination of the plates and separators did not indicate any discrepancies. However, microscopic analysis of samples obtained from two different positive plates revealed cracks within the positive active material, small pores, and small particle size. This would result in higher internal cell resistance when charging and discharging a battery. These cracks appear to have been produced during the manufacturing operation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0
37475 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-10-30 12:30 | 2000-10-30 13:23 | 2000-10-30 | EMERGENCY SIRENS INOPERABLE DUE TO FAILURE OF RADIO REPEATERS The licensee reported that all offsite emergency sirens were inoperable during the period from 0150 10/29/00 through 0745 10/30/00 due to the failure of both radio repeaters. This condition was discovered during siren troubleshooting on 10/30/00. One of the repeaters has been restored to service. The NRC resident inspector will be informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37474 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-10-29 19:54 | 2000-10-30 12:26 | 2000-11-07 | 24-HOUR GASEOUS DIFFUSION PLANT REPORT "At approximately 1954 hours, 10/29/00, operations personnel investigated a LAW CADP smoke head alarm. While investigating the alarm for smoke head SXE 2786 for LAW 2A compressor the operations personnel did not identify any visible release but smelled HF in the area. The 'SEE & FLEE' emergency procedures were immediately implemented. The affected LAW station withdrawal loop was in standby at the time of the alarm. Results of all surveys performed during the emergency response were less than MDA. At 2102 hours, an all clear was granted on the emergency response. PORTS is reporting this alarm as a valid actuation of a 'Q' Safety System. "This is reportable to the NRC as a valid actuation of a 'Q' Safety System in accordance with Safety Analysis Report, section 6.9 (24-HOUR REPORT)." *** UPDATE/RETRACTION AT 1639 ON 11/07/00 FROM ERIC SPAETH TO LEIGH TROCINE *** The following text is a portion of a facsimile received from Portsmouth personnel: "An engineering evaluation performed following the event determined that the small leak, which caused the smoke head actuation, originated from the LAW 1A compressor. This compressor had been shutdown for several weeks prior to the event for maintenance. Engineering determined that the compressor had been purged to a UF6 negative and subsequently pressurized to atmosphere to allow work to be performed. The compressor was in Mode VI (Shutdown) when the smoke head actuation occurred." "Based on the above, the plant conditions that the CADP smoke detection system was designed to protect against were not present when the small leak occurred, and this event may be retracted." Portsmouth personnel notified the NRC resident inspector. The NRC operations officer notified the R3DO (Wright) and NMSS EO (Brach). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37473 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-10-30 11:40 | 2000-10-30 12:00 | 2000-10-30 | SECURITY REPORT Unescorted access granted inappropriately. Compensatory measures taken upon discovery. The NRC resident inspector has been informed of this event by the licensee. Contact the NRC Operations Center for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 0
37472 | 0 | PHILIP MORRIS USA |  |  |  |  | 2000-10-29 10:56 | 2000-10-30 10:17 | 2000-10-30 | GAUGE SHUTTER FAILED TO CLOSE "On Sunday October 29, 2000, an Authorized User was conducting a routine, monthly radiation safety audit. The factory was running that weekend, but Bay 1 was shut down. At 10:56 a.m. he noticed the shutter indicator on maker 1B4 indicated the shutter was open. The maker at 1B4 is a Hauni Protos 100 (maker # 1004) with a Hauni weight control system and a Hauni SRM 8000 scanning head (gauge # 1319). This gauge has three Strontium 90 sealed sources for a combined strength of 0.025 curies. "The Authorized User inserted a cigarette rod in the pass tube to reduce the radiation level and called the Electrical Supervisor on duty. An Instrument Electrician (IE) was called to diagnose the weight control system. The IE found a defective circuit board. This Circuit board is located in the main electrical panel that controls the weight control system and the scanning head. The Authorized User stayed at the scanning head while the IE removed the defective circuit board and took it to the Electrical Repair Shop for repair. When the repaired circuit board was installed, the problem was fixed and the shutter closed properly. The Authorized User used the key switch to test the shutter several times and conducted a final survey with the shutter closed to ensure the shutter was closed and the scanning head was safe. The maker and scanning head were placed in service on C Shift, at approximately 11:00 p.m., October 29, 2000. The scanning head shutter would not open and the circuit board was removed and repaired again. The maker and scanning head were returned to service at approximately 6:30 a.m., October 30, 2000." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 30.50(b)(2)(ii) |  |  |  | 0
37471 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-10-29 01:08 | 2000-10-29 01:30 | 2000-10-29 | SAFETY PARAMETER DISPLAY SYSTEM NOT FUNCTIONING At 0008 hours (EST) on 10/29/00, the Safety Parameter Display System (SPDS) portion of the emergency Response Facility Computer System (ERFCS) was noted to be inoperable, due to all inputs being displayed in magenta color. Several attempts were made to reboot the system, but were unsuccessful. Troubleshooting of the ERFCS with Maintenance is continuing at this time. A return to service time for the SPDS portion of the ERFCS has not been determined. This report is being made pursuant to 10CFR50.72 (b)(1)(v). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Intermediate Shutdown |  | Power Operation | Intermediate Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37470 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-10-28 17:50 | 2000-10-28 21:27 | 2000-10-28 | PENETRATION LEAKAGE EXCEEDED BOTH THE PRIMARY CONTAINMENT LEAKAGE LIMITS AND THE 10CFR100 RELATED LIMITS. On May 4, 2000 the Suppression Chamber Containment Purge System Inlet valves 2CPS*AOV105 and 2CPS*AOV107 were leak tested as required by Technical Specification Quarterly Leak Rate requirements. The local leak rate test (LLRT) determined that the Inboard valve leak rate was out of spec and the penetration was isolated with the Outboard valve to maintain primary containment. With the failure of the inboard isolation valve and due to system configuration the outboard valve could not be tested in the proper direction. On 05/10/00 a leak test was performed on the down stream manual isolation 2CPS-V1 and this valve was locked closed to satisfy primary containment requirement. This was necessary because the surveillance period of the outboard isolation valve 2CPS*AOV105 would expire with no acceptance test method available to satisfy the LLRT requirements of the valve. The manual valve 2CPS-V1 has resilient seats and is subject to a quarterly LLRT requirement. On 10/20/00 a LLRT was attempted on 2CPS-V1 but was aborted due to the high leakage past the outboard valve 2CPS*AOV105 and into containment. On 10/27/00 the leakage past the outboard valve 2CPS*AOV105 was corrected and a LLRT of 2CPS-V1 was performed. 2CPS-V1 failed the LLRT. A blank flange was installed to reestablish primary containment. On 10/28/00 a Mass Flow Leakage test was performed on 2CPS-V1 and it was determined that the leakage past the valve exceeded measurement capability of test instrumentation, and therefore leakage was in excess of maximum pathway leakage. This means that the penetration leakage exceeded both the primary containment leakage limits and the 10CFR100 related limits in Technical Specification Table 3.6.1.2-1. Therefore this condition could have prevented the Primary Containment from performing its safety function to limit the release of radioactive material. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 25 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37469 | -1 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-10-28 15:11 | 2000-10-28 17:40 | 2000-11-27 | RWST CROSS-TIE VALVES UNEXPECTEDLY OPENED DURING PLANNED MAINTENANCE At 1511 hours, with Unit 2 in Intermediate Shutdown (ISD), approximately 375 degrees F, Unit 1 and Unit 2 RWST Cross-tie-valves opened when the High Steam Flow SI signal was unblocked for planned maintenance. By design, the Header to Line SI signal which opens these valves is unblocked when High Steam Flow is unblocked. At the time of the unblock, a header to line condition existed on Unit 2 due to plant conditions. This design was newly implemented during the current Unit 2 refueling outage and procedures did not provide adequate steps to prevent the valves from opening. A Header to Line SI signal was not received as it was properly defeated in accordance with station procedures. The cross-tie valves were manually closed when the condition was identified as not required. Unit 1 is currently at 100% power. Unit 2 is in Intermediate Shutdown with RCS heatup and pressurization in progress. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1725EST ON 11/27/00 FROM ALLEN HARROW TO S. SANDIN * * * The licensee is retracting this report based on the following: "At 1740 hours on 10/28/00, Surry Power Station made a 4 hour Non-Emergency Notification in accordance with 10CFR50.72(b)(2)(ii) due to the opening of the RWST Cross-tie valves when the High Steam Flow SI signal was unblocked for planned maintenance (Event Number 37469). "Based on further review of the event reported on October 28, 2000 it has been determined that the conditions did not meet the criteria of 10CFR50.72 as clarified in NUREG 1022, Rev 1. The NUREG states: 'Usually, the staff would not consider this to include single component actuations because single components of complex systems, by themselves, usually do not mitigate the consequences of significant events. However, in some cases a component would be sufficient to mitigate the event (i.e. perform the ESF function) and its actuation would, therefore, be reportable. This position is consistent with the statement that the reporting requirement is based on the premise that ESFs are provided to mitigate the consequence of a significant event. 'Single trains do mitigate the consequences, and, thus, train level actuations are reportable.' "Specifically, the initial assessment considered the event as an ESF actuation and therefore reportable under criterion 10CFR50.72(b)(2)(ii). The nature of this event does not constitute a train actuation. The only signal affected was that going to the RWST Cross-tie valves. This occurred because the block signal was unblocked due to placing the RCS narrow range temperature loops in trip while performing the RTD cross calibrations while heating up Unit 2 following a refueling outage. The details of this event are consistent with the discussion and examples of NUREG 1022 that would not be reported. "This notification is being made to retract the report made on 10/28/00 based on the above discussion." The licensee informed the NRC resident inspector. Notified R2DO(Rodgers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37468 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-28 12:09 | 2000-10-28 16:36 | 2000-10-28 | GREATER THAN ONE PERCENT OF STEAM GENERATOR 1-2 TUBES WERE DETERMINED TO BE DEFECTIVE. On October 28, 2000, during the Unit 1 tenth refueling outage, analysis of eddy current data on steam generator (SG) 1-2 indicated that greater than one percent of the total tubes inspected in SG 1-2 were defective. Thirty eight (38) defective tubes in SG 1-2 were detected and plugged. Most of the pluggable indications are due to either primary water stress corrosion cracking or outside diameter stress corrosion cracking. Review of the eddy current inspections are complete. Results of the steam generator tube inspection fall into Category C-3, which requires a four-hour non-emergency report in accordance with Technical Specification (TS) Table 5.5.9-2 and 10 CFR50.72(b)(2)(iii)(C). An LER in accordance with 10 CFR50.73(a)(2)(v)(C) and Special Report in accordance with TS 5.6.10.c will be submitted within thirty days. The NRC Resident Inspector will notified of this event notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37467 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-10-27 09:10 | 2000-10-28 02:24 | 2000-10-28 | 24-HOUR NRC 91-01 BULLETIN REPORT INVOLVING LOSS OF GEOMETRY CONTROL FOR STACKED PIPE "Two sections of removed seal exhaust/wet air station exhaust piping were discovered stacked near the C-310 seal exhaust/wet air station in violation of NCSA 310-002. Requirement 3.1.3.b of this NCSA limits the height of equipment items stored in the slab configuration less than or equal to 4.75 inches. The purpose of the requirement is to maintain a safe geometry of the removed equipment items. "SAFETY SIGNIFICANCE OF EVENTS: "The safe geometry relied on for double contingency was violated; however the analysis demonstrating sub-criticality was performed at an enrichment above the current assay limit. In addition the actual configuration of the violation state is smaller than the analyzed configuration. Therefore, additional uranium material would be required to initiate a criticality. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: "In order for a criticality to be possible, the pipes would need to be entirely full of slugged oil with uranium at an enrichment of 5.5% and an additional violation would have to occur. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Double contingency for this scenario relies upon geometry and a second independent and concurrent process upset. "ESTIMATED AMOUNT, ENRICHMENT FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): "The pipes contain an oily film. The assay of any material is less than or equal to 2 wt. % U235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Double contingency for this scenario relies upon geometry and a second independent and concurrent process upset. "The first leg of double contingency is based on maintaining a safe geometry. This is controlled by limiting the slab configuration to no greater than 4.75 inches. The two pipes were stacked in a manner which exceeded the 4.75 inch slab height. Thus, the control was violated and the process condition was not maintained. "The second leg of double contingency is based on the geometry upset being sub-critical and the need for a second independent violation to occur before a criticality is possible. This control was not violated. "Since the safe geometry process condition was not maintained, double contingency was lost. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "Access to the area has been controlled by ropes and signs. The specific corrective actions will be specified in a remediation guide." The NRC resident inspector was informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37466 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-10-27 22:28 | 2000-10-27 23:53 | 2000-10-27 | CONTAINMENT VENTILATION ISOLATION SIGNAL RECEIVED DURING REACTOR CAVITY DRAINDOWN OPERATION. "Received containment ventilation signal from the particulate radiation monitor (2R11A). Reactor refueling cavity draindown after core reload was in progress. Along with other post refueling restoration activities. All containment isolation valves were closed at the time of the isolation, so no position changes occurred. The isolation was reset and occurred again at 2311[EDT] no valves again were open at the time. The signal will not be reset pending further investigation. Monitor isolation setpoint is 3960 counts per minute and the current reading is 3750 counts per minute with occasional spiking into alarm." Air samples taken confirm that the particulate radiation monitor is functioning properly. The licensee suspects that the airborne activity is related to the draindown of the reactor cavity. The licensee will inform Lower Alloways Creek Township and the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37465 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2000-10-27 14:00 | 2000-10-27 18:06 | 2000-10-27 | EXCESSIVE BACKLEAKAGE OF HPSI TRAIN "B" CHECK VALVE DISCOVERED DURING SURVEILLANCE TESTING. At approximately 1600 MST on October 23, 2000, Palo Verde Unit 2 surveillance testing revealed that the "B" train high pressure safety injection (HPSI) pump discharge check valve (2PSIBV405) exhibited backleakage exceeding the acceptance criterion. Palo Verde Unit 2 is shutdown in Mode 6 for its ninth refueling outage with RCS at approximately 105 degrees F and atmospheric pressure. As a result of the surveillance test failure, additional testing and engineering evaluation ensued. At approximately 1400 MST on October 27, 2000, upon disassembly of the check valve internals, engineering personnel observed excessive articulation between the swing arm and the valve disc. This condition may have developed during the previous operating cycle. Therefore, during some previous periods of on-line unavailability of the "B" train HPSI system, the redundant "A" train HPSI system might not have design basis minimum flow to the RCS due to backleakage through the "B" train check valve. During those on-line periods of unavailability, check valve 2PSIBV405 alone may have prevented the fulfillment of the safety function of the HPSI system to mitigate the consequences of an accident. (10CFR50.72(b)(2)(iii)(D)). Similarly, had check valve backleakage been found while the reactor was in operation and on-line maintenance of the "B" train HPSI in progress, the HPSI system may have been seriously degraded, (10CFR50.72(b)(2)(i)). No Technical Specification were entered since Unit 2 is in Mode 6, refueling. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND | ACCIDENT MITIGATION |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iii)(D) |  |  | 0
37464 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2000-10-27 08:10 | 2000-10-27 12:55 | 2000-10-27 | OFFSITE NOTIFICATION MADE TO THE MISSOURI PUBLIC SERVICE COMMISSION On 10/26/00 at 1300 CT an injured person was transported offsite to the University of Missouri Burn Center located in Columbia. The licensee notified the Missouri Public Service Commission of the incident this morning at 0810 CT. The injured person should be released from the hospital sometime today. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37463 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2000-10-27 10:28 | 2000-10-27 12:00 | 2000-10-27 | MANUAL TRIP OF REACTOR DUE TO UNDERWATER DIVER TRAPPED IN FOREBAY. Unit 1 was manually tripped at 1028 CDT as a result of the control room being contacted by security that an underwater diver was trapped in the north forebay. All control rods fully inserted into the core. All safety systems operated as expected. The circulating water system was secured. Steam Generator Atmospheric valves were used to maintain the plant in a Hot Standby condition. Neither Steam Generator has any primary to secondary leakage. All personnel involved with the underwater diving activity were removed from the circulating water forebay area and were examined by emergency medical personnel. No personnel were injured. An incident investigation is underway. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. Reactor restart preparations are in progress. The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37462 | 0 | SOIL & MATERIALS ENGINEERS |  |  |  |  | 2000-10-25 07:00 | 2000-10-27 10:02 | 2000-10-27 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM VEHICLE IN MISHAWAKA, INDIANA A TROXLER MOISTURE DENSITY GAUGE CONTAINING 8 mCi Cs-137 AND 44 mCi Am-241 WAS STOLEN FROM AN EMPLOYEE'S VEHICLE PARKED OVERNIGHT AT A HOTEL IN MISHAWAKA, IN. THE DEVICE WAS SUBSEQUENTLY RECOVERED BY THE LOCAL FIRE DEPARTMENT AND RETURNED TO THE LICENSEE. THERE DOESN'T APPEAR TO BE ANY DAMAGE. THE LICENSEE CONTACTED THE NRC REGION III OFFICE AND WILL SUBMIT A WRITTEN REPORT. HOO NOTE: SEE EVENT #37457 FOR FURTHER DETAILS ON RECOVERY. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
37461 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2000-10-26 14:15 | 2000-10-26 18:57 | 2000-10-26 | SAFE SHUTDOWN MAKEUP PUMP (SSMP) DECLARED INOPERABLE. At approximately 1415 hours on 10/26/00, the Safe Shutdown Makeup Pump (SSMP) tripped unexpectedly during quarterly operability testing. At the time of the trip, the in-plant operator was transferring the flow controller to automatic from the manual position to obtain proper IST flows. At 1525 hours, during a second attempt, the pump again tripped under the same circumstances. The SSMP was run a third time, this time using the flow controller in manual without transferring to automatic. On this attempt, the SSMP obtained the proper pressure and flow but the local controller indications remained erratic. The SSMP was declared inoperable from the time of the first trip. The licensee entered Technical Specification 3.8.(j) a 14 day Limiting Condition of Operation. All other Emergency Core Cooling Systems for Unit 2 are fully operable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 95 | 0 |  | 95 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(A) |  |  |  | 0
37460 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-10-26 14:45 | 2000-10-26 16:40 | 2000-10-26 | KAOWOOL ISSUE During a plant walkdown to identify specific raceway configurations as part of their plan to address Kaowool issues, a condition was found that may affect both divisions of ESF switchgear room coolers. This condition is conservatively being reported pursuant to 10CFR50.72(b)(1)(ii). These areas were already under fire watch in accordance with their fire protection program, as a precautionary response to issuance of SECY-99-0204 - Kaowool. Fire detection and fires suppression are available in the affected area. The NRC Resident Inspector will be informed of the event by the Licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRAD COND DURING OP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(1)(ii) |  |  |  | 0
37459 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2000-10-24 12:00 | 2000-10-26 16:03 | 2000-10-26 | STRONTIUM-90 SOURCE FOUND IN SCRAP METAL. Environmental Radiation Program (ERP) personnel were notified by South Carolina DHEC of a shipment of scrap metal returning to Newell Recycling; East Point, Georgia; from SMI Steel in Caycese, South Carolina. October 25, 2000 ERP staff surveyed the exterior of the truck and located the area with elevated radiation levels in the front left corner of the trailer. Personnel from Newell and the ERP began unloading scrap until a Sr-90 source was located lying on the floor of the trailer. The source was removed, bagged up and isolated approximately 30 yards away from the trailer in another trailer that could be locked and secured as a temporary storage area until remedial actions can be taken by Newell. Source markings were as follows 3F1L, 100mCi, SR-90, 3M1389, 7-84. Note: Based on the information on the source, the Registry of Radioactive Sealed Sources and Devices registry number for this source is NR-460-S-921-S. Initial radiation measurements on the outside of the trailer in the area of the front corner were as high as 300 micro-R/hour. Levels in the immediate area of the source inside the trailer were greater than 3R/hour (beta/gamma) unshielded and in contact with the source. After isolating the source, the remaining scrap metal was surveyed by ERP personnel using Ludlum Micro-R Meter and Eberline ESP-2 with HP-260 probe. No radiation levels above background were noted. General radiation levels inside the trailer ranged from 5 to 15 micro-R/hour while background radiation levels outside of the trailer were 15 to 20 micro-R/hour. 26 smears were taken on various pieces of scrap removed from the trailer and the floor in the vicinity of where the source was found. No removable or fixed contamination was noted once the source had been removed and isolated State of Georgia event number is GA-2000-20I. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | GA | OTH | AGR |  |  |  |  | 0
37458 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-10-26 14:05 | 2000-10-26 15:54 | 2000-10-26 | SINGLE FAILURE RESULTING IN BOTH SAFEGUARDS TRAINS BECOMING INOPERABLE Prairie Island has three safeguard vertical cooling (service) water pumps. These pumps are equipped with an air/vacuum valve that acts to expel air from the pump upon starting. A ball float closes off the valve opening after the air is expelled, and is held closed by pump developed head. It was postulated that the air/vacuum valve could fail to close and the flow of water out of the valve could cause flooding. Plant evaluation determined that documentation does not exist that conclusively demonstrates that the failure cannot occur or that the resultant flooding does not affect the opposite safeguards train pump. Since the operability determination is indeterminate, both trains of safeguards pumps were declared inoperable. A single failure resulting in both safeguards trains becoming inoperable is outside the plant design basis. Compensatory actions are being put into place to restore operability of the safeguards pumps. The initial actions are to station a qualified individual in the safeguard pump area. The qualified individual will observe any start of a safeguard pump and ensure no failure of the air/vacuum valve has occurred. If a failure occurs such that flooding is an immediate concern, the qualified individual will contact the Control Room to secure the pump. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37457 | 0 | NATIONAL RESPONSE CENTER |  |  |  |  | 2000-10-25 20:10 | 2000-10-26 00:25 | 2000-10-26 | RECOVERY OF TROXLER MOISTURE DENSITY GAUGE FROM THE LOADING DOCK OF A DEPARTMENT STORE. AT 2010 LOCAL TIME ON 10/25/00 A TROXLER MOISTURE DENSITY GAUGE [MODEL 3430, S/N 29119] CONTAINING BOTH A CESIUM-137 AND AMERICIUM-241 SOURCE WAS DISCOVERED ON THE LOADING DOCK OF A DEPARTMENT STORE LOCATED IN MISHAWAKA, IN. THE RESPONDING FIRE DEPARTMENT CONTACTED THE SOUTH BEND FIRE DEPARTMENT FOR HAZMAT (RADIOLOGICAL) ASSISTANCE. A PRELIMINARY RAD SURVEY SHOWED APPROXIMATELY 2mR/HR CONTACT. THE INDIANA STATE DEPARTMENT OF HEALTH WAS INFORMED. THE CONDITION OF THE TROXLER TRANSPORT CASE SUGGESTS THAT IT MAY HAVE BEEN STOLEN. FIRE STATION #3 IN MISHAWAKA HAS TAKEN CUSTODY OF THE TROXLER AND IS STORING THE DEVICE IN A LOCKED SECURE AREA. THE INITIAL REPORT FROM THE NATIONAL RESPONSE CENTER INDICATED THAT 75 MEMBERS OF THE PUBLIC WERE EVACUATED. REGION 3 WILL FOLLOWUP IN THE MORNING. SEVERAL FEDERAL AND STATE AGENCIES WERE INFORMED BY THE STATE OF INDIANA AND THE NATIONAL RESPONSE CENTER. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN |  |  |  |  | 0
37456 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-10-25 15:30 | 2000-10-25 17:06 | 2000-10-25 | CONTROL ROOM VENTILATION(CRV) TRAINS DECLARED INOPERABLE. Both CRV trains declared inoperable due to degraded relays. An investigation continues to determine the affects on Emergency Filter train( EFT) systems as well. (share the same type of relays) Repair/replacement has been initiated and an investigation is ongoing. The plant is in a 24 hour LCO action statement which returning one train to service or be in hot shutdown in the following 12 hours. The NRC Resident Inspector was notified. * * * UPDATE ON 10/25/00 @ 1816 BY WITSCHEN TO GOULD * * * The licensee verified that both Emergency Filter trains are also affected by the degraded relays. They are in the same LCO action statement, but they have to restore one Control Room Vent train and one Emergency Filter train to service within 24 hours. The NRC Resident was notified. The REG3 RDO(Vegel) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37455 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-25 11:59 | 2000-10-25 16:07 | 2000-10-25 | ISOLATION CAPABILITY OF MANUAL VALVES IN THE COMPONENT COOLING WATER SYSTEM During the tenth refueling outage on Unit 1(1 R10), a leakage test of several component cooling water (CCW) System manual valves was conducted. The subject valves are used to separate the two vital normally cross-tied CCW trains in case of a CCW leak either as an independent event or as a passive failure following a loss of coolant accident. The leakage rate was determined to be approximately 70 gpm. Manual adjusting of the valves reduced the leakage rate to an insignificant level. The licensing/design bases for the CCW system, as discussed in Table 9.2-7 of the FSAR and in SER 16, is for a maximum 200 gpm leak to occur. Leakage would be detected by falling level in the CCW surge tank. Because of the remaining 4000 gallons in the CCW surge tank after receipt of the low-level alarm, there would be at least 20 minutes for the operator to isolate the leak before the surge tank is empty. The period is extended if the automatically operated, Design Class II, normal makeup path functions as designed and adds makeup water to the system. PG&E's abnormal operating procedure, OP AP-11, has provision for aligning a 250 gpm Class I supply of water to the CCW surge tank. The design/licensing basis of a 200 gpm leak being isolated in 20 minutes assumes that manual valves used during the isolation operation hold and terminate the leak. There is no evidence that PG&E nor the NRC have considered that a leak would not be isolated upon completion of actions to separate the trains. The identified condition, though not believed to represent a safety concern, is different than that discussed in SSER 16. Therefore, the condition is considered to be outside the design basis for the plant. Preliminary investigations of the Unit 2 valves have, not identified any gross leakage. Additional investigations are ongoing. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37454 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-10-25 11:47 | 2000-10-25 12:28 | 2000-10-25 | SECURITY EVENT INVOLVING AN INDIVIDUAL GRANTED SITE ACCESS Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 0
37453 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-10-24 07:41 | 2000-10-24 10:30 | 2000-10-24 | AUTOMATIC REACTOR TRIP DUE TO WORK DONE ON WRONG UNIT'S EHC "At 0741 hours, with Surry Power Station Unit 1 at 100% reactor power, a low low S/G level condition was received and an automatic reactor trip occurred. lmmediately prior to the trip, the Main Steam Dump Valves were observed to have received an open demand, and a loss of turbine load was exhibited. The loss of turbine load was caused by human error due to work on the wrong unit. It was determined that work was being conducted on the Unit 1 EHC System. The work was intended to be one on the Unit 2 EHC System. "All control rods inserted into the core as designed. IRPI B8 rod bottom light was not received due to a burned out light bulb. The light bulb was replaced and indicated properly. The IRPI indication for this rod trended with all other IRPI indications, and indicated <20 steps withdrawn. The shutdown margin for Unit 1 was determined to be satisfactory. Auxiliary feedwater automatically initiated as designed on low low steam generator level following the trip. Primary RCS temperature decreased to approximately 543 degrees following the reactor trip. "No primary safety or power operated relief valves were actuated during he event. As a result of the loss of turbine load, the secondary power operated relief valves actuated during the transient. No indication of primary to secondary leakage exists, therefore no adverse radiological consequences resulted from this event. "All electrical busses transferred properly following the trip and all emergency diesel generators are operable. There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. The cause of the event is being investigated. "Unit 1 is currently at Hot Shutdown with RCS temperature being maintained at approximately 547 degrees. "Unit 2 was not affected by this event and remains stable at CSD with RCS temperature at approximately 100°F and the RCS depressurized to atmospheric pressure with containment Type A test conditions being established. "This event is being reported in accordance with 10CFR50.72(b)(2)(ii)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37452 | -1 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-24 04:58 | 2000-10-24 09:35 | 2000-10-25 | ESF ACTUATION RESULTING IN A SINGLE VALVE ISOLATION "On October 24, 2000, at 0458 hours, while Unit 1 was operating at 100% power, a spurious actuation of the Train C Phase B Containment Isolation Signal occurred. This actuation resulted in the closure of a single Engineered Safety Features Containment Isolation Valve servicing the cooling supply to the Reactor Coolant Pumps. Cooling to the Reactor Coolant Pumps was not interrupted since there are two parallel paths in this penetration to prevent inadvertent isolation of the cooling supply. No other components changed position and the Unit continued to operate at 100% power. The cause of the actuation is not yet known, but the actuation only effected valve 1-CC-MOV-0404. Trouble shooting is in process to determine the cause of the event, No other components are controlled by the Train C Phase B actuation logic." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 10/25/00 @ 1557 BY MOOKHOEK TO GOULD * * * RETRACTION South Texas Project notified the NRC of an Engineered Safety Feature actuation at 0835 CDT on October 24, 2000 (Event #37452) as a result of a spurious actuation of the Train C Phase B Containment Isolation Signal. Review of the guidance in NUREG 1022 Revision 1 on ESF actuations indicates that the actuation of single components would not be reportable. The referenced notification reported the actuation of a single component. 1-CC-MOV-0404. Cooling to the Reactor Coolant Pumps was not interrupted by the closure of 1-CC-MOV-0404 since there are two parallel paths in this penetration to prevent inadvertent isolation of the cooling supply. Since this actuation did not stop the flow of cooling water through the containment penetration and only a single component was actuated, South Texas Project has determined that this event is not reportable and retracts the notification. The NRC Resident has been informed. REG 4 RDO(Pick) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37451 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-10-23 16:37 | 2000-10-23 21:25 | 2000-10-23 | PLANT HAD AUTO START OF ALL THREE DIESEL GENERATORS DUE TO PERSONNEL ERROR Startup Power was being cleared to Unit 1 for refueling outage maintenance. Part of the clearance was to open switch 211-1 for Unit 1 Startup Transformer. Operators inadvertently opened switch 211-2 for Unit 2 Startup Transformer. This caused all three Unit 2 Diesel Generators (D/G) to start on loss of Startup Power signal. Starting of the D/G's is considered to be an ESF actuation and constitutes a 4 hour non-emergency report per 10CFR50.72(B)(2). Startup Power was restored three minutes later and the D/G's returned to standby condition. The D/G's did not load on the bus and no other ESF systems were affected. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37450 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-10-23 13:00 | 2000-10-23 13:31 | 2000-10-23 | THE LICENSEE MADE NOTIFICATION TO FLORIDA FISH AND WILDLIFE CONSERVATION COMMISSION This notification was made due to a live loggerhead turtle being found in the intake net. The turtle was not in very good condition. It will be sent off site for rehabilitation. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37449 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2000-10-22 17:55 | 2000-10-22 18:41 | 2000-10-22 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN The licensee reported that one of the suppression chamber to drywell vacuum breakers cannot be seated completely and the unit 2 primary containment has been declared inoperable. Technical Specification 3.6.1.1 Condition b requires that the unit be taken to a hot shutdown condition within 12 hours. The licensee intends to reduce reactor power in order to make a drywell entry if possible to correct the problem. If the problem cannot be corrected, the licensee intends to take the unit to cold shutdown and deinert the containment. The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37448 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-10-22 01:50 | 2000-10-22 07:55 | 2000-10-24 | 24 HOUR REPORT - 10 CFR 50.72 AND APPENDIX R "A section of the high pressure fire header will be isolated and drained. The reason for the impairment is planned maintenance for the replacement of a section of 12" piping and various small bore valve replacements. This header section provides fire protection for the Units 1 and 2 Intake Structure, the Auxiliary Boiler Feed Pump Building, the Transformer Yard and the Electrical Tunnel Deluge System. "Indian Point Station is in cold shutdown with the reactor defueled and steam generator replacement in progress. Therefore, the Auxiliary Boiler Feed Pumps and the Main and Unit Auxiliary Transformers are out of service and do not require fire protection. The safety related equipment that is required to be protected under this plant condition are the Service Water Pumps and the 480 VAC Electrical Cables for the Spent Fuel Cooling Pumps and Component Cooling Pumps which traverse the Electrical Tunnel. Compensatory hoses will be staged prior to applying the tagout. Fire tours will also be established to supplement the frequency with which these and the other impaired areas are surveilled. "The 24 Hour notification to the NRC for the Fire header impairment will made pursuant to 10CFR50.72 and App. R as well as the written report to follow within 14 days. The alternate fire protection system will not be established since the station is already in cold shutdown. A 30 day action statement will be entered for the inoperable hydrants protecting the Intake Structure and Service Water Pumps. A separate 14 day action statement will be entered for the inoperable Electrical Tunnel Deluge System. The duration of the impairment will be minimized and further compensatory measures may be necessary should any of the time limits be approached due to unforeseen circumstances." The licensee intends to notify the NRC Resident Inspector. * * * UPDATE ON 10/24/00 @ 1524 BY DONNELLY TO GOULD * * * The following update is providing additional information to clarify this event report. The following is an update to NRC event number 37448. A section of the high-pressure fire header will be isolated and drained for planned maintenance. A section of 12-inch piping is being replaced along with various sections of valves. The isolated section of piping supplies high pressure fire water to the Unit 1 and Unit 2 Intake structure, the Auxiliary Boiler Feed Pump Building, and the Electrical Tunnel Deluge System. The Indian Point Unit 2 Fire Protection Program requires that all piping and valves necessary for proper functioning of any portion of the system required for protection of safe shutdown systems be operable. If this condition is not restored within 24 hours, then an alternate fire protection system must be established or the plant must be placed in the hot shutdown condition utilizing normal operating procedures. Within the next 48 hours, if the system is not restored or an alternate system is not established, then the plant must be placed in the cold shutdown condition. Currently, Indian Point 2 station is in the de-fueled condition, with the core fully unloaded. Therefore, compensatory actions are not required to maintain the plant in the shutdown condition.. Compensatory measures are being undertaken by Indian Point 2 station for prudence. The intake structure contains the Service Water Pumps, which are safe shutdown equipment and are used to cool the Spent Fuel Pool. The inoperable hydrant on the intake structure will be supplemented by staged fire hoses and a 4 hour fire tour, and Indian Point 2 will enter a 30 Day Action Statement per SAO-703. Additional fire hoses will also be staged for the inoperable hydrant outside the auxiliary pump building. The electrical tunnel contains the 480 VAC Electrical cables for the Spent Fuel Cooling Pumps, the Component Cooling Water Pumps as well as additional electrical loads. Compensatory hoses will be staged in this area and the fire detectors are all still operational. A 14 Day Action Statement per SAQ-703 will be entered for this impairment. The 24 Hour Notification to the NRC for the fire header impairment will be made pursuant to 10CFR50.72 and Appendix R by telephone and a follow up facsimile. The duration of the impairment will be minimized and further compensatory measures may be necessary should any of the time limits be approached. due to unforeseen circumstances. Additional action statements may be entered if changes in plant status are required. The NRC Resident Inspector was informed. The Reg 1 RDO(Silk) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
37447 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-21 18:00 | 2000-10-22 00:22 | 2000-10-22 | ESF LOAD SHED SIGNAL GENERATED WHILE RESTORING RELAYS "While restoring vital 4160 Bus G Auto-Transfer Relays to service, a shed load signal was initiated to the Bus G components, apparently due to Bus G First Level Undervoltage Relays not resetting after they were energized. When the Feature Cutout Switch was subsequently cut-in to the Load Shed Relay (27XHGT) the load shed was then actuated. The only load available to be shed was Auxiliary Salt Water Pp 1-2 which shut down. Auxiliary Saltwater was aligned from Unit 2 at 1805 (PDT) and remained in that configuration until 1940 (PDT), when Auxiliary Saltwater Pp 1-1 was placed in service. DCPP Unit One is currently in its 10th Refueling Outage, with the core off-loaded to the Spent Fuel Pool. The temperature of the Spent Fuel Pool did not change. The cause of the event is under investigation." The licensee intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37446 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2000-10-21 14:18 | 2000-10-21 17:58 | 2000-10-21 | MANUAL REACTOR TRIP DUE TO LOSS OF CIRCULATING WATER PUMP Operators manually tripped the unit from 70% power, in accordance with plant procedures, after the 'B' circulating water pump tripped. Following the trip, all systems functioned as expected, with the following exceptions: the main feedwater pumps tripped due to seal differential pressure problems, and intermediate range neutron monitoring channel N-36 failed downscale. The licensee is investigating these problems, as well as the cause of the circulating water pump trip. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37445 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-10-21 04:25 | 2000-10-21 05:23 | 2000-10-21 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER TO THE VITAL BUSSES An unusual event was declared at 0435 EDT on 10/21/00 due to the loss of offsite power to the 4 kv vital busses. The startup transformer was tripped due to a lockout for an unknown reason. Both emergency diesel generators started and energized their respective busses. The licensee is investigating the cause of the lockout. The unusual event will be exited when offsite power is restored to the vital busses. The licensee has notified the state and local authorities and intends to notify the NRC Resident Inspector. * * * UPDATE AT 0620 EDT ON 10/21/00 BY BOB STEWART TO FANGIE JONES * * * During attempts to restore offsite power a safety injection occurred at 0553 EDT due to differential pressure on the steam lines. The main steam isolation valves were closed with main steam line pressure indication nulled at 585 psig and steam generator pressure dropped to 485 psig during the cooldown giving the 100 psid for the safety injection. The licensee was slowed by natural circulation in the process of reducing reactor coolant system pressure to clear the override setpoint for the safety injection, but didn't make it. When the safety injection occurred all equipment operated as required. Offsite power was restored at 0616 EDT and the emergency diesel generators were being shutdown. The licensee is waiting to ensure the startup transformer is stable prior to exiting the unusual event. The licensee notified the NRC Resident Inspector. The R2DO (Caudle Julian), NRR EO (Bruce Boger) and the IRO (Frank Congel) have been informed. * * * UPDATE AT 0701 EDT ON 10/21/00 BY BOB STEWART TO FANGIE JONES * * * The licensee exited the unusual event at 0645 EDT. The safety injection has been terminated and the plant is stable in mode 3 with one reactor coolant pump running. The cause of the loss of the startup transformer was due to a short in a backup relay for breaker protection. The licensee has notified the NRC Resident Inspector and the state and local authorities. The R2DO (Caudle Julian), NRR EO (Bruce Boger) and the IRO (Frank Congel) have been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | ESF ACTUATION |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a)(1)(i) | 50.72(b)(2)(ii) |  |  | 0
37444 | -1 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-10-20 19:45 | 2000-10-20 22:50 | 2000-10-31 | DESIGN ISSUE REGARDING MSIV CLOSURE ABILITY DURING MODE TRANSITION "The main steam isolation valves, which accomplish the steam line isolation function, require steam pressure assist to close (fast close). They can also be closed hydraulically (slow close). "The main steam isolation valve function had been demonstrated to be acceptable in Mode 1, 2, and 3. However, the analyses performed for Mode 3 do not explicitly address all steam pressures in region between the NOP/NOT area of Mode 3 and the entry condition to Mode 4. The potential could exist where the plant is in a Mode 3 condition in transition to a Mode 4 condition. During this transition condition, if a steam line break were to occur, closure of the MSIVs would be required. If the steam pressure in this transition condition were near the minimum pressure required to close the MSIVs at the initiation of the event, it is possible that the steam pressure in the system could decay below the required pressure to close the MSIVs. This would mean that the fast close Main Steam Isolation Function could-be inoperable in Mode 3. "This function is operable in Modes 1 and 2. Further analysis is required to demonstrate operability in all conditions bounded by Mode 3." The NRC resident inspector will be informed of this notification by the licensee. * * * RETRACTION 1636 EST 10/31/2000 FROM SIMPSON TAKEN BY STRANSKY * * * "On October 20, 2000, Salem Units 1 and 2 reported that the potential exists with the plant in Mode 3 conditions that if a steam line break were to occur, closure of the Main Steam Isolation Valves (MSIVs) may be required and may not be available for fast closure. If the steamline pressure was near the minimum pressure required to close the MSIVs at the initiation of the event, it is possible that the steamline pressure during a steamline break could decay below the required pressure to close the MSIVs. This would mean that the fast close Main Steam Isolation function could be inoperable in Mode 3. "Upon further evaluation at the main steam line break analysis during Mode 3 Conditions, PSEG now concludes that the MSIVs will be and have always been operable in all parts of Mode 3. The evaluation concluded that although the MSIVs may not always close automatically for the range of steam line break sizes and initial conditions in Mode 3, for those situations where the MSIVs do not close upon receipt of an automatic or manual signal, MSIV closure has been shown to not be required to provide protection to satisfy design basis requirements (e.g. minimum DNBR remains above the minimum DNBR limit value and peak containment pressure remains below 47 psig). "Based on the above information, the 4-hour report made in accordance with 10CFR50.72(b)(2)(iii) is being retracted." The NRC resident inspector has been informed of this retraction. Notified R1DO (McFadden). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37443 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-10-20 13:43 | 2000-10-20 14:08 | 2000-10-20 | OFFSITE NOTIFICATION The licensee notified the Florida Fish and Wildlife Conservation Commission (FF&WCC) regarding the rescue of a live green sea turtle from the intake canal. The animal will be transferred to the FF&WCC for rehabilitation at the Sea Turtle Hospital in Marathon, Florida. The NRC resident inspector has been informed of this notification. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37442 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-10-19 13:40 | 2000-10-19 15:53 | 2000-10-19 | BORIC ACID RESIDUE DISCOVERED ON REACTOR COOLANT SYSTEM INSTRUMENT NOZZLES "During a bare metal inspection of reactor coolant system hot leg instrument nozzles, boric acid residue was found on two of the three mechanical nozzle seal assembly (MNSA) clamps installed during the previous refueling outage (3/99). The MNSA clamps were installed on previously identified leaking nozzles. The leakage from the clamps constitutes a reinitiation of RCS pressure boundary leakage, which is a degradation of the RCS pressure boundary." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37441 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2000-10-18 09:30 | 2000-10-19 08:53 | 2000-10-23 | FAILURE OF VAPORIZE LEVEL PROBE IN "3A" VAPORIZER NRC BULLETIN 91-01 24 HOUR NOTIFICATION Periodic testing of the condensate level detection system in the 3A vaporizer steam chest determined that the system could not perform its intended function due to blockage in the system by loose debris. Further investigation determined that paint flaked from the recently processed cylinder and collected in the bottom of the vaporizer. However, the debris did not block the main condensate removal drain which allowed condensate to be removed from the vaporizer, so there was no condensate accumulation. The vaporizer bottom was cleaned and the level detection system was checked. The system responded correctly. SAFETY SIGNIFICANCE OF EVENTS: No contingency occurred. No accumulation of water in the bottom of the vaporizer occurred. No SNM was involved. CONTROLLED PARAMETER: Mass and moderator are the controlled parameters for the vaporizer. ESTIMATED AMOUNT, ENRICHMENT, FORM of LICENSED MATERIAL: Cylinders heated in the vaporizer contain uranium hexafluoride gas with a uranium-235 enrichment less than 5.0 weight percent. No SNM was involved in this incident since uranium hexafluoride was contained at all times within the uranium hexafluoride piping system. NUCLEAR CRITICALITY SAFETY CONTROL(s) OR CONTROLLED SYSTEM(s) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The condensate level detection system in the 3A vaporizer was rendered inoperable as a result of a drain line that was blocked by debris which came from the most recently processed cylinder. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The debris in the 3A vaporizer was removed and proper functioning of the level detection system was verified. The 3A vaporizer was released for restart on October 19, 2000 at 0730 hours. Other vaporizers not in use at the time of the incident were checked for proper functioning of the level detection system; each system responded correctly. Other vaporizers in use at the time were subject to increased-frequency checks to verify proper functioning of the condensate removal system; all vaporizers were draining properly. In addition, the condensate level detection system for in-use vaporizers will be function-tested immediately after the uranium hexafluoride cylinder currently being processed is removed. * * * UPDATE ON 10/23/00 @ 1210 BY HEATH TO GOULD * * * Reason for submitting supplemental information: Supplemental information is submitted to provide further information on the as found condition and to clarify the safety significance of the event. Double Contingency Protection: 30B UF6 cylinders are heated in the vaporizers with saturated steam. The steam is removed via a condensate removal system. Double contingency protection for the vaporizers is based on mass and moderator control. Mass control consists of controls to prevent and detect an uncontrolled release of UF6 inside the vaporizer. Moderator control consists of controls to detect accumulation of moderator (specifically condensate) and prevent the accumulation of moderator in the bottom of the vaporizer. As Found Condition: Two drains are present in the bottom of each vaporizer which allow steam to enter the condensate removal system. Each drain has an individual drain screen. A larger removable debris screen rests in the bottom of the vaporizer above the two individual drain screens. One drain flows through a pot in which reside the high and high-high level probes. The second drain proceeds directly to the condensate system. In this event the screen which covers the drain which flows to the level pot was obstructed with paint residue, thereby isolating the level probes. As a result of the isolation of the level probes, the ability to detect high level was lost. However, at no time was the condensate removal path closed. There was no accumulation of water in the vaporizer and no SNM was present. The cylinder from which the paint residue came was provided by Urenco. Urenco has been advised by this facility of the situation. Prior to processing, the paint showed no indication of being defective. The paint was not chipped, peeling, bubbling from the surface, discolored, or otherwise distinguishable as flawed. It is also very likely that the plugging of the drain occurred as a result of the functional test which detected it. The functional test of the vaporizer level probes is performed by filling the bottom of the empty vaporizer with water from a hose. During steady state operation the expected flow rate of condensate through a vaporizer is on the order of 1.48 gallons per hour. As was described earlier, the larger debris screen rests above the two drains. The seal along the bottom perimeter of the debris screen is not air or water tight and need not be due to the fact that it sees a low flow rate of steam and not a flow of liquid. During the functional test, it is likely the paint debris was sluiced underneath the debris screen by the relatively high flow rate of water which is used for the test. Notification was nevertheless made due to the fact that there is a small possibility that the vaporizer was operated in this condition. Conclusions related to safety significance: * Loss of double contingency protection may have occurred. * No UF6 leaks occurred in the vaporizer. No failure of mass controls occurred. No SNM was involved. * The condensate flow path from the vaporizer was not blocked. No moderator accumulated in the vaporizer * At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. * The safety significance of this event is evaluated to be low. The Reg 2 RDO(Belise) and the MNSS EO(Schnieder) were notified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0
37440 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2000-10-19 05:30 | 2000-10-19 07:00 | 2000-10-19 | MAIN STEAM LINE ISOLATION VALVES FAIL LOCAL LEAK RATE TEST At 0530 CT on 10/19/00, the total maximum pathway leakage for all main steam line isolation valves was determined by Local Leak Rate Testing to be in excess of Technical Specification 4.7.D.6 limit of < 46 scfh when tested at a test pressure of 25 psig. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37439 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-10-18 14:37 | 2000-10-18 18:45 | 2000-11-10 | UNIT EXPERIENCED A MOMENTARY GRID DISTURBANCE RENDERING SEVERAL SAFETY-RELATED RADIATION MONITORS INOPERABLE "At 1437CDT on 10/18/00, River Bend Station experienced an electrical perturbation in the Baton Rouge area. Line 758 [138 kV] was lost which feeds a local refinery and this loss resulted in a momentary grid undervoltage condition. This undervoltage condition lasted less than one (1) second. As a result of this undervoltage condition, power to selected radiation monitor sample pumps was lost. Specifically, the Control Room Fresh air intake radiation monitors on both Division I and Division II lost sample pump power and this resulted in these monitors being inoperable for approximately three (3) minutes. The monitors were subsequently restarted. As a result of this condition, the radiation monitors would have been unable to initiate the Control Room Fresh Air Filter trains upon receipt of a high radiation signal. This signal is required to be operable when handling irradiated fuel; modes 1, 2, 3 and/or performing operations with the potential to drain the reactor vessel. No fuel handling or reactor vessel drain activities were in progress. This condition also existed for the Fuel Building ventilation radiation monitors. This condition is conservatively being reported as a loss of safety function for the Control Room Fresh Air System. Further evaluation if this condition is in progress." The licensee informed the NRC resident inspector. * * * RETRACTION 1111 11/10/2000 FROM HUSTON TAKEN BY STRANSKY * * * "At 1746 on October 18. 2000 River Bend Station (RBS) reported a loss of power to radiation monitors in accordance with 10 CFR 50.72(b)(2)(iii)(D). Both divisions lost power for approximately 3 minutes until the units were restored due to operator action. "A review indicated a concern for two safety functions related to charcoal filtration. One was related to control room fresh air and one related to the fuel building, specifically related to fuel handling accidents. "The radiation monitors sensed low voltage during the grid transient and correctly shut down. They restarted automatically when voltage was restored: however, the sample pump must be restarted by the operator. The radiation monitors operated correctly per design for the conditions they sensed. "Review of the event by RBS Engineering and Licensing personnel indicate that the loss of both divisions of radiation monitors for Control Room Fresh Air (CRFA) is covered by technical specifications. The allowed outage time in technical specifications was met when the radiation monitor sample pumps were restored within about three minutes. Additionally, plant procedures account for operator action to ensure the safety related monitors are operating and restarting the sample pumps is considered non-heroic, assessed action. Therefore this occurrence is not reportable. "A review of the alarm history for the fuel building radiation monitors indicated that one division did not lose the sample pump and remained operable throughout the transient. Therefore, there was no loss of safety function for the fuel handling accident. "Based on this information, RBS concluded that the loss of the radiation monitor sample pumps is not reportable and the previous report is retracted." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37438 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2000-10-17 19:00 | 2000-10-18 16:15 | 2000-10-18 | AGREEMENT STATE REPORT INVOLVING A MEDICAL MISADMINISTRATION (UNDERDOSE) AT 1650EDT ON 10/17/00, A 31 YEAR OLD MALE PATIENT UNDERGOING TREATMENT FOR LIVER CANCER RECEIVED 23.4% OF THE PRESCRIBED 150 GRAY DOSE USING YTTRIUM-90 GLASS SPHERES PRODUCED BY NORDION. THE LICENSEE HAS PERFORMED 10 SUCCESSFUL THERAPIES OF THIS TYPE IN THE PAST. THE MANUFACTURER IS EVALUATING THE ENTIRE DELIVERY SYSTEM IN ORDER TO DETERMINE ROOT CAUSE. THE LICENSEE'S PRELIMINARY EVALUATION INDICATES A DIFFICULTY IN THE DELIVERY RESULTING FROM AN AIR LEAK IN THE RUBBER CAP OF THE SOURCE VIAL AT THE SITE OF THE NEEDLE INSERTION. THE LICENSEE SUSPECTS THAT THE INLET NEEDLE AND THE OUTLET NEEDLE MAY HAVE BEEN INSERTED TOO CLOSE WHICH CAUSED THE RUBBER CAP TO LOSE ITS SELF-SEAL CAPABILITY. AT 1900EDT ON 10/18, THE LICENSEE DETERMINED THAT THE UNDERDOSE MET THE REPORTING REQUIREMENTS AS A MEDICAL MISADMINISTRATION. THE STATE OF MARYLAND INTENDS TO CONDUCT AN INVESTIGATION OF THIS INCIDENT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0
37437 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-10-18 14:00 | 2000-10-18 15:04 | 2000-10-18 | LICENSEE IDENTIFIED DURING SURVEILLANCE TESTING THAT THE CONTAINMENT LEAK RATE EXCEEDS THE ALLOWABLE LEAK RATE "PRIMARY CONTAINMENT AS-FOUND MINIMUM PATHWAY LEAK RATE EXCEEDED THE ALLOWABLE LEAK RATE OF 1.5%/DAY DURING REFUELING OUTAGE 14. THE MAJOR CONTRIBUTOR TO TOTAL CONTAINMENT LEAKAGE WAS THE 'D' MAIN STEAM LINE WHOSE LEAK RATE WAS NOT ABLE TO BE QUANTIFIED." THE LICENSEE HAS APPROXIMATELY 35 ADDITIONAL COMPONENTS TO EVALUATE PRIOR TO COMPLETING LEAK RATE TESTING. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37436 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-10-18 12:00 | 2000-10-18 13:47 | 2000-10-18 | OFFSITE AGENCIES NOTIFIED OF INADVERTENT ACTUATION OF OFFSITE SIRENS DURING "SILENT TEST" "At approximately, 1200 on 10/18/2000, the Prompt Notification System (PNS) sirens were inadvertently actuated during a 'Silent Test' of the PNS system by the Hamilton County Emergency Management Agency (HCEMA). The Corporate Emergency Planning (EP) personnel were in contact with the HCEMA and Tennessee Emergency Management Agency (TEMA) Staff at the time of the test and immediately canceled the activation of PNS system at approximately 1201. The Corporate Operations Duty Specialist (ODS) notified the Sequoyah Operations Shift Manager at approximately 1205. Tennessee Valley Authority (TVA) Public Information personnel notified the media. Due to heightened public and media interest and notifications, this incident is being reported under 10CFR 50.72(b)(2)(vi)." The licensee informed state/local agencies, local media and the NRC resident inspector. | 0 | 78 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37435 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2000-10-18 10:52 | 2000-10-18 12:00 | 2000-10-18 | OFFSITE NOTIFICATION TO LOCAL FIRE DEPARTMENT FOR FIRE ON OWNER CONTROLLED POPERTY "REFERENCE NUREG [1022 - SECTION] 3.3.7: NOTIFICATION OF CONTACT OF ST. LUCIE '911' (FIRE) TO REQUEST OFFSITE FIRE DEPARTMENT TO EXTINGUISH A SMALL GRASS FIRE EAST OF PLANT BETWEEN DUNE LINE AND MANGROVES, IN A GRASS COVERED PARKING AREA. TOTAL TIME FROM DISCOVERY UNTIL NOTIFICATION OF 'FIRE IS OUT' WAS 38 MINUTES. NO E-PLAN ACTIVATION WAS REQUIRED. FIRE [WAS] NOT ON PLANT SITE." THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR AND LOCAL AUTHORITIES. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37434 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-10-17 19:53 | 2000-10-17 22:15 | 2000-10-17 | INDICATION OF RCS PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING INSPECTION OF PRESSURIZER HEATER SLEEVE "A SMALL AMOUNT OF BORIC ACID WAS DISCOVERED IN THE AREA AROUND PRESSURIZER HEATER SLEEVE NUMBER F4 DURING A BARE METAL INSPECTION PERFORMED ON 10/17/00. THE BORIC ACID IS BELIEVED TO BE EVIDENCE OF PRIMARY STRESS CORROSION CRACKING OF THE INCONEL ALLOY 600 HEATER SLEEVE. THE BORIC ACID IS BELIEVED TO BE EVIDENCE OF REACTOR COOLANT SYSTEM (RCS) PRESSURE BOUNDARY LEAKAGE, CONSTITUTING A DEGRADATION OF THE RCS PRESSURE BOUNDARY." THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37433 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2000-10-16 18:30 | 2000-10-17 12:13 | 2000-10-17 | 24-HOUR FITNESS-FOR-DUTY REPORT INVOLVING A CONTRACT SUPERVISOR A contract supervisor was determined to be under the influence of alcohol during a test for cause. The individual's access to the plant has been terminated. Contact the Headquarters Operations Officers for additional details. | 0 | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0
37432 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-10-16 09:21 | 2000-10-16 12:43 | 2000-10-16 | MANUAL SCRAM INSERTED PRIOR TO REACHING AUTOMATIC SCRAM SETPOINT FOLLOWING REPLACEMENT OF ATWS POWER SUPPLIES "Clinton Power Station is currently in day 3 of refueling outage RF-7. At 09:20 I&C Technicians were performing PMs (PCIMSA017 and PCIMSA019) which replaced power supplies in the Anticipated Transient Without Scram system (ATWS). During reenergization of the ATWS system, the ARI (Alternate Rod Insertion) initiation alarm occurred. The 'A' RO observed Scram Discharge Volume Vents and Drains closing and a rising level in the Scram Discharge Volume (SDV). At 09:21 a manual scram was inserted at approximately 11 gallons SDV level prior to reaching the automatic scram setpoint of 19.6 gallons Scram Discharge Volume level. "Prior to this event Reactor Water Level was at 195 inches. The extra input of water into the reactor due to this scram caused a level rise to 200 inches. The Reactor Operators raised Reactor Water Cleanup letdown rate from the RPV to bring level back to the preferred range of 190 - 200 inches. "Investigation has revealed that reenergizing the ATWS instrumentation causes actuation of the ATWS trip system." There was no rod motion since all rods were fully inserted prior to the event. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37431 | -1 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-14 16:40 | 2000-10-15 01:42 | 2000-10-15 | UNPLANNED, MONITORED, RADIOACTIVE RELEASE OF NOBLE GASES THROUGH THE UNIT VENT DURING ALIGNMENT FOR SAMPLING OF THE REACTOR COOLANT SYSTEM PRESSURIZER STEAM SPACE WHILE ENTERING A REFUELING OUTAGE The following text is a portion of a facsimile received from the licensee: "[Based on preliminary data, the licensee reported that an] airborne radioactive release that may have exceeded the reportability limits in Appendix 'B' of 10 CFR [Part] 20, Table 2. Preliminary results from data available as of 2200 hours on 10/14/00 appear to indicate that the release has exceeded the reportability criterion. Additional review and calculation of preliminary results are in progress to determine the actual release. Followup notification will be made to validate or retract this notification." The licensee reported that this unplanned, monitored, gaseous, offsite release occurred at 1640 on 10/14/00 and that it was terminated within approximately 20 minutes. The weather conditions were very stable at the time. The site boundary dose and noble gas release rate were not available at the time of the event notification. However, the available data indicated the dose at the unit vent. Two radiation monitors exceeded their Trip II setpoints. Plant Stack Other EMF 36 EMF 41 Radiation Monitor Readings 3.63 E3 cpm 2.24 E4 cpm Alarm Setpoints: Trip II 2.71 E3 cpm 4.54 E3 cpm Percent of Technical Specification Limit Not Available Not Available The licensee stated that there is no direct correlation between the radiation monitor setpoints or readings and the technical specification limits. The technical specification limits are based upon dose at the site boundary, and determination of the site boundary dose requires extensive calculations and review. The licensee currently anticipates that this information will be available in the followup notification. At this time, the licensee believes that the release was well below the technical specification limits. The licensee stated that nothing was unusual or misunderstood and that all systems functioned as required. The licensee plans to notify the NRC resident inspector, the States of North Carolina and South Carolina, and the applicable counties (York, Gaston, and Mecklenburg). The licensee does not plan to issue a press release, and media interest is not anticipated at this time. HOO NOTE: At 0735 and 0818 on 10/15/00, representatives from the Environmental Protection Agency (Paul Wagner) and the South Carolina Department of Health and Environmental Control (John Jesse), respectively, called the NRC Operations Center for information regarding this event. (Call the NRC operations officer for contact information.) * * * UPDATE ON 10/15/00 @ 1438 BY FRITZ TO GOULD * * * RETRACTION The Radiation Protection staff have evaluated the release and determined that it did not exceed any limits and also did not meet any reporting requirements of 10 CFR 50.72(b)(2)(iv)(A). Therefore, the licensee is retracting this event. The NRC Resident Inspector will be notified. The following individuals have been notified of this update: Reg 2 RDO Barr NRR EO Boger IRO Giitter DOE Stambaugh EPA(NRC) Crews FEMA Stinederf USDA Conley NMSS Holahan HHS Cruz HP Pederson SCDHEC Jesse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | AIRBORNE RAD RELEASE |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(A) |  |  |  | 0
37430 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-10-14 18:30 | 2000-10-14 18:50 | 2000-10-14 | UNUSUAL EVENT DECLARED AT 1830 HOURS DUE TO FIRE IN THE PROTECTED AREA LASTING GREATER THAN 10 MINUTES. "2A" Heater Drain Pump motor fire reported. Fire reported at 1815 hours, the area was secured and the fire was extinguished using carbon dioxide by the onsite fire brigade at 1831 hours. No injuries. Offsite fire department assistance was initially requested by the licensee but was not needed to extinguish the fire. Damage caused by the fire was the top back of the heater drain pump motor. Plant operation was not affected by the fire. Emergency facilities on site were not activated. State and local counties were notified by the licensee. After "2A" Heater Drain Pump tripped "2C" Heater Drain Pump was started. The NRC Residence Inspector was notified of this event by the licensee. * * * UPDATE on 10/14/00 at 1912ET by Schall taken by MacKinnon * * * Unusual Event terminated at 1908 ET. R2DO (Ken Barr), FEMA (Belcher), IRO (C. Miller). The NRC Resident Inspector was notified by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a)(1)(i) | 50.72(b)(2)(vi) |  |  | 0
37429 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-10-14 03:24 | 2000-10-14 05:14 | 2000-10-18 | AUTOMATIC REACTOR SCRAM DUE TO A MAIN GENERATOR TRIP FOR UNKNOWN REASONS The following text is a portion of a facsimile received from the licensee: "At 0324 [CDT], a reactor scram occurred due to a main generator trip. Group isolations 2, 3[, and] 6 occurred due to low reactor water level. The lowest [reactor water] level recorded was -20 inches on [the] wide range level recorder. Reactor water level recovered, and both reactor [feedwater] pumps tripped on high reactor water level. Group isolations have been verified and reset. [The] 'A' reactor [feedwater] pump has been returned to service and is being used to control water level. [High pressure coolant injection] and [reactor core isolation cooling] did not inject and were not needed to control reactor water level. The plant will be placed in Cold Shutdown. The electrical grid is stable." The licensee stated that all control rods fully inserted and that all systems functioned as required. The licensee also stated that alternate rod insertion initiated as a result of high pressure due to the transient. The highest pressure observed was 1,085 psi. None of the relief valves lifted, and the main steam isolation valves remained open throughout the event. Steam is currently being dumped to the condenser. In addition, the licensee stated that the cause of the main generator trip is currently under investigation. There were no related surveillance or maintenance activities ongoing at the time of the event. The licensee notified the NRC resident inspector. * * * UPDATE on 10/18/00 at 0428 ET by Myers taken by MacKinnon * * * A detailed review of the plant response to the scram has been conducted. This review indicated the following clarification to the initial report are needed: Alternate Rod Insertion initiated on low level, rather than high pressure. The low level was not in long enough to trip the Recirculation pumps. The pumps trip after a 9 second delay, and the low level signal was only in for ~ 7 seconds. Initial indications were that reactor pressure had reached 1085 psig, based on pressure recorder LRPR97, the highest reading of the pressure recorders. Additional pressure recorders and the plant computer indicate pressure reached a maximum of ~ 1068 psig. Evaluation of the recorder indicates it is in calibration, and the "overshoot" of indicated pressure is due to mechanical characteristics of the recorder linkage. NRC R4DO (John Pellet) notified. The NRC Resident Inspector was informed of this update by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37428 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-13 17:14 | 2000-10-13 22:18 | 2000-10-13 | THE PLANT HAD AUTO START OF THE ONE COMPONENT COOLING WATER PUMP During testing of vital bus "F" components,(first and second level undervoltage relays) with the emergency diesel generator 1/3 parallel to the aux. Power(bus "F"), a signal was generated which tripped the aux feeder breaker and that separated bus "F" from the PG&E system or auxiliary power. This event picked up a safety relay which started the third component cooling water(CCW) pump 1/1, which is an ESF component. They do not need three pumps running, so they secured pump 1/2. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37427 | 0 | ITT INDUSTRIES |  |  |  |  | 2000-08-18 | 2000-10-13 16:20 | 2000-10-25 | PART 21 INVOLVING POSSIBLE ITT INDUSTRIES TRANSDUCER FAILURES Since the date of discovery, design alternatives continue to be evaluated. The methods under investigation for corrective action will be mechanical in nature. ITT Conoflow expects to conclude the analysis phase of their investigation by 12/15/00 and currently estimate that replacement units would be available by 2/15/01. Advice to Customers Each site location should analyze their system and corresponding potential for failure with regard to this notification. In the absence of a seismic event resulting in radiation and/or a steam line break, they do not believe this unit will cause an operational problem. Please note that the product qualification was simulated for a ten, (10) year design life. Those units with a service life of ten, (10) years or more should not be considered qualified. Individual customers will be advised by letter when replacement IEEE I/P transducers are available. Nature of the Deviation The nature of the deviation is to the test and performance requirements associated with IEEE 323 and IEEE 344. An inappropriate bonding process was utilized in the manufacture of the IEEE I/P Transducer. This process change began in 1986 and could, during a seismic event involving high radiation and/or high temperature steam, result in the potential failure of the transducer to perform its intended safety function. Product Models involved GT25CA1826 GT65CA1826 GT45CA1826 GT25FA1826 GT45FA1826 GT65FA1826 Identification of the Company ITT Conoflow ITT Conoflow, Division of ITT Grinnell Valve Company ITT Conoflow, Division of ITT Fluid Technology Corporation ITT Conoflow, ITT Industries Location of Components in Use DUKE ENERGY CORPORATION, CATAWBA NUCLEAR STATION FORT CALHOUN STATION KOREA ELECTRIC POWER CORPORATION, KANONAM ERGYTECH INCORPORATED, HOUSTON, TEXAS PONTON INDUSTRIES, INCORPORATED, SANTA FE SPRINGS, CALIFORNIA ONTARIO POWER GENERATION, DNGD, BOWMANVILLE, ONTARIO LIC 3Z8 CANADA COMMONWEALTH EDISON, MAY WOOD, ILLINOIS COPES-VULCAN, INCORPORATED, LAKE CITY, PENNSYLVANIA PETRO-CHEM EQUIPMENT COMPANY, BATON ROUGE, LOUISIANA ASIAM INTERNATIONAL (TAIWAN) INCORPORATED, TAIPEI 105 TAIWAN, R.O.C. NEW YORK POWER AUTHORITY, JA FITZPATRICK NUCLEAR PLANT CONTROL COMPONENTS, INC., RANCHO SANTA MARGARITA, CALIFORNIA NORTHEAST NUCLEAR ENERGY, HARTFORD, CONNECTICUT These companies were also informed. OMAHA PUBLIC POWER DISTRICT, FORT CALHOUN STATION DETROIT EDISON COMPANY ALABAMA POWER COMPANY, SOUTHERN NUCLEAR OPERATING COMPANY GPU NUCLEAR CORPORATION, C/O GPU SERVICE CORPORATION * * * UPDATE ON 10/25/00 @ 1425 BY FAX(PATTON) TO GOULD * * * This deviation to IEEE 323 and IEEE 344 was discovered during a design change history review. Their records indicate that in September, 1986, a change was made to the magnet assembly which was not properly documented for compliance to the IEEE standards. This change was to the adhesive used to bond the magnet assembly together. Upon researching the new adhesive, there is no test data, either in ITT Conoflow records or the adhesive supplier adhesive properties data, which assures that the bond will withstand the rigors of thermal shock, radiation or high temperature/steam exposure. These facts are what prompted the Part 21 NRC notification. The potential failure of the adhesive bonds within the I/P transducer magnet assembly could, under seismic loading, cause the magnet to shift laterally and bind the floating coil which drives the pilot nozzle flapper valve. If that were to occur, the transducer would fail in the last operating output pressure. A change in electrical signal to the transducer may not cause the corresponding change in output pressure. To date, no units have failed. The potential failure mode will require two conditions to occur: 1. The thermal/steam or radiation conditions must exist for the adhesive bond to fail. 2. There must be sufficient seismic energy (vibration/shock) to move the magnet in a lateral direction. Nature of the Deviation The nature of the deviation is to the test and performance requirements associated with IEEE 323 and IEEE 344. An inappropriate bonding process was utilized in the manufacture of the IEEE I/P Transducer. This process change began in 1986 and could, during a seismic event involving high radiation and/or high temperature steam, result in the potential failure of the transducer to perform its intended safety function. Corrective Action Since the date of discovery, design alternatives continue to be evaluated. The methods under investigation for corrective action will be mechanical in nature. ITT Conoflow expects to conclude the analysis phase of our investigation by 12/15/00 and currently estimate that replacement units would be available by 2/15/01 Advice to Customers Each site location should analyze their system and corresponding potential for failure with regard to this notification. In the absence of a seismic event resulting in radiation and/or a steam line break, we do not believe this unit will cause an operational problem. Please note that the product qualification was simulated for a ten, (10) year design life. Those units with a service life often, (10) years or more should not be considered qualified. Individual customers will be advised by letter when replacement IEEE I/P transducers are available. Two more models have been added to the list: GT25CD1826 GT25FD1826 NRR(Hodge), RDOs(Silk, Boland, Vegel, and Pick) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | SC | OTH | PAR | 21.21 |  |  |  | 0
37426 | 0 | NATIONAL INSTITUTE OF HEALTH |  |  |  |  | 2000-10-13 | 2000-10-13 16:04 | 2000-10-13 | THE NATIONAL INSTITUTE OF HEALTH REPORTED A MISSING PHOSPHORUS - 32 SOURCE On September 22, 2000 a researcher and Authorized User within the NIH Radiation Safety Program reported to his area health physicist that approximately 600 microcuries of Phosphorus-32 labeled DCTP was missing from a source vial. The source vial of NEN Catalog Number BLU513Z had been first opened the previous day, September 21, 2000, by another researcher who remembered removing only 400 microcuries of the total activity of 1000 microcuries for an experiment. This researcher then replaced the vial into the refrigerator, noting that 30 microliters (600 microcuries) were left. The research laboratory staff distinctly recalled locking the laboratory at the end of that day, in accordance with NIH policy for the security of radioactive materials, and also recalled having to unlock the laboratory the next morning. However, on September 22 at 11 A.M., when a third researcher went to use the remaining P-32 DCTP from the same vial as was used the previous day, the vial was completely empty. The researchers performed extensive contamination surveys to determine if the contents had spilled; no contamination was found. Following notification of the Radiation Safety Branch, the area health physicist performed extensive contamination checks throughout the Department to ensure that the material had not been used to intentionally contaminate anything. Again, no contamination was found. The Authorized User notified the NIH Police of the missing material. The Authorized User contacted everyone within the Department to determine the resolution of the missing P-32. The Department Chief has held meetings with his staff and interviewed all Authorized Users within the Department; to date no one has admitted using the F-32 DCTP. However, it is the belief of everyone involved that the P-32 DCTP was borrowed by another researcher, who is not willing to admit it, for a legitimate research experiment. This is based on the fact that the P-32 compound was within the locked laboratory; therefore, someone with a key to that laboratory, i.e. a member of the Department, is most likely to have used the P-32. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0
37425 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-10-12 18:59 | 2000-10-12 19:05 | 2000-11-07 | SPRAY ADDITIVE TANK 31 INOPERABLE DURING MAINTENANCE On July 21, 2000, the Spray Additive Tank 31 Outlet Isolation Valve (SI-1841) was shut for approximately eight and one half-hours, to perform maintenance on one of the downstream automatic Sodium Hydroxide isolation valves. This would have effectively prevented Sodium Hydroxide from being sprayed into Containment if the Spray Pumps had been required. This is not in accordance with Tech Spec 3.3.B.1.a and the associated Bases which requires the Spray Additive Tank to be operable above Cold Shutdown. Therefore, isolation of this tank could have potentially placed the Containment Spray System outside of its design basis; however, the investigation of this event is ongoing. This event was discovered by the System Engineer while performing a periodic review of system unavailability (time) in accordance with the Maintenance Rule. The NRC Resident Inspector will be notified. *** UPDATE AT 1537 ON 11/07/00 FROM TRACY SUDOKO TO LEIGH TROCINE *** The following text is a portion of a facsimile received from the licensee: "This notification is an update to Event No. 37425. [Indian Point 3] reported, on 10/12/00, that the Containment Spray (CS) System NaOH Spray Additive Tank (SAT) outlet isolation valve (SI-1841) was shut for approximately eight and one-half hours on 07/21/00 to perform preventative maintenance on a downstream automatic NaOH SAT isolation valve. This report was made because this event placed the CS system outside of its design basis as per 10 CFR 50.72(b)(1)(ii)(B)." "The Technical Specification (TS) provides no allowed outage time for the SAT, so a TS-required shutdown should have been initiated, and the plant [should have been shut down] within 4 hours. Further review of the Emergency Plan Action Levels (EAL), specifically EAL 7.1.1, determined that [a Notification of Unusual Event (NUE)] is required to be declared if the plant is not brought to the required operating mode within the TS [limiting condition for operation (LCO)] action statement time. Entry into an NUE was not made when the event occurred on 07/21/00." The licensee plans to notify the NRC resident inspector as well as applicable state and local agencies. The NRC operations officer notified the R1DO (Michele Evans), NRR EO (Tad Marsh), IRO (Joe Giitter), and FEMA (Tony Cegielsky). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37424 | 0 | SIEMENS POWER CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2000-10-11 10:45 | 2000-10-12 13:39 | 2000-10-12 | 24-HOUR 91-01 BULLETIN VIOLATION OF MASS CONTROL "On 10/10/00 at about 11:30 a.m. while sorting drums of 'wet waste' in the Modular Extraction/ Recovery Facility (MERF), SPC process operators found three sock filters that contained larger than expected amounts of sludge. These sock filters came from two separate waste drums that had been packaged in 1993 or early 1994. Per Criticality Safety Specifications and Standard Operating Procedures, the process operators removed the sludge from the filters and placed it into three separate 4-gallon containers. Operators sampled the material in each of the containers and sent the samples to the SPC laboratory for analysis. The 4-gallon containers were transferred from MERF to an authorized storage location for moderated material. The lead process operator contacted the process engineer who in turn contacted Criticality Safety." "On 10/11/00 at about 10:45 a.m., the SPC laboratory reported the percent U in the sludge. The results are summarized in the following table." "Container # Net Wt.(kg) %U %235U Grams U Grams 235U 56696 15.4 71.4 3.55 10,979.8 389.8 56697 8.7 74.4 1.88 6,635.8 123.1 56698 13.9 72.4 1.89 10,111.2 191.3 Total 38.1 NA NA 27,626.8 704.2 " "The total 235U present in the process batch at MERF (in the sock filter sludge plus other waste material) was calculated to be 895.9 grams, which exceeds the 790 gram 235U limit for the facility by about 106 grams." "This data also indicates an infraction of the 200 g 235U mass control limit placed on individual waste drums on the waste storage pad." "Safety Significance Of Event:" "The safety significance of this event is low. The mass of uranium present in the process batch of waste drums being sorted in MERF was less than a safe mass (45% of critical) for the enrichments actually present. The actual enrichment of the materials involved was less than 3.6% 235U, however if the facility enrichment limit of 5 wt.% 235U is assumed, the total 235U mass was about 51% of a minimum critical mass. The information derived from the MERF infraction reveals an infraction of the mass control limit for drums on the storage pad." "The criticality safety limit on surface density restricts a vertical stack of waste drums to 626 grams 235U. This is controlled by limiting any drum in a three tier array of waste drums to 200 grams 235U. If the two drums containing sock filters and another drum at the 200 g 235U limit were present in a three tier stack, the total mass in the stack would have been approximately 965 g 225U. A criticality area density is over 550 g 235U per sq. ft. which corresponds to 1,512 g 235U in a 2.75 sq. ft. area, the footprint area of a single drum. This is less than 64% of a minimum critical surface density." "Potential Criticality Pathways:" "For criticality to occur in a single waste drum requires a minimum of about 40 kg U02 enriched to 5 wt.% 235U. Current SOPs require sorting of waste and NDA assay before waste can be moved to the waste pad." "To exceed an allowed surface density for stacked drums on the waste pad would require more than 600 grams 235U in a vertical stack of drums. This surface density limit would result in drum arrays that are substantially subcritical." "For criticality to occur in the processing equipment in MERF would require a minimum of 40 kg U02 enriched to 5 wt.% 235U. Before such large amounts could be processed in this equipment, the operating staff would have to fail to perform the following actions required by the applicable criticality safety specification (CSS) and SOPs: * re-sort the waste and remove all uniquely identifiable quantities of uranium, * shred cartridge filters, HEPA filters and similar items * re-assay the sorted and shredded waste * remove any material in excess of 250 grams 235U mass from the mass controlled area and stage it to become part of the next process batch to be processed through the MERF equipment." "Controlled Parameters:" "For the MERF process, the controlled criticality parameter is mass. Per the SPC operating license, mass control as the only controlled parameter is allowed provided:" "1. The work station shall be limited to one safe batch, where a safe batch is defined as no more than 0.45 of the minimum critical mass of the material in process;" "2. No more than one safe batch may be moved at one time when introducing or removing material from a workstation;" "3. Individual safe batches shall be spaced a specified minimum distance apart;" "4. A record shall be maintained of the SNM inventory at each mass-limited workstation; and" "5. SNM inventory control shall assure material buildup over time will not cause the batch limit to be exceeded." "In MERF the mass limit is 790 g 235U, < 45% of a minimum critical mass at 5 wt.% enriched. An inventory of the material processed through the facility is maintained and the facility is inspected by operating and engineering personnel for potential holdup after each batch is processed through the facility. The following controls are used to ensure compliance with the 790 g 235U mass limit:" "Prior to being considered for a process batch, each drum / HEPA filter has a three party check or an electronic comparison between two separate record systems to ensure that the mass assigned to the drum is free from transcription / transposition errors. If sufficient data does not exist, the drum or HEPA must be recounted." "Target batch size is limited to 250 g 235U." "SPC operating staff selects a batch of drums and transfer them to a locked location." "SPC engineering staff verifies the target batch size of 250 g 235U is not exceeded." "SPC Process Operator and Supervisor or lead technician verify the drums in the locked area are part of the designated batch and that the target batch size of 250 g 235U is not exceeded." "Operating staff then resorts the waste to identify any uniquely identifiable quantities of U compounds prior to processing the waste through the washer." "After resorting and shredding cartridge filters, HEPA filters and similar items, the material in the process batch is recounted using NDA. Any material in excess of 250 g 235U is set aside outside the mass controlled area and becomes a part of the next process batch." "Estimated Amount, Enrichment, and Form Of Licensed Material:" "The licensed material is urania sludge. The total 235U present in the process batch was calculated to be 895.9 grams. This is 51% of the minimum critical mass for this type of material enriched to 5 wt.% 235U. The actual material involved was enriched to less than 3.6 wt% 235U." "Nuclear Criticality Safety Control(s) Or Control Systems and a Description of the Failures Or Deficiencies:" "The filters came from two separate waste drums that had been packaged in 1993 or early 1994. Although waste segregation/accumulation controls were not as robust at that time as they are presently, wastes placed in such drums were required by criticality safety instructional card to contain only contamination levels of uranium. Therefore, sock filters containing this much U bearing material should not have been placed in a waste drum. The NDA system used to determine the U content of waste drums does not provide accurate results for concentrated high density materials such as the sludge contained in the sock filters. This is a known limitation of the NDA system. SPC currently takes extra precautions to ensure that the use of NDA is compatible with the known limitations of this equipment and that the waste matrix in the waste drums is adequately similar to that in the standard used to calibrate the NDA system. As previously stated, in 1993 and 1994 the procedures for segregating and processing waste were not as stringent as they are now." "Corrective Actions To Restore Safety Systems and When Each Was Implemented:" "The MERF process operators promptly segregated, sampled, and then removed from MERF the sludge accumulations discovered in the waste drums, thereby restoring compliance with the mass control limit for the facility." "SPO operating, engineering and safety personnel have reviewed all other stored containerized waste types and have confirmed that only wet waste drums may be subject to this type of failure. This determination is based on the date of generation of the other drums in storage and the types of material in the drums." "As a precautionary measure, SPC operating personnel have started placing wet waste drums on the waste storage pad into a single tier storage array. Because record keeping requirements dictate that the storage location of each drum be accurately recorded, this action is expected to be completed in about 1 week." "Additional corrective actions are still being evaluated." The licensee will notify NRC Region 4. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 4 | WA | FUE | [5 empty] | 0
37423 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2000-10-12 06:30 | 2000-10-12 09:07 | 2000-10-12 | POTENTIAL CONDITION OF A REACTOR COOLANT SYSTEM BOUNDARY DEGRADATION The following text is s portion of a facsimile received from the licensee: "... The plant is currently in Cold Shutdown (Mode 6) of Refueling Outage 12." "On October 7 [at] 2000 [hours], plant personnel identified an accumulation of approximately 100 pounds of boric acid in the 'A' hot leg area of the reactor vessel. Some boric acid and insulation was removed from the area of the suspected leak path to allow for further inspection." "On October 12 at 0630 hours, plant personnel visually identified a potential leak area on the first weld off the reactor vessel at the nozzle to pipe connection of the 'A' loop hot leg. Visual inspection has revealed trace amounts of boron buildup on the weld between the vessel nozzle and the hot leg pipe. Based on this preliminary information, plant personnel suspect some leakage has occurred through the pressure boundary at this weld." "The RCS is currently depressurized. We have suspended preparations to remove the reactor vessel head to allow time to perform [non-destructive examination (NDE)] on the weld. V.C. Summer expects the NDE inspection to be completed around noon today. The results will be used to develop repair plans." "The NRC Resident Inspectors have been informed of the condition." * * * UPDATE ON 10/12/00 @ 1452 BY CROGEN TO GOULD * * * V. C. Summer is providing an update to the initial 10 CFR 50.72(b)(2)(i) notification made at 0907 this morning. Plant personnel have completed the cleanup and dye penetrant test of the weld on the 'A' RCS Hot Leg. The test has confirmed a 4" long hairline crack in the weld between the hot leg piping and the Reactor vessel nozzle. This pipe is about 30" in diameter. This weld is located about 3 feet from the vessel wall and is accessible in the inspection port at the Reactor vessel flange area. The crack is located about 17" from the top of the pipe. The plant will continue defueling and initiate weld repair of the affected nozzle. Technical and repair support is being pursued at this time to make appropriate inspections and repairs. The NRC Resident Inspector has been made aware of the latest findings. The Reg 2 RDO(Barr), EO(Goodwin), IRO(Giitter) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37422 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2000-10-10 17:00 | 2000-10-11 16:12 | 2000-10-11 | 24-HOUR NRC BULLETIN 91-01 REPORT "At approximately 1700 hours on October 10, 2000 GNF-A Operations determined that one of two controls established for moderation control on material feed to a process area located within an Moderation Restricted Area (MRA) had been lost. The controls require two samples that verify acceptable moisture content for the feed material. One of two required moisture samples was not analyzed due to an inadvertent purge of the moisture sample request from the IMR (In-process Material Release) database, and the material was improperly released for processing. "The second independent moisture sample was performed and confirmed the measured moisture content was satisfactory, therefore no unsafe condition existed. "This event is reported pursuant to NRC Bulletin 91-01 (within 24 hours) due to loss of a single control on moderation. Material can feed to affected moderation restricted area (MRA) of process have been suspended pending investigation and implementation of corrective actions. "SAFETY SIGNIFICANCE OF EVENTS: Low safety significance - independent control on moderation remained intact; material met moisture specifications. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: Multiple failure modes required before a criticality accident could occur. "CONTROLLED PARAMETER(S) (MASS, MODERATION , GEOMETRY, CONCENTRATION, ETC.): Moderation: Process equipment limited to uniform moisture content of 10.5 wt. % (105,000 ppm H2O). Moderation Safety Factor = safety moderation limit / process moderation limit = 105,000 / 4000 = 26.2. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST BASE CRITICAL MASS): Affected equipment contained approximately 100 kgs of UO2 and gadolinia (Gd2O3) at a target enrichment of ~4.40 wt. % U235. The vibromill blender process equipment is located in the moderation-restricted area, which is demonstrated safe for uniform moderation limit of 10.5 % water equivalent moderation (105,000 ppm H2O). "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: One of two required moisture samples was not analyzed due to an inadvertent purge of the moisture sample request from the IMR (In-process Material Release) database, and the material was improperly released for processing in the gad shop MRA. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Feed material re-sampled for moisture content - results satisfactory (<4000 ppm H2O). 2. Suspended material can feed to the affected process area. 3. Investigation and implementation of corrective actions pending." The licensee intends to notify the NRC Region 2 (David Ayres), the New Hanover County and North Carolina State agencies of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0
37421 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-10-10 19:07 | 2000-10-10 20:05 | 2000-10-10 | THE TURBINE DRIVEN AUXILIARY FEEDWATER PUMP STARTED UNEXPECTEDLY "During turbine driven auxiliary feedwater pump testing the pump started when it should not have. A check of the procedure found that it was not correctly removed from service for the test." It is believed that a jumper placement was done wrong and is being investigated. The licensee intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37420 | 0 | MIDAMERICA PETERBUILT |  |  |  |  | 2000-09-25 | 2000-10-10 15:17 | 2000-10-10 | LOST STAT ATTACK GUN WITH POLONIUM-210 SOURCE The company lost an anti-static device used in painting vehicles. The device is a Stat Attack Gun, containing a nominal 10 mCi Po-210 sealed source. The device is a model # PBM1002H, serial #9807KB. The device is believed lost in the trash after an extensive search of the facility. The company notified NRC Region 3 (Monte Phillips). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37419 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-09 00:42 | 2000-10-09 01:03 | 2000-10-09 | HYDRAZINE LEAK IN TURBINE BUILDING. Salem Unit 1 declared an Unusual Event at 0042 based on ammonia smell in Unit 1 Turbine Building. Area was evacuated - no personnel were working in the area. It appears as though hydrazine leaked from a chemical addition tank due to a failure of a chemical transfer pump. Loss prevention personnel verified no one in area. Air samples all less than 1ppm hydrazine. Odor is dissipating. Abnormal Operating Procedure for Toxic Gas Release has been implemented and Control Room Ventilation placed in Fire Outside Control Room Alignment. Unit 1 remained at 100%. No safeguards activated or needed. All safeguards equipment is available . Hydrazine was contained in a dike and directed to chemical waste. Air sampling will continue until spill is cleaned up and no odor remains. State and local Counties notified. The NRC Resident Inspector will be notified of this event by the licensee. * * * Update on 10/09/00 at 0502 ET by Przekop taken by MacKinnon * * * Unusual Event terminated at 0500 ET. All hydrazine was cleaned up (25 to 50 gallons). State & local counties will be notified by the licensee. R1DO (Linville), NRR EO (Grimes), IRO (Miller), & FEMA (Canupp) notified. DOE, USDA, HHS and DOT(EPA) notified via fax. The NRC Resident Inspector will be notified by the licensee of the termination of the Unusual Event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37418 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-10-08 16:20 | 2000-10-08 18:11 | 2000-10-08 | "B" REACTOR RECIRC PUMP MOTOR GENERATOR OVERSPEED STOPS FOUND SET HIGH (NON-CONSERVATIVE) DURING SURVEILLANCE TESTING "During the performance of the 18 month surveillance requirement to demonstrate operability of the reactor recirc pump motor set scoop tube mechanical and electrical stop overspeed setpoints to be less than or equal to 109% and 107%, respectively, the 'B' MG set stops were found non-conservatively high. The magnitude of offset has not been calculated as of this time, but the setpoints have been readjusted to their proper settings as of 1732 hours this date. "The potential impact of this condition would be a function of the reactor recirc pump 'runaway' transient. If that analyzed transient were to have occurred, the potential existed for the flow dependent minimum critical power ratio to have been exceeded. This could result in exceeding the safety limit (MCPR) under those postulated conditions. "Evaluation of the potential cause of the improper settings is under way." The licensee will inform the NRC resident inspector and the Lower Alloways Creek Township. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37417 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-10-08 05:18 | 2000-10-08 17:59 | 2000-10-08 | 24-HOUR REPORT INVOLVING A SAFETY SYSTEM ACTUATION DUE TO FAILURE OF FREEZER/SUBLIMER INLET VALVE TO CLOSE "At 0518 on 10/8/00 the PSS office was notified that the C-333 Unit 4 Cell 9 freezer/sublimer (F/S) 'B' valve had failed to close following completion of a high-high weight safety system trip test. The F/S high-high weight trip actuated due to accumulation of UF6 in the vessel caused by the failure of the 'B' valve. The F/S high-high weight trip system is required to be operable while in modes F/S 1 and F/S 3 per TSR 2.4.3.1. The F/S high-high weight trip actuated within the specified limiting control settings of TSR 2.4.3.1. The F/S 'B' valve was manually closed, the F/S was declared inoperable and the excess UF6 was removed from the vessel. The F/S was placed in mode F/S 6 (out of service). "The safety system actuation is reportable to the NRC as required by Safety Analysis Report section 6.9, table 1, criteria J.2, Safety System actuation due to a valid signal as a 24-hour event notification. "The NRC Resident inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37416 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-10-06 19:39 | 2000-10-06 21:19 | 2000-10-06 | AUTOSTART OF AUXILIARY FEEDWATER PUMPS WHILE PREPARING TO ROLL THE MAIN TURBINE "At 1939 hours on 10/6/2000, with the reactor in mode 1 at 13 % power, preparations to roll the Main Turbine for Main Turbine testing, the 'B' Main Feedwater Pump tripped on low condenser vacuum. 'A' Main Feedwater Pump was not in service, and 'B' Main Feedwater Pump was supplying all Steam Generators. "Off Normal Instruction (AOI-16) was entered and the Standby Main Feedwater Pump was started to supply all Steam Generators, the reactor was maintained at 13 % power. All Auxiliary Feedwater Pumps started upon receipt of the ESF signal (loss of both Main Feedwater Pumps). "This is Reportable event under 10 CFR 50.72(b)(2)(ii) and 50.73(a)(2)(iv), any event or condition that results in a manual or automatic actuation of any engineered safety feature (ESF)." The licensee informed the NRC resident inspector. | 13 | 0 | 0 | 13 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37415 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-10-05 | 2000-10-06 19:45 | 2000-10-06 | AGREEMENT STATE REPORT - SOURCE DETACHED FROM DRIVE ROD "The licensee notified the WA Department of Health, Division of Radiation Protection (WDOH), of an additional mechanical failure involving the same Ronan Engineering Company Model SA-4 gauging device which suffered a 'source disconnect' as reported in event #WA-00-046. The device is specifically licensed for density process measurements and uses a Cesium 137 sealed source, Amersham Model CDC.711M not to exceed 74 gigabecquerels (2 curies). The source is normally mounted at the end of a source rod, approximately six feet long. In this particular model version, the source rod consists of two screw-together extensions (approximately two and a half feet each) which screw into the same diameter source holder (approximately half a foot long). When operating, the rod with source is lowered through the shielded storage position, into the integral and enclosed dry well tube. When not in operation, the rod with source is raised to place the source into a safe position inside the main shielding. On September 13, the top screw connection came unscrewed apparently due to prolonged mechanical vibration. This 'disconnect' was repaired and the gauge returned to operation on September 18. At the same time the lower screw connection was found to be partially unscrewed as well. Both connections were opened, cleaned, coated with 'Lok-tite' and tightened. "On October 5, during routine 'end of shift' return of the source to the shielded position, the source rod snapped off at the lower screw connection. The operator was able to quickly grab the exposed end of the source holder and prevent the source from falling to the bottom of the dry well. The source was successfully locked out in the shielded storage position. Examination of the source rod indicates that the male screw connector sheared off at its juncture with the main body of the rod section. The cause of this additional failure is under investigation. The manufacturer is working on a retrofit for all four gauges of this type at this licensee's facility. Department staff will be present during the retrofit." HOO NOTE: See event #37353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37414 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-10-06 09:20 | 2000-10-06 09:47 | 2000-10-06 | OFFSITE NOTIFICATION - THE LICENSEE NOTIFIED THE FLORIDA FISH & WILDLIFE CONSERVATION COMMISSION ABOUT A LIVE LOGGERHEAD SEA TURTLE THAT WAS FOUND IN THE INTAKE NET. THE TURTLE WILL BE SENT OFF FOR REHABILITATION. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37413 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-10-05 15:00 | 2000-10-05 16:52 | 2000-10-05 | UNIT OUTSIDE DESIGN BASIS OF FIRE PROTECTION PROGRAM "During evaluations associated with a condition (CR-WF3-2000-1088), previously reported in a one hour call on 9/18/00 (Event #37341 ), it was determined today that a similar condition exists in Fire Area 39. The condition found today, assuming a hypothetical Appendix R fire in the area, could conceivably have resulted in the loss of all three charging pumps. The Waterford 3 FSAR (Section 9.5.1) states that (for Fire Area 39) 'in the event that an unmitigated fire is in the charging pump area, either Charging Pump A or Charging Pump B and AB will be available for reactivity control and reactor coolant makeup...'. This availability is based on an exemption granted per SSER 8 and LP&L exemption request letter W3P84-0709. The exemption for part height firewalls around charging pump 'A' cable trays and conduit being provided with fire wrap. It was determined today that the conduits and cable trays for Charging Pump A and AHI8A (which provides cooling to the charging pump 'A' area) have not been completely wrapped. Thus an appendix R fire in fire area RAB39 has the potential to disable all three charging pumps. The charging pumps are required for cold shutdown actions and as such per Appendix R, repairs are allowed. However in order to take credit for repair actions, specific procedures and staged materials for such repairs are required. These provisions were not in place. This condition is being reported as being outside the design basis of the fire protection program. The cables and conduits were immediately identified as impaired and compensatory actions were established (hourly fire watches). The condition has been entered into the plant corrective action program (CR-WF3-2000-1169)." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37412 | 0 | WILLS EYE HOSPITAL |  |  |  |  | 2000-10-04 | 2000-10-05 16:48 | 2000-10-05 | POTENTIAL MEDICAL MISADMINISTRATION INVOLVING MISTARGETED GAMMA-KNIFE TREATMENT A PATIENT UNDERGOING GAMMA-KNIFE TREATMENT FOR AN ACOUSTIC TUMOR, RECEIVED APPROXIMATELY 4 GRAY TO TISSUE 8 MILLIMETERS ABOVE THE TARGET DUE TO AN ERROR INPUTTING ONE OF THREE COORDINATES DURING THE FIRST OF THREE SHOTS ON 10/4/00. THE ERROR WAS RECOGNIZED WHILE SETTING UP FOR THE REMAINING TWO SHOTS. THE PHYSICIAN WAS INFORMED AND THE TREATMENT PLAN MODIFIED SO THAT THE TARGET WOULD RECEIVE THE CORRECT DOSE. THE LICENSEE PLANS ON CONTACTING NRC REGION I TO DISCUSS REPORTABILITY OF THIS EVENT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.33 |  |  |  | 0
37411 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2000-10-04 23:00 | 2000-10-05 15:48 | 2000-10-05 | EVIDENCE OF RCS PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING INSERVICE INSPECTION OF PRESSURIZER HEATER NOZZLE SLEEVE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 4, 2000 at approximately 23:00 MST, Palo Verde Nuclear Generating Station (PVNGS) Unit 2 inservice inspection personnel discovered evidence of reactor coolant system (RCS) pressure boundary leakage. PVNGS Unit 2 was shutdown in Mode 4 conducting cooldown and depressurization into its ninth refueling outage at the time of discovery. Currently, PVNGS Unit 2 is in Mode 5. RCS temperature is approximately 170 degrees Fahrenheit and RCS pressure is approximately 350 psia. "The leakage was discovered at pressurizer heater nozzle sleeve A06 during inservice inspection (ISI) activities. The leakage was detected in the form of a small deposit of boron accumulation at the sleeve. PVNGS has conducted inspections of these heater sleeves during each refueling outage since the discovery that Inconel alloy 600 heater sleeves are susceptible to cracking. No evidence of leakage was detected when inspected during the last outage approximately 18 months ago. The apparent cause is primary water stress corrosion cracking (PWSCC) from the inside diameter of the sleeve. "The timing of this ENS report was based on the determination at 10:30 MST on October 5, 2000 that the boron accumulation represented a serious degradation of a principal safety barrier. PVNGS Unit 2 Technical Specification Limiting Condition for Operation (LCO) 3.4.14 (RCS Operational Leakage) permits no reactor coolant system pressure boundary leakage. It was therefore conservatively concluded that any evidence of pressure boundary leakage, regardless of magnitude, represents serious degradation of a principal safety barrier. Technical Specification Limiting Condition for Operation 3.4.14 is applicable in Modes 1, 2, 3 and 4. Unit 2 entered Mode 5 at 01:50 MST on October 5, 2000, in compliance with LCO 3.4.14 ACTION B.2. The sleeve will be repaired or replaced prior to re-entering Mode 4. "No ESF actuations occurred and none were required. No structures, systems or components were inoperable that contributed to this event, particularly the fuel cladding and the containment fission product barriers. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode2: Hot Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37410 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-10-04 18:20 | 2000-10-04 19:50 | 2000-10-10 | POTENTIAL OUTSIDE DESIGN BASIS ISSUE DUE TO LACK OF DOCUMENTATION TO SHOW THAT ATMOSPHERIC STEAM DUMP VALVE CAPACITY WILL SUPPORT THE COOLDOWN ASSUMPTIONS FOR A STEAM GENERATOR TUBE RUPTURE EVENT WHEN OFFSITE POWER IS NOT AVAILABLE The following text is a portion of a facsimile received from the licensee: "During a main steam and steam dump system validation, no documentation could be found to show that the atmospheric steam dump (ADV) valve capacity will support the 44-minute cooldown assumptions for a steam generator tube rupture (SGTR) event as described in the FSAR when offsite power is not available. FSAR Chapter 14 and plant procedures include assumptions and procedure steps that require use of the [ADVs] to cool down the reactor coolant system (RCS) within 44 minutes of a SGTR event to allow the RCS pressure to equalize with the faulted steam generator pressure to terminate primary to secondary break flow. The SGTR radiological dose assessment is based upon this 44-minute time frame for ending flow to the ruptured steam generator." "The current licensing basis calculation for the SGTR event calculates steam releases from the intact and the faulted steam generators for the purpose of determining offsite dose releases. However, this calculation does not appear to support a demonstration of the capability of the ADV on the intact steam generator to reduce the primary system temperature (with sufficient subcooling margin) to allow depressurizing the RCS to equilibrium pressure with the faulted steam generator. No calculation or other documentation has been located that provides an evaluation of the amount of heat in the form of steam to be removed by the intact steam generator's ADV to provide the cooldown within the 44-minute time assumed in the accident analysis. An operability determination is being performed per [Generic Letter] 91-18." The licensee stated that there was nothing unusual or not understood and that all systems functioned as required. The licensee also stated that the units were not in any limiting conditions for operation as a result of this issue. The licensee notified the NRC resident inspector. * * * RETRACTION on 10/10/00 at 0934 ET by John Sell taken by MacKinnon * * * The licensee's engineering staff has completed an Operability Determination (OD) in accordance with GL 91-18, which investigated the applicability of the existing SGTR analysis for Point Beach Nuclear Plant (PBNP). This evaluation concluded that the actual installed capacity of the ADV supports the 44 minute cooldown assumption and that there exists ample assurance that under design and licensing conditions, the PBNP physical plant can actually support a significantly shorter duration mitigation. The limiting factor for the SGTR mitigation remains the operator response and the procedures driving that response. The approved OD concluded that the ADV system is operable and fully meets performance requirements. R3DO (John Madera) notified. The NRC Resident Inspector was notified of this event retraction by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37409 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2000-10-03 20:55 | 2000-10-04 11:12 | 2000-10-04 | NON - LICENSED OPERATOR INADVERTENTLY STARTED THE "A" EMERGENCY DIESEL GENERATOR (EDG). At 2055 on October 3, 2000, the "A" EDG received an emergency start signal in response to an inadvertent actuation of the EDG local emergency start pushbutton. The local emergency start pushbutton was inadvertently actuated by non-licensed Operations personnel while reviewing procedural guidance for emergency starting the EDG from the local control panel. The EDG achieved rated voltage and speed following the start signal, but was not required to connect to the Class 1E distribution system during the event. The EDG was subsequently secured and restored to a standby status. Evaluations to determine the cause for why reporting requirement 10CFR50.72(b)(2)(ii) was not initially identified will be addressed within the station's corrective action program. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37408 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-10-03 15:28 | 2000-10-04 09:33 | 2000-10-05 | LOAD CELL CALIBRATION DATA FOR SOME FREEZER SUBLIMERS FOUND TO BE NON - CONSERVATIVE. At 1528 on 10/03/00, the Plant Shift Superintendent (PSS) was notified by engineering that load cell calibration data for some freezer sublimers was suspected to be in error. The load cells are part of the High High Weight Trip System for the freezer sublimers which is required by Technical Safety Requirement (TSR) to be operable. Data for many of the load cells calibrated on site shows the identified load cells do not meet the specifications credited in the existing setpoint calculations and the calibration procedures. The problem appears to be consistent among the load cells. The load cells data indicates less weight than what was actually applied. It has been determined that this deficiency may affect the ability of the freezer sublimers' ability to actuate the High High Weight Trip System at the required Limited Control Setting (LCS). This deficiency would not affect the ability of the freezer sublimers to actuate the High High Weight Trip System below the Safety Limit (SL). There are 30 of the 10,000 lb. Capacity and 4 of the 20,000 lb. capacity load cells that are affected. Investigation revealed that none of the four 20,000 lb. Load cells have been installed. The 20,000 lb. Load cells are being controlled to ensure they are not installed. The affected in service freezer sublimers were declared inoperable by the PSS. Engineering is reviewing work package data and the freezer sublimers that do not contain suspected load cells are being returned to service. Resolution of this issue is being pursued by Operations, Maintenance, and Engineering. The equipment is required by TSR to be available and operable and should have been operating. No redundant equipment is available and operable to perform the required safety function. The NRC Resident Inspector has been notified of this event. * * * UPDATE 2140EDT ON 10/5/00 FROM ERIC WALKER TO S. SANDIN * * * "UPDATE: During the investigation of the initiating event, a more detailed review of load cell data, including vendor calibration data, was performed with additional load cells being called into question. The vendor data indicated levels which were in the non-conservative direction. The location of the additional load cells was determined and 8 additional freezer sublimers were declared inoperable (two of these 8 were already inoperable). 6 freezer sublimers had been in operation with the suspect load cells installed, and the High High Weight Trip System was required, but would not have operated as required by the TSR. This deficiency would not have allowed the freezer sublimer to exceed the TSR Safety Limit. No redundant equipment was available to perform the intended safety functions. This is reportable as required by 10 CFR 76.120(c)(2)." The NRC Resident Inspector and DOE Site Representative have been informed. Notified R3DO(Madera) and EO(Hodges). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0
37407 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-10-03 21:51 | 2000-10-04 01:23 | 2000-10-04 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE Failed to receive proper indication of turbine position circuitry indicating lamp following HPCI system run at rated pressure. Investigation by station personnel identified a failed oil pressure switch which provides indication of stop valve closure to turbine reset circuit. Failure of the switch prevents automatic and remote reset of HPCI turbine trips. This failure renders HPCI inoperable and would prevent it from fulfilling its safety function. Technical Specification 3.5.a (14 days to return to service or shutdown) entered. All other Emergency Core Cooling Systems are fully operable. Efforts are proceeding to repair/replace the switch. The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37406 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-10-03 | 2000-10-03 17:56 | 2000-10-03 | AGREEMENT STATE REPORT REGARDING A SHIPMENT OF CONTAMINATED SCRAP METAL AT AMERICAN METAL AND IRON COMPANY IN SAN JOSE, CALIFORNIA A few months ago, American Metal and Iron Company sent a shipment of scrap metal to South Korea. South Korea subsequently rejected the material and returned it to American Metal and Iron Company in San Jose, California, because the material was contaminated with radium-226. (American Metal and Iron Company is a scrap metals dealer/metal recycler, and the scrap metal involved was a mixture of sheet metal conduit that had been compressed into a 4' by 4' by 6' block weighing approximately 1 ton.) American Metal and Iron Company representatives originally thought that the material had come from Lawrence Livermore and that it was the responsibility of the Department of Energy (DOE). Accordingly, American Metal and Iron Company representatives contacted DOE, and a DOE representative responded to the site to characterize the contamination. The highest radiation reading at the surface of the scrap metal was 0.2 mR/hour, and the highest wipe test result was 3,000 dpm. DOE subsequently denied that this was their material because the contract for Lawrence Livermore expired in January and because American Metal and Iron Company received the material a few months ago. In addition, DOE regulations would not allow DOE to sent out metal contaminated with oil. At the time of this notification, American Metal and Iron Company personnel did not know where they got the material. On the premise that this is not DOE material, the State of California Radiologic Health Branch plans to assume responsibility to make sure that American Metal and Iron Company either sends the material to a licensed waste site for disposal or gets a health physicist to characterize the material and provide a request as to why they should not sent it to a licensed waste site. The State (Kent Prendergast) requested that this information be entered as an event report and into the N-Med system. The State also reported that they had received calls from both the Environmental Protection Agency (EPA) and the NRC Region 4 office regarding this issue. HOO NOTE: At 1312 EDT on 10/03/00, the NRC Operations Center received some information regarding this issue from an independent marine surveyor in Oakland, CA. At 1354 EDT, the same individual reported that the survey meter had been read incorrectly and that this was a none issue. In order to ensure that all of the appropriate parties were involved and that appropriate actions were being taken, a conference call was subsequently conducted at 1500 EDT with representatives from the State of California, EPA Region IX, and the NRC. Participants included the State of California Office of Emergency Services (Richard Osborne) and EPA San Francisco (Terry Brubaker) as well as NRC representatives from the Region IV office (Dave Loveless and Dwight Chamberlain), the Office of Nuclear Materials Safety and Safeguards (Brian Smith and Fred Brown), and Incident Response Operations (Charles Miller). During this conference call, it was agreed that the State would followup on this event and report the results to both EPA and NRC Region IV. (Call the NRC operations officer for a State contact telephone number, the address for American Metal and Iron Company, and the name and telephone number of the independent marine surveyor.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37405 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-10-03 08:35 | 2000-10-03 17:39 | 2000-10-03 | DISCOVERY THAT AN AUTOMATIC SHUTDOWN OF AN AUTOCLAVE ON 09/26/00 WAS A VALID SAFETY SYSTEM ACTIVATION (24-hour report) The following text is a portion of a facsimile received from Portsmouth personnel: "At 0835 [hours] on 10/03/00, the Plant Shift Superintendent was informed by the Autoclave System Engineer that a Safety System actuation that occurred on 09/29/00 was a valid event. At the time of the event, all indications available to the operators indicated an invalid activation. The autoclave was declared inoperable, and testing of the instruments for as-found readings was performed. After obtaining the as-found readings on the instrument loops, additional testing was conducted during the evening of 10/02/00. This steam load testing allowed the pressure to reach the trip point assigned value for shell high steam shutdown. Based on this information, we are reporting an actuation of a safety system. There was no release of radioactive material from this event." Portsmouth personnel notified the NRC resident inspector as well as the Department of Energy site representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
37404 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-10-02 10:00 | 2000-10-03 16:17 | 2000-10-03 | AGREEMENT STATE REPORT REGARDING THE LOSS OF FIVE SEALED SOURCES AT ADAC LABORATORIES IN MILPITAS, CALIFORNIA Adac Laboratories (State license #2760-43) in Milpitas, California, manufactures nuclear medicine equipment and utilizes sealed sources for testing cameras, etc. The sources are stored in a depleted uranium storage container. On 09/26/00, Adac Laboratories performed an audit, and the location of five sealed sources could not be determined (one 28.5 mCi cesium-137 source and four gadolinium-153 sources with activities of 14.2 mCi, 0.87 mCi, 0.2 mCi, and 0.15 mCi). Adac Laboratories has taken action to secure that remaining sources and is making efforts to locate the missing sources. The licensee notified the State of California at approximately 1000 PDT on 10/02/00, and a representative from the State of California Radiologic Health Branch (Kent Prendergast) in turn notified the NRC Operations Center of the loss of five sealed sources at 1617 on 10/03/00. (Call the NRC operations officer for a State contact telephone number, licensee address, and licensee radiation safety officer name.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37403 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2000-10-03 15:22 | 2000-10-03 16:05 | 2000-10-03 | DISCOVERY THAT REACTOR POWER EXCEEDED 100% FOR A PERIOD OF GREATER THAT 8 HOURS DUE TO AN INSTRUMENT FAILURE ON THE LEADING EDGE FLOW METER The following text is a portion of a facsimile received from the licensee: "St. Lucie Unit 2 average power level was calculated to have been 100.1% power for greater than 8 hours on September 25, 2000. This power level resulted from an instrumentation failure on the Leading Edge Flow Meter (LEFM) which was utilized by the [Digital Data Processing System (DDPS)] Plant Computer Calorimetric power level indication. A failure in the DP1 transducer path on the 'A' Loop of the LEFM instrument resulted in a decreasing feedwater (FW) flow output value." "Detailed analysis of the plant's performance over September 24, 2000, and September 25, 2000, indicate an unexpected decrease in 'A' LEFM Feedwater Flow indicated to the DDPS beginning approximately mid-day on September 24, 2000, without a corresponding decrease in 'A' Venturi based Feedwater Flow. A direct and corresponding decrease in DDPS Calorimetric Power results from the 'A' LEFM FW Flow decrease. A corresponding decrease in 'B' side LEFM or Venturi FW Flow was not present. This confirmed the Vendor's initial report of an 'A' side instrumentation problem within the LEFM System. The Operations Crew questioned this decrease and initiated conservative action as a result of DDPS Calorimetric Power observed to be lowering. Prior to and during the LEFM instrument failure, the indicated Calorimetric Power level in use by the plant operators did not exceed 100.0% for greater than 8 hours. The LEFM transducer was repaired and returned to service [on] October 1, 2000." "Based upon subsequent analysis of 'B' side LEFM FW Flow and 'A' [and] 'B' side Venturi FW Flow, the change in power was approximately 0.2% reactor power. The maximum power level was approximately 99.9% on September 24, 2000, and approximately 100.1% (with a maximum of 100.2%) power on September 25, 2000. An increase to 100.2% is well within the uncertainty for DDPS Calorimetric Power of 1.3% and initial power assumed within the Safety Analysis of 2%." "This event was determined to be reportable at 15:22 on October 3, 2000, in accordance with St. Lucie Unit 2 Operating License condition 2.F: Operation of St. Lucie Unit 2 in excess of 100% power for greater than 8 hours is in excess of the plant's Operating License limit of 'not in excess of 2700 megawatts thermal (100% power).' The Unit 2 License requires that [the licensee] 'shall report any violations of these requirements within 24 hours by telephone and confirm by telegram, mailgram, or facsimile transmission to the NRC Regional Administrator, Region II, or his designee, no later than the first working day following the violation, with a written follow-up report with 14 days.' " The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0
37402 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2000-10-03 12:50 | 2000-10-03 13:16 | 2000-10-03 | ISSUANCE OF A PRESS RELEASE REGARDING A TEMPORARY WORK STOPPAGE ON MOST PLANT DISMANTLEMENT ACTIVITIES FOLLOWING A CONTAMINATION INCIDENT At 1250 on 10/03/00, the licensee issued a press release regarding an incident that occurred on 09/29/00. The following text is a portion of a this press release: "Maine Yankee has temporarily halted work on most plant dismantlement activities following an incident last Friday [09/29/00] where the clothing of 4 workers was slightly contaminated with radiological material. The workers were welding shielding plates in 2 waste shipping containers on the non-nuclear side of the plant. The shipping containers previously had been mistakenly released from the nuclear side of the facility. There was no measurable internal dose to the workers or skin contamination from the incident. The radiological dose to the exposed workers was less than one millirem. In Maine, the annual radiological dose an individual receives from all sources, natural and manmade, is about 350 millirem." "The clothing contamination was discovered early Saturday morning when one of the workers who had been sent to perform a task on the nuclear side of the plant alarmed a radiation monitor when exiting. Technicians identified the shipping containers as the source of the contamination and evaluated 3 other workers who had been working on the containers. No contamination was found on the clothing of these individuals. Maine Yankee also followed up with another ten workers who worked on the containers during the day shift Friday to determine whether there were any additional articles of contaminated clothing. Three of these individuals were found to have slightly contaminated clothing. As a precautionary measure, Maine Yankee is surveying the homes and vehicles of the affected workers. No additional contamination has been identified." "An analysis is underway to determine specifically how the contaminated containers were released to the non-nuclear side of the plant. Radiological work will only resume when Maine Yankee's senior management is convinced work control procedures are appropriate and are being implemented thoroughly and completely. Maine Yankee has discussed this incident and our response with the U.S. Nuclear Regulatory Commission and the State of Maine." " 'Controlling radiological material is fundamental to the success of the decommissioning project. That is why, even though there is no health concern as a result of this incident, we stopped plant dismantlement activities until we have convinced ourselves that we are ready to return to work,' said Mike Meisner, Maine Yankee President. Meisner added, 'I am pleased, however, that redundant controls and processes we have in place as well as our professional staff helped us identify the problem and react appropriately.' " The licensee notified an onsite NRC inspector. (Call the NRC operations officer for a licensee contact name and telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37401 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-10-02 15:41 | 2000-10-02 22:52 | 2000-10-17 | HISTORICAL INFORMATION REGARDING A FAILURE TO COMPLETE X-333 LOW ASSAY WITHDRAWAL (LAW) COMPRESSOR PYROTRONIC SMOKE DETECTION SYSTEM ENGINEERING MODIFICATIONS AS DESIGNED (24-hour report) The following text is a portion of a facsimile received from Portsmouth personnel: "The engineering modifications to the X-333 LAW compressor Pyrotronic smoke detection system were not completed as designed. The modifications were intended to cause the safety system to alarm with only one smoke head firing instead of requiring two smoke heads to activate the alarm. The investigation into this matter was completed 10/02/00 at 1541 [hours]. The investigation identified that on one occasion, a LAW station compressor was in an applicable operating mode where the Pyrotronic smoke detection safety system was required to be operable and one of the heads was in fact inoperable making the system inoperable. Operations personnel did post an immediate smoke watch to maintain [Technical Safety Requirement (TSR)] compliance." "This finding is reportable to the NRC as a 24-hour event due to the fact the equipment was required by the TSR to be available and operable and should have been operating, and no redundant equipment was available to provide the required safety function." "Note: The engineering modifications were completed 10/01/00, and applicable [post-maintenance tests were completed satisfactorily]." It was reported that the inoperable head that was identified to be inoperable on 10/01/99, but this issue was not identified until the investigation was completed today (10/02/00) at 1541 hours. It was also reported that there was nothing unusual or misunderstood and that all systems functioned as required. NOTE: The X-333 building LAW station was reported to be a UF6 withdrawal station. Portsmouth personnel have notified the NRC resident inspector and plan to notify the Department of Energy site representative. * * * UPDATE 2125EDT ON 10/17/00 FROM KURT SISLER TO S. SANDIN * * * "NRA [Nuclear Regulatory Affairs] has reviewed the basis for the above NRC event notification and determined that this event can be retracted. The following provides the basis for this conclusion. "On October 2, 2000, the NRC was notified of a design problem which caused the LAW UF6 Smoke Detection system to be inoperable at a time when the system was required to be operable in accordance with TSR 2.5.3.3 (outside each compressor housing one smoke detector must be operable in modes II or III). The design problem resulted from the fact that Pyrotronics smoke detectors were installed in series. In this configuration, the failure of one detector could prevent the redundant detector from activating the alarm contacts in the event of a UF6 release. "A review was conducted by engineering to determine if LAW had ever been in Mode II or III with a failed outside compressor housing Pyrotronics detector. The review identified one occasion in the past where this was the case. As a result of the series configuration, the remaining Pyrotronics detector would not have been able to perform its design function at that time. Although there were CADP smoke detectors available for this area, operating procedures did not recognize that CADP smoke detectors provided backup to the Pyrotronics detectors. Based on the fact that the Pyrotronics smoke detection system was inoperable and no redundant equipment was available to perform the required safety function, the PSS notified the NRC of this past safety system failure. This safety system failure was documented on Problem Report PR-PTS-00-04649. "A followup evaluation by engineering confirmed that there was an outside compressor housing CADP smoke detector available and operable at the time the event occurred. The evaluation also confirmed that the SAR, Table 3.2-4B, recognizes that CADP detectors provide smoke detection for outside compressor enclosures. Engineering also confirmed that CADP detectors were available and operable in all cases since March 3,1997, when any single Pyrotronics head was inoperable. "Based on the above, redundant outside compressor housing CADP smoke coverage was available at all times when the Pyrotronics heads were inoperable and this event may be retracted." The NRC resident inspector was informed. Notified R3DO(Lanksbury) and NMSS(Holonich). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37400 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-10-02 17:10 | 2000-10-02 19:00 | 2000-10-02 | DISCOVERY OF A DISCREPANCY BETWEEN A PROCEDURE, THE PLANT CONFIGURATION TO ESTABLISH PORTABLE SHIELDING, AND THE FINAL SAFETY ANALYSIS REPORT (FSAR) ANALYSIS FOR CONTROL ROOM DOSE The following text is a portion of a facsimile received from the licensee: "During a engineering review for placing a table adjacent to an exterior Control Room wall, it was noticed that the calculation for placing portable shielding in front of the Control Room window and South access door assumes the shielding [is] in place from the on set of the event. A discrepancy exists between the procedure and the plant configuration to establish the portable shielding to limit the whole body dose to Control Room operators and the FSAR analysis for Control Room dose (FSAR 14.3.5). The analysis (FSAR 14.3.5-1 of 14, last paragraph, Calculation 97-0115) assumes that the portable shielding is in place at initiation of event; however, the procedure necessary to implement the portable shielding (EOP-1, step 18) provides instructions to set up the portable shielding some time after the initiating event." "At this time, portable shielding is being installed until further engineering reviews of this calculation and its assumptions can be made." The licensee plans to notify the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37399 | 0 | SCHNABEL ENGINEERING ASSOCIATES |  |  |  |  | 2000-10-02 10:00 | 2000-10-02 17:11 | 2000-10-02 | SCHNABEL ENGINEERING ASSOCIATES REPORT OF A VEHICLE CONTAINING A LOCKED TROXLER NUCLEAR DENSITY GAUGE THAT WAS STOLEN FROM AN EMPLOYEE'S RESIDENCE IN RICHMOND, VIRGINIA Schnabel Engineering Associates reported that an employee worked over the weekend and locked a Troxler nuclear density gauge in the back of his 1988 Chevy Blazer located in the parking lot at his residence (an apartment building or townhouse complex in Richmond, Virginia). At approximately 0700 on 10/02/00, the employee discovered that his Chevy Blazer had been stolen from the parking lot at his residence. Bob Hill (the licensee's Radiation Safety Officer for the Richmond, Hampden, Charlottesville, Leesburg Office) was notified at approximately 1000 on 10/02/00, and several attempts were made to located the vehicle. The licensee notified the Police of the stolen vehicle and that a locked nuclear density gauge was in the back of the stolen vehicle. So far, there has been no record of the truck being found. The licensee also checked with local towing companies, and there is also no record of the vehicle being towed. The missing nuclear density gauge (model #3430, serial #29171) had a sealed source containing 40 mCi of Americium-241/beryllium and 8 mCi of cesium-137. The gauge also had two locks on it (one on the trigger and one on the box), and the box was locked inside the back of the enclosed vehicle. The vehicle was also locked. The licensee notified the NRC Region 2 office (Wade Loo) via telephone at approximately 1130 on 10/02/00. The licensee also reported to the NRC Operations Center that the NRC Region 2 office planned to notify the Virginia Bureau of Radiological Health and planned to issue a Preliminary Notification. The licensee also plans to submit a 30-day written report. (Call the NRC operations officer for licensee contact telephone numbers, a licensee address, the employee's name, and the employee's address.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37398 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-10-02 12:20 | 2000-10-02 14:02 | 2000-10-02 | DISCOVERY THAT A HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM STEAM ADMISSION VALVE MAY NOT CLOSE AGAINST DESIGN BASIS DIFFERENTIAL PRESSURE The following text is a portion of a facsimile received from the licensee: "Engineering review has determined that the steam admission valve (inboard primary containment isolation valve) for the HPCI system may not close against design basis differential pressure (dP). Engineering review has determined that the valve position limit switch may not indicate true stem and disc position and, therefore, under design basis dP conditions, may stop closure before hard seat contact. Evaluation of operability is continuing. A review of 1995 test data is underway which may determine that this valve is in fact operable. In the event this review determines that this valve is operable, this notification will be retracted." The licensee notified the NRC resident inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37397 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2000-10-02 13:10 | 2000-10-02 13:23 | 2000-10-02 | RECEIPT OF A PACKAGE WITH EXTERIOR RADIATION LEVELS GREATER THAT THE LIMIT A package containing radioactive tools was received onsite, and the bottom side of one of the packages had a dose rate of 550 mR/hour on contact. (The limit is 200 mR/hour on contact.) The package came from a Chem Nuclear facility on a flat bed truck, and the radioactive tools were going to be used for a spent fuel pool cleanup effort. The box in question is still located on the truck. Radiation Protection Department personnel have posted the area and roped it off as a Radiation Area in order to control access. The licensee plans to unload the box and perform an investigation to find out what is in the box and why the event happened. The licensee also plans to continue controlling access to the area until the investigation is complete. The licensee reported this event as a 1-hour report in accordance with 10 CFR 20.1906(d)(2). Radiation Protection Department personnel notified Chem Nuclear. The licensee plans to notified the NRC resident inspector and the Vermont Department of Public Service. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor |  | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  |  | 50.72(b)(2)(vi) |  |  | 0
37396 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2000-10-02 06:25 | 2000-10-02 07:42 | 2000-10-02 | REACTOR WAS MANUALLY SCRAMMED FROM <1% DUE TO INDICATIONS OF THE ELECTROMATIC RELIEF VALVE(ERV) BEING OPEN. The manual scram was inserted due to indications of main steam ERV 111 being stuck open. All rods fully inserted, no ECCS initiations, no relief valves lifted and all systems functioned as expected. They also had isolation of the main steam isolation valves due to the mode switch being in the shutdown position, condenser vacuum less than LoLoLo and reactor pressure less than 600 psig. Following the reactor scram they declared an Unusual Event (@0712) due to unidentified drywell internal leakage greater than 10 gpm (they have not yet determined the maximum leakage rate). Initial indication of this problem is the #11 main steam line ERV 111 is stuck open. The cause of the Drywell leakage is suspected to be a failure of one of the ERV line vacuum breakers to close resulting in leakage from Torus back to the Drywell. The unit also entered TS S/D LCO 3.2.5.a(1&2), Reactor Coolant System Leakage, which requires the plant to be in cold shutdown within 24 hours. They plan to depressurize and cool down the reactor using shutdown cooling to reach cold shutdown. The NRC Resident Inspector, State and Local Agencies were notified. There will be a press release issued by the licensee. * * * UPDATE 0912 10/2/00 FROM MICHAUD TAKEN BY STRANSKY * * * The Unusual Event was terminated at 0905 EDT. Total unidentified leakage is approximately 0.5 gpm. The unit is in cold shutdown, and is continuing to cool down. The NRC resident inspector has been informed of this update by the licensee. Notified R1DO (Linville), EO (Goodwin), IRO(Congel), and FEMA (Steindurf). | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION | TECH SPEC LCO A/S |  | IMode1: Startup; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37395 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-10-01 | 2000-10-01 10:40 | 2000-10-01 | NONCREDIBLE BOMB THREAT RECEIVED BY HOO. FOR DETAILS SEE HOO LOG BOOK/MISCELLANEOUS INFORMATION. NOTIFIED INDIAN POINT 2 (MONTROSS) AND INDIAN POINT 3 (MC ELROY). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 0
37394 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-09-30 23:33 | 2000-10-01 03:56 | 2000-10-30 | PLANT ENTERED LCO ACTION STATEMENT WHEN BOTH PRIMARY CONTAINMENT UNIT COOLERS WHERE DECLARED INOPERABLE. On 09/30/00 at 2333, both Primary Containment Unit Coolers were declared inoperable based on an apparent failure to fully meet required volumetric flow rates. The Tech Spec SR 3.6.1.7.2 required values are greater than or equal to 50,000 CFM. Actual calculated values were determined to be approximately 45,000 CFM for Unit cooler A and 48,000 CFM for Unit cooler B. This condition may impact the ability of these unit coolers to perform their design safety functions. This report is being made pursuant to 10 CFR 50.72 b.2.iii.D for loss of function required to mitigate an accident. Activities to restore function include evaluation of test data and methodology, cleaning of unit cooler coils, verification of calibration data, and verification of system alignment. The plant is in a 8 hour LCO to restore one of the coolers to operable status or be in mode 3 within the following 12 hours. The NRC Resident Inspector was notified. * * * UPDATE ON 10/1/00 AT 2320 BY HUSTON, RECEIVED BY WEAVER * * * Both Primary Containment Unit Coolers A and B (Divisions I and II) have been re-tested satisfactorily verifying both safety function and Tech Spec operability. The station declared both Containment Unit Cooler A and B operable and exited the LCO regarding Primary Containment Unit Coolers at 1048 hours on 10/1/00 The station is evaluating information developed to determine whether a retraction is warranted. The licensee will notify the NRC resident inspector. The Operations Center notified the R4DO (Cain). * * * RETRACTION 2005 EST 10/30/2000 FROM CHASE TAKEN BY STRANSKY * * * "On September 30, 2000 at 2333, both primary containment unit coolers A and B were declared inoperable based on an apparent failure to meet required volumetric flow rates (50,000 CFM) as stated in Technical Specification Surveillance Requirement (SR) 3.6.1.7.2. This event was reported as a loss of function in accordance with 10CFR50.72 b.2.iii.D. "During Engineering evaluations of unit cooler condition, the surveillance test methodology was noted to contain a unit cooler face area that was smaller than the area depicted in the applicable design information. In-field measurements were taken on the unit coolers. These field measurements confirmed that a larger face area value should have been incorporated into the test methodology. Effectively, RBS had imposed a more conservative face area value resulting in lowering the as calculated flow rates that are used to determine acceptability. "Recalculation of the volumetric flow using the appropriate area resulted in the required Technical Specification SR 3.6.1.7.2 flow rate of 50,000 cubic feet per minute being achieved for primary containment unit cooler B. Therefore, primary containment unit cooler B was actually operable on September 30, 2000, at 2333 and at least one operable unit cooler was always maintained. Therefore, this issue was not reportable. "The coils of primary containment unit coolers A and B were also cleaned. Subsequently, using either the previous or recalculated value for the unit cooler face area, both unit coolers re-tested satisfactorily and were restored to service." The NRC resident inspector will be informed of this retraction by the licensee. Notified R4DO (Harrell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37393 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2000-09-30 01:10 | 2000-09-30 05:14 | 2000-10-04 | HPCI DECLARED INOPERABLE AND THE UNIT ENTERED A 14 DAY LCO ACTION STATEMENT. At 0110 hours on September 30, 2000, the Unit One High Pressure Cooling Injection (HPCI) system was declared inoperable following failure to successfully complete QCOS 2300-26, HPCI CCST Suction Check Valve Closure Test. QCOS 2300-26 is an Inservice Testing surveillance used to verify closure of the HPCI pump Contaminated Condensate Storage Tank (CCST) suction check valve. The valve could not be verified to be closed by the surveillance and the system was declared inoperable, as required by the procedure. The time of the LCO entry was at 0048 hours when the system was made inoperable for performance of the surveillance. Unit One is currently in a 14 day LCO per Technical Specification 3.5.A.3. The HPCI system is currently in the normal standby line-up, available for injection if required, pending troubleshooting. The NRC Resident Inspector was notified. ***** RETRACTION RECEIVED AT 1724 EDT ON 10/04/00 FROM DAVE BOWMAN TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "This is a retraction of the ENS call made on 09/30/00 concerning the inoperabilty of the HPCI system following the failure of the HPCI Contaminated Condensate Storage Tank (CCST) suction check valve to close during a surveillance." "We have completed our evaluation and have determined that a redundant isolation valve was operable and would have isolated the CCST suction to HPCI and would not have prevented the HPCI alternate suction from the torus to provide an adequate source of water for HPCI to meet its safety function." The licensee notified the NRC resident inspector. The NRC operations officer notified the R3DO (Madera). | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37392 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-09-29 15:22 | 2000-09-29 22:46 | 2000-10-04 | SAFETY SYSTEM ACTUATION At 1522 on 09/29/00, the PSS office was notified that a secondary condensate alarm was received on the C-360 position 3 autoclave Water Inventory Control System (WICS). The WICS system is required to be operable while heating in mode 5 according to TSR 2.1.4.3. The autoclave was checked according to the alarm response procedure, removed from service and the WICS system was declared inoperable by the Plant Shift Superintendent. Troubleshooting was initiated and is continuing in order to determine the reason for the alarm. The safety system actuation is reportable to the NRC as required by Safety Analysis Report section 6.9, table 1 criterion J.2 Safety System actuation due to a valid signal as a 24-hour event notification The NRC Senior Resident has bean notified of this event. ***** RETRACTION RECEIVED AT 2155 EDT ON 10/04/00 FROM KEVIN BEASLEY TO LEIGH TROCINE ***** The following text is a portion of a facsimile received from Paducah personnel: "THIS EVENT HAS BEEN RETRACTED. Investigation and troubleshooting by the System Engineer revealed that the gain adjustment on one of the WICS channels had drifted out of tolerance. Historical discussions with the component manufacturer had concluded that the WICS alarm cards are susceptible to drift, due to age and fluctuations in temperature. These cards are exposed to ambient temperatures, but the cards are rated for the range of temperatures at the autoclaves. Given this and other indications that the WICS actuation signals were invalid, i.e., not the result of water backing up in the drain, it has been concluded that the subject actuations were caused by invalid signals (instrument drift) and thus, [do] not meet the criteria for reporting." Paducah personnel notified the NRC resident inspector. The NRC operations officer notified the R3DO (Madera) and NMSS EO (Hodges). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37391 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2000-09-29 13:20 | 2000-09-29 17:40 | 2000-10-24 | HIGH PRESSURE CORE SPRAY DIESEL GENERATOR INOPERABLE At 1320 hours on 9/29/00, the seismic bolts of the Division 3 Diesel Generator (DG) control panel door were discovered missing. At 1450, Engineering determined that the seismic qualification of the control panel was in question with these bolts missing. On 9/27/00, during the day shift, the Division 3 DG was tested per Clinton Power Station (CPS) procedure 9080.02, DIESEL GENERATOR 1C OPERABILITY - MANUAL AND QUICK START OPERABILITY. This procedure requires instrumentation to be connected within the local control panel (1E22-S001B). The bolts to this panel were discovered missing today at 1320. It is possible that they had been missing since the performance of CPS 9080.02 but is unknown at this time. The Division 3 DG is not analyzed for these missing bolts and is considered inoperable while in this condition. This event is being reported pursuant to 10CFR50.72 (b)(2)(iii)(D) as a condition that alone could have prevented the fulfillment of the High Pressure Core Spray (HPCS) system, a single-train safety system needed to mitigate the consequences of an accident, since the Division 3 DG is an essential support system for the HPCS system needed to mitigate a small break LOCA concurrent with a Loss of offsite power. The bolts were restored at 1442 today and the Division 3 DG is operable. The licensee notified the NRC resident inspector. * * * UPDATE ON 10/24/00 @ 1826 BY SCHOTTEL TO GOULD * * * RETRACTION Further evaluation of this condition by engineering concluded that the absence of the bolts was seismically acceptable. A calculation determined that the estimated impact acceleration resulting from the unsecured door impacting the panel is 0.06g. Because this acceleration is small in relation to the seismic test margin documented in the original seismic calculation of the panel, the unsecured door would not have prevented the control panel from performing its safety function during seismic events. On this basis, the Division 3 DG and HPCS safety functions were not adversely affected by the absence of the bolts. Therefore, this issue Is not reportable under the provisions of 10CFR50.72 or 10CFR50.73 and this event notification is retracted. The NRC Resident Inspector was notified. The Reg 3 RDO(Vegel) was informed. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37390 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-09-29 13:57 | 2000-09-29 14:54 | 2000-09-29 | MANUAL REACTOR SCRAM FROM 55% POWER At 1357 on 09/29/00, while performing planned refueling outage shutdown activities, a manual scram (RPS actuation) was actuated in response to decreasing reactor water level due to both reactor feed pump turbines (RFPT) being tripped. RFPT 'B' had been secured as per planned activities; RFPT 'A' tripped on low suction pressure (cause unknown at this time). At the time of the manual scram, reactor water level was 22" and decreasing. HPCI and RCIC both automatically actuated to recover reactor water level. The lowest observed reactor water level was - 48". PCIV Groups 2 and 5, and Secondary Containment isolated as expected. SBGT actuated as expected. Investigation is continuing. Recirculation pumps continued to run and decay heat is being removed by steaming to the main condenser. The 'A' reactor feed pump has been started. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 55 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37389 | 0 | NC DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-09-29 | 2000-09-29 09:40 | 2000-09-29 | AGREEMENT STATE REPORT An employee of the Union Regional Medical Center received an overexposure based upon the results of dosimetery readings for the May-June 2000 monitoring period. The individual's whole body TLD indicated the following doses: 7762 mrem deep, 8168 mrem eye lens, and 8577 mrem shallow. In addition, the individual's ring TLD indicated a dose of 11460 mrem. The State of North Carolina is currently investigating this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0
37388 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2000-09-28 17:30 | 2000-09-28 19:26 | 2000-09-28 | POTENTIAL LOSS OF RHR AND ACCIDENT MITIGATION CAPABILITY ON 09/28/00 AT 04:30 HRS. SURVEILLANCE TESTING SHOWED THAT A CHECK VALVE FAILED TO ISOLATE FLOW BETWEEN THE EMERGENCY SERVICE WATER (ESW) SYSTEM AND THE NON-SAFETY RELATED UNIT 2 SERVICE WATER (SW) SYSTEM. FAILURE TO PREVENT FLOW FROM THE EMERGENCY SERVICE WATER SYSTEM TO THE SERVICE WATER SYSTEM COULD RENDER BOTH ESW SUBSYSTEMS INOPERABLE. AT 05:58 ON 09/28/00, A MANUALLY OPERATED BLOCK VALVE WAS CLOSED BETWEEN THE SYSTEMS TO MAINTAIN INTEGRITY OF THE ESW SUBSYSTEMS. THIS ACTION ENSURES THAT BOTH ESW SUBSYSTEMS ARE MAINTAINED OPERABLE. FURTHER EVALUATION AND TESTING WAS PERFORMED AND AT 17:30 HRS. ON 09/28/00, THE CONCLUSION WAS REACHED THAT THIS CONDITION COULD ALONE HAVE PREVENTED THE FULFILLMENT OF THE ESW SYSTEM SAFETY FUNCTION. The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(D) |  |  | 0
37387 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2000-09-28 18:35 | 2000-09-28 18:43 | 2000-09-28 | OUTSIDE DESIGN BASIS - PUMP POWER SUPPLY DOES NOT MEET SAFE SHUTDOWN REQUIREMENTS On September 28, 2000 at approximately 1835, it was determined that the power cable routing for the 'B' charging pump is not in accordance with the assumptions in the Millstone Unit 3 Fire Safe Shutdown Analysis. This condition could have resulted in the inability to maintain RCP seal cooling in the event of a design basis fire. This condition is historical in nature. In accordance with the Millstone Unit 3 Technical Requirements Manual, a fire watch has been established in the affected area as a compensatory measure until a corrective action plan can be developed and implemented. All other fire protection features in the affected areas are operable. The cable is supposed to be run inside of a fire curtain, but instead was run outside of this curtain. The licensee notified the NRC resident inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37386 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-28 01:21 | 2000-09-28 01:23 | 2000-10-01 | ELECTRICAL BUS OUTAGE WILL AFFECT TSC VENTILATION SYSTEM "This event notification is for planned maintenance on Cook Unit 1's electrical buses that remove power from a portion of the TSC ventilation system. Contingencies are established to restore power to the TSC ventilation fan (if needed) to support Emergency Plan execution. The fan that will be unavailable boosts airflow through the TSC ventilation charcoal clean-up filter subsystem. Ventilation flow will still pass through this filter without the booster fan, but TSC pressure will not be boosted to limit infiltration. Use of this fan is dependent on radiological conditions, if radiological conditions warrant its use, and it is not available, the TSC will relocate to the Unit 2 Control Room in accordance with plant procedures. Reporting this event is consistent with NUREG-1022, Rev 1 criteria for reporting loss of ERFs. "No adverse consequences are expected from this outage. The TSC ventilation booster fan is expected to be unavailable for 48 hours, starting at 0121 hours on 9-28-2000. Contingencies have been planned to restore power to the booster fan in 8 to 10 hours if needed. Follow-up notification will be made when the TSC is again fully available. The NRC Senior Site Resident Inspector has been informed of this planned evolution." * * * UPDATE ON 10/01/00 @ 0948 BY COBB TO GOULD * * * The onsite TSC emergency response facility has been restored as of 0515 and it is fully available for use. The NRC Resident Inspector was notified. The Reg 3 RDO(Clayton) has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37385 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-09-27 18:45 | 2000-09-27 21:04 | 2000-09-27 | INCORRECT TAP SETTING DISCOVERED During the Division II UV Test, it was discovered the tap setting on the overvoltage coil on the undervoltage relay (127-2-B-34) on Bus 34 was incorrectly set at 0.2 amps versus 2 amps. The failure of this relay causes a failure to re-energize Bus 34 from Bus 34-1 after a Loss of Off-Site Power (LOOP) occurs requiring the Unit 3 Emergency Diesel Generator (EDG) to supply power to the bus. The failure to re-energize Bus 34 prevents starting the 3C & 3D Containment Cooling Water Pumps. Based on the events discovered during D3R16 Division II UV Test, it is suspected the ability of this relay to perform its design function has been lost since 02/12/99 during D3R15. Surveillance testing during the fuel cycle would not have identified this deficiency due to paralleling the Unit 3 EDG with off-site power. In this configuration the relay in question is not challenged. With the failure of this relay and a Design Basis Accident ,Loss Of Off-Site Power with a Loss of Coolant Accident (LOOP/LOCA) and a single active failure of the 2/3 EDG (or Div I CCSW Loop Inoperable) a loss of containment cooling function would occur. Work Package Instruction used on 02/12/99 to set the tap setting specified 0.2 amps instead of the correct value of 2 amps. All other Unit 3 Buses have the correct tap setting for the overvoltage coil on the undervoltage relay. Investigation into root cause is in progress. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37384 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2000-09-27 01:23 | 2000-09-27 03:15 | 2000-09-27 | AUTOMATIC REACTOR SCRAM SIGNAL WITH ALL CONTROL RODS ALREADY INSERTED "While in Cold Shutdown conditions, Nine Mile Point Unit 1 experienced a Reactor Scram initiated by Low water level. All rods were fully inserted at the time of the initiation and all required safety functions operated as required. The cause of the low water level condition was due to a level transient experienced while placing the Reactor Water Cleanup System in service. The lowest indicated water level was 133 inches above top of active fuel. Emergency Operating Procedures and Special Operating Procedures were implemented and reactor water level was returned to the normal cold shutdown level of 149 inches above top of active fuel. There were no adverse effects on Reactor Plant Systems." The NRC resident inspector will be informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37383 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-09-26 17:30 | 2000-09-26 20:40 | 2000-10-01 | 4-HOUR NRC BULLETIN 91-01 REPORT INVOLVING THE X-705, DECON FACILITY, COMPLEXING HANDTABLE DUCTWORK At 1730 during a review of Nuclear Criticality Safety Approval (NCSA) Corrective Action Plan (CAP) with NCS it was noted that the X-705 Complexing Handtable was not covered by an active NCSA. NCSA 705_014A00 had been cancelled and the PORC approved 705_014A01 was not activated. Based on security sweep data completed by Applied Nuclear Technology (ANT) personnel it can be conservatively estimated that greater than 15 grams of U-235 exist in the duct work associated with the handtable. TSR 3.11.2 Requires a NCSA when operations involve uranium enriched to 1.0% or higher U-235 and 15 grams or more U-235. The complexing handtable has not been in operation since NRC transition on 03/03/97 and remains out of service. Upon notification of this issue the Plant Staff Superintendent office directed the facility management to enter an anomalous condition. This is reportable under UE2-RA-RE1030 (Event Report Criteria) 3.C.1 as a 4 hour NRC Bulletin 91-01 event. SAFETY SIGNIFICANCE OF EVENT: The safety significance of this event is very low. No operation had taken place on the complexing handtable since transition on 03/03/97. The small amount of hold up may be greater than 15 grams of U-235, however, the available data for the remainder of the handtable operation shows reading at or near background levels. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO OF HOW CRITICALITY , ETC.): Since the handtable and associated piping are favorable geometry for any enrichment, material would have to accumulate in the ductwork or pile up to achieve a critical configuration. The operation is not currently being performed and the ductwork is not connected to any system, therefore, a criticality does not appear credible. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameter is geometry. The approved, but not implemented NCSA establishes two controls based on geometry. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The amount of U-235 is not more than 25 grams. Enrichment is not known, but could be as high as 100%. The form of material is either uranyl fluoride or uranyl nitrate. NUCLEAR CRITICALITY SAFETY CONTROL OR CONTROL SYSTEMS AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The only deficiency is that the ductwork for the handtable potentially contains more than 15 grams U-235 without an active NCSA to establish the necessary controls to ensure double contingency. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Anomalous condition remains in effect until evaluations and testing are completed. The NRC Resident Inspector was notified of this event by the certificate holder. * * * UPDATE ON 10/01/00 @ 1010 BY SPAETH TO GOULD * * * Non-Destructive Assay (NDA) analysis completed on 9/28/00 indicates less than 15 grams of U-235 are present in the X-705 complexing handtable and associated ductwork. The total U-235 identified in the and associated ductwork is less than 6 grams including measurement uncertainties. An NCSA is, therefore, not required for this equipment per TSR 3.11.2. The NRC Resident Inspector was notified. The DOE Representative will be notified. The Reg 3 RDO(Clayton) and NMSS(Hickey) were notified. HOO Note: Portsmouth does not retract 91-01 Bulletins reports. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37382 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-09-26 16:20 | 2000-09-26 18:45 | 2000-09-26 | EXCESS FLOW CHECK VALVE FOR "A" RECIRCULATION PUMP # 2 SEAL PRESSURE SIGNAL FAILED TO SEAT OFF WHEN TESTED. Excess flow check valve 1B31F003A failed to check (seat off) when tested per S7SV-SUV-004-1S. This excess flow check valve provides isolation for the "A" Recirculation Pump # 2 seal pressure signal. The excess flow check valve will be isolated per Technical Specification 3.6.1.3.C (Primary Containment Isolation Valve). Technical Specification 3.6.1.3.C states that ,if the valve cannot be isolated, the plant must be in Mode 3 (Hot Shutdown) within 12 hours. The licensee stated that the valve will be isolated before the TS time limit runs out. The NRC Resident Inspector will be notified by the licensee of this event. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37381 | 0 | PHILLIP MORRIS, USA |  |  |  |  | 2000-09-25 17:00 | 2000-09-26 18:28 | 2000-09-26 | ACCURAY MICRO 10 GAUGE LEAD FUSIBLE LINK MELTED AND CAUSED THE SHUTTER OF THE GAUGE TO REMAIN OPEN. 24 HOUR NOTIFICATION An Accuray Micro 10 gauge, containing a 25 millicurie Sr-90 sealed source, fusible lead link melted, preventing the gauge shutter from closing. A warning light associated with Accuray Micro 10 gauge warned plant personnel that the shutter to the gauge was still open. Nobody was exposed. The Accuray Micro 10 gauge registration number is NR-109-D-125-B. The shutter of the gauge was closed, placed in a lead pig and stored in a lead safe. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 30.50(b)(2)(ii) |  |  |  | 0
37380 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-09-26 06:00 | 2000-09-26 18:10 | 2000-09-26 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM THE BACK OF A PICKUP TRUCK. An employee of Law Engineering Environmental Service of Kentucky had reciprocity with the state of Nevada. After the employee had completed his work in Las Vegas, NV he decided to take the long way home. He spent the night at the Holiday Inn in downtown Sacramento, CA. In the morning the person discovered that the chain had been cut to the Troxler Moisture Density gauge, Model #3411-B S/N 12599. The Sacramento Police Department was notified of the theft of the gauge. An ad will be placed in the Sacramento Bee newspaper with a $1,000 reward for the return of the gauge. The Radiation Safety Officer for Law Engineering Environmental Service was notified of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37379 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-09-26 13:00 | 2000-09-26 16:35 | 2000-09-26 | OFFSITE NOTIFICATION MADE TO THE CALIFORNIA DEPARTMENT OF ENVIRONMENTAL HEALTH AND THE OFFICE OF EMERGENCY SERVICES FOR A SODIUM HYPOCHLORIDE TANK LEAK. On September 26, 2000, at about 0816 PDT, control room personnel were notified of a small leak from Unit 2 sodium hypochloride tank. The leak was in the tank discharge line upstream of the outlet isolation valve. At about 1020 PDT, site personnel completed installation of a soft patch to terminate the leak (SCE is planning to implement a more permanent repair after the tank contents have been offloaded). All of the estimated 300 gallons that leaked from the tank was contained within a tank sump and was not released to the environment. The NRC Resident Inspector has been informed of this event by the licensee. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37378 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-09-26 00:43 | 2000-09-26 01:23 | 2000-09-26 | UNIT 1 MET THE CONDITIONS FOR AN UNUSUAL EVENT BASED ON RCS LEAKAGE > 25 GPM WHILE IN MODE 4. "While placing the '1A' RHR Pump in service for shutdown cooling, the Unit experienced an RCS leak of approximately 45 gpm. It is believed that the cause of the leak is a relief valve that lifted and failed to reseat. The leak was isolated from the RCS when the RHR suction valves from the RCS (1-FCV-74-1 and 1-FCV-74-2) were closed. The leak lasted approximately 10 minutes. "According to the Plant's Radiological Emergency Plan, the conditions for a Notification of Unusual Event (NOUE) were met, but before it could be declared the leak was isolated, so an NOUE was not declared but will be reported." The RCS which leak occurred at 0002EDT was terminated at 0012EDT (10 minutes). Operators estimated the leakage at 45 gpm based on the change in PRT (pressurizer relief tank) level. The two relief valves involved are 1-VLV-63-626 and 1-VLV-63-627 with setpoints of approximately 600 psig. RCS pressure was 345 psig when the RHR suction valves were opened. The RHR pumps develop approximately 180 psig which combined with the 345 psig RCS pressure (inlet) indicated about 525 psig RHR discharge pressure in the control room. Both trains of RHR have been declared inoperable pending identification and correction of the problem. Decay heat is current being removed by the main condenser through the steam dumps using both motor-driven auxiliary feedwater pumps. The licensee has no plans for a press release at this time and did inform the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37377 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-09-25 14:00 | 2000-09-25 14:30 | 2000-09-25 | Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. Refer to the HOO Log for additional details. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 0
37376 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-09-25 08:15 | 2000-09-25 12:47 | 2000-09-25 | LICENSEE TECHNICAL REQUIREMENT 24 HOUR REPORT The licensee, in accordance with their Technical Review (Requirement) Manual 15.7.5.c, reported that one of their diesel fire pumps and one pretreatment water storage tank (# 12) was removed from service for planned maintenance. The diesel fire pump was taken out of service to install a flange to isolate the pretreatment water storage tank for maintenance. The pump being out-of-service and having one of two sources of water out-of-service prompted the 24 hour report. The NRC Resident Inspector was notified of this event by the licensee. See similar Event # 37367 reported on 09/22/00. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW | [5 empty] | 0
37375 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-09-25 10:33 | 2000-09-25 11:18 | 2000-09-25 | REACTOR TRIP FROM 78% POWER DUE TO A LOW STEAM GENERATOR LEVEL The event was initiated at 1030 EDT when the "1A" main feedwater pump tripped. An automatic runback [from 100%] to 75% turbine power occurred, however, the "1B" main feedwater pump did not automatically speedup to full load as designed. An attempt to manually load the "1B" main feedwater pump was ineffective and a trip occurred as a result of a low steam generator level. All rods fully inserted, no ECCS initiated and no safety valves lifted. They are investigating the cause of this event. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37374 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-09-25 07:30 | 2000-09-25 09:14 | 2000-09-25 | TEXAS DEPARTMENT OF HEALTH WAS NOTIFIED BY ONE OF THEIR LICENSEES OF A STOLEN TROXLER GAUGE IN BROWNSVILLE, TEXAS A Troxler Model 3430, Serial No. 31532, sources: 8 millicurie Cs-137, Serial No. 750-6340; and 40 millicurie Am-241 /Be, Serial No. 47-28154 was apparently stolen from the back of a company truck at an overnight lodging in Brownsville Texas. The operator/driver discovered the theft between 7:30 a.m. and 8:00 a.m. this morning. The security chains in the bed of the truck had been cut. The gauge and the operators tool box were stolen. A police report has been filed with the Brownsville Police Department. The gauge was to be used at a temporary jobsite today. The owner of the stolen gauge is a Texas Licensee, L04964-001. The licensee is considering offering a reward for return of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37373 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2000-09-23 16:15 | 2000-09-23 17:29 | 2000-09-23 | TECHNICAL SUPPORT CENTER LOST POWER UNEXPECTEDLY DURING MAINTENANCE It was determined at 1615 EDT on 9/23/00 that the unexpected loss of power to the Technical Support Center (TSC) during a planned maintenance procedure on 9/18/00 at 2000 EDT constituted a reportable event as a major loss of assessment capability. Power was restored at 2107 on 9/18/00 and all functions restored. It has been determined that the loss of power should have been expected as part of the maintenance and a review of the event is ongoing. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37372 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-09-23 01:20 | 2000-09-23 05:09 | 2000-09-23 | OFFSITE NOTIFICATION TO STATE OF NEW JERSEY INVOLVING RELEASE OF SECONDARY CONDENSATE CONTAINING HYDRAZINE TO THE DELAWARE RIVER "During a planned downpower, a flange leak developed on the 15C feedwater heater condensate line. The leakage rate was approximately 100 gpm. This resulted in water containing hydrazine entering a storm drain which leads to the Delaware River. A 15 minute notification was made to the State of New Jersey at 0135. Sample results indicated 30 ppb hydrazine with the limit being 10 ppb. The 15C feedwater heater is being isolated and cooled down with leakage at approximately 25 gpm. The plant is stable with power at 18% and the turbine offline in accordance with the scheduled downpower. [The] 15 SW pump is INOPERABLE but available due to planned maintenance. [The] 13 Charging Pump is INOPERABLE due to a preexisting condition." The licensee estimates that 8-12 hours will be required to cooldown and isolate the affected feedwater heater condensate line. Meanwhile, efforts are underway to contain the leakage for reprocessing. There were no injuries associated with the 250 degree condensate leakage. The licensee informed the state of New Jersey, the Lower Alloways Creek Township and will inform the NRC resident inspector. | 18 | 0 | 0 | 40 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37371 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-09-23 00:37 | 2000-09-23 03:02 | 2000-09-23 | AUTOMATIC FEEDWATER ISOLATION DURING PLANT SHUTDOWN "Beaver Valley Unit 2 experienced an Automatic Feedwater Isolation on high steam generator water level from the 21 B steam generator. The main turbine valves were closed and the unit was off line. This occurred during plant shutdown for refueling at 00:37. Unit 2 was at 7% reactor power at the time of the feedwater isolation. The steam generators were being fed using normal feedwater through the bypass feedwater regulating valves. Steam removal was via the condenser steam dump system. The feedwater isolation occurred shortly after the planned main turbine overspeed trip test was completed. The feedwater isolation resulted in the closure of feed water isolation valves 2FWS-HYV157A, B, and C and the trip of the running main feedwater pump 2FWS-P21A. The motor driven auxiliary feedwater pumps started as designed upon the trip of the running main feedwater pump. All ESF equipment was verified to respond as expected. New positioners were installed on the bypass feedwater regulating valves prior to the Unit 2 shutdown for refueling and may have changed the control response. "Plant shutdown continued and at 00:39 Unit 2 entered Mode 2. After the steam generator water level returned to below the ESF setpoint, normal feedwater flow was re-established via 2FWS-P21A and the bypass feedwater regulating valves at 00:42. Heat removal was maintained at all times via the condenser steam dump removal system. The auxiliary feedwater pumps were manually secured at 00:46. Unit 2 entered Mode 3 at 01:12 and preparations are being made for cooldown to Mode 5. A root cause analysis is being performed to investigate the ESF actuation." The licensee informed the NRC resident inspector. | 0 | 7 | 0 | 0 | 7 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37370 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-09-22 19:15 | 2000-09-22 20:04 | 2000-09-22 | TESTING FOUND 20 OF 165 OFFSITE EMERGENCY SIRENS DETERMINED TO BE INOPERABLE "On September 22, 2000 at 19:15, it was determined that 20 of Limerick Generating Station's 165 Emergency Offsite Sirens were inoperable. The exact cause of the inoperable sirens is not known at this time, but the ability of the licensee and counties to detect the inoperable sirens has been compromised. A plan is being developed to repair the degraded sirens, and appropriate interim compensatory measures are being implemented to compensate for the degraded condition." This was the result of routine testing, there was no cluster of inoperable sirens, the inoperable sirens reported appeared operable from remote testing at the county, and an investigation will continue. These sirens have been maintained by the same contractor as mentioned in NRC report #37361 of 9/21/00. The licensee has notified the NRC Resident Inspector and contacted the local authorities as part of the interim compensatory measures. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37369 | 0 | SIBLEY MEMORIAL HOSPITAL |  |  |  |  | 2000-09-22 13:00 | 2000-09-22 16:15 | 2000-09-22 | 2 PATIENTS RECEIVED MEDICAL MISADMINISTRATION DUE TO CALCULATION ERROR The hospital discovered today that a mistake was made in ordering sources for medical procedures, a change had been made to order sources in 'air kerma strength' instead of millicuries (mCi). The conversion is suppose to be mCi divided by 1.2 instead they multiplied by 1.2. Two patients received I-125 plaques to the eye for melanoma and were suppose to receive 7000 rads, instead received 10,866 and 11,470 rads. There is not expected to be any consequences beyond what was expected with the prescribed dose. The procedure was a try at preserving the eye as it would have been removed otherwise. The prescribing physician has been contacted and the patient will be counseled. The hospital has determined that no other sources were ordered with the wrong calculation and is taking steps to insure this mistake is not repeated. The hospital has contacted NRC Region 1 (Teresa Darden). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.33 |  |  |  | 0
37368 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-09-22 06:00 | 2000-09-22 13:07 | 2000-09-22 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM THE BACK OF A PICKUP TRUCK AGREEMENT STATE REPORT A Troxler Moisture Density gauge, Model # 3411-B (serial (12622) was stolen from the back of a pickup truck in Concord, California this morning around 0600 PT. The gauge was locked in the back of the licensee's pickup truck with a hasp lock going through the handle of the Troxler gauge case. The hasp lock cable was cut with a chain cutter. The person driving the pickup truck drove the truck home and was away from the truck approximately 15 minutes. The Concord police department was notified of the theft. Troxler Model # 3411-B: 9 mCi of Cs-137 and 44 mCi of Americium-241. State of California report number is 092200. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37367 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-09-22 09:40 | 2000-09-22 12:17 | 2000-09-22 | LICENSEE TECHNICAL REQUIREMENTS 24 HOUR REPORT The licensee, in accordance with their technical requirements, reported that the diesel fire pump was removed from service for approximately 2 hours. The pump was removed from service as part of ongoing maintenance of the pretreatment water storage tank. The pump being out-of-service and having one of two sources of water out-of-service prompted the 24 hour report. The pump has been restored to service. The licensee informed the NRC Resident Inspector. See similar event #37376 reported on 09/25/00. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW | [5 empty] | 0
37366 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-09-22 11:10 | 2000-09-22 11:49 | 2000-09-22 | SEVERAL PIECES OF SCAFFOLDING KNUCKLES AND ELBOWS RECEIVED FROM VENDOR FOUND TO HAVE LOW LEVELS OF RADIOACTIVITY. OFFSITE NOTIFICATION MADE TO THE STATE OF FLORIDA While performing routine surveys, Turkey Point Health Physics personnel discovered low levels of radioactivity on several pieces of scaffolding knuckles and elbows received from a vendor. The knuckles never entered the site's radiation controlled area. These items were counted in a Small Articles Monitor (SAM) and indicated low level contamination was present. In total 3 out of approximately 700 item's surveyed indicted the presence of low level fixed activity. The highest level measured was 15,000 disintegration's per minute (dpm) using a standard HP-210 (pancake GM) probe. Isotope analysis indicated Cobalt-60 and Cesium-137. No loose surface contamination was found. The items identified with low level fixed contamination are now being held inside the Turkey Point radiation controlled area. The state of Florida was notified of this event. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 88 | 0 | 100 | 88 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37365 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-09-22 03:40 | 2000-09-22 06:37 | 2000-09-22 | PLANT HAD ESF ACTUATIONS DURING A REACTOR SCRAM A main turbine trip resulted in a reactor scram. As expected following the scram, reactor water level dropped to the actuation setpoint for Groups 2, 6 and 8 isolations. The main turbine trip apparently resulted from a fire in B main power transformer. The fire was reported to the control room at 0346. The site fire brigade responded and the fire was extinguished at 0402 using the automatic deluge system and fire hoses. Offsite fire department assistance was requested but was not needed to extinguish the fire. An Unusual Event was declared at 0400 in accordance with the plant's emergency procedures. The Unusual Event was terminated at 0512 based on the plant being in a stable condition. During the transient the startup level control did not control level in the automatic mode. Reactor level was controlled using a feedwater bypass valve. A second reactor scram signal was generated due a low reactor water level signal received while manual level control was being established, however all rods were already fully inserted. The plant emergency diesels started but did not load. Offsite power remained available throughout the event. The NRC Resident Inspector was notified. HOO Note: see event # 37364 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37364 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-09-22 04:00 | 2000-09-22 04:26 | 2000-09-22 | FIRE IN THE PROTECTED AREA LASTING GREATER THAN 10 MINUTES RESULTING IN A REACTOR SCRAM. AN UNUSUAL EVENT WAS DECLARED @ 0400 DUE TO A FIRE IN THE MAIN TRANSFORMER THAT LASTED >10 MINUTES. OFF SITE FIRE DEPARTMENT WAS CALLED IN TO RESPOND AND THE FIRE WAS EXTINGUISHED WITHIN 14 MINUTES, HOWEVER THE PLANT STILL REMAINS IN THE UNUSUAL EVENT. A REACTOR SCRAM FROM 100% POWER OCCURRED FOLLOWING A MAIN TURBINE GENERATOR LOCKOUT WHICH RESULTED FROM THE TRANSFORMER FAILURE. THERE WERE SOME ERRONEOUS INDICATIONS OF CONTROL ROD POSITION, BUT ALL RODS APPEAR TO BE FULLY INSERTED. THERE WAS NO ECCS ACTUATION AND NO SAFETY RELIEF VALVES LIFTED DURING THIS EVENT. THE PLANT DID NOT LOSE OFFSITE POWER DUE TO THE AUTO TRANSFER FROM THE MAIN TRANSFORMER TO THE STARTUP AUXILIARY TRANSFORMER. THE DIESELS AUTOMATICALLY STARTED AND WERE STILL RUNNING AT THE TIME OF THIS REPORT. GROUP 2,6 AND 8 ISOLATIONS WERE ALSO RECEIVED. THERE WAS A PROBLEM WITH THE STARTUP LEVEL CONTROL VALVE WHEN THEY REESTABLISHED REACTOR FEED PUMP, VALVE DID NOT OPEN PROPERLY SO THEY HAD TO USE THE BACKUP PATH IN THE FEED SYSTEM. AS A RESULT OF THIS THE LEVEL WENT LOW ENOUGH TO RECEIVE A SECOND REACTOR SCRAM SIGNAL. THE CONDENSER IS BEING USED AS THE HEAT SINK AND THE PLANT IS STABLE. THE CAUSES FOR THE TRANSFORMER FIRE AND THE ERRONEOUS CONTROL ROD INDICATIONS ARE BEING INVESTIGATED. THERE HAVE BEEN NO INJURIES REPORTED AND IT IS NOT KNOWN AT THIS TIME IF A PRESS RELEASE WILL BE ISSUED. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. * * * UPDATE ON 9/22/00 @ 0528 BY HAMM TO GOULD * * * THE NOUE WAS TERMINATED AT 0512 DUE TO THE FIRE BEING COMPLETELY EXTINGUISHED. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED. THE EO(BATEMAN), RDO(DECKER), FEMA (HEYMAN) AND IRO(GIITTER) WERE NOTIFIED. SEE EVENT # 37365. * * * UPDATE AT 1313 EDT ON 9/22/00 BY KEN CHISM TO FANGIE JONES * * * The licensee, after further review, has determined that the fire was extinguished in 16 minutes versus the 14 minutes originally reported. The licensee has issued a press release concerning the declaration of Unusual Event. The licensee intends to notify the NRC Resident Inspector. The R2DO (Thomas Decker), NRR (Ed Goodwin), IRO (Joseph Giitter) have been notified. * * * UPDATE AT 1653 EDT ON 9/22/00 BY KEITH REQUARD TO FANGIE JONES * * * The licensee notified the State of North Carolina due to an oil spill resulting from the event. On September 22, 2000, at approximately 1350 hours, a notification was made to Mr. Jim Bushard, of the North Carolina Division of Water Quality, Wilmington Regional Office. The incident began when a transformer overheated. The overheated transformer developed a leak at an oil flange, and caught fire. The transformer deluge system activated and, as a result, a mixture of water and transformer oil escaped the concrete containment structure surrounding the transformer. It is estimated that greater than 25 gallons and less than 100 gallons of transformer oil is outside of the containment structure. The oil is contained onsite and poses no environmental hazard. The oil is a mineral oil and contains no PCBs. Clark Environmental Services Inc. is performing the cleanup. The licensee notified the NRC Resident. The R2DO (Thomas Decker), IRO (Joseph Giitter), and NRR EO (Bill Bateman) have been notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | OFFSITE NOTIFICATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(vi) |  |  | 0
37363 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-09-19 07:30 | 2000-09-21 19:09 | 2000-09-21 | OFFSITE NOTIFICATION DUE TO A SULFURIC ACID LEAK CONTAINED ON SITE "This 4-hour telephone notification is being provided in accordance with 10CFR50.72(b)(2)(vi) for notification of other government agencies. For the event below, on September 19, 2000, at 0920 PDT, SCE notified the Department of Environmental Health and the Office of Emergency Services (OES Incident number 00-4232). This notification was delayed due to an internal miscommunication. "On September 19, 2000, at about 0730 PDT, control room personnel were notified of a sulfuric acid leak from the High Flow Makeup Demineralizer Bulk Acid Storage Tank. The leak was from a gasket located between level transmitter 2/3LT5045 and isolation valve AST-38. The isolation valve was closed and the leak stopped. All acid (estimated to be about 650 gallons) was contained within the tank's bermed area and then routed to the waste neutralization sump. The entire sump contents (about 2,500 gallons of sulfuric acid and water) were removed for disposal off-site. This occurrence was not a significant impact to the environment and did not hamper site personnel in the performance of their duties necessary for safe operation. "At the time of this occurrence, both Units 2 and 3 were operating at about 100 percent power; Unit 1 remains permanently defueled. SCE will notify the NRC resident inspectors about this notification and will provide them with a copy of this report." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37362 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-09-21 11:38 | 2000-09-21 16:15 | 2001-01-18 | POSSIBILITY THAT BOTH DIVISION 1 AND 2 DIESEL GENERATORS WERE INOPERABLE FOR 9 HOURS "This condition deals with a past Reportability issue. During a condition report review for Functional Failure/Maintenance Preventable Functional Failure determination (FF/MPFF), River Bend has determined that both Standby Diesel Generators may have been inoperable at the same time. "A failure in a light socket related to the Division I Diesel Generator created a functional failure in that during a seismic event, the breaker logic for the Division I diesel generator output breaker could have been affected in such a way that the breaker would not close. The failed light socket was identified and corrected on 9/5/00 as part of work to replace the light bulb. Since the MAI on the light bulb failure was written on 8/22/00, it is assumed that the socket failure occurred at that time. "During the same time period, a lube oil leak developed on the Division II oil supply which has been determined to be a functional failure. The damaged oil line was replaced on 8/30/00. "Therefore, based on the functional failure determinations, there is an overlapping period of approximately 9 hours that the Division I and II diesel generators may not have been capable of performing their design bases function. "This report is being made based on the information available at this time. River Bend will continue to evaluate the condition associated with the potential Division I inoperability and will assess the reportability of this condition further based on the results of that evaluation." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1317 ON 1/18/2001 BY WYMORE, RECEIVED BY WEAVER * * * The original conclusion assumed that the two light socket wires in the Division I panel which were dislodged but still energized would come into contact during a seismic event and potentially blow a fuse in the safety bus breaker control circuit. A detailed mockup was tested to the RBS seismic response curves. The wires never contacted each other and there was no short circuit. A seismic event would not have caused a breaker control failure as had been assumed. The results of the seismic test indicates that the Division I diesel generator was fully capable of responding to an automatic start signal despite the damaged light base and loose wiring. Based on the observed condition and the seismic test data obtained, a determination was made that there was no concurrent time of inoperability for Division I and Division II diesel generators. Division I diesel generator was out-of-service for approximately 4 hours on September 5, 2000, to replace the light socket and some adjacent wiring. Division II diesel generator was out-of-service on August 30, 2000, to repair the lube oil pipe. Based on this information, the condition is not reportable and the 50.72 report is retracted. The licensee notified the NRC resident inspector. The HOO notified the R4DO (Kennedy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(A) | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(C) | 50.72(b)(2)(iii)(D) | 0
37361 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2000-09-21 15:30 | 2000-09-21 16:07 | 2000-09-23 | OFFSITE EMERGENCY SIRENS IN DEGRADED CONDITION "On September 21, 2000 at 1530, it was identified that at least 17 of Peach Bottom's 97 Emergency Offsite Sirens were in a degraded condition. The exact cause of the degraded sirens is not known at this time, but the ability of the licensee to detect the degraded sirens has been compromised due to poor maintenance practices. A plan is being developed and implemented to repair the degraded sirens and appropriate interim compensatory measures are being put in place to compensate for the degraded condition." An investigation is underway into this matter. The contractor responsible for the siren maintenance has no other responsibilities on site. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 2253 EDT ON 9/23/00 BY JIM VASH TO FANGIE JONES * * * The licensee reported that 15 of the 17 sirens that were in degraded conditions have been restored to service. The remaining 2 sirens are expected to be restored to service early next weeks. The licensee intends to notify the NRC Resident Inspector. The R1DO (Richard Barkley) has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37360 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2000-09-20 14:30 | 2000-09-21 09:48 | 2000-09-22 | LOST TROXLER MOISTURE DENSITY GAUGE REPORTED TO THE MARYLAND DEPARTMENT OF THE ENVIRONMENT (MDE) Maryland licensee, D W Kozera Inc. of Baltimore, Md. lost a Troxler moisture density gauge model 3430 serial # 25607 in Adamstown, Md. The gauge was missing from the back of a flat bed truck , which had its tailgate down, that was being driven around the Greenhill Manor Residential subdivision(New Design Rd & Union Ridge Rd in Fredrick City). The gauge, which apparently fell out of the back of the truck, was not in its case and the source rod was not padlocked. The source (7.2 millicuries of cesium 137 and 39.7 millicuries of americium 241), as far as they know, was in the shielded position and has not been found. MDE has conducted an initial investigation and it appears that they may issue a press release. * * * UPDATE ON 09/22/00 AT 0842 ET BY R. MANLEY TAKEN BY MACKINNON * * * The Troxler gauge was picked up from the middle of road (New Design Rd & Union Ridge Rd) by a sub contractor shortly after it fell from the back of the flat bed truck. The casing of the Troxler gauge had minor damage and the source never left its shielded position. After reading the article in the newspaper about the missing Troxler gauge the Sub Contractor contacted the licensee, D W Kozera Inc. The Troxler gauge case had a phone number and address on it but the Sub Contractor was unable to contact the licensee until reading the newspaper article which gave where the licensee could be contacted. The Troxler gauge will be checked over today by Troxler. NRC R1DO (Bill Ruland) and NMSS EO (Brian Smith) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0
37359 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2000-09-21 06:00 | 2000-09-21 06:51 | 2000-09-21 | TURBINE DRIVEN EMERGENCY FEED PUMP DISCHARGE VALVE WAS DISCOVERED LOCKED. The turbine driven Emergency Feed pump discharge valve (XV601036-EF) was discovered locked closed instead of locked open as required. This condition rendered the turbine driven Emergency Feed pump inoperable. The valve was last operated on 8/4/00. During the period when the discharge valve was closed, both diesels had been removed from service for maintenance. The "A" D/G was removed from service between 9/5/00 - 9/6/00 and the "B" D/G was removed from service between 9/19/00 - 9/20/00. The licensee is investigating the cause. The NRC Resident Inspector will be notified. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED COND OP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(ii)(A) |  |  |  | 0
37358 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-09-20 16:05 | 2000-09-20 17:51 | 2000-09-21 | PLANT OUTSIDE 10 CFR PART 50 APPENDIX R DESIGN BASIS DUE TO PROCEDURAL ISSUES "During the final review of the new Appendix R rebaselining project, it was discovered that the refueling water storage tank (RWST) inventory could be lost if AOP 10A, 'Safe Shutdown-Local Control' and AOP 10B 'Safe to Cold Shutdown in Local Control' were performed as written. The postulated event occurs during an Appendix R fire where SI-851(RHR pump suction from containment sump B) encounters a spurious open signal, causing the RWST to drain via backflow into containment. The procedures do not address this potential failure early enough into the event to preclude a potential loss of RWST inventory. This puts Point Beach Nuclear Power Plant outside of its design basis because 10CFR50 Appendix R Section III.L.2.b performance goals might not be met for the above scenario." The NRC resident inspector will be informed of this notification by the licensee. * * * UPDATE AT 1424 EDT ON 9/21/00 BY RYAN RODE TO FANGIE JONES * * * "This is an update to Event Notification 37358. That notification reported a procedural deficiency involving AOP 10A, 'Safe Shutdown - Local Control' and AOP 10B. 'Safe to Cold Shutdown in Local Control,' in the event of a postulated Appendix R fire which results in a spurious open signal to the SI-851A/B valves, 'RHR Pump Suction from Containment Sump B.' This notification discussed the concern with this spurious valve opening occurring during AOP 10A, which was a potential loss of RWST inventory to the containment sump through the SI-856A/B, 'RHR Pump Suctions From RWST,' valves. "Although appropriately identified in the License's condition report, this notification did not include a discussion of the concern identified during conduct of procedure AOP 10B. Specifically, since no action is specified to verify that the SI-851 A/B valves are closed in either AOP 10A or AOP 10B, in the event of the Appendix R fire which results in the spurious opening of those valves, when the RHR system is aligned for normal recirculation during the cooldown, the RCS inventory could be reduced by leakage through the open SI-851 valve to the containment sump. As mentioned in the original event notification, 10 CFR 50 Appendix R Section III.L.2.b requires the performance goal for maintaining RCS level within the level indication in the pressurizer be met. The procedures as written do not assure this performance goal would be met and are reported as a potential condition that is outside the Appendix R design basis." The licensee notified the NRC Resident Inspector. The R3DO (Bruce Burgess) has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37357 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-09-20 12:15 | 2000-09-20 14:33 | 2000-09-20 | RWCU ISOLATION VALVE FAILED TO CLOSE DURING TEST During performance of a reactor water cleanup (RWCU) logic system functional test, RWCU inboard isolation valve 1G31-F001 failed to close when a simulated high area temperature signal was applied. Subsequent testing indicates that a relay failed in the isolation circuitry. The licensee will replace the failed relay. The NRC resident inspector will be informed of this notification by the licensee. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37356 | 0 | TVA |  |  |  |  | 2000-09-11 | 2000-09-11 11:35 | 2000-09-20 | UNESCORTED ACCESS GRANTED INAPPROPRIATELY On September 11, 2000, TVA reported that inappropriate access may have been granted to some TVA employees based upon developed references utilized by RCM Power Services (formally Cataract Engineering, Inc.) in background investigations. TVA-IG discovered five individuals may have been granted access based on incomplete information. Workers at other licensees may be affected. Immediate compensatory measures were taken upon discovery. Refer to HOO log for additional details. Hoo Note: This applies to the following reactor sites, as reported: Browns Ferry, Sequoyah, and Watts Bar. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | OTH | GEN | 73.71(b)(1) |  |  |  | 0
37355 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-20 12:15 | 2000-09-20 12:55 | 2000-09-20 | SECURITY REPORT Unescorted access granted inappropriately. Immediate compensatory measures taken upon discovery. Contact the NRC Operations Center for additional information. The NRC resident inspector will be informed of this notification. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 0
37354 | 0 | SCIENTECH/NUSI |  |  |  |  | 2000-09-14 | 2000-09-20 07:42 | 2000-10-18 | PART 21 RELATED TO DEFECTS IN DELTA T TIME DOMAIN MODULES SUPPLIED TO GINNA STATION SCIENTECH Inc.'s subsidiary NUS Instruments, Inc. (NUSI) has determined that a Basic Component, supplied to Rochester Gas & Electric Ginna Station Nuclear Plant under RG&E purchase order NQ-l5877-A-JW, may contain a defect that is reportable under 10CFR21. NUSI became aware of this potential defect September 14, 2000. SCIENTECH, Inc. President was informed September 19, 2000. RG&E is aware of this problem and the affected components have been modified to remove any undesirable effects on their systems. A formal written report will be provided within 30 days of this notification. The components, DELTA T Time Domain Modules, M/N: TMD500-08/08/08/08-15-08-01/2, P/N: MBA-E062PA-l, Rev. 0 (4 ea.), were manufactured by NUSI. These components have been supplied to no other utility for use in Safety Related Systems. NUSI has opened a 10CFR21 file concerning this component and has numbered it as 21-00-01. * * * UPDATE 1343EDT on 10/18/00 from Marty Booska to S. Sandin * * * The licensee submitted a formal copy of the Part 21 via fax with a hard copy being sent by mail tomorrow. Notified R1DO(Cook) and NRR(Vern Hodge) via fax. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MD | OTH | PAR | 21.21 |  |  |  | 0
37353 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-09-13 | 2000-09-19 20:02 | 2000-09-19 | AGREEMENT STATE REPORT - SOURCE DETACHED FROM DRIVE ROD "The licensee notified the WA Department of Health, Division of Radiation Protection (WDOH), of a mechanical failure involving a Ronan Engineering Company Model SA-4 gauging device. The device is specifically licensed for density process measurements and uses a Cesium 137 sealed source, Amersham Model CDC.711M not to exceed 74 gigabecquerels (2 curies). The source is normally mounted at the end of a source rod, approximately six feet long. In this particular model version, the source rod consists of two screw-together extensions (approximately two and a half feet each) which screw into the same diameter source holder (approximately half a foot long). When operating, the rod with source is lowered through the shielded storage position, into the integral and enclosed dry well tube. When not in operation, the rod with source can be raised to place the source into a safe position inside the main shielding. An authorized user realized that a problem existed when attempting to withdraw the source to the safe position. Apparently the rod did not have a normal feel when it was raised. Preliminary indication was the source had separated from the source rod and fallen to the bottom of the insertion dry well. The licensee's RSO and its health physics consultant surveyed the area and determined there wasn't a dose rate problem since the process slurry was still providing ample shielding. The slurry was maintained in-place and the area adjacent to the dry-well access point was posted as a restricted area. "The recovery operation took place on September 18, with WDOH staff actively overseeing the operation. The health physics consultant determined the upper source rod section appeared simply to have come unscrewed from the lower sections, apparently from the vibration of the slurry separator on which the gauge was mounted. However, it was necessary to remove the device from it's bracket and up-end it to allow the source to slide back to the top of the device. Once the end was visible the parts were screwed back together and the unit re-installed. It was also determined that the source holder was partially unscrewed from the middle rod section as well. Both connections were coated with "lock-tight" and tightened. "Radiation readings increased from background to about 50 mR/hr in the general area during the recovery operation. Contact reading on the dry well near the estimated source position was greater than 5 R per hour. Actual recovery working time was about 20 minutes. Both individuals involved received an indicated 25 millirem exposure on their pocket dosimeters. "The health physics consultant indicated that this source rod was of an older style for this particular Ronan device. The three other devices of this model at the licensee's facility were checked and appeared not to be in danger of separating. The licensee plans on upgrading to a newer style rod during an up-coming maintenance shutdown. The recovery operation was successfully completed." HOO NOTE: see event #37331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37352 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2000-09-19 14:00 | 2000-09-19 16:53 | 2000-09-19 | 10 CFR PART 50, APPENDIX R ISSUE "During part of the Appendix R safe shutdown circuit review, it was discovered that a fire in the screenhouse could cause grounds to undervoltage cable L785 for bus 17 that could blow the control circuit fuses for 'B' D/G, preventing it from starting. The 'A' D/G would not be available for a fire in the screenhouse since it does not have an isolation breaker located outside the screenhouse to isolate the 'A' D/G from bus 18. Consequently, neither D/G would operate without repairs to place the 'B' D/G to local and replace the blown fuses." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37351 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-09-14 | 2000-09-19 15:32 | 2000-09-19 | AGREEMENT STATE REPORT - LOST/STOLEN TROXLER GAUGE "Troxler Model 3411B: Serial No. 12037, with the following sources: assayed 5.4 millicurie Cs-137; Serial No. 40-9359 and assayed 39 millicuries Am-241/Be; Serial No. 47-7153. The gauge was stolen or lost on the job site September 14, 2000. The gauge was placed in the back of a company pickup without a case and was not secured. The driver/operator remembers placing the tailgate in the up/closed position. The driver had a short conversation away from the truck and then departed the worksite. While driving along RM620 between Texas Highway 183 and Interstate Highway 35 (Austin, Texas), he noticed his tailgate was in the down/open position and immediately stopped. The gauge was gone. It is not known if the gauge was stolen from the worksite or lost along the highway. The gauge was not found by a company search of the route taken by the driver. A police report was filed with the Austin Police Department. Texas Licensee is Raba-Kistner (L01571-002) of Austin, Texas. The gauge was unsecured and not under direct surveillance at the time of the loss The gauge has not been recovered." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37350 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-08-01 | 2000-09-19 15:32 | 2000-09-19 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE "Troxler Model 3430: Serial No. 26131, with the following sources: 8 millicuries Cs-137; Serial No. 75-9150 and 40 millicuries Am-241/Be; Serial No. 47-22513. Stolen from an unauthorized storage location - 16545 Loch Katrine Land, Houston, Texas (residence of the driver/operator) on July 31-August 1, 2000. A police report was made with the Houston Police Department. Texas Licensee is Tolunay Wong Engineers, Inc. (L04848-001) of Houston, Texas. Steel cables securing the gauge in the truck were cut. The gauge was stolen during the hours of darkness. The gauge has not been recovered." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37349 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-01-14 | 2000-09-19 15:32 | 2000-09-19 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE "Troxler Model 4640: Serial No. 240, with the following source: 8 millicuries Cs-137; Serial No. 50-3271. Stolen January 14, 2000, from a parked vehicle at a Kroger store at 525 North Galloway, Mesquite, Texas. Gauge was stolen between 6 and 7 p.m. while the driver/operator stopped enroute to the company storage facility. Texas Licensee is (QTE) Quality Testing and Engineering, Inc. (L05222-001) of Dallas, Texas. Mesquite Police Department was notified. The gauge has not been recovered." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37348 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-09-19 13:00 | 2000-09-19 15:07 | 2000-09-19 | LICENSEE 24-HOUR REPORT "While 12 Pretreated Water Storage Tank (PTWST) was removed from service for planned maintenance, the Diesel Driven Fire Pump was also removed from service to realign its suction flowpath to 11 PTWST on 7/6/00. Per the Technical Requirements Manual, this nonconformance requires that a Special Report be submitted to the NRC, by telephone, within 24 hours." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW | [5 empty] | 0
37347 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-09-15 04:46 | 2000-09-19 11:23 | 2000-09-19 | ESF ACTUATION - CONTROL ROOM FILTRATION SYSTEM (CREFS) On 9/15/00, at 0446 the CREFS initiated due to receiving an actuation signal based on control building high gas activity. All automatic actions were verified to have occurred. It was determined that the control building high gas activity was caused by a temperature inversion and not an actual plant condition (i.e., radiological release). The control building high gas activity alarm cleared at 0450 and at 0459 CREFS was returned to a normal standby lineup. It was originally believed that this condition was not reportable due to it being an invalid actuation. Further review of this condition has determined that the condition was the result of a valid signal caused by an environmental condition. Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37346 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-09-18 22:30 | 2000-09-19 01:26 | 2000-09-20 | DEGRADED WHILE SHUTDOWN - FAILED CONTAINMENT LEAK RATE TEST System Engineering reports the local leak rate test results for 3A Feedwater Header Inboard and Outboard Drywell Check Valves (3-0220-58A & 3-0220-62A) are indeterminate due to excessive leakage. This exceeds the containment pathway leakage values allowed by Technical Specifications Primary Containment Leakage Rate Testing Program. The licensee will notify the NRC resident inspector. * * * UPDATE 2216 9/20/2000 FROM BRIAN GRANT TAKEN BY BOB STRANSKY * * * The "B" main steam inboard and outboard isolation valves also exceeded their maximum allowable leakage. The NRC resident inspector has been informed by the licensee. Notified R3DO (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37345 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-09-18 15:09 | 2000-09-18 19:56 | 2000-09-18 | MANUAL REACTOR SCRAM DUE TO DECREASING CONDENSER VACUUM "At 1425 PDT the plant experienced a sudden increase in offgas flow and decreasing condenser vacuum. Reactor power was reduced from 100% to 65% in accordance with the plant abnormal procedures for the loss of condenser vacuum. When the condenser back pressure continued to rise, a manual scram was inserted. All safety systems functioned as designed. The plant is currently stable in mode 3. The cause of the increase in off-gas flow is currently under investigation." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37344 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-18 17:10 | 2000-09-18 19:51 | 2000-09-18 | ECCS PERFORMANCE POTENTIALLY IMPAIRED DUE TO VALVE CLOSURE DURING TESTING "During review of emergency core cooling system (ECCS) valve operability test procedures, it was determined that, on one occasion in 1995 and again in 1997, one safety injection (SI) system containment isolation valve (CIV) was closed for valve operability testing with reactor power at or near 100%. With a CIV closed, injection from the two SI pumps following a small break loss of coolant accident (SBLOCA) would be directed to only two of the four reactor coolant system loops. At this power level, the high head SI system function of maintaining peak clad temperature (PCT) below 2200°F following a SBLOCA may not be satisfied. The condition becomes worse if a single failure is considered to affect one of the two SI pumps. Further evaluation of the condition is in progress." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37343 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2000-09-17 06:20 | 2000-09-18 15:55 | 2000-09-18 | OPERATORS MANUALLY STARTED EMERGENCY CONTAINMENT AIR COOLERS "On September 17, 2000, at about 0620 PDT, 2-ME-201 (non-safety containment normal chiller) tripped on low oil pressure. Operators began to start the containment normal chiller 2-ME-202, but stopped when prestart checks indicated low freon level. Because containment temperatures were slowly increasing, plant operators placed the emergency containment cooler units in service and started an additional containment dome air circulator. To perform their ESF function, the containment emergency coolers automatically actuate on safety injection actuation signal and on containment pressure, but not on containment temperature. SCE considered that the emergency coolers were not performing an ESF function during this occurrence, and a report to the NRC was not required. "On September 18, 2000, at 1000 PDT, SCE determined that actuation of the emergency cooler units could be considered to meet the clarification provided in section 3.3.2 of NUREG-1022, Rev. 1. Therefore, SCE is conservatively and voluntarily providing this report to the NRC. After determining that 2-ME-202 was functional with an indicated low freon level, plant operators started 2-ME-202 at about 0818 PDT, terminating this occurrence. The emergency coolers and dome air circulators operated as designed. At the time of this occurrence, both units 2 and 3 were operating at about 100% power. Unit 1 remains permanently defueled." The NRC resident inspector will be informed of this notification by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37342 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-09-18 14:15 | 2000-09-18 15:26 | 2000-09-18 | MAIN GENERATOR PARTIAL LOAD REJECT MAY NOT CAUSE REACTOR SCRAM AS ASSUMED "During evaluation of the data from a recent Reactor scram (Event #37325 on 9/15/00) a possible unanalyzed condition was found. Specifically, a Main Generator partial Load Reject can actuate a circuit contained in the turbine controls that may not always activate a reactor scram/recirculation pump down shift as required by analysis. Theoretically, with the partial load reject that fails to actuate the Reactor Scram/Recirculation pump trip and assuming failure of the bypass valves, MCPR limits could be affected. Immediate corrective action is to change the setpoint of the EHC trip to ensure that a partial load reject will result in a scram and Recirculation pump transfer to slow speed." The NRC resident inspector has been informed of this notification by the licensee. | 13 | 0 | 0 | 13 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED COND OP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(1)(ii)(A) |  |  |  | 0
37341 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-09-18 11:50 | 2000-09-18 13:41 | 2000-09-18 | UNIT OUTSIDE DESIGN BASIS OF FIRE PROTECTION PROGRAM "During review of the plant Cable and Conduit List (CCL) database, it was observed that six essential cables were not listed as requiring fire wrap and the cables are not wrapped in the field. The cable, with one exception, is listed in the safe shutdown analysis as required for hot and cold safe shutdown, but are not provided with Appendix R separation per 10CFR50 Appendix R Section IIIG. The cables are located in Room 299 on the +46 ft elevation of the Reactor Auxiliary Bldg (RAB) in Fire Area RAB 2. The condition has existed since plant original construction. At the time of discovery, the plant is operating at 100% Reactor Power. The cables were immediately listed as impaired, and compensatory actions were established (hourly fire watches). The condition has been entered into the plant corrective action program (CR-WF3-2000-1088). The equipment would be affected by a hypothetical fire in that fire area include the A/B Essential Chillers, RAB HVAG Exhaust Fan A, RAB HVAC Equipment Room Supply Fan AH-13 (3A-SA) Dampers. These components should be the protected components in the fire area. The condition affects the ability to achieve safe shutdown. Therefore, the condition is considered to be outside the design basis of the fire protection program." The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37340 | 0 | NORTH CAROLINA DIV OF RAD HEALTH |  |  |  |  | 2000-09-17 12:00 | 2000-09-18 10:12 | 2000-09-18 | AGREEMENT STATE REPORT A member of the cleaning staff at Watauga Regional Medical Center in Boone, NC removed the linens from the room of an I -131 patient in isolation. The mistake was caught by one of the nuclear medicine technicians and the linens were retrieved from the linen company. There was no spread of contamination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0
37339 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2000-09-18 05:03 | 2000-09-18 06:47 | 2000-09-18 | AUTOMATIC REACTOR TRIP DURING PLANT SHUTDOWN "A plant shutdown was in progress for a refueling outage, RCS pressure was at 2236 psig, Tavg at 541F. Power as indicated on intermediate range channels N35 & N36 was 4 x10 minus 12 amps and 7.5 x 10 minus 11 amps, respectively. Control room operator was in the process of driving control rods to 5 steps on Bank A, when P-6 permissive reset. Coincident with P-6 reset, a control power fuse blew on IR channel N-36, causing a Rx trip from 1/2 IR channels high. All rods fully inserted on the trip. Cause of the blown fuse is under investigation and plant shutdown will continue using normal operating procedures." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37338 | -1 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-09-18 04:50 | 2000-09-18 06:16 | 2000-10-11 | BOTH TRAINS OF RHR (RECIRC CAPABILITY) INOPERABLE FOR APPROXIMATELY SEVEN HOURS "While placing RHR Train 'B' in shutdown cooling during a refueling outage the pump minimum flow valve did not close as expected. Investigation revealed that the mini-flow transmitter 1 FIS-0611 was isolated causing the valve 1 FV0611 to remain open with RHR flow in excess of setpoint that would cause the valve to close. Work was performed on August 29, 2000, to calibrate this transmitter. On September 9, 2000, RHR Train 'A' seal cooler was isolated for maintenance rendering both trains of RHR inoperable for 6 hours and 54 minutes. The Cold leg injection capability from RHR Train 'A' remained available during this time. The Cold leg recirculation capability during these inoperabilities was not available. This would have required entry into T. S. 3.0.3. "RHR Train 'B' mini-flow transmitter 1FIS-0611 was discovered isolated causing the valve 1FV0611 to remain open with RHR flow in excess of setpoint that would cause the valve to close. The transmitter has been returned to service and the valve 1 FV0611 is operating properly." The licensee notified the NRC resident inspector. * * * RETRACTED AT 1524 EDT ON 10/11/00 BY BILL DUNN TO FANGIE JONES * * * "This retracts the 9-18-2000 notification made per 10 CFR 50.72 (b)(2)(iii)(D). That notification described an event where both trains of RHR were inoperable for 6 hours and 54 minutes when one train was in a system outage and the inservice train was found to be inoperable. Full flow to the RCS cold legs was apparently not available because it was determined that the inservice train's miniflow line valve would not close had a design basis accident occurred. Design engineering reviews have revealed that, with the mini-flow valve open, the inservice RHR train remained capable of providing minimum flow to the RCS for analyzed accident scenarios. Therefore, because one train of RHR remained operable, a condition did not exist that would have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. The R2DO (Ken Barr) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37337 | 0 | IDAHO NAT ENGR & ENVIRONMENTAL LAB |  |  |  |  | 2000-09-17 16:47 | 2000-09-17 19:07 | 2000-09-17 | COURTESY NOTIFICATION OF A DOE EMERGENCY DECLARATION AT AN INDEPENDENT SPENT FUEL STORAGE INSTALLATION (ISFSI) IN IDAHO. At 1647MDT, DOE INEEL declared a Site Area Emergency due to wildland fires on DOE controlled property, 2 miles North East of INTEC. The ISFSI containing the TMI spent fuel is not threatened. This notification is a courtesy call only and does not involve the NRC Radiological Emergency Plan. No NRC assistance is requested. DOE INEEL has notified the State of Idaho, all surrounding counties and DOE Headquarters. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | ID | OTH | GEN |  |  |  |  | 0
37336 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-17 06:46 | 2000-09-17 17:45 | 2000-09-17 | A licensee employee in the protected area was found with a metal flask containing a small amount of alcohol, approximately one teaspoon or less. It was later determined that the individual was unaware that the flask was in his coat pocket. The individual was escorted offsite. A behavior observation was performed, and the individual was allowed to return to work. The NRC Resident will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0
37335 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-09-17 15:20 | 2000-09-17 16:33 | 2000-09-17 | UNEXPECTED MAIN TURBINE TRIP CAUSED AN AUTOMATIC REACTOR SCRAM. During power ascension following a planned outage, Nine Mile Point Unit 2 automatically scrammed from approximately 70% reactor power. The scram signal was generated when the Main Turbine tripped. The cause of the Turbine Trip is being investigated. All control rods fully inserted. Reactor pressure is stable and being controlled through Turbine Bypass Valves to the Main Condenser. One additional scram signal was received on low Reactor Vessel Water Level during level recovery efforts. Reactor level control is stable and being fed from the condensate/feedwater system. All Emergency Core Cooling Systems are operable and in standby. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37334 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-09-17 08:09 | 2000-09-17 11:03 | 2000-09-17 | BRIEF ENTRY INTO TECHNICAL SPECIFICATION 3.0.3 "During attempts to restore Train 'A' Safety Injection (SI) system following planned testing, the Train 'B' SI system was rendered inoperable for 1 minute requiring entry in TS 3.0.3. The high and low head injection systems were operable. "Train 'A' SI was inoperable due to planned RCS pressure isolation valve inservice testing. During the Train 'A' SI testing, valve 1HV-8802A (SI-PMP A TO HOT LEG 1&4 ISO VLV) had to be manually closed. In order to return Train 'A' SI to service, 1HV-8802A would have to be manually unseated and then electrically stroked. The Train 'A' SI pump was placed in PTL [pull-to-lock] to ensure that the SI pump would not run out should the SI pump auto start. The control room staff, however did not recognize the impact on Train 'B' SI, during stroke of 1HV-8802A with the SIP TO COLD LEG isolation valves (1HV-8821 A&B) open. In this configuration, the potential existed to run out the Train 'B' SI pump should the pump auto start. The control staff within a few minutes of stroking 1 HV-8802A recognized the entry into TS 3.0.3." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37333 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-09-16 23:15 | 2000-09-16 23:43 | 2000-09-18 | UNUSUAL EVENT - HURRICANE WARNING The licensee declared an unusual event at 2315 due to a hurricane warning being declared for Citrus County, Florida. Further actions will be taken depending upon the direction Hurricane Gordon takes in the next 24 hours. The licensee intends to remain at power and will continue to evaluate this storm. The licensee notified both state and local governments of the declaration as well as the NRC resident inspector. * * * UPDATE AT 0049 ON 9/18/00 BY GAGNEY, RECEIVED BY WEAVER * * * The licensee exited the unusual event at 0035. The hurricane warning is no longer in effect. The storm caused no damage at the plant and it continues to operate at full power. The licensee notified both state and local governments of the declaration as well as the NRC resident inspector. HOO notified FEMA (CIBOCH); RDO (CAHILL); EO (ZWOLINSKI); IRO(CONGEL) | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37332 | 0 | PALISADES | 1 |  |  | [1] CE | 2000-09-15 23:25 | 2000-09-15 23:47 | 2000-09-16 | UNUSUAL EVENT - UNIDENTIFIED LEAKAGE GREATER THAN 1GPM The plant is in hot shutdown making preparations for startup. Reactor coolant is back leaking from loop "1A" through two check valves into a safety injection tank. The safety injection tank is approximately 95% full. If the tank should over pressurize the relief valve will relieve to the containment. The primary containment integrity is set. The maximum leak rate observed was 1.64 GPM. The licensee has taken steps to seat the check valves and is now measuring the leak rate again. The unusual event was declared at 2325. The licensee notified the NRC resident inspector, the state and Van Buren county. * * * UPDATE AT 0145 ON 9/16/00 BY SLEEPER, RECEIVED BY WEAVER * * * The licensee terminated the unusual event at 0121. Unidentified leakage has returned to its normal value of less than 1 GPM. The licensee will notify the NRC resident inspector. The Operations center notified the RDO (RING); NRR EO (ZWOLINSKI); IRO (CONGEL) and FEMA (CEGIELSKI). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37331 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-09-13 | 2000-09-15 19:32 | 2000-09-15 | MECHANICAL FAILURE OF A RONAN MODEL SA-4 GAUGING DEVICE THE FOLLOWING EVENT WAS E-MAILED TO THE HEADQUARTERS OPERATION CENTER Transalta Centralia Mining LLC notified the WA Department of Health, Division of Radiation Protection, of a mechanical failure involving a Ronan Engineering Company Model SA-4 gauging device. The device is specifically licensed for density process measurements and uses a Cesium-137 sealed source, Amersham Model CDC.711M not to exceed 74 gigabecquerels (2 curies). The source is normally mounted at the end of a source rod and secured by pins. When not in operation, the rod with source can be withdrawn into a safe position inside the shielding device. When operating, the rod with source is inserted into the process area through a dry well. An authorized user realized that a problem existed when attempting to return the source to the safe position. Apparently the rod did not have normal feel when it was withdrawn. The licensee's RSO and their health physics consultant surveyed the area and stated there wasn't a dose rate problem since the process mixture was still providing ample shielding. The mixture will remain in-place until the source can be returned to the device's normal shielded position. The area adjacent to the dry-well access point has been marked as a restricted area. Preliminary indications are the source has separated from the source rod and fallen to the bottom of the insertion well. The consultant indicated that this type Ronan device (but not this particular device) has suffered similar failures in the past. The consultant has contacted Ronan Engineering requesting they send procedures and special equipment. The recovery operation is anticipated to take place on September 18. The Department of Health, Division of Radiation Protection will be on-site during the recovery operation. Type of License: Fixed Gauge Washington Event Report: WA-00-046. HOO NOTES: see event #37353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37330 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2000-09-15 15:05 | 2000-09-15 17:57 | 2000-10-03 | MANUALLY SCRAMMED THE REACTOR AFTER ENTERING THE RESTRICTIVE AREA OF THE POWER TO FLOW MAP. On September 15, 2000 at Peach Bottom Atomic Power Station (PBAPS), Unit 2 was manually scrammed per operating procedure during turbine testing in preparation for the refuel outage. The manual scram was due to entering restricted area of the power to flow map from Technical Specification 3.4.1, after the trip of the "2B" recirculation pump. All rods fully inserted and the reactor was shutdown. Reactor level during the scram lowered to 0" and a Group II and III primary and secondary containment isolation was received. The isolations functioned as designed. The plant is stable in hot shutdown with the main condenser as a heat sink and the feedwater system is in service for level control. No radioactive release or Emergency Core Cooling System injection occurred during the scram. The turbine was tripped in accordance with the refuel outage plan when the recirculation pump tripped. The plan was to perform turbine testing and then to manually scram the reactor at the same power level. The reactor was manually scrammed less than one minute after entering the restricted area of the power to flow map. No power oscillations were seen. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED AT 1715 EDT ON 9/21/00 BY ANDREW WINTER TO FANGIE JONES * * * "On September 15, 2000 PBAPS reported that Unit 2 was manually scrammed in accordance with operating instructions during turbine testing. The report identified that the manual scram was initiated based on entering the restricted area of the power to flow map after the tripping of the 2B Recirculation Pump. This notification is being retracted based on the following: "NUREG 1022 Revision 1 specifically states that 'The Commission is interested both in events where an ESF was needed to mitigate the consequences (whether or not the equipment performed properly) and events where an ESF actuated unnecessarily....This indicates an intent to require reporting actuations of features that mitigate the consequences of significant events.' Therefore, the following is an analysis of these two underlying reasons for reporting ESF actuations: 1. The need for the ESF to mitigate the consequences of an event: The September 15, 2000 PBAPS manual scram was initiated because the plant operator made a conservative decision in accordance with station procedures to initiate a reactor scram. At the time this decision was made, the plant conditions were approximately 16 percent power and 24 percent core flow. Although this condition is close to an operational limit conservatively established by the licensee and the operator made the correct decision to commence the plant shutdown, the ESF actuation was not necessary to mitigate the consequences of this evolution. Moreover, plant conditions were not changing in a direction that would have required the manual scram to mitigate the consequences of significant events. 2. Events where an ESF actuated unnecessarily: The actuation of a manual scram and the subsequent PCIS Group II and Ill actuations were part of a preplanned shutdown for the commencement of the PBAPS Unit 2's thirteenth refueling outage (2R13) and were necessary to complete the plant shutdown. The decision to insert the manual scram in accordance with station procedures, resulted in the preplanned shutdown commencing slightly early. Therefore, the ESP did not actuate unnecessarily since it was already planned to shutdown the plant by inserting a manual scram. "Therefore, based on the above discussion, this event is not reportable because the manual scram resulted from and was, in accordance with the licensee's procedure, and part of a preplanned sequence of reactor operation." The licensee notified the NRC Resident Inspector. The R1DO (William Ruland) has been notified. ***** UPDATE AT 1554 ON 10/03/00 FROM ANDREW WINTER TO LEIGH TROCINE ***** Via this update, the licensee is resubmitting this event notification because the event was determined to represent an unplanned ESF actuation. The licensee is also providing additional clarification to the original report because it was determined that the unit was not operating in an unrestricted region of the technical specifications. The following text is a portion of a facsimile received from the licensee: "On September 23, 2000, PBAPS submitted a retraction to Event #37330. After further review, it was determined that the basis for the PBAPS retraction was not consistent with the NRC interpretation of the reporting requirement. Therefore, the following event report is being resubmitted:" "On September 15, 2000, PBAPS Unit 2 was manually scrammed. The manual reactor scram was initiated by the plant operator based on the understanding that the plant conditions placed the plant in the restricted area of the power-to-flow map after the unplanned tripping of the 2B Reactor Recirculation Pump. The plant conditions at the time of the manual scram were approximately 16 percent power and 24 percent core flow. Although this condition is close to an operational limit conservatively established by the licensee to commence the plant shutdown, the ESF actuation was not necessary to mitigate the consequences of this evolution. Furthermore, the plant was not in an unrestricted region of Technical Specification 3.4.1, and emergency systems subsequently performed as required." "Although the ESF actuation was not necessary to mitigate an event, it is the conclusion of the licensee that this event does represent an unplanned ESF actuation. Therefore, this event is reportable under 10 CFR 50.72(b)(2)(ii)." The licensee notified the NRC resident inspector and plans to submit a Licensee Event Report by 10/15/00. The NRC operations officer notified the R1DO (Linville). | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37329 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-08-15 | 2000-09-15 17:04 | 2000-09-15 | 187 MICROCURIE PROMETHIUM-147 SOURCE LOST Promethium-147 is held under a General License. State of California event # CA-09-15-00 Agilent Technologies, Inc. located in Newark, CA was preparing to ship a 187 microcurie Promethium-147 source back to Hewlett Packard located in San Jose, CA. The source was taken out of its container and placed on a desk in a cubicle located in an Agilent Technology, Inc. building. When the person came back to get the source it was missing. Employees in the area were asked if they had seen or taken the small source and a survey of the area was performed to find the source. The source was not found. The original activity of the source, November 1994, was 900 microcuries. The half life of Promethium-147 is 2.62 years. The missing Promethium-147 was used in a Betascope which is used to measure the thickness of silicon wafers. Agilent Technologies, Inc. notified the State of California regarding the missing source on 08/17/00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37328 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-09-01 | 2000-09-15 15:38 | 2000-09-15 | LEAKING SOURCE, SODIUM-22, DISCOVERED DURING LEAK TEST. THE FOLLOWING EVENT WAS EVENT WAS E-MAILED TO THE HEADQUARTERS OPERATION CENTER Washington State University located in Pullman, WA Radiation Safety Officer performed a leak test on a 1.5 millicurie sodium-22 source that was planned to be transferred from one authorized user to another. The source was found to be leaking and will be disposed. Surveys of the storage area and work area were done and decontamination performed on the remote handling tools. The source is one of four custom made by a researcher at Brookhaven National Lab in June 1996 and transferred to Washington State University (WSU) when the researcher moved to WSU. Of the four sources, one was found to be leaking and disposed of several years ago, one is still at WSU, and the last was transferred to another academic institution (WSU has notified the recipient of this event). Leak test? 0.027 microcuries of removable contamination detected. Activity and isotope involved: 1.5 millicuries of Na-22 as of June 1996. Washington State event report: WA-00-044. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37327 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-09-14 18:30 | 2000-09-15 10:38 | 2000-09-15 | ERROR IDENTIFIED IN LOCA MODEL THAT COULD RESULT IN PEAK CLAD TEMPERATURE > 2200°F "At 1830 hours on September 14, 2000, a condition potentially outside the design basis of the facility was identified at CR-3. This event notification is being made as required by 10 CFR 50.46 for an error identified in the Evaluation Model for CR-3 which may result in peak clad temperature in excess of 2200°F. This notification is being made while the unit is shutdown prior to entry into MODE 2 following a recent maintenance outage. "The condition is that, in the event of a small break loss of coolant accident involving the core flood line at CR-3, it may be necessary to shut down the CR-3 reactor coolant pumps within 1 minute of loss of subcooling margin in order to limit peak cladding temperatures to less than 2200 degrees Fahrenheit (the 10 CFR 50.46 limit for peak cladding temperatures). The current licensing/design basis analysis assumes that the pumps are shut down within 2 minutes of loss of subcooling margin. "Existing procedural guidance in Emergency Operating Procedure requires turning off the reactor coolant pumps as an immediate manual action in response to loss of subcooling margin. Operator actions to trip the reactor coolant pumps are routinely monitored in training. Thc action to turn off the reactor coolant pumps upon loss of subcooling margin is routinely completed within 1 minute in plant simulator accident training unannounced casualty scenarios. "Plant personnel for CR-3 have determined that, based upon the existing procedural guidance and simulator training experience, there is reasonable expectation that procedurally directed operator actions will successfully shut down the reactor coolant pumps within 1 minute of loss of subcooling margin and therefore, the peak cladding temperature will remain unchanged and below the 2200 degrees Fahrenheit limit of 10 CFR 50.46. Thus, the CR-3 emergency core cooling systems continue to be operable because, based upon engineering judgement, the systems are capable of performing their intended safety function. "This determination that a condition potentially outside the design basis of the plant will be followed with more detailed evaluation and analysis of the issue. It is possible that the-follow-up analysis-will provide technical justification which demonstrates that CR-3 remains within the existing design basis. "CR-3 is reporting this prior to placing the plant in operation. This report is being made under 10 CFR 50.72(b)(1)(ii)(B) as 'Any event or condition during operation that results in a condition that is outside the design basis of the plant.' CR-3 is currently in a shutdown condition in the process of performing a plant start-up. Therefore, the one-hour criteria of this reporting requirement is not in effect. "At its most fundamental level, PSC 2-00 identifies an analytical issue that requires resolution. A telecon with NRC technical staff held on 9/13/2000 identified the analytical issue as one that is principally concerned with an ECCS evaluation model assumption. The safety significance was alleviated by discussions on consistent, demonstrated performance of immediate operator action to trip the RCPs well within 1 minute, with no challenge to the preliminary (conservative) accident analysis. Additionally, discussions were also presented on the relative probability of this specific scenario. The combination of the break with the specific failure represents a very small probability (<E-10), which helps diminish the safety significance of this scenario. "CR3 is proceeding with an approach that conservatively addresses Mode 2 restraint because decay heat power is low at this time since the reactor is shutdown and will not increase significantly until further power operation is commenced." The NRC resident inspector has been informed of this notification by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37326 | 0 | KANSAS CITY RESEARCH MEDICAL CENTER |  |  |  |  | 2000-08-30 | 2000-09-15 10:36 | 2000-09-15 | LOSS OF ONE I-125 SEED, 0.55 mCi The licensee discovered 1 of 65 iodine-125 seeds missing when installing them in an applicator for a permanent implant on 8/17/00. Multiple surveys failed to find the seed if present in the shipment. The shipment was received on 8/15/00 and surveyed, but not opened until the applicator was ready to be loaded. The licensee contacted the manufacturer, Uramed Company, of Norwood, MA about the missing seed. The manufacturer could not determine that they had not sent 65 seeds. The seed is considered lost, probably in the hot lab of the hospital, and the licensee does not consider it to be a serious health risk. A written report will be submitted to the NRC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0
37325 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-09-15 06:30 | 2000-09-15 10:27 | 2000-09-15 | AUTOMATIC REACTOR SCRAM DUE TO ELECTRICAL GRID DISTURBANCE A Baxter Wilson Station 500 kV breaker opened inducing a grid disturbance that caused a reactor scram for an unknown reason. The breaker opening cause a loss of one offsite source. The disturbance also was picked up as an undervoltage on bus 15, which caused the division 3 (high pressure core spray) diesel generator to start. The bus 16, which is fed from the same engineered safeguards features transformer, did not pick up the undervoltage condition. The reactor core isolation cooling system started and injected. The licensee is investigating the actual cause of the reactor scram. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37324 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-09-14 23:33 | 2000-09-15 01:40 | 2000-09-15 | PRIMARY CONTAINMENT ISOLATION LOGIC RELAY COIL FAILED CAUSING SOME ISOLATIONS The primary containment isolation logic relay 16A-K61 coil apparently burned out causing the relay to de-energize. This caused valves 20 MOV-94 (DW equipment sump pump inboard isolation), 20 MOV-82 (DW floor sump pump inboard isolation), and 10 MOV-18 (RHR shutdown cooling inboard isolation) to receive a close signal. 20 MOV-94 and -82 went closed while 10 MOV-18 was already closed. The drywell sumps can not be pumped down. This places the plant in the coolant leakage monitoring per technical specification 3.6.d which allows 24 hours for repair of the problem. The problem is being worked on and investigated and it is expected to be completed within the 24 hour limit. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37323 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2000-09-04 14:24 | 2000-09-14 18:47 | 2000-09-14 | FEEDWATER ISOLATION During Post Trip review, it was discovered that a second feedwater isolation signal that occurred was not reported. This second feedwater isolation signal occurred following the reactor trip, see event # 37287, previously reported on 09/04/00. This notification is to report the additional feedwater isolation signal that occurred September 4, 2000 at 1424 hours. The feedwater isolation signal occurred when the steam dump valves that were being used to control reactor coolant system temperature popped open . This caused "B" steam generator water level to swell above the feedwater isolation signal setpoint of 78%. All equipment operated as required. The feedwater isolation valves closed due to the feedwater isolation signal. These valves were the only equipment not already in the feedwater isolation system required position. The effect of the feedwater isolation signal on the plant was minimal. The feedwater isolation valves were reopened at 1514 hours to allow feeding steam generators with the Motor Driven Startup Feedwater Pump. The plant is currently in Mode 1 at 100% power. The NRC Resident Inspector will notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37322 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-09-14 14:22 | 2000-09-14 17:52 | 2000-09-14 | BOTH TRAINS OF STANDBY LIQUID CONTROL (SLC) SYSTEM DECLARED INOPERABLE During the performance of a sample of the SLC storage tank, the chemistry technician discovered a small piece of foreign material in the sample. Upon further investigation several pieces of foreign material (appears to be plastic) were found floating on the top, and what appears to be 2 large plastic bags floating near the bottom of the tank. At time 1422 CST the SLC system was declared inoperable due to a potential for the bags to cause a loss of the SLC safety function. Riverbend Station entered Limiting Condition of Operation for Technical Specification 3.3.1.7 action C to restore one SLC subsystem to OPERABLE within 8 hours. Efforts are underway to remove all foreign material from the SLC system storage tank. If one train of SLC system has not been restored within 8 hours the licensee has an additional 12 hours to be in Hot Shutdown. All other Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 09/14/00 AT 2247 ET BY HUSTON TAKEN BY MACKINNON * * * The foreign material found in the SLC Tank has been removed to the extent possible. Additional inspections with underwater camera and boroscopic equipment reveal no additional plastic. Riverbend Station has declared the system operable and has exited the Technical Specification Limiting Condition of Operation for the system at time 2059 CT. Safety function has been restored. Foreign material removed appears to be two large thin plastic bags, light brown in color. R4DO (G. Sanborn) notified. The NRC Resident Inspector was notified by the licensee of the update. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37321 | 0 | IOWA DEPT OF RADIATION CONTROL |  |  |  |  | 2000-09-11 11:00 | 2000-09-14 13:31 | 2000-09-14 | UNEXPECTED EXPOSURE TO IRIDIUM-192 SOURCES An individual at Mercy Hospital thought that she had ordered both dummy seeds and real iridium-192 seeds. A package containing seeds from Best Industries, Inc. was delivered to Mercy Hospital on 09/11/00. The shipping papers for the package stated 1 each leader, and on the next line 1 each ribbon with six seeds. The person thought that the 1 each leader was the dummy iridium-192 seeds and the 1 each ribbon with six seeds was the real iridium-192 seeds. The individual did not realize that the package shipping papers meant 1 each leader with 1 each ribbon with six seeds. The individual did not make a routine radiation survey before removing a ribbon of iridium-192 seeds from a lead pig. The individual carried the ribbon of seeds in her hand to a room where a practice simulation of a upcoming operation was to be performed using dummy seeds. The simulation was never performed because of some problems with loading the ribbon of seeds into a catheter. The ribbon of iridium-192 seeds was stored in a storeroom overnight at the foot of a bench. That night, the individual realized that she may have handled iridium-192 seeds instead of dummy seeds. The next morning, she discovered that she had handled actual iridium-192 seeds. Total activity of the iridium-192 seeds was 18.54 mCi. The state of Iowa has calculated that the individual received 29 rem to her right hand and a whole body dose of 55 mrem (she had the ribbon of iridium-192 seeds in her hand for an estimated time of 20 minutes.) The doctor who was to have performed the simulated operation received a calculated whole body dose of 60 mrem. This event was initially reported to NRC Region 3 (Jim Lynch). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0
37320 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2000-09-13 13:00 | 2000-09-14 11:35 | 2000-09-14 | 10 CFR 40.60 24-HOUR REPORT DUE TO FAILURE OF EDG TO START The licensee reported that a Cummins model V12-500GS failed to start when tested. The licensee is investigating the cause of the failure to start. The EDG was repaired as of 2045 CDT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 3 | IL | FUE | [5 empty] | 0
37319 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2000-09-14 10:10 | 2000-09-14 10:32 | 2000-09-14 | OFFSITE NOTIFICATION DUE TO A DEAD MANATEE FOUND IN ONE OF THE PLANT CANALS The licensee made a call to the U. S. Fish and Wildlife Agency and the Florida Fish and Wildlife Conservation Commission to notify them of a dead manatee found in canal C107, directly southwest of the plant. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37318 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2000-07-22 | 2000-09-13 18:40 | 2000-09-13 | TRITIUM RELEASE FROM THE UNIVERSITY OF ARIZONA At approximately 10:30 AM, September 6, 2000, the Agency was advised by the Radiation Safety Officer of the University that a laboratory had reported approximately 100 microcuries of tritium had been picked up by the custodial staff. The University Radiation Control office commenced an investigation of the problem and on September 7, 2000 reported that approximately 31 millicuries of tritium may have been lost out of a fume hood stack. This release was confirmed on September 11, 2000. The release occurred around July 22 - 30, 2000. The University and the Agency continue to investigate this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0
37317 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2000-09-13 16:36 | 2000-09-13 17:51 | 2000-09-13 | MANUAL REACTOR SCRAM FROM 77% POWER FOLLOWING LOSS OF CONDENSER VACUUM This occurred when the plant lost condenser vacuum after the steam jet air ejector valves closed. This valve closure was the result of a blown valve indication light bulb being changed. The reactor was manually scrammed from 77% power when the vacuum reached 6.5" Hg and decreasing. After the reactor scram the reactor vessel water level dipped below 127"(as low as 121") initiating groups 2, 3, 4 and 5 isolations and start of the standby gas treatment system. All rods fully inserted, no ECCS injection occurred and no relief valves lifted. The NRC Resident Inspector will be informed | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37316 | 0 | UNIVERSITY OF VIRGINIA HOSPITAL |  |  |  |  | 2000-09-07 | 2000-09-13 16:39 | 2000-09-13 | THE UNIVERSITY OF VIRGINIA HOSPITAL REPORTED A MEDICAL MISADMINISTRATION DURING BRACHYTHERAPY. A patient being treated for cervical cancer was given a higher dose (8 gray) instead of the prescribed dose (5 gray) due to human error resulting in the wrong dwell times being used. It appears there will be no adverse affects to the patient. The patient and the referring physician will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 2 | VA | HOS |  | 35.33 |  |  |  | 0
37315 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-09-13 11:19 | 2000-09-13 14:38 | 2000-09-13 | PLANT OUTSIDE DESIGN BASIS FOR CONTROL ROOM EMERGENCY FILTRATION SYSTEM UNFILTERED INLEAKAGE BASED UPON TRACER GAS TESTING - IMPACT ON CONTROL ROOM DOSE CONSIDERATIONS "During September 8 through 11, 2000, a series of special tests, using a tracer gas decay methodology, were performed to determine the total inleakage into the control room and the associated impact on control room dose. These tests were performed in support of a proposed Technical Specification amendment request that is in the process of being developed for removal of main steam leakage control system test requirements and resolution of a long-standing issue pertaining to secondary containment/standby gas treatment system performance, using alternative source term methodology. The testing was also performed in response to NRC-industry initiative efforts to resolve the generic issue of the validity of control room unfiltered air infiltration rate assumed by licensees in control room habitability assessments. "On September 13, 2000, test results were evaluated and a preliminary assessment shows the highest train measured unfiltered inleakage for the control room emergency filtration system, as determined by the tracer gas testing, to be 83 ± 37 cfm. This is in excess of the current licensing and design basis limit of 10.55 cfm. The impact of this unfiltered inleakage increase on control room dose was evaluated and it was determined that the design basis thyroid dose of 30 rem to the control room operators would be exceeded during post-accident conditions. "A Follow-Up Assessment of Operability (similar to a Justification for Continued Operation) was prepared to allow continued plant operation in this condition. The operability determination, which was based upon an evaluation of control room dose for several accident scenarios, concluded that the as-found inleakage did not render the control room emergency filtration system inoperable (based upon 10CFR50, Appendix A, GDC 19). In addition, a follow-up interim compensatory measure to reduce the calculated control room thyroid dose below the 30 rem limit includes administration of potassium iodide in accordance with requirements contained in abnormal operating procedures. Final resolution of this issue will be addressed by implementation of alternative source term methodology at WNP-2 and as part of the proposed Technical Specification amendment request. A feasibility study, using alternative source term methodology, has shown that inleakage rates well in excess of 83 ± 37 cfm (approximately 300 cfm) would result in control room doses below the regulatory limit. This is a design basis analysis issue and no plant hardware changes are required in the resolution of the problem. We are continuing to follow the NRC-industry initiative efforts to resolve generic issues related to control room habitability." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37314 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2000-09-13 09:54 | 2000-09-13 13:15 | 2000-09-13 | THE "2A" DIESEL GENERATOR WAS INADVERTENTLY STARTED BY THE UNIT OPERATOR Unit 2 was operating at 100% power. A Division 2 Residual Heat Removal (RHR) Surveillance was in progress, which required the "2A" Diesel Generator Cooling Water Pump to be started. The Unit Operator inadvertently placed the Control Switch for the "2A" Diesel Generator to START. The Unit Operator recognized the error and the Diesel Generator Control Switch was immediately placed in STOP. The "2A" Diesel Generator and Diesel Generator Cooling Water Pump switches are side by side on the panel. The Diesel Generator reached at Least 150 RPM as indicated by the Auto Start of the "2A" Diesel Generator Cooling Water Pump. The Diesel Generator was returned to a Standby Operable condition. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37313 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-09-13 04:33 | 2000-09-13 07:58 | 2000-09-22 | AUTOMATIC START OF THE HIGH PRESSURE CORE SPRAY PUMP The licensee reported that the high pressure core spray (HPCS) pump automatically started when the pump control switch was taken out of the "pull-to-lock" position. The HPCS system was out of service for maintenance at the time of the event and had been declared inoperable on 09/12/00 at 0520 EDT. The HPCS spray injection valve did not open, as it was deenergized closed. The divisional diesel generator did not start as it was configured in the maintenance mode. There was no impact on the plant. The plant is in cold shutdown with the mode switch in the refuel position. The cause of the actuation is unknown and an investigation is in progress. The licensee intends to notify the NRC Resident Inspector. * * * RETRACTED AT 1650 EDT ON 9/22/00 BY THOMAS CHWALEK TO FANGIE JONES * * * "Subsequent evaluation of the system condition at the time concluded that the system was appropriately removed from service with the injection valve de-energized closed (it was known at the time that the initiation signal was invalid). In addition, removal of the system from service as part of a planned evolution for maintenance or surveillance testing is generally not reportable (NUREG 1022). "In summary, the system was properly removed from service with the injection valve de-energized closed. The event is not reportable and this retraction is notification thereof." The licensee intends to notify the NRC Resident Inspector. The R1DO (Bruce Barkley) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION | ACCIDENT MITIGATION |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(iii)(D) |  |  | 0
37312 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2000-09-12 07:40 | 2000-09-13 07:35 | 2000-09-13 | 24 HOUR FITNESS FOR DUTY REPORT A licensed operator was administered a for-cause breathalyzer test after observation by operating staff that the individual's breath smelled of alcohol. The operator was oncoming and was not allowed to take the watch. Operations management personnel directed that the individual be taken home pending management review of the situation. Corrective action for consideration of resumption of licensed duties will follow management's review. The licensee notified the NRC Resident Inspector and will notify the State of Connecticut. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0
37311 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-11 17:20 | 2000-09-12 15:55 | 2000-09-12 | CONTRACTOR TESTED POSITIVE DURING RANDOM TEST FOR DRUGS AND ALCOHOL Contract Supervisor determined to test positive as a result of a random drug and alcohol screening. Per applicable administrative procedures the individual's access authorization to the protected area was terminated. The NRC Resident Inspector was notified. | 84 | 100 | 0 | 84 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0
37310 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-12 07:52 | 2000-09-12 09:30 | 2000-09-12 | LOSS OF ENS AND COMMERCIAL TELEPHONE SERVICE The licensee reported that the Emergency Notification System telephone line, as well as all commercial telephone lines have been lost. This may have occurred as a result of thunderstorm activity near the site. The licensee is currently attempting to troubleshoot and correct the problem. The NRC resident inspector has been informed of this event by the licensee. | 82 | 100 | 0 | 82 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ENS INOPERABLE | OTHER ASMT/COMM INOP |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(v) | 50.72(b)(1)(v) |  |  | 0
37309 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2000-09-11 19:30 | 2000-09-11 20:24 | 2000-09-11 | THE LICENSEE HAS DETERMINED A CONDITION THAT COULD BE POTENTIALLY OUTSIDE THE DESIGN BASIS At 1930 hours on September 11 2000, a condition potentially outside the design basis of the facility was identified at TMI-1. The condition is that in the event of a small break loss of cooling accident involving the core flood line at TMI-1, it may be necessary to shut down the TMI-1 reactor coolant pumps within 1 minute of loss of subcooling margin in order to limit peak cladding temperatures to less than 2200 degrees Fahrenheit (the 10 CFR 50.46 limit for peak cladding temperatures). The current design basis analysis assumes that the pumps are shut down within 2 minutes of loss of subcooling margin. Existing procedural guidance in site procedure 12 10-10 requires turning off the reactor coolant pumps as an immediate manual action in response to loss of subcooling margin. Operator training supervision and training instructors have been queried. They report that the action to turn off the reactor coolant pumps upon loss of subcooling margin is routinely completed within 1 minute in plant simulator accident training unannounced casualty scenarios. The Shift Manager for TMI-1 has determined that based upon the existing procedural guidance and the past simulator training experience, there is reasonable expectation that procedurally directed operator actions will successfully shut down the reactor coolant pumps within 1 minute of loss of sub-cooling margin and therefore, the peak cladding temperature will remain below the 2200 degrees Fahrenheit limit of 10 CFR 50.46. Thus, the TMI-1 emergency core cooling systems continue to be operable because, based upon engineering judgement, the systems are capable of performing their intended safety function. This determination that a condition potentially outside the design basis of the plant will be followed with more detailed evaluation and analysis of the issue. It is expected that the follow-up analysis will either provide technical justification that demonstrates that TMI-1 remains within the existing design basis or that action will be taken to place TMI-1 back to within conformance to the design basis. The actions to be taken based upon the follow-up analysis will be provided to the NRC in a Licensee Event Report that follows this immediate notification per 10 CFR 50.73. The Resident Inspector will be informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37308 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-09-11 15:53 | 2000-09-11 19:47 | 2000-09-11 | FOUR HOUR 91-01 BULLETIN At 1555 on 9/11/00 during review of flowdown of NCSA-PLANT012.A01 (Favorable Geometry Vacuum Cleaner) it was discovered that the NCSA failed to provide adequate guidance for handling and storing sintered metal filters removed from favorable geometry vacuum cleaners. The vacuums are used during maintenance and operational activities to collect potentially contaminated material. The filters are therefore handled as uranium bearing materials once removed from the favorable geometry vacuum cleaners. The NCSA fails to provide adequate guidance for handling these filters and has therefore been identified to be deficient in that necessary controlled parameters were not established by the NCSA. Geometry control was not maintained in this event, interaction and moderation control were in place, although not required by the NCSA. Therefore one control of the double control contingency principle was lost. SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this is low. The filter assembly is a favorable geometry while installed in the vacuum. The maximum internal volume of the filter is less than 5.49 liters which is less than a minimum critical volume (5.67 liters) assuming optimum conditions for criticality (fully enriched, optimum geometry, optimum moderation, and full reflection). Therefore, a criticality could not occur even if the uranium in the filter achieved an optimum configuration. All filters were safely spaced from other uranium bearing material. POTENTIAL .CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): The potential pathway for a criticality are that the fitter assembly is removed from the vacuum, it is placed in a plastic bag, spaced adjacent to other uranium bearing material, the material becomes moderated and is reflected. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameters are geometry. interaction, and moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The maximum internal volume of the filter is less than 5.49 liters. This amount of material is less than a minimum critical volume (5.67 liters) assuming fully enriched, optimally moderated and fully reflected conditions. The maximum enrichment that could credibly be on the filters is 20% U-235. The material in the filters is bounded by UO2F2, and the likely moderation level is less than H/U=20. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The geometry control was lost. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Corrective actions are in progress and consist of performing walkdowns of all potentially affected facilities and then quantifying the material in any filters discovered through Non-Destructive Assay analysis. The NRC Resident Inspector and DOE Representative were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37307 | 0 | COMMONWEALTH OF KENTUCKY |  |  |  |  | 2000-09-11 06:00 | 2000-09-11 17:21 | 2000-09-18 | AGREEMENT STATE REPORT - STOLEN GAUGE "On September 11, 2000, Fuller, Mossbarger, Scot and May Engineers, Inc., reported a stolen moisture/density gauge. The gauge was a Troxler 3440, serial number 24606, containing an 8 millicurie cesium-137 and a 40 millicurie americium-241 source. "The gauge was stolen sometime between 12:00 am. and 6:00 a.m. on September 11 from an employee's residence located in Lexington, KY. The police have been notified. The employee had stored the gauge, in its transport container, in his garage. He put the gauge, in its transport container in the bed of his truck at about midnight in order to be ready to leave for the job Site the next morning. One of the owners of the company stated that the container was locked to the bed of the truck with a chain and padlock. The thief used a hacksaw to cut the chain and remove the transport container with the gauge inside. "The owner stated he believed the source rod to also be locked and that the employee would have still have the keys to this lock." * * * UPDATE 1133 9/18/2000 FROM VICKI JEFFS VIA FACSIMILE * * * "The gauge, Troxler 3440, S/N 24606, was found, undamaged, on the side of the road. The licensee now has possession of it. Licensee was cited for improper gauge storage." Notified R2DO (Cahill). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | KY | OTH | AGR |  |  |  |  | 0
37306 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-09-11 10:20 | 2000-09-11 13:53 | 2000-09-11 | ESF ACTUATION - CONTAINMENT ISOLATION VALVES During performance of procedure 34SV-SUV-026-1S, Primary containment Isolation valves Logic Sequence Functional Test , valves 1B21-F111 and 1B21-F112 (post accident reactor coolant containment isolation valves) were opened for prerequisites. When 1B21-F111 and 1B21-F112 were opened the 1B21-F051C EFCV isolated. 1B21-F051C is the EFCV (Excess Flow Check Valve) for jet pump #20 instrument piping. The isolation caused instrumented core flow, process computer flow and jet pump #20 flow to increase. Isolations were reset and 1B21-F051C was reopened at 1022 (It had closed at 1020). All indications returned to normal. The licensee will inform the NRC resident inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37305 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-09-11 11:45 | 2000-09-11 12:42 | 2000-10-06 | OUTSIDE DESIGN BASIS - STATION BATTERY CALCULATIONS An engineering review of voltage drop calculations for station battery systems (A & B) has identified an error in the assumed value for the current rating for the starting coil on the A & B ESW pump motor starter. The starting coil is actually rated for 44 amps vs. 6 amps as originally assumed. This discrepancy results in a calculated terminal voltage at the coil below that stated on the name plate. This condition is considered to be outside the design basis of the plant. The licensee notified the NRC resident inspector. * * * RETRACTION on 10/06/00 at 1059 ET by Abramski taken by MacKinnon * * * Subsequent testing has determined that there would in fact be sufficient terminal voltage at the starting coil of the A & B ESW Pump motor starters during a postulated Loss of Offsite Power. Therefore the plant was not outside its design basis and this event is being retracted. R1DO (Linville) notified The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37304 | -1 | LAKEHEAD PIPE LINE CO., INC |  |  |  |  | 2000-09-11 08:00 | 2000-09-11 11:20 | 2000-09-21 | REPORT INVOLVING POSSIBLE EQUIPMENT SAFETY DEVICE FAILURE THE LAKEHEAD PIPE LINE RADIATION SAFETY OFFICER (RSO), WAS INFORMED AT 0800 ON 9/11/00 THAT THE COUNTER ON A NUCLEAR DENSITY GAUGE HAD STOPPED WORKING SOMETIME IN MAY OF THIS YEAR AT THEIR LEWISTON STATION LOCATED IN LEWISTON, MICHIGAN. THE SOURCE IS IN THE SHIELDED AND LOCKED POSITION. THE DEVICE IS A MODEL 7400 MANUFACTURED BY BERTHOLD SYSTEMS CONTAINING A 350 MILLICURIE CS-137 SOURCE. * * * RETRACTED AT 1601 EDT ON 9/21/00 BY ROBERT POLLOCK TO FANGIE JONES * * * After discussion with NRC Region 3 (Geoffrey Wright), it was determined that this event was not reportable as the source was not involved, safely stored at all times, and the problem was only with the electronics. This event notification is retracted. The R3DO (Bruce Burgess) and the NMSS EO (John Greeves) has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN |  |  |  |  | 0
37303 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2000-09-10 21:23 | 2000-09-10 23:02 | 2000-09-11 | AUTOMATIC REACTOR TRIP DUE TO CLOSURE OF MAIN STEAM ISOLATION VALVES An automatic reactor trip/turbine trip occurred due to the spurious closure of both main steam isolation valves (MSIVs). The spurious MSIV closure was the result of a failed logic module in the engineered safety features actuation system (ESFAS). All control rods inserted following the trip, and all systems functioned as expected. The auxiliary feedwater (AFW) system automatically started as designed following the trip. The unit is currently stable in Hot Standby with decay heat being removed through steam released via the steam generator atmospheric dump valves. Steam generator water levels are being maintained by the AFW system. The licensee anticipates that replacement of the logic module and establishment of decay heat removal via the main condenser will occur within the next few hours. The NRC resident inspector has been informed of this event by the licensee. The licensee reported that nearby residents have contacted emergency services regarding the noises caused by the steam release through the atmospheric dump valves. The licensee plans to make a press release regarding this event. * * * UPDATE 0428EDT ON 9/11/00 FROM ROBERT PACE TO S. SANDIN * * * The MSIVs were reopened and the main condenser placed back in service at 0420EDT for decay heat removal. Preparations are underway to restore one main feedwater pump and secure the AFW system. Notified R1DO(Dimitriadis). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ESF ACTUATION | RPS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37302 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-09-10 16:28 | 2000-09-10 19:55 | 2000-09-10 | AUTOMATIC START OF TURBINE DRIVEN AUXILIARY FEEDWATER PUMP "At 1628 hours on 9/10/2000, with the reactor in Mode 5 for a refueling outage; Watts Bar engineering reported preliminary results of an investigation into the inadvertent start of the turbine driven auxiliary feedwater pump. At approximately 0200 hours on 9/10/2000, operators found the auxiliary feedwater pump operating without the presence of start signal. Steam generator level was being provided by previously started motor driven AFW pumps and operations secured the turbine driven pump. There was no impact from the event on plant refueling preparations and no safety consequence. "There was no valid AFW start signal in place at the time and plant conditions were not such that a signal was required. Engineering was requested to investigate the event and identified that at about the time of the pump start, maintenance technicians were working in an adjacent part of this rack where the relay believed to have been involved in the actuation is located. A review of the circuit determined that an inadvertent bump of the relay could result in the start of the pump and the independent actuation of turbine driven AFW steam generator level control valves. Based on this information, Operations concluded that based on the preliminary engineering information an invalid start of an ESF train had occurred and declared the event reportable under 10 CFR 50.72(b)(2)(ii) and 50.73(a)(2)(iv). "At the time the pump was found in operation it was known that there was no valid start signal, but it was thought that the issue involved only a single component. Because other S/G level maneuvers were in process independent of the AFW start, it was not recognized at the time that the level control valves were involved in the event. After the preliminary engineering review, it was concluded that although it was an invalid actuation, the event involved a train level actuation and was, therefore, reportable." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37301 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2000-09-09 18:30 | 2000-09-10 09:52 | 2000-09-10 | CONDITION OF LICENSEE REPORT INVOLVING A MONITOR WELL EXCURSION RESULTS OF SAMPLES REPORTED AT 1830MDT ON 9/9/00 CONFIRMED THAT FOUR PARAMETER SINGLE UPPER CONTROL LIMITS (UCLs) AND THE FIFTH MULTIPLE UCL WERE EXCEEDED IN SHALLOW MONITOR WELL SM6-12. PARAMETERS /UCLs/ MEASURED VALUES[UNITS] ARE: SODIUM /36/ 43 [milligrams/liter] SULFATE /19/ 85 [milligrams/liter] CHLORIDES /7/ 55 [milligrams/liter] CONDUCTIVITY /736/ 910 [microMHOs/cm] ALKALINITY /290/ 294 [milligrams/liter] THE LICENSEE WILL DISCUSS POSSIBLE CORRECTIVE ACTIONS WITH THEIR HYDROLOGIST AND GEOLOGISTS IN THE MORNING. THIS COULD INCLUDE DRILLING SAMPLE TEST WELLS. THE LICENSEE WILL NOTIFY THE NEBRASKA DEPARTMENT OF ENVIRONMENTAL QUALITY AND THE NRC PROJECT MANAGER. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | NE | OTH | GEN |  |  |  |  | 0
37300 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-09-08 20:00 | 2000-09-09 10:21 | 2000-09-21 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING SAFETY SYSTEM ACTUATION "On 9/8/2000 at 2000 hours a safety system actuation occurred in the X344 building. Autoclave #4 was in Mode II 'Heating' when the High Condensate Level Shutoff safety system actuated. Per TSR 2.1.3.7, the autoclave was placed in Mode VII 'Shutdown', a mode in which the High Condensate level Shutoff system is not required, and declared inoperable. This is being reported as a valid safety system actuation. An engineering evaluation has been initiated to review the system conditions that surrounded the actuation of the safety system." Operations notified both the NRC resident inspector and DOE site representative. * * * RETRACTED AT 2323 EDT ON 9/21/00 BY ERIC SPAETH TO FANGIE JONES * * * "RETRACTION: On 09/21/00, the Plant Shift Superintendent retracted the above Event. At the time of the High Condensate Level Shutoff (HCLS) system actuation, the autoclave was being cycled on and off in accordance with the applicable procedure for heating a Russian cylinder. Follow up investigation by engineering and operations has determined the HCLS actuation occurred while AC #4 was in Mode VII 'Shutdown'. "Discussions with building supervision and the operator who witnessed the HCLS actuation revealed the AC #4 had been shutdown as part of the on/off heating cycle before the actuation occurred. Based on the configuration of AC #4 at the time, the AC would have been in Mode VII 'Shutdown'. "Since the HCLS system is not required to be operable in Mode VII 'Shutdown', the HCLS system actuation was invalid, and is not reportable in accordance with 10CFR76.120(c)(2). Accordingly, this event is being retracted." The plant has informed the NRC Resident Inspector. The R3DO (Bruce Burgess) and NMSS EO (John Greeves) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37299 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-09-08 13:30 | 2000-09-08 15:39 | 2000-09-08 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE "At 1330 on 09/08/00, HPCI Flow Controller, 1E41-R612, was observed to be exhibiting erratic indication of flow. Flow indication was oscillating from 0 to >500 gpm with HPCI in its standby condition. Investigation is continuing." The NRC resident inspector will be informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37298 | 0 | SOUTHEAST MISSOURI STATE UNIVERSITY |  |  |  |  | 2000-06-12 | 2000-09-07 10:04 | 2003-02-13 | POTENTIAL PERSONNEL OVEREXPOSURE OF A CONTRACT EMPLOYEE AT SOUTHEAST MISSOURI STATE UNIVERSITY IN CAPE GIRARDEAU HOO NOTE: Information regarding the same event was reported to the NRC Operations Center on 09/01/00 by Engelhardt & Associates. (Refer to event #37282.) The licensee was advised by the NRC Region 3 Office to followup on the report made by Engelhardt & Associates because the work was performed on the Southeast Missouri State University Campus. The licensee is making this notification because they want to document that they are aware of this issue and that they agree with the Engelhardt & Associates report. Another reason for the report is that there may be an issue of who the responsible party is at this point in time. As a result of an NRC visit in February, Southeast Missouri State University discovered that a spill had occurred in the basement of Magill Hall. Accordingly, Engelhardt & Associates was contracted to perform several tasks including cleanup of the spill. At the time, the spill was thought to be minor, and the licensee has since found out that the spill was quite major. In addition to cleanup of the spill, Engelhardt & Associates was contracted to help the licensee get ready for a waste haul and help prepare a new Radiation Plan. An Engelhardt & Associates representative arrived on 06/12/00, and he worked in (and out) the basement of Magill Hall for 5 days. On 09/01/00, the NRC Region 3 Office (Kevin Null) notified the licensee that the Engelhardt & Associates employee had received a dose of 9 REM CEDE. As a result, the licensee is in the process of trying to arrange followup testing for the Engelhardt & Associates employee. The licensee has also hired another firm (SAIC) to cleanup some areas of Magill Hall because of a secondary spill that occurred quite some time ago. SAIC representatives have been on campus for a 1-week period already and are expected to return to the campus on 09/18/00. SAIC will also be handling the licensee's dose assessment. Call the NRC operations officer for licensee contact information. * * * UPDATE ON 2/13/02 FROM WALT LILLY TO MIKE RIPLEY /HOWIE CROUCH * * * Final bioassays and lung counts from individuals exposed during the above incident indicate that another individual had an intake of Am-241. This individual received an estimated intake of 9.4 nanocuries with a final dose assigned of 76 REM CDE to bone surfaces and 4.2 REM CEDE. The individual is undergoing chelation therapy at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2202(a)(1) |  |  |  | 0
37297 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-09-07 09:58 | 2000-09-07 10:01 | 2000-09-07 | EMERGENCY SIREN OUTAGE DUE TO A PLANNED ACTIVATION ANTENNA UPGRADE The following text is a portion of a facsimile received from the licensee: "The sirens covering the North Anna Power Station will be taken out of service for a planned upgrade to the siren activation antenna. This will occur between the hours of 1000 and 1300. Total outage time is approximately 15 minutes." "Nuclear Emergency Preparedness [personnel have] notified the Virginia Department of Emergency Management. Just prior to the outage, the State [Emergency Operations Center will notify the [five] local jurisdictions. They will also notify these jurisdictions in the [Emergency Planning Zone] when the system is returned [to] operable [status]." The licensee plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37296 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-09-06 16:21 | 2000-09-06 18:38 | 2000-09-06 | DURING SURVEILLANCE AN AUTOMATIC ISOLATION SIGNAL WAS GENERATED DUE TO MISSED SWITCH POSITIONING "Reactor Core Isolation Cooling (RCIC) system isolated during performance of Annual Leak Detection surveillance (06-IC-A-1003-02). Investigation revealed leak detection switches not in bypass during test. System responded as designed. ES1-F064 (Mn Steam isolation) and trip Throttle valve closed. System restored to standby." The licensee determined there was a missed step in the surveillance procedure. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37295 | 0 | R.D. ZANDE & ASSOCIATES |  |  |  |  | 2000-09-06 | 2000-09-06 15:45 | 2000-09-06 | TROXLER GAUGE DAMAGED BY TRUCK RUNNING OVER IT R.D. Zande and Associates (of Columbus, OH) was conducting a back scatter test on asphalt on State Route 220 in Kyser, WV when an asphalt truck backed over it. The gauge is a Troxler Model 3411 with a cesium source. The case was damaged , case cracked, and the extension rods were damaged. The source was extended at the time and not believed to be damaged. The source was recovered into the shielded position. The gauge will be transported to Cline Technical Services in Amanda, Ohio, will be wipe tested there and final disposition of the gauge will be determined. The company has contacted NRC Region 3 (John Madera and Sam Mulea). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 2 | WV | MAT | [5 empty] | 0
37294 | 0 | PHILIP MORRIS |  |  |  |  | 2000-06-01 | 2000-09-06 15:42 | 2000-09-06 | SHUTTER ON SCANNER DISABLED ON CONVEYOR LINE A small piece of lead fell off the inside of a shield for a sealed beam source which prohibited the full closure of the shutter on the source. There was no exposure to personnel and repairs will be made by Philip Morris. This was discovered on 6/1/00 during a normal inventory of sources. It wasn't known to be reportable until today. The scanner is used to monitor cartons for missing packs of cigarettes. It is manufactured by Industrial Dynamics, model FT14, with two 100 mCi Am-241 sources. The company also notified NRC Region 2 (Orysia Bailey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 30.50(b)(2)(ii) |  |  |  | 0
37293 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-06 08:45 | 2000-09-06 12:13 | 2000-09-06 | VITAL BUS SUPPLY BREAKER FOUND TO HAVE IMPROPER TRIP SETTING AFFECTING OPERABILITY "On August 29, 2000, at 0038 CDT, Unit 2 experienced a loss of power to Class 1 E 480v motor control center (MCC) E2C1. The power loss resulted in a loss of normal letdown in the Chemical Volume Control System and loss of other safety related loads. The MCC was re-energized at 0108 CDT and plant systems were restored to normal. "An investigation found the long time overload settings for the feeder breaker to MCC E2C1 to be one-half of the required values. The condition had existed since October 23, 1999, when the breaker was placed in service. At 0845 on September 6, 2000, this condition was determined to be reportable after completion of an engineering evaluation. The engineering evaluation determined that the breaker had a high potential for opening under accident conditions because of the improper settings. The condition was corrected on August 29, 2000, at 1806 CDT. The corresponding breakers in the other ESF trains and in Unit 1 were found to have the correct settings. "Some safety related equipment powered from the MCC was determined to have been inoperable since October 23, 1999, because opening of the breaker would have interrupted the equipment's ability to perform its design function. The duration of inoperability exceeded the Technical Specification allowed outage time for some systems, which include: - 1 of 3 trains of Essential Chilled Water (TS 3/4.7.14): inoperable essential chilled water pump 21C - 1 of 3 trains of Control Room Envelope HVAC (TS 3/4.7.7): inoperable makeup fan 21C - 1 of 3 Standby Diesel Generators (TS 3/4.8.1): inoperable emergency supply fan 21C (support system for SDG 23) "This condition is reportable under 10CFR50.73(a)(2)(i)(B) and notification is required within 24 hours by Section 2G of the Unit 2 Operating License (NPF-80)" The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
37292 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-09-05 18:10 | 2000-09-05 20:15 | 2000-09-19 | BOTH TRAINS OF RIVER WATER SUPPLY SYSTEM DECLARED INOPERABLE The licensee had a failure of the river water instrument air system at 1810 CDT, resulting in the loss of the automatic traveling screen control and the high screen differential level alarm function. With both automatic screen wash functions inoperable, both river water supply systems were declared inoperable. The systems were returned to operable at 1820 CDT when the alternate air dryer was placed in service, the problem being the air dryer that had been in service stopped passing air. The licensee notified the NRC Resident Inspector. * * * RETRACTION 1600 9/19/2000 FROM KARRICK TAKEN BY STRANSKY * * * "The DAEC is retracting event reports 37248 (8/24/00) and 37292 (9/5/00) that involved a loss of the River Water Supply (RWS) System's instrument air. These two 10CFR50.72(b)(2(ii) reports (an event or condition alone that could have prevented safety function fulfillment) were based on the initial determination that both loops of RWS System were inoperable, due, in part, to a Precaution and Limitation (P&L) contained in the system's Operating Instruction (OI-410). The loss of air had impacted a portion of the RWS screen wash support system. The P&L provides guidance on the screen wash subsystem's impact on RWS System operability. Follow-up engineering assessment has concluded that a loss of instrument air, by design, does not prevent the RWS system from fulfilling its intended safety function. The RWS system would have been capable of fulfilling its intended safety function during both events. "Technical Specification (TS) Bases 3.7.2 defines RWS subsystem operability as having, 'an OPERABLE UHS, one OPERABLE pump, and an OPERABLE flow path capable of taking suction from the intake structure and transferring the water to the RHRSW/ESW Stilling Basin in the pump house.' For both of the events, the only question regarding operability was that of the OPERABLE flowpath. The follow-up engineering assessment concluded that the flowpath remained operable. Actual river water flow, as indicated in the control room, was not impacted by the loss of instrument air throughout the (short) duration of these events. Also, there is no question regarding past or historical operability because the cause of the loss of air was related to air system modifications, which were in process at the time or the events. "Therefore, there was no event or condition alone that could have prevented safety function fulfillment. Once discovered, the appropriate TS action statements were entered. No TS 3.0.3. entry was made (or required to be made). There were no Operations or Conditions Prohibited by TS. No other reporting criteria apply to these events. These events are considered not-reportable under 10CFR50.72 or 10CFR50.73." Notified R3DO (Burgess). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
37291 | 0 | PALISADES | 1 |  |  | [1] CE | 2000-09-05 18:25 | 2000-09-05 19:19 | 2000-09-05 | PLANT SHUTDOWN REQUIRED PER TECHNICAL SPECIFICATIONS DUE TO POTENTIAL FOR LOOSE PARTS AFFECTING EMERGENCY CORE COOLING SYSTEM OPERABILITY The licensee was conducting radiography examinations and discovered at 1800 EDT that the internal parts of check valve CK-3332 are not in place. The valve is the common miniflow recirculation line check valve for train 'A' emergency core coolant system (ECCS) . A second radiography of the valve, at 1825 EDT, was inclusive in determining if all the parts are located in the valve body. Train 'A' ECCS was declared inoperable. Technical specification 3.0.3 was entered at 1901 EDT due to the possibility that loose parts may adversely affect the operability of other ECCS components and the plant has commenced shutdown. The licensee has notified the NRC Resident Inspector. | 98 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37290 | 0 | VA MEDICAL CENTER, |  |  |  |  | 2000-09-05 10:10 | 2000-09-05 10:20 | 2000-09-05 | SURFACE CONTAMINATION OF 6,300 DPM/100 CM² FOUND ON PACKAGE DELIVERED BY SYNCOR OF RALEIGH, NC. Radiation Safety Officer (RSO) for the VA Medical Center located in Durham, NC gave the following information. A metal ammo box containing Thallium-201 (cyclotron produced) delivered by Syncor to the VA Medical Center was found to have outside surface contamination levels as high as 6,300 disintegration per minute per 100 cm² on the opening lid of the ammo box. The RSO called Syncor and informed them of the surface contamination found on the ammo box lid. The RSO will take another reading in about 6 hours using a sodium iodide probe to make sure that the surface contamination is Thallium-201 instead of Technetium-99m, after which the ammo box will be placed in a store room to decay. The ammo box will be returned to Syncor after the outside surface contamination has decayed off. * * * UPDATE ON 09/05/00 AT 1059 ET BY FURR TAKEN BY MACKINNON * * * RSO Furr has determined that the surface contamination on the outside of the ammo box is Technetium-99m. R2DO (Mark Lesser) and NMSS EO (Brian Smith) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | [10 empty] | NON EMERGENCY | 2 | NC | MAT | [5 empty] | 0
37289 | -1 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-09-05 02:00 | 2000-09-05 05:42 | 2000-09-06 | "2B" AUXILIARY FEEDWATER (CA) PUMP RAN 2 HOURS AND 55 MINUTES BEFORE BEING DISCOVERED IT WAS OPERATING. STEAM GENERATORS WERE ISOLATED FROM THE AFW SYSTEM. At 0200 ET the "B" Train of the Solid State Protection System (SSPS) was deenergized for part of their refueling outage maintenance. When the SSPS was deenergized the blocks for the Main Feedwater Pump blocks cleared, which resulted in an automatic start signal to the "2B" AFW pump. The on shift reactor operator did not notice the "2B" AFW pump run light was on until 0455 ET due to refueling outage maintenance activities in Control Room. The "2B" AFW pump recirculated water to the Upper Surge Tank since the Steam Generators were isolated. No damage occurred to the AFW pump. The licensee is investigating this event. The NRC Resident Inspector will be notified of this event. * * * RETRACTED AT 1630 EDT ON 9/6/00 BY LARRY TUMBLESON TO FANGIE JONES * * * "Further investigation has determined that, prior to and during the automatic start, the 2B CA Pump had been properly removed from service. This was accomplished when valves that isolate flow from the pump to the Unit 2 Steam Generators were closed as a result of planned Unit 2 shutdown operations using plant procedures. In addition, the automatic start of the 2B CA Pump was not the result of a valid ESF actuation intended to mitigate the consequences of an event. Instead, the ESF actuation signal which started the pump upon reset of the SSPS relay was present because the MFP's were already off as a result of planned refueling outage shutdown operations. "Based upon the above, the September 5, 2000, automatic start of the 2B CA Pump occurred as a result of an invalid ESF actuation signal received while the pump was properly removed from service. Consequently, this is not reportable under the requirements of 10 CFR 50.72(b)(2)(ii) - Actuation of An Engineered Safety Feature (ESF) and NRC Notification 37289 is retracted. "The Resident Inspector has been notified." The R2DO (Mark Lessor) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37288 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-09-04 14:16 | 2000-09-04 15:30 | 2000-09-04 | INADVERTENT DEENERGIZATION OF THE '2A' RPS MG SET CAUSED GROUP 2 AND 5 ISOLATIONS Plant personnel inadvertently tripped breaker to the '2A' reactor protection system motor generator (RPS MG) set resulting in de-energization of the '2A' RPS bus. This resulted in the closure of the inboard Group 2 containment isolation valves, the inboard Group 5 reactor water cleanup valve, inboard reactor water sample valve, the control room ventilation swapped to the pressurization mode of operation, and a half scram in the 'A' RPS channel. All actuations have been reset and the '2A' RPS bus is energized from the alternate supply while an investigation is being conducted. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37287 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2000-09-04 11:32 | 2000-09-04 15:00 | 2000-09-04 | REACTOR TRIP DUE TO FIRE IN UNIT AUXILIARY TRANSFORMER At about 1132 CDT a fire was reported in the unit auxiliary transformer, alarms were received in the control room with a unit trip, all rods fully inserted. The on-site fire brigade and the off-site fire department were called to respond. The fire was extinguished by installed fire suppression equipment and declared out at 1143 CDT. The fire is being investigated by fire protection personnel. The off-site fire department was released. The plant is stable in Hot Standby at normal temperature and pressure. Heat removal is via the main condensers with steam generator level being maintained by auxiliary feedwater. The auxiliary feedwater system, both turbine and motor driven, started automatically on low steam generator level as expected with this event. All safety equipment performed as designed. Concurrent with the reactor trip, the 'C' and 'D' reactor coolant pumps tripped along with other loads due to one (PA02) of the two non-vital busses not automatically transferring as expected to off-site power. The bus is presently energized by off-site power and the 'D' reactor coolant pump was restarted. The actual cause of the problem is being investigating. One of the reactor coolant system power operated relief valve opened and closed one time due the transient of the 'D' reactor coolant pump trip and subsequent loss of pressurizer spray. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION | OFFSITE NOTIFICATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) | 50.72(b)(2)(vi) |  | 0
37286 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-09-03 15:10 | 2000-09-03 15:49 | 2000-09-03 | UNUSUAL EVENT - FIRE IN CONTAINMENT The licensee declared an unusual event at 1510 because of a fire in containment that lasted more than 15 minutes. A fire was reported at 1440 in a tarp that was being used in containment. The tarp is believed to have been ignited by some cutting or grinding going on in the vicinity. The licensee called for assistance from the local fire department, but they extinguished the fire before the fire company could assist. The fire was reported out at 1509. The unusual event was terminated at 1615. The reactor is defueled with all fuel having been moved to the spent fuel pool. No radioactivity was released. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a)(1)(i) |  |  |  | 0
37285 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-09-01 19:40 | 2000-09-01 21:08 | 2000-10-12 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE PLACING THE PLANT IN A 14 DAY LCO ACTION STATEMENT. During the performance of 8.5.4.1 (HPCI operability test), HPCI failed to meet acceptance criteria. The HPCI pump failed to meet the required flow, pressure and rpm requirements. Troubleshooting of the problem is in progress to make HPCI operable within the 14 day LCO action statement requirement. The NRC Resident Inspector was informed. * * * UPDATE ON 10/12/00 @ 1736 BY OLSON TO GOULD * * * RETRACTION After further analysis of this event, it was determined HPCI would have performed its safety function, therefore, this event is not reportable and is being retracted. The NRC Resident Inspector was notified. Region 1 RDO(Doerflein) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
37284 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2000-09-01 14:19 | 2000-09-01 18:49 | 2000-09-01 | REACTOR CORE ISOLATION COOLING SYSTEM RECEIVED AN ISOLATION SIGNAL DURING MAINTENANCE. Unit 2 was operating at 100% power. The Reactor Core Isolation Cooling System was removed from service for scheduled maintenance. Following valve packing adjustment, the Reactor Core Isolation Cooling system steam supply outboard isolation valve was opened per approved procedure. Approximately 10 seconds after the Reactor Core Isolation Cooling system steam inboard isolation bypass valve was throttled open for warming. "Division 2 Reactor Core isolation Cooling system steam line DP hi" and "Reactor Core Isolation Cooling system Steam Line/Turbine isolation" alarms were received. The Reactor Core Isolation Cooling system steam inboard isolation bypass valve automatically closed due to an isolation signal. The Reactor Core Isolation Cooling system remains isolated by the inboard isolation valves. The cause of the isolation signal is unknown at this time. An investigation is in progress to determine the cause of the isolation and initiate actions to restore the Reactor Core Isolation Cooling system to an operable and available status and exit the LCO action statement. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37283 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-09-01 11:30 | 2000-09-01 12:20 | 2000-09-01 | PLANT HAD CLOSURE OF THE POST ACCIDENT SAMPLING SYSTEM INBOARD PRIMARY CONTAINMENT ISOLATION VALVE During performance of Reactor Building Isolation LSFT (34SV-SUV-027-1S), 1E41-F122, Post Accident Sampling System Inboard PCIV, failed closed between approximately 1145 and 1230 on 08/31/00. 1E41-H22 was verified to be open at approximately 1145 following completion of channel A performance test (section 7.2). After returning from lunch break, operators observed 1E41-F122 closed and could not be reopened with control switch. The isolation has not been reset and they have also isolated the outboard valve by TS requirement. Investigation into cause of closure is continuing. During discussions with Nuclear Safety and Compliance Department at 1130 on 09/01/00 it was determined that this PCIV failing closed was a reportable ESF actuation. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37282 | 0 | ENGELHARDT & ASSOCIATES |  |  |  |  | 2000-06-12 | 2000-09-01 10:09 | 2000-09-01 | AN EMPLOYEE OF A RADIATION CONSULTING FIRM MAY HAVE RECEIVED A PERSONNEL OVEREXPOSURE ENGELHARDT & ASSOCIATES, INC. WAS HIRED BY SOUTHEAST MISSOURI STATE UNIVERSITY LOCATED IN CAPE GIRARDEAU, MO. TO ASSESS AND UPGRADE THE UNIVERSITY'S RADIATION SAFETY PROGRAM. SEVERAL YEARS BEFORE THE UNIVERSITY INFORMED THE NRC THAT A COUPLE OF AMERICIUM-241 SOURCES HAD BEEN REMOVED. DURING AN NRC RIII INSPECTION LATE LAST YEAR, THE SOURCES WERE FOUND ON CAMPUS. DURING THE CONSULTANTS ASSESSMENT, HE DISCOVERED THAT ONE OF THE SOURCES HAD BEEN SPILLED (LIQUID FORM) CAUSING A LARGER PROBLEM THAN INITIALLY BELIEVED. THE EMPLOYEE'S UPTAKE WAS DETERMINED BY ARGONNE NATIONAL LAB TO BE ON THE ORDER OF 9 REM CUMULATIVE DOSE EQUIVALENT. NRC REGION III (WRIGHT, JORGENSEN) WAS INFORMED BY ENGELHARDT. HOO NOTE: Information regarding the same event was reported to the NRC Operations Center on 09/07/00 by Southeast Missouri State University. (Refer to event #37298.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.2202(b)(1) |  |  |  | 0
37281 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-08-31 17:47 | 2000-08-31 21:32 | 2000-09-01 | PLANT ENTERED 72 HOUR LCO ACTION STATEMENT WHEN DIVISION III DIESEL GENERATOR WAS DECLARED INOPERABLE During performance of Fire Protection Surveillance 9337.81 (performs a functional check of the Division III Diesel Generator (DG) Carbon Dioxide (CO2) system operation), the Division III DG ventilation system tripped during restoration. Electrical Maintenance personnel were performing a functional check of the Division III DG room thermal detectors when the panel reset push button was depressed. The anticipated resets did not occur and the decision was made to restore the system to a safe condition. During restoration, a sticking relay prevented restoration of the Division III DG ventilation system. The relay has been reset and the ventilation system restored. Division III DG was declared INOPERABLE at 1747 and the plant entered LCO 3.8.1. Action B.1- Perform 9082.01 within 1 hour and every 8 hours thereafter. Action B.2- Declare required features supported by Division Ill DG inop when the redundant required features are inop, within 4 hours. Action B.3.1- Determine Operable DG are not inop due to common cause failure within 24 hours - This action -completed. Action B.4- Restore Div 3 DG to Operable within 72 hrs. Division Ill DG was declared OPERABLE at 1813 and the LCO was exited. The NRC Resident Inspector was notified.. * * * UPDATE ON 09/01/00 @ 1400 BY SHELTON TO GOULD * * * The time the diesel became inoperable was 1420 but it was not declared inoperable until 1747. This event is being reported pursuant to 10CFR50.72 (b)(2)(iii)(D) as a condition that alone could have prevented the fulfillment of the High Pressure Core Spray (HPCS) system, a single-train safety system needed to mitigate the consequences of an accident, since the Div. 3 DG is an essential support system for the HPCS system needed to mitigate a small break LOCA concurrent with a loss of offsite power. The NRC Resident Inspector will be notified. The Reg 3 RDO (Leach) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37280 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-08-24 08:38 | 2000-08-31 19:42 | 2000-08-31 | THE CONTROL ROOM EMERGENCY OUTSIDE AIR SYSTEM(CREOAS) FUNCTION IS DEFEATED WHEN THE CONTROL ROOM SMOKE REMOVAL FANS OPERATE. On August 24, 2000, Susquehanna Unit 1 was Operating at 100% power and Unit 2 was in Mode 2 at 0% power. Operations had placed the Control Structure (CS) Smoke Removal ventilation system in service aligned to the Control Room (CR) and Technical Support Center (TSC) areas to exhaust the foul odor created by welding on the CR ventilation duct as part of modification work. The CS Smoke Removal System was shutdown after personnel noticed a negative differential pressure was created in the CR and TSC areas. This mode of operation existed for 2 hours and 18 minutes. Subsequent review of the event on August 31, 2000 concluded that when the CR Smoke Removal fans operate, they act to defeat the function of the CREOAS fans which are intended to maintain the CS pressure positive. Maintaining a positive pressure in the CS assures that all air entering the CS has passed through the CREOAS filter train (thus assuring no air enters via infiltration). The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Startup |  | Power Operation | Startup |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37279 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2000-08-31 10:00 | 2000-08-31 10:55 | 2001-10-30 | 2 SETS OF CALIBRATION SOURCES DISCOVERED MISSING "At 10 AM on August 31, 2000 Global Nuclear Fuel - Americas determined that two sets of instrument calibration sources are missing following a thorough search. Each source set contains four metal disks electroplated with Pu-239, Total activity contained in both source sets is approximately 1.7 microcuries. The sources had been sent to a vendor for calibration re-certification. "The sources were unaccounted for during a routine source inventory at GNF-A. The vendor performing the calibration recertification last accounted for the sources when shipped on August 2, 2000. Records of the common carrier which transported the sources from the vendor to GNF-A indicate the material was shipped as an excepted package limited quantity and delivered to GNF-A on August 7. 2000. The inner packaging and each source are marked with radioactive warning labels. There is no measurable radiation dose rate from this type of package. A search of likely locations at GNFA has been conducted with negative results. "This event is reportable pursuant to 10CFR20.2201, 10CFR70.52 and 10CFR74.11. Efforts to locate the sources continue." The licensee intends to notify New Hanover County, North Carolina State Department of Radiation Protection, and NRC R2(Ayers). * * * UPDATE 1558 10/30/2001 FROM R. FOLEK TAKEN BY R. STRANSKY * * * On September 21, 2001, the licensee found the missing sources in the shipping and receiving warehouse. The sources were still in the origional shipping container and were undamaged. The sources have been placed into the licensee's inventory control system. Notified R2IRC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN LNM>10X | LOSS OF SNM/FISSILE | [8 empty] | NON EMERGENCY | 2 | NC | FUE |  | 20.2201(a)(1)(ii) | 70.52(b) |  |  | 0
37278 | 0 | U.S. AIR FORCE |  |  |  |  | 2000-08-30 14:00 | 2000-08-31 10:15 | 2000-08-31 | 4 MISSING EXIT SIGNS CONTAINING TRITIUM The licensee reported that 4 exit signs, 'Safety Sign' by SRB Technologies Inc., each containing 20 curies of tritium, were discovered missing and presumed stolen from building 1245. An investigation is underway and a report will follow in 30 days. The licensee notified NRC R4 (Gaines). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37277 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-08-30 16:10 | 2000-08-31 05:30 | 2000-08-31 | AREA CONTROL ROOM (ACR) ALARM POWER LOST DUE TO A FAILURE IN THE POWER TRANSFER SWITCH "At 1610 on 08-30-00 the PSS was informed of a C-331 CAAS Cluster J Trouble alarm. Investigation of trouble alarm revealed that C-331 CAAS Horns solenoids had lost DC power. The C-331 ACR DC alarm power was lost due to the failures in the power transfer switch. Contacts fused together and a solenoid failed which allowed the transfer switch to reposition to the mid (no power) position and prevented repositioning to the emergency power position. Since the CAAS horns did not have power, they were unable to perform the intended safety function, rendering the system inoperable for audibility. The system is required to be operable according to TSR 2.4.4.7.b for the current mode of operation. The horns were without power (inoperable) for approximately 30 minutes until the transfer switch was physically forced to the emergency power position. This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. The NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | EQUIP DISABLED/FAILS | REDUNDANT EQUIP INOP | [7 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) | 76.120(c)(2)(ii) | 76.120(c)(2)(iii) |  | 0
37276 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-08-30 15:05 | 2000-08-30 17:18 | 2000-08-30 | FAILURE OF A MAIN STEAM LINE DRAIN PRIMARY CONTAINMENT ISOLATION VALVE TO COMPLETELY OPEN DUE TO LOOSE TORQUE SWITCH WIRE CONNECTIONS The following text is a portion of a facsimile received from the licensee: "During plant shutdown, primary containment isolation valve MO-2373 failed to properly function. The failure was caused by loose torque switch wire connections which caused a failure of the valve to completely open. Improper electrical connections could have prevented full closure of the valve. Therefore, the valve was determined to be inoperable prior to the repair. ([The] valve has been repaired.) The safety function of the redundant primary containment isolation valve was available." The licensee plans to notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37275 | 0 | EATON CUTLER-HAMMER |  |  |  |  | 2000-07-31 | 2000-08-30 15:06 | 2000-08-30 | 10 CFR PART 21 NOTIFICATION REGARDING THE POTENTIAL FAILURE OF EATON-CUTLER-HAMMER DS-206 CIRCUIT BREAKERS TO CLOSE ON DEMAND The following text is a portion of a facsimile received from Eaton Cutler-Hammer Nuclear Programs personnel: "The following information is provided pursuant to the requirements of 10 CFR Part 21 to report a potential safety concern. This issue concerns the possibility for malfunction of the Eaton Cutler-Hammer DS-206 circuit breakers due to 'shock-out' of Direct Trip Actuators (DTA). Shock-out is defined as the unwarranted or undesired change in the state of a DTA from the normally un-tripped state to a tripped state. Shock-out occurs as a result of shock caused by the circuit breaker cycling from the open position to the closed position. The shock force is supplied by the closing springs striking the bottom plate of the breaker frame during the breaker closing operation. The result of shock-out is that the DTA trips immediately, returning the breaker to an open condition, which is neither required nor desired." "[Eaton Cutler-Hammer Nuclear Programs (C-HNP)] has determined that the root cause of DTA shock-out in DS-206 breakers is the replacement of operating mechanisms and/or closing springs with new operating mechanisms and/or new closing springs, as part of the standard reconditioning process. DTA shock-out has not been observed in vintage DS-206 breakers that are reconditioned in accordance with C-HNP procedures, which does not include the replacement of operating mechanisms and/or closing springs as part of the standard reconditioning process. The standard C-HNP reconditioning process DOES include installation of design upgrades." "To eliminate the possibility of shock-out, when the DS-206 breaker reconditioning process includes installation of a new operating mechanism and/or closing springs, C-HNP recommends the installation of a modified bottom plate to eliminate transmission of shock to the DTA. A modified bottom plate has been designed, [and] tested and is being seismically qualified by C-HNP." "This deficiency was identified and determined to be of a chronic reportable nature on approximately July 31, 2000." "The installed base of the C-HNP supplied operating mechanisms and closing springs is limited to a single utility and plant, Tennessee Valley Authority Sequoyah Nuclear Plant. C-HNP does not know where operating mechanisms and closing springs, procured commercially by third party dedicators, may have been installed in safety-related applications." (Contact the NRC operations officer for supplier contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0
37274 | 0 | QSL INSPECTION |  |  |  |  | 2000-08-29 14:00 | 2000-08-30 11:30 | 2000-08-30 | 30 CURIE IRIDIUM-192 SOURCE'S PIG TAIL DISCONNECTED FROM ITS DRIVE CABLE. Event was reported by the Radiation Safety Officer for QSL Inspection. Disconnect of a Sentinel Amersham 660 exposure device occurred in Bensalem, Pa., yesterday afternoon. After completing an exposure it was discovered that the source had become disconnected from its drive cable and it could not be retracted back to its storage position. The pig tail had become disconnected from the drive cable. The licensee shielded the source and retrieved it. Maximum reading of the radiographers pocket dosimetry devices was 130 mRem (the radiographers actual exposure in retrieving the 30 curie Ir-192 source was less than 130 mRem because he had been wearing the same pocket dosimetry devices during other radiography shots) . On investigation the licensee found that the drive cable selector ring was worn (connects the drive cable to the pig tail). The licensee has taken all of their 30 exposure controls and 27 devices out of service and is inspecting them for any problems. The licensee notified NRC Region 1, John Kinneman, of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2)(ii) |  |  |  | 0
37273 | 0 | U.S. ARMY |  |  |  |  | 2000-08-23 | 2000-08-30 10:01 | 2000-08-30 | MISSING M43A1 CHEMICAL AGENT DETECTOR The licensee reported that one M43A1 chemical agent detector, containing 250 µCi of Am-241, had been lost during a training exercise at Camp Shelby, Mississippi. The Alabama National Guard was conducting a class, removed the cell containing the chemical agent detector which apparently was not replaced. This was discovered when the assembly was sent in for the detector to be leak checked. An investigation has looked for the missing detector and is still looking for it. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37272 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-08-29 10:40 | 2000-08-29 13:28 | 2000-08-29 | OFFSITE EMERGENCY SIRENS INADVERTENTLY ACTUATED "At 1040 Central Daylight time the Atchison County Missouri emergency sirens were inadvertently actuated by State/Local officials during an Emergency Preparedness Drill. Local radio Stations were verbally notified of the false alarm, however an official press release is not planned at this time." State and Local officials were notified by the licensee of this event. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37271 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-08-29 11:00 | 2000-08-29 11:34 | 2000-08-29 | EMERGENCY SIRENS INOPERABLE "Loss of Offsite siren capability in Harnett County NC for greater than one hour for planned maintenance. On August 29, 2000, Harnett County was performing planned maintenance on the county primary repeater tower. This repeater is used to activate the Harris Plant offsite notification sirens in Harnett County. The primary repeater was taken out of service at 10:00 a.m. on August 29, 2000, and as of 11:00 a.m. had not been returned to service. The primary repeater is expected to be returned to service at approximately 1:00 p.m. on August 29, 2000. In case of an emergency occurring while the outage is ongoing, Harnett County is prepared to perform backup route alerting as necessary." The NRC resident inspector has been informed of this notification by the licensee. * * * UPDATE ON 08/29/00 AT 1519 ET BY JAMES ABRAHAM TAKEN BY MACKINNON * * * Harnett County Emergency Sirens were returned to service at 1510 ET. NRC R2DO (Haag) notified. The NRC Resident Inspector will be informed of this notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37270 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2000-08-28 11:00 | 2000-08-29 10:57 | 2000-08-29 | STOLEN MOISTURE/DENSITY GAUGE A CPM brand moisture/density gauge, model MC1DR, serial #MD9119207, was stolen from the back of a pickup truck in Columbus, Ohio. The gauge contains one 10 mCi Cs-137 source and one 50 mCi Am-241/Be source. The gauge and overpack were chained to the bed of the truck, but the chain was cut. The licensee has filed a report with the Columbus Police Department. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0
37269 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-08-29 03:15 | 2000-08-29 06:37 | 2000-08-29 | HPCI SYSTEM DECLARED INOPERABLE "While performing valve strokes for a normally scheduled High Pressure Coolant Injection (HPCI) surveillance test, the outboard suppression pool suction Primary Containment Isolation Valve (PCIV) to HPCI failed to stroke open. HPCI was declared inoperable. Investigation as to why the valve failed to stroke is in progress." The NRC resident inspector has been informed of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37268 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-08-28 15:29 | 2000-08-29 01:36 | 2000-09-09 | 24-HOUR NRC BULLETIN 91-01 REPORT "On 8/28/00 at 1529, during implementation of NCSA 0705_076 (Inadvertent Containers) a concern was raised about the maximum distance of spray from a leak from a pressurized pipe. Calculations were reevaluated and the corrected spray distance for the system in question resulted in a distance of 106 feet. This new distance for the system in question is greater than the original implementation distance of 15 feet, which the NCSA had previously predicted for the entire X-705. This is considered a loss of one control. The control considered lost is control #2 which states in part, 'When unattended all potential inadvertent containers shall be: -modified to prevent unsafe accumulation -covered to prevent the in-leakage of spilled materials -oriented to prevent an unsafe accumulation "The PSS(Plant Shift Superintendent) directed the facility custodian to enter an anomalous condition. The system in question was previously shut down prior to recalculation of the spray distance. The same equipment remains shutdown until compliance with NCSA 0705_076 can be determined. "SAFETY SIGNIFICANCE OF EVENTS: "Safety significance is low. The resulting situation is conservatively being identified as a violation of one control contained in NCSA 0705_076 which requires that all potential inadvertent containers utilized in the X-705 be modified, covered, or oriented to prevent an unsafe accumulation. However, since the system in question maintained its physical integrity and thus no uranium bearing material was involved the safety significance of this event is low. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "If a sufficient amount of uranium bearing material had leaked, spilled, splashed from the micro filtration system and the resuming material accumulated on/in an inadvertent container, an unsafe geometry could have resulted. If the leaking solution had contained a sufficient amount of uranium, the resulting configuration could have been sufficient for a criticality to occur. it should be noted that the allowed safe geometry and volume limits established in NCSA 0705-076 are based on optimally moderated solution which contains uranium enriched to 100 wt% U235. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): "The parameter which was violated during this upset was maintaining geometry/volume controls regarding potential accumulation points available on/in nearby inadvertent containers. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "No uranium-bearing material was actually involved in the upset. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "NCSA 0705_076 takes credit for the physical integrity of systems which contain uranium bearing materials. NCSA 0705_076 also takes Credit that unsafe volume/geometry containers are either modified, covered or oriented while in areas where uranium bearing material can leak, spill or spray to prevent an unsafe configuration from resulting in the event of a leak. The administrative control #2 was not being followed for the new area identified where uranium bearing materials can leak, spill or spray. The resulting situation is conservatively being identified as a violation of the administrative control in NCSA 0705_076. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "The PSS (Plant Shift Superintendent) directed the facility custodian to enter an anomalous condition. The system in question was previously shut down prior to recalculation of the spray distance. The same equipment will remain shutdown until NCS (Nuclear Criticality Safety) can assist in determination of operability of that system and compliance with NCSA 0705_076." The NRC resident inspector has been informed of this event. * * * UPDATE 1021EDT ON 9/9/00 FROM JEFF CASTLE TO S. SANDIN * * * "9/9/00 - Update #1 - An engineering evaluation (EVAL-PS-2000-0415) of the system and pumps associated with implementation of NCSA_0705_076 identified that the spray distances used to originally determine the reportability of this event were excessive. The original distance (15 feet) used to implement this NCSA has since been identified to adequately bound the credible scenarios for solutions spraying from various systems in the X-705. This issue would not have been reportable based on the newly acquired information as a result of the recent technical review." The NRC resident inspector and DOE site representative have been informed. Notified R3DO(Shear). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37267 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-08-28 13:10 | 2000-08-28 22:22 | 2000-08-28 | NRC BULLETIN 91-01 RESPONSE (24-HOUR REPORT) - LOSS OF ONE CRITICALITY CONTROL The following text is a portion of a facsimile received from Portsmouth personnel: "At 1310 on 08/28/00, during a self assessment in the X-710 room 229, it was discovered that the U-235 mass log was not verified as required by NCSA 710-022. NCSA 710-022 control #4 states in part, 'A log entry shall consist of the measured U-235 mass values plus analytical uncertainty and shall be verified by a second knowledgeable person or supervisor.' This is [considered] a loss of one control." "The PSS (Plant Shift Superintendent) directed the facility owner to enter an anomalous condition and directed NCS to oversee the recovery of the loss of one control." "The log in question was verified as required by NCSA 710-022. Control [was] regained[,] and [the] anomalous condition [was] exited within 4 hours." "[The] safety significance is low. The inventory log for the room showed 138 [grams] U-235. The allowable limit is 350 grams U-235." "SAFETY SIGNIFICANCE OF EVENTS: The safety significance is low. The inventory log for the room showed 138 grams U-235 with an enrichment of <5% present in the room. The total allowable mass for the room is 350 grams U-235." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): If the U-235 for the room was at the maximum allowable value, there would need to be an additional 456 grams U-235 present [in] the room before the critical mass for full reflection, optimum moderation, and spherical geometry was exceeded. For this amount of U-235 to be present, multiple errors in the log book would need to occur." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The control parameter for this operation is mass. NCSA-0710-022 places two controls on this parameter. The combined mass of all fissile material is limited to 350 grams U-235. The [NCSA] requires [that] a log of U-235 mass inventory be maintained to demonstrate that the mass limit is not exceeded. Each log entry consists of the [mass] value plus analytical uncertainty. A log entry is made by the person responsible [for] the movement of U-235 into the room and is verified by a second knowledgeable person." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): Approximately 138 grams [was] in the room [with] less than 5% U-235 solution." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: One of the controls on the mass parameter was not performed. A second knowledgeable person did not perform the log verification as required by [the] NCSA. The safety significance of the event is low due to the small amount of U-235 involved." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "A second knowledgeable person verified the current mass log. A [second] person verified today's log to ensure administrative correctness." Portsmouth personnel notified the NRC resident inspector and the Department of Energy site representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37266 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-08-28 16:30 | 2000-08-28 20:17 | 2000-09-08 | INOPERABILITY OF THE PASS AND BOTH DIVISION I/II H2O2 MONITORING SYSTEMS The following text is a portion of a facsimile received from the licensee: "On 8/28/2000, at 1630, [the Division] I and [II] Hydrogen/Oxygen (H2O2) Containment Monitoring Systems were declared inoperable. The Division I system was declared inoperable on 8/28/2000, at 0818, for planned maintenance. Subsequently, the Division II system was declared inoperable due to a failed channel check." "In addition, the Post Accident Sampling System (PASS) was previously declared inoperable. With the PASS and both Division I/II H2O2 Monitoring Systems inoperable, this event is reportable in accordance with 10 CFR 50.72(b)(2)(iii)(D)." "Also, on 8/28/2000, at 1905, the Division I H2O2 Monitor was restored to operable [status] following completion of planned maintenance." The licensee stated that the unit remained in a 30-day limiting condition for operation (LCO) and that a 7-day shutdown LCO was exited when the Division I H2O2 Monitor was restored to operable status. The licensee notified the NRC resident inspector. ***** UPDATE/RETRACTION AT 0024 ON 09/08/00 FROM ANTHONY PETRELLI TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "On 08/28/00, 1630 EDT, Nine Mile Point Unit 2 reported that Divisions 1 and 2 of the Hydrogen/Oxygen (H2/02) Containment Monitoring Systems were declared inoperable under Event Number 37266." "[The licensee is] retracting that notification based on the fact that the Division 1 H2/O2 monitoring system was removed from service as part of planned maintenance in accordance with approved procedures and plant Technical [Specifications]. During planned maintenance, a discrepancy was found in the Division 1 H2/O2 system. Subsequent evaluation indicated that the condition discovered would not have prevented the system from performing its safety function if called upon. Therefore, this event is not reportable." The licensee notified the NRC resident inspector. The NRC operations officer notified the R1DO (Dimitriadis). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37265 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-08-28 08:51 | 2000-08-28 17:31 | 2000-08-28 | UNEXPECTED CLOSURE OF A RESIDUAL HEAT REMOVAL SYSTEM OUTBOARD SUCTION ISOLATION VALVE The following text is a portion of a facsimile received from the licensee: "During preparation to place the 'A' side residual heat removal system (RHR) into the shutdown cooling mode, it was discovered that the outboard suction isolation valve (10MOV-17) had gone closed. Previous to this evolution, both the 'A' [and] 'B' recirculation pumps were shut down. It is suspected that securing the [recirculation] pumps causes a pressure surge in the suction piping to the RHR system which causes a pressure switch to actuate. This pressure switch causes [valve] 10MOV-17 to go closed. No reactor pressure instruments indicated a pressure surge. Initial assessment determined that this event was not reportable. Upon subsequent review, it was determined that a [4]-hour notification should have been made." The licensee stated that no alarms were received. A panel operator noticed that the valve had gone closed while verifying the system lineup before starting a pump. The 'A' side RHR system was subsequently placed in shutdown cooling, and everything operated properly. It was also reported that the event occurred at 0851 on 08/28/00 and that the event was determined to be reportable at approximately 1630 on the same day. In addition, the licensee stated that similar events had previously occurred. The licensee notified the NRC resident inspector. (Refer to event #31648 dated 01/24/97, #25534 dated 05/19/93, #25231 dated 03/11/93, #25134 dated 02/25/93, #24447 dated 10/17/92, #18770 dated 06/26/90, #18330 dated 04/25/90, #18325 dated 04/24/90, #18183 dated 04/09/90, #18026 dated 03/20/90, and #17598 dated 01/20/90 for events involving closure of shutdown cooling suction/isolation valves for various [possibly similar] reasons.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37264 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2000-08-28 11:00 | 2000-08-28 13:16 | 2000-08-28 | MEDICAL MISADMINISTRATION INVOLVING AN INITIAL UNDERDOSE OF IODINE-131 BECAUSE ONE OF TWO CAPSULES GOT STUCK IN A VIAL AT VA MEDICAL CENTER IN ALBANY, NEW YORK On 08/09/00, a patient was scheduled to receive a prescribed iodine-131 dose of 5 mCi in order to facilitate a whole body scan. A nuclear medical technologist measured the applicable vial at 5 mCi and emptied the contents of the vial for administration to the patient. Apparently, only one of two capsules came out of the vial, and the patient was given only one capsule which represented 1.1 mCi of the prescribed 5-mCi dose. The nuclear medical technologist identified the error approximately 1 hour after the initial administration. The patient was immediately contacted but was unable to return to the Medical Center that day. The patient received the second capsule (3.68 mCi) on the following morning (08/10/00) approximately 21 hours after administration of the first capsule. It was reported that there were no negative impacts on the outcome of the scan, no adverse health affects to the patient, and no health and safety concerns. The licensee did not believe that this event represented a medical misadministration but discussed the event with the NRC Region 1 office (Jim Dwyer). At approximately 1100 on 08/28/00, the NRC Region 1 office notified the licensee that this issue was considered to be a medical misadministration. Therefore, at 1316 on 08/28/00, the VA's National Health Physics Program reported this event to the NRC Operations Center for the VA Medical Center in Albany, New York. (Call the NRC operations officer for the VA's National Health Physics Program contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | NY | HOS |  | 35.33 |  |  |  | 0
37263 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2000-08-27 | 2000-08-27 18:07 | 2000-08-27 | AGREEMENT STATE REPORT OF A POTENTIAL OVEREXPOSURE TO MEMBER OF THE PUBLIC Testing Technology Inc. (TTI) was conducting radiographic slab inspections with a 47 Ci Co-60 source at 1100 L Street in northwest Washington, DC. Right after a 'shoot' a gentleman walked out of the office next door; he had gone in to do some work in his office. The individual said he had seen no warnings or postings when he had entered his office area. A reenactment by TTI after the area was clear indicated a field of 200 mrem/hr with an estimated exposure to the individual of 16 mrem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | DC | OTH | AGR |  |  |  |  | 0
37262 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-08-27 10:37 | 2000-08-27 13:21 | 2000-08-27 | NOTIFICATION TO THE NATIONAL RESPONSE CENTER OF A CHLORINE RELEASE TO THE JAMES RIVER The licensee discovered an overflowing containment dike around the sodium bromide tank for the circulating water chemical treatment system at about 0640 EDT on 8/27/00. The rate of flow was estimated at about 0.5 gpm. The overflow was to the storm drain system then to the discharge canal and ultimately the James River. There is no discharge limit on sodium bromide. The licensee pumped the containment area down to stop the overflow and placed absorption rags around the storm drain. At 0935 EDT the licensee investigating the source of the overflow found that a discharge hose on a sodium hypochloride pump, located in the sodium bromide tank area, had come loose and the source of the overflow. The discharge limit for sodium hypochloride is 13.6 gallons. The licensee estimated approximately 380 gallons had actually been discharged, based on storage tank level decrease and the rain water level in other containment dikes. The licensee notified the National Response Center (incident report #540082) and the State Department of Emergency Services (DES) at 1037 EDT. The National Response Center notified the US Coast Guard and the State DES notified the State Department of Environmental Quality. The licensee intends to notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37261 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2000-08-26 15:39 | 2000-08-26 22:37 | 2000-08-26 | AUTOMATIC REACTOR TRIP DUE TO UNEXPECTED CLOSURE OF ALL MAIN STEAM ISOLATION VALVES "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On August 26, 2000, at approximately 15:39 MST Palo Verde Unit 2 experienced an automatic reactor trip (RPS actuation) from approximately 100% rated thermal power due to pressure exceeding the high pressurizer pressure reactor trip setpoint. The high pressure resulted from the closure of all main steam isolation valves (MSIVs) coincident with the annunciation of a loss of 'A' train power to the MSIV control cabinet. The unit was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. No ESF actuations occurred and none were required. An investigation has commenced to determine why the MSIVs closed. "Due to the MSIV closure, main steam safety valves lifted for a short period. Operators restored reactor coolant system heat removal using atmospheric dump valves and the main steam safety valves reseated. Feedwater to the steam generators was initiated using the 'B' motor driven essential auxiliary feedwater pump and is now maintained by the 'N' motor driven non-essential auxiliary feedwater pump. "Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. Power distribution for one of the two non-safety buses did not automatically transfer to offsite power. Condenser vacuum was lost and has not yet been restored, thus heat removal remains via the atmospheric dump valves. Unit 2 Operations entered LCO 3.4.17(A) for RCS specific activity greater than 1.0 µCi/gm. No other significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event nor contributed to the event. "Unit 2 is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to the fission product barrier. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "Steam generator tube leakage was approximately 0.07 gpd prior to the reactor trip, (0.047% of the technical specification limit. "RCS dose equivalent iodine was approximately 4.28E-02 µCi/gm prior to the reactor trip. (4.28% of the technical specification limit.) "The first post-trip RCS dose equivalent iodine sample indicated 2.06 µCi/ml. "RCS chemistry continues to be monitored." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37260 | 0 | US STEEL, GARY WORKS |  |  |  |  | 2000-08-26 03:00 | 2000-08-26 10:14 | 2000-08-26 | TWO NUCLEAR GAUGES DISPLACED ON MANUFACTURING LINE Two nuclear gauges (2061T and 2061B) were displaced from their mountings on the #6 East galvanizing line when a strip of sheet steel broke. These gauges are both Nucleonic Data Systems model 200 devices, each containing 2.001 Ci of Am-241. The sources are generally licensed under Valmet license GA458-3G. The gauges came to rest on a roll of steel approximately one foot from their mounting positions. A health physics consultant responded to the site and performed surveys and wipe samples, but no damage or leakage was detected. A full investigation of the event is currently being conducted. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT | [5 empty] | 0
37259 | -1 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-08-25 17:30 | 2000-08-25 18:16 | 2000-09-05 | PHYSICAL SECURITY REPORT Potential tampering event, immediate compensatory measures taken upon discovery. Contact the NRC Operations Center for additional details. The licensee intends to notify the NRC Resident Inspector and the R2 Security Inspector (Dave Thompson). * * * RETRACTED AT 1206 EDT ON 9/5/00 BY VERIDA BELLAMY TO FANGIE JONES * * * After investigation it was determined that during a planned work activity workers manipulated the wrong component and it was not tampering. Therefore, this event notification is retracted. There will be no written followup to this event. The licensee notified the NRC Resident Inspector. The NRC Operations Center notified the R2DO (Caudle Julian) and IAT (John Davidson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 0
37258 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 1999-09-14 | 2000-08-07 18:22 | 2000-08-25 | AGREEMENT STATE REPORT "During a routine inspection of Zeneca Ag Management, the licensee informed an inspector from the California Radiation Control Program that someone may have intentionally contaminated areas in laboratories B200, B202 and B204 in building 96. After becoming aware of the incident on 9/14/1999, the licensee changed the locks for the storage location of the carbon-14, installed locks on all other refrigerators, and performed bioassays of personnel who worked in these laboratories. All bioassay results were negative. No further facility contaminations occurred." The release of this report was delayed for investigative reasons. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37257 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2000-08-25 | 2000-08-25 12:31 | 2000-08-25 | LEAK IN PRIMARY LINER The company had high conductivity on the monitor for primary liner leak detection for a settling pond for ion exchanger backwash. The pond mainly contains brine with some residual uranium. An investigation discovered a previously repaired tear had reopened, the tear is located about 3 feet above the water level. It is thought that wind action formed waves were the source of the water. There is no indication of leakage past the secondary liner. The company plans to continue inspecting the primary liner and will lower water level further to make repairs. The company contacted the Nebraska Department of Environmental Quality. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
37256 | 0 | NORTHWOOD PANELBOARD |  |  |  |  | 2000-08-25 05:00 | 2000-08-25 11:05 | 2000-08-25 | TRACTOR TRAILER TRUCK CARRYING 8 SEALED SOURCES OVERTURNED ON HIGHWAY. Licensee, Northwood Panelboard, located in Solway, MN reported the following event. Northwood Panelboard was shipping 8 sealed source holders, each containing 100 mCi of Cs-137, in two boxes to Radiation Technology located in Odessa, Texas. Vitran Express, the shipping company, informed Northwood Panelboard that the shipping tractor trailer had been involved in an accident on a major highway outside of Mauston, Wi. The tractor trailer is lying on its side blocking traffic. Four sealed source holders are contained in each padlocked crate. The crates are type A packages with a transportation index of 0.1. Wisconsin HAZMAT team has been dispatched to the seen of the accident. NRC Region 3 (Darrel Wiedeman & Robert Gattone) were notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | TRANSPORTATION EVENT | [9 empty] | NON EMERGENCY | 3 | WI | TRA | [5 empty] | 0
37255 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2000-08-22 12:00 | 2000-08-25 10:29 | 2000-08-25 | POSSIBLE OVEREXPOSURE AGREEMENT STATE REPORT Kansas Department of Health & Environment faxed the following information: "On 08/24/00 at 5 pm this office received a call from Labette Med Center reporting that a nuclear medicine technologist had received an exposure reported by their dosimetry vendor of 8263 mR whole body. "Preliminary Investigation by the dosimetry vendor indicates a possibility of the exposure being to the badge and not the individual. Their Investigation is ongoing. "Labette Med Center has performed blood work and a thyroid profile on the individual and results will be provided when available." The State of Kansas Event Number for this report is KS000018. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0
37254 | -1 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-08-24 20:30 | 2000-08-24 21:22 | 2000-09-15 | CONTROL ROOM VENTILATION NOT ALIGNED PROPERLY FOR TOXIC CHEMICAL DELIVERY The licensee reported that they were potentially outside of design license basis for the receipt of hazardous/toxic chemicals, specifically ammonium hydroxide 15 % by weight. A delivery truck arrived at the site and was admitted to the protected area before the proper alignment was made for receipt. The control room was contacted, but the alignment of control room ventilation was not completed prior to admitting the truck. The control room ventilation has been placed in full recirculation for chemical receipt at this time. The total time ventilation was not properly aligned is not available at this time. The licensee intends to notify the NRC Resident Inspector. * * * UPDATE AT 2345 EDT ON 8/24/00 BY VAN FORD TO FANGIE JONES * * * The licensee reported there were no spills or discharges during the offloading process and there was no risk to onsite or offsite personnel at any time. The chemical unloading procedure contains all requirements for personal protective equipment and appropriate precautions. The chemistry department procedure for chemical delivery may be in conflict with Salem UFSAR requirements (Section 2.2.3.3), Hazardous Chemicals - Offsite. Station personnel are evaluating the issue. The licensee intends to notify the NRC Resident Inspector. The NRC Operations Officer notified the R1DO (Christopher Cahill). * * * RETRACTION AT 1412 ET ON 09/15/00 BY FRANK SOENS TO JOHN MACKINNON * * * An assessment of the consequences of a postulated failure of the ammonia tanker with the control room ventilation system being in its normal mode of operation results in a maximum Salem control room concentration of approximately 2.11 ppm which is less than the 100 ppm limit of Reg Guide 1.78. Salem was within the design basis for the given situation, therefore, this event is being retracted. R1DO (Jim Trapp) notified. The NRC Resident Inspector was notified of this event retraction by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37253 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-08-24 04:35 | 2000-08-24 05:27 | 2000-09-06 | SMOKE AND SMALL FLAMES FROM "B" REACTOR FEED PUMP (RFP) OUTBOARD BEARING. FIRE LESS THAN 15 MINUTES. Control room plant received a high bearing temperature alarm from the "B" RFP. Plant personnel were dispatched to investigate. Smoke and small flames were seen around the outboard bearing of "B" RFP. Onsite fire brigade was dispatched to extinguish the fire. Fire brigade was unsuccessful in extinguishing the fire using carbon dioxide. Fire was extinguished using a fire hose. No other electrical systems were wetted by the fire hose. Reactor power was reduced from 100% to approximately 53% power at which time the "B" RFP was taken out service. A reflash fire watch is stationed at the "B" RFP. Lagging has been removed from the RFP and the lagging where the smoke and fire issued from is oil soaked. Investigation of fire is in progress. Unnecessary personnel were evacuated from the area of the fire. "B" RFP is located in the Turbine Building lower level (252'). All Emergency Core Cooling Systems are fully operable except for HPCI (see event # 37252). Offsite electrical grid is stable. No offsite site help was needed. Fire lasted from 0435 ET until 0449 ET. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED AT 1348 EDT ON 9/6/00 BY BOB STEIGERWALD TO FANGIE JONES * * * "This notification retracts an earlier report made on 08/24/00, at 05:27 (EDT), per 10CFR50.72(b)(1)(vi). A fire was reported at the outboard bearing of the 'B' Reactor Feed Pump. The fire was minor in nature, limited to the 'B' feed pump room, extinguished within 15 minutes of discovery, and did not hamper the ability of personnel to perform safety-related activities affecting plant safety. Reactor power was reduced and the 'B' feed pump was removed from service. Therefore, this event notification is being retracted." The licensee notified the NRC Resident Inspector. The R1DO (Anthony Dimitriadis) was notified. | 53 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INTERNAL THREAT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(vi) |  |  |  | 0
37252 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-08-23 14:15 | 2000-08-24 02:28 | 2000-08-24 | BOTH DIVISIONS OF CORE SPRAY AND HPCI RENDERED INOPERABLE. During a walkdown of equipment required to be environmentally qualified, plant staff identified electrical circuits which do not conform to the requirements of 10 CFR 50.49. These circuits control the minimum flow motor operated valves for both divisions of Core Spray and HPCI (High Pressure Coolant Injection). This condition rendered both divisions of Core Spray and HPCI inoperable. Technical Specification Limiting Condition of Operation for Core Spray and HPCI were entered. This condition therefore constitutes a condition that alone could have prevented Core Spray and HPCI from removing decay heat. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
37251 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2000-08-23 15:00 | 2000-08-23 18:22 | 2000-09-21 | - ECC SYSTEM MOV MAY NOT CLOSE DURING A LOCA AND A LOOP AS REQUIRED - While reviewing motor operated valve (MOV) data from December, 1999, plant staff personnel identified an error in the analyzed data for the closing torque for an MOV in the Emergency Closed Cooling (ECC) System that is required to close during a Loss of Coolant Accident (LOCA) and a Loss of Offsite Power (LOOP). The valve, #OP42-F0295B, isolates the ECC System from the Nuclear Closed Cooling (NCC) Water System. A second isolation valve, #OP42-F0290, was subsequently found to have insufficient data to ensure that it alone would have provided the required isolation. Failure of both valves to potentially not close completely could cause the ECC System to transfer the system's cooling water inventory via the NCC Water System to the Intermediate Building resulting in the loss of cooling capability of the ECC System. This would result in the loss of cooling capability for the systems required to support the Residual Heat Removal (RHR) 'B' and 'C' Subsystems. The #F0290 valve has been successfully tested to ensure that it has adequate torque to close under accident conditions; however, there is insufficient leakage test data available on this valve at this time. Therefore, assuming that valve #F0290 leaks and valve #F0295B does not fully close, a total loss of inventory would potentially occur for Division 2. Therefore, this condition is being conservatively reported to the NRC as a loss of safety function during a past outage which removed RHR 'A' from service, until further evaluation is completed. Valve #OP42-F0295B has been electrically closed under static flow conditions to ensure continued operability of the ECC System. Licensee planned actions include further evaluation of past test data or performance of a specific leak test on valve #OP42-F0290 and further evaluation of data on valve #OP42-F0295B. The licensee notified the NRC Resident Inspector. * * * RETRACTED AT 1622 EDT ON 9/21/00 BY MICHAEL McFARLAND TO FANGIE JONES * * * "A 10 CFR 50.72, four (4) hour non-emergency notification was initially made on 8-23-2000, due to Emergency Closed Cooling Loop B inoperability subsequent to valve OP42-F0295B inoperability, due to inadequate closing torque under dynamic flow conditions concurrent with an outage on the alternate, Division 1, equipment. it was indeterminate at that time if sufficient torque existed for the valve to close under accident conditions. "Subsequent to the event notification, the valve has been tested under dynamic flow and reevaluated. This information has resulted in a determination that the OP42-F0295B valve has been, and continues to be, operable under both normal and accident conditions. "Since the valve was determined to have been continuously operable, no Technical Specification Required Actions were exceeded and both loops of ECC remained operable. This event was determined not reportable and ENF 37251 is retracted." The licensee notified the NRC Resident Inspector. The R3DO (Bruce Burgess) was notified. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(D) |  |  | 0
37250 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-08-23 16:04 | 2000-08-23 16:57 | 2000-08-23 | - PUBLIC NOTIFICATION SIRENS INOP FOR 20 MINUTES DUE TO TRIPPED POWER SUPPLY BREAKER - At 1604 on 08/23/00, the licensee was notified that the Saint Lucie public notification sirens were inoperable from 1445 to 1505 due to a tripped power supply circuit breaker. The sirens are now fully operable. All other emergency notification system, emergency assessment, and state notification equipment remained operable during this event. The licensee is investigating the cause of the tripped breaker. The licensee notified local officials and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37249 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-08-23 15:10 | 2000-08-23 16:31 | 2000-08-23 | - MD Department of Environment to be notified of high coliform levels in visitor's center domestic water system - The licensee plans to notify the Maryland Department of Environment that high coliform levels were discovered in the Calvert Cliffs visitor's center domestic water system. The licensee isolated the system and provided portable water to the visitor's center. The licensee plans to re chlorinate the water system and resample the system prior to restoring it to service. The licensee plans to notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37248 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-08-23 02:30 | 2000-08-23 05:14 | 2000-09-19 | BOTH RIVER WATER SUPPLY SYSTEMS WERE DECLARED INOPERABLE. At 0230 the River Water Supply (RWS) instrument air system failed resulting in an invalid low RWS pit level alarm. Operators restored system air pressure at 0243. The loss of instrument air pressure also resulted in the loss of automatic traveling screen control and the screen high differential level alarm function. Because both of the automatic traveling screen wash systems were inoperable, both RWS systems were declared inoperable for the 13 minute duration. Failure of both systems resulted in a loss of safety function (supplies water to the Residual Heat Removal Service Water Pumps and the Emergency Service Water System). The licensee entered the applicable Technical Specifications for the loss of the RWS system. A new air dryer was installed recently and when the operator cycled the power supply to the air dryer it hung up. This caused the Instrument Air blockage. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1102 FROM BRIAN VOSS TAKEN BY STRANSKY * * * The licensee made the following corrections to the event report: (1) the operator cycled the power supply to the compressor after it stopped, not before, as noted above; and (2) there was no instrument air blockage, as stated above. Notified R3DO (Hiland). * * * RETRACTION 1600 9/19/2000 FROM KARRICK TAKEN BY STRANSKY * * * "The DAEC is retracting event reports 37248 (8/24/00) and 37292 (9/5/00) that involved a loss of the River Water Supply (RWS) System's instrument air. These two 10CFR50.72(b)(2(ii) reports (an event or condition alone that could have prevented safety function fulfillment) were based on the initial determination that both loops of RWS System were inoperable, due, in part, to a Precaution and Limitation (P&L) contained in the system's Operating Instruction (OI-410). The loss of air had impacted a portion of the RWS screen wash support system. The P&L provides guidance on the screen wash subsystem's impact on RWS System operability. Follow-up engineering assessment has concluded that a loss of instrument air, by design, does not prevent the RWS system from fulfilling its intended safety function. The RWS system would have been capable of fulfilling its intended safety function during both events. "Technical Specification (TS) Bases 3.7.2 defines RWS subsystem operability as having, 'an OPERABLE UHS, one OPERABLE pump, and an OPERABLE flow path capable of taking suction from the intake structure and transferring the water to the RHRSW/ESW Stilling Basin in the pump house.' For both of the events, the only question regarding operability was that of the OPERABLE flowpath. The follow-up engineering assessment concluded that the flowpath remained operable. Actual river water flow, as indicated in the control room, was not impacted by the loss of instrument air throughout the (short) duration of these events. Also, there is no question regarding past or historical operability because the cause of the loss of air was related to air system modifications, which were in process at the time or the events. "Therefore, there was no event or condition alone that could have prevented safety function fulfillment. Once discovered, the appropriate TS action statements were entered. No TS 3.0.3. entry was made (or required to be made). There were no Operations or Conditions Prohibited by TS. No other reporting criteria apply to these events. These events are considered not-reportable under 10CFR50.72 or 10CFR50.73." Notified R3DO (Burgess). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37247 | 0 | MIDWEST INSPECTION SERVICES |  |  |  |  | 2000-08-22 15:00 | 2000-08-22 17:30 | 2000-08-22 | - FILM BADGE WITH HIGH READING FOR JULY, 2000 MAY HAVE BEEN TAMPERED WITH - On 07/24/00, an employee resigned from Midwest Inspection Services, Oak City, OK. The individual's film badge for the month of July, 2000, was sent to Landauer Company for processing. At 1500 CDT on 08/22/00, Landauer reported to Midwest Inspection Services that the badge read 710 Rem for the month of July, 2000. Mr Ezzell, Midwest Inspection Services, feels that the film badge reading is incorrect and that the badge may have been tampered with possibly by a disgruntled employee who also resigned from Midwest Inspection Services in July, 2000. Blood samples of the first individual will be taken on 08/23/00 and his red and white blood cells will be counted. Mr Ezzell notified NRC Region 4 Mark Shaffer and plans to continue to investigate this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 4 | OK | OTH | GEN | 20.2202(a)(1) |  |  |  | 0
37246 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-08-19 | 2000-08-22 15:10 | 2000-08-22 | AGREEMENT STATE REPORT: LOST PORTABLE MOISTURE DENSITY GAUGE This notification of an event in Washington state as reported to the WA Department of Health, Division of Radiation Protection. (WA Event Report #WA-00-039) Date of event: August 19, 2000 Licensee: Columbia Asphalt & Gravel City and state: Yakima, WA License number: WN-10440-1 Type of license: Portable Gauge Location of Event: Toppenish, WA ABSTRACT: Tired and exhausted after a 60 hour work week, the gauge operator packed up and headed for home. The next morning when he went out to his van, parked in a secured lot, he discovered that the van was unlocked and the gauge transport box was open. The Campbell Pacific Model MC3 was missing. He called the police to report it stolen and called the Division's emergency number. The Division provided him instructions on issuing a press release and suggested offering a reward. The gauge operator also drove back to the job site to double check that he had not inadvertently left the gauge behind. No one was working at the site on August 20, 2000, and he did not find the gauge. On Monday, August 21, 2000, the gauge operator reported that the gauge had been returned to him by the "flaggers". One of the employees of the traffic control contractor at the site was familiar with portable gauges and realized that the gauge operator had inadvertently drove off without the gauge at the end of work on Saturday. The flagger secured the gauge and notified the gauge operator immediately at the start of the next workday. The gauge was returned safely and this case is closed for purposes of reporting to NRC. What is the notification or reporting criteria involved? WAC 246-221-240 Activity and isotope(s) involved: 10 millicuries Cs-137; 50 millicuries Am-24 1/Be Lost, Stolen or Damaged? Campbell Pacific, Model MC3, S/N M370803865 Disposition/recovery: Recovered Status: Closed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | MAT | [5 empty] | 0
37245 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-08-21 18:00 | 2000-08-21 19:33 | 2000-08-22 | OFFSITE NOTIFICATION REGARDING OIL SPILL ONSITE "Oil was discovered covering the gravel over an approximate 1 meter diameter area. The area was located under vent pipe for the main turbine generator air detraining tank on the turbine building roof." The NRC resident inspector will be notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37244 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-08-21 15:31 | 2000-08-21 17:53 | 2000-08-21 | - MANUAL REACTOR SCRAM FROM 100% POWER DUE TO REDUCED MAIN CONDENSER VACUUM - At 1531(CDT) on 08/21/00 with the plant in Operational Condition 1 at 100% power, the operating crew inserted a manual reactor scram signal due to the inability to maintain main condenser vacuum greater than 25 inches Hg. Prior to this condition, the operating crew was responding to a low flow condition in the in-service offgas system train in accordance with alarm response procedures. While admitting air to the offgas system train as directed, a low main condenser vacuum condition occurred, requiring the operators to insert a manual reactor scram signal. All control rods inserted completely. No safety/relief valves lifted. Steam is being dumped to the main condenser. Subsequent to the reactor scram, a reactor vessel low water level 3 signal was received, as expected, which resulted in an ESF isolation of the suppression pool cooling system. The suppression pool cooling system was in the suppression pool cooling mode at the time of the isolation. The reactor vessel water level has been restored to its normal level. Following the reactor scram, all systems functioned as expected. The plant is stable in Operational Condition 3 (Hot Shutdown). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37243 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-08-21 14:15 | 2000-08-21 15:52 | 2000-08-21 | - 3 OF 3 AFW PUMPS INOPERABLE DUE TO UNDERSIZED PUMP SUCTION STRAINERS - During an inspection of the 'A' Auxiliary Feedwater (AFW) pump, the licensee observed that the length and hole size of the pump suction strainer were different than those assumed in a previous operability determination. The installed pump strainer is approximately 10 inches long and has 1/16 inch diameter holes. The operability determination assumed a 6 inch long strainer with 1/8 inch diameter holes. The licensee could not determine whether the smaller strainer would plug and therefore, declared the 'A' AFW pump inoperable. The licensee inspected the suction strainers of the 'B' and 'C' AFW pumps and determined that their suction strainers may be identical to the 'A' AFW pump strainer and therefore, declared the 'B' and 'C' AFW pumps inoperable. With 3 of 3 AFW pumps inoperable, plant tech specs prohibit the licensee from changing plant operating modes. The licensee plans to remove the suction strainers from all 3 AFW pumps. With the 'A' AFW pump strainer removed and the 'A' AFW pump declared operable, the plant will be in a 4-hour shutdown LCO with the other AFW pumps inoperable. The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED COND OP | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(A) |  |  |  | 0
37242 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-08-21 13:15 | 2000-08-21 14:54 | 2000-08-21 | - WESTINGHOUSE ANALYSIS OF UNBORATED SFP NOT WITHIN NRC APPROVED DESIGN CRITERIA - Westinghouse has notified the Prairie Island Nuclear Plant that the analysis for the Spent Fuel Pool (SFP) with zero boron concentration is not within the NRC approved design criteria. The current NRC approved analysis for unborated water in the SFP states that the Keff should be less than 1.0. The Westinghouse analysis assumed a nominal fuel pellet density lower than the as-fabricated density. This results in a Keff of 1.00086 in an unborated SFP. Westinghouse reanalyzed the condition using a methodology that takes credit for the effect of spacer grids and spacer sleeves. With this factor, the analysis concludes that Keff in an unborated SFP would be less than 1.01; however, this change to the methodology has not been approved by the NRC. The approved analysis includes a case that takes credit for 750 ppm borated water. Westinghouse has reevaluated this case using higher density fuel pellets and concluded the acceptance criteria (Keff < 0.95) is still met. Prairie Island Plant Technical Specifications require the SFP boron concentration to be greater than 1800 ppm. Current SFP boron concentration is 3210 ppm. Additional compensatory measures are being evaluated. Reference: Tech Specs 3.8.E.2.a and 5.6.A.1.b. The licensee notified state and local officials and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37241 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-08-21 06:45 | 2000-08-21 12:30 | 2000-08-21 | - 2 OF 3 TRAINS OF ESSENTIAL CHILLED WATER SYSTEM INOPERABLE; TECH SPEC 3.0.3 ENTERED - At 0645 CDT on 08/21/00 with the 'C' train Essential Chilled Water System inoperable for maintenance activities, the 'A' train Essential Chilled Water System became inoperable due to an oil leak. This condition of two trains of the Essential Chilled Water System being inoperable is not allowed by Technical Specification 3.7.14 and required entry into Technical Specification 3.0.3. No maintenance work had yet been performed on the 'C' train Essential Chilled Water System. At 0754 CDT on 02/21/00, the licensee released the equipment clearance tags and restored the 'C' train Essential Chilled Water System to operable status and exited Technical Specification 3.0.3. This event is reportable to the NRC in accordance with the requirements of 2G of the South Texas Project's Operating License to notify the NRC within 24 hours of any violation of Technical Specifications. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | TECH SPEC LCO A/S | LICENSEE 24 HR REPORT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
37240 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-08-19 11:05 | 2000-08-19 16:10 | 2000-08-19 | FAILURE OF A 35-CURIE IRIDIUM-192 SOURCE TO RETRACT TO ITS SHIELDED POSITION WITHIN A RADIOGRAPHY CAMERA OPERATED BY RAYTHEON PERSONNEL (48-HOUR REPORT BASED ON MANAGEMENT DISCRETION) The following text is a portion of a facsimile received from the licensee: "CONDITION DESCRIPTION:" "[A] radiography source would not return to shielded container of camera. On 19 August 2000, Washington Group (Raytheon) was conducting radiography on welder test coupons in the CSB Hallway, 53' elevation. The radiography was being conducted under [Radiation Work Permit (RWP)] 491 utilizing a 35-curie [Iridium]-192 source, license number L02662. The task had continuous [Health Physics (HP)] coverage assigned. The following is a synopsis of the event:" "1. All notifications and announcements for radiography were completed." "2. The first shot was a scheduled 45-second shot and commenced at 1105." "3. Following the exposure period, the source was retracted. The radiographer noted that he had not heard the characteristic 'snap' signifying full retraction." "4. By operating guidance, the radiographer ran out the source and attempted retraction. This effort was unsuccessful." "5. [The] radiographer noted that the emergency procedure was with the camera, thus unavailable. [The] radiographer obtained an additional copy of the procedure from [the] onsite office." "6. The source was run out again to full exposure and again retracted. Indication on the camera was that both the red and green [lights] were lit, indicating the source was in an intermediate reaction." "7. At approximately 1127, the radiographer informed the HP Technician that they were entering their emergency procedure. The HP technician notified the ConEd HP supervisor of the event." "8. The ConEd HP supervisor reported to the scene at 1135 and notified SGR HP staff of the event." "9. At 1140, the source was fully retracted following two more attempts." "10. The camera was surveyed to confirm full retraction." "11. The camera was secured in the 53' NSB source vault, and RWP 491 was placed on hold pending investigation of the event." "Subsequent to the event, the radiographer met with SGR HP management and [committed] that this camera [would] not be utilized and [would be] tagged as such. The radiographer stated that the camera [would] have to be transported to their home office for maintenance/repair. Written statements were obtained from the principal parties[,] and relative documentation for the event [has] been gathered [...] ." "IMMEDIATE ACTION:" "The following actions were taken:" "1. ConEd Hp management [was] notified of the event." "2. Personnel that were involved in the event were assembled, and the sequence of events [was] ascertained." "3. The camera was locked in the 53' NSB source vault." "4. RWP 491 was placed in an on hold status." "5. The radiographer assured SGR HP management that the camera would not be returned to service and would be tagged as such." "6. SGR and SGT project management were notified." The licensee stated the no one was exposed and that everything was properly shielded and monitored by HP personnel. The work was being performed in a hallway located in a support facility. The hallway was not used for traffic, and it was shielded with heavy concrete. The brand name of the radiography camera was not available at the time of this report. The licensee decided to notify the state of this event, and the control room was informed of this decision at 1358. The decision to notify the NRC was made as a 48-hour report per procedure based on management discretion. At the time of the licensee's notification to the NRC, the licensee had notified the state and planned to notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
37239 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-08-18 19:35 | 2000-08-19 00:09 | 2000-08-19 | PLANT HAD GREATER THAN 20% OF THEIR WARNING SIRENS OUT OF SERVICE. More than 17 of the 81 warning sirens became out of service due to power outages. This represents greater than 20% of the warning sirens, therefore making it reportable. The number of warning sirens available was back within acceptable limits at 2035 on 8/18/00. Currently only 8 warning sirens are out of service. This information was obtained at 2320 and determined reportable at 2327. The NRC Resident Inspector, the State and local agencies will be informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37238 | 0 | KEEGAN TECHNOLOGY AND TESTING |  |  |  |  | 2000-08-18 13:00 | 2000-08-18 13:53 | 2000-08-18 | HUMBOLT NUCLEAR DENSITY GAUGE STOLEN FROM A JOBSITE LOCATED IN HILLSIDE, NEW JERSEY. At approximately 1300 on 08/18/00, a Humbolt soil moisture density gauge (model #5001C, serial number 1852) was stolen from a jobsite located in Hillside, New Jersey. Apparently, the gauge was locked inside its case, and the case was located inside an unlocked truck. It was reported that the gauge user entered and exited a trailer and discovered the gauge to be missing after exiting the trailer. The gauge contained cesium-137 and americium-241/beryllium sources. The activity levels of the sources were not known at the time of this notification. The licensee notified both the Hillside New Jersey Police Department and the NRC Region 3 office (John McGrath). (Contact the NRC operations officer for the licensee's contact telephone number and address as well as the contact name, telephone number, and case number for the Hillside New Jersey Police Department.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37237 | 0 | AGILENT TECHNOLOGIES |  |  |  |  | 2000-07-19 | 2000-08-18 08:30 | 2000-08-18 | MISSING Ni-63 SOURCE In early May 2000, Agilent Technologies shipped two(2) 15 mCi Ni-63 sources to Sandia Lab located in Albuquerque, NM. The Lab had only ordered one(1) source. When the second source arrived the Sandia shipping department notified their accounting staff who directed that they return the item to Agilent. Agilent was not informed of the error nor was a return authorization or FEDEX tracking number obtained. Agilent has no record of receiving the returned source. The missing source is an electron capture detector Model #G2397A, S/N U2216 [general license]. The RSO was informed of the incident on 7/19 and determined that the error occurred due to a problem with the FEDEX labeling system. Agilent shipping department prepared a separate label for the first shipment since their FEDEX labeling system was not available that morning. When the labeler was restored, a label was prepared which resulted in a second shipment to Sandia. FEDEX was informed of the missing shipment by Sandia personnel. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | TRA |  | 20.2201(a)(1)(ii) |  |  |  | 0
37236 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-08-17 11:15 | 2000-08-17 14:30 | 2000-08-17 | PLANNED OFFSITE NOTIFICATION REGARDING HIGH EFFLUENT CHLORINE CONCENTRATION IN THE SEWAGE TREATMENT PLANT OUTFALL The licensee stated that the sewage treatment plant effluent chlorine concentration exceeded the SPDES permit allowable limit of 2 ppm. The chlorine concentration was measured at 20 ppm. Preliminary evaluation indicates that chlorine was improperly diluted when the supply tank was recharged. The duration that the effluent chlorine concentration exceeded the allowable limit is currently estimated to be no longer than 4 hours. The sewage treatment plant outfall ultimately leads to Lake Ontario. The licensee plans to notify the New York State Department of Environmental Conservation. The licensee has notified the NRC resident inspector. | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37235 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-08-16 11:15 | 2000-08-17 13:34 | 2000-08-21 | OFFSITE NOTIFICATION REGARDING A LARGE FISH KILL The following text is a portion of a facsimile received from the licensee: "[The] decision was made today (08/17/00) at 1130 [CDT] to notify offsite agencies concerning a large fish kill at Prairie Island. This [was the] result of the planned zebra mussel treatment that was taking place at the plant." The licensee stated that the event occurred on 08/16/00 and that the fish kill involved approximately 7,500 young fish (mainly catfish and minnows approximately 2" to 5" in length). The majority of these fish were discovered in the plant's recycle canal. However, a few dead fish were also found in the Mississippi River. The licensee notified both the state and Goodhue County. The licensee also plans to notify the NRC resident inspector. In addition, a press release may be issued because this may be a media sensitive event. * * * UPDATE 1145EDT 8/21/00 FROM BILL MATHER TO S. SANDIN * * * The licensee is correcting this report to read that 75,000 young fish were killed. The licensee informed the NRC resident inspector. Notified R3DO(Hiland). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37234 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-08-17 13:00 | 2000-08-17 13:22 | 2000-08-17 | OFFSITE NOTIFICATION REGARDING POSITIVE COLIFORM RESULTS IN DRINKING WATER SAMPLES TAKEN AT THE VISITOR'S CENTER The licensee notified the Maryland Department of the Environment of positive coliform results in drinking water samples taken at the visitor's center today. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37233 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2000-08-16 08:10 | 2000-08-17 12:02 | 2000-08-17 | LOAD REDUCTION DUE TO SEA GRASS INTRUSION (72-HOUR REPORT) The following text is a portion of a facsimile received from the licensee: "[This was a] 72-hr phone call for compliance with [procedure] AP-0005762, Rev. 12B, Section 8.4.1.E., 'increase in nuisance organisms (sea grass) or conditions which may require action to prevent detrimental impact to plant operating equipment.' Unit 2 down powered to 50% on 08/16/00 @ 0810 hrs. Sea grass accumulation [was] mitigated. Unit 2 returned to 100% power on 08/17/00 @ 0835 hrs. Reference Tech. Spec. Appendix B, EPP 4.1." The licensee plans to notify the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0
37232 | -1 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-08-16 16:25 | 2000-08-16 17:59 | 2000-08-18 | SMOKE SEEN COMING FROM "2C" SERVICE WATER PUMP MOTOR "2C" Service Water Pump (swing) motor was seen having smoke coming from it. On site fire brigade was sent out to the Service Water building and extinguished the fire at 1609 CT. The licensee declared an Alert at 1625 CT due to the potential of the fire affecting ECCS equipment. No offsite assistance was needed and no other equipment onsite was damaged by the fire. Service Water Pumps "2A", "2B", "2D", & "2E" remain in service. All Emergency Core Cooling Systems are fully operable if needed. Fire Alarm for Service Water pump was received in control room at 1548 CT. A person was immediately dispatched to investigate the alarm. Person reported back to control room at 1552 CT that smoke was coming from "2C" Service Water motor. Licensee entered AOP 29 (Plant Fire) at 1552 CT. At 1555 CT "2C" Service Water Pump tripped for unknown reason. Service Water pump flow was degraded for approximately 15 seconds at which time another Service Water pump was placed in service. Lowest service water pressure reached was 70 psi (min pressure is 60 psi). At 1609 CT report received that fire had been extinguished using carbon dioxide. 1616 CT AOP 29 was exited. The licensee notified state and local officials of entering Alert classification. The NRC Resident Inspector was in the control room during the event. NRC Operation Center was notified by Brad Grinstead of the Alabama Department of Public Health and by Kerri Seber of the Florida State Warning Point of the Farley Unit 2 Alert. * * * UPDATE ON 08/16/00 AT 1845 ET BY G RHODES TAKEN BY MACKINNON * * * Alert was terminated at 1736 CT due to fire being out and all systems operating properly. NRC R2DO (Paul Fredrickson), Acting DEDR (Ellis Merschoff), IRO (Frank Congel), NRR EO (Bill Beckner), NRC PAO (Bill Beecher), NRR (Roy Zimmerman), EDO STAFF (Mark Satorius), NRC RCT (John Jolicoeur), FEMA (Belcher), DOE (Yates), USDA (Lori Thomas), EPA Reg IV (Runge), and HHS (Burger), notified. The NRC Resident Inspector was onsite in control room during this event. * * * UPDATE ON 08/16/00 AT 2031 ET BY G. RHODES TAKEN BY MACKINNON * * * "At 1625 [CT] FNP staff declared an Alert Emergency classification based on criteria found in site procedures. The 2C Service Water Pump motor had faulted resulting in a small fire in the Service Water Intake Structure. The Site Fire Brigade responded and the fire was extinguished promptly. No other equipment was damaged. The FNP Unit 2 Service Water system has 5 pumps and requires 2 pumps per train (4 pumps total) to ensure that system design functions are met. The 2C Service Water Pump is a swing pump that can be aligned to either train. The remaining four Unit 2 Service Water pumps are currently operable and in service. "The FNP staff has assessed this event. No plant personnel were injured and only limited damage to plant equipment as described above occurred. There was no affect on the health and safety of the general public and no release of radiation. The Alert was terminated at 1736 [CT]. Both Units are continuing to operate at 100% power." R2DO (Paul Fredrickson) & IRO (Congel) notified. The NRC Resident Inspector was notified of this update by the licensee. ***** UPDATE/RETRACTION AT 1727 ON 08/18/00 FROM CHERI COLLINS TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "Farley Nuclear Plant ENS Update - Retraction of Alert Emergency due to Fire at the Service Water Intake Structure" "Farley Nuclear Plant [(FNP)] is retracting the Alert Emergency Declaration that occurred at 1625 CDT and was terminated at 1736 CDT on August 16, 2000. FNP Staff personnel made this declaration based on a conservative interpretation of the classification requirements in their internal site procedures. The site procedure requires an Alert Classification to be declared when a fire occurs that potentially affects Emergency Core Cooling Systems (ECCS). The Service Water System supplies cooling water to ECCS components, and therefore, when a 2C Service Water Pump motor fault occurred requiring site fire brigade response, FNP staff felt that the most appropriate and conservative approach was to declare the Alert Classification." "Subsequently, [the] FNP Staff determined that while there was a fire internal to the motor casing of the 2C Service Water Pump, the ECCS was not affected since the required number of Service Water pumps remained available to support ECCS operation. Although a fire in a vital area represents a potential safety hazard, this fire did not rise to the level of safety hazard warranting an Alert Emergency Classification. [The] FNP Staff now believes that no classification should have been declared, and we are retracting this event notification." The licensee notified the Alabama Department of the Emergency Management, Georgia Emergency Management Agency, Florida Division of Emergency Management , and other appropriate local officials. The licensee has also notified the NRC resident inspector. In addition, the licensee plans to issue a press release on Monday (08/21/00). The NRC operations officer notified the R2DO (Fredrickson), NRR EO (Beckner), IRO (Miller), and PAO (Beecher). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor |  |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 2 | AL | POW | [5 empty] | 0
37231 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-08-16 09:10 | 2000-08-16 16:22 | 2000-08-16 | A contract supervisor tested positive for alcohol during random testing. His access was immediately suspended. Review of his work determined that their was no impact on plant safety. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.73 |  |  |  | 0
37230 | 0 | NORTH CAROLINA DIV OF RAD PROTECTIO |  |  |  |  | 2000-08-16 10:00 | 2000-08-16 11:26 | 2000-08-16 | The North Carolina Division of Radiation Protection reported a radiography camera with a disconnected source. The state discovered, while reviewing records, they had mis-filed an incident report from a licensee reporting a source had disconnected on a Source Production and Equipment Co. (SPEC) model #150 serial #316 radiography camera. This occurred when Quality NDE(currently Janx) was performing work in Roaring River, N.C. and while they were retrieving the source to its shielded position, the drive cable broke at the gearbox. The licensee followed emergency procedures and brought two more radiographers to the site and retrieved the source to the shielded position manually. Readings of 2mr/hr @ 6" were measured when the source was retracted to the shielded position. The source(#EH1804) at the time of the incident(01/18/99) measured 25 curies @ Iridium-192 and it was disposed 3/99. The individuals involved in the recovery of the source received an actual dose of <8 millirem. The licensee had filed this incident report on 02/09/99 with the State, which was within the required time. N.C. incident report #00-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | GEN |  |  |  |  | 0
37229 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-08-16 00:30 | 2000-08-16 02:15 | 2000-08-16 | UNIT 1 DECLARED HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABLE DUE TO A FAILURE DURING SURVEILLANCE TESTING "While performing weekly exercise per Operating Order 00-01-0200S, High Pressure Coolant Injection turbine stop valve failed to close when trip solenoid pushbutton was depressed. "High Pressure Coolant Injection was declared inoperable. "Cause of turbine stop valve failure to close is under investigation." With HPCI inoperable, Unit 1 entered a 14 day LCO Action Statement. Both Maintenance and Engineering are evaluating corrective actions. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37228 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-08-14 18:00 | 2000-08-15 17:12 | 2000-08-15 | AGREEMENT STATE REPORT CONCERNING MISSING AMERICIUM-241 CALIBRATION SOURCE. State of California Department of Health was notified today by SAIC, Inc., located in San Diego, that a 14 millicurie Americium-241 calibration source has been missing since yesterday evening. The lab in which the calibration source was located has been surveyed and now other rooms are being surveyed to locate the missing source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37227 | 0 | UNIVERSITY OF PITTSBURGH |  |  |  |  | 2000-08-15 14:00 | 2000-08-15 16:20 | 2000-08-15 | POSSIBLE MEDICAL MISADMINISTRATION INVOLVING YTTRIUM-90 (Y-90). This event occurred at the University of Pittsburgh Presbyterian Hospital located at 200 Lothrop St, Pittsburgh, PA. A patient was to have received 80 millicuries of Y-90 for cancer treatment. The Y-90 was contained in glass microspheres which were to be transferred to the patient cancer site via a catheter. The Thera Sphere delivery device made by Nordion did not delivery most of the microspheres to the patient and at this time it is unknown how much of the 80 millicuries of Y-90 is still in the catheter. The caller, a Health Physicist, did not know what caused the Nordion Thera Sphere delivery device to fail. No one was contaminated or overexposed by this incident. The patients physician was notified of the potential Medical Misadministration. NRC Region 1 Jim Dwyer was notified of this event by the licensee. Half Life of Y-90 is 64 hours. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.33 |  |  |  | 0
37226 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2000-08-14 12:00 | 2000-08-15 14:03 | 2000-08-15 | AGREEMENT STATE REPORT INVOLVING A MEDICAL MISADMINISTRATION On 08/14/00, the Medical Physicist at Cumberland Medical Center called to report a therapy misadministration. Two patients were treated for prostate cancer with I-125 implants. The pre-plan called for patient 1 to be treated with 78 seeds containing 0.326 millicurie per seed. The pre-plan called for patient 2 to be treated with 123 seeds containing 0.229 millicurie per seed. During the post plan review, it was discovered that an error had occurred when ordering the seeds. Patient 1 was treated with seeds containing 0.414 mCi/seed and Patient 2 was treated with seeds containing 0.291 mCi/seed. The physicist has implemented measures to prevent reoccurrence. The licensee will submit a written report within 15 days. Tennessee event Report No. is TN-00-122. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0
37225 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-08-15 01:40 | 2000-08-15 01:45 | 2000-08-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF SECONDARY CONTAINMENT Two reactor building isolation valves (V-28-21 and V-28-22) are not performing their isolation function. The plant is required to be in the shutdown mode by 0704 EDT on 8/15/00 and cold shutdown mode by 0904 EDT on 8/15/00. The valves were discovered at 0304 EDT on 8/14/00 and the licensee has been working on restoring their function. The licensee is continuing to try to restore their function and qualify other valves to perform their function. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 08/15/00 AT 1241 ET BY WRONKA TAKEN BY MACKINNON * * * Correction: This event notification corrects the above reported Oyster Creek Notification. The plant was required to be in shutdown mode by 0704 ET today, 08/15/00. A loss of Secondary Containment Integrity was discovered at 0304 ET on 08/14/00. Subsequent troubleshooting determined at 1120 ET on 08/14/00 that V-28-21 and V-28-22, Reactor Building Exhaust Valves, leak by when closed. A 30 hour LCO, Cold Shutdown, was in effect at the time of the initial notification which was determined to be not applicable and was exited at 0438 ET on 08/15/00. R1DO (Cliff Anderson) notified. The NRC Resident Inspector was notified of this update by the licensee. | 78 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37224 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-08-14 | 2000-08-14 16:55 | 2000-08-14 | AGREEMENT STATE REPORT INVOLVING STOLEN HUMBOLT MODEL 51001 GAUGE "Gauge was stolen from the back of a Company truck while the operator was in a FINA Station at 2910 Loop 12, Dallas, Texas. The driver had not chained the gauge in the truck and had noted the presence of "unsavory" persons that seemed to be following him and were present at the station when he exited his vehicle. When he returned to his vehicle the gauge was missing. He had the keys and the equipment with which to secure the gauge. "The missing gauge is a Humbolt Model 51001, Serial No.: 2692 with 10 millicurie Cs-137 source, Serial No.: 6604GQ and 40 millicurie Am-241 Be source, Serial No.: NJ02854. "The operator has been counseled by the RSO. "Texas License L03157-008. Licensee is located in Fort Worth, Texas." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37223 | -1 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-08-14 06:58 | 2000-08-14 07:42 | 2000-08-16 | BOTH TRAINS OF HIGH PRESSURE INJECTION DECLARED INOPERABLE The licensee, in the process of a routine train swap between the 1B nuclear volume control (NV) pump and the 1A NV pump, the 1B discharge check valve did not fully seat. Flow from the 1A NV pump was being returned through the 1B NV pump to the suction header. This could have affected the capability of both of the NV pumps to perform their required actions in the event that high head injection to the reactor coolant system was needed. Both pumps were declared inoperable at 0658 EDT which made the high head injection system inoperable. The discharge valve on the 1B NV pump was shut at 0710 EDT to restore the 1A NV pump to operable. The method to be used to restore the 1B NV pump to operable is being considered. The licensee intends to notify the NRC Resident Inspector. * * * RETRACTION ON 08/16/00 AT 1711 ET BY T. HEAFNER TAKEN BY MACKINNON * * * "Subsequent to the report, further evaluation determined that the calculated back flow through the 1B NV pump would not have prevented proper starting and operation of that pump. Consequently, that pump was capable of performing it's safety function. With one NV pump operable, there is sufficient injection flow capacity to the reactor coolant system during the event. In addition, for the short time that the 1A NV pump was inoperable, it was not required to assume a single failure of the 1B NV pump during an event. Consequently, McGuire Nuclear Station was not outside it's design basis and Event Report 37223 is retracted." NRC R2DO (Paul Fredrickson) notified. The NRC Resident Inspector was notified of this event retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37222 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-08-11 18:05 | 2000-08-11 19:46 | 2000-08-11 | - CONTAINMENT MONITORING SYSTEM INOP DUE TO DRAIN LINES FILLING WITH CONDENSATION - On 08/09/00, the licensee declared both divisions of the containment monitoring system (CMS) inoperable after engineering department personnel determined that during a design basis loss of coolant accident, the return lines to the suppression pool would fill with condensation which would result in the system being unable to perform its safety function, At 1805 on 08/11/00, the licensee recognized that with both division of the CMS inoperable and the post accident sampling system previously inoperable, this event is reportable to the NRC in accordance with 10CFR50.72(b)(2)(iii)(D). At 1935 on 08/11/00, this issue no longer affects the operability of the CMS. The licensee made procedure enhancements to the Unit 2 Emergency Operating Procedures to periodically drain the condensation that would accumulate in the return lines during Post Accident Conditions. The licensee plans to notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37221 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-08-11 14:40 | 2000-08-11 19:18 | 2000-08-11 | - STUCK OPEN DOOR COULD PREVENT THE SBGT SYSTEM FROM DRAWING A VACUUM IN AUX BLDG - At 1440 CDT on 08/11/00, the licensee prepared a condition report to identify that personnel access door #PW-95-02 between the auxiliary and turbine buildings had been stuck open about 8 inches for approximately 18 minutes beginning at 2250 CDT on 08/10/00. A faulty door assist device lever arm prevented closure. This condition could have resulted in a loss of function of the secondary containment since the standby gas treatment (SBGT) system may not have been able to draw down pressure in the auxiliary building to the required vacuum. The door device has been repaired and the door is now closed properly. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37220 | 0 | COGEMA MINING, INC. |  |  |  |  | 2000-08-09 13:00 | 2000-08-10 10:13 | 2000-08-10 | MONITOR WELL ON EXCURSION STATUS A routine quarterly (every 3 months) water sample collected on August 7, 2000, from monitor well M2, exceeded 2 of its 3 upper control limits (UCLs). A confirmation sample was collected August 9, which also exceeded 2 UCLs. Monitor well M2 was then placed on excursion status per license section 11.2 and its sampling frequency increased to weekly. Monitor well M2 is a perimeter ore zone monitor well located approximately 300 feet east of the restored Production Unit 2 boundary, at the Irigaray Mine, Johnson County Wyoming. The nearest community is Linch, Wyoming, approximately 23 miles to the southeast. Date Chlorides Conductivity Alkalinity Uranium Sampled (mg/I) (umhos/cm2) (mg/I) (mg/I U-308) (UCL 18.0) (UCL 685) (UCL 131.1) (no UCL) 08-07-00 18.2 733 105.5 <0.4 08-09-00 19.0 779 98.8 <0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 4 | WY | MAT | [5 empty] | 0
37219 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-08-09 15:20 | 2000-08-10 01:55 | 2000-08-10 | BULLETIN 91-01 24 HOUR REPORT At 1520 hours on 8/9/00, it was discovered that a Nuclear Criticality Safety Approval (NCSA) non-compliance had occurred in the X-705 decontamination facility. During a routine walk-through by the NRC Resident Inspector, two (2) violations of the X-705 Inadvertent Containers NCSA, NCSA-0705_076, were noted. The conditions noted were as a follows: - An open plastic bag containing used personal protective clothing (PPE) was discovered lying in the Tunnel Basement. - A shelving unit, adjacent to the Microfiltration system was found to contain cardboard boxes, loosely wrapped in plastic. Both of these areas are covered by the controls of NCSA-0705_076. It was determined that these arrays had the potential to collect an unsafe configuration of Uranium-bearing material. This event resulted in the loss of one control (geometry/volume) of the double contingency control principle. The physical integrity of all nearby systems containing uranium-bearing material was maintained throughout this event. NCSA-0705_076 compliance was restored at 1620 hours when the on duty NCS engineer authorized the removal of these items from there respective areas. The licensee informed the NRC resident inspector that this report would be made. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37218 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-08-09 17:51 | 2000-08-09 19:06 | 2000-08-09 | AUTOMATIC REACTOR TRIP Salem Unit 1 experienced an automatic reactor trip due to unknown causes. The first out annunciator was "Power Range Negative Flux Rate Hi." All control rods inserted following the trip and all systems functioned as expected. The auxiliary feedwater system automatically started as expected. The unit is stable in Hot Standby with decay heat being exhausted to the main condenser via the steam dumps. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37217 | 0 | U.S. AIR FORCE |  |  |  |  | 2000-08-08 16:30 | 2000-08-09 16:35 | 2000-08-09 | TWO AM-241 SOURCES LOST IN CRASH OF AIRCRAFT On 8/8/00, at approximately 1630 PDT, an F-16 crashed on a mountain north of Glendale, NV. The aircraft was equipped with a LANTIRN pod, which contains two 4 µCi Am-241 sources (registry number NR-0136-S-0208-5; Amersham model AMM.7). The crash occurred approximately 5,000 feet up the side of a mountain that is approximately 7,000 feet high in a very remote location. The Air Force incident investigation team has not yet accessed the crash site. Wreckage is reported to be spread along a 1,000 foot distance. The licensee will make reasonable efforts to retrieve the sources. The licensee has already contacted NRC Region IV (Gaines) regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | NV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37216 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-08-09 09:07 | 2000-08-09 11:22 | 2000-08-09 | OFFSITE NOTIFICATION - FISH KILL The licensee reported finding 300 dead shad to the Texas Parks and Wildlife Department. The shad were observed in the Circ water discharge. This condition is believed to be the result of local weather and not due to a spill or plant related event. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37215 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-08-09 10:28 | 2000-08-09 10:32 | 2000-08-09 | OFFSITE NOTIFICATION - AIRCRAFT WARNING LIGHTS The licensee notified the Federal Aviation Administration that the aircraft warning lights on the containment would be without power during planned maintenance. The maintenance is expected to last less than one hour. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37214 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2000-08-08 18:44 | 2000-08-08 21:35 | 2000-08-16 | AUTOSTART OF ANNULUS EXHAUST GAS TREATMENT SYSTEM FAN DURING TESTING "During performance of surveillance testing, the lifting of an incorrect lead caused a low flow condition on the in service AEGTS fan. This caused the auto start of the standby AEGTS fan. No low flow alarm was received on the in service fan, but the system functioned properly." The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTION ON 08/16/00 AT 1435 ET BY KEN RUSSELL TAKEN BY MACKINNON * * * The low flow signal which started the Annulus Exhaust Gas Treatment System fan is not an ESF signal. Therefore, this event is being retracted since the autostart did not occur based on a valid ESF signal. R3DO (John Jacobson) notified. The NRC Resident Inspector was notified of the retraction by the licensee. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37213 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-08-08 08:39 | 2000-08-08 10:42 | 2000-08-08 | PLANT HAS LOST ENS, STATE NOTIFICATION PHONE LINES AND LOCAL COMMERCIAL PHONE LINES. THE ENS LINES, DIRECT LINES TO THE STATE, AND LOCAL COMMERCIAL LINES HAVE BEEN CUT RESULTING IN THE LOSS OF THE USE OF THESE PHONE SYSTEMS. HOWEVER, THEY DO HAVE OPERABLE FOREIGN EXCHANGE B/U PHONES AVAILABLE, SO THAT EMERGENCY RESPONSE CAPABILITY IS NOT AFFECTED. THE TELEPHONE COMPANY IS AWARE OF THE PROBLEM AND IS CURRENTLY WORKING ON IT. THE LICENSEE ALSO HAS A SATELLITE PHONE AVAILABLE THE NRC RESIDENT INSPECTOR AND THE STATE HAVE BEEN INFORMED. * * * UPDATE 1453 8/8/2000 FROM SCHOTTEL TAKEN BY STRANSKY * * * All telephone lines have been restored. The NRC resident inspector has been informed. Notified R3DO (Gardner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ENS INOPERABLE | OTHER ASMT/COMM INOP |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(v) | 50.72(b)(1)(v) |  |  | 0
37212 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2000-08-07 21:26 | 2000-08-08 01:24 | 2000-08-10 | AUTO REACTOR SCRAM FROM 100% POWER ON A FALSE LOW REACTOR WATER LEVEL INDICATION Unit 3 experienced an automatic reactor scram when an instrument line "root" valve failed causing a water leak which resulted in a false low reactor water level signal indication sensed by the reactor protection system. The water leak was immediately isolated by the engineered safety features actuation of the excess flow check valve in the same reactor instrumentation line. All control rods fully inserted, no emergency core cooling system injection occurred, no relief valves lifted and all safety systems responded correctly. Unit 3 also had an actuation of the primary containment isolation system following the reactor scram. The NRC Resident Inspector will be notified by the licensee. * * * UPDATE AT 1230 ON 08/10/00 BY STEVE BECK TO JOLLIFFE * * * The following additional information regarding this event is provided by the licensee: During scram recovery, due to a false low reactor water level signal, the reactor building ventilation system could not be reset and placed in service. Reactor building temperatures increased to the alarm setpoint and the crew entered the Secondary Containment Control Emergency Operating Procedure (EOP). The EOP directed the crew to restore ventilation via a supplemental procedure which directed overriding the false low reactor water level signal using jumpers. The crew installed the jumpers and restored the normal ventilation system and reactor building temperatures returned to normal. With the jumpers installed, the high drywell pressure and low reactor water level initiation signals to the Standby Gas Treatment (SBGT) System were overridden. Inhibiting the SBGT System initiation signals is reportable per 10CFR50.72(b)(2)(iii)(C) and 10CFR50.73(a)(2)(v). All systems have since been restored to normal status. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R1DO John Rogge. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37211 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-08-07 08:13 | 2000-08-07 12:00 | 2000-08-07 | OFFSITE NOTIFICATION DUE TO A DEAD IMMATURE SPERM WHALE FOUND NEAR SITE The licensee made a courtesy call to the Florida Fish and Wildlife Conservation Commission and the Florida Marine Patrol were notified of a dead immature sperm whale was discovered in the surf in the front of the licensee's property (not on the property). The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37210 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-08-07 10:50 | 2000-08-07 11:13 | 2000-08-07 | SMALL ONSITE OIL LEAK REQUIRED OFFSITE NOTIFICATION There was a spill of about 10 gallons of hydraulic oil from a contracted bucket truck on the backside of the site, work was being performed on overhead lines. The spill was contained and cleanup is in progress. The licensee notified the NRC Resident Inspector, the New Jersey Department of Environmental Protection and the Ocean County Department of Health. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37209 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2000-08-05 20:54 | 2000-08-05 21:45 | 2000-08-05 | DURING TESTING ONE CUBICLE OF THE CONTROL BUILDING ENVELOPE, THE 1D 4160 VOLT SWITCHGEAR ROOM WAS FOUND TO BE SLIGHTLY NEGATIVE IN PRESSURE. "At 2054 hours on Saturday, August 5, 2000-AmerGen identified a condition that is outside the design basis at TMI Unit 1. Functional testing of the TMI-1 Control Building Envelope {CBE} was in process to verify that the design basis of the Control Building Emergency Ventilation System had been maintained following plant modifications to improve the reliability of the system. Results of the Functional testing found that one cubicle of the Control Building Envelope, the 1D 4160 Volt Switchgear room, located on the 338' elevation of the Control Tower, 1 floor below the Control Room, was slightly negative in regards to internal atmospheric pressure as compared to outside air pressure. The TMI-1 UFSAR, Update 15 states in section 7.4.5.2.1 in part: " ....A positive pressure of > or equal to 0.10 inches w.g. {water gauge} is not a criterion for the entire CBE. The pressure requirement in the cubicles of the CBE, other than the Main Control Room, is that they are maintained at a positive pressure with respect to the areas outside the CBE. "The functional testing found that the ID 4160 Switchgear room was approximately 0.04 inches w.g. negative in regards to areas outside the CBE. Subsequent adjustments to the Control Building Emergency Ventilation System restored the area to a positive pressure in regards to areas outside the CBE. Additional evaluation and testing is in progress to determine the root cause of the event. "The potential consequences of the condition found are believed to be minimal. No actual in-leakage pathway was identified and if the Control Building Emergency Ventilation System been called upon to operate in the re-circulation mode and had in-leakage occurred, the air in-leakage would have been filtered by the CBEVS charcoal filters prior to supply to the Control Room. Thus, the dose consequences to the operators would have been very minimal due to the low amount of in-leakage and filtration prior to supply to the control room." A follow up 30 day LER will be submitted. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37208 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-08-05 04:28 | 2000-08-05 08:07 | 2000-08-21 | DISCOVERY OF A MINIMAL AMOUNT OF WATER IN THE REACTOR CORE ISOLATION COOLING OIL SYSTEM The following text is a portion of a facsimile received from the licensee: "EVENT: The Unit 2 the Reactor Core Isolation Cooling (RCIC) system was discovered to have a minimal amount of water in the oil system. Following investigation of the event and replacement of the oil, the RCIC turbine was successfully manually started and operated normally. During a subsequent automatic start for post-maintenance test requirements, the turbine tripped on high exhaust pressure apparently caused by the governor system's slow response time. Investigation of the turbine control system is continuing." "CORRECTIVE ACTION(S): Continue the investigation to determine the root cause of the water in the oil system and the response of the governor control system." "INITIAL SAFETY SIGNIFICANCE EVALUATION: Minimal. The High Pressure Coolant Injection System, Automatic [Depressurization] System, Low Pressure Core Spray, and the Low Pressure Coolant Injection System were operable throughout the event." The licensee stated that, as a result of this issue, the unit is currently in a 14-day limiting condition for operation in accordance with Technical Specification 3.5.2. The licensee also stated that all other systems functioned as required. The licensee notified the NRC resident inspector. * * * UPDATE ON 8/21/00 @ 1050 BY ELBERFELD TO GOULD * * * RETRACTION Upon further investigation, it has been determined that the condition resulting in the RCIC turbine trip developed during the period of time that the system was inoperable for maintenance, and that there was no loss of safety function. After the notification was made it was determined that the trip of the RCIC turbine was caused by the presence of air in the control system for the governor valve positioning servo. The presence of air delayed the closing of the governor valve during the RCIC turbine start sequence, allowing the turbine speed to increase, thus increasing turbine exhaust pressure above the trip setpoint. The presence of air was introduced by the maintenance activities associated with changing the turbine lube oil. An acknowledged industry expert was consulted and confirmed that one controlled manual start would not be considered adequate to remove air from the governor control system even with a substantial run duration. Experience has shown that multiple starts, at least 2 to 3 governor valve strokes, may be needed to remove the air that can cause abnormal turbine starts. Review of the "as found" condition of the RCIC system and the RCIC system performance before and after the turbine trip indicates that the RCIC system would have successfully performed its intended functions prior to being taken out of service for maintenance on August 4, 2000. This is based on the following. * The system quick started and ran successfully on August 2, 2000, prior to the oil sample being taken that contained the water. * The presence of water in the lube oil did not cause the turbine trip and did not have an adverse impact on short-term system operability. * Both turbine trips during the quick-starts were the result of minimal governor valve stroking after the lube oil changes introduced air into the governor valve control system. * The RCIC turbine was able to achieve a quick-start without tripping, during the performance of OPT-10.1.1 on August 7, 2000, after the governor valve had been stroked twice (i.e., the controlled manual start and a failed quick-start). This event is being retracted by the licensee. The NRC Resident Inspector was notified by the licensee. The R2DO (Paul Fredrickson) was notified by the NRC Operations Officer. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37207 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-08-03 11:21 | 2000-08-03 12:16 | 2000-08-03 | POTENTIAL OIL SPILL TO JAMES RIVER REPORT IS BEING MADE UNDER CORE OF VIRGINIA 62.1-44.34:19, REPORTING OF DISCHARGE. WHILE PERFORMING WORK ON FISH FLUME PIPING AT THE LOW LEVEL INTAKE STRUCTURE, A BACKHOE LOST TRACTION AND SLID INTO DEEPER WATER. THE BACKHOE WAS IN STATE WATERS (JAMES RIVER) FOR THIS EVENT. FUEL OIL WAS REMOVED AND POTENTIAL OIL PATHS WERE PLUGGED TO PREVENT OIL DISCHARGE TO THE JAMES RIVER. ALSO AN OIL BOOM WAS PLACED AROUND THE BACKHOE. NO OIL WAS OBSERVED ON THE SURFACE OF THE WATER. THE STATE DEQ AND NATIONAL RESPONSE CENTER HAVE BEEN NOTIFIED OF THE THREAT THAT OIL WILL ENTER STATE WATERS. THIS REPORT IS BEING MADE UNDER CODE OF VIRGINIA 62.1-44.34:19, REPORTING OF DISCHARGE. THE NRC RESIDENT INSPECTOR WILL BE INFORMED OF THIS EVENT BY TH E LICENSEE. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37206 | 0 | CONAM INSPECTION |  |  |  |  | 2000-08-02 11:15 | 2000-08-03 11:03 | 2000-08-03 | INDUSTRIAL RADIOGRAPHY SOURCE STUCK IN THE OUT POSITION Conam Inspection was performing radiographs at the Tosco Refinery in Trainer, PA. During the performance of a shot, the source assembly fell over denting the source tube preventing the recovery of the source (64 curies of Iridium-192). The area had already been secured for the radiography operation and lead shot was used to cover the source until recovery of the source could be made. The regional Radiation Safety Officer (RSO) was contacted and reported to the site. Repairs were made to the source tube and the source was recovered. A thirty day written report will be made. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2)(ii) |  |  |  | 0
37205 | 0 | U.S. AIR FORCE |  |  |  |  | 2000-08-02 08:00 | 2000-08-02 15:04 | 2000-08-02 | INADVERTENT HALON DISCHARGE AT IRRADIATOR FACILITY The licensee reported that a halon fire suppression system at the Kirkland AFB irradiator facility discharged without an alarm or manual actuation. The source rack was in the shielded position throughout the event. All other safety systems, including the fire detection system, remained functional. The licensee has contacted the fire suppression system vendor to investigate the discharge. The licensee has contacted NRC Region IV (Gaines) regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 30.50(b)(2)(ii) |  |  |  | 0
37204 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-08-02 13:37 | 2000-08-02 14:20 | 2000-08-02 | EMERGENCY SIRENS INOPERABLE A FAILURE OF THE SIREN TRANSMITTER HAS CAUSED A FAILURE OF ALL EMERGENCY SIRENS. REPAIR EFFORTS ARE IN PROGRESS AND REPAIR IS EXPECTED TONIGHT. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37203 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-08-01 13:30 | 2000-08-02 10:19 | 2000-08-02 | 24 HOUR FITNESS FOR DUTY REPORT Package containing small quantity of a controlled substance discovered in protected area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0
37202 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2000-08-01 18:47 | 2000-08-01 19:06 | 2000-08-01 | OUTSIDE DESIGN BASIS - EDG COOLING WATER This report is being made pursuant to 10CFR50.72(b)(1)(ii) due to the plant being in a condition outside the design basis. During initial analysis of data acquired from the Emergency Diesel Generator (EDG) GL 89-13 testing, it has been determined that cross flow exists between the jacket water and air cooler loops on the EDGs. As a result, the air cooler heat exchanger capacity may be exceeded during a LOCA / LOOP condition when heat sink temperature is greater than approximately 80°F. Previous hot weather conditions during the summer of 1999 and early 2000 resulted in heat sink temperatures being greater than 80°F for several days. Currently, heat sink temperatures are below 80°F. The EDGs are currently operable, further analysis is being conducted to increase margin, and compensatory actions are being developed to reduce cross flow between heat exchangers. The NRC resident has been notified. | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37201 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-08-01 10:20 | 2000-08-01 10:44 | 2000-08-01 | - CARM ISOLATION VALVES LABELS IN CONTROL ROOM DIFFERENT THAN UFSAR DESCRIPTION - Tables 7.5-1 and 7.5-2 of the Turkey Point UFSAR indicate that "Open/Close" position indication is provided in the control room for the containment atmosphere radiation monitor (CARM) isolation valves #SV-*-2911, #SV-*-2912 and #SV-*-2913 (containment isolation valves) in compliance with commitments related to NRC Reg Guide 1.97 (Revision 3). Contrary to this, the stated containment isolation valves are provided with "Open/Not Open" position indication in the control room. Tech Spec LCO 3.3.3.3, Action 39 requires the licensee to restore the valves to operable status within 72 hours or isolate the related containment penetrations within 4 hours in accordance with Tech Spec 3.6.4. Since the installed configuration does not meet the plant design as described in the UFSAR, the condition is considered to be reportable under the requirement of 10 CFR 50.72(b)(1)(ii)(B) as a condition that is outside the plant design basis. The licensee is determining corrective actions. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37200 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-07-31 10:18 | 2000-07-31 12:11 | 2000-07-31 | EMERGENCY SIRENS INOPERABLE On 7/31/00, a system test of the emergency sirens was conducted. During this test it was discovered that a large number of emergency sirens are not functioning. It is believed that the sirens are not functional due to a lightning strike which occurred during storms which passed through the area last night. The licensee notified the NRC resident inspector and Dewitt County. * * * UPDATE AT 2317 ON 7/31/00 BY FUNKHOUSER RECEIVED BY WEAVER * * * The sirens were restored at approximately 1600 CDT on 7/31/00. The licensee notified the NRC resident inspector. The NRC Operations Officer notified the R3DO (Jim Creed). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37199 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2000-07-30 16:35 | 2000-07-30 18:39 | 2000-08-01 | INDICATION OF REACTOR COOLANT LEAKAGE ON PRESSURIZER HEATER PENETRATIONS "Boron was discovered on the reactor coolant system (RCS) pressurizer heater power cables. An inspection of the heater sleeves was performed and it appears that two heaters (B2 and D2) are leaking. B2 is on backup heater bank #4 and D2 is on backup heater bank #6. The leakage appears to be the result of primary water stress corrosion cracking (PWSCC) of either the heater sleeve or the J-groove weld between the heater sleeve and the pressurizer cladding. The insulation will need to be removed to positively determine which heater sleeve(s) had been leaking. Currently, Unit 2 is in reduced inventory with the pressurizer empty. The pressurizer heater sleeve penetrations were inspected during 2R-13 [between 1/9/99 and 2/25/99] as part of the routine I-600 inspections performed each refueling outage. No indication of leakage was evident during that inspection. Pressurizer heater sleeve leakage is considered RCS pressure boundary leakage." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0052 ON 07/31/00 BY LARRY McLERRAN TO JOLLIFFE * * * After removing insulation from the pressurizer and RCS hot legs, the licensee discovered 9 or 10 additional pressurizer heater sleeves that are leaking and also a hot leg temperature element (TE) that is leaking. The licensee is continuing to inspect the hot leg penetrations for evidence of leakage. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified R4DO Bill Jones. * * * UPDATE AT 0829 ON 07/31/00 BY WAYNE AHO TO JOLLIFFE * * * The licensee discovered indications on RCS hot leg TE #2TE-4710-3 that is indicative of a RCS pressure boundary leak. The TE is installed above the water line in the 'B' hot leg on the reactor coolant pump #2P-32C side. The licensee is continuing to inspect the hot leg penetrations for evidence of leakage. The licensee plans to notify the NRC Resident Inspector. The NRC Operations Officer notified R4DO Bill Jones. *** UPDATE/PARTIAL RETRACTION AT 1047 ON 08/01/00 FROM WAYNE AHO TO BOB STRANSKY *** The licensee is retracting the last update. The following text is a portion of a facsimile received from the licensee: "This information is provided as an update to Event #37199, and applies only to the update given on 07/31/00 at 0829 EDST, and only to the RCS boundary at the nozzle for 2TE-4710-3. "The remaining information in Event #37199 remains correct at this time. "The nozzle for 2TE-4710-3 was re-inspected, and there was a very fine ring of white material immediately around the nozzle penetration into the hot-leg. No indication of leakage was observed down the side of the hot-leg pipe. Chemistry personnel took a small sample of the white material for analysis. The results of the analysis was conclusive that the white material was not boron. Because of the location of the white material and the results of the chemistry analysis, it is concluded there is high confidence that 2TE-4710-3 is not leaking around this nozzle. "The source of the white ring was from a Component Cooling Water (CCW) leaking flange located above the TE-4710-3 nozzle." The NRC operations officer notified the R4DO (Spitzberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(i) |  |  |  | 0
37198 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2000-07-28 11:07 | 2000-07-28 15:06 | 2000-07-28 | 1 HOUR SECURITY REPORT SAFEGUARDS SAFETY DEGRADATION RELATED TO THE CONTROL OF CLASSIFIED DOCUMENT(S)/SAFEGUARDS INFORMATION. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR ADDITIONAL DETAILS. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 0
37197 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  |  | 2000-07-10 | 2000-07-28 14:29 | 2000-08-04 | POTENTIALLY LEAKING SOURCE A 5mCi Sr-90 source in the form of a brachytherapy seed used for investigational purposes may be leaking. There is no known personnel exposure or spread of contamination involved. The source was manufactured by Novoste which is located in GA . The evaluation will continue to determine whether the source is actually leaking. * * * UPDATE ON 08/04/00 AT 1459 ET BY JIM O'REAR TAKEN BY MACKINNON * * * Up on further investigation it was determined that the brachytherapy seed was damaged by NIST personnel during calibration work. The seed was packaged up and returned to AEA Technologies located in Massachusetts. NRC Region 1, John McGrath, was informed of this update by NIST. NRC R1DO (Jack McFadden) and NMSS EO (John Hickey) notified. Correction To Initial Report: The brachytherapy seed was manufactured by AEA Technologies for Novoste. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | MD | MAT | [5 empty] | 0
37196 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-07-28 12:30 | 2000-07-28 13:07 | 2000-07-29 | UNIT OUTSIDE DESIGN BASIS BASED ON THE POSITION OF THE MECHANICAL STOP ON THE "A" RECIRC PUMP SPEED LIMITER "The mechanical stop for the 'A' Recirc Pump speed limiter was found to have exceeded the value assumed in the calculation for the flow dependent minimum critical power ratio (MCPR) (K-sub f) in the Core Operating Limit Report (COLR). If a Recirc Pump transient (runaway recirc flow) is postulated from a low flow condition, the flow dependent MCPR (K-sub f) may be exceeded. This could result in exceeding the safety limit MCPR under these postulated conditions. This condition is outside the design basis of the plant." This condition was discovered by Engineering and has existed since the last outage in mid-April of this year. Evaluation of the 'B' Recirc Pump is currently in progress. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1126 ON 07/29/00 BY BERNARD HORNING TO JOLLIFFE * * * At 1105 on 07/29/00, the licensee has determined that the mechanical stop for the 'B' Recirc Pump speed limiter also exceeded the value assumed in the calculation for the flow dependent minimum critical power ratio (MCPR) (K-sub f) in the Core Operating Limit Report (COLR). If a Recirc Pump transient (runaway recirc flow) is postulated from a low flow condition, the flow dependent MCPR (K-sub f) may be exceeded. This could result in exceeding the safety limit MCPR under these postulated conditions. This condition is outside the design basis of the plant. The licensee informed the NRC Resident Inspector. The NRC Operations Officer informed the R1DO Mohamed Shanbaky. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37195 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-07-28 09:41 | 2000-07-28 10:25 | 2000-07-28 | CEILING OF THE "C" BATTERY ROOM DOES NOT MEET FIRE RATING REQUIREMENTS. OYSTER CREEK NUCLEAR GENERATING STATION HAS DETERMINED THAT THE "C" BATTERY ROOM CEILING DOES NOT MEET THE REQUIREMENT OF A 3 HR FIRE RATING. THIS CONDITION WAS DISCOVERED AS PART OF AN EXTENT REVIEW PER LER 2000-04. THIS WAS DETERMINED TO BE REPORTABLE BECAUSE THE CONDITION IS NOT A RECENT DEGRADATION BUT THE RESULT OF A DESIGN DEFICIENCY WHICH PLACES THE "C" BATTERY ROOM OUTSIDE DESIGN BASES. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 64 | 0 | 0 | 64 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37194 | 0 | NOVARTIS PHARMACEUTICAL CORP |  |  |  |  | 2000-06-29 15:50 | 2000-07-28 10:07 | 2000-07-28 | NOVARTIS PHARMACEUTICAL CORPORATION REPORTED AN OVEREXPOSURE OF ONE OF THEIR EMPLOYEES. An employee was working with carbon-14 in a hood wearing gloves when a drop of the organic compound solution went onto the gloves. He immediately removed the gloves and noticed discoloration to his skin due to the chemical going through the gloves to a certain extent. He then proceeded to decontaminate himself using normal decontaminating procedures. Surveys were made and further decontamination was conducted, and based on their preliminary calculations at this point, the dose at skin depth of .007 cm is approx. 100 rads(includes the step wise decon). They do not believe he exceeded the NRC dose limit until early July. The solution was on the tip of the left index finger where the skin is much thicker(approx. .04 cm) than the NRC depth of skin dose calculation of .007 cm. The dose, if the material is deposited on the surface of the skin, to the live tissue at a skin depth of .04 cm is zero from carbon-14 due to its low energy. Initially they counted 250,000 cpm on 6/29/00 and after various steps of decontamination it was reduced to 6,000 cpm after one week. Daily urine samples were taken and monitoring continued for a week. By 7/19/00 counts per minute were down to 100 cpm. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | GEN | 20.2202(b)(1) |  |  |  | 0
37193 | 0 | IDAHO NAT ENGR & ENVIRONMENTAL LAB |  |  |  |  | 2000-07-27 15:55 | 2000-07-27 19:22 | 2000-07-29 | COURTESY NOTIFICATION OF A DOE EMERGENCY DECLARATION AT AN INDEPENDENT SPENT FUEL STORAGE INSTALLATION (ISFSI) IN IDAHO At 1555MDT, DOE INEEL declared a Site Area Emergency due to wildland fires on DOE controlled property. The ISFSI containing the TMI spent fuel is not threatened. This notification is a courtesy call only and does not involve the NRC Radiological Emergency Plan. No NRC assistance is requested. DOE INEEL has notified the State of Idaho, all surrounding counties and DOE Headquarters. *** UPDATE AT 0304 EDT ON 07/28/00 FROM JOE GARCIA AND FOREST HOLMS TO LEIGH TROCINE *** This event status update was provided as a courtesy notification. The Site Area Emergency remains in progress. There is a site-wide emergency action level in effect because of a wildland fire. The TMI-2 ISFSI is located at the Idaho National Engineering & Environmental Laboratory (INEEL), but the Site Area Emergency does not impact the TMI-2 ISFSI. However, INEEL has been directed by the Department of Energy (DOE) to notify the NRC when emergency action levels of this nature are in place. The Site Area Emergency will remain in effect until the fire is extinguished. The following text is a portion of a facsimile received from the INEEL: "Description of Incident: Wildland fire on the INEEL. Fire suppression efforts continue. Emergency response centers [are] operational at RWMC, CFA, INTEC, TRA, EOC with reduced staffing. INTEC and TRA [are] continuing to monitor facilities." The NRC operations officer notified the R4DO (Jones), R4RA (Merschoff), NMSS EO (Collins), IRO (Miller), and the Federal Emergency Management Agency (FEMA) (Storer). DOE, U.S. Department of Agriculture (USDA), Department of Health and Human Services (HHS), Environmental Protection Agency (EPA), and Department of Transportation (DOT) (via the National Response Center) were also notified via facsimile. * * * UPDATE 1709EDT 7/29/00 FROM GREG BYBEE TO S. SANDIN * * * The Site Area Emergency was terminated at 1500MST. The NRC operations officer notified the R4DO (Jones), R4RA (Merschoff), NMSS EO (Collins), IRO (Miller), and the Federal Emergency Management Agency (FEMA) (Eaches). DOE, U.S. Department of Agriculture (USDA), Department of Health and Human Services (HHS), Environmental Protection Agency (EPA), and Department of Transportation (DOT) (via the National Response Center) were also notified via facsimile. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | ID | OTH | GEN |  |  |  |  | 0
37192 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-07-27 09:02 | 2000-07-27 13:54 | 2000-08-09 | POTENTIAL LOSS OF SAFETY FUNCTION RELATED TO CONTROL ROOM CHILLED WATER SYSTEM "While alternating Divisions of Control Room Chilled water to perform post maintenance testing on HVK-CHL1B the 'B' chiller tripped. When actions were taken to restart the 'A' chiller the breaker for the service water recirc valve SWP-MOV 27A tripped. The breaker was reset and the chiller was started. Due to the indeterminate nature of the breaker trip on the valve, the 'A' chiller was declared Inoperable. The 'C' & 'D' chillers were already Inoperable due to non-related existing conditions. This places the unit in Action 'B' of Tech Spec 3.7.3. We are conservatively reporting this pending the investigation of the condition and it's affect on the system response to postulated events to determine if the safety function was truly lost. System is currently operating and maintaining normal control room temperature." The licensee will inform the NRC Resident Inspector. * * * UPDATE AT 0924 ON 8/9/00, REPORTED BY NORTHRUP, RECEIVED BY WEAVER * * * The event occurred when the control building chilled water system was being shifted from Division I to Division II. The "A" chiller subsystem (Division I) had been operating normally for approximately one week, and was to be shut down to allow shut down of the "B" chiller subsystem (Division II). The "C" and "D" chillers were already inoperable for reasons unrelated to this event. During the transition to the "B" chiller, it failed to start. The "A" chiller did not immediately restart due to the configuration of its support systems at this point in the transition. Operator actions were promptly taken to restart the "A" chiller. Approximately nine minutes elapsed from the initial shutdown of the "A" chiller until it was restored to service. During the event, the "A" chiller was capable of performing its safety function with reasonable operator actions. This event had no bearing on the previous operability of the "A" chiller. Based on the above information, this event did not result in a loss of safety function. This event notification is retracted. The licensee informed the NRC resident inspector. The Operations Center notified the R4DO (Kennedy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37191 | -1 | UNIV OF ARIZONA |  |  |  | 100 KW TRIGA MARK I | 2000-07-27 08:45 | 2000-07-27 12:00 | 2000-07-27 | 24-HOUR REPORT INVOLVING POTENTIAL I-131 CONTAMINATION "FACILITY LICENSE R-52 "Report, possibly spurious, of I-131 contamination "July 27, 2000 "Description of the Occurrence: "On the afternoon of July 18, 2000, a routine contamination survey was performed at the Nuclear Reactor Laboratory (NRL), University of Arizona by staff of the Radiation Control Office (RCO). On July 26, at approximately 0845, the Reactor Supervisor received word that four out of 30 wipe samples showed contamination, with the highest count rate about 1100 counts per minute. Subsequently, he was told that I-131 (8-day half life) was identified by gamma spectrometry. "Immediate surveys of the Reactor Laboratory and reviews of records showed no confirmatory evidence, which should have been found if the reported contamination was genuine. "Contamination of the samples while in RCO custody is suspected, and this possibility is being investigated. "On the morning of 18 July a group of 20 visitors, members of the public, was present for about one hour in the morning. One half of the visitors, mostly school children grades 6 to 9, carried pocket dosimeters, which showed no exposure. The continuous air monitor showed no indication. The area monitors showed no indication. Finally, no indication of I-131 could be found in the laboratory yesterday, even though no clean-up had been attempted. "The report we received from RCO is at the moment considered to be spurious. This report is transmitted within 24 hours of our receiving that report, however, in case it proves to have some foundation. Investigation is in any case needed of how this occurred, and of why the report we received from RCO was not timely." * * * UPDATE 7/27/00 FROM J. WILLIAMS TO S. SANDIN VIA FAX * * * The licensee is retracting this report based on the following: "FACILITY LICENSE R-52 Withdrawn: previous report, dated today, entitled, "Report, possibly spurious, of I-131 contamination" "July 27, 2000 "Investigation of information that formed the basis for my previous report, dated today, has led to the conclusion that there exists no credible evidence of any violation of 10CFR20 at this facility or of any other basis for an immediate report in accordance with our Technical Specification. In particular no exposure or contamination of any person has occurred. Therefore, the previous report is withdrawn. "The basis for this conclusion, briefly, is as follows: "- The Radiation Control Office has reason to believe that the gamma spectrometer used to identify I-131 may have been previously contaminated with I-131. "- I-131 is not an isotope in use in the Reactor Laboratory. It is present in the reactor fuel elements, but could not have leaked from them without causing other indications that were not present. "- The liquid scintillation counts were incorrectly reported by an inexperienced analyst (though experienced in operating the equipment). "- At low counting levels, the techniques used to obtain the liquid scintillation counts may be sensitive to spurious effects such as static electricity. "- Even if accurate, the count rates reported would not credibly lead to the possibility of exposures above 10CFR20 limits. "- The absence of indications from Reactor Laboratory instruments, as reported previously, cannot be explained if there were any reactivity released from the reactor. Channel checks of those instruments had been performed on the day in question (7/18/00), and their calibrations were current. "- In addition to the absence of air monitor indication and area monitor indication, the reactor pool water monitoring system showed no indication. "- Further wipe samples of the locations occupied by visitors on 7/18/00, showed no indications of activity above background, and other wipes from areas not accessible to visitors showed no significant indications. "As stated in the original report, the reasons for the reporting of possibly spurious data, also after an apparently undue delay, require investigation. The results will be reported in writing to the NRC within 30 days, as an 'observed inadequacy in the implementation of administrative or procedural controls,' (Tech. Specs. 6.7.c.4)." Notified R4DO(Jones) and NMSS(Collins). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 4 | AZ | NPR | [5 empty] | 0
37190 | 0 | PALISADES | 1 |  |  | [1] CE | 2000-07-26 14:27 | 2000-07-27 11:50 | 2000-07-27 | EMERGENCY OFFSITE FACILITY (EOF) TELEPHONE LAND LINES CUT DURING CONSTRUCTION. "ON 7/26/00 AT APPROXIMATELY 1427 HOURS, IT WAS DISCOVERED THAT ALL LAND LINKED TELEPHONES IN THE EMERGENCY OFFSITE RESPONSE FACILITY WERE INOPERATIVE. SUBSEQUENT INVESTIGATION REVEALED A MAJOR TELEPHONE TRUNK LINE HAD BEEN SEVERED AT APPROXIMATELY 1130 HOURS DURING CONSTRUCTION ACTIVITIES APPROXIMATELY ONE MILE FROM THE EOF. THIS SIGNIFICANT LOSS OF TELEPHONES WOULD HAVE IMPAIRED THE CAPABILITY TO ACTIVATE THE EOF IN THE EVENT OF AN ACCIDENT OR EMERGENCY. AT THE TIME OF THE DISCOVERY, COMMUNICATIONS FROM THE CONTROL ROOM TO THE NRC AND OFFSITE AGENCIES WERE VERIFIED AS OPERATIONAL. THE PHONE LINES WERE REPAIRED BY 1700 HOURS ON 7/26/00. "REPORTABILITY OF THE OCCURRENCE WAS DETERMINED AT 1100 HOURS ON 7/27/00." THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37189 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2000-07-26 12:52 | 2000-07-27 11:33 | 2000-07-27 | 24-HOUR NRC BULLETIN 91-01 REPORT "During a routine procedure review associated with a plant-wide procedure upgrade process, a Nuclear Criticality Safety (NCS) engineer noted that a procedure was not written in compliance with the documented criticality safety evaluation. "The procedure under review was 'Filter Disassembly Process' which provides instructions for the disassembly of HEPA filters to remove non-combustible material and recover gross contamination (i.e. particles which are not imbedded in the media) prior to incineration. The procedure instructed the operator to 'Place paper filter media into a 30-gal paper bag for shredding.' The NCS engineer subsequently examined the criticality safety evaluation for the shredder system and found that mass control in the system is maintained by administrative controls which prohibit the shredding of filters surveyed to contain greater than 5g U-235/10 liters. It was determined that the procedure for shredding of the paper bags filled with un-assayed filter media failed to provide the documented double contingency protection for the system. "Double Contingency Protection: Double contingency protection for the shredder is based on mass control (prevent greater than 43 kg U from accumulating in the feeder hopper or the receiver drums). It was determined that less than double contingency protection remained for the system. However, at no time was greater than a safe mass involved. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5), this event meets the criteria for a 24 hour notification because it constitutes a 'nuclear criticality safety incident, in an analyzed system, for which less than previously documented double contingency protection remains ...and: Less than a safe mass ... is involved...' "Summary of Activity: Immediately upon determining that less than double contingency protection remained, the NCS engineer directed that shredding of bags containing disassembled filter media be stopped. Thus double contingency protection was immediately restored. "Conclusions: * Loss of double contingency protection occurred. * At no time was greater than a safe mass involved. * At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved. * The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A formal root cause analysis is underway. * Notification was the result of a deficient procedure, not 'a deficient NCS analysis." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0
37188 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-07-27 08:30 | 2000-07-27 10:13 | 2005-08-26 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE OWNED BY QORE, INC. d/b/a ATLANTA TESTING & ENGINEERING, INC. LOCATED IN TAMPA, FLORIDA The following text is a portion of a facsimile received from the Florida Bureau of Radiation Control: "Licensee: Qore, Inc., d/b/a Atlanta Testing & Engineering, Inc." "City, State, and Zip Code: Tampa, FL 33313" "License #: 1646-1" "License Type; Category: Specific; 3L(1)" "Isotope(s): Cs-137; Am-241:Be" "Activity(s): 8 mCi, 40.2 mCi" "Material Form; Chemical Form; Physical Form: By-product: Special Form" "Probable Disposition of Material: Unknown" "Exposure? No" "Number: N/A" "Type of Individual(s): N/A" "Exposure Source: N/A" "Dose Delivered to: N/A" "Maximum Dose Received: N/A" "Incident Category: Loss of Control - Lost, Abandoned, or Stolen Materials" "Incident Location: 2306 Isabel St., Tampa, FL" "Location Classification: Unrestricted Area" "Incident Description: [The] licensee reported that a gauge was stolen from a technician's home between 8 p.m. on 26 July and 8 a.m. on 27 July. The technician had worked late at a job and went home for the evening. When he checked the container the next morning[,] the gauge was missing. The gauge is locked[,] but the container had not been locked. The keys to the gauge were not stolen. The Tampa PD and the Florida Bureau of Radiation Control are investigating. The licensee is considering [offering] a $500 reward for the gauge's return." "Device Type (Quantity): Soil Moisture/Density Gauge (1)" "Manufacturer: Troxler" "Model Number: 3430" "Serial Number: 23299" "Emergency Groups at Scene: None" "Organizations Notified: NRC, Tampa PD" "Media Contacted: None" "Investigator's Name; Title: Charles Adams, Environmental Specialist II" "Office: Environmental Radiation Control" "Date; Time Investigated: 27-Jul-00; 0830" "[NRC] Region II has been notified." Call the NRC operations officer for contact information. * * * UPDATE FROM STATE OF FLORIDA (ADAMS) TO JEFF ROTTON AT 1633 EDT ON 08/26/05 * * * The State provided the following information via facsimile: "[State of Florida Bureau of Radiation Control] was contacted by a [customer] concerning a Troxler gauge for sale on E-Bay. The seller [located in Florida] indicated that he had bought the gauge at a flea market. Tampa PD retrieved gauge 8/25/05. Investigator inspected gauge and it was undamaged. Licensee will pick it up from Tampa PD on 8/29/05. [State of Florida Bureau of Radiation Control] will take no further action on this incident." FL Incident Number: FL05-116 Notified R1DO (Cook) and NMSS EO (Brach) This is less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37187 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-07-26 18:33 | 2000-07-26 20:05 | 2000-07-26 | REACTOR TRIP DUE TO STEAM GENERATOR LOW LEVEL The '2C' steam generator feedwater regulating valve failed closed for an unknown reason, this led to low level in the steam generator causing a reactor trip. The plant's system responded as designed and all control rods fully inserted. The steam generator power operated relief valves opened momentarily then fully shut. The plant is presently stable in Hot Standby with feed from the auxiliary feedwater pumps and heat removal via the steam dumps to the main condenser. An investigation is in progress to determine the cause of the main feedwater regulating valve closure. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37186 | 0 | CE NUCLEAR POWER |  |  |  | URANIUM FUEL FABRICATION | 2000-07-25 17:00 | 2000-07-26 15:22 | 2000-07-26 | NRC BULLETIN 91-01, 24 HOUR REPORT The following is taken from the report faxed to the NRC concerning a degradation of criticality controls: EVENT DESCRIPTION At approximately 1700 on 07/25/2000, six cans without moisture ok tags were discovered on the Erbia can conveyer storage system. Under guidance of the criticality safety engineer, the cans were moved and staged with proper spacing. The cans were than sampled and laboratory results confirmed that each can contained less than the 1.0 wt.% water limit for the conveyer storage. Thus, no unsafe condition existed. SAFETY SIGNIFICANCE OF EVENT: Medium significance, because most of the scrap generated in cans is unmoderated and confirmatory samples verified that the contents of each can were less than 1.0 wt.% water. SAFETY EQUIPMENT STATUS: N/A STATUS OF CORRECTIVE ACTIONS: The cans were moved and staged with appropriate spacing. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Calculations demonstrate that a single row of cans will remain subcritical. Therefore, in order for a criticality to occur, the cans would have to contain moderated contents and additional cans would have to have been misplaced before a criticality would have been possible. CONTROLLED PARAMETERS: Moderation is the primary controlled parameter. Each can stored on conveyer storage racks is required to contain less than 1.0 wt.% water. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSE MATERIAL: The six cans contained approximately a total of 106.4 kg of U02 powder and scrap. The maximum enrichment was 4.95% U-235. The cans also contained erbium neutron absorber. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The cans are stored with proper spacing and meetings are planned for each shift to discuss the event and reemphasize criticality safety practices. Notification of this report was made to NRC Inspector (Frank Gee) who was onsite at the time conducting inspection of the criticality controls. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | MO | FUE | [5 empty] | 0
37185 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2000-07-25 17:13 | 2000-07-25 17:40 | 2000-07-25 | DEAD AMERICAN JUVENILE CROCODILE FOUND IN THE COOLING CANALS The licensee discovered a dead juvenile American crocodile in the cooling canals. Notification was made to the Florida Fish and Wildlife Agency and the Federal Fish and Wildlife Agency. The NRC resident inspector will be notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37184 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-07-24 13:22 | 2000-07-24 15:20 | 2000-07-24 | APPENDIX R REVIEW DISCOVERED A CONDITION OF NONCOMPLIANCE WITH THE SAFE SHUTDOWN CAPABILITIES OF THE RHR SYSTEM "On 7/24/2000 at approximately 1322 CST, a review of the Appendix R Safe Shutdown Program revealed that a condition of noncompliance with 10CFR50 App R Criteria III L.2 existed for Units 2 and 3, for availability of the minimum flow valves for the RHR Pumps. The BFN Appendix R program assumes the Residual Heat Removal (RHR) minimum flow valves are open following the initiation of RHR and remain open until vessel injection is initiated. Contrary to this assumption, the cables to the valves have not been verified to be protected from the effects of a fire. Consequently the valves could spuriously close and dead head the pump for an extended period of time. "This condition is being reported lAW 10 CFR 50.72.b.1.ii(c) as a 1 hour report as '... a condition not covered by the plant's operating and emergency procedures.'' The licensee is conducting an investigation and posting fire watches in the mean time. The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | COND OUTSIDE EOPS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(1)(ii)(C) |  |  |  | 0
37183 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-07-23 20:10 | 2000-07-23 20:42 | 2000-07-23 | LOSS OF PLANT COMPUTER "At 1910 hours on 7/23/00, the Safety Parameter Display System (SPDS) portion of the Emergency Response Facility Computer System (ERFCS) was noted to be inoperable, due to all outputs being displayed in magenta color. Several attempts were made to reboot the system, but were unsuccessful. The air conditioning system for the Technical Support Center (TSC) computer room (which houses the ERFCS) had failed earlier in the day, and the air conditioning system was secured to perform repairs. Portable cooling fans were being used to cool the TSC computer room and the room temperature had stayed at about 80 degrees F. The system must be secured if temperature rises above 85 degrees F. "Repairs to the TSC computer room air conditioning system are continuing at this time. A return to service time for the SPDS portion of the ERFCS has not been determined at this time." The licensee will notify the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37182 | 0 | NTH CONSULTANTS |  |  |  |  | 2000-07-23 12:00 | 2000-07-23 18:00 | 2000-07-23 | STOLEN TROXLER GAUGE A model 3440 Troxler moisture/density gauge was stolen along with a company truck from NTH Consultants in Detroit, MI. The theft occurred between noon and 3:30pm on 7/23/00. The gauge contains 8 mCi of Cs-137 and 40 mCi of Am-241. The gauge was chained to the bed of the truck at the time of the theft. A report is being filed with the Detroit Police Department, the Michigan State Police and the State radiation offices will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37181 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-07-21 08:20 | 2000-07-21 11:26 | 2000-07-21 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF OFFSITE SIREN During maintenance on an out-of-service emergency offsite siren, it was inadvertently actuated for about 30 seconds. The licensee notified the Massachusetts Emergency Management Agency as well as the Newbury and Newbury Port Emergency Directors. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37180 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-07-20 10:15 | 2000-07-20 13:54 | 2000-07-20 | INACTIVE LICENSED REACTOR OPERATOR STOOD WATCH FOR ONE HOUR On July 20, 2000, at 0915 hours, it was determined that a violation of Technical Specification 6.2.2.b occurred. This notification is being made pursuant to Operating License NPF-76 Condition 2.G for a condition prohibited by Technical Specifications. On July 17, 2000, a licensed reactor operator with an inactive license stood a watch for one hour to cover shift duties. The normal watchstander for day shift was late and a day staff reactor operator was requested to provide shift coverage. According to the posted active license list, the reactor operator's license was active. It was later determined that the active license list was in error and the license was not active. While on watch this individual performed no reactivity manipulations, and was supervised by two licensed Senior Reactor Operators. Section 6.2.2.a of Technical Specifications requires specific staffing levels for the operating shift crew. The required shift staffing was not met at all times and is therefore reportable as a violation of Technical Specifications. This event presented no risk to the health and safety of the general public. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
37179 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-07-20 08:15 | 2000-07-20 08:55 | 2000-07-20 | EMERGENCY SIRENS INOPERABLE The licensee reported that offsite emergency sirens are inoperable due to a transmitter failure. The transmitter associated with one of the sirens has failed in the transmit mode, and radio interference from this siren is affecting the ability to activate all of the other sirens. The licensee is attempting to locate the failed siren and deenergize the transmitter. The NRC resident inspector has been informed of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37178 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-07-20 03:52 | 2000-07-20 04:28 | 2000-07-20 | UNIT OUTSIDE OF DESIGN BASIS "On July 20, 2000 at 0352 hours a Reactor Coolant system leakrate of 0.30 gpm was calculated. Currently the Charging and Letdown systems are isolated for maintenance. Investigation revealed the leakage being from the Excess Letdown system to the systems isolated for maintenance, which are located outside Containment. This leakrate exceeds the limit of 0.68 gph outside Containment and therefore is a condition outside the design basis of the plant. The Control Room Ventilation system is inoperable and a 72 hour limiting condition of operation has been entered." The NRC resident inspector will be informed of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37177 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2000-07-18 18:45 | 2000-07-18 19:40 | 2000-07-18 | PHYSICAL SECURITY EVENT - ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PLANT PROTECTED AREA. COMPENSATORY MEASURES WERE IMMEDIATELY TAKEN UPON DISCOVERY. THE LICENSEE PLANS TO NOTIFY THE NRC RESIDENT INSPECTOR. CONTACT THE NRC OPERATIONS OFFICER FOR ADDITIONAL DETAILS. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 0
37176 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-07-18 12:12 | 2000-07-18 14:17 | 2000-07-18 | - UNEXPECTED ESF ACTUATION DURING PREPLANNED MAINTENANCE ACTIVITIES - At 1212 CDT on 07/18/00, during preplanned maintenance activities on the 'B' standby gas treatment system logic, an unexpected, invalid ESF actuation occurred. Specifically, a planned fuse removal resulted in an unexpected isolation of a containment nitrogen makeup valve and a recirc minipurge valve. All isolations were completed, as designed. The licensee plans to restore all components to their normal positions prior to completing the maintenance activities. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37175 | 0 | GRAND VIEW HOSPITAL |  |  |  |  | 2000-06-30 11:00 | 2000-07-18 12:57 | 2000-07-18 | - GRAND VIEW HOSPITAL, SELLERSVILLE, PA, MISSING TWO 0.38 MILLICURIE I-125 SEEDS - At 1100 on 06/30/00, Grand View Hospital, Sellersville, PA, received a shipment of two vials of I-125 seeds from Imagyn Medical Technologies, Lenexa, KS. The shipping papers stated that the first vial contained one calibration seed and the second vial contained 81 seeds. Each seed contained 0.38 millicuries of I-125. However, when hospital personnel opened the vials, the second vial contained only 80 seeds instead of 81 seeds. Hospital personnel notified Imagyn, the shipper, International Isotopes, Benton, TX, and NRC Region 1 (Neelam Bhalla). Imagyn started an investigation into the missing seed. On 07/17/00, Grand View Hospital received another shipment of two vials of I-125 seeds from Imagyn. The shipping papers stated that the first vial contained one calibration seed and the second vial contained 94 seeds. Each seed contained 0.38 millicuries of I-125. However, when hospital personnel opened the shipping container, the container contained only one vial, the one with the calibration seed. Hospital personnel notified Imagyn and requested an emergency shipment of the missing vial containing 94 seeds. At 0300 on 07/18/00, hospital personnel received the emergency shipment of one vial of I-125 seeds from Imagyn. The shipping papers stated that the vial contained 94 seeds. However, when hospital personnel opened the vial, it contained only 93 seeds instead of 94 seeds. Hospital personnel notified Imagyn and NRC Region 1 (Neelam Bhalla). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0
37174 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2000-07-18 05:48 | 2000-07-18 08:29 | 2000-07-18 | REACTOR SCRAM FROM 100% POWER DUE TO A GENERATOR LOAD REJECT FOLLOWED BY TURBINE TRIP. THE UNIT 2 REACTOR SCRAM WAS RECEIVED DUE TO A GENERATOR LOAD REJECT APPARENTLY CAUSED BY A DISTURBANCE ON THE 345 KV SYSTEM. ALL RODS FULLY INSERTED, NO INJECTION INITIATED AND NO SAFETY/RELIEF VALVES LIFTED. THEY ALSO HAD GROUP 2 AND GROUP 3 ISOLATIONS, AS EXPECTED, DUE TO A REACTOR WATER LEVEL LOW SIGNAL FOLLOWING THE REACTOR SCRAM. THE UNIT 2 AND SHARED EMERGENCY DIESEL GENERATORS AUTOSTARTED AND RAN UNLOADED AS THE RESULT OF THE AUTOMATIC BUS TRANSFERS. UNIT 1 REMAINS AT 100% POWER WITH ITS RESERVE AUXILIARY TRANSFORMER DE-ENERGIZED AND UNIT 2 IS IN MODE 3 WITH ITS NORMAL WATER LEVEL BAND. THE CAUSE OF THIS EVENT, WHICH PROBABLY OCCURRED OUTSIDE THE YARD, IS STILL BEING INVESTIGATED. THE SECTIONS OF THE RING BUS THAT THEY LOST LEFT UNIT 1 WITHOUT ITS RESERVE AUXILIARY TRANSFORMER, SO IT IS RUNNING OFF ITS AUXILIARY TRANSFORMER. THE NRC RESIDENT INSPECTOR WAS NOTIFIED BY THE LICENSEE. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37173 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-07-17 13:35 | 2000-07-17 23:18 | 2000-08-16 | NRC BULLETIN 91-01, 24 HOUR REPORT - At 1335 on 07/17/00, it was discovered that an NCSA mass control was lost in a compressor seal can storage area in the X-330 building. Two seal cans were identified to contain more items than specifically permitted by NCSA-0330_003.A02 requirement #4 which states: "Only one seal set shall be in each seal can." One seal can was discovered to contain two seal sets and a second seal can was discovered to contain one seal with several (3 or 4) additional seal parts. This deficiency was discovered during recovery activities for NCS event report PTS-00-065 (NRC Event Number #37172) involving a spacing violation of NCSA-0330_003.A02, requirement #8. This event resulted in the loss of one control (mass) of the double criticality control principle. NCS interaction and enrichment control was maintained throughout this event. NCSA-0330_003.A02 requirement #4 compliance was restored at 1415 when the extra seal and seal parts were stored individually in seal cans under NCS Engineering guidance. Complete compliance with NCSA-0330_003.A02 (refer to NCS event #PTS-00-065) was established at 1705. SAFETY SIGNIFICANCE OF EVENT: The safety significance of this event is low. NCSE-0330_003.101 analyzes greater than safe mass in a group of seal cans. In this analysis it states that with an enrichment limit of 15% U-235, the amount of uranium in a seal can would have to be exceeded by 4.6 times the normal amount to reach the minimum critical mass. In this event two seal cans were found to be double loaded. Assuming that both overloaded seal cans were next to each other, the mass in the cans is less than the minimum critical mass. Note: these cans were found because the group they were in was being moved to correct a spacing violation between two other seal can groups. The overloaded seal cans were not directly involved in the spacing violation. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR]: For a criticality to occur, the seal cans would have to have more than a double batch and the enrichment exceed 15% U-235. CONTROLLED PARAMETERS (MASS, MODERATION, (GEOMETRY, CONCENTRATION, ETC): The controlled parameters in this case are mass, enrichment and interaction. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The total amount of uranium in the 47 seal cans involved (including the two overloaded cans) is estimated to be 1715 grams uranium or 257.3 grams of U-235. The maximum enrichment for this NCSA is limited to 15% U-235 and the form of the material is dry UO2F2. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The NCS mass control was lost in this case. Only one seal is allowed to be placed In a seal can. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At 1415, NCSA-0330_ 003.A02 compliance was restored. The extra seal parts were removed and stored individually in separate seal storage cans. The NRC Resident Inspector and the DOE Site Representative were notified of this event. PTS-2000-03534 PR-PTS-00-066 * * * UPDATE AT 1252 ON 8/2/00, BY SISLER RECEIVED BY WEAVER * * * On 8/2/00 at 0035 hours maintenance personnel performing walkdown verifications for NRC Event PTS-00-066 discovered a seal can containing several pieces of seals that were more than volume of one seal. Compliance was re-established at 0250hrs under NCS Engineering guidance. The various seal parts were separated into three seal cans and properly stored per the NCSA. At the time of this Update, a 100% Walkdown of all Seal Cans in storage is in progress. The licensee notified the NRC resident inspector. The operations center notified the RDO(Creed); EO (Hickey) * * * UPDATE ON 8/16/00 @ 0756 BY VANDERPOOL TO GOULD * * * On 8/15/00 @ 2150 hours maintenance personnel performing walkdown verification for NRC Event PTS.00-066 discovered a seal can containing several pieces of seals that involved more volume than that of one seal. Compliance was re-established at 0032 hours on 08/16/00 under NCS Engineering guidance. The various seal parts were separated into the appropriate seal cans and properly stored per the NCSA. At the time of this update, a 100% walkdown of all seal cans In storage Is in progress. The NRC Resident Inspector was notified along with the DOE Representative. The Reg 3 RDO(Jacobson) and NMSS EO(Piccone) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37172 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-07-17 13:20 | 2000-07-17 23:14 | 2000-07-17 | NRC BULLETIN 91-01, 24 HOUR REPORT - At 1320 on 07/17/00, it was discovered that an NCSA spacing control was lost in a compressor seal can storage area in the X-330 building. It was identified that two groups of seal cans were not spaced in accordance with control #8 of NCSA-0330_003.A02. The NCSA requires that groups of up to 50 seal cans be spaced a minimum of 48 inches edge-to-edge. One group of 48 and one group of 11 seal cans were discovered spaced 38 inches edge-to-edge in the X-330 building cold recovery seal storage area, This event resulted in a loss of one control (interaction/spacing) of the double criticality control principle. NCS mass control was maintained for the affected seal groups throughout this event. NCSA-0330_003.A02 compliance was restored at 1705 at which time the seal can groups were properly spaced under NCS Engineering guidance. SAFETY SIGNIFICANCE OF EVENT: The safety significance of this even is low. NCSE-0330_003.101 states: "If two groups of fifty seals are not spaced as required, the mass of uranium is estimated to be 3500 grams uranium or 525 grams of U-235. This amount of uranium is a factor of 2.2 less than the minimum critical mass and is therefore subcritical. Also since the seal sets are placed in cylindrical cans approximately 19 inches in diameter and 9.5 inches tall and limited to a stack not greater than six high, the material is not in its optimum geometry. Therefore, even if two groups of fifty seals are placed together or if spacing is not maintained while placing the seal groups in place, criticality will not result since greater than the allowable mass would have to be present also." POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR]: For a criticality to occur, the spacing would have to be violated and the controls on mass would also need to be violated. CONTROLLED PARAMETERS (MASS. MODERATION, GEOMETRY, CONCENTRATION, ETC): The controlled parameters in this case are interaction and mass. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The maximum amount of uranium in the 59 seal cans involved is estimated to be 2055 grams uranium or 309.7 grams of U-235. The maximum enrichment assumed in the analysis is 15% U-235 and the form of the material is dry UO2F2. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The NCS interaction control was lost in this case. The seal can group was required to be spaced 48 inches edge-to-edge and was found to be spaced only 38 inches edge-to-edge. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The NCS interaction control was reestablished at 1705 when the proper spacing for the seal can groups was restored. The NRC Resident Inspector and the DOE Site Representative were notified of this event. PTS-2000-03533 PR-PTS-00-065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37171 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-07-17 16:15 | 2000-07-17 16:33 | 2000-07-17 | - LICENSEE NOTIFIED MD DOE OF COLIFORM FOUND IN PLANT DOMESTIC WATER SAMPLES - THE LICENSEE NOTIFIED THE MARYLAND DEPARTMENT OF ENVIRONMENT (DOE) THAT THE LICENSEE HAD OBTAINED POSITIVE COLIFORM RESULTS IN PLANT DOMESTIC WATER SAMPLES DRAWN ON 07/10/00. THE LICENSEE IS DETERMINING THE SOURCE OF THE COLIFORM AND TAKING CORRECTIVE ACTIONS. THE LICENSEE PLANS TO INFORM THE NRC RESIDENT INSPECTOR. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37170 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-07-17 13:10 | 2000-07-17 13:55 | 2000-07-17 | - LICENSEE NOTIFIED NY STATE DEC OF FAILURE OF PLANT FISH DETERRENT SYSTEM - AT 1310 ON 07/17/00, IN ACCORDANCE WITH THE LICENSEE'S STATE POLLUTANT DISCHARGE ELIMINATION SYSTEM PERMIT, THE LICENSEE NOTIFIED THE NEW YORK STATE DEPARTMENT OF ENVIRONMENTAL CONSERVATION (DEC) REGARDING THE FAILURE OF THE PLANT INTAKE STRUCTURE FISH DETERRENT SYSTEM. THE LICENSEE IS INVESTIGATING THE CAUSE AND DETERMINING CORRECTIVE ACTIONS. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37169 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2000-07-16 | 2000-07-16 18:30 | 2000-07-16 | TWO VIALS WITH RADIOACTIVE MARKERS FOUND IN NATIONAL PARK, NO RADIOACTIVITY DETECTED Two vials, apparently liquid scintillation counter vials, with radioactive markings, were found in the Gateway National Seashore Park in Queens, New York City. Radioactivity of the vials was background when checked with survey instruments, they will be checked with scintillation counter tonight, 7/16/00, for further determination of any radioactive materials. The vials did not appear to have been in the water. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | INFORMATION ONLY | [8 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0
37168 | 0 | NEW YORK CITY HEALTH DEPARTMENT |  |  |  |  | 2000-07-15 | 2000-07-16 05:19 | 2000-07-16 | PACKAGE SHIPPED WITH RADIOACTIVE MATERIAL NOT CORRECTLY PACKAGED AND LABELED. The New York City Health Department reported that a package, which arrived at New York JFK Airport on a passenger airliner from Nigeria, set off the radiation monitors at the airport postal facility. The package was not in a type A container, but was wrapped in plain brown paper and did not have any hazardous labels attached. The package was seized by US Customs and is being held by them in a remote shed at the airport. They believe the material is cobalt-60 and being shipped to Source Production and Equipment in Rose, La. The weight of the package is 67lb, so it appears that there may be some lead shielding, since the package is small for its weight. The wrapping paper on the package was torn, but metal box has not been opened. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0
37167 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2000-07-14 21:49 | 2000-07-14 23:20 | 2000-07-15 | LOSS OF POWER TO THE TSC LEADING TO LOSS OF OTHER ASSESSMENT CAPABILITY The licensee lost electrical power to the Technical Support Center (TSC) due to weather related problems. The associated loss of emergency assessment capability is the basis for this notification. Operation of both Unit 2 and 3 have been unaffected. Normal main control room function and the availability of the Emergency Operations Facility (EOF) have not been effected. Efforts are underway to restore power to the TSC. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 7/15/00 @ 0055 BY KOVALCHICK TO GOULD * * * Power restored to the TSC at 0053 on 7/15/00. The NRC Resident Inspector will be notified. The Region 1 RDO (Conte) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37166 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-07-14 13:30 | 2000-07-14 14:55 | 2000-08-01 | VEHICLE ADMITTED TO THE PROTECTED AREA WITHOUT BEING COMPLETELY SEARCHED. The licensee admitted a new 2-ton truck to the protected area for use as a designated vehicle. They discovered 23 hours after the truck had been admitted to the protected area, that two compartments on the truck had not been searched. They were immediately searched with nothing found. The licensee intends to notify the NRC Resident Inspector and the state and local authorities. * * * UPDATE AT 1240 ON 8/1/00, BY CHRISTIAN RECEIVED BY WEAVER * * * This event has been retracted. Upon further review it has been determined that this event does not fall into the reportable categories identified in NUREG 1304 or Generic Letter 91-03. This event will continue to be tracked as a logable event. The licensee will notify the NRC resident inspector. The Operations center notified the R3DO (Creed). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 0
37165 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-07-13 16:00 | 2000-07-13 16:43 | 2000-07-13 | CONTROL ROOM RADIATION SIGNAL DISCOVERED NOT TO FUNCTION AS DESIGNED DURING LOSS OF OFFSITE POWER The licensee discovered that the control room radiation signal would not function as designed during the loss of offsite power. They have taken manual action per technical specifications to insure proper action during the loss of offsite power. A written LER will be submitted within 30 days. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37164 | 0 | LAW ENG. AND ENV. SERVICES |  |  |  |  | 2000-07-11 | 2000-07-12 12:39 | 2000-08-19 | MISSING MOISTURE/DENSITY GAUGE The licensee reported that a Troxler Model 3411 nuclear moisture/density gauge containing 8 mCi of Cs-137 and 40 mCi of Am-241/Be (S/N 18561) was missing from the Sterling, VA area. A company employee, who resides in West Virginia, was scheduled to bring the gauge to a job site in the northern VA area on 7/11/2000, but failed to show up. Neither the individual, the company vehicle that he was using, nor the gauge can be located. The company last had contact with the employee on 7/7/2000. The licensee did not believe that the individual was a disgruntled employee. The licensee has contacted local law enforcement agencies regarding the missing individual and gauge. ***** UPDATE AT 1820 ON 08/19/00 BY LEIGH TROCINE ***** The following text is a portion of Preliminary Notification of Event or Unusual Occurrence PNO-II-00-027A dated 08/18/00: "On July 12, 2000, the licensee informed the [NRC] Region II office of a missing Troxler Electronic Laboratories Model 3411 portable gauge. The licensee recovered the portable gauge, vehicle[,] and other stolen equipment on August 15, 2000. The radioactive sources in the gauge have been tested for potential leakage and contamination of radioactive material. There was no evidence of leakage or contamination." "This information is current as of 1045 on August 18, 2000." "The Commonwealth of Virginia and State of West Virginia have been notified [by Region II personnel.] The NRC operations officer notified the R2DO (Fredrickson) and NMSS EO (Ting). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | GA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37163 | -1 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2000-07-11 19:50 | 2000-07-11 21:40 | 2000-07-24 | UNIT OUTSIDE DESIGN BASIS DUE TO 10 CFR PART 50, APPENDIX R ISSUE "At approximately 1610 on 7/11/2000, it was identified by plant walkdown that in electrical switchgear Bus 142Y (1AP06B) cubicle 4 (for the Unit 1 B Residual Heat Removal pump) that an unsealed borehole of approximately three (3) inches in diameter existed. This borehole is located in the floor separating the Unit 1 Division 2 Switchgear room from the Unit 1 Division 1 switchgear room. The borehole is located in a three (3) hour rated fire barrier that is required by Administrative Technical Requirement 3/4.7.6 (Fire Rated Assemblies). This has been considered an event that is outside the design basis due to required design basis protective features for safe shutdown trains as described in 10 CFR 50, Appendix R and Final Safety Analysis Report [being] lacking. Compensatory measures (fire watches) have been established per Administrative Technical Specifications and plans for repairs are in progress." The NRC resident inspector has been notified of this event by the licensee. * * * UPDATE 1155 7/12/00 FROM ROCKY HASTY TAKEN BY BOB STRANSKY * * * "Additionally, on 7/7/2000, another unsealed borehole of 2.75 inches in diameter was identified in non-safety Switchgear bus 152 (1AP02B) cubicle 4. Both boreholes are located in the floor separating the Unit 1 Division 1 switchgear room from the Unit 1 Division 2 Switchgear room. Both boreholes are in a three (3) hour rated fire barrier that is required by Administrative Technical Requirement 3/4.7.6 (Fire Rated Assemblies). This has been considered an event that is outside the design basis due to required design basis protective features for safe shutdown trains as described in 10 CFR 50, Appendix R and Final Safety Analysis Report (FSAR) [being] lacking." The NRC resident inspector has been informed of this update. Notified R3DO (Jorgensen). * * * RETRACTED ON 7/24/00 AT 1617 EDT BY JOHN REIS TO FANGIE JONES * * * "...The preliminary evaluation could not determine whether or not the two unsealed penetrations in the three-hour fire barrier between the Unit 1 Division 1 switchgear room and the Unit 1 Division 2 switchgear room would cause failure of both electrical divisions during a fire in either division switchgear room. Should such a fire cause division failure in both switchgear rooms, the station would be outside the safe shutdown analysis performed to meet 10 CFR 50, Appendix R as described in the LaSalle County Station Updated Final Safety Analysis Report. The NRC event number was 37163. "The investigation has determined that LaSalle County Station Unit 1 was operating within the plant design basis while operating Unit 1 with two unsealed openings in the fire barrier assembly separating the Division 1 and Division 2 Switchgear Rooms. "A fire evaluation has been performed that concludes that Unit 1 could have been safely shutdown following a design basis fire in either Switchgear Room based on the fire loading in the rooms, the design of the switchgear, the type of electrical cables, fire detection and the fire brigade. Therefore, LaSalle County Station was operating within plant design basis when operating Unit 1 with the condition described above. Extent of condition evaluation/walkdowns have not identified any 10 CFR 50 Appendix R deficiencies. Unit 2 remains unaffected. "Therefore it has been determined that this event is not reportable to the NRC, and this event notification is being retracted." The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO (Michael Parker). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37162 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-07-11 09:45 | 2000-07-11 18:02 | 2000-07-11 | 24-HOUR NRC BULLETIN 91-01 REPORT "NCSA-PLANT-012 (Favorable Geometry Vacuum Cleaner) Control number 3 requires a steel liner to be used in an F-can when enrichment is known or expected to exceed >80%. At 0945 on 7/11/00, it was discovered that the steel liner was constructed of expanded metal (grating), therefore the liner would not perform its intended function as described in the associated NCSE. The intended function is to reduce the internal diameter of the F-can to less than five inches. The affected F-cans were verified to contain less than the safe mass of U-235. The NCSA is deficient since it references a drawing of a liner that cannot perform its intended function. SAFETY SIGNIFICANCE OF EVENTS: Safety significance is low because the highest mass in any F-can on site with greater than 80% enrichment material is 304 grams U-235 and the USEC site limit for >20% enrichment material is 1000 grams U-235. The mass in the F-cans and the site limit are well below the contingency limit for not using an F-can liner(2500 grams U-235 at 80% enrichment) and current NCSA-PLANT-012 operations are below 80% enrichment, in the unlikely event that 2500 grams of high enriched U-235 was present in the F can, an additional event, such as the presence of full reflection or spacing violation would be required before obtaining a critical configuration "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "A critical configuration would require an F-can to be used to collect 80% or greater enriched material that exceeded 2500 grams. In the unlikely event of exceeding 2500 grams of 80% enriched material in the F-can, an additional unlikely event, such as the F-can being exposed to full water reflection or a spacing violation would have [been] necessary before a critical configuration existed. The probability of all of these conditions existing simultaneously is very low. "CONTROLLED PARAMETERS (MASS, MODERATION. GEOMETRY, CONCENTRATION, ETC.): "Volume, geometry, moderation and interaction are controlled. Geometry control could have been lost since the referenced drawing for the liner does not meet the geometry requirements of the NCSE. Full reflection or an interaction violation is required before a criticality configuration could exist. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "The highest mass in any F-can with greater than 80% enriched material on site is 304 grams U-235. Since this is 87% of safe mass, the safety significance is low. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The NCS control system is deficient since the NCSA references a steel liner in a drawing that does not perform its intended function of reducing the F-can liner diameter to 5 inches or less. The safety significance is low since the mass in F-cans is low and an additional event such as full reflection or a spacing violation would have to accompany an excessive F-can mass before a criticality would be possible. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "A stop work notice was issued for favorable geometry vacuum cleaners when enrichment is known or suspected to exceed 80%." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37161 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-07-11 16:10 | 2000-07-11 16:33 | 2000-07-11 | FITNESS FOR DUTY REPORT A licensed operator tested positive for illegal drug use during a random test administered on 6/29/00. The individual's site access has been suspended. The NRC resident inspector will be informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.73 |  |  |  | 0
37160 | 0 | U.S. AIR FORCE |  |  |  |  | 2000-07-10 12:00 | 2000-07-11 10:33 | 2000-07-11 | TWO AIRCRAFT ENGINE SET OFF PORTAL ALARMS TWO AIRCRAFT ENGINES SENT TO CMC LEXINGTON IN LEXINGTON, SC SET OFF THE PORTAL ALARMS AT THEIR FACILITY ON 6/7/00. CMC LEXINGTON NOTIFIED THE U.S. AIR FORCE OF THE EVENT. THE AIR FORCE HAD INITIALLY ASSUMED THAT THE ALARMS WERE CAUSED BY A MAGNESIUM THORIUM ALLOY USED IN THE ENGINES. HOWEVER, SURVEYS CONDUCTED ON 7/6/00, DISCOVERED LOW LEVELS OF BOTH BETA/GAMMA AND ALPHA CONTAMINATION. THE AIR FORCE IS SENDING A TEAM TO THE SITE TOMORROW TO FURTHER ANALYZE THE CONTAMINANTS AND PLAN A COURSE OF ACTION. THE ISOTOPE(S) INVOLVED WERE NOT KNOWN AT THE TIME OF THE REPORT. THE ENGINES HAVE BEEN PLACED IN A LOCATION TO PREVENT ANY SPREAD OF CONTAMINATION. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | SC | MAT |  | 30.50(b)(1) |  |  |  | 0
37159 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-06-22 | 2000-07-10 20:10 | 2000-07-10 | AGREEMENT STATE REPORT "Date of event: June 22, 2000 "Location of Event: Rochester, NY "During a device sales demonstration the potential customer happened to measure higher than expected dose rates on a MAP-4 series model FA4C2 portable x-ray fluorescence device. It was later determined that the source, 125 millicuries of Am-241, had fallen out of the source block but was still contained within the device, although unshielded. The device was shielded and subsequently returned to the manufacturer, EDAX, Inc. To compound matters, the device was being referred to as a model 'CT3000' by the sales demonstrator and the initial reporting of the incident by the state of New York was believed to concern the recently approved, but unrelated, CT5000 series devices. On June 28, 2000, the EDAX RSO responded to the state of Washington Department of Health that EDAX had manufactured four MAP-4 (FA4C2) devices for research and development with source blocks that had not been approved by the department for general production. One of the research devices had been mistakenly assembled with an experimental source block design that was previously rejected as unsatisfactory. This device was involved in the incident in New York State while being tested for effectiveness and market potential. "EDAX has accounted for all its experimental source blocks and has removed the one faulty block from the device and marked it so that it can not be used in the future. The remaining R&D devices will be surveyed whenever used. Although this manufacturing error did not involve the production of devices intended for sale to licensees, staff from the Division of Radiation Protection will be reviewing the manufacturer's quality control process as well as model designation practices. "What is the notification or reporting criteria involved? WAC 246-221-250; re: Equipment failure. "Activity and isotope(s) involved: 125 mCi Am-241 source, serial number 7887LQ. "Device (HDR, etc.) Mfg., Model; computer code: EDAX, Inc., MAP-4 series model FA4C2 x-ray fluorescence device, serial number 1525." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37158 | -1 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-07-10 10:38 | 2000-07-10 17:28 | 2000-07-19 | FITNESS FOR DUTY REPORT A licensed training supervisor tested positive for alcohol use during a random drug and alcohol test. The individual's access has been suspended and the licensee will review the individual's work for the past 90 days. The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTION ON 07/19/00 AT 1122 ET BY STEWART TAKEN BY MACKINNON * * * After discussions with NRC Region 2 it was determined that the above reported event did not have to be reported and is being withdrawn. The individual was not a supervisor at the time of the event. This report will be reported on the licensee's Semi - Annual Fitness for Duty Report. NRC R2DO (Bonser) notified. The NRC Resident Inspector was notified of this update by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0
37157 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-07-10 13:30 | 2000-07-10 17:28 | 2000-07-10 | FITNESS FOR DUTY REPORT A contract supervisor tested positive for cocaine use during a random drug and alcohol test. The individual's access has been suspended and the licensee will review the individual's work for the past 90 days. The NRC resident inspector has been informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0
37156 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-07-10 13:00 | 2000-07-10 13:37 | 2000-07-10 | OFFSITE NOTIFICATION TO STATE REGARDING ONSITE WATER QUALITY Results of domestic water samples taken on 7/6/00 indicate the presence of fecal coliform. The licensee will be making a notification to the State of Maryland regarding the results. The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37155 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-07-10 10:51 | 2000-07-10 11:41 | 2000-07-10 | UNIT 1 EXPERIENCED A REACTOR SCRAM FOLLOWING TURBINE TRIP AFTER RECEIVING A TURBINE ALARM UNIT 1 RECEIVED A TURBINE SUPERVISORY EQUIPMENT FAILURE ALARM FOLLOWED BY A TURBINE TRIP. THE LOWEST INDICATED REACTOR VESSEL WATER LEVEL (RVWL) WAS +18 INCHES. THE RVWL WAS RECOVERED TO NORMAL. BY REACTOR FEED PUMPS. INDICATION SHOWS THAT NINE (9) SAFETY RELIEF VALVES (SRVs) OPENED DURING THIS TRANSIENT. PRELIMINARY INDICATION SHOWS HIGH VIBRATION ON #10 GENERATOR BEARING. THE LICENSEE SUSPECTS EITHER A BAD PROBE, WIRING OR ELECTRONIC CARD PROBLEM. UNIT 1 IS CURRENTLY STABLE WITH "A" REACTOR FEED PUMP SUPPLY WATER TO THE REACTOR VESSEL AND STEAM REMOVING DECAY HEAT VIA THE TURBINE BYPASS TO THE MAIN CONDENSER. ALL SRVs RESEATED AND THERE IS NO SAFETY RELATED EQUIPMENT OUT OF SERVICE AT THIS TIME. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37154 | 0 | U.S. ARMY |  |  |  |  | 2000-07-08 12:17 | 2000-07-10 09:26 | 2000-07-10 | STOLEN CHEMICAL AGENT DETECTOR AN M43A1 CHEMICAL AGENT DETECTOR WAS STOLEN FROM THE TWIN BRIDGES TRAINING AREA IN THE REPUBLIC OF KOREA DURING A RECENT EXERCISE. THE DETECTOR CONTAINS 250 µCi of Am-241. THE ARMY HAS NOTIFIED THE REPUBLIC OF KOREA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37153 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-07-08 21:07 | 2000-07-08 22:19 | 2000-07-17 | UNIT OUTSIDE OF DESIGN BASIS FOLLOWING CIRCULATING WATER SYSTEM BACKFLUSHING The licensee reported that the service water system inlet temperature exceeded the design basis temperature of 75° F for approximately 9 minutes following the completion of a condenser backwashing operation. Actual system temperatures increased from an initial temperature of 66° F to a high of 90.6° F before returning to normal. The licensee stated that a new procedure for cleaning the circulating water system was being used; instead of elevating and holding system temperature ("mussel cooking"), a high flow rate "velocity flush" was performed. The flushing was performed for approximately four minutes, during which time service water inlet temperatures remained normal. However, after the flushing was completed, service water system inlet temperatures, as measured at various system headers, increased unexpectedly. The licensee has cancelled additional flushing operations that had been planned for the weekend. The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE ON 7/17/00 @ 1049 BY NELSON TO GOULD * * * RETRACTION Subsequent review and evaluation determined that the plant did operate within the confines of its design basis. Therefore, this event was not reportable pursuant to 10 CFR 50.72(b)(1)(ii)(B). This report is therefore withdrawn. Specifically, as stated in the Basis for the Ultimate Heat Sink Technical Specification (TS 3.7.11), the limitation on the ultimate heat sink temperature ensures that sufficient cooling is available to either: 1.provide normal cooldown of the facility, or 2. to mitigate the effects of accident conditions within acceptable limits. This limitation is based on a 30 day cooling water supply to safety related equipment without exceeding their design basis temperature. This basis constitutes the design basis for the ultimate heat sink temperature limitation. The temperature excursion that occurred was approximately 8 minutes in duration. This period of time constitutes less than 2/1000 of 1 percent of the aggregate time and is therefore insignificant relative to maintaining a 30 day cooling water supply. Additionally, the indicated temperature at the Vital switchgear cooling heat exchanger (X-183), while peaking at 90.6 °F, was not indicative of the bulk (i.e. Long Island Sound) temperature of the ultimate heat sink but rather was a localized effect resulting from the planned backwashing evolution that was the direct cause of the increased temperature indication. The magnitude and duration of the temperature excursion was such that it would not have inhibited the units ability to perform a normal cooldown of the facility if it had been required. In addition, since the ultimate heat sink temperature was restored to less than 75 °F within 8 minutes, the ability to provide a 30 day cooling water supply to safety related equipment without exceeding their design basis temperature supply was not impacted. Therefore, the power plant was not in a condition during operation that resulted in the nuclear power plant being outside of the design basis. The NRC Resident Inspector was notified. The Reg 1 RDO(Cranston) was informed. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37152 | -1 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-07-08 04:40 | 2000-07-08 08:33 | 2000-07-24 | UNANALYZED CONDITION At 04:40 the Unit 2 #4 Main Turbine control valve closed. No testing or maintenance was in progress at the time of the valve closure. Plant Operating procedures specify that the MCPR thermal limit is not analyzed for this condition. The appropriate technical specification action is being entered to reduce power to below 25% power within 6 hours. Reactor power is currently 52% and being reduced. At 07:47 it was determined that an unanalyzed condition exists on Unit 2 that has the potential to compromise plant safety based on the above condition. The cause of the control valve failure is not determined at this time. At the time of the control valve closure, reactor power and pressure remained stable with one main turbine bypass valve opening approximately 40%. Power was immediately reduced to 95% in accordance with plant procedures. The bypass valve closed. The licensee notified the NRC resident inspector. * * * RETRACTED AT 1341 EDT ON 7/24/00 BY STAN GAMBLE TO FANGIE JONES * * * "This is a retraction of a notification made on 07/08/00 at 08:33 hours, (event #37152). This event was reported as an unanalyzed condition under requirement 10CFR50.72(b)(1)(ii)(A). "Unit 2 Main Turbine control valve (TCV) failed closed at 100% power. The Technical Specification MCPR thermal limit is not analyzed for extended operation with one TCV in the closed position. Power was reduced to less than 25% within the TS AOT. "The basis for this retraction is that the effect of the closed TCV has been evaluated by PECO Energy engineering with the following results. The TCV slow closure resulted in a mild pressure transient that did not challenge the MCPR Safety Limit. This phase was bounded by the limiting MCPR event of load reject without bypass. "The load drop to 25% power was uncomplicated and completed within four (4) hours and twenty (20) minutes. The leading MFLCPR value for this period was 0.961. This complied with the MCPR TS AOT of six (6) hours. This period was of short duration and bounded by the existing Design Bases Accidents. "The MCPR TS LCO is not applicable to operation at less than 25% power. This period of operation is also considered analyzed. "Since all phases of the transient and reduced power operation are explicitly analyzed or bounded by existing analysis, this event is considered analyzed. In addition, this event did not significantly compromise plant safety. An unanalyzed condition that significantly compromises plant safety did not occur. Therefore, this event is not reportable per the guidance of NUREG-1022, Rev 1." The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R1DO (Mohamed Shanbaky) | 0 | 52 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED COND OP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(A) |  |  |  | 0
37151 | 0 | U.S. ARMY |  |  |  |  | 2000-05-27 | 2000-07-07 15:22 | 2000-07-26 | MISSING M43A1 CHEMICAL AGENT DETECTOR The licensee reported that one M43A1 chemical agent detector, containing 250 µCi of Am-241, had been lost during a field training exercise at Fort Campbell, KY. A field artillery unit had deployed the detector in accordance with the field manual, but was later unable to locate the detector. Another unit may have taken the detector. * * * UPDATE AT 1017 ON 07/26/00 BY JEFF HAVENER TO JOLLIFFE * * * At 0920 CDT on 07/26/00, a U.S. Army representative located the subject detector in the fort calibration shop during an inventory. The detector was undamaged. The NRC Operations Officer notified the R3DO Tom Kozak. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | KY | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37150 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-07-07 13:47 | 2000-07-07 15:03 | 2000-07-07 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "This report is being made in order to comply with the requirements of 10CFR50.72(b)(1)(i)A due to the initiation of a Technical Specification Required Plant Shutdown. "At 0831 CDT while operating at 100% power Reactor Equipment Cooling (REC) Pump 'C' unexpectedly tripped. This condition required entering Technical Specification LCO 3.7.3 Condition B due to both REC subsystems being Inoperable. REC pump 'C' is in Division 2 of REC. Division 1 of REC had been declared Inoperable on 7-5-2000 at 2134 when REC pump 'A' tripped. "The Required Actions of LCO 3.7.3 Condition B require the Plant to be in Mode 3 in 12 hours and Mode 4 in 36 hours. The first power drop occurred at 1347 CDT. "The electrical grid is stable at this time. The cause of the REC pump 'C' trip is currently under investigation. It is suspected the thermal overloads on REC Pump 'A' are the cause of that pump trip and they are being replaced at this time." The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE 1848 7/7/00 FROM CROW TAKEN BY STRANSKY * * * "At 1545, both REC subsystems were declared Operable. This was based on an operability determination requiring the operation of all four REC pumps, which will add margin to where the pumps are operating compared to the thermal overload setpoints. The Technical Specification shutdown was exited at that time. Power had been lowered to approximately 80% prior to both REC subsystems being declared Operable. The return to 100% power is in progress." The NRC resident inspector has been informed of this event by the licensee. Notified R4DO (Graves). | 88 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37149 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-07-06 | 2000-07-07 13:29 | 2000-07-07 | AGREEMENT STATE REPORT "The licensee reported that a radioiodine therapy patient had self-discharged the previous evening at 8 PM. The patient, a 45 year old male, had been administered 200 millicuries of sodium iodide at approximately 11 AM on Wednesday, July 5. Retained activity was determined to be 60 millicuries at 9 AM and 47 millicuries at 5 PM on Thursday, July 6. The patient was counseled by the authorized user as late as 5 PM on July 6 as to the radiological hazard that he would present to others and he was informed that hospitalization was a regulatory requirement. Nevertheless, the patient had his wife pick him up from the hospital at 8 PM on July 6. The estimated activity at the time of departure was 40 millicuries. The licensee will determine the patient's subsequent activities and whether there were any children in the home. The licensee estimated that the patient would have been released at noon July 7. "Activity and isotope(s) involved: 40 millicuries I-131." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37148 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-07-07 02:05 | 2000-07-07 05:18 | 2000-08-03 | MAIN CONTROL ROOM HVAC EMERGENCY VENTILATION DECLARED INOPERABLE "During performance of scheduled monthly surveillance testing, it was determined that overall differential pressure on the Main Control Room HVAC Emergency Ventilation Train Air Filtration Unit (AFU) was out of specification high. The AFU is a single train system required to provide habitable conditions for control room personnel during design basis accident conditions. This condition is reportable under the requirements of SAF 1.17 'Could alone have prevented safety function.' and 10CFR50.72(b). This condition places both Units in a 7 day shutdown LCO." The licensee will inform the NRC Resident Inspector. * * * RETRACTION AT 1755 ET ON 08/03/00 BY KEN HOUSH TAKEN BY MACKINNON * * * A more detailed review performed by Dresden Operations and Engineering personnel has determined that the Differential Pressure across the Air Filtration Unit filter could be up to a maximum of 10 inches of water gauge and perform its design function. The Technical Specification value will be increased to the maximum allowable value (at least 8.0 inches of water gauge); which will remain within the design parameters required for each component of the Control Room HVAC system. The Control Room HVAC system was able to perform its intended safety function and therefore the reportability of CFR 50.72(b)(2)(iii)D does not apply to this condition. NRC R3DO (Jim Creed) notified. On 07/07/00 at 0205 CT the Control Room HVAC Air Filtration Unit Differential Pressure was found to be at 6.03 inches of water which is above their Technical Specification 3/4.8.D during a routine surveillance test. The NRC Resident Inspector will be notified of this event retraction by the licensee. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37147 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-07-05 10:35 | 2000-07-05 17:14 | 2000-07-05 | USE OF ILLEGAL CONTROLLED SUBSTANCE An employee was tested for cause for illegal controlled substance with the results being negative. However, he admitted during the interview he had used such substance. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0
37146 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2000-07-05 15:00 | 2000-07-05 15:16 | 2000-07-05 | CONTRACT EMPLOYEE FAILS FITNESS FOR DUTY TEST A contractor employee failed a Fitness For Duty test administered on July 5, 2000. Specific details of the event are not for public disclosure. Appropriate action has been taken accordance with the company Fitness For Duty program. The NRC Resident Inspector will be notified. State and Local agencies have been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0
37145 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-07-05 13:07 | 2000-07-05 14:17 | 2000-07-05 | REACTOR TRIP FROM 100% POWER DUE TO TURBINE TRIP. The plant had a reactor trip from 100% power due to a turbine trip. Cause of the turbine trip is being investigated. All control rods fully inserted and no relief valves lifted or ECCS actuated. The plant is stable in mode 3 with RCS temperature and pressure at 547°F and 2235 Psig. There were no radiological releases and no RCS or steam generator tube leaks. All safety related equipment functioned as required and remains operable. The aux feed system started as expected and decay heat is being removed via the steam bypass system to the condenser. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37144 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-07-05 09:20 | 2000-07-05 13:58 | 2000-07-05 | REACTOR CORE COOLING SYSTEM ISOLATION DURING A SURVEILLANCE "On 7/5/2000 at 0920 CDT, the Reactor Core Isolation Cooling (RCIC) System isolated due to a sensed high steam supply line differential pressure. Instrument technicians were performing required surveillance test STP-207-4248 on Division 1 pressure transmitter, E51-PDTN084A. This surveillance requires the transmitter to be hydraulically isolated from the system in order to perform a calibration and also generates a Division 1 RCIC Isolation signal. Per the plant design, the Division 1 and 2 pressure transmitters share a common sensing line. While removing the Division 1 transmitter from service, the Division 2 transmitter, E51-PDTN084B, spiked high causing a Division 2 RCIC isolation signal and subsequent closure of E51-MOVF063, RCIC Steam Supply Inboard Isolation Valve. Although the RCIC system was inoperable for scheduled maintenance at the time of the Division 2 isolation, the containment isolation function was still in service and considered operable. High Pressure Core Spray and all other ECCS systems remained operable while the RCIC system was isolated. RCIC will be returned to service following the completion of the scheduled maintenance activities. The RCIC System Isolation Instrumentation is designated as an Engineered Safety Features system and this event is therefore reportable in accordance with 10CFR50.72." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37143 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-07-05 05:32 | 2000-07-05 13:06 | 2000-07-05 | POSITIVE FOR-CAUSE ALCOHOL TEST A contractor supervisor tested positive for alcohol during a for-cause test upon entering the site. His access was suspended at 0930. The NRC Resident Inspector was notified. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0
37142 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-07-05 11:05 | 2000-07-05 13:01 | 2000-07-05 | POTENTIALLY CONTAMINATED PERSON TRANSPORTED TO THE HOSPITAL "On 7/5/00 at 1105, a potentially contaminated worker was taken offsite by ambulance to John Warner Hospital in Clinton, Illinois. The worker, an Electrician, was working on the Fuel Building bridge on 755' Fuel Building when he passed out. The Electrician was working in a potentially contaminated area. Radiation Protection personnel accompanied the electrician to the hospital but were not able to verify that he was not contaminated at the time he left site to be taken to the hospital. The electrician regained consciousness while on the Fuel Building bridge. At 1132, Radiation Protection personnel frisked the electrician at the hospital and found no contamination on the individual or his clothing. This notification is being made pursuant to 10CFR50.72(b)(2)(v), Offsite Medical." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(v) |  |  |  | 0
37141 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-07-04 11:54 | 2000-07-04 14:13 | 2000-07-04 | THE PLANT HAD ESF ACTUATIONS DUE TO LOSS OF THE "B" RPS BUS. "While operating at 100% power, Susquehanna Unit 2, experienced ESF actuations for containment isolations as a result of an unexpected loss of "B" RPS Bus caused by a trip of the RPS MG Set Output Breaker. All containment isolations associated with a loss of "B" RPS Bus actuated and went to completion. "B" RPS power was swapped to the alternate power supply and affected systems restored to normal configuration." The actuations received were cooling water to recirc pump isolation, RWCU isolation, containment sampling isolation, reactor building secondary containment isolations and coolant sampling isolations. They also had standby gas treatment initiation. The cause of the trip of the MG set is being investigated. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37140 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-07-03 10:20 | 2000-07-03 11:10 | 2000-07-03 | LOSS OF THE 'A' REACTOR PROTECTION SYSTEM BUS CAUSING MULTIPLE AUTOMATIC ACTIONS The unit experienced a loss of 'A' reactor protection system (RPS) bus. RPS motor generator output breakers opened and deenergized the bus, this caused the 'A' standby gas treatment to automatically start. Also the 'A' hydrogen/oxygen monitor isolation valves closed, reactor building ventilation isolated, and the reactor water cleanup system tripped due to isolation valve closure. This trip appears to be "identical" to a trip reported on 6/26/00, event #37119. The licensee has energized the 'A' RPS bus and returned all systems to normal operation with the exception of reactor water cleanup, which is being restored. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37139 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-07-01 00:50 | 2000-07-01 02:01 | 2000-07-02 | SPDS OUT-OF-SERVICE FOR GREATER THAN 8 HOURS "Clinton Power Station's Safety Parameter Display System (SPDS) was inoperable at 1650 on 06/30/00 due to the plant process computer system supporting SPDS was removed from service for maintenance, At 0050 on 7/1/00 the SPDS function is still not restored to operable due to the plant process computer system outage is still in progress. Thus, based on the unavailability of the SPDS function for greater than an 8 hour period, this condition is being reported pursuant to 10CFR50.72(b)(1)(v). The control room operators are monitoring other information sources for the information unavailable on SPDS." The licensee intends to notify the NRC Resident Inspector. * * * UPDATE ON 7/2/00 AT 0530 EDT BY RICH CHEAR TO FANGIE JONES * * * The SPDS was returned to service at 2250 CDT on 7/1/00. The SPDS is now available and operational. The licensee intends to notify the NRC Resident Inspector. The operations officer notified the R3DO (Melvyn Leach) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37138 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2000-06-13 14:00 | 2000-06-30 15:43 | 2000-07-13 | UNIT OUTSIDE OF DESIGN BASIS "On 6/13/00, Vermont Yankee (VY) discovered that a turbine building to radwaste hallway door had been breached open for maintenance activities without proper engineering review. The condition has been corrected. "The door serves as a high energy line break (HELB) barrier such that a HELB in the turbine building would not propagate into the radwaste hallway and cause subsequent failure of masonry block wall between the hallway and the main plant switchgear rooms. Redundant equipment in the switchgear rooms is not qualified for operation in the environment postulated by the TB HELB. "VY review has determined that a compensatory measure to close the door in the event of a HELB that had been established at the time of the maintenance activities would not have provided adequate protection against the postulated HELB. "Based on the above, this condition is reportable in accordance with 10 CFR 50.72(b)(1)(ii)(B) as a condition found during operation that results in a condition that is outside the design basis of the plant." The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTED AT 1831 EDT ON 7/13/00 BY MARK MAGNUSON TO FANGIE JONES * * * "On June 30, 2000 Vermont Yankee reported that a planned compensatory measure associated with a breached door would not have been adequate to protect plant equipment in the unlikely event of a high energy line break in the turbine building. The condition was reported under 10 CFR 50.72(b)(1)(ii)(B) as a condition that was outside the design basis. The associated NRC event number is 37138. "Vermont Yankee has since determined that the door had not been tied open for a period of time greater than the 24 hours allowed by VY technical specifications for equipment that may have been affected by the high energy line break. In addition, VY assessment has concluded that redundant equipment would not have been challenged and that the overall risk of the short term event was minimal. "Based on this information, the 50.72 ENS notification is retracted." The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R1DO (Richard Conte). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37137 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-06-29 21:12 | 2000-06-30 00:28 | 2000-06-30 | OFFSITE NOTIFICATION - FAILURE OF A WARNING SIREN During normal plant operations, a spurious and sustained actuation of siren #7 of the Off Site Emergency Warning System occurred. The actuation was not as a result of personnel actions. Local government agencies were notified. The affected siren actuated at 2112 and was deactivated at 2201. The area covered by the siren has been placed on backup route alerting. The licensee will inform the NRC resident inspector. | 92 | 100 | 0 | 92 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37136 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2000-06-29 16:44 | 2000-06-29 17:06 | 2000-06-29 | UNIT OUTSIDE DESIGN BASIS DUE TO 10 CFR PART 50 APPENDIX R ISSUE "10 CFR 50, Appendix R, Section (III)(L)(5) requires that alternate and dedicated shutdown facilities have the means to achieve and maintain cold shutdown condition within 72 hours. TMI committed to this requirement. "Review of current analysis has determined that the commitment to achieve cold shutdown within 72 hours cannot be met. At 1644 on 6/29/00, this condition has been determined to be reportable under 10 CFR 50.72 (b)(1)(ii)(B), which says 'any event or condition during operation that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded or results in the nuclear power plant being in a condition that is outside of the design basis of the plant.' It has been determined that the equipment is operable, but in a nonconforming condition since the 10 CFR 50 Appendix R requirement to achieve cold shutdown within 72 hours cannot be achieved." The NRC resident inspector has been informed of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37135 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-06-27 | 2000-06-29 16:51 | 2000-06-29 | AGREEMENT STATE REPORT The film badge of a radiographer for Radiographic Specialists, Houston, TX, received an exposure of 5.755R during the period from 5/10/00-6/9/00. The licensee reported that the individual may have left the film badge clipped to his shirt in a high radiation area. The State of Texas is investigating the incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
37134 | 0 | METOREX, INC. |  |  |  |  | 2000-06-28 | 2000-06-29 12:15 | 2000-06-29 | SOURCE RECEIVED WITH SURFACE CONTAMINATION The licensee reported that a gauge containing a 40 mCi Fe-55 source (S/N 6674LG) was received with surface contamination (based upon wipe samples) calculated to be 1.37 µCi. The licensee reported that no contamination was detected on the outside of the shipping package. The source had been shipped to the licensee from AK Steel in Ashland, KY. The licensee has contacted the shipper. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | [10 empty] | NON EMERGENCY | 1 | NJ | MAT | [5 empty] | 0
37133 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-06-28 16:53 | 2000-06-29 12:14 | 2000-06-29 | PLANT FOUND TO BE IN A CONDITION OUTSIDE OF TECHNICAL SPECIFICATIONS "On June 28, 2000, at 1653 hours, it was determined that Containment Penetration M-85 was not properly isolated in accordance with Technical Specification 3.6.3. "On December 25, 1999, the 2A RCS Hot Leg Primary Sampling system Inside Containment Isolation Valve FV-4454 was declared inoperable and was deenergized in the closed position to comply with Technical Specification 3.6.3 Action b. "In order to perform a stroke test on valve FV-4454, on June 12, 2000, at 1246 hours, the associated Outside Containment Isolation Valve FV-4456 was deenergized in the closed position to comply with Technical Specification 3.6.3 Action b, and subsequently on June 13, 2000, at 1012 hours, the equipment clearance order for FV-4454 was lifted and the valve was energized. However, the associated Post Accident Sampling System Outside Containment Isolation Valve FV-2455/2455A for Penetration M-85 was not deactivated in the closed position as required. "This condition was discovered on June 28, 2000, at 1653 hours, during testing and valve line-up verification on the Post Accident Sampling System. Although not deenergized, valve FV-2455/2455A is a normally closed valve and flow through the penetration has occurred briefly during Post Accident Sampling System testing. "On June 28, 2000, at 1700 hours, Inside Containment Isolation Valve FV-4454 was deenergized in the closed position in order to restore compliance with Technical Specification 3.6.3 Action b. "This notification is being made pursuant to Operating License NPF-80 Condition 2.G for operation or condition prohibited by Technical Specifications." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
37132 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-06-29 06:22 | 2000-06-29 09:50 | 2000-06-29 | COURTESY CALL RELATED TO BRUSH FIRE This is a courtesy call regarding a brush fire located in the vicinity of the Columbia Generating Station located within the Department of Energy (DOE) Hanford Area in South Eastern portion Washington State. Columbia Generating Station is monitoring a brush fire (30,000 to 40,000 acres) located 2 to 4 miles west of the station. Currently the local Benton County Emergency Operations Center (EOC) and the DOE EOC are coordinating fire fighting efforts. Current weather forecast anticipate winds climbing to 30 knots with continued hot & dry weather. At present the access roads to the station remain open with the DOE restricting access to essential personnel only. The DOE has indicated that later this morning a substantial increase in federal fire fighting assets will be available to fight the fire. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW | [5 empty] | 0
37131 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-28 08:32 | 2000-06-29 09:05 | 2000-06-29 | BULLETIN 91-01 24 HOUR REPORT Loss of one of two criticality controls was lost in Drum Room of the C-331 building. The controlled parameter is moderation. The temperature control was lost when the door to the room was left open, this allowed the room temperature to drop below the NCSA specified limit of 105 F (the lowest temperature reached was 103 F). The other controlled parameter, pressure, was maintained throughout this event. The cause of the door being left open is under investigation. The plant notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37130 | 0 | SIEMENS POWER CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2000-06-28 21:15 | 2000-06-29 00:55 | 2000-06-29 | ALERT DECLARED - OFFSITE FIRE RANGE FIRE ON AND ADJACENT TO THE HANFORD NUCLEAR RESERVATION HAS PROMPTED BENTON COUNTY EMERGENCY MANAGEMENT, IN CONJUNCTION WITH LOCAL LAW ENFORCEMENT, TO REQUIRE A PRECAUTIONARY EVACUATION OF THE HORN RAPIDS TRIANGLE INDUSTRIAL AREA IN WHICH THE SIEMENS FUEL FABRICATION PLANT IS LOCATED. THE PLANT PRODUCTION HAS BEEN SHUT DOWN. ESSENTIAL PLANT PERSONNEL ARE ONSITE. BASED ON DISTANCE AND CURRENT WIND DIRECTION, THE PLANT IS NOT THREATENED. * * * UPDATE AT 0451 ON 6/29/00 BY PROBASCO, RECEIVED BY WEAVER * * * THE ALERT WAS TERMINATED AT 0150 PDT BECAUSE THE FIRE HAS MOVED FURTHER AWAY FROM THE SITE AND IS CONTINUING TO MOVE IN THAT DIRECTION. NRC NOTIFIED RDO (GOOD); EO (HICKEY); IRO (MILLER); FEMA (STEINDURF); DOE (STAMBAUGH); NRC (TURMAN) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 4 | WA | FUE |  | 50.72(a)(1)(i) |  |  |  | 0
37129 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-06-28 22:24 | 2000-06-28 22:31 | 2000-06-28 | UNIT 2 COMMENCED A TECH SPEC REQUIRED SHUTDOWN AFTER TWO IRPIs IN THE SAME GROUP WERE DECLARED INOPERABLE The following information was received by fax: Notification time: 2231 hrs EDT 6-28-00 Event Notification No.: 37129 NRC Contact: Steve Sandin Cook Caller: SJ Cherba Power Level Prior to event: 79.6% Notification Script: This is Steve Cherba at the Cook Unit 2 Nuclear Plant making a one hour, non-emergency notification for initiation of a nuclear plant shutdown required by Technical Specifications in accordance with 10CFR50.72(b)(1)(i)(A). The shutdown was initiated to comply with TS 3.0.3 @ 2224 hrs EDT on 6-28-00. The TS 3.0.3 one hour limit for initiating a shutdown would have expired @ 2228 hrs EDT on 6-28-00. TS 3.0.3 was entered when it was discovered that the unit had two Individual Rod Position Indicators (IRPIs ) in one group that were INOPERABLE, exceeding the allowable actions of TS 3.1.3.2 a., which only allows a maximum of one INOPERABLE IRPI per rod group. These IRPIs became INOPERABLE when, without any associated rod movement, the indicated rod position drifted above the allowable rod deviation limit. Instrument technicians are in the process of calibrating these IRPIs and we expect to exit this situation within two hours without completing the shutdown. The control rod IRPIs were H12 & M8, both associated with Control Bank D, Group 2. Post Script to this notification: The two IRPIs were calibrated for drift caused by the RCS temperature increase associated with the unit power increase following the outage and are within allowable limits and OPERABLE @ 2250 hrs EDT 6-28-00. The shutdown was halted and power stabilized @ 2250 hrs EDT 6-28-00. NRC resident personnel were informed of the condition and shutdown at 2230 hrs EDT ( J Maynen) & 2240 hrs EDT ( B Bartlett). Power Level when shutdown stopped: 78.9%. | 0 | 79 | 0 | 0 | 79 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37128 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-06-28 20:20 | 2000-06-28 21:08 | 2000-06-28 | SECURITY REPORT SAFEGUARDS SYSTEM DEGRADATION RELATED TO PERIMETER MONITORING. IMMEDIATE COMPENSATORY MEASURES NOT FULLY IMPLEMENTED WITHIN THE TIME REQUIRED BY THE SECURITY PLAN. COMPENSATORY MEASURES NOW ARE FULLY IMPLEMENTED. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR ADDITIONAL DETAILS. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 0
37127 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2000-06-28 12:50 | 2000-06-28 13:19 | 2000-06-28 | MONTHLY SIREN TEST FAILED On 6/26/00 at 0915 EDT, the offsite emergency siren silent test failed at both the Wayne County EOC and the 911 actuation center. Upon arrival of maintenance personnel, the test was completed satisfactorily. Root cause for the test failure has not been determined. The licensee was not notified until 1250 EDT on 6/28/00. There is an investigation in progress to determine the root cause of the test failure. The licensee notified the NRC Resident Inspector and the local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37126 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-06-27 21:25 | 2000-06-27 22:00 | 2000-06-27 | LOSS OF EMERGENCY SIRENS DUE TO ADVERSE WEATHER "At 2125 Notified by Emergency Preparedness that Chatam County lost all Siren Capability for a period of 8 minutes due to a lightning strike. Siren capability has been restored." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37125 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-06-27 15:29 | 2000-06-27 20:35 | 2000-06-27 | MAIN STEAM ISOLATION VALVES CLOSED "The Main Steam Isolation Valves closed due to Low Vacuum closure isolation signal. The low vacuum isolation logic had not been completely bypassed as required by PPM 3.2.1, prior to breaking main condenser vacuum. "The RPV is in Shutdown Cooling at 137°F cooling down to a band of 100 to 120°F. Shutdown cooling was not impacted by the isolation." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37124 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2000-06-27 11:45 | 2000-06-27 17:01 | 2000-06-27 | FITNESS FOR DUTY REPORT INVOLVING CONTRACT EMPLOYEE A CONTRACT EMPLOYEE WAS DETERMINED TO BE UNDER THE INFLUENCE OF AN ILLEGAL DRUG DURING A RANDOM TEST. THE EMPLOYEE'S ACCESS TO THE PLANT HAS BEEN TERMINATED. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR ADDITIONAL DETAILS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.73 |  |  |  | 1
37123 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-06-27 14:00 | 2000-06-27 14:17 | 2000-06-27 | EMERGENCY SIRENS INOPERABLE DUE TO PLANNED MAINTENANCE "PLANNED LOSS OF POWER TO THE NEWINGTON SIREN ACTIVATION CONTROL REPEATER FOR GREATER THAN 1 HOUR. POWER SHOULD BE RESTORED WITHIN 1-2 HOURS. THE EOF LOST CAPABILITY TO ALL 94 SIRENS TO BE ACTIVATED. EACH LOCAL COMMUNITY STILL HAD THE ABILITY TO ACTIVATE THEIR RESPECTIVE SIRENS." THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37122 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-06-27 09:30 | 2000-06-27 12:04 | 2000-06-27 | NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION (NJ DEP) NOTIFIED OF EFFLUENT DISCHARGE TEMPERATURE VIOLATION ON 6/26/00 AT 1844EDT AND 1859EDT, EFFLUENT DISCHARGE TEMPERATURE WAS MEASURED AT 106.62 AND 106.60 DEGREES F. THIS EXCEEDS THE LIMIT OF 106 +0.5 DEGREES F WHICH REQUIRES NOTIFICATION TO NJ DEP. CORRECTIVE ACTION TAKEN INCLUDED LOWERING POWER TO REDUCE EFFLUENT TEMPERATURE. THE LICENSEE ALSO INTENDS TO CHECK THE ALARM SETPOINTS. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 85 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37121 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-06-27 05:30 | 2000-06-27 11:57 | 2000-06-27 | MAIN STEAM ISOLATION VALVES (MSIVs) ISOLATED DUE TO SPURIOUS GROUP 1 ISOLATION SIGNAL "This event is being reported per 10CFR50.72(b)(2)(ii). "At 0530 hours the MSIVs inadvertently isolated due to a spurious group 1 primary containment isolation valve logic (NS4) signal. "In support of required surveillance testing of RPS EPA breakers, RPS 'B' bus had been transferred to normal from its alternate power supply. NS4 'B' isolation logic was inadvertently not reset as part of the restoration following this power supply transfer. When bus RPS 'A' was de-energized as part of the planned transfer to the alternate power supply it caused the NS4 'A' isolation logic relays to de-energize and resulted in a closure signal to all MSIVs. All eight MSIVs closed as expected. "The plant was in Mode 4 at approximately 180°F at the time of the event. Shutdown cooling had been removed from service in preparation for the power supply transfer. Following reset of the NS4 isolation logic. shutdown cooling was restored with the reactor coolant temperature at approximately 187°F. The MSIVs may be re-opened as needed," The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37120 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-26 12:40 | 2000-06-27 08:36 | 2000-06-27 | NRC BULLETIN 91-01 RESPONSE (24-HOUR REPORT) The following text is a portion of a facsimile received from Portsmouth personnel: "At 1240 hours on 06/26/00, it was discovered that a Nuclear Criticality Safety Approval (NCSA) requirement had not been met during sampling and batching operations in the X-710 building. The contents of four polybottles were batched into two five-gallon containers without adequate documentation showing that the sampling data was for Nuclear Criticality Safety purposes. A review of the sample results indicated that all the results did not meet the NCSA requirements for independent measurements. This violated NCSA-PLANT053.A03 requirement #13 which states, 'The results of sample analysis or NDA (Non-Destructive Assay) measurements shall not be used for NCS purposes if the documentation does not show that the results were determined as NCS significant results.' (Basis: The measurements and analysis must be performed to independent criteria to be acceptable for NCS purposes.)" "Two independent measurements of mass of the batching material are required to ensure double contingency. Only one independent measurement of mass was available. The other measurement did not meet independent criteria per NCSA requirements. The absence of a second independent measurement constituted a loss of one control of the double contingency principle." "A second independent measurement was performed, and compliance was reestablished with NCSA-PLANT053.A03 at 1557 hours on 06/26/00." "SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is very low. The total U235 involved in each of the two batches [is] 0.2154 grams and 2.1868 grams, respectively. To re-establish NCS compliance, repeat NCS measurements for each batch were performed to confirm that the total mass meets the requirements of NCSA-PLANT013, Batching Solutions and Solids." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): Prior to batching the contents in accordance with NCSA-PLANT013, documentation of analysis results are checked to ensure that the measurements were handled as 'NCS Significant' and independently analyzed in accordance with NCSA-PLANT053. Without independent results, a single measurement error could result in more than a safe mass being batched into a container. If this mass were then subject to the correct geometry, moderation, and reflection conditions, a criticality could occur." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Mass is the only controlled parameter. Two independent measurements of mass are required to ensure double contingency. Since independence of NDA mass measurements is called into question, only one independent estimate of mass is available. The absence of a second independent NDA mass measurement represents a loss of one double contingency control." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The total U235 involved in each of the two batches [is] 0.2154 grams and 2.1865 grams, respectively. Uranium mass is measured in batching operations to ensure the U235 mass in the final container is less than 350 grams U235 which is less than half the minimum critical mass at 100% enrichment and optimum moderation, geometry, and reflection conditions." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Nuclear criticality safety controls include independent mass measurements of U235. Failure to ensure that NCS significant measurements were used lead to a potential failure of the measurements." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: A second independent NDA measurement was performed to verity total mass of U235 (<1 gram per bucket/container). Compliance with NCSA-Plant053.A03 was re-established at 1557 hours based on the results of the NDA measurements." Portsmouth personnel notified the NRC resident inspector and the site Department of Energy manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37119 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-06-26 23:22 | 2000-06-27 01:14 | 2000-06-27 | PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATIONS DUE TO THE TRIPPING OF ELECTRICAL PROTECTION ASSEMBLIES (EPA) AND SUBSEQUENT HALF SCRAM The following text is a portion of a facsimile received from the licensee: "[The unit experienced a loss] of [the] 'A' [reactor protection system (RPS)] bus[. Output] EPAs tripped causing [this 120-volt AC] bus to de-energize. This caused the reactor building ventilation to isolate[,] both [standby gas treatment systems (SBGT)] to start[, and the] 'A' [hydrogen/oxygen (H2/O2)] monitor to trip (PCIS valves). [The reactor water cleanup (RWCU)] system tripped on low flow due to 12MOV-15 closure (PCIS valve)." The licensee stated that there was nothing unusual or not understood and that all systems functioned as required. The licensee also stated that the cause of this event is currently under investigation. The EPAs tripped under normal supply, and the RPS motor-generator set was functioning properly. There were no maintenance or surveillance activities underway at the time of the event. The reactor building and H2/O2 analyzers have since been un-isolated. SBGT is currently under normal operation and is being used for venting. RWCU has not yet been restored to normal. The licensee plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37118 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-06-26 20:58 | 2000-06-26 22:17 | 2000-06-27 | LOSS OF A SIGNIFICANT PORTION OF OFFSITE EMERGENCY SIRENS "NOTIFIED BY EMERGENCY PLANNING PERSONNEL THAT AS OF 2058[EDT] ON 6/26/00, NINETEEN [19] OFFSITE SIRENS HAD BEEN LOST. AS OF 2158[EDT] EFFORTS TO RESTORE ARE STILL IN PROGRESS. OF THE NINETEEN [19], SIXTEEN [16] ARE IN DELAWARE AND THREE [3] ARE IN NEW JERSEY. THE NINETEEN [19] SIRENS REPRESENTS LOSS OF GREATER THAN 25% OF THE TOTAL OF SEVENTY-ONE [71] SIRENS." THE LICENSEE COULD NOT IDENTIFY THE CAUSE, HOWEVER, THEY ARE CURRENTLY EXPERIENCING ADVERSE WEATHER. THIS REPORT ALSO AFFECTS THE HOPE CREEK STATION. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. ********** UPDATE AT 0043 ON 06/27/00 FROM STEVE SAUER TO LEIGH TROCINE ********** At 2340 on 06/26/00, the licensee was notified that the bulk of the offsite emergency sirens (all but three) had been restored to service. The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R1DO (Morris). | 92 | 100 | 0 | 92 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37117 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-06-26 18:53 | 2000-06-26 19:23 | 2000-06-27 | UNIT MANUALLY TRIPPED FOLLOWING A LOSS OF THE "A" MAIN FEEDWATER PUMP (MFP) AT 1900EDT ON 6/26/00, THE UNIT EXPERIENCED A PLANT SETBACK TO 55% POWER FOLLOWING THE LOSS OF THE "A" MFP. OPERATORS INSERTED A MANUAL REACTOR TRIP AS STEAM GENERATOR LEVELS APPROACHED THE LOW LEVEL TRIP SETPOINT. ALL SYSTEMS FUNCTIONED AS REQUIRED WITH ALL CONTROL RODS FULLY INSERTING. EMERGENCY FEEDWATER (EFW) ACTUATED AS EXPECTED. THE MAIN CONDENSER IS AVAILABLE ACCEPTING DECAY HEAT VIA STEAM BYPASS. NO PRIMARY/SECONDARY SAFETIES/RELIEFS LIFTED DURING THE TRANSIENT. ALL THREE OFFSITE POWER SOURCES ARE AVAILABLE. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR AND WILL ISSUE A PRESS RELEASE. ********** UPDATE AT 0015 ON 06/27/00 FROM DAMON RITTER TO LEIGH TROCINE ********** The licensee updated this event notification to document an abnormal post-trip response and to correct the event time. The following text is a portion of a facsimile received from the licensee: "Subsequent to the trip, one channel of intermediate and source range nuclear instrumentation did not energize. The cause is under investigation. [The licensee stated that this did not place the unit in a limiting condition for operation because there was still one channel in operation.] Additionally, the event time for the event notification is corrected. The reactor trip was initiated at 1853 [on] 26 June 2000 [in lieu of 1900]." The licensee plans to notify the NRC resident inspector. The NRC operations officer notified the R1DO (Morris). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37116 | 0 | INGERSOLL-DRESSER PUMP COMPANY |  |  |  |  | 2000-06-26 | 2000-06-26 16:30 | 2000-06-26 | PART 21 REPORT INVOLVING A DESIGN DEFECT IN A SPLIT RING RETAINER (DRAWING B65573) "This report is written to satisfy the requirements of paragraph 21.21.4. The numbering of the information given here correlates with the numbering in 21.21.4: (i) Bill Shaffer Director of Operations Ingersoll-Dresser Pump 5715 Bickett Street Huntington Park, CA 90255 (ii) Split Ring Retainer Drawing B65573 Rev. (iii) Ingersoll-Dresser Pump 5715 Bickett Street Huntington Park, CA 90255 (iv) The Split Ring Retainer (Drawing B65573 Rev. 0) specifies a drilled and counter bored bolt hole diameter too large to allow the bolting to secure this retainer in its intended position. Based on an evaluation of this condition, it has been determined that this design defect could allow the subject Split Ring Retainer and other adjacent parts including the Split Ring Retainer bolting, split ring and pressure reducing sleeve to move out of position. This could result in a seal failure or a catastrophic pump failure. (v) IDP Huntington Park was informed of this defect on 6-22-00. (vi) Three defective split ring retainers were manufactured. The location of all three are known to IDP-HP. Three were shipped to STP Nuclear Operating Co. One of the defective split ring retainers was installed and put into service at STP. (vii) On June 23rd Dennis Stark of STP was notified of the defective split ring retainer and that it could result in a catastrophic failure. Replacement split ring retainers with corrected design will be ship[ed] by June 30, 2000. (viii) IDP-HP advised Dennis Stark of STP that the pump with the installed defective split ring retainer should be taken out of service." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0
37115 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-06-13 10:30 | 2000-06-26 14:20 | 2000-06-26 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER GAUGE The following information was received via fax (event report #WA-00-022): This is notification of an event in Washington state as investigated by the WA Department of Health, Division of Radiation Protection. STATUS: new Licensee: Washington Department of Transportation City and state: Seattle, WA License number: WN-L073-1 Type of license: Portable Gauge Date of event: 6/13/00 Location of Event: Lynnwood, WA ABSTRACT: At approximately, 10:30 AM, a construction contractor working for the Washington Department of Transportation (DOT) drove a bulldozer over a Troxler Model 3430 moisture/density gauge adjacent to the northbound off ramp at exit 186 on Interstate 5. The exact cause of the accident is not known at this time. However, an underlying cause seems to be the constant pressure to keep working. This brings huge machinery and tiny testing equipment into the same area at the same time. The gauge was in use at the time with the 8 millicuries Cs-137 source extended from the gauge body which also contains a 40 millicuries Am-241/Be source. A representative from the Division of Radiation Protection (DRP) was on the scene by 11:30 AM. The local Fire Department, the State Patrol and at least one news crew also responded. The work site was stopped and both off ramps and the overpass were closed by the Fire Department as an additional precaution. The DRP representative determined that the impact demolished the gauge and jammed the extended source so that it could not be returned to the shielding. The DRP representative assisted the licensee in securing the sources in the transport box and filling it with dirt to provide additional shielding. The sources were transported to the Olympia DOT Materials Lab where proper shields were available. The sources will remain there until the manufacturer sends an appropriate shipping container. DOT issued a press release and coverage appeared on television and in local and regional newspapers. What is the notification or reporting criteria involved? WAC 46-221-250 (damaged equipment) Activity and isotope(s) involved: 8 mCi Cs-137 and 40 mCi Am-241/Be Overexposures? none Lost, Stolen or Damaged? Damage to Troxler Model 3430 portable gauge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37114 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-06-26 08:25 | 2000-06-26 12:05 | 2000-06-26 | UNIT EXPERIENCED AN AUTOMATIC REACTOR SCRAM FOLLOWING A TRIP OF THE MAIN TURBINE "MAIN TURBINE TRIP RESULTING IN AUTOMATIC REACTOR SCRAM. ALL RODS INSERTED. TWO MAIN STEAM RELIEF VALVES AUTOMATICALLY OPENED ON HIGH PRESSURE. EMERGENCY OPERATING PROCEDURES WERE ENTERED ON LOW REACTOR LEVEL [+13 INCHES]. BYPASS VALVE #1 OPENED AND STUCK OPEN RESULTING IN REACTOR PRESSURE DECREASE TO APPROXIMATELY 500 PSIG. COOLDOWN RATE WAS NOT EXCEEDED. THE BYPASS VALVE IS CURRENTLY CLOSED. REACTOR WATER LEVEL INCREASED ABOVE LEVEL 8 [+54.5 INCHES]. PRESSURE CONTROL IS CURRENTLY ON SRVs [SAFETY RELIEF VALVES]. LEVEL CONTROL IS CURRENTLY ON CONDENSATE AND BOOSTER PUMPS. ALL SYSTEMS STABLE." ALL SAFETY-RELATED EQUIPMENT IS AVAILABLE, IF NEEDED. ELECTRICAL LOADS ARE CURRENTLY SUPPLIED BY OFFSITE POWER. ONE TRAIN OF SUPPRESSION POOL [SP] COOLING IS IN OPERATION MAINTAINING SP TEMPERATURE AT 86 DEGREES F. THE LICENSEE IS INVESTIGATING THE CAUSE OF THE MAIN TURBINE TRIP AND FAILURE OF THE #1 BYPASS VALVE TO CLOSE. THERE WAS NO ELECTRICAL MAINTENANCE OR SURVEILLANCE TESTING IN PROGRESS PRIOR TO THE MAIN TURBINE TRIP. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37113 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-06-25 23:53 | 2000-06-26 01:28 | 2000-06-26 | LOSS OF POWER TO AT LEAST 13 OF 43 EVACUATION PUBLIC NOTIFICATION SYSTEM SIRENS FOR APPROXIMATELY 20 MINUTES FOLLOWED BY SIRENS FALSELY IN ALARM FOR ABOUT 4 MINUTES Tensas Parish in Louisiana reported a loss of power to evacuation public notification system sirens. At least 13 of 43 sirens lost power for approximately 20 minutes, and upon restoration, the sirens were in alarm for approximately 4 minutes. Local public address station KNOE was notified of the false alarm by Tensas Parish. The system has been restored to normal. All systems functioned as required once power was restored. The licensee made applicable local and media notifications and plans to notify the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37112 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-06-25 17:45 | 2000-06-25 20:27 | 2000-06-27 | PLANT MADE NOTIFICATION TO THE NATIONAL RESPONSE CENTER AND THE ILLINOIS EMERGENCY MANAGEMENT AGENCY OF AN OIL SPILL. These notifications were made due to a small quantity of oil in the runoff ditch. The quantity of oil is estimated to be 5 gallons and was due to an overflow of their lube oil separator. Cleanup efforts are in progress. The NRC Resident Inspector was notified. * * * UPDATE ON 6/27/00 AT 1240 EDT BY CAL WALRATH TO FANGIE JONES * * * The licensee made a press release and notified the NRC Resident Inspector and the state and local authorities of the press release. The operations officer notified the R3DO (Melvyn Leach). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37111 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-06-23 01:00 | 2000-06-23 20:54 | 2000-06-23 | THE LICENSEE NOTIFIED THE NATIONAL MARINE FISHERY SERVICE OF A TRAPPED LOGGERHEAD SEA TURTLE. THE LICENSEE FOUND A LIVE LOGGERHEAD SEA TURTLE AT THE DILUTION STRUCTURE INTAKE TRASH BARS, REMOVED AND TRANSPORTED IT TO THE MARINE MAMMAL STRANDING CENTER. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37110 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-06-23 16:17 | 2000-06-23 19:33 | 2000-06-23 | REACTOR SCRAM FROM 100% POWER DUE TO TURBINE TRIP. During normal reactor operation at 100% power a turbine trip occurred causing a reactor SCRAM. A reactor recirc pump trip initiated and functioned normally. Four SRVs and both bypass valves opened to initially control reactor pressure. No. 1 bypass valve remained open for subsequent pressure control. The reactor vessel level transient (164 to 198 inches) resulted in a low level (170 inches) Group 2, 3, and 4 isolations. Subsequent to the reactor SCRAM, a Reactor Feed Pump and HPCI turbine high level trip occurred (HPCI was not running at this time) at 211 inches. Operator took action to restore reactor vessel level and restart the 'B' reactor feed pump. The exact cause of the turbine trip is unknown at this time. An intermittent 125 VDC Div 1 ground occurred following the SCRAM which is also under investigation. A reactor recirc pump could not be restarted due to a high temperature difference and a normal cooldown was initiated to mitigate concerns of thermal stratification. All rods fully inserted and the condenser is being used as the heat sink. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37109 | 0 | US AIR FORCE |  |  |  |  | 2000-06-23 11:00 | 2000-06-23 12:54 | 2000-06-23 | THE US AIR FORCE REPORTED 18 LOST/STOLEN LENSATIC COMPASSES. In March, 2000 the Air Force recalled all lensatic compasses NSN 6605-00-151-5337 and Barksdale AF Base, La. inadvertently sent 17 of these compasses to the Defense Reutilization Management Organization (DRMO) in Texarkanna,Tx. DRMO has no record of receiving these 17 compasses from Barksdale AFB. Since this time, Barksdale base supply had collected 3 more of these compasses and as of 6/3/00 one has been identified as being missing. Each of these 18 missing compasses contain 120 millicuries or less of tritium. Barksdale base supply is conducting an intense search for these compasses. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | LA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
37108 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-06-22 16:16 | 2000-06-22 21:40 | 2000-06-22 | AT 1616 PDT ON 06/22/00, THE LICENSEE NOTIFIED THE CALIFORNIA OFFICE OF EMERGENCY SERVICES AND THE SAN DIEGO DEPARTMENT OF ENVIRONMENTAL HEALTH OF A SODIUM HYPOCHLORIDE LEAK. At 0830 PDT on 06/22/00, a 3 to 5 gpm leak occurred from the Unit 2 sodium hypochloride storage tank. As a precaution, the licensee evacuated nonessential personnel from the area of the leak. The spilled liquid was fully contained by a berm around the tank. This event did not pose a threat to the nuclear power plant or hamper site personnel in the performance of duties necessary for safe plant operation. Even though there was no threat to control room personnel and plant conditions did not require it, at 1005 PDT, operators manually initiated Toxic Gas Isolation Signal (TGIS) as a precautionary measure in response to changing wind direction. (TGIS is designed to terminate the supply of outside air to the control room and initiate operation of the control room emergency HVAC system to minimize operator exposure.) All system components operated as expected. The event was terminated at approximately 1145 PDT. There were no injuries. The NRC Resident Inspector will be informed by the licensee. |  | 100 | 100 |  | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37107 | -1 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-06-22 14:07 | 2000-06-22 18:07 | 2000-07-19 | THE PLANT ENTERED A 14 DAY LCO ACTION STATEMENT DUE TO HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM BEING DECLARED INOPERABLE. During routine surveillance testing of the Containment Cooling Water System (CCWS), required system flow through the HPCI Room Cooler could not be obtained due to leakage past 2-3999-252 check valve. With the HPCI Room Cooler inoperable, the HPCI System was declared INOPERABLE, a 14 day LCO Action Statement was entered, and an action request for repair of the 2-3999-252 valve was submitted. The NRC Resident Inspector was notified by the licensee. * * * UPDATE AT 1917 ON 07/19/00 BY MARK RUNION TO JOLLIFFE * * * Upon further review of this event by Dresden Operations and Engineering Department personnel, the licensee determined that with the HPCI Room Cooler blower available, even without CCWS flow to the HPCI Room Cooler, the HPCI System will perform its required function and remain operable. Thus, the HPCI System was not inoperable at the time of the notification of this event and therefore, this event is not reportable to the NRC. Based on this, the licensee desires to retract this event. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO Mike Parker. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37106 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-22 11:00 | 2000-06-22 17:43 | 2000-06-22 | At 1100 hours on 06/22/00, it was determined by the Plant Shift Superintendent, Engineering, and Nuclear Regulatory Affairs that Criticality Accident Alarm System Technical Safety Requirement (TSR) required actions were not entered as required. The concern was whether a TSR Limiting Condition for Operation (LCO) should be entered prior to performing Safety Analysis Review required horns and light testing. All previous testing has correctly been accomplished under site operability procedures, even though no LCO actions were initiated due to taking credit for the nitrogen system. The issue was raised due to the fact that when the cascade strombos horns are sounding, the nitrogen horns could not be heard to meet required LCO requirements. Currently, all plant site Criticality Accident Alarm Systems are fully operable. This condition is reportable to the NRC per 10CFR76.120(c) "Safety Equipment Failure/Actuation". The equipment is required by a TSR to be available and operable and no redundant equipment is available and operable to perform the required safety function. The DOE Site Representative and NRC Resident Inspector were notified by the licensee.. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
37105 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2000-06-22 15:13 | 2000-06-22 17:26 | 2000-06-22 | THE LICENSEE ISSUED THE FOLLOWING PRESS RELEASE REGARDING A FIRE IN A PLANT SUPPORT BUILDING: "BURLINGTON, KS - A small, localized fire occurred early this afternoon at Wolf Creek Generating Station. The fire was contained in the welding area of a support building about 150 yards from where electricity is generated. The fire appears to have originated from an equipment malfunction. No injuries were reported. The plant's fire brigade responded and with assistance from the Coffey County Fire Department, quickly extinguished the fire. The fire was extinguished at about 1:41 p.m. The equipment, a plasma-arc cutter, is used to cut metal such as stainless steel. Workers were cutting one and one-half inch stainless when the fire started. Wolf Creek Nuclear Operating Corporation operates Wolf Creek Generating Station near Burlington, Kan. Wolf Creek is owned by Kansas City Power & Light Company; KGE, a Western Resources Company; and Kansas Electric Power Cooperative, inc. The plant is in Coffey County, Kansas, about four miles northeast of Burlington. The plant is 55 miles south of Topeka, 90 miles southwest of Kansas City, and 120 miles northeast of Wichita." The fire lasted for approximately 20 minutes (1321-1341 CDT) and the only damage was to the piece of equipment. The NRC Resident Inspector was notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37104 | 0 | GEORGE WASHINGTON UNIV. HOSPITAL |  |  |  |  | 2000-06-14 14:30 | 2000-06-22 16:51 | 2000-06-22 | GEORGE WASHINGTON UNIVERSITY HOSPITAL REPORTED AN UNDERTREATMENT DURING BRACHYTHERAPY. THE HOSPITAL REPORTED THAT A FEMALE PATIENT WAS BEING TREATED WITH CESIUM 137 SEEDS IN THE FIRST OF A TWO PHASE TREATMENT SEQUENCE WITH EACH DELIVERING APPROXIMATELY 1,680 RADS. DURING THIS TREATMENT THE DEVICE THAT CONTAINED THE SEEDS SLIPPED OUT OF THE AREA BEING TREATED. IT IS NOT KNOWN WHEN THIS ACTUALLY OCCURRED, BUT THE UNDERTREATMENT COULD HAVE LASTED BETWEEN 3.25 - 6 HOURS. THEY ARE ESTIMATING THAT THE PATIENT MAY HAVE ONLY RECEIVED 1,478.5 RADS. A CORRECTION FOR THIS UNDERTREATMENT CAN BE DONE DURING THE SECOND PHASE. THERE ALSO MAY HAVE BEEN OTHER AREAS NOT DESTINED FOR TREATMENT THAT WERE EXPOSED TO THE RADIATION WHEN THE DEVICE SLIPPED. THE PATIENT HAS BEEN REEXAMINED A WEEK FOLLOWING THIS MISADMINISTRATION AND NO ADVERSE AFFECTS WERE DETERMINED. A SECOND FOLLOWUP EXAMINATION WILL BE DONE WITHIN A WEEK. THE PATIENT WAS INFORMED AND THE ATTENDING PHYSICIAN WAS NOTIFIED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.33 |  |  |  | 0
37103 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2000-06-21 10:00 | 2000-06-22 11:18 | 2000-06-22 | AGREEMENT STATE REPORT - DAMAGED CPN PORTABLE MOISTURE DENSITY GAUGE At 1000 on 06/21/00, a CPN portable moisture density gauge belonging to David V. Lewin Corporation, Cleveland, OH, was damaged at a construction site at State Route 91 a mile north of Twinsburg, OH. The gauge had been struck by a backhoe while the Cs-137 source was extended from the gauge. The gauge is a CPN model MC3 containing a 10 mCi Cs-137 source and a 50 mCi Am-241 source. The gauge was damaged in a way that prevented the Cs-137 source from being secured in the safe position. The licensee contacted CTS, license #03225230000, a licensed gauge repair facility for advice. Ohio Department of Health inspectors were dispatched to the site to monitor the recovery. CTS recommended that the guide tube be cut which would allow the Cs-137 source to be retracted into the safe position. The guide tube was cut and the source was secured in the safe position. The source was not damaged and no contamination was detected. Dose rates with the source extended were 350 mrem/hr. The gauge was taken back to the David V. Lewin Corporation and will be shipped to CTS for evaluation and possible repair. The licensee will issue a report to the Ohio Department of Health within 30 days. Ohio Report #00-019. Mike Snee notified NRC Region 3 Jim Lynch. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | DAMAGE MEASURE GAUGE | [8 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0
37102 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2000-06-22 07:28 | 2000-06-22 09:57 | 2000-06-22 | - AUTO REACTOR SCRAM FROM 98% POWER CAUSED BY LOSS OF REACTOR FEEDWATER PUMP - At 0728 CDT on 06/22/00, LaSalle Unit 2 experienced an automatic reactor scram from 98% power due to low reactor vessel water level (+12.5 inches, Level 3). Normal reactor vessel water level is +36 inches. The low reactor vessel water level was caused by a loss of the #2A turbine driven reactor feedwater pump for unknown reasons. The lowest reactor vessel water level reached was -23 inches on the wide range recorders. All control rods inserted completely. Steam is being dumped to the main condenser. No emergency core cooling system actuations occurred or were required during the transient. All systems operated as designed with the exception of the Unit 2 station air compressor, which went into a surge condition. The air compressor has been secured and the Unit 0 station air compressor was started to pick up the additional load. Unit 2 is stable in Condition 3 (Hot Shutdown) with reactor vessel water level and pressure being maintained in their normal bands. The licensee is investigating the cause of the #2A reactor feedwater pump loss. This event had no effect on Unit 1 which is at 100% power. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37101 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-06-21 06:30 | 2000-06-21 11:01 | 2000-06-23 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE OWNED BY PROFESSIONAL ENGINEERING & INSPECTION COMPANY, INC. (PEICO) LOCATED IN PLANTATION, FLORIDA The following text is a portion of a facsimile received from the Florida Bureau of Radiation Control about the theft of a Troxler Soil/Moisture Density Gauge, Model #3440, Serial #13201, Isotope(s): Cs-137 (8.0 mCi); Am-241:Be (40 mCi): "Licensee: Professional Engineering & Inspection Company, Inc. (PEICO) "Incident Location: 1385 S.W. 19th St., Miami, Florida 33145 "Incident Description: Licensee reported that a gauge was stolen from a technician's home at approximately 6:30 am.. The technician had come to work and noted that his first job was later in the morning, so he returned home for breakfast. When he came out of his home he noticed that the container, gauge and the securing cable and lock were missing. The keys were not stolen. The Miami Police Department and the Florida Bureau of Radiation Control are investigating. "Miami PD case #173-1159Z "Office: Environmental Radiation Control "Date: Time Investigated: 21-June-00; 0930" Call the NRC operations officer for contact information. * * * UPDATE ON 6/23/00 @ 1323 BY EAKINS TO GOULD * * * The gauge was found in the early morning on 6/23/00 outside of a locked gate to a salvage yard. The gauge appeared to be intact and the licensee has it in possession and will conduct a leak test. Notified Reg 2 RDO(Barnhard) and NMSS EO(Ramsey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37100 | 0 | DNX TRANSGENIC SCIENCES |  |  |  |  | 2000-06-07 11:00 | 2000-06-21 10:35 | 2000-06-21 | - LOSS OF LICENSED MATERIAL - On 06/02/00, one vial of 500 µCi of [alpha-32] deoxycytidine 5'-Triphosphate (dCTP) was received at DNX Transgenic Sciences, Cranbury, NJ. The concentration of the material was 10 µCi/µl. Upon arrival, this vial was designated as vial #153. At 1130 on 06/07/00, Roland Felkner, a DNX Transgenic Sciences research associate, was planning to remove 50 µCi of material from this vial to do a DNA labeling experiment. However, he discovered that there was no material in the vial. According to the isotope inventory log of vial #153, there should have been 150 µCi of the 500 µCi still available in the vial. Upon investigation, it was determined that 200 µCi, rather than 150 µCi, was actually missing. This error is attributed to a computational mistake made in the log by another research associate. Joe D'Ippolito, DNX Transgenic Sciences Radiation Safety Officer (RSO), interviewed lab personnel, conducted a survey of the lab area and performed an internal investigation to locate the missing material. There was no indication of radiation exposure to lab personnel. Based on the results of the investigation, the RSO and members of the DNX Transgenic Sciences Radiation Safety Committee believe that less material had been sent in vial #153 by their supplier, NEN Life Science Product, than was reported on the vial label. The RSO is continuing his investigation and will determine corrective actions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37099 | 0 | NC DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-06-20 15:10 | 2000-06-21 10:28 | 2000-06-21 | - TROXLER MOISTURE DENSITY GAUGE RUN OVER BY A TRUCK - A truck owned by APA Construction Company backed over a Troxler Moisture Density Gauge, Model #4640, Serial #1717, at State Road 1554, Siler City, NC. The gauge sources, 8 millicuries Cs-137 and 40 millicuries Am-241-Be, were not damaged and are in their shielded position. The gauge appeared to be functioning properly. The licensee plans to send the gauge to Troxler for inspection/repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | DAMAGE MEASURE GAUGE | [8 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0
37098 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2000-06-21 02:57 | 2000-06-21 05:08 | 2000-06-21 | - MANUAL REACTOR TRIP FROM 68% POWER DUE TO UNISOLABLE EHC SYSTEM OIL LEAK - At 0257 on 06/21/00, control room operators manually tripped the plant from 68% power due to an unisolable electrohydraulic control (EHC) system oil leak which caused main turbine control valve oscillations. Two control rod bottom lights, shutdown bank 'A' and control bank 'C' did not illuminate; however, the control rod position indications showed that all control rods were fully inserted into the core. The auxiliary feedwater system actuated, as expected. Steam is being dumped to the main condenser. The plant is stable in Mode 3 (Hot Standby). The licensee is repairing the oil leak and investigating the problem with the control rod bottom lights. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37097 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-06-20 16:31 | 2000-06-20 18:45 | 2000-06-20 | MANUAL REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL DUE TO INADVERTENT CLOSURE OF MAIN FEEDWATER ISOLATION VALVE The plant suffered an inadvertent closure of the 'A' Main Feedwater Isolation Valve (MFIV) for an unknown reason, investigation in progress. The licensee initiated a manual reactor trip before the automatic reactor trip for low steam generator level could initiate, all rods fully inserted. The three Auxiliary Feedwater (AFW) Pumps automatically started due to the reactor trip and reduced feedwater flow. The plant has been stabilized in Mode 3 pending completion of troubleshooting of the 'A' MFIV closure. Heat removal is via the steam dumps to the main condenser with feed flow from the AFW pumps. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37096 | 0 | US STEEL, GARYWORKS |  |  |  |  | 2000-06-20 09:30 | 2000-06-20 15:00 | 2000-06-20 | POSSIBLE DAMAGED GAUGE ON PLATE LINE A Daystrom manufactured gauge, serial number 3014 with 20 curies of Cs-137, the north gauge on the plate line was struck by a moving plate on the water cooling jacket. There is no apparent damage to the gauge, radiation monitoring did not indicate anything unusual. The service company, Radiometry, has been contacted and will be at the plant tomorrow to check the gauge for damage. US Steel intends to submit a written report to the NRC within thirty days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT | [5 empty] | 0
37095 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2000-06-19 15:25 | 2000-06-19 16:22 | 2000-06-22 | PLANT SHUTDOWN REQUIRED BY TECH SPEC 3.0.3 DUE TO FAILED VALVE TESTING The licensee was conducting Instrument and Control testing under DB-MI-03211 which failed to produce the expected response for solenoid SP6A2 on valve SP6A, Steam Generator Main Feedwater Valve. The problem is with the solenoid or associated limit switch. Due to a lack of specific Technical Specification guidance, 3.0.3 has been entered which requires the plant to initiate action to place the plant in a mode in which the specification does not apply. It is expected that the plant will be able to repair and test prior to a full plant shutdown. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1710 EST ON 6/19/00 BY CRAIG GILLIG TO FANGIE JONES * * * The licensee determined the problem was with the limit switch, has exited the tech spec required shutdown, and is returning to full power from 96%. The licensee intends to notify the NRC Resident Inspector. The R3DO (Roger Lanksbury) has been notified. * * * UPDATE ON 6/22/00 @ 1334 BY WOLF TO GOULD * * * RETRACTION The suspect limit switch for solenoid valve SVSP6A2 has been adjusted and satisfactorily tested via Surveillance Test DB-MI-03211. This testing confirmed that the problem was only with the limit switch. The solenoid valve and associated Steam Generator Main Feedwater Control Valve SPGA remained operable during this event. Therefore, the plant was not in the Action Statement for Technical Specification 3.0.3, and no plant shutdown was required. Therefore, the licensee desires to retract this event. The NRC Resident Inspector has been notified of the retraction by the licensee. The Reg 3 RDO (Lanksbury) was informed by the NRC Operations Officer. | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37094 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2000-06-19 11:30 | 2000-06-19 14:51 | 2000-06-19 | POTENTIAL PERSONNEL OVEREXPOSURE A technician opened a "package" on the loading dock to check the contents after an apparent miscommunication. The package contained 1650 curies of Co-60 in a shielded container. The technician received an undetermined dose to the head and shoulder areas of the body, possibly in excess of 5 rem. The dose will be determined but there is a good chance that it will be less than 5 rem. Even after removal of the outer plug there was still 1.125 inches of tungsten shielding. The Massachusetts Radiation Control Program plans to go to the site and conduct an investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | PERS OVEREXPOSURE/TEDE >= 5 REM | [8 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  | 20.2202(b)(1) |  |  | 0
37093 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-06-17 11:15 | 2000-06-17 13:00 | 2000-07-14 | UNIT ENTERED A TECH SPEC REQUIRED SHUTDOWN AFTER DECLARING BOTH CONTAINMENT SPRAY TRAINS INOPERABLE "BOTH LOOPS OF RHRSW (RESIDUAL HEAT REMOVAL SERVICE WATER) WERE DECLARED INOPERABLE DURING THE FILL PROCESS FOLLOWING MAINTENANCE ON '14' RHRSW PUMP MOTOR. PER TECH 3.5.C.3, BOTH LOOPS OF CONTAINMENT SPRAY/COOLING WERE DECLARED INOPERABLE REQUIRING A REACTOR SHUTDOWN AND TEMPERATURE LESS THAN 212°F IN 24 HOURS. INITIAL INVESTIGATION ASSUMES THE DISCHARGE CHECK VALVE ON THE '14 RHRSW PUMP DID NOT SEAT. AT THIS TIME THE 'A' LOOP OF RHRSW HAS BEEN RESTORED AND THE PLANT IS IN A 7 DAY LCO." THE UNIT ENTERED AND EXITED THE SHUTDOWN ACTION STATEMENT AT 1115CDT AND 1130CDT, RESPECTIVELY WITH NO POWER REDUCTION OCCURRING. THE LICENSEE WILL INFORM STATE/LOCAL AGENCIES AND THE NRC RESIDENT INSPECTOR. * * * RETRACTED ON 7/14/00 AT 1640 EDT BY JIM McCAY TO FANGIE JONES * * * "This notification retracts a notification made 6/17/00 for both loops of RHRSW being declared inoperable due to low system standby pressure. The original notification should have been made under 10CFR50.72 (b)(2)(iii) , as a condition that alone could have prevented fulfillment of a safety function, rather than under 10CFR50.72 (b)(1)(a) as initiation of a plant shutdown required by Tech Spec. No plant shutdown was initiated. The low RHRSW standby pressure condition is a concern with respect to voids forming in the piping system with subsequent water hammer during pump start. Review of system response when 'A' loop was returned to service indicated no voiding had occurred and 'A' loop or RHRSW was operabie during the event. Thus, the 'A' loop could have performed the required safety functions of RHRSW and the condition is not reportable." The licensee notified the NRC Resident Inspector and the state and local authorities. The NRC Operations Officer notified the R3DO (Bruce Jorgensen). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37092 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2000-06-05 15:30 | 2000-06-16 18:07 | 2000-06-16 | AGREEMENT STATE REPORT INVOLVING A LEAKING NI-63 SOURCE While performing a routine wipe test on 3/9/2000 of a Varian Gas Chromatograph Detector Cell at the Utah State University in Logan, UT, leakage from the 8 mCi Ni-63 source was detected. Accelerated leakage tests were ordered to monitor the source. On 6/5/2000 the test results indicated 0.02 µCi which exceeded the reportability criteria of >0.005 µCi. The room and surrounding area was surveyed, with the results indicating no contamination. The source was removed from service and will be returned to the vendor for repair or replacement. The instrument is model # 02001972-00, serial # A8615. Utah has assigned incident # UT-00-0003. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0
37091 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-06-11 13:13 | 2000-06-16 17:28 | 2000-06-16 | ACTUATION OF THE CONTROL ROOM EMERGENCY AIR CLEANUP SYSTEM DURING RADIOGRAPHY "On June 11, 2000, at approximately 1313 PDT, SCE was performing radiography on the 56' elevation of the Unit 2 Turbine Building when the Train B radiation monitor (2/3RT7824) for the Control Room Isolation Signal (CRIS) actuated. At approximately 1317 PDT, the Train A CRIS radiation monitor (2/3RT7825) actuated. The Train A and B Control Room Emergency Air Cleanup System (CREACUS) actuated as expected. "SCE was performing the radiography on the Unit 2 Main Steam Throttle Stop Valves with an 82 Ci iridium-192 source. The unshielded beam emanating from the collimated radiographic source was directed away from the CRIS radiation monitors, which are about 150 feet away. The radiography was scheduled to last approximately 3.5 minutes. "Because the actuation of the CRIS radiation monitors did not occur as a result of airborne contamination or actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system, SCE did not consider this to be a valid actuation requiring a report. However, if a 'valid signal' were to be defined as output from a radiation monitor detecting any radiation source, then this event would be reportable. Because questions have been raised regarding which definition of 'valid signal' is applicable in this instance, SCE is conservatively reporting this condition in accordance with 10CFR50.72(b2)(ii). "The trend data for the CRIS radiation monitors showed no readings above the setpoint of 1E-5 µCi/cc. Because no actual airborne radioactive contamination was present, this event has no safety significance. "At the time of this occurrence, both Units 2 and 3 were operating at about 100 percent power; Unit 1 remains permanently defueled. SCE will notify the NRC resident inspectors about this notification and will provide them with a copy of this report." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37090 | 0 | YALE UNIVERSITY |  |  |  |  | 2000-06-15 16:58 | 2000-06-16 16:01 | 2000-06-16 | POTENTIAL PERSONNEL OVEREXPOSURE A technician employed by Yale University in the Environmental Services Group expressed a concern regarding ALARA during an inventory of both byproduct and accelerator produced radioactive material. He noticed a vial containing Na-22 (accelerator product) in the millicurie source range sitting on its side in the "cave." The "cave" is a shielded storage location for both waste and byproduct material. The technician's film was sent for an emergency read. The results were received at 1658EDT on 6/15/00 and indicated a whole body exposure of 6930 mRem. A thyroid scan and bioassays were performed with negative results. Contamination surveys were performed, again with negative results. The technician had taken his film badge with him to Texas during the period of time the badge was used (May). The University RSO has submitted the other technicians (between 30-35) film badges for reading as part of the investigation. The University has contacted the state of CT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | OTH | GEN |  |  |  |  | 0
37089 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-06-16 11:20 | 2000-06-16 13:13 | 2000-06-16 | SECURITY REPORT INVOLVING VIOLATION OF PHYSICAL SECURITY PLAN MINIMUM SECURITY PERSONNEL STAFFING REQUIREMENTS NOT MET. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS CENTER FOR ADDITIONAL DETAILS. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 0
37088 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2000-06-15 21:37 | 2000-06-15 22:10 | 2000-06-15 | UNIT COMMENCED A CONTROLLED TECH SPEC REQUIRED SHUTDOWN TO MODE 2 FOR REPAIRS "The 'C' steam generator Feedwater Isolation Valve, XVG1611C, air operator developed an air leak and was declared inoperable 6/13/00 at 1549EDT. Efforts to stop the leak were unsuccessful. At 2137EDT on 6/15/00 a controlled power reduction to mode 2 was started. Current plans are to repair the operator in mode 2 and return to power operation." The air leak is ongoing with the affected valve in use (open). The licensee anticipates entering mode 2 by 0600EDT on 6/16/00 and has informed the NRC Resident Inspector. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
37087 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2000-06-15 19:15 | 2000-06-15 21:54 | 2000-06-27 | HIGH PRESSURE CORE SPRAY (HPCS) DECLARED INOPERABLE DUE TO INCOMPLETE POST MODIFICATION TESTING OF IT'S ASSOCIATED DIESEL GENERATOR "At 1915 on 6/15/00 a Engineering review of a plant modification to the Division 3 Diesel Generator (DG) determined that the Post Modification Testing did not verify proper operation of the Loss of Off-Site Power (LOOP) circuitry. This modification had only been performed to Division 3 DG and therefore Division 1 and 2 DG's are not affected. Division 3 DG provides power to the High Pressure Core Spray (HPCS) pump. The failure of Division 3 DG to operate during a LOOP would have prevented HPCS from operating. The loss of a single train safety system such as HPCS is reportable under 10CFR50.72(b)(2)(iii)(D)." The plant modification involved rewiring the electrical circuit to correct for a degraded voltage condition and was completed on 1/24/99. Post modification testing was completed on 1/31/99. HPCS has been declared inoperable but is available, if needed, pending completion of additional testing. The licensee will inform the NRC Resident Inspector. * * * UPDATE 2115EDT ON 6/27/00 FROM CHEAR TO S. SANDIN * * * The licensee is retracting this report based on the following: "Further review of this issue has determined that Division 3 Diesel Generator (DG) output breaker control circuit has been operable since installation of the modification and the plant was never in a condition that alone could have prevented fulfillment of the safety function. Therefore, Clinton Power Station is retracting Event Notification # 37087." The licensee informed the NRC Resident Inspector. Notified R3DO(Leach). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37086 | 0 | SIOUX VALLEY HOSPITAL |  |  |  |  | 2000-04-04 12:30 | 2000-06-15 13:52 | 2000-06-15 | PATIENT DID NOT RECEIVE THERAPEUTIC DOSE OF I-131 AS PRESCRIBED On 4/4/2000 at 1230 hours a patient undergoing treatment for thyroid cancer did not receive the 100 mCi of I-131 as stated in the written instructions. The Patient Appointment Center misinterpreted the instruction "100mCi I-131 followed by a whole body scan" to mean "I-131 whole body scan." A diagnostic administration of 4.26 mCi I-131 was given for the whole body scan. The whole body scan results were reviewed and the prescribing physician concluded that the therapeutic dose was not required. The patient was informed. The Heath Physicist consultant to the hospital reviewed the incident and advised the hospital that the error was recordable but not reportable. This report is being made following an inspection by NRC Region 4 (J. Cruz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | SD | HOS |  | 35.33 |  |  |  | 0
37085 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-06-14 09:00 | 2000-06-15 10:25 | 2000-10-30 | AGREEMENT STATE REPORT The State of Florida Bureau of Radiation Control reported that a Troxler soil moisture/density gauge (Model 3430, Serial #30059), containing 8 mCi of Cs-137 and 40 mCi of Am-241/Be, had been stolen from a state licensee. The licensee reported that the gauge was stolen from a temporary job site between the hours of 6 p.m. on 6/13/00 and 9 a.m. on 6/14/00. The chain link fence surrounding the site was not damaged, but the door to the shed had been pried open. The lock on the storage locker containing the container and gauge had been cut. The gauge and container were the only items taken. The Hillsborough Sheriff's Office and the Florida Bureau of Radiation Control are investigating. The Sheriff's Office is planning to issue a press release. * * * UPDATE 1544 EST 10/30/2000 FROM ADAMS TAKEN BY STRANSKY * * * "Licensee reported that a gauge was stolen on June 14th. The gauge was found on October 30 at Veterans Memorial Park in Tampa. Item was found along a bike path. The gauge was slightly damaged, but the sources were intact locked in the gauge. Swipes showed no contamination. Item has been returned to owner." Notified R2DO (Boland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37084 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-06-15 06:57 | 2000-06-15 07:51 | 2000-06-15 | LOSS OF NINE EMERGENCY OFFSITE SIRENS DUE TO LOSS OF LOCAL POWER The licensee was notified that at 0657 EDT that nine of the offsite emergency warning sirens were deenergized at 0408 EDT due to local power outage and were inoperable for greater than one hour. Six were restored in 1 hour and 16 minutes and the other three were restored in 2 hours and 16 minutes. All sirens are now operable. The licensee notified the NRC Resident Inspector and the State authorities. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) | 50.72(b)(2)(vi) |  |  | 0
37083 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-14 14:00 | 2000-06-14 20:29 | 2000-06-14 | NRC BULLETIN 91-01 RESPONSE - FAILURE TO MAINTAIN THE ESTABLISHED DOUBLE CONTINGENCY INVOLVING THE LOSS OF ONE OF TWO CONTROLS (24-HOUR REPORT) The following text is a portion of a facsimile received from Paducah personnel: "The plant water hose containing valve W-10 on the C-400 cylinder wash stand was long enough to allow a physical connection to the cylinder wash solution tanks in violation of a safety-related item contained in NCSE.006.03. Safety-related item 5.5.7 states that the hose shall not be long enough to connect the plant water system to the cylinder wash tanks. This is to prevent the potential for backflow of fissile solution into the plant water system, which is not analyzed for fissile solution." "SAFETY SIGNIFICANCE OF EVENTS:" "The plant water hose was never connected to the cylinder wash tanks. The normal plant water system pressure is well above the maximum pressure in the cylinder wash tanks and would preclude backflow even if connected. In addition, the connecting fittings on the plant water hose and on the cylinder wash tanks were incompatible." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIOS) OF HOW CRITICALITY COULD OCCUR:" "In order for a criticality to be possible, the hose would have to be connected to the solution storage tanks, fissile solution would have to backflow into the plant water system, and it would have to accumulate a critical mass in an unsafe geometry." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY CONCENTRATION, ETC):" "[The] double contingency for this scenario is established by implementing two controls on mass." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS):" "None. The C-400 cylinder wash was out of service at the time of discovery. The plant water hose was never connected to the cylinder wash tanks when the cylinder wash was in operation." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES:" "[The] double contingency for this scenario is established by implementing two controls on mass." "The first leg of double contingency is an administrative control, which prohibits connecting the plant water hose directly to the cylinder wash tanks. This control was not violated, and the first leg of double contingency was maintained." "The second leg of [the] double contingency is a physical control on the length of the plant water hose to prevent connection to the cylinder wash tanks. The hose containing valve W-10 was physically long enough to connect to the cylinder wash tank at air sparge valve A-22. This control was violated, and [the] double contingency was not maintained." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED:" "This area is being controlled to ensure that the hose is not moved without NCS approval. The corrective action will be to reduce the length of the hose such that it is compliant with the safety-related item." Paducah personnel notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
37082 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2000-06-14 13:35 | 2000-06-14 14:59 | 2000-06-14 | OFFSITE NOTIFICATION REGARDING A 2-GALLON OIL SPILL INSIDE THE PROTECTED AREA At 1430 on 06/14/00, the licensee notified the National Response Center of an oil spill onsite. Approximately 5 to 10 gallons of hydraulic oil spilled onto the ground near the shoreline of the Back River, and approximately 2 gallons of this hydraulic oil subsequently entered the Back River (a body of water located off of the Sheepscot River). The oil leaked from a hydraulic fitting on a tractor trailer (a heavy hauler) located near the shore line inside the protected area. At the time of the event, the tractor trailer was being utilized to load a pressurizer onto a barge. The initial spill was reported to the control room at 1315, and it was discovered that some of the oil entered the water at 1335. The leak has been stopped, booms have been placed into the water to contain the oil, and clean up efforts are currently in progress. Oil pads have been placed both on the surface of the water and on the ground to contain and soak up the oil. The licensee has also called a local hazardous waste response organization (Clean Harbors) and their estimated time of arrival is approximately 1630. The unit is currently shutdown, and decommissioning is in progress. There is no NRC resident inspector assigned to this site at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37081 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-06-14 08:50 | 2000-06-14 09:48 | 2000-06-14 | LOSS OF ACTIVATION CAPABILITY OF ALL OFFSITE SIRENS Citrus County notified the licensee that the offsite sirens were not able to be activated. Subsequent tests indicated that all offsite sirens were inoperable. The vendor has been notified and is on the way to make repairs. The licensee notified the local counties, Citrus and Levy, and intends to notify the State Warning Point and the NRC Resident Inspector. ********** UPDATE AT 1525 ON 06/14/00 FROM SHAWN SIMON TO LEIGH TROCINE ********** At 1510 on 06/14/00, the licensee was notified that the sirens were fully operable. The licensee plans to notify the NRC resident inspector and plans to make a courtesy notification to the state. The NRC operations officer notified the R2DO (Bernhard). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37080 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-13 10:25 | 2000-06-13 20:50 | 2000-06-13 | DISCOVERY OF SIXTEEN CORRODED SPRINKLER HEADS (24-HOUR REPORT) The following text is a portion of a facsimile received from Paducah personnel: "On 06/13/00 at 1025 CDT, the Plant Shift Superintendent (PSS) was notified that sixteen sprinkler heads were corroded, affecting sprinkler system A-9 in C-333, such that the ability of the sprinklers to flow sufficient water was called into question. Subsequently, this sprinkler system was declared inoperable, and TSR required actions establishing a roving fire patrol [were] initiated. This deficiency was detected during scheduled system inspections conducted by Fire Protection personnel." "It has been determined that this event is reportable under 10CFR76.120(c)(2) as an event in which equipment is disabled or fails to function as designed." Paducah personnel notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
37079 | 0 | MORRISON MAIERLE CONSULTING ENGINEE |  |  |  |  | 2000-06-13 14:00 | 2000-06-13 18:00 | 2000-06-13 | MORRISON MAIERLE CONSULTING ENGINEERS REPORTED THAT A VEHICLE DAMAGED A TROXLER MOISTURE DENSITY GAUGE IN BELGRADE, MONTANA. Morrison Maierle Consulting Engineers (located in Kalispell, Montana) reported that a Troxler-3411B gauge was damaged at Gallatin Field (an airport located in Belgrade, Montana, approximately 9 miles west of Bozeman, Montana). Apparently, a vehicle backed into the gauge and damaged the face plate. The gauge contained 8 mCi (±1%) of cesium-137 and 40 mCi (±10%) of americium-241/beryllium. The highest radiation survey reading was 12 mR/hour at 0 feet (on contact), and it was reported that a normal reading for this gauge was approximately 7 mR/hour at 0 feet (on contact). The sources are currently in the safe position, and the device has been packed and evacuated to a licensee office located in Bozeman, Montana. The licensee stated that there were no injuries or overexposures associated with this event. NRC Region 4 plans to notify the state. (Call the NRC operations officer for a licensee telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 4 | MT | MAT | [5 empty] | 0
37078 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-06-13 10:50 | 2000-06-13 14:00 | 2000-06-13 | OFFSITE NOTIFICATION REGARDING THE DISCOVERY OF AN OIL SHEEN ON THE PLANT'S COLD WATER CHANNEL The following text is a portion of a facsimile received from the licensee: "The National Spill Response Center was notified at 1210 [CDT] that an oil sheen was discovered on the waters of the U.S. (cold water channel). The oil spilled from cooling tower 2 fan gear boxes. The spilled oil is being contained and removed." The licensee stated that the oil sheen was discovered at 1050 CDT and that the volume of oil spilled was unknown. The licensee also stated that the outlet of the cooling tower spills into the cold water channel which is an extension of the Tennessee River. In addition to the National Spill Response Center, the licensee notified the Alabama Environmental Management Association. The licensee also plans to notify the NRC resident inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37077 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-06-12 09:15 | 2000-06-12 11:50 | 2000-06-12 | INADEQUATE SERVICE WATER SYSTEM FLOW TO EDGs (HISTORICAL REPORT) "On June 2, 2000, Kewaunee completed a scheduled refueling outage. During the outage, comprehensive flow data was measured on the plant's service water system. Subsequent analysis of the flow data revealed that for less than one hour on August 8, 1991, both of the redundant diesel generators could have had cooling water flow below design basis post-accident requirements. The cause of the condition is a combination of elevated cooling water temperatures, conservative calculation assumptions using recent data, and a previously unidentified design problem that results in reduced flow through the diesel coolers. The design problem occurs due to system backpressure caused by the diesels' cooling water discharges being connected to a common header. During the outage, the diesel generator heat exchangers were replaced for reasons unrelated to this report. The new heat exchangers' increased capacity precludes recurrence." The NRC resident inspector has been informed of this event by the licensee. | 71 | 0 | 0 | 71 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iii)(D) |  |  | 0
37076 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-06-09 16:51 | 2000-06-09 20:21 | 2000-06-09 | ESF ACTUATION - CONTROL BUILDING VENTILATION ISOLATED DUE TO CHLORINE PROTECTION MODE Control Building Ventilation isolated to the Chlorine Protection Mode during maintenance activities on the transfer line between the Chlorine Tank Car and the Chlorination Building. The isolation occurred when maintenance personnel loosened a fitting in the transfer line which allowed the release of residual chlorine. At the time of the isolation, the Chlorine Tank Car was isolated and under clearance. All systems functioned as expected. The Control Building Ventilation System was returned to normal lineup at 1814. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37075 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-06-09 18:30 | 2000-06-09 20:00 | 2000-06-29 | LICENSEE MAY HAVE EXCEEDED LICENSED THERMAL POWER LIMIT While reviewing the plants thermal performance, Oyster Creek discovered that the plant was potentially operating above the Technical Specification licensed thermal limit. Based on a comparison of the various inputs to the plant's thermal heat balance, it appears that the total feedwater flow venturi is reading non-conservatively (lower than actual) in comparison to the summation of the individual feedwater strings flows. As a result of this disparity, the plant's Engineering Staff has tentatively concluded that the heat balance is non-conservatively calculating 5 MWth less than actual based on the lower flow reading. The plant's Technical Specification steady-state thermal power limit is 1930 MWth. Oyster Creek has administratively limited thermal power to 1920 MWth until this situation can be fully analyzed. The plant's Engineering Staff is presently developing a plan to confirm this information and initiate the appropriate corrective actions to resolve this disparity. This condition has been determined reportable under the plant's Technical Specifications Section 2.E (24 Hour Notification) which requires notification of the NRC for all Technical Specification violations. The plant's Technical Specifications require maintaining core thermal power less than 1930 MWth under steady-state conditions and the plant might have been operated for prolonged periods at as high as 1935 MWth. The safety significance of this discrepancy is minimal because the plant's licensing bases includes a 2% error margin which was never challenged. * * * RETRACTION 1623 6/29/2000 FROM FULLER TAKEN BY STRANSKY * * * "After further review, it has been determined that Oyster Creek Nuclear Generating Station did not operate above the licensed limit of 1930 MWt, and we are retracting the notification made on 6/9/00. We determined that the mismatch between the computer generated heat balance and the manual heat balance was due to a feedwater heater leak, and not due to degradation of the final feedwater venturi. The feedwater heater leak will be repaired at the earliest opportunity during the upcoming scheduled refueling outage. As a result, Oyster Creek Nuclear Generating Station has removed the administrative thermal power limit of 1915 MWt, and has returned to full power." The NRC resident inspector will be informed of this retraction. Notified R1DO (Rogge). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0
37074 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-06-09 17:30 | 2000-06-09 19:19 | 2000-06-09 | SAFEGUARD SYSTEM DEGRADATION RELATED TO THE VITAL AREA BOUNDARY. IMMEDIATE COMPENSATORY ACTIONS TAKEN UPON DISCOVERY. THE LICENSE NOTIFIED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 0
37073 | 0 | CROWE BUTTE RESOURCES |  |  |  |  | 2000-06-09 12:00 | 2000-06-09 18:15 | 2000-06-09 | APPARENT LEAK IN AN EVAPORATION POND LINER. The licensee detected an increase in the level in an evaporation pond underdrain. The level had increased from about 1 inch up to 5 inches. Tests on the water were conducted and the results suggest a leak in the inner pond liner. The outer pond liner is believed to be intact. The licensee intends to find and repair the leak. The pond's level may be reduced to aid in leak detection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
37072 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-09 11:58 | 2000-06-09 15:52 | 2000-06-09 | INFORMATION CALL - TRACTOR/TRAILER CARRYING TWO UF6 CYLINDERS STRUCK BY A CAR At 1158 hours, the PORTS PSS was informed that a tractor/trailer carrying 2 empty 10 ton uranium hexaflouride (UF6) cylinders had been struck by a car approximately 10 miles North of Chillicothe, Ohio on State Route 104. The cylinders which contained only residual quantities of UF6 were not damaged and there was no release of radioactive materials. The accident generated media attention and the Ohio EPA was also notified of the incident by the Ohio highway patrol. The Trailer sustained minor damage and will be towed to the Portsmouth Site for repairs. The PORTS NRC Resident has been notified of this incident. This incident is reportable in accordance with the Safety Analysis Report, Section 64 Criteria P, since the media and other government agencies have been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37071 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-06-09 13:11 | 2000-06-09 15:42 | 2000-06-09 | REACTOR TRIP CAUSED BY GENERATOR AND TURBINE TRIPS "On June 9, 2000, at approximately 1311 hours, an automatic reactor trip occurred due to an automatic turbine trip caused by a main generator trip. The main generator trip was caused by actuation of the generator 86 lockout relays due to a direct trip from the 345 KV Buchanan substation. All primary and secondary systems appear to have responded as required after the automatic reactor trip. The Auxiliary Feed Water system automatically started as result of this trip due to low row steam generator (S/G) level (8%) resulting from S/G water level shrink. The plant is stable in the hot shutdown condition. The cause of this main generator 86 lockout is under investigation. The NRC resident inspector was notified." All control rods fully inserted during the reactor trip. The S/Gs are being fed by auxiliary feedwater and decay heat is being removed by dumping steam to the main condenser. Reactor Coolant Pumps are running. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37070 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-06-08 07:45 | 2000-06-08 15:59 | 2000-06-08 | 24 HOUR REPORT - HIGH BATTERY ELECTROLYTE LEVEL On May 15, 2000, a surveillance test was performed on the E1A11 battery. The electrolyte level in cell #18 was reported as + ¼ inch above the high level line on the cell which exceeds the Tech spec limit of < ¼ inch, as stated in Tech Spec Table 4.8-2, Battery Surveillance Requirements for Category B. This condition was not recognized during Maintenance review of the data. Tech Spec Surveillance 4.8.2.1.b.1 which allows 7 days to restore electrolyte level within the Category B limits or declare the battery inoperable was exceeded and the battery was considered inoperable. The LCO for an inoperable battery, which is 2 hours to restore to operable or be in hot standby within 6 hours, was not met. This was a violation of Tech Spec 3.8.2.1.a. The condition was corrected on May 30, 2000. There is no safety significance to this event. The electrolyte level in cell 18 at no time compromised the ability of the E1A11 battery to perform its design function. 24-hour notification is being made pursuant to Operating License NPF-76, paragraph 2.G. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
37069 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-06-08 15:15 | 2000-06-08 15:26 | 2000-06-08 | OUTSIDE DESIGN BASIS - CABLE SEPARATION ISSUE At approximately 1515 hours on June 8, 2000, operations determined that plant cable separation criteria had potentially been violated which would place the plant outside the design basis. Two wires were routed from a test jack in the control rod cabinets located in the cable spreading room to a terminal block in Rack C3 in the control room. The routing of the wires takes them into cable trays in the cable spreading room that are carrying control cables for channels 1, 2 and 3. This is in violation of the electrical separation criteria defined in the FSAR. Corrective action is being taken to remove the wires from the cable trays. A preliminary evaluation indicates the wires were used during testing of the control rod drive mechanism during initial plant startup. They are no longer in use. This event was identified during an extent of condition walkdown for the separation criteria violation identified in incident log 37043, dated May 26, 2000. The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37068 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-06-08 09:31 | 2000-06-08 13:11 | 2000-06-08 | THE PLANT HAD AUTOSTART OF THE EMERGENCY DIESELS ON BOTH UNITS On June 8, 2000, at 0931 hours, power was lost to the CD bus on each unit during switching operations involving the #4 and #5 transformers in the main switchyard. During the switching operation a loss of offsite power occurred, affecting one train of 4KV electrical power in each unit and causing the auto start of the CD EDGs on each unit. The EDGs started and loaded as expected. Unit 1 is currently defueled. When power was lost, the Spent Fuel Pool Cooling pump that was in service tripped. It was placed back in service 0953 hours. The spent fuel pool temperature rose 1 degree from 84 to 85 during this time. Temperature is now stable at 85 degrees. Unit 2 is currently in Mode 4. When power was lost to the CD bus, Reactor Coolant pumps (RCPs) #22 and #23 tripped. Additionally, the 4 KV bus under frequency signal caused the #21 and #24 RCPs to trip as designed. As a result, Unit 2 was in the natural circulation mode using the steam generators as a heat sink. RCS temperature at the time of loss of power was 335 degrees and cooled to approximately 315 degrees during the time the unit was in natural circulation. Offsite power was restored through TR5 at 1019 hours. #24 RCP was restarted at 1047 hours, restoring forced circulation, #23 RCP was restarted at 1159 hours. RCPs #21and #22 are still currently secured. The unit is stable and equipment is being restored. An Event Response Team has been convened to assess the event, and develop recovery plans. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | Refueling | Hot Shutdown |  | Refueling | Hot Shutdown |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37067 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-06-07 11:16 | 2000-06-08 11:09 | 2000-06-08 | LICENSEE EMPLOYEE TESTED POSITIVE FOR ALCOHOL DURING A RANDOM FITNESS-FOR-DUTY TEST (24-HOUR REPORT) A non-licensed employee tested positive for alcohol during a random fitness-for-duty test conducted on 06/07/00. The individual has been relieved of duty and placed on indefinite suspension. The individual's access authorization has been suspended, and the licensee is currently reviewing the individual's activities. (Call the NRC operations officer for additional information.) The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0
37066 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-06-07 20:00 | 2000-06-07 20:25 | 2000-06-07 | AT 2000 HOURS IT WAS NOTED THAT THE EMERGENCY RESPONSE DATA ACQUISITION DISPLAY SYSTEM (ERDADS) DATA LINK TO THE EMERGENCY RESPONSE DATA SYSTEM WAS DOWN (LOCKED UP). PERSONNEL HAVE BEEN CALLED TO COME IN AND REPAIR THE ERDADS SYSTEM. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED OF THIS EVENT BY THE LICENSEE. * * * UPDATE ON 06/07/00 AT 2159 ET BY FREW TAKEN BY MACKINNON * * * ERDADS RETURNED TO SERVICE AT 2157 ET (ERDADS HAD LOCKED UP). THE NRC RESIDENT INSPECTOR WAS NOTIFIED OF THIS UPDATE BY THE LICENSEE. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37065 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-06-07 17:55 | 2000-06-07 19:28 | 2000-06-07 | DEFECT IN A SPENT FUEL STORAGE CASK STRUCTURE At 1755 hours, as a result of troubleshooting due to a low pressure alarm at the Surry ISFSI Facility, it was determined that a leak existed in the lid seal system on Dry Storage Cask #2-3 which exceeds the ISFSI Tech Spec limit of 1E-5mbar-l/sec. This is a TN-32.01 cask that was placed at the Surry ISFSI Facility, pad #2 in 1996. It has been verified that the cask's overpressure monitoring system does not leak and continued to maintain a pressure greater than the cask's internal fuel cavity pressure. Therefore, it was not possible for any release of potentially radioactive material as a result of a seal failure. The cask was returned from the ISFSI pad to the station on Friday, June 2, 2000 due to the low pressure alarm. Radiation levels at the cask prior to transport to the station were normal. Additional tests are being conducted to determine which seal (either inner or outer) is affected. Investigation is on going for determining the cause and required corrective actions for this issue. Both Unit 1 and Unit 2 are currently at 100% power. Pursuant to 10CFR72.75(b)(2), this is being reported as a defect in a spent fuel storage cask structure, system, or component that is important to safety. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SPENT FUEL CASK EVENT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 72.75 |  |  |  | 0
37064 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-06-07 13:42 | 2000-06-07 15:36 | 2000-06-07 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) BREAKER OPENED CAUSING A LOSS OF INPUTS TO THE CONTROL ROOM TERMINAL. CONTROL ROOM EXPERIENCED A LOSS OF SPDS DUE TO A BREAKER TRIPPING WHICH SUPPLIES POWER TO THE CONTROL ROOM SPDS TERMINAL. INVESTIGATION OF WHY THE BREAKER TRIPPED AND RESET IS UNDERWAY. SHORTLY BEFORE THE BREAKER TRIPPED A CARPET CLEANER WAS ENERGIZED IN THE CONTROL ROOM. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED OF THIS EVENT BY THE LICENSEE. * * * UPDATE ON 06/07/00 AT 1728 ET BY WEAVER TAKEN BY MACKINNON * * * SPDS WAS RETURNED TO SERVICE AT 1608 CDT. IT WAS DISCOVERED THAT A FUSE HAD BLOWN INSTEAD OF A BREAKER OPENING. THE FUSE WAS REPLACED AND THE SPDS WAS RETURNED TO SERVICE. R4DO (PELLET) NOTIFIED. THE NRC RESIDENT INSPECTOR WAS NOTIFIED OF THIS UPDATE BY THE LICENSEE. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37063 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-06-06 23:10 | 2000-06-07 01:32 | 2000-06-07 | PLANT HAD A MANUAL REACTOR TRIP FROM 35% POWER. At 2243 on 06/06/2000 an alarm for high reactor coolant pump "A" bearing water temperature came in on the plant process computer. At 2310 the reactor coolant pump "A" bearing water temperature exceeded 225°F and a manual reactor trip was initiated and the "A" reactor coolant pump was secured. Following the reactor trip all three auxiliary feed water pumps started and equipment response was as expected. All rods fully inserted and no safety relief valves lifted. Currently the turbine driven aux feed is secured, but the motor driven aux feed is still operating. They are investigating if the cause was a temperature indicating problem or a bearing failure. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 35 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ESF ACTUATION | RPS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37062 | -1 | SOUTH COAST MEDICAL CENTER |  |  |  |  | 2000-06-06 14:30 | 2000-06-06 19:04 | 2000-06-07 | WIPE TEST OF PACKAGE EXTERIOR RESULTED IN A COUNT LEVEL OF 4442 DPM A package containing technetium - 99m (NaTcO4) delivered by NYCOMED Amersham to South Coast Medical Center was found to have surface contamination level above the 2.2 DPM per square centimeter limit. The wipe of the outer surface of the package (metal canister) was placed in a well counter and the counter indicated the that total count on the wipe was 4442 +/-149 DPM. The outer dimensions of the metal canister are 15 centimeters by 25 centimeters by 29 centimeters. The licensee will contact NYCOMED Amersham located in Anaheim, CA, and ask them to pickup the package. The package was not opened. Activity of the technetium-99m (NaTcO4) was originally 25 millicuries and the quantity is 2.4838 milliliters. * * * RETRACTION ON 06/07/00 AT 1152 ET BY JOSE BRUNO TAKEN BY MACKINNON * * * The licensee is retracting this event because the surface contamination of the metal container in DPM per square centimeter is below the reportable limit of 2.2 DPM per square centimeter. The surface area of the metal container was 2990 square centimeters and the count of the wipe was 4442 DPM. Therefore the average surface contamination per square centimeter is 1.49 DPM which is below the reportable limit of 2.2 DPM per square centimeter. NMSS EO (Josie Piccone) & R4DO (John Pellet) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | [10 empty] | NON EMERGENCY | 4 | CA | MAT | [5 empty] | 0
37061 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2000-06-06 10:20 | 2000-06-06 12:47 | 2000-06-27 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE After completion of HPCI pump surveillance testing, a check for freedom of movement and proper reset action of the overspeed trip tappet was performed. As a result of this check, an adjustment was found to be necessary for the turbine stop valve reset time. Attempts to make this adjustment resulted in inoperability of the reset function of the overspeed trip. HPCI was declared inoperable and Technical Specification limiting condition for operation 3.5E(3) was entered. HPCI will still start if called upon but if it trips on overspeed HPCI will become inoperable. Reactor Core Isolation Cooling, Emergency Diesel Generators, and all other Emergency Core Cooling Systems are fully operable if needed. The electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1252EDT ON 6/27/00 FROM DAVID HALLONQUIST TO S. SANDIN * * * The licensee is retracting this report based on the following: "This notification serves as retraction of a prior 10 CFR 50.72 notification regarding High Pressure Coolant Injection (HPCI) operability. The original notification is NRC event report number 37061 and was reported on 6/6/00. "At that time, during routine surveillance testing, it was discovered that the HPCI over-speed trip did not reset without additional operator action. The event was reported because the cause for the failure to reset had not been determined and, therefore, it was not known whether the condition could have challenged HPCI ability to perform its intended function. "Subsequent engineering review identified that the failure to automatically reset had been caused by inappropriate test methods. It was also determined that the over-speed trip reset concern would not have affected HPCI system ability to meet its design function for high pressure injection. "In addition, the HPCI over-speed reset is NOT a safety function of the VY safety system. As addressed in the VY licensing basis, the reset is required if the HPCI system had already malfunctioned. The identified condition, therefore, would not have impacted system operability. "Based on the above, the 50.72 notification is retracted." The licensee will inform the NRC Resident Inspector. Notified R1DO(Morris). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37060 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-06-06 02:36 | 2000-06-06 06:02 | 2000-06-21 | SECONDARY CONTAINMENT DECLARED INOPERABLE DUE TO LOSS OF WATER SEAL CAUSED BY PIPE CORROSION "A 4 inch diameter floor drain outlet pipe inside the Standby Gas Treatment Sump was identified by Operating personnel to be corroded through near the wall of the sump. This piping is designed to act as a Secondary Containment boundary which is used to form a loop seal between the Reactor Building and the SBGT room. Normally, the piping would come out from the wall and make a 90 degree turn to near the bottom of the sump, and open under water. However, with the erosion occurring near the wall of the sump, a breech of secondary containment exists. Due to the amount of corrosion, the opening was estimated to be 12.57 square inches. Additionally, damaged seals on two other doors (#225 and #128) located on airlocks associated with Secondary Containment accounted for another 7 square inches, for a total of 19.57 square inches. Openings in excess of 12.7 square inches in this configuration have not been tested/evaluated. Therefore, Secondary Containment was considered inoperable. Operations entered Technical Specification LCO 3.6.4.1, condition A, for Secondary Containment inoperable in Mode 1 at 0236[CDT]. Required action A.1 is to restore Secondary Containment to operable status in 4 hours. "Operations took actions to prohibit access through the two seal damaged doors/airlocks by posting them to prevent access. Once administrative control of the doors was established, the known opening in secondary containment was reduced to the corroded pipe in the SBGT sump, or 12.57 square inches. This is less than the 12.7 square inches allowed. Technical Specification LCO 3.6.4.1, condition A, was exited at 0258[CDT]." The licensee informed the NRC Resident Inspector. * * * UPDATE AT 0903 ON 06/21/00 BY BOB NURRELL TO JOLLIFFE * * * Upon further engineering review, the licensee has determined that during this event, secondary containment was operable based on the actual measured opening size (2.25 square inches). Therefore, since secondary containment was not inoperable, this event is not reportable under the specified criterion and no other criteria apply and thus, the licensee desires to retract this event. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO Roger Lanksbury. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37059 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-06-05 12:37 | 2000-06-05 15:40 | 2000-06-05 | AUTOMATIC REACTOR TRIP ON HIGH STEAM GENERATOR WATER LEVEL Automatic reactor trip from 100% power due to a feedwater transient caused by a loss of control power to 2B main feedwater pump. The feedwater transient resulted in a 2B steam generator high-high setpoint being reached which tripped both main feedwater pumps, caused a feedwater isolation signal, and tripped the main turbine which caused the reactor trip. All rods fully inserted into the core. Steam generators levels are being maintained at normal level with auxiliary feedwater at this time. The loss of control power has been attributed to water intrusion into the 2B feedwater pump control panel from extremely heavy rains and roof repairs being in progress. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The electrical grid is stable an Unit 1 was not affected by Unit 2's reactor trip. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37058 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-06-05 11:40 | 2000-06-05 13:52 | 2000-06-05 | MANUAL REACTOR TRIP DUE TO MAIN STEAM ISOLATION VALVE CLOSING. AT 1140 EDT the Unit One Control Room crew received a trouble alarm on Steam Generator Loop 4 Inboard Main Steam Isolation Valve (MSIV). The operators observed no light indication on the MSIV, a decreasing level in the Steam Generator, a large decrease in indicated steam flow, and control rods began inserting. The Shift Superintendent directed that the reactor be manually tripped. The reactor was manually tripped and all systems functioned as required with the exception of a non-1E 4160 V bus (loss steam dump bypass control panel open/close indication) , which failed to auto transfer to it's startup power source. Auxiliary Feedwater System (both motor and the turbine driven pumps) actuated as expected on Steam Generator Lo-Lo levels. The Control Room crew has exited the Emergency Operating Procedures and the unit is stable in Mode 3 at normal operating temperature and pressure. The 4160 V breaker which failed to close was racked out of it's cubicle, inspected and racked back into it's operating position, after which it was successfully closed by the Control room crew. This reenergized the non-1E 4160V bus and its associated loads. Investigation into the cause of the MSIV closure is ongoing. An Event Review Team is being formed, and a restart date will be decided upon following management review of the results of their investigation. Steam Generator Atmospheric valve controller was reduced to its lowest setpoint and maintained the Reactor Coolant System at its Tave no load condition (Steam Generator 1 & 4 Atmospheric valves opened/closed a few times). The Steam Dump Bypass Control System was fully operable and operated properly. Approximately one hour after the event non-1E 4160V bus was re-energized. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37057 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-05 09:27 | 2000-06-05 13:22 | 2000-06-05 | 4 HOUR NRC BULLETIN 91-01 NOTIFICATION CONCERNING LOSS OF 2 CONTROLS OF DOUBLE CONTINGENCY ON 6/5/00 AT 0927 HOURS PLANT PERSONNEL WERE REMOVING INSULATION FROM THE X-705 PROCESS PIPING WHEN THEY DISCOVERED EVIDENCE OF A FAILURE OF THE INTEGRITY OF SAID PIPING (material residue visible on the insulation). THIS FAILURE VIOLATES NCSA-0705_076 WHICH TAKES CREDIT FOR THE INTEGRITY OF THE PROCESS PIPING, THUS CONSTITUTING A LOSS OF ONE CONTROL. THE FACT THAT THE ENCAPSULATING INSULATION PHYSICALLY CAPTURED THE LEAKING MATERIAL MEETS THE DEFINITION FOR AN INADVERTENT CONTAINER THUS CONSTITUTING A LOSS OF ONE CONTROL AS DESCRIBED BY NCSA-0705_076 WHICH TAKES CREDIT FOR COVERING, MODIFICATION OR ELEVATION OF ABSORBENT MATERIALS TO PREVENT THE COLLECTION OF URANIUM BEARING LIQUID IN AN INADVERTENT CONTAINER. IT SHOULD BE NOTED THAT IT IS NOT CLEAR WHETHER OR NOT THE TOTAL VOLUME OF MATERIAL INVOLVED WAS GREATER THAN THE ALLOWED SAFE VOLUME (4.8 Liters ) CREDITED IN THE EVALUATION FOR ENSURING DOUBLE CONTINGENCY. BASED ON VISUAL INSPECTION OF THE MATERIAL PRESENT IN/ON THE INSULATION, IT IS ESTIMATED THAT THE TOTAL AMOUNT OF URANIUM BEARING MATERIAL IS LESS THAN 350 GRAMS. MORE RELIABLE ANALYSIS IS CURRENTLY BEING PERFORMED FOR MORE PRECISE DETERMINATION OF THE AMOUNT OF MATERIAL. SINCE THE FAILURE TIME OF THE PROCESS PIPING IS UNKNOWN, THE ENRICHMENT PERCENTAGE OF THE MATERIAL COULD BE (worst case) 100% wt. U-235. THE MATERIAL PROCESSED IN THE X-705 RECOVERY AREA PRIMARILY INVOLVES URANYL NITRATE, ALTHOUGH SOME URANYL FLUORIDE MAY BE PRESENT. THE PSS HAS SUSPENDED ALL WORK/PROCESS EVOLUTIONS IN THE AFFECTED AREA PENDING INVESTIGATION. CONTROLS WERE RE-ESTABLISHED UNDER THE DIRECTION OF THE NUCLEAR CRITICALITY SAFETY STAFF AT 1156 HOURS THIS DATE. Safety Significance of Events: On June 5, 2000, it was discovered that the insulation around the A loop density pot was contaminated by uranium-bearing material. This insulation was approximately 1 to 3 inches in thickness and constructed out of an absorbent material. The density pot is 4-inch schedule 40 piping located below the A loop evaporator and is approximately 24-inches in length. Clamp-on density transmitters are used for density control in the uranium-bearing feed solution to the extractor/strippers. After removal from the density pot, the insulation was observed to be coated with a yellowish material, which, based on high count readings, appears to be uranium-bearing. The material appeared dry in nature. It is not clear when the material accumulated on/in the insulation or how much was present during that accumulation. This insulation represents a violation of NCSA-0705_076 in that the absorbent material (i.e., the insulation) was not covered or modified properly. In addition, there is a potential loss of control in the failure of the nearby system integrity. It is not clear when or exactly how the uranium-bearing material was transported such that it accumulated on/in the insulation. It should be noted that it is not clear whether or not the total volume of material involved (i.e., which could /did accumulate on/in the insulation) was greater than the allowed (i.e., safe) volume credited in the evaluation for ensuring double contingency. Thus, while the anomalous condition is being treated as a loss of both controls the most likely scenario is that the material involved less than a safe amount of material and so the safety significance of this event is low. 2. Potential Criticality Pathways Involved; If a sufficient amount of uranium-bearing material had accumulated on/in the insulation, an unsafe geometry could have resulted and if the leaking solution had contained a sufficient amount of uranium, the resulting configuration could have been sufficient for a criticality to occur. It should be noted that the allowed safe geometry and volume limits established in NCSA-0705_076 are based on optimally moderated, UO2F2 and water solution which contains uranium enriched to 100 wt%. 3. Controlled Parameters: The parameter which was violated during this upset was the geometry of potential accumulation present on/in the insulation. In addition, the physical integrity of nearby piping was violated at some point in the past. As stated previously, the total amount of solution involved (i.e., the volume of solution which leaked onto the insulation and resulted in the uranium-bearing material being deposited on/in the insulation) is unknown, so it is conservatively being evaluated as though the volume was greater than the safe volume allowed. This represents the failure of both controls relied upon for ensuring double contingency. 4 Estimated Amount, Enrichment, Form of Licensed Material: Based on visual inspection of the material present on/in the insulation, it is estimated that the total amount of uranium-bearing material is less than 350 grams. More reliable analysis is currently being performed for a more precise determination of the amount of material. Since the failure time is unknown, the enrichment of the material could be up to 100 wt% U-235. The material processed in the X-705 recovery primarily involves uranyl nitrates (U02(N03)2) , although some uranyl fluoride (UO2F2) may also be present. 5. Nuclear Criticality Safety Control(s) or control system(s) and description of the failures or deficiencies: NCSA-0705_076.A00 takes credit for the physical integrity of systems which contain uranium-bearing material and that unsafe volume/geometry containers (including absorbent materials like the insulation) are either modified, covered, or oriented to prevent an unsafe configuration from resulting in the event of a leak. The absorbent material was not modified, covered, or oriented to prevent an unsafe configuration. In addition, there is evidence that at some time in the past a loss of nearby system integrity occurred such that the insulation was exposed to an uranium-bearing solution. 6. Corrective Actions to Restore Safety System and when each was Implemented: Under the direction of the nuclear criticality safety staff NCSA controls were re-established at 1156 hours, with all maintenance work and process evolutions suspended pending the ongoing investigation by facility management and nuclear criticality safety staff personnel. The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37056 | 0 | NC DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-06-04 16:15 | 2000-06-05 09:53 | 2000-06-05 | THE DURHAM, N.C. VA HOSPITAL SENT SOME RADIOACTIVE WASTE TO THE DURHAM WASTE TRANSFER STATION. A WASTE INDUSTRIES TRUCK SETOFF THE PORTAL MONITOR AT THE DURHAM WASTE TRANSFER STATION. THE TRUCK HAD PICKED UP A LOAD OF WASTE FROM THE DURHAM VA HOSPITAL. THE WASTE WAS RETURNED TO THE HOSPITAL. ONE BAG CONTAINED IN THE WASTE WAS MEASURING 150,000 CPM AT ONE FOOT AND OFF SCALE AT THE BAG. A DIAPER IN THE BAG WAS DETERMINED TO BE THE SOURCE. IT WAS DISCOVERED THE PATIENT WHO HAD WORN THE DIAPER HAD RECEIVED 20 MILLICURIES OF TECHNETIUM-99 ON THAT MORNING. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR |  |  |  |  | 0
37055 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-06-04 15:15 | 2000-06-04 15:45 | 2000-06-04 | NY STATE DEC TO BE NOTIFIED OF 5 - 15 GALLONS LUBE OIL SPILL INTO PLANT DISCHARGE CANAL - At 1515 on 06/04/00, the licensee notified the DOT National Response Center and plans to notify the NY State Department of Environmental Conservation (DEC), local officials, and the NRC Resident Inspector that 5 to 15 gallons of lube oil had overflowed from the plant oil collection system into the plant discharge canal which drains into the Hudson River. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37054 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-06-04 05:54 | 2000-06-04 06:42 | 2000-06-04 | UNIT 3 EXPERIENCED A REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL FOLLOWING A TURBINE TRIP "[A] plant startup [was] in progress. [The] main turbine generator [was] tied to [the] grid at 0452 [EDT]. Power was being raised to 30% power. "At 22% reactor power while feeding steam generators via manual control of [the] feedwater regulatory valves, '33' Steam Generator level reached a high level trip point and tripped the turbine. The subsequent shrink in steam generator '31' levels resulted in a reactor trip at 0554 [EDT]. "All plant equipment functioned as required, no malfunctions noted at this time. [A] post trip review [is] in progress. ESF Actuation; '31' and '33' auxiliary feed pump[s] started." All rods fully inserted following the trip. There is no safety equipment out of service at this time. Offsite power is supplying electrical loads. The auxiliary feed pumps and main condenser are removing decay heat. The licensee informed the NRC Resident Inspector and plans to issue a press release. | 0 | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37053 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-06-04 00:12 | 2000-06-04 01:28 | 2000-06-04 | UNIT 2 EXPERIENCED A REACTOR TRIP ON TURBINE TRIP DURING SURVEILLANCE TESTING OF THE TURBINE AT 0128 EDT ON 6/4/00 WHILE PERFORMING TURBINE SURVEILLANCE PROCEDURE 2651T, "POWER LOAD UNBALANCED PUSH-TO-TEST", THE TURBINE TRIPPED UNEXPECTEDLY CAUSING A REACTOR TRIP. ALL CONTROL RODS FULLY INSERTED. ALL SYSTEMS FUNCTIONED AS REQUIRED. THE MAIN FEEDWATER SYSTEM AND MAIN CONDENSER REMAIN IN SERVICE FOR DECAY HEAT REMOVAL . NO PRIMARY OR SECONDARY SAFETIES/PORVs LIFTED DURING THE TRANSIENT. ELECTRICAL LOADS TRANSFERRED TO THE RSST TRANSFORMER WITH ALL EDGs AVAILABLE IF NEEDED. THERE IS NO SAFETY EQUIPMENT OUT OF SERVICE AT THIS TIME. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR AND BOTH STATE AND LOCAL AGENCIES. A PRESS RELEASE IS ANTICIPATED. | 0 | 0 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37052 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-06-02 13:30 | 2000-06-03 10:44 | 2000-06-03 | 24-HOUR NRC 91-01 BULLETIN REPORT INVOLVING POTENTIAL LOSS OF CRITICALITY CONTROL IN SHUTDOWN CELLS "On 6/2/00 the Plant Shift superintendent was notified of a potential NCSA noncompliance. NCSAs 326_013, NCSA 330_004, and NCSA 333_015 require that cells that are shutdown and at a UF6 negative be buffered with dry air or nitrogen to maintain moderation control as part of double contingency. For cells that have less than a safe mass, procedure guidance allows the cell to be maintained less than atmospheric pressure, when not at a UF6 negative. Various leaks (either from the dry air system or from wet atmospheric air) can enter the cell allowing pressure to increase. This pressure must then be evacuated to maintain the cell less than atmospheric pressure. Repeated cycles of 'leak up' and evacuation will eventually achieve a UF6 negative unknown to operators since there are no periodic sampling requirements. The NCS requirement to buffer a cell within eight hours of achieving a UF6 negative may then be violated because the state of a UF6 negative is not known. "Presently all cells that are shutdown that have less than a safe mass in them are at a UF6 negative, and there is currently no violation of this moderation control. However, it cannot be guaranteed that this control was not violated during past operations, and is being reported as a loss of one control. "SAFETY SIGNIFICANCE OF EVENTS: "The safety significance of this event is low. Only affected cells that when shutdown have less than a safe mass of material in them. Failure to establish or maintain the buffer as required could result in wet air entering a shutdown cell. This would moderate a UO2F2 deposit due to the hygroscopic properties of UO2F2. If this unbuffered condition were permitted to continue for longer periods, the H/U of the deposit could eventually reach a maximum of 4 (the maximum H/U ratio of a deposit exposed to ambient cascade building air is 4). However, due to being less than a safe mass, a criticality could not occur. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "For a criticality to occur the mass of the deposit would have to be greater than a safe mass, moderation level would have to reach an H/U ratio of 4, the deposit would have to be reflected. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "The controlled parameters for this event are mass and moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "The highest possible enrichment for event is 20% and the material will be at or below a safe mass. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The failure in this case is the implementation of the control on moderation. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: [Not specified]." Department Operating Instructions (DOIs) have been issued pending procedural revisions to address this deficiency. The NRC Resident Inspector and DOE Site Representative have been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37051 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-06-02 17:21 | 2000-06-02 19:24 | 2000-06-21 | REACTOR CORE ISOLATION COOLING SYSTEM INOPERABLE DUE TO A FAULTY LEVEL SWITCH - At 1721 on 06/02/00, Nine Mile Point Unit 2 received a Reactor Core Isolation Cooling (RCIC) System high point vent low level annunciator alarm. This alarm came in and cleared repeatedly. The licensee declared the RCIC System inoperable but functional and entered Technical Specification 3.7.4 which requires the RCIC System to be restored to operable status within 14 days. The licensee closed the RCIC System turbine trip throttle valve, #2ICS*MOV150 in accordance with the annunciator response procedure. The licensee then performed the RCIC System fill and vent procedure #N2-OSP-ICS-M001 satisfactorily with a solid stream of water being vented and no evidence of air in the system. The high point vent low level annunciator alarm remained in solid following the fill and vent procedure. The licensee suspects that a faulty high point vent level switch is the problem and prepared a Problem Identification to repair the switch. The licensee has returned the RCIC System to available status (but still inoperable) and is reviewing compensatory actions for the faulty level switch to support the return of the RCIC System to operable status. This event has no effect on Unit 1 which is at 100% power. The licensee plans to notify the NRC Resident Inspector. * * * RETRACTED AT 1446 EDT ON 6/21/00 BY MATT WALDECKER TO FANGIE JONES * * * "On June 2, 2000 at 1721 hours, the reactor core isolation cooling system was declared inoperable when a high point vent level low annunciator alarmed and cleared repeatedly. The reactor core isolation cooling trip throttle valve was closed in accordance with the annunciator response procedure. "Subsequent review has determined that the high point vent level low annunciator alarming and clearing repeatedly was due to a failed level switch. Correct high point vent water level was verified utilizing an approved operating procedure. 50.72(b)(2)(iii) and 50.73(a)(2)(v) reporting criteria covers an event or condition where structures, components, or trains of a safety system could have failed to perform their safety function because of equipment failures. The failure of the high point level switch does not constitute an event or condition which rendered the Reactor Core Isolation Cooling System incapable of performing its safety function. In addition, the level switch is only used to warn the operators of decreasing water inventory in the reactor core isolation cooling discharge line. No credit is taken for the level switch in any safety analyses and does not directly control the removal of residual heat (the safety function) from the Reactor Vessel. Therefore, this event is not reportable. "The operator action to close the reactor core isolation cooling trip throttle valve in accordance with the annunciator response procedure does not constitute an event or condition as discussed in the NUREG-1022. Therefore, notification of this event is being retracted." The licensee notified the NRC Resident Inspector. The R1DO (Robert Summers) was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37050 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2000-06-01 16:00 | 2000-06-02 14:31 | 2000-06-02 | I-131 OVERDOSE - MEDICAL MISADMINISTRATION/AGREEMENT STATE EVENT - A female patient at Allen County Hospital, Iola, KS, was given 100 microcuries of I-131 for an thyroid uptake measurement during a diagnostic study instead of the prescribed 50 microcuries. The cause of this medical misadministration event was due to the hospital hot lab delivering two capsules of 50 microcuries each; one to be given to the patient and the other to be used as a standard. The patient was mistakenly given both capsules. This overdose poses no adverse medical effects to the patient. The patient's doctor has been informed. The doctor plans to inform the patient. The hospital is determining corrective actions. (KS Case #KS-00-0011). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | MED MISADMINISTRATION | [8 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  | 35.33 |  |  | 0
37049 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2000-06-02 04:15 | 2000-06-02 11:57 | 2000-06-02 | OUTSIDE CONTAINMENT ISOLATION VALVE INOPERABLE DUE TO INCOMPLETE PLANT MODIFICATION At 0415 CDT on 06/02/00, I&C technicians began to perform tech spec surveillance test #ISF-SB-OA30A to test the operability of 'A' train steam line isolation valve slave relay #K-634. In establishing the initial conditions at step 4.2 of the test procedure, solid state protection system white light #26 was not illuminated as required by the procedure. The procedure was exited at that time and the control room crew was informed of the finding. The control room crew replaced the light bulb and the light still did not illuminate. Another light bulb, known to be good, was then installed in the light socket. The light still did not illuminate. The Shift Supervisor contacted the System Engineer at approximately 0530 CDT when the engineer arrived onsite, and requested that the engineer investigate what the white light indicated when the light was not illuminated. After review of the system schematics, the engineer found that there was the possibility of outside containment isolation valve #EGHV-0061 being INOPERABLE if relay #K-802 did not function properly. (Reference electrical drawing #E-23EG09A.) This situation was reported to the control room crew. The Shift Supervisor declared valve #EGHV-0061 INOPERABLE using the time of discovery at 0415 CDT and closed the valve and deenergized power to the valve per Tech Spec action statement 3.6.3.A at 0800 CDT. Equipment out of service log entry #7986 was made. I&C technicians were dispatched to support troubleshooting efforts. After some initial troubleshooting, some results did not agree with the drawing. The engineer noted the drawing showed that the circuitry had recently been changed by Plant Modification #CMP 98-1020. The drawing had been updated on 04/07/00. The engineer called the Construction Supervisor of the plant modification installation. The supervisor reviewed the modification package and found a connection between a terminal block at the motor control center for valve #EGHV-0061 and the solid state protection system cabinet #SB030A had not been performed. This made containment isolation valve #EGHV-0061 INOPERABLE because it would not close on a phase B containment isolation signal. The control room crew was notified of this finding. This finding meant that the valve had been INOPERABLE since the installation of the plant modification on 04/06/00. The Construction Supervisor initiated field change notice #FCN-11 to plant modification package #MP 98-1020 and initiated work document #W657017 to correct the circuitry wiring. Retest documents #R657017A and #R6S70173 was also initiated for post maintenance testing of the circuit. The licensee determined that this event was reportable to the NRC at 1030 CDT. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRAD COND DURING OP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(1)(ii) |  |  |  | 0
37048 | 0 | TRI STATE CONSULTANTS |  |  |  |  | 2000-06-01 14:30 | 2000-06-02 07:26 | 2000-06-02 | SOURCE ASSEMBLY, CONTAINING 24 CURIES OF IRIDIUM-192, BECAME DETACHED FROM ITS DRIVE ASSEMBLY While checking a radiographic exposure device manufactured by AEA Technology, the source assembly became detached from its drive mechanism. The licensee was checking the swage end, the locking mechanism, of the exposure assemble when the assembly failed. The swage connection had a crack and this caused the swage connection to fail, becoming detached. The Assistant Radiation Safety Officer (ARSO) cleared the room and made several trips into the room to place lead shielding over the source assembly. After the source assembly was covered with lead, the ARSO took radiation surveys around the room to make sure radiation levels were within acceptable limits. The ARSO spent the night guarding the entrance to the room to prevent anyone from entering. AEA Technology was notified of this event on 06/01/00 and they are sending a retrieval team out on 06/02/00 to retrieve the source. The source model number is 424-9. The ARSO was the only one to be exposed and he received 78 millirems as indicated by his pocket dosimeter. The source, Iridium-192, was originally manufactured on 12/17/99 with a strength of 114.5 curies. The present strength of the Iridium-192 source is 24 curies (half life of Iridium-192 is 74.2 days). Tri State Consultants' main office is located in Pittsburgh, PA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | ACCESS DENIED OTHER | [8 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2)(ii) | 30.50(b)(1)(iii) |  |  | 0
37047 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-31 10:00 | 2000-06-01 09:34 | 2000-06-01 | CATEGORY 1 AND CATEGORY 2 MATERIAL FOUND WITHIN 2 FEET OF EACH OTHER NRC Bulletin 91-01 24 hour notification On May 31, 2000, PORTS plant personnel discovered NCSA-PLANT048 non-compliance during the monthly Nuclear Criticality Safety (NCS) walk through. Category 1 contaminated metal was discovered in close proximity (less than 2 feet) to Category 2 contaminated metal. Category 1 contaminated metal is defined as items that have no visible uranium on them, items only contaminated with non-fissile radiological isotopes, items from a non-fissile material operation or items with hidden cavities from non-fissile material operations. Category 2 contaminated metal is defined as an item that has a hidden cavity with potential for significant uranium material in the cavity. This was a violation of NCSA-PLANT048 requirement # 2 which states, "Category 2 contaminated metal shall not be stored in a Category 1 contaminated metal storage area". This constituted the loss of one control (spacing) of the double contingency principle. The first control (that of not storing Category 2 Items with Category 1) was lost. The second control (that of categorizing the Category 1 metal Items correctly, mass control) was maintained throughout this event. This condition was corrected under NCS Engineering guidance and compliance re-established at 1205 hours. The monthly NCS walk through also identified a NCSA-PLANT048 administrative noncompliance. NCSA-PLANT048 "Contaminated Metal" requires that a sign be posted for Category 2 contaminated metal storage areas. The converters stored outside of the X-700 building meet the requirements of Category 2 contaminated metal but the area was not posted. Temporary signs were posted to re-establish compliance with NCSA-PLANT048. SAFETY SIGNIFICANCE OF EVENTS: This event has low safety significance. The six converters on the west side of X-700 contain less than a safe mass at the indicated enrichment. There were no visible uranium compounds on the Category 1 contaminated metal that was stored In close proximity to the converters. Since there was no visible uranium on the Category 1 metal, there was no additional risk of a criticality occurring. NCSE-PLANT048.E04 documents that Category 1 contaminated metal can have at most 24.2 grams 235U per 2,500 square feet of metal surface. In no case was more than 2500 square feet of Category 1 material found within 2 feet of the six converters. NDA results indicate (with uncertainty applied) that the largest amount of 235U in one converter is 1099 grams at an enrichment of 2.3 wt% 235U in the form of UO2F2. At 3 wt% 235U, the estimated minimum critical mass is 3,077 grams 235U and the safe mass is 1180 grams of 235U. Assuming 25 additional grams of 235U due to the presence of the Category 1 metal, the total amount of 235U (1124 grams 235U) is still below a safe mass, for the converter unit with the highest loading. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): A 'dirty' metal item classified as Category 1 with the 'dirt' containing a large amount of enriched uranium stored with a Category 2 item such that the total uranium present exceeds a critical mass and is in the proper geometry for a criticality to occur CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameters are the segregation (proper spacing) of Category 1 and 2 storage areas and the proper classification of the Category 1 contaminated metal items (mass control). ESTIMATED AMOUNT, ENRICHMENT. FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): NDA results indicate (with uncertainty applied) that the largest amount of 235U in one converter is 1099 grams at an enrichment of 2.3 wt% 235U in the form of UO2F2. At 3 wt% 235U, the estimated minimum critical mass is 3,077 grams 235U due to the presence of the Category 1 metal, the total amount of 235U (1124 grams 235U) is still below a safe mass, for the converter unit with the highest loading. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first control that of not storing Category 2 items with Category 1 Items (spacing) was lost. The second control, that of categorizing the Category 1 metal items was done correctly (mass control). The Category 1 items were observed to have no visible uranium on them. Thus, the first control was lost but the second control of categorizing the Category 1 contaminated metal items was done correctly. This resulted in a lost on one control (spacing) relied on for double contingency. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At 1205 hours, under NCS engineering guidance, the Category 1 contaminated metal was spaced at least 2 feet from all Category 2 contaminated metal (converters). Signs were posted identifying the Category 2 contaminated metal storage area. The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37046 | -1 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2000-05-31 13:30 | 2000-05-31 18:04 | 2000-06-02 | PLANT ENTERED A 7 DAY LCO DUE TO HPCS BEING DECLARED INOPERABLE. While performing monthly surveillance start LOS-DG-M3, for the High-Pressure Core Spray (HPCS) systems Emergency Diesel Generator, the Diesel automatically tripped off on an over-speed signal. The Diesel was being started from an idle condition while an operator was attempting to maintain speed between 400 and 500 rpm. The Diesel does not appear to have been damaged but remains shutdown and unavailable for on-going investigation of the failure. The High-Pressure Core Spray system is inoperable but available from normal power source only. The failure mechanism is being investigated and corrective actions will be performed. The NRC Resident Inspector was notified. * * * UPDATE AT 2211 ON 06/01/00 BY SHANE MARIK TO JOLLIFFE * * * The licensee investigation has determined that the cause of the event was due to operator overcompensation of the engine governor during the start that resulted in the EDG accelerating to the overspeed setpoint and tripping on overspeed. The operator performing the slow (idle) start in accordance with the monthly Technical Specification surveillance procedure was a trainee under supervision by a qualified operator. The EDG was already inoperable for the performance of the monthly surveillance test that verifies operability of the EDG to start and carry full load for at least 60 minutes. During inspection, no mechanical or electrical malfunctions were found associated with governor settings, the start circuitry, the engine fuel racks, or fuel injector linkages. The fuel rack and associated fuel injector linkages were then verified to have freedom of movement without binding. A subsequent fast start was performed (same as an automatic start) that verified that the EDG did not have a malfunction that would cause it to trip on overspeed. The EDG would have satisfied its intended safety function when in standby (no operator interface is required for the governor/fuel rack control. except for surveillance testing). Therefore, the overspeed trip of the High Pressure Core Spray System EDG is not reportable as a condition that alone could have prevented fulfillment of a safety function. Since the failure occurred after the EDG was inoperable due to not being lined up for standby operation (removed from service as part of a planned evolution in accordance with an approved procedure), the start was a slow start controlled by an operator and restoration of the EDG was less than 12 hours and well within the 14 day Technical Specification allowed outage time. The licensee has determined that this event is not reportable to the NRC, and desires to retract this event notification. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO Bruce Jorgensen. | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37045 | 0 | US AIR FORCE |  |  |  |  | 2000-05-30 09:00 | 2000-05-31 13:19 | 2000-05-31 | SOURCE COULD NOT BE MOVED TO THE EXPOSURE POSITION WHILE ATTEMPTING TO USE AN IRRADIATOR AT BROOKS AFB, TEXAS. A J L SHEPHERD 81-10 IRRADIATOR CONTAINING 130 CURIE SOURCE OF CS-137 WOULD NOT OPERATE PROPERLY WHEN THE OPERATOR ATTEMPTED TO USE IT. THE SOURCE APPEARS TO BE STUCK IN THE SHIELDED POSITION AND CAN NOT BE MOVED TO THE EXPOSURE POSITION. THE AIR FORCE IS CURRENTLY TROUBLESHOOTING WITH THE VENDOR VIA TELEPHONE TO CORRECT THE PROBLEM. IF NOTHING CAN BE DONE THEY WILL CALL IN THE VENDOR. THE SOURCE IS IN THE SHIELDED POSITION. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 4 | TX | OTH | GEN | 30.50(b)(2)(ii) |  |  |  | 0
37044 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-05-26 | 2000-05-30 10:24 | 2000-05-30 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER GAUGE OWNED BY SPRINGSTEAD ENGINEERING, INC., d/b/a CENTRAL TESTING LABORATORY LOCATED IN FLORAL CITY, FLORIDA The following text is a portion of a facsimile received from the Florida Bureau of Radiation Control: "Licensee: Springstead Engineering, Inc., d/b/a Central Testing Laboratory" "City, State, and Zip Code: Floral City, FL 34436" "Isotope(s): Cs-137; Am-241:Be" "Activity(s): 6.0, 39.2 mCi, respectively" "Material Form; Chemical Form; Physical Form: By-product: Special Form" "Probable Disposition of Material: Transferred to Another Licensee" "Exposure? No" "Number: N/A" "Type of Individual(s): N/A" "Exposure Source: N/A" "Dose Delivered to: N/A" "Maximum Dose Received: N/A" "Incident Category: Equipment Problems (Licensed Material)" "Incident Location: Intersection of CR 226 and US 27, just west of I-75 exit 70" "Incident Description: While gauge was in use (calibration position, with sources retracted), a front loader ran over the gauge. The housing and case were destroyed, but the lead case around the source was intact with the source retracted. The licensee asked for assistance in surveying the area, the loader, and the source housing. Survey of the area and the front loader were background. Wipes of the source housing were background. Troxler has been notified and will pick up the gauge for repair. Cause of the accident was front loader driver inattention." "Device Type (Quantity): Soil/Moisture Density Gauge (1)" "Manufacturer: Troxler" "Model Number: 3440" "Serial Number: 14821" "Emergency Groups at Scene: None" "Organizations Notified: NRC" "Media Contacted: None" "Investigator's Name; Title: Reno Fabii, Environmental Specialist II" "Office: Environmental Radiation Control" "Date; Time Investigated: 26-May-00; 1115" Call the NRC operations officer for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
37043 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-05-26 14:42 | 2000-05-30 09:07 | 2000-05-30 | MAY 26, 2000, DISCOVERY OF A VIOLATION OF ELECTRICAL SEPARATION CRITERIA (DETERMINED TO BE REPORTABLE ON MAY 30, 2000 AT 0835) The following text is a portion of a facsimile received from the licensee: "At approximately 0835 hours on May 30, 2000, operations [personnel] determined that plant cable separation criteria had been violated placing the plant outside the design basis. A cable routed from a Channel 'C' instrument bus had been retired in place by terminating the cable from the equipment it was routed to, taping the cable end, and placing the rolled cable in a cable tray. The rolled cable, still power by the instrument bus, was placed in a Channel 'B' cable tray. This resulted in a condition outside the plant's design basis since channel electrical separation criteria is defined by the [Final Safety Analysis Report (FSAR)]. The event was originally identified on May 26, 2000, at approximately 1442 hours, but [it was] not recognized as reportable at the time. Corrective action was taken when the event was identified by removing the Channel 'C' cable from the Channel 'B' cable tray." The licensee plans to notify the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37042 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2000-05-28 16:52 | 2000-05-28 20:17 | 2000-06-14 | ENTERED LIMITING CONDITION OF OPERATIONS (LCO) AFTER REACTOR CORE ISOLATION COOLING (RCIC) DECLARED INOPERABLE. RCIC was declared inoperable during surveillance testing after RCIC minimum flow isolation valve failed to open during testing. Technical Specification 3.5.3, 14 day LCO , was entered after RCIC was declared inoperable. All other Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. Offsite electrical grid is stable. Startup testing is continuing. The NRC Resident Inspector was notified of this event by the licensee. ********** UPDATE AT 1420 ON 06/14/00 FROM BILL GREEN TO LEIGH TROCINE ********** The licensee is retracting this event notification. The following information is a portion of a facsimile received from the licensee: "On 28 May, 2000, at 2017 hours, a [4-]hour report (Event Notification 37042) was made to the NRC on RCIC system being inoperable due to the failure of the minimum flow isolation valve to open during surveillance testing. Subsequently, it has been determined that RCIC was operable, and this event is not reportable under 10 CFR 50.72(b)(2)(iii) as a loss of safety function." "The surveillance procedure, 6.RCIC.102, fulfills inservice testing and full flow testing requirements. Although the procedure does not require the minimum flow valve to open during the performance of this surveillance, it has operated during past performances. Procedure 6.RCIC.102 did reference Technical Requirements Manual TSR 3.3.2.2 which contains a [>=] 40 gpm Allowable Value for the RCIC Low Pump Discharge Flow Function, i.e., a minimum flow requirement." "Further review determined that the reference to TSR 3.3.2.2 is unnecessary in 6.RCIC.102. During the performance of 6.RCIC.102, the system line-up initially allows full flow through the test line, and therefore, minimum flow valve operation is not required. Minimum flow valve operation is dependent upon system variations in flow and pressure during RCIC pump start up and is possible, but not required with the test flow path already established. It has subsequently been determined that the minimum flow valve logic is and was operable and that the minimum flow valve will open when required." "As such, RCIC was able to perform its required function and was operable. Therefore, this event is not reportable, and event notification 37042 is retracted." The licensee notified the NRC resident inspector. The NRC operations center notified the R4DO (Linda Smith). | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37041 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-05-28 05:47 | 2000-05-28 07:06 | 2000-05-28 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL FOLLOWING A LOSS OF FEEDWATER DUE TO AN ELECTROHYDRAULIC CONTROL (EHC) MALFUNCTION Prior to this event, power on Unit 1 had been decreased to 14% and the turbine had been taken off line for performance of a balance move due to high vibration of bearing #9 after exiting a refueling outage. Subsequent to this load reduction, an EHC malfunction caused a feedwater pump to roll back, and this in turn resulted in a loss of feedwater. Operators attempted to reduce power to 2% but were unable to restore the main feedwater pump. Auxiliary feedwater was manually started, but the reactor automatically tripped from approximately 4% power at 0547 CDT due to low steam generator water level. All rods fully inserted. There were no emergency core cooling system actuations, and none were required. The licensee stated that all systems functioned as required in response to the reactor trip. The unit is currently stable in Mode 3 with the reactor coolant system at normal operating temperature and pressure. The reactor coolant pumps, pressurizer heaters and sprays, and normal charging and letdown are being utilized for primary system transport, pressure, and inventory control. Secondary steam is being dumped to the main condenser, and auxiliary feedwater is supplying water to the steam generators. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37040 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-05-26 16:10 | 2000-05-26 18:03 | 2000-05-26 | RESIDUAL HEAT REMOVAL (RHR) HEAT EXCHANGER (HX) TO SAFETY INJECTION (SI) PUMP MOTOR VALVES DO NOT MEET THEIR DESIGN BASIS. At 1610 on May 26,2000 it was determined that the as built condition of the plant did not meet its design basis. The condition involves the RHR HX to SI (low head injection) pump motor valves. These valves are interlocked with a pressure signal from the RHR system. The signal that allows these valves to open, was found not to meet the requirement of IEEE 279. The pressure signal prevents the valves from opening when RHR pressure is greater than the design pressure of the SI suction piping. This permissive was designed to prevent the valves from being inadvertently opened when RHR is in its cooldown line up. Its only function when the RHR system is in its at power line up is to not malfunction and thus allowing the valves to open. Original documentation from the plant construction and discussions with Westinghouse, the NSSS vendor, indicates that the original design intent was that this interlock did not need to meet IEEE 279. This was based on the assumption that local manual action could be taken if the interlock malfunctioned. However the USAR does not reflect this design philosophy. The USAR appears to assume the valves can be positioned from the control room and that no local manual action is required. A temporary change has been initiated to defeat the interlock while the plant is at power. This will ensure the plant meets its design basis. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRAD COND DURING OP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii) |  |  |  | 0
37039 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2000-05-26 12:00 | 2000-05-26 17:37 | 2000-05-26 | SULFATE AND CHLORIDE LIMITS EXCEEDED The licensee reported that their confirmatory samples that they received back today confirmed that monitor Well # SM 613 exceeded its sulfate limit and monitor Well # SM 628 exceeded its sulfate and chloride limits. The licensee has not started mining the site. Both the initial and confirmatory samples taken for monitor Well # SM 613 showed a sulfate level of 25ppm. The multiple limit for sulfate is 18 ppm and the single limit for sulfates is 21 ppm. Monitor Well # SM 628 initial sample indicated a chloride level of 7.7 ppm and the confirmatory sample indicated a chloride level of 7.3 ppm. The multiple parameter limit for chlorides is 7.0 ppm and the multiple parameter limit is 7.3 ppm. Initial sulfate sample indicated a sulfate level of 46 ppm and the confirmatory sulfate sample indicated a sulfate level of 43 ppm. The multiple parameter limit for sulfates is 33 ppm and the single parameter limit for sulfates is 39 ppm. Initial samples were taken on 05/25/00 and the confirmatory samples were taken on 05/26/00. The licensee thinks that the base line water quality is very clean and that they are seeing natural variations of the water. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
37038 | 0 | TENNESSEE DIV OF RAD CONTROL |  |  |  |  | 2000-05-26 | 2000-05-26 16:35 | 2000-05-26 | 300 MILLIREM/HR SPOT FOUND ON A B-25 CONTAINER. On 05/26/00, the Radiation Safety Officer at Frank W. Hake & Associates notified the Memphis field office of the Division of Radiological Health of a transportation event. The licensee received a shipment from GTS Duratek in Oak Ridge, TN. One of the B-25 containers had a hot spot on the bottom of the container that exceeded the limits in 49CFR173.441 for an uncovered conveyance. The licensee offloaded the shipment to investigate. This event dose does not pose a risk to public health and safety. The State of Tennessee event report ID number for this event is TN-00-088. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | TRA | [5 empty] | 0
37037 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-05-26 10:00 | 2000-05-26 11:03 | 2000-05-26 | "B" CONTROL ROOM HVAC SYSTEM OUTSIDE DESIGN BASIS The 'B' control room HVAC system has been determined to be outside design basis per Generic Letter 91-18. There is a non-conforming condition in the system. There is reasonable expectation that the HVAC system is Operable, due to a new methodology, Acron 96, expected results indicate that the HVAC system would be within the design basis. Some of the assumptions made in the original calculations, when the system was installed, were determined to be incorrect. The licensee intends to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37036 | 0 | HOLTEC INTERNATIONAL |  |  |  |  | 2000-05-26 | 2000-05-26 10:59 | 2000-05-26 | 10 CFR PART 21 REPORT An audit of the company's Holtite-A shielding material test qualification and manufacturing program identified that a 10 CFR 21 report was not made in the wake of the company's discovery of defective neutron shielding material supplied under a safety significant procurement. The material, NS-4-FR, used for dry cask storage use contained internal voids where solid material was expected. The problem is lack of specific installation procedure to eliminate voids in the poured samples. The samples were still considered suitable for use in thermal stability testing. However, the samples failed and together with the voids was considered unsuitable for use. The firm supplying the basic component was NAC International of Norcross, GA. The problem was originally noted in April 1998. NAC was not informed, in part because Holtec was not aware of any installation in any cask with significant heat loads. Holtec has no information on actual usage or locations of use as they are not the supplier of the hardware with the potential defect. Holtec has no NAC supplied NS-4-FR in any cask system supplied to its customers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21 |  |  |  | 0
37035 | 0 | ANHEUSER-BUSCH |  |  |  |  | 2000-05-22 | 2000-05-26 10:05 | 2000-05-26 | MISSING TRITIUM EXIT SIGN During the semiannual inspection, one Permx model P160 series tritium exit sign was discovered missing. It is believed to have been destroyed during demolition of a wall as part of an expansion of the plant. A search of the plant was conducted and the contractors involved in the demolition were questioned with no real findings. A written report will be submitted to the NRC Region 2 office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37034 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-05-25 22:54 | 2000-05-26 02:29 | 2000-05-26 | FOUR FILTRATION RECIRCULATION AND VENTILATION FANS TRIPPED UNEXPECTEDLY "On 5/25/00 at 22:54 hours, four operating Filtration, Recirculation. and Ventilation System (FRVS) recirculation fans (A, B, D, E) unexpectedly tripped while they were running for a monthly surveillance. An FRVS ventilation fan, that was also in service, continued to run. "The FRVS consists of two subsystems, the Recirculation System and the Ventilation System. The FRVS Recirculation System is an Engineered Safety Feature (ESF) System, located inside the Secondary Containment, that reduces offsite doses significantly below 10CFR100 guidelines during a LOCA, refueling accident, or high radioactivity in the Secondary Containment. Upon a Secondary Containment isolation, the FRVS Recirculation System is actuated and recirculates the Secondary Containment air through filters for cleanup. This subsystem is the initial cleanup system before discharge is made via the FRVS Ventilation subsystem to the outdoors. The FRVS Ventilation System is an ESF system, located inside the Secondary Containment, that maintains the building at a negative pressure with respect to the outdoors. The system takes suction from the discharge duct of the FRVS Recirculation system and discharges the air through filters to the outdoors. "Investigation into the cause of the fan trips has identified a manual damper in the ventilation system ductwork that failed to the closed position. This manual damper is normally open during power operation. This damper is repositioned closed during refueling outages to redistribute ventilation through the Secondary Containment. Immediate actions were taken to return the damper to the open position. Recirculation fans have been returned to service and are operating satisfactorily. "The ventilation system ductwork was reviewed to identify other manual dampers that could have the same or similar affect on system operation. Two other dampers were identified, their positions have been verified to be correct. "Hope Creek is presently in Operational Condition 1 at 15% power with the turbine/generator off-line awaiting replacement of the 'C' Main Power Transformer. All safety related equipment is available." The fans had been operating about 10 hours before tripping, it is suspected that the damper was not adequately secured in the open position when the plant exited the refueling outage. The licensee is investigating. The licensee notified the NRC Resident Inspector and the local township authorities. | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37033 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-25 18:00 | 2000-05-25 23:52 | 2000-05-26 | NRC BULLETIN 91-01, 24 HOUR NOTIFICATION The following is the faxed report from Portsmouth: On May 16, 2000, PORTS plant personnel initiated a review of an NRC event (# 36993) submitted by Paducah Gaseous Diffusion Plant (PGDP), to assess applicability at the Portsmouth sight. Errors associated with calibration correction factors used to determine uranium masses were found to have not occurred at the PORTS sight. On May 25, 2000, after further review by Nuclear Criticality Safety dept. personnel, a violation of double contingency was identified when it was determined that the independence of non-destructive assay (NDA) measurements was not maintained. NCSA-PLANT013.A00 indicated that NDA measurements will be maintained independent. However, calibration of instruments was not maintained independent and therefore the resulting measurements were not independent. As a result, the calibration process failed to ensure that a single failure could not effect two independent mass measurements. Double contingency was violated in cases where two independent uranium mass measurements were required to establish double contingency. A review of NDA calibration data confirmed that no measurement errors actually existed which would have affected the mass readings taken to establish double contingency. This event is being reported because the independence or mass measurement readings was not established and maintained. SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is very low. All historical calibrations were reviewed (Ref. POEF-38.340.00.086) and no discrepancies were identified with historical measurements. Furthermore, ongoing laboratory Quality Assurance programs and practices help ensure errors of this nature remain sufficiently unlikely to be relied on as criticality controls. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): An error in NDA measurements plus uncertainty would have to be low by greater than a factor of two or results in a critical mass of uranium going undetected. if this mass were then subject to the correct geometry, moderation and reflection conditions a criticality could error CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Mass is the only controlled parameter. Two independent measurements of mass are required to ensure double contingency. Since independence of NDA of NDA mass measurements is called Into question, only one independent estimate of mass is available. The absence of a second independent NDA mass measurement represents a loss of one double contingency control. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium was involved in the event. NDA measurements are used to classify cascade deposits as either greater than safe mass or less than safe mass. (Safe Mass is 43.5% of minimum critical mass.) NDA measurements are also used in batching operations to ensure the 235U mass in the final container is less than 350 grams 235U which is less half the minimum critical mass at 100% enrichment and optimum moderation, geometry and reflection conditions. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES Nuclear criticality safety controls include independent mass measurements of 235U. Failure to ensure the calibration of the NDA instrumentation was independent lead to a potential failure of the mass measurements. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: NDA measurements performed for criticality safety purposes have been suspended until independent verification of calibration data requirements is flown into applicable procedures and programs. The certificate holder notified the NRC Resident Inspector and will notify the DOE representative. * * * UPDATE ON 05/26/00 AT 2012 ET BY McCLEERY TAKEN BY MACKINNON * * * Update 1, 5/26/00 The NCSE for the above NCSA failed to specifically address failure in calibration or source checks as part of the contingency event "erroneous uranium analysis or operator error." Therefore, this indicates that the NCSE failed to analyze or bound a credible scenario that could lead to a criticality. A review of past calibration data revealed no suspect calibration or measurements. No known or suspected error in NDA measurements has been discover DOI-344-00-02, Rev A was issued to ensure NDA measurements supporting NCS activities were suspended until requirements for independent verification of NDA calibration data and factors are flowed into applicable procedures. R3DO (Monty Phillips) & NMSS EO (Hodges) notified. The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37032 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-05-25 20:46 | 2000-05-25 21:47 | 2000-05-30 | TURBINE RUNBACK TO 50% DUE TO LOSS OF A MAIN FEEDWATER PUMP FOLLOWED BY A REACTOR TRIP ON LOW LOW STEAM GENERATOR WATER LEVEL. ONE AUXILIARY FEEDWATER PUMP HAD TO BE MANUALLY STARTED. Reactor automatic trip occurred at 2046 ET. Initiating event was steam generator low low water level on "C" steam generator. Prior to the trip Channel 1 vital 120 volt AC power was lost due to the tripping open of EVIA (DC/AC ) inverter AC output breaker. No testing was in progress at this time and the cause of the AC breaker trip is under investigation. When the AC output breaker opened it caused a loss of Channel 1 power. Main feedwater pump "1A" control circuitry interfaces with Channel 1 120 volt AC power and when Main Feedwater pump "1A" control circuitry power was lost main feedwater pump "1A" turbine tripped. The loss of Main Feedwater pump "1A" turbine initiated an automatic main turbine runback to 50% power. After the main turbine runback to 50% power the reactor tripped on steam generator "1C" low low water level. Only one of two motor driven auxiliary feedwater pumps automatically started on steam generator "1C" low low water level. Auxiliary feedwater pump "1A" was manually started approximately 2 minutes after the automatic reactor trip. The licensee is investigating why the "1A" auxiliary feedwater pump did not automatically start. All rods fully inserted into the core and reactor coolant temperature is being maintained at Tave no load condition of 557 degrees F. No PORVs or code safety valves on either the primary or secondary side of the plant opened. All the Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. Offsite electrical grid is stable. The licensee's investigation into the initiating event is continuing. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 05/26/00 AT 1640 EDT BY HEAFNER TAKEN BY MACKINNON * * * Only the Turbine Driven Auxiliary Feedwater Pump and the Motor Driven Auxiliary Feedwater Pump "1B" automatically started. The "1A" Motor Driven Auxiliary Feedwater Pump did not automatically start since its control circuitry is supplied electrical power from Channel 1 vital 120 volt AC power, which was lost. As stated in the original event report, Auxiliary Feedwater Pump "1A" was manually started approximately 2 minutes after the automatic reactor trip. Two of three Primary side Power Operated Relief Valves (PORV) opened and subsequently closed. No secondary side PORVs or code safety valves on either the Primary or Secondary side of the plant opened. Investigation into the event is continuing. R2DO (Tom Decker) notified. The NRC Resident Inspector was notified of this update by the licensee. * * * UPDATE ON 05/30/00 @ 1634 BY DIAL TO GOULD * * * An ongoing evaluation has determined that Main Feedwater Pump "1A" tripped as a result of high discharge pressure which occurred due to the response of the Feedwater Regulating Valves control circuitry. This circuitry was associated with the failed power supply. The NRC Resident Inspector will be informed by the licensee. The R2DO (McAlpine) was notified by the NRC Headquarters Operations Officer. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37031 | -1 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-05-25 08:32 | 2000-05-25 09:21 | 2000-06-22 | AUXILIARY BUILDING FILTERED EXHAUST MAY NOT HAVE BEEN ABLE TO PERFORM ITS DESIGN FUNCTION The licensee discovered both doors on the vestibule to the '1A' Centrifugal Charging Pump Room not fully closed, this may have prevented the Auxiliary Building filtered exhaust system from maintaining a negative pressure in that room. This would render both trains of Auxiliary Building exhaust inoperable per Technical Specifications 3.7.12 and would require entry into Technical Specification 3.0.3. The doors were closed on discovery which returned the unit to compliance with Technical Specifications. The licensee will followup with an investigation into when and how the doors came to be open. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 6/22/00 @ 1610 BY BURGESS TO GOULD * * * RETRACTION After further engineering evaluation, it has been determined that the plant was not outside the design basis during this event. Therefore, this notification is being retracted. The NRC Resident Inspector will be notified by the licensee. The Reg 2 RDO (Landis) was informed by the NRC Operations Officer. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37030 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-05-24 18:04 | 2000-05-24 20:27 | 2000-05-24 | MAIN TRANSFORMER EXPLOSION AND FIRE WITHIN FIVE FEET OF THE TURBINE BUILDING. PRIOR TO THE EVENT, THEY HAD JUST CLOSED THE MAIN TURBINE AND GENERATOR OUTPUT BREAKERS SO THAT THE TURBINE WOULD SYNCHRONIZE TO THE GRID. AT 1804 A MAIN TURBINE TRIP AND MAIN TRANSFORMER TROUBLE ALARM WAS RECEIVED IN THE CONTROL ROOM. SUBSEQUENT TO THE TURBINE TRIP, MAIN GENERATOR TRANSFORMER FIRE ALARMS WERE RECEIVED AND VISUAL VERIFICATIONS CONFIRMED A FIRE ON THE "C" PHASE OF THE MAIN GENERATOR TRANSFORMER. THE FIRE DELUGE SYSTEM ACTIVATED, AND ALTHOUGH EXTERNAL INDICATION THE FIRE HAD CEASED, IT IS EXPECTED THAT THE FIRE CONTINUES TO BURN INTERNALLY TO THE TRANSFORMER. ALL OFFSITE POWER SOURCES ARE STILL AVAILABLE. NO OFFSITE FIRE ASSISTANCE HAS BEEN REQUESTED. THE FIRE HAS BEEN ONGOING INTERNALLY FOR APPROXIMATELY TWO HOURS. THEY ARE IN THE PROCESS OF ELECTRICALLY ISOLATING THE TRANSFORMER FROM BOTH THE GENERATOR AND THE GRID AND TAGGING IT OUT. DELUGE ACTUATION HAS BEEN SECURED AND THEY ARE SPRAYING THE TRANSFORMER WITH FIRE WATER. THEY ARE ALSO MAKING PREPARATIONS TO USE A FOAM FIRE SUPPRESSION AGENT. FURTHER EVALUATION CONTINUES IN REGARD TO THE ENVIRONMENTAL IMPLICATIONS OF THE EVENT. SPECIFICALLY, THE ABILITY OF THE PLANT OIL WASTE SYSTEM TO PROPERLY PROCESS THE MIXTURE OF WATER AND OIL THAT WERE PRODUCTS OF THE COMPONENT FAILURE AND SUBSEQUENT FIRE FIGHTING EFFORTS. THE LICENSEE WILL KEEP THE NRC INFORMED OF ANY ADVERSE CHANGES. THE NRC RESIDENT INSPECTOR WILL BE INFORMED. | 19 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0
37029 | 0 | WASHINGTON DEPARTMENT OF HEALTH |  |  |  |  | 2000-05-22 18:00 | 2000-05-24 18:26 | 2000-05-30 | LICENSEE REPORTED A STOLEN PORTABLE GAUGE. The licensee reported on May 23 that at approximately 6:00 PM the previous evening a Seaman Nuclear C-200 gauge, serial number A-872, with 4.5 milligrams of Ra-226 was stolen. The licensee's technician had stopped by a friend's house in South Seattle on his way home. While there, his pickup truck was stolen from in front of the house. The gauge was locked, in a locked transport box, and the box was chained and locked in the bed of the truck. The licensee believes the thief wanted only the truck and will probably abandon the gauge. The police were notified and the licensee was advised to notify the local papers and post a reward. Overexposures? Unknown. Disposition/recovery: Unknown at this time. * * * UPDATE ON 05/30/00 @ 1400 BY FRAZEE TO GOULD * * * On May 27, 2000, the gauge was found intact and abandoned along a side street in South Seattle, Washington. (The abandoned pickup truck was eventually found elsewhere.) Police and Fire Department personnel responded to the scene and called 206-NUCLEAR (the Washington State radiation emergency line). The Division's Emergency Response Duty Officer determined that the gauge was not leaking, surveyed the exterior, and impounded it. The retrieval was covered by all the major Seattle television stations. The gauge will be returned to the licensee. The R4DO (Sanborn) and NMSS EO ( Hickey) were notified by the NRC Operations Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37028 | 0 | WASHINGTON DEPARTMENT OF HEALTH |  |  |  |  | 2000-05-11 | 2000-05-24 18:05 | 2000-05-24 | Licensee had a source disconnect occur due to a mechanical failure of the drive cable connector. A source disconnect attributable to mechanical failure of the drive cable connector occurred during use of a cobalt 60 radiographic exposure device on May 11. Radiography is routinely conducted by this licensee in a shielded vault (a permanent radiographic installation). An AEA Technologies Model 676 cobalt 60 camera, serial number B105, is generally left set-up between shots. The routine daily equipment check includes a visual check to confirm that the drive cable and camera are still connected. The last quarterly maintenance inspection was at the end of March 2000 and no problems with the drive cable connector were noted. However, during the first shot of the day, the radiographer noticed that the source did not go out smoothly and then failed to retract. The RSO was contacted and after several more attempts to retract the source the licensee decided to secure the area and call in the manufacturer's retrieval experts. Additional shielding, locks and posting were added and a survey of the area including the roof showed no readings above 1 mrem per hour. The state Division of Radiation Protection was notified and staff observed the retrieval on May 12. Once the source was secured, the failed equipment was inspected. No problems were noted with the source assembly or the camera. However, the ball fitting at the drive cable connector's end had become separated from the cable. AEA Technologies took the separated ball and 4 inches of the end of the drive cable back to AEA for analysis. What is the notification or reporting criteria involved? WAC 246-221-250 Notification of incidents (equipment failure) Activity and isotope(s) involved: 71 curies of Cobalt 60. Overexposures? There were no overexposures (however, retrieval personnel received 130 and 65 mrem whole body exposures) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
37027 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-05-24 13:54 | 2000-05-24 15:50 | 2000-05-24 | THE PLANT HAD A REACTOR SCRAM FROM 100% POWER DUE TO LOW REACTOR WATER LEVEL At 13:54 CDT, unit 3 reactor scrammed due to low reactor water level. All rods fully inserted into the core. The expected groups 2, 3, 6 and 8 isolations were received. Both recirc pumps tripped, all Standby Gas Treatment trains started and the 'A' CREV started. The expected Refuel zone and unit 3 reactor zone isolations were received. Both the HPCI system and the RCIC system automatically initiated and injected due to low level following the scram. The actual signal perturbation that caused the reactor trip on low water level is still being investigated. Currently the plant is in a stable condition in mode 3 with investigations in progress. No relief valves lifted and HPCI was secured within the first 5 minutes and RCIC secured a few minutes later. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | ECCS INJECTION | RPS ACTUATION | ESF ACTUATION |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(1)(iv) | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  | 0
37026 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-05-24 14:08 | 2000-05-24 15:48 | 2000-05-24 | LOSS OF VENTILATION TO PAB BATTERY AND INVERTER ROOMS DURING AN APPENDIX R FIRE DURING THE FINAL REVIEW OF THE NEW APPENDIX R REBASELINE PROJECT IT WAS DISCOVERED THAT VENTILATION TO THE PAB BATTERY AND INVERTER ROOMS WOULD BE LOST FOR GREATER THAN 2 HOURS FOR AN APPENDIX R FIRE. FIRE ROUNDS IN THE AFFECTED AREAS HAVE BEEN STARTED AND PROCEDURE REVISIONS ARE IN PROGRESS TO ESTABLISH PORTABLE VENTILATION AS NEEDED. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37025 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-05-24 12:50 | 2000-05-24 14:45 | 2000-05-24 | DISCOVERY OF COMPROMISE OF CLASSIFIED DOCUMENTS/SAFEGUARDS INFORMATION. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. REFER HOO LOG FOR ADDITIONAL DETAILS. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 0
37024 | 0 | CALIFORNIA DEPT OF HEALTH SERVICES |  |  |  |  | 2000-05-23 12:29 | 2000-05-24 13:10 | 2000-05-24 | THE RADIOLOGICAL HEALTH BRANCH OF THE CALIFORNIA DEPARTMENT OF HEALTH SERVICES WAS NOTIFIED BY STERIGENICS INTERNATIONAL THAT THEY HAD A CABLE JAM ON THEIR SOURCE HOIST ARRAY. THIS OCCURRED ON THEIR 600,000 CURIE POOL IRRADIATOR WHILE THEY WERE LOWERING THE SOURCE ARRAY INTO THE SHIELDED POSITION AND THE SOURCE HOIST CABLE JAMMED DUE TO A FRAY ON THE CABLE. THEY LOOSENED THE SHIELDING AROUND THE SOURCE HOIST CABLE AND THAT ALLOWED THE SOURCES TO BE RETURNED TO THE SAFE POSITION. THERE WERE NO OVEREXPOSURES AND NO ABNORMAL RADIATION LEVELS. THE PLANT WAS SHUTDOWN UNTIL MAINTENANCE WAS COMPLETED THIS MORNING @ 6:00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
37023 | 0 | LAKEHEAD PIPELINE |  |  |  |  | 1997-09-30 | 2000-05-23 11:23 | 2000-05-23 | HISTORICAL EVENT REGARDING THE LOSS OF SHUTTER POSITION INDICATION ON A BERTHOLD DENSITY GAUGE A nuclear gauge shutter failed during a routine semi-annual shutter test on 09/30/97. The manufacturer of the nuclear gauge (Berthold Instruments) was notified immediately, and a repair date of 10/07/97 was established. The shield mechanism was replaced on 10/07/97. It was assumed that the shutter was in a partially closed position, but there was no way to tell for sure. The gauge has a shaft control rod that runs from the shutter to the turn knob. Apparently, the shaft control rod broke, and the licensee could no longer determine the position of the shutter. The licensee stated that survey meter readings near the gauge are normally quite low when the shuttle is fully open. The licensee also stated that this failure held no danger to employees or the public because normal operation of the gauge is with the shutter fully open at all times. The nuclear gauge is located on a pipeline, and it is used for density determination of the fluid flowing through the pipe. It has a 1,000-mCi of cesium-137 source located on one side of the pipe and a detector located on the other side of the pipe. The licensee stated that this issue was determined to be reportable during a recent NRC inspection/audit. The licensee notified the NRC Region 3 office (Mike Lafranzo). (Call the NRC operations officer for a site contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 30.50(b)(2)(ii) |  |  |  | 0
37022 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-05-23 09:40 | 2000-05-23 11:07 | 2000-05-23 | DISCOVERY OF A LOOSE CONNECTION WHICH CAUSED INOPERABLE PROCESS COMPUTER SYSTEM (PCS) SITE DATA SYSTEM (SDS) COMMUNICATION IN THE EMERGENCY OPERATIONS FACILITY (EOF) The following test is a portion of a facsimile received from the licensee: "During troubleshooting of an unrelated LAN problem, Telecommunications [personnel] apparently bumped a cable causing the connection to become loose. This loose connection caused the communication to TT10 and TT11 PCS SDS in the EOF to become inoperable. The SDSs were inoperable from 05/22/00 [at] 1523 [CST] to 05/23/00 [at] 0739 [CST] for a total of 16 [hours and] 16 [minutes]." The licensee stated that the control room was notified of this condition at 0940 CST on 05/23/00. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(1)(v) |  |  |  | 0
37021 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-05-23 05:05 | 2000-05-23 08:44 | 2000-06-08 | - HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE DUE TO STUCK OPEN CHECK VALVE - At 0505 on 05/23/00, the High Pressure Coolant Injection (HPCI) System was determined to be inoperable as a result of the discharge check valve being stuck partially open. This condition was discovered during investigation of a low injection header pressure alarm, and subsequent attempts to fill and vent the discharge header were unsuccessful. It is believed that the check valve stuck partially open when the system was secured after a low pressure surveillance test at about 0305. The discharge check valve was mechanically agitated at 0700, and reseated as evidenced by an audible sound and rise in injection header pressure. At the time of discovery, the plant was in Operational Condition 2 with reactor power at 4% and reactor pressure at approximately 500 psig. All other safety related equipment was operable at the tune of discovery, with the exception of the 'A' Residual Heat Removal Pump, which was aligned for suppression pool cooling mode of operation. There was no significant impact to overall plant safety as a result of this condition. Plant maintenance and engineering personnel are currently evaluating the failure of the HPCI System discharge check valve. injection header fill and vent is in progress to determine the amount of air that is present and restore the system to an available condition. This information will be used to determine if the safety function of the HPCI System was unavailable as a result of the discharge check valve malfunction. A root cause investigation team has been assembled, and evaluation of system and personnel performance is in progress. The licensee notified the NRC Resident Inspector and plans to notify local officials. * * * UPDATE ON 6/8/00 @ 1219 BY CONICELLA TO GOULD * * * RETRACTION As discussed in the notification. the HPCI low discharge header pressure alarm was received, prompting an immediate investigation. The discharge check valve was mechanically agitated which resulted in the seating of the valve and clearing of the alarm. Sticking of the discharge check Valve provided a leakage path thus preventing the keep fill system from achieving pressure sufficient to clear the alarm setpoint. The amount of mechanical agitation required was minimal. HPCI was then removed from service to allow maintenance troubleshooting on the valve. It is believed that the discharge check valve stuck in the partially open position following the low pressure response time surveillance testing which had been completed approximately two hours prior to the event. This was a result of the low delta P across the valve associated with that testing. Prior to the cited surveillance test, a different HPCl surveillance (HPCI Flowpath Verification) had been successfully completed and HPCI had been determined to be operable. Investigation of the valve revealed very minor misalignment which may have been the cause at the slight binding. This condition would not prevent the safety function of HPCI from being performed. Following the investigation HPCI was removed from service and the plant entered a 14 day LCO. The valve was repaired and HPCI was retested and declared operable. The keep fill system was always sufficient. The NRC Resident Inspector will be notified. The Reg 1 RDO (Moslak) was notified. | 4 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
37020 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-05-23 02:00 | 2000-05-23 06:10 | 2000-05-23 | PHYSICAL SECURITY REPORT - UNSECURED/UNATTENDED SECURITY GUARD WEAPON AND AMMUNITION INSIDE PLANT PROTECTED AREA FOR ABOUT 25 MINUTES. COMPENSATORY MEASURES WERE IMMEDIATELY TAKEN UPON DISCOVERY. THE LICENSEE PLANS TO NOTIFY THE NRC RESIDENT INSPECTOR. CONTACT THE NRC OPERATIONS OFFICER FOR ADDITIONAL DETAILS. * * * UPDATE ON 5/23/00 @ 1342 BY PLUMLEE TO GOULD * * * RETRACTION LICENSEE IS RETRACTING THIS EVENT SINCE NO WEAPON WAS LOST. THE NRC RESIDENT INSPECTOR WILL BE INFORMED. THE REG 4 RDO (JOHNSON) WAS NOTIFIED. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 0
37019 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-05-22 23:38 | 2000-05-23 02:52 | 2000-05-23 | - HIGH PRESSURE COOLANT INJECTION SYSTEM AUTO ISOLATED WHILE BRINGING IT ON LINE - At 2338 on 05/22/00, the High Pressure Coolant Injection (HPCI) System isolated due to a spurious high steam flow isolation signal. A valid high steam line flow condition would normally be indicative of a piping break; however, a piping break did not occur. Although the signal was not valid, this is nonetheless considered an Engineered Safety Features (ESF) Actuation since a containment isolation had occurred. The Hope Creek reactor was in Operational Condition 2 (Startup) with Reactor Coolant System (RCS) pressure at 200 psig and power at about 4%. The HPCI System steam line warmup, which is required to place the HPCI System in a standby alignment, had just commenced. When shutdown, the HPCI steam line is isolated from the reactor by three containment isolation valves. These valves are an outboard valve, an inboard valve, and a bypass valve around the inboard valve for steam line warm-up purposes. As part of the steam line warmup procedure, the outboard valve is fully opened and the inboard bypass valve is throttled to slowly heat up and pressurize the steam line. Once the steam line is pressurized, the inboard valve is opened. During the initial phases of the steam line warmup process, a high steam line flow signal was generated when the bypass valve was throttled open. This occurred due to steam pressure and flow perturbations within the steam line. As a result, an isolation signal was generated and the bypass valve automatically closed as expected for this isolation signal. Prior to resetting the isolation signal, the HPCI steam line was verified to be operable. The HPCI System warmup was then recommenced and the HPCI System is currently in its standby alignment. The licensee notified the NRC Resident Inspector. | 4 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37018 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2000-05-22 21:59 | 2000-05-23 00:11 | 2000-05-23 | - AUTO Rx SCRAM FROM 100% AFTER REPLACEMENT OF MAIN TURBINE CONTROL VALVE SOLENOID - On 05/21/00, the Unit 2 Main Turbine #1 Control Valve Fast Acting Solenoid failed its required Tech Spec Surveillance Test. At 2159 CDT on 05/22/00, during return to service activities following replacement of this solenoid, Unit 2 automatically scrammed from 100% power due to receipt of an APRM High-High RPS Actuation signal. All control rods inserted completely. No safety/relief valves lifted. Steam is being dumped to the main condenser. During the transient, reactor vessel water level dropped to +8 inches (normal level is +30 inches) and all PCIS Group II actuations occurred, as expected. These actuations included Reactor Building Ventilation Valves closed, Train 'A' Standby Gas Treatment System auto started (Train 'B' SBGT System was inoperable), Control Room Ventilation System isolated, and Containment Isolation Valves closed. Quad Cities has one Emergency Diesel Generator (EDG) for each unit and a shared EDG. The Unit 2 EDG received a spurious auto start signal during the 4 KV auxiliary bus power transfer to the reserve transformer. The licensee secured the Unit 2 EDG. Unit 2 is now stable in Condition 3 (Hot Shutdown) with reactor vessel water level within its normal band. This event had no effect on Unit 1 which is at 100% power. The licensee is investigating the cause of this reactor scram. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0708 ON 05/23/00 BY JOHN LECHMAIER TO JOLLIFFE * * * During the above transient, the reactor vessel water level reached +8 inches and all PCIS Group II actuations occurred, as expected. The reactor vessel water level then increased to +48 inches, the Reactor Feedwater Pump trip level. At 2215 CDT, the Reactor Water Cleanup (RWCU) System was placed in service to assist in reactor vessel water level control. The reactor vessel water level decreased again and subsequently, at 2229 CDT, reached +8 inches. The RWCU System isolated and all PCIS Group II actuations occurred. Unit 2 remains stable in Condition 3 (Hot Shutdown) with reactor vessel water level within its normal band. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO Pat Hiland. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37017 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-05-22 11:53 | 2000-05-22 16:27 | 2000-05-22 | POSITIVE TEST FOR ALCOHOL AN ENTERGY EMPLOYEE TESTED POSITIVE FOR ALCOHOL FOLLOWING A FOR-CAUSE TEST. UPON NOTIFICATION, THE EMPLOYEE'S PLANT ACCESS AUTHORIZATION WAS SUSPENDED AT RIVER BEND STATION PENDING FURTHER INVESTIGATION. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.73 |  |  |  | 0
37016 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-05-22 12:59 | 2000-05-22 13:42 | 2000-06-19 | REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM MAY NOT BE PROTECTED BY STEAM LEAK DETECTION CIRCUITRY. A LICENSEE ENGINEERING REVIEW IDENTIFIED A SECTION OF RCIC SYSTEM PIPING WHICH MAY NOT BE PROTECTED BY THE STEAM LEAK DETECTION CIRCUITRY. SPECIFICALLY, THE STEAM SUPPLY ISOLATION SIGNAL MAY NOT ISOLATE A POSTULATED CRACKED STEAM SUPPLY LINE PRIOR TO CRACK PROPAGATION AS IN THE DESIGN INTENT OF THE STEAM LEAK DETECTION SYSTEM. THE LICENSEE IS CONTINUING WITH ITS INVESTIGATION. THE RCIC SYSTEM WAS NOT DECLARED INOPERABLE AND THE LICENSEE HAS NOT ENTERED ANY LCO ACTION STATEMENTS. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. * * * RETRACTED ON 6/19/00 AT 1254 EST BY MARK ABRAMSKI TO FANGIE JONES * * * "A review of plant design and licensing basis documentation has confirmed that the design and licensing basis requirements for the SLD system as defined in the UFSAR have not been properly maintained. It is therefore not clear that the ability to detect and isolate a leak prior to the leak propagating to a break in this section of pipe is in fact a design basis requirement. "LER 99-013 identified the condition where the SLD system was outside the design basis of the plant because the system could not reliably detect a 7 GPM leak (but could detect a 25 GPM leak). The review of plant design and licensing basis documentation discussed above has identified the need to revise corrective actions identified in LER 99-013 to include a more comprehensive redefinition of the design and licensing basis requirements for the SLD system. The event reported in 10 CFR 50.72 notification log number 37016 is therefore an extent of the condition reported in LER 99-013 and will therefore be discussed in the revision to LER 99-013. "On this basis 10 CFR 5072 notification log number 37016 is redundant to the condition reported in LER 99-013 and 10 CFR 50.72 notification log number 37016 is therefore retracted." The licensee notified the NRC Resident Inspector. The R1DO (Robert Summers) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
37015 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2000-05-22 02:53 | 2000-05-22 04:48 | 2000-05-23 | - ESF ACTUATION OF REACTOR WATER CLEANUP SYSTEM FOR UNKNOWN REASONS - At 0253 on 05/22/00, the plant experienced an isolation of the Reactor Water Cleanup System on a Division 2 isolation signal when the Residual Heat Removal heat exchanger vent valve closed unexpectedly. An apparent electrical power supply spike to the Division 2 isolation instrumentation occurred. No testing or maintenance activities or electrical storms were occurring at the time of the isolation. The licensee is investigating the cause of the isolation. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/23/00 @ 1317 BY SANFORD TO GOULD * * * RETRACTION Upon further review, "the power supply fluctuation was determined to be caused by a failed capacitor in a Division 2 regulating transformer and the Division 2 electrical distribution subsystem was declared inoperable. The momentary power system perturbation caused a partial ESF isolation to be generated with the voltage on the Division 2 electrical distribution system remaining at the specified value. Since there was not an actual loss of power to the divisional subsystem that would have required an ESF actuation on loss of power, this is not a valid signal. Therefore, in accordance with 10 CFR 50.72(b)(2)(ii)(B), Reactor Water Clean-Up isolations from invalid signals are not reportable. "Additionally, the Residual Heat Removal (RHR) Heat Exchanger Vent valve is a single component of a complex train (Both RHR and Isolation System) and does not, in itself, mitigate the consequences of a significant event. Therefore, in accordance with the guidance provided in NUREG 1022, Section 3.3.2, the vent valve closure is not reportable. "The electrical distribution power supply was restored to Operable at 1701, May 22. 2000." The NRC Resident Inspector was notified. The Reg 3 RDO (Hiland) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37014 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2000-05-19 | 2000-05-19 16:55 | 2000-05-19 | EVAPORATION POND LINER LEAKING The licensee reported that the inner liner of evaporation pond #4 appears to be leaking. Increased conductivity has been detected in the underdrain system. The pond contains a brine solution with trace amounts of Ra-226 and uranium. The licensee believes that the leakage is through a poor weld on a six inch patch of the inner liner located just above the waterline. High winds in the area have been pushing the water level above the patch. Samples taken from a standpipe located near the patch indicate conductivity approaching that of the brine solution. The licensee is pumping down the pond for a liner inspection. No leakage into the soil has occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
37013 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2000-05-19 10:45 | 2000-05-19 14:34 | 2000-05-19 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM REFRIGERATION CONTROL UNIT INOPERABLE "On May 19, 2000, at 1045 hours, while performing the Control Room Emergency Ventilation System monthly operability test. the refrigeration control unit failed to start. The cause of the failure is unknown, and troubleshooting is in progress. Technical Specification 3.8.D, Action 1.b was entered, placing both units in a 30 day LCO. "This is being reported per 10 CFR 50.72(b)(2)(iii)(D), loss of a safety function needed to mitigate the consequences of art accident." The NRC resident inspector will be informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
37012 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-05-19 11:38 | 2000-05-19 12:23 | 2000-05-19 | OFFSITE NOTIFICATION REGARDING SPURIOUS SIREN ACTIVATION At 1138, the licensee was notified that prompt notification siren #4 in Barnegat Township had spuriously activated. The siren was deactivated at 1210, and a faulty circuit board was identified in the siren. The licensee contacted the Barnegat Township Police Department, the Ocean County Sheriff's office and the New Jersey State Police of the siren activation. The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37011 | 0 | OKLAHOMA GAS & ELECTRIC |  |  |  |  | 2000-05-17 | 2000-05-18 17:16 | 2000-05-18 | MISSING RADIOACTIVE SOURCE The licensee reported that a 200 mCi Cs-137 source was discovered to be missing from a group of sources removed from the Muskogee Power Plant for disposal. Several Omart model SHDP source holders (with sources) were transferred to Radiation Technology, Inc., a contractor, for disposal. These source holders had been stored in a warehouse at the power plant for some time before being transferred to the contractor. The licensee was notified on 5/17/2000 by the contractor that one of the source holders was empty. The licensee has searched their facility for the source but has been unable to locate it. The licensee has already contacted NRC Region 4 (L. Howell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | OK | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
37010 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-05-18 07:30 | 2000-05-18 09:43 | 2000-05-18 | OFFSITE NOTIFICATION REGARDING THE FAILURE OF A MAIN DAM SKIMMER GATE TO CLOSE The following text is a portion of a facsimile received from the licensee: "[The] Federal Energy Regulatory Commission (FERC) was notified at 0730 on 05/18/00 in accordance with 18CFR12.10(a)(1) for a condition affecting the safety of the project." "Skimmer gate 1B at the main dam failed to close under normal operating conditions. The gate is currently open, providing minimum flow. Corrective action is in progress." The licensee stated that the skimmer gate is used to provide minimum flow downstream to the river and to provide adequate level control of the main reservoir for the lake (which supplies cooling water to the plant). The required downstream flow of 40 scfm is currently being maintained. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37009 | -1 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2000-04-18 | 2000-05-17 15:41 | 2000-05-19 | LOST ONE SEED CONTAINING 0.5 MILLICURIE OF IRIDIUM-192 After applicator removal and the seeds were inventoried, it was determined that one seed out of sixty four seeds was missing. Each of the seeds contained 0.5 mCi of Ir-192. A survey of the patient and room did not find the missing seed. An investigation is ongoing to find the lost seed. It is possible that the right number of seeds were not implanted. The applicator was removed with the seed intact, the seeds are contained in ribbons and the ribbons are retained in the applicator, making it unlikely that the seed would have been lost during the treatment. The patient has been discharged and there is no problem with dose administered with one seed missing at the beginning. Also, there is little safety implications to the public. * * * RETRACTION 1533 5/19/2000 FROM MARK RICHARD TAKEN BY BOB STRANSKY * * * The licensee reported that the seed was not missing. The initial count of seeds was erroneous. When the seeds were independently recounted, all seeds were present. Notified R3DO (Madera). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0
37008 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-05-17 09:14 | 2000-05-17 12:56 | 2000-05-17 | MANUAL REACTOR TRIP AFTER LOSS OF TWO CONDENSATE PUMPS The licensee was performing preventative maintenance on electrical equipment when an error caused the loss of the '1B' 4160 volt non-vital bus. When the bus deenergized, two condensate pumps were lost resulting in loss of feed to the reactor. The operators manually scrammed the reactor, all rods fully inserted and the plant is stable in Mode 3 with level control from the balance of the condensate and feed system. Pressure control is by RCIC supplemented by SRVs as needed. The plant is continuing to Cold Shutdown and an investigation into the initiating event is pending. A press release is planned by the licensee. The licensee has notified the local and state authorities as well as the NRC Resident Inspector. * * * UPDATE AT 1547 EDT ON 5/17/00 BY VINCE PATTEN TO FANGIE JONES * * * During the plant cooldown received a MSIV closure signal due to low vacuum as a result of breaking vacuum as a result of loss of seal steam to the main turbine. RHR reject to radwaste, 1E12-F049, automatically isolated on a level 3 signal due to momentary reactor vessel level shrink from SRV operations. The licensee is continuing to cooldown the plant. Pressure control is being maintained by RCIC and SRVs. Level control is being maintained with control rod drive (CRD) with level at 29.7 " (about 2 " below normal). The licensee notified the NRC Resident Inspector. The Headquarters Operations Officer notified the R3DO (John Madera). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
37007 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2000-05-15 09:30 | 2000-05-16 07:28 | 2000-05-16 | 24 HOUR FITNESS FOR DUTY EVENT - At 0930 on 05/15/00, a licensee supervisor tested positive for alcohol during a random drug and alcohol test. The licensee withdrew the employee's access authorization to the plant protected area after verification of the positive test. The licensee is determining further corrective actions. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.73 |  |  |  | 0
37006 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-15 15:30 | 2000-05-15 18:50 | 2000-05-15 | REPORTABLE QUANTITY FOR OIL DISCHARGE EXCEEDED "On 05/15/00 at 1530, it was determined that the Reportable Quantity (RQ) value for oil (i.e, greater than 25 gallons) was exceeded. Operations personnel reported that a lubrication oil spill had occurred on the roof of the X-330 Process Building and after an investigation was initiated by Environmental Compliance personnel, it was determined that the total quantity of the spill was approximately 500 gallons. The cause of the spill is still under investigation. "The spill resulted in a release of oil to the environment exceeding the RQ in accordance with Ohio Administrative Code Rule 3750-25-20 thereby initiating the release reporting requirements contained therein. Oil was discharged via the storm sewer system to the X-230J-7 East Holding Pond and the southernmost branch of the West Drainage Ditch. "At the time of this report, the oil is contained on-site and no off-site consequences have occurred. The spill is currently being cleaned up by Chemical Operations personnel using oil diversion equipment and absorbent material." The licensee notified the NRC Resident Inspector as well as local and state authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
37005 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-05-15 06:53 | 2000-05-15 16:30 | 2000-05-15 | TRAFFIC ACCIDENT INVOLVING TRUCK TRANSPORTING EQUIPMENT FROM BYRON STATION "At 0753 EDT on 05/15/00, a traffic accident occurred involving a semi-tractor trailer and a car in the state of Pennsylvania (State Route 4005, New Galilee Road, Darlington Township). The truck was carrying a spent fuel rack shipped from Byron Station as Radiological Material LSA n.o.s 7 UN 2912 Fissile Excepted (ComEd, Byron, Illinois) that was to be recycled by vendor "Alaron" in Wampum, Pennsylvania. The container for the rack was not damaged. There was no affect to the surrounding area due to the shipment. The vehicle accident caused traffic to be suspended on Route 4005. A nearby school utilized a different building for classes. The Pennsylvania State Police responded to the scene and managed the vehicle traffic. A Safety Officer from Alaron responded to the site to confirm there was no radiological issues. The Pennsylvania State Police issued a traffic report discussing hazardous materials involved in a traffic accident. This press release requires notification of NRC in accordance with 10 CFR 50.72(b)(2)(vi)" The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37004 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-05-15 12:16 | 2000-05-15 14:25 | 2000-05-15 | OFFSITE NOTIFICATION TO LOCAL AND STATE AUTHORITIES DUE TO LEAKING FUEL OIL TANK "This report is being made for an event for which a notification to another government agency (i.e., NYSDEC/WCDOH) has been made. On May 15, 2000 at 1216 hours, a notification was made to the Westchester County Department Of Health (WCDOH) and subsequently a notification to the New York State Department of Conservation (NYSDEC), Spill Report Number 00-01912, for a failed leak tightness test on the sewage treatment plant underground fuel oil storage tank. A vacuum leak test was performed by a NYS qualified vendor on the underground storage tank. A vacuum could not be maintained and air in-leakage could be heard indicating a leak in the tank. Fuel oil is being removed from the tank and excavation initiated to perform visual inspections." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
37003 | 0 | MALLINCKRODT, INC. |  |  |  |  | 2000-04-23 | 2000-05-15 13:12 | 2000-05-15 | LOST DEPLETED URANIUM SHIELD WITH USED TECHNETIUM-99 GENERATOR On April 23, 2000, a depleted uranium (DU) shield was declared lost in accordance with Mallinckrodt, Inc. (Ml) site procedures for tracking and accountability of this material. This shield was shipped as part of a Mo-99/Tc-99m Generator from the Maryland Heights facility on March 12, 1999. It was shipped to a Mallinckrodt, Inc pharmacy in North Attleboro, MA. The pharmacy received the generator and it was offered for return shipment to our site on March 31, 1999. At the time it was offered for shipment, the safe also contained a generator column with approximately 440 mCi of Mo-99. The generator was shipped via Del Med, Inc. The generator went to a Del Med warehouse in South Plainfield, NJ and was stored until April 8, 1999. Del Med records indicate the package was then shipped to the Maryland Heights facility via Associated Courier. Associated Courier has indicated the generator was returned to the Maryland heights facility. Return generator packages are not tracked by the couriers with an individual package number. The packages are generally collected on a pallet in the courier's warehouse and transported to Maryland Heights when a pallet is full. They generally arrive at Maryland Heights with a single bill of Lading. We do not become aware of a particular generators serial number until the package is inspected, opened, and the generator bar code is scanned into our system. We have no record of this generator being scanned back into our system. This indicates to us that it never arrived on our site. We have no record of this DU shield returning to the Maryland Heights facility. If the safe was reused without check-in, it would have shown up on subsequent scanning when shipped from our facility or upon arrival after it's subsequent use. Mallinckrodt believes the package was not delivered to the Maryland Heights facility and was lost in the transportation cycle. The location of this safe is unknown to Mallinckrodt and the carriers involved in it's transportation. Our site procedures allow a one year time frame for a depleted uranium shield to be returned to our site after the expected return date. This allows time for customers to utilize the generator and make necessary transportation arrangements, couriers to search their warehouses, and time for the shields to cycle through Mallinckrodt's systems. This package had an expected return date of April 23, 1999. The one year time frame for this missing safe expired on April 23, 2000. As part of our investigation, we contacted the original pharmacy and the two couriers who handled this package. The pharmacy has provided a copy of a bill of lading indicating they offered the DU safe for shipment. The couriers have indicated they have conducted a search of their warehouses and do not have the DU safe in their possession. The safe itself contains approximately 8000 µCi of U-238 metal encapsulated in stainless steel. The safe is stamped with the legend "Caution-Radioactive Shielding-Uranium" in accordance with 10CFR40.13(c)(6). The dose rate on contact with the DU safe is approximately 3 to 4 mrad/hr. As a result of the construction of the safe, and the low dose rates exhibited by this material, no significant exposures would be expected to members of the public. MI has been in contact with NRC Region 3 (James Cameron). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
37002 | -1 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-05-15 04:48 | 2000-05-15 11:47 | 2000-06-06 | OUTBOARD MAIN STEAM ISOLATION (MSIV) VALVE FOUND CLOSED. At 0448 PDT on 05/15/00, the outboard main steam isolation valve # MSIV-V-28A was found in the closed position (green indicating light on). Follow-up verification of the 'A' main steam line flow (0%) and the plant computer valve position verified that the valve was closed. The plant computer indicated that the valve closed at 0254 PDT and it was discovered closed at 0448 PDT. No work was being performed on the main steam system or in the area of the main steam system when the valve closed. The plant computer indicated that the valve had fast closed. The plant entered the Limiting Condition of Operation for Primary Containment Isolation Valve and placed the control switch for the MSIV in the closed position. There was no valid ESF Actuation signal that caused the valve closure. The plant was operating at 62% power and did not experience a transient as a result of the MSIV closure (no flux tilt). Licensee investigation into the cause of the closure is continuing. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 6/6/00 @ 1155 BY MCBRIDE TO GOULD * * * RETRACTION The event notification report associated with the above event is hereby retracted. The event and conditions associated with the event do not meet NUREG 1022, Rev. 1, reporting criteria. Only a single component, MSIV-V-28A, actuated (closed). The single component (MSIV) is not sufficient to mitigate the consequences of single events. There was not a manual or automatic ESE system actuation. An ESF signal (valid or invalid) was not generated. Therefore, in accordance with the statements of considerations for NUREG 1022, Rev. 1,( 10CFR50.72(b)(2)(ii), there was not a sufficient number of channels (zero) in a multichannel ESF actuation system to meet the definition of actuation of enough channels to complete the minimum actuation logic for a train or the system. For these reasons, this event does not meet the reporting criteria of 10CFR50.72(b)(2)(ii) and is hereby retracted. The NRC Resident Inspector was notified. The Reg 4 RDO (Pellet) was notified. | 62 | 0 | 0 | 62 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
37001 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-05-15 00:43 | 2000-05-15 04:04 | 2000-05-16 | UNUSUAL EVENT DUE TO AUXILIARY TRANSFORMER EXPLOSION & FIRE; LOSS OF OFFSITE POWER - At 0043 PDT on 05/15/00, the licensee declared an Unusual Event due to auxiliary transformer #1-1 exploding and catching on fire. This resulted in the loss of offsite power and an automatic trip of Unit 1. The licensee called the offsite fire department and they responded to the plant. Auxiliary transformer #1-1 is located outside the turbine building (north end). Three of three Unit 1 emergency diesel generators started and loaded and are supplying emergency power to vital Unit 1 buses. Auxiliary transformer #1-1 supplies backup power to Unit 1 emergency buses. The Unit 1 12 KV buses are energized. Unit 1 reactor coolant pumps are running providing forced circulation. Unit 1 automatically tripped from 100% power. All control rods inserted completely. Steam is being dumped to the atmosphere. Unit 1 has no steam generator tube leaks and no fuel leaks. The auxiliary feedwater system automatically started, as expected. A #1-2 steam generator code safety valve failed open for about 25 - 30 minutes about 30 minutes after the reactor trip. The valve is now closed. There was no safety injection actuation. Unit 1 is stable in Mode 3 (Hot Standby). This event had no effect on Unit 2 which is stable at 100% power. The licensee notified state and local officials and the NRC Resident Inspector. At 0143 PDT, the fire is out. No personnel were injured. At 0405 CDT, NRC Region 4 entered the Monitoring Phase of Normal NRC Response Mode. * * * UPDATE AT 0726 ON 05/15/00 FROM MARK LEMKE TO JOLLIFFE * * * The licensee determined that an electrical fault on the low voltage side of auxiliary transformer #1-1 caused extensive damage to the 12 KV buswork and nearby buswork used to supply the Unit 1 4 KV buses from offsite power following a plant shutdown. Auxiliary transformer #1-1 did not explode and is intact. The licensee also determined that there was not a failure of a main steam code safety valve. However, following closure of the main steam isolation valves, a code safety valve on the #1-2 steam generator did lift and did not fully reseat. Plant operators took manual action to lower steam generator pressure, causing the valve to reseat. There was no release of radiation from the plant. The California Department of Forestry responded to the site. The licensee is continuing to investigate the cause of this explosion and has issued a press release. * * * AT 0900 ON 05/15/00 COMMISSIONERS' ASSISTANTS BRIEFING * * * IRO (Frank Congel, Joe Giitter); NRR Projects (Steve Dembek); OPA (Bill Beecher); OSP (Cardelia Maupin); IP (Howard Faulkner); CA (Tom Combs); Chairman Meserve Asst (Mike Tschiltz); Comm Dicus Asst (Joe Olencz); Comm McGaffigan Asst (Jeff Sharkey); Comm Diaz Asst (Tony Hsia); Comm Merrifield Asst (John Thoma); NRR (Ed Goodwin); R4 (Elmo Collins [Briefer], Bill Jones, et al). * * * UPDATE AT 1358 EDT ON 5/16/00 BY D. PETERSON TO FANGIE JONES * * * The licensee terminated the Unusual Event at 0959 PDT. Offsite power has been restored to the 4 KV vital busses. The diesel generators have been shutdown. The RCS temperature is 380 °F and pressure is 920 psig. The plant will continue to Cold Shutdown after chemistry hold is complete. The licensee notified the NRC Resident Inspector. The NRC Headquarters Operation Officer notified the R4DO (Bill Jones), IRO (Joseph Giitter), NRR (William Beckner), EDO Office (Mark Satorius), PAO (Sue Gagner), FEMA (Austin). NRC Region 4 exited the Monitoring Phase of Normal Mode at 1414 EDT. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION | ESF ACTUATION | COMM ASST BRIEF | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a)(1)(i) | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  | 0
37000 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-05-14 15:05 | 2000-05-14 20:01 | 2000-05-17 | THE LICENSEE DECLARED THE DIVISION 3 EMERGENCY DIESEL GENERATOR (EDG) INOPERABLE AND THE PLANT ENTERED AN LCO ACTION STATEMENT. THE DIVISION 3 EDG WAS DECLARED INOPERABLE DUE TO THE SOAK BACK PUMP (SUPPLIES LUBE OIL TO THE DIESEL SO THAT IT IS READY TO START) TRIP FAILURE. THE CAUSE OF THE FAILURE IS A FAULTY RELAY FOR THE PUMP. THEY WILL REPLACE THIS RELAY. THIS EDG SUPPORTS THE HIGH PRESSURE CORE SPRAY (HPCS) SYSTEM FOR SAFETY FUNCTIONS. THE HPCS SYSTEM HAS NOT BEEN DECLARED INOPERABLE AND THE DIVISION 3 EDG IS STILL FUNCTIONAL. THE PLANT HAS 12 HOURS TO BE IN CONDITION 3 AND 36 HOURS TO BE IN CONDITION 4. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. * * * RETRACTED AT 1155 EDT ON 5/17/00 BY CHRIS MILLER TO FANGIE JONES * * * The licensee is retracting this event notification, after further review, it was determined that this event was not reportable as there was a 72 hour delay before action to shut down the plant became necessary. Offsite power was in service and the other EDG was available and in accordance with Tech Specs the licensee had 72 hours to restore the EDG before further action was necessary The Division 2 EDG was returned to service well within the 72 hours. The licensee informed the NRC Resident Inspector. The R4DO (Bill Jones) was notified by the NRC Operations Officer. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36999 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-05-13 13:26 | 2000-05-13 16:25 | 2000-05-13 | At 1325 on 05/13/00, a Reactor Protection System scram signal was received due to a high Scram Discharge Volume level condition. The high Scram Discharge Volume level condition occurred as a result of an Alternate Rod Insertion test signal that was initiated from the Redundant Reactivity Control System during a planned valve testing activity. The Alternate Rod Insertion test signal depressurized the scram air header, causing all control rod scram inlet and outlet valves to open and Scram Discharge Volume vent and drain valves to close as designed. Control room personnel involved in the valve testing activity incorrectly believed that manipulation of the Alternate Rod Insertion test switches for one second would allow an Alternate Rod Insertion valve to be tested following planned maintenance, without depressurizing the scram air header. Control Room personnel reset the Redundant Reactivity Control and Reactor Protection Scram signals in accordance with plant procedures at 1343, after initial validation of the sequence of events. At the time of the event, reactor core reload was in progress in Operational Condition 5. All control rods were previously verified to be fully inserted in support of core alterations. 'B' and 'D' channel equipment are considered protected for defense in depth, and planned maintenance is in progress on 'A' and 'C' channel equipment. The 'B' Residual Heat Removal pump remained in service in shutdown cooling throughout the event, and reactor cavity level and temperature were unaffected. There was no impact to overall plant safety as a result of this event. The response of the Alternate Rod Insertion valve that was to be tested is currently being evaluated. A root cause investigation team has been assembled, and evaluation of system and personnel performance is in progress. The NRC Resident Inspector will be informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36998 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-05-12 18:00 | 2000-05-12 18:57 | 2000-05-13 | PLANT ENTERED A TECH SPEC REQUIRED SHUTDOWN DUE TO THE ELECTROMATIC RELIEF VALVES AND ASSOCIATED ADS BEING DECLARED INOPERABLE. While preparing a spare Electromatic Relief Valve for installation in the upcoming refueling outage, Oyster Creek identified that the valve's electrical (Patel) connector was not properly sealed. As such, the Environmental Qualification of the electrical connectors for these valves are questionable. Based on this discovery, Oyster Creek has declared all the Electromatic Relief Valves (and associated Automatic Depressurization System) inoperable. During a Small Break LOCA, these valves are required to function in order to depressurize the reactor. In accordance with the plant's Technical Specifications, Oyster Creek is in the process of shutting down. The plant has 24 hours to be <110°F and be in Cold Shutdown Condition in the following six hours. This condition is reportable under 10CFR50.72(b)(1)(ii)(B) for operation of the plant outside design basis. Testing is being conducted in parallel with the shutdown in order to determine if the existing configuration is acceptable for continued operation. The NRC Resident Inspector was notified. * * * UPDATE ON 05/13/00 AT 0836 EDT BY PIETRUSKI TAKEN BY MACKINNON * * * After a review of the Electromatic Relief Valve power connectors bench test for EQ requirements, it has been concluded that there is reasonable assurance that the Electromatic Relief Valves will perform their function as designed. The Electromatic Relief Valves are considered operable, the Limiting Condition of Operation has been exited, and shutdown has been terminated at 0654 EDT. Reactor power is currently 75% and plans are to return to 100% power. The NRC Resident Inspector was notified of this update by the licensee. The NRC Operations Officer notified the R1DO (John Rogge). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | OUTSIDE DESIGN BASIS | TECH SPEC LCO A/S |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(i)(A) | 50.72(b)(1)(ii)(B) |  |  | 0
36997 | 0 | NORTH CAROLINA DIV OF RAD PROTECT |  |  |  |  | 2000-05-12 09:15 | 2000-05-12 16:30 | 2000-05-12 | HUMBOLDT NOTIFIED THE NORTH CAROLINA DIVISION OF RADIATION PROTECTION OF A MISSING MOISTURE DENSITY GAUGE. A HUMBOLDT MOISTURE DENSITY GAUGE, MODEL #5001C, SERIAL #1966, WAS SHIPPED FROM THE MANUFACTURER IN RALEIGH, NC, TO COPLAY, PA, VIA THEIR CARRIER, ROADWAY EXPRESS. AFTER FIVE DAYS THE CUSTOMER NOTIFIED HUMBOLDT THAT THEY HAD NOT RECEIVED THE GAUGE. HUMBOLDT THEN CALLED ROADWAY AND FOUND OUT THAT THE GAUGE WAS MISSING IN TRANSIT. A TRACE WAS PUT OUT BY ROADWAY FOR THE GAUGE AND THEY BELIEVE IT MAY HAVE BEEN TRANSFERRED TO ANOTHER TRAILER IN WINSTON-SALEM, NC WHICH WAS SCHEDULED TO GO TO INDIANAPOLIS, IN. THE SUSPECTED TRAILER HAS BEEN LOCATED IN INDIANA, AND THEY WILL TAKE IT BACK TO THEIR HUB IN INDIANAPOLIS TO UNLOAD IT TO VERIFY IF THE GAUGE IS THERE. THE GAUGE CONTAINED 10 MILLICURIES OF CESIUM-137 AND 40 MILLICURIES AMERICIUM/BERYLLIUM. THEY ARE ALSO CHECKING OTHER TRAILERS THAT LEFT FROM THE WINSTON/SALEM, NC HUB. * * * UPDATE ON 5/12/00 @ 2244 BY ACCATTATO TO GOULD * * * THE GAUGE WAS RECOVERED IN INDIANAPOLIS AND HAS BEEN REDIRECTED TO THE ORIGINAL CUSTOMER. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | NC | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0
36996 | 0 | COGEMA MINING INC |  |  |  |  | 2000-05-09 | 2000-05-12 15:30 | 2000-05-12 | SAMPLES COLLECTED AT A MONITOR WELL EXCEEDED TWO OF ITS THREE UPPER CONTROL LIMITS. A routine quarterly water sample collected on 05/09/00 from monitor well #M2 exceeded two of its three upper control limits (UCLs). A confirmation sample was collected on 05/11/00, which also exceeded two UCLs. Monitor well #M2 was then placed on excursion status as per license section 11.2 and its sampling frequency increased to weekly. Well #M2 is a perimeter ore zone monitor well located approximately 300 feet west of the restored Production Unit 2 boundary, at the Irigaray Mine, Johnson County, Wyoming. The nearest community is Linch, Wyoming, approximately 23 miles to the southeast. Analysis data: Date Chloride Conductivity Alkalinity Uranium Sampled mg/l µmhos/cm2 mg/l mg/l U3O8 ULC 18.0 UCL 685 UCL 131.1 UCL none 05/09/00 19.3 814 94.3 <0.4 05/11/00 19.3 799 96.6 <0.4 Health and Environmental Hazards: None. Investigative Action: Conduct further sampling to try to determine the extent and direction of the excursion. Written Notification: Written notification will be submitted to NRC Uranium Recovery Branch Chief. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | WY | OTH | GEN |  |  |  |  | 0
36995 | 0 | U.S. AIR FORCE |  |  |  |  | 1998-11-01 | 2000-05-12 14:56 | 2000-05-12 | THE LICENSEE REPORTED POSSIBLE LOSS OF CHEMICAL AGENT MONITORS (CAM). THE LICENSEE WAS NOTIFIED AT 1030 ON 05/12/00 BY MAJ WISEMAN OF THE 3RD AMDS/SGPB AT ELMENDORF AFB, ALASKA, OF A RECENT INSPECTION SHOWING A DISCREPANCY IN DOCUMENTATION FOR THE TRANSFER OF EIGHT AUTOMATIC CHEMICAL AGENT ALARMS (CONTAINING 250 MICROCURIES EACH OF AMERICIUM-241) IN NOVEMBER, 1998. THE TRANSFER OF THESE EIGHT CHEMICAL AGENT DEVICES WAS TO KELLY AFB, TEXAS, WHERE THE RETURNED PAPERWORK STATED THAT ONLY FIVE DEVICES WERE RECEIVED. THE LICENSEE IS NOW TRYING TO DETERMINE IF ONLY FIVE DEVICES INSTEAD OF EIGHT WERE RECEIVED AND THE NUMBER 5 WAS A TYPOGRAPHICAL ERROR ON THE RECEIPT FORM. THE LICENSEE IS CONTINUING THE INVESTIGATION. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AK | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
36994 | 0 | JOHNSON CONTROLS |  |  |  |  | 2000-05-12 10:30 | 2000-05-12 10:30 | 2000-05-12 | IN-LINE STATIC DE-IONIZATION GUN MISSING. Johnson Controls leased an in-line static de-ionization gun from Amstat Industries on 04/0 9/99. While looking for the static de-ionization gun to return it to Amstat Industries, Johnson Controls discovered that the static de-ionization gun was missing. The in-line static de-ionization gun contains 10 millicuries of Polonium-210 (alpha emitter). Johnson Controls did not know when the in-line static de-ionization gun was last seen. The in-line static de-ionization gun, model number P2021-8101 was made by NRD, Grand Island, NY. The serial number of the source is 110700. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36993 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-11 10:55 | 2000-05-12 09:34 | 2000-05-12 | NRC BULLETIN 91-01, 24 HOUR NOTIFICATION INSTRUMENT USED TO DETERMINE URANIUM MASSES WAS FOUND TO BE IN ERROR IN THE NON-CONSERVATIVE DIRECTION. The calibration factor of an instrument used to determine uranium masses was discovered to be in error. This error was in the non-conservative direction (approximately 30% off) and resulted in the under reporting of uranium masses, violating NCSA GEN-010, Requirement 3.1.3. The purpose of this requirement is to ensure proper uncomplicated handling/planned expeditious handling (UH/PEH) classification to ensure safe handling of the item. SAFETY SIGNIFICANCE OF EVENTS: Both of the controls relied upon for double contingency are based on determination of a uranium mass. Both of these controls were lost; therefore, double contingency was not maintained. However, based on Non-Destructive Analysis recalculation of the measured values using the correct calibration factor, an unsafe mass of uranium was not involved. POTENTIAL CRITICALITY PATHWAYS INVOLVED OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, a critical mass of uranium would be needed to be accumulated in an unsafe geometry. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing two independent controls on mass. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Each item or group has been verified to be less than the always safe mass and enrichment could be as much as 100%, in the form of uranyl fluoride. The process limit of 400 grams is less than half of the worst case mass. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Double contingency for this scenario is established by implementing two controls on mass. Since the measurements were performed with an improperly calibrated instrument, the reported masses could not be relied upon and double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Access to the identified items is being controlled with ropes and postings until they can be retagged with the correct uranium masses. After the uranium mass has been corrected, the ropes and postings may be removed. The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36992 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-05-11 16:40 | 2000-05-11 16:41 | 2000-05-11 | THE LICENSEE IDENTIFIED A DEGRADED FIRE BARRIER BETWEEN THE 4160 C AND D VAULTS. The licensee identified the wall protecting the C & D 4160 vaults/rooms from each other as a 3 hour rated fire barrier. It has been determined that the wall as is does not meet the requirement for a 3 hour rating. Structural steel for the wall does not have the required thickness of "Pyrocrete 102" to provide a 3 hour rating. The wall is considered functional given the low fire loading in each room and the presence of automatic fire detection and manual suppression. They have commenced an hourly watch for the effected area. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36991 | 0 | WAYNE CTY ENG TESTING OFFICE |  |  |  |  | 2000-05-11 14:00 | 2000-05-11 15:00 | 2000-05-11 | WAYNE COUNTY ENGINEERING REPORTED DAMAGE TO CPN DENSITY GAUGE. THE GAUGE WAS BEING USED IN DETROIT, MI. AT A ROAD MAINTENANCE SITE WHEN IT WAS RUN OVER BY A CAR. THERE WAS NO MAJOR DAMAGE OR CRACKS TO THE DEVICE(CPN MODEL MC3-82 PORTABLE) WHICH CONTAINED 10 MILLICURIE OF CS-137 AND 50 MILLICURIE OF AMERICIUM-241/BERYLLIUM. NO LEAKAGE WAS DETECTED WHEN THEY MADE A SURVEY. THE DEVICE, WHICH HAD A SLIGHT DENT AND BENT ROD WAS PLACED BACK INTO ITS BOX AND WILL BE TAKEN TO THEIR FACILITY FOR STORAGE. THE MANUFACTURER WILL BE CONTACTED TOMORROW. WAYNE COUNTY ENGINEERING CONTACTED NRC REGION 3 (SIMMONS). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN |  |  |  |  | 0
36990 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-05-11 08:18 | 2000-05-11 12:27 | 2000-05-11 | THE PLANT HAD A REACTOR WATER CLEANUP ( RWCU) ISOLATION WHILE THEY WERE PLACING A DEMINERALIZER FILTER IN SERVICE. "While placing Reactor Water Cleanup Demin "B" in service following a precoat, received Division 2 isolation on sustained High Differential flow of 55 gpm for 45 seconds. The following valves received closed signals G33-F001, RWCU PUMPS INBD SUCTION VALVE, G33-F040, RWCU RETURN INBOARD ISOL. VALVE, G33-F053, RWCU PUMPS INBD DISCH VALVE, G33-F02, RWCU INBD DRAIN VAL. The Systems responded as designed with all valves closed and the Reactor Water Cleanup Pumps tripped. Note: G33-F028 RWCU INBD DRAIN VAL was already closed. "The isolation appears to be valid. The cause of the isolation appears to be that valves used to flush a strainer were not full closed, causing flow to the Backwash Receiving Tank where it was fully contained. The valves were locally visibly verified closed, but the valves were actually 1/2 open. Local position indications for both valves appeared to be defective. The plant is stable and plans for restoration of the RWCU system are in progress." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36989 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-05-11 01:00 | 2000-05-11 09:29 | 2000-05-11 | AN APPARENT LIGHTNING STRIKE CAUSED THE LOSS OF ALL EMERGENCY SIRENS. An apparent lightning strike caused the loss of all Emergency Sirens. Emergency Sirens were discovered inoperable at 0815 ET. Both repeaters for the Emergency Sirens were found inoperable. Emergency Sirens were returned to service at 0840 ET when one of the repeaters was restored to service. The licensee will inform state and local officials of the loss of their Emergency Sirens. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36988 | 0 | UNIVERSITY OF CONNECTICUTT |  |  |  |  | 2000-05-05 09:30 | 2000-05-10 11:56 | 2000-05-10 | POSSIBLE LOSS OF A TRITIATED EXIT SIGN During final walkthrough for renovation of the Waring Chemistry Building, one tritiated exit sign appears to be missing. Eleven signs were collected, but there appeared to be a "spot" on the wall at one exit where it appears a sign had hung. A search was conducted of the building without finding any indication of the sign. There is no inventory of the signs so there is no positive way of determining that a sign is actually missing. The sign would by a model 101 by Shield Source Incorporated if it matches the rest of the signs. The sign contained 7 curies of tritium on 1/93 and would contain about 5 curies now. The university plans to send out a flyer looking for the sign and provide warning of the hazards involved. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36987 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-05-09 20:39 | 2000-05-09 21:19 | 2000-05-10 | COMPENSATORY MEASURES TEMPORARILY SUSPENDED DUE TO INCLEMENT WEATHER. CONTACT THE OPERATIONS CENTER FOR ADDITIONAL DETAILS. * * * Updated on 5/10/00 to reflect correct reactor mode of cold shutdown vice hot shutdown * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0
36986 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-05-08 20:25 | 2000-05-08 20:56 | 2000-05-18 | OUTSIDE DESIGN BASIS - FOULING OF THE REACTOR BUILDING CLOSED COOLING WATER HEAT EXCHANGER (RBCCW HX). Surveillance testing has identified fouling of the Salt Service Water (SSW) side of the RBCCW HX. The extent of the fouling on one of the two heat exchangers would prevent design basis containment heat removal post-accident at maximum design basis ultimate heat sink (UHS) temperature (75°F). Engineering evaluation has determined that design basis heat removal can be achieved with UHS temperature less than 70°F. Periodic evaluation will be performed to ensure that additional fouling has not further degraded the heat exchangers heat transfer capability. The licensee will inform the NRC resident inspector. * * * RETRACTION 1653 5/18/2000 FROM ERIC OLSON TAKEN BY BOB STRANSKY * * * The licensee has determined that the unit was not operated outside of the design basis. At the time of the report, the seawater temperature was 50°F. Therefore, the licensee is retracting this notification in accordance with NUREG-1022, Section 3.2.4. The NRC resident inspector has been informed of this retraction by the licensee. Notified R1DO (Lew). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36985 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-05 21:30 | 2000-05-08 17:22 | 2000-05-08 | FAILURE OF A SAFETY SYSTEM (CELL 8) At 2130 CDT on 5/05/2000, the C-337 Unit 3 Cell 8 Freezer/Sublimer A-valve failed to open while in TSR mode F/S 3 which requires operability of the A-valve in order for the valve to open if required to do so upon actuation of the Freezer/Sublimer High-High Weight Trip System. An operator was attempting to place the Freezer/Sublimer into mode F/S 2 which does not require operability of the High-High Weight Trip System. The Freezer/Sublimer was unable to enter Mode F/S 2 due to inability to open A-valve because of mechanical failure. Actuation of High-High Weight Trip system did not occur. However, had it been required to do so while in mode F/S 3, there is potential that the A-valve would not have opened as required if actuation of system occurred. Upon discovery of valve failure, Freezer/Sublimer was placed in mode F/S 4 which does not require operability of the High-High Weight Trip system. The valve failure was caused by a failure of limit switch on the valve. The NRC Senior Resident Inspector has been notified of this event. See related event 36984. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0
36984 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-05 21:30 | 2000-05-08 17:22 | 2000-05-19 | SAFETY EQUIPMENT FAILURE (CELL 2) At 2130 CDT on 5/05/2000, the C-337 Unit 3 Cell 2 Freezer/Sublimer A-valve failed to open while in TSR mode F/S 3 which requires operability of the A-valve in order for the valve to open if required to do so upon actuation of the Freezer/Sublimer High-High Weight Trip System. An operator was attempting to place the Freezer/Sublimer into mode F/S 2 which does not require operability of the High-High Weight Trip System. The Freezer/Sublimer was unable to enter Mode F/S 2 due to inability to open A-valve because of mechanical failure. Actuation of High- High Weight Trip system did not occur. However, had it been required to do so while in mode F/S 3, there is potential that the A-valve would not have opened as required if actuation of system occurred. Upon discovery of valve failure, Freezer/Sublimer was placed in mode F/S 4 which does not require operability of the High-High Weight Trip system. The valve failure was caused by a failure of the motor operator in this six inch valve. The NRC Senior Resident Inspector has been notified of this event. See related event 36985. * * * RETRACTION 1718 5/19/2000 FROM MIKE UNDERWOOD TAKEN BY BOB STRANSKY * * * "On May 18, 2000, troubleshooting and functional testing of the F/S in the failed condition determined that the valve was opening in response to DPCS demands, but the limit switches were not correctly communicating the valve position to the DPCS. This caused the DPCS to indicate a mode equipment state failure on May 5, 2000. In addition the F/S was subjected to the high-high weight trip safety system functional test while in cold standby and with the system engineer visually monitoring the A-valve. The valve operated as designed, but due to the failed limit switches, the DPCS tripped the unit into hot standby, recreating the events of May 5, 2000. Thus, the A-valve was capable of performing its intended function if required, and the reporting requirements of 10CFR76.120(c) (2) were not met. "Based on this evaluation, this event has been retracted." The NRC resident inspector has been informed of this retraction. Notified R3DO (Madera). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0
36983 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-05-08 03:56 | 2000-05-08 05:25 | 2000-05-18 | POST-ACCIDENT SAMPLING SYSTEM ISOLATION DURING TAGOUT While performing a tagout on the 'A' train of the post-accident sampling system (PASS) H2/O2 sampling system, solenoid isolation valve SV-5065-20B, which is a 'B' train valve, closed unexpectedly. The licensee restored the 'A' train of PASS H2/O2 monitoring to service and closed the redundant solenoid isolation valve in the 'B' train. The licensee declared valve SV-5065-20B inoperable. After review of system electrical diagrams, the licensee determined that the closure of valve SV-5065-20B was appropriate, although its closure was not anticipated in the tagout procedure. The NRC resident inspector has been informed of this event by the licensee. * * * RETRACTION 1653 5/18/2000 FROM ERIC OLSON TAKEN BY BOB STRANSKY * * * The licensee is retracting this notification in accordance with NUREG-1022, Section 3.3.2, Paragraph 5. The licensee has determined that this event did not constitute an ESF actuation because only a portion of the system logic tripped. The NRC resident inspector has been informed of this retraction by the licensee. Notified R1DO (Lew). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36982 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-05-07 22:43 | 2000-05-08 01:37 | 2000-05-08 | REACTOR WATER CLEANUP ISOLATION DUE TO INADVERTENT STANDBY LIQUID CONTROL SIGNAL "On 5/7/00 at 2243 hours, a Reactor Water Cleanup System (RWCU) isolation occurred due to an inadvertent Standby Liquid Control System (SLC) initiation. At the time of the event, Hope Creek was in Operational Condition 5, Refueling, with core reload activities recently initiated and with all control rods fully inserted. SLC was not required to be operable and was removed from service (injection line check valves were closed) when the SLC initiation signal occurred. No sodium pentaborate was injected into the Reactor Coolant System. Preliminary investigation into the event determined that the SLC initiation signal resulted from activities supporting required surveillance testing of SLC along with surveillances of the Redundant Reactivity Control System (RRCS). The RRCS provides automatic SLC initiation. Although the RWCU isolation instrumentation was also not required to be operable at the time of the event, it was not removed from service. The RWCU isolation due to a SLC initiation signal is an ESF actuation. Both SLC pumps actuated as designed in response to the initiation signal, however, a crack was observed in a weld in the 'A' SLC injection line when the SLC pump was removed from service. Event investigation is continuing and repairs to SLC are being initiated. The RWCU isolation signal was reset and the RWCU was placed back in service. Core reload activities are continuing." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36981 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-05-08 00:15 | 2000-05-08 00:44 | 2000-05-08 | DIESEL GENERATOR STARTED DURING TESTING The 'A' emergency diesel generator (EDG ) automatically started due to a bus undervoltage signal that was inadvertently caused when a procedural step was misinterpreted. The EDG was secured. The licensee has informed the NRC resident inspector of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36980 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-05-07 11:25 | 2000-05-07 13:53 | 2000-05-23 | UNEXPECTED LOAD SHED OCCURRED DURING ELECTRICAL MAINTENANCE TESTING "On May 7, 2000 at 0933, electrical testing was being performed on the emergency diesel generator A load sequencer. The diesel generator was out-of-service at the time [for annual maintenance]. An unexpected load shed signal was developed, which removed charging pump C, service water pump A2, containment fan coil A, and residual heat removal (RHR) pump A from the train A emergency safeguards bus (Bus 5). In response to the load shed, equipment was manually restarted from the control room. RHR pump A was restarted in 90 seconds, restoring shutdown cooling. The cause of the load shed was the post modification testing of the load sequencer, and is continuing to be investigated." There was no increase in reactor coolant temperature during the 90 seconds without RHR flow. Also, the RHR B pump was available if it had been needed. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/23/00 @ 1216 BY HARRINGTON TO GOULD * * * RETRACTION After further review, appears this event is NOT reportable based upon the initiation signal was invalid and the system was properly removed from service. Also the Load Shed Signal is a component of the Diesel Generator engineered safety feature (ESF) and not the actuation of the ESF train. "NUREG 1022, "Event Reporting Guidelines: 10 CFR 50.72 and 50.73" Revision I (NUREG 1022) provides guidance on what the NRC wants the industry to report. Under section 3.3.2, "Actuation of an Engineered Safety Feature or the RPS" is a definition of "valid signals." Valid signals are those signals that are initiated in response to actual plant conditions or parameters satisfying the requirements for ESF initiation. The actual plant condition that actuates this ESF is an undervoltage condition on Bus 5, this did not occur therefore it was an invalid signal. "During the test for DCR 3002 initial conditions were in place to prevent the ESF from providing its intended feature. Preventive Maintenance Procedure (PMP) 42-14, "DGE-Train "A" Auto Sequencing Test with Diesel A in Pullout (Degraded Grid)" disables the ESF by placing the control switch (ES 46641) for Emergency Diesel Generator A in "PULLOUT." To start the test the control room operator places the Bus 5 Voltage Restoring Logic Test switch to the "TEST" position, this disables the rest of the ESF from actuating unless a valid signal is generated. "By looking at the actions required to mitigate the consequences of a significant event, the load shed is only one component of the safety feature. The shedding of loads from bus 5 does not, of itself, mitigate the consequences of any significant event. "In addition, during the test sequence the load shed relays are in a state which, if not blocked, would cause the same equipment to trip. This event occurred because the block was removed prior to the load shed relays resetting to their normal state. "Therefore, one component, Load Shed, of the Diesel Generator ESF actuated due to an invalid signal while the ESF was properly removed from service. Thus the event is not reportable." The NRC Resident Inspector was notified. Reg 3 RDO (Hiland) was informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36979 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2000-05-05 11:25 | 2000-05-07 13:45 | 2000-05-07 | POTENTIAL FOR RESIDUAL HEAT REMOVAL SYSTEM NOT ABLE TO PERFORM SAFETY FUNCTION "During the performance of the cold shutdown surveillance N1-ST-V 14 (SERVICE WATER CHECK VALVE AND EMERGENCY SERVICE WATER PUMP AND CHECK VALVE TEST) it was determined that ESW (EMERGENCY SERVICE WATER) check valves 72-21 and 72-22 failed to isolate. The failure of these valves to close may have resulted in ESW not being able to perform its safety function to support residual heat removal (RHR)." The two check valves serve to isolate the non-safety loads of ESW. The valves were serviced and the test was performed again successfully. It was on 5/7/00 about 1230 CDT that the licensee recognized that a four hour notification should have been made on 5/5/00. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
36978 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-05-07 07:57 | 2000-05-07 09:42 | 2000-05-07 | AUTOMATIC TURBINE/REACTOR TRIP DUE TO FAULT OF GENERATOR OUTPUT BREAKER "Unit 1 generator output breaker malfunction (G12) causing Unit 1 Reactor Trip and AFW pump actuation." A generator lockout occurred after the generator output breaker (G12) faulted. The generator lockout caused an automatic turbine trip/reactor trip. All control rods inserted completely following the trip. The unit is currently stable in Hot Standby with steam generators being fed by the auxiliary feedwater system and decay heat being removed by the main condenser. The licensee reported that smoke and flames were observed in the area of the G12 breaker. The site fire brigade responded, and the fire and smoke subsided within 10 minutes. The licensee plans to investigate the cause of the breaker fault and any necessary repairs. The NRC resident inspector will be informed of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36977 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-05-06 23:24 | 2000-05-07 03:01 | 2000-05-07 | AUTOMATIC REACTOR SCRAM SIGNAL WITH ALL CONTROL RODS INSERTED AND UNIT DEFUELED "At the time of the event, the Hope Creek reactor was in a preplanned outage with the core completely offloaded to the spent fuel pool, all control rods inserted, and the control rod drive hydraulic system isolated. "Outage work required isolating air to the scram discharge volume vent and drain valves which resulted in these valves being closed. Water inleakage was identified to the scram discharge volume. Since there was no drain path, water level continued to rise in the discharge volume until the high scram discharge volume level scram signal was reached. No components repositioned as a result of the scram signal since they were already in their fail safe positions as a result of preplanned outage work. "Based on the condition of the reactor, the control rod drive hydraulic system, and the reactor protection system at the time of the event, the validity of the ESF signal is being evaluated." The licensee will inform the NRC resident inspector of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36976 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2000-05-05 09:40 | 2000-05-05 12:40 | 2000-05-05 | REACTOR SCRAM DURING PLANNED INSTRUMENT MAINTENANCE "At 0940 hours on 5-5-00, Unit 2 scrammed while performing a scheduled Instrument Maintenance surveillance that resulted in a Group 1 isolation. The Unit 2 Emergency Diesel Generator received a spurious Auto Start signal during the Auxiliary Power transfer. During the transient reactor water level reached +8 inches and all Group 2 actuations occurred as expected. Unit 2 is now in Mode 3 with reactor water level within its normal band." All rods fully inserted with the reactor scram and the plant is now stable in normal plant configuration for Mode 3. Preliminary investigation determined that a technician valved out one instrument then tripped a different instrument causing the reactor scram. Investigation is still on going and startup will not proceed until complete. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36975 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-05-04 20:18 | 2000-05-04 22:09 | 2000-05-04 | DECREASING CONDENSER VACUUM REQUIRED MANUAL REACTOR SCRAM "During unit startup from D3F30 forced outage, condenser vacuum was reducing on 2 of 3 condenser hoods and condensate demin inlet temperatures were rising. The abnormal operating procedure for loss of condenser vacuum was entered and actions followed to scram at 135 °F condensate temp. All systems responded as designed with no abnormalities noted. Investigation into cause in progress." All rods fully inserted following the manual reactor scram. Group 2 and 3 isolations were received as expected on reduced reactor vessel level. The licensee intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36974 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2000-05-04 13:18 | 2000-05-04 19:02 | 2000-05-04 | REACTOR WATER CLEANUP SYSTEM AUTOMATICALLY ISOLATED The reactor water cleanup system (RWCU) isolated due to ESF signal "high flow isolation signal". Originally it was determined to be an invalid signal caused by a pressure pulse induced by human error. Additional information indicates that it cannot be proven that the isolation was not caused by system flow, therefore it has been determined that the event is reportable. The system isolated as designed and has been restored. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36973 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-05-04 14:41 | 2000-05-04 18:00 | 2000-05-04 | ABOUT 25 DEAD FISH DISCOVERED IN DISCHARGE CANAL "On May 4, 2000, at approximately 1441 hours, plant personnel discovered dead fish in the discharge canal. There were no plant events or occurrences that appear to be causally related. The fish numbered about 25, had an average length of about one foot and consisted of gizzard shad, not an endangered species. The water in the discharge canal is river water used for cooling plant equipment in both Indian Point 2 and 3 during plant operation. The fish could not have traveled through the plant to the discharge canal since the river water intake has screens to prevent this type of fish intrusion. "This event is reported, within 24 hours, pursuant to Non-radiological Environmental Technical Specification 4.1 as an unusual event, a fish kill. The cause is being evaluated." The licensee intends to notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
36972 | 0 | U.S. ARMY |  |  |  |  | 2000-05-04 | 2000-05-04 16:54 | 2000-05-04 | SOURCE SET LOST DURING SHIPPING Operations for US Army Communications Electronics Command at Fort Monmouth, New Jersey shipped, via FedEx, an Amersham large area alpha calibration source to US Army at Redstone Arsenal, Alabama on 3/15/2000. The calibration set (serial # LAAS-003) contains 3 sources (serial #'s ES-927, 928 and 929) with a total of about 18 microcuries of Pu-238. On 4/18/2000, Redstone Arsenal contacted US Army Communications Electronics Command in New Jersey to inquire about a leak test that was due on the calibration source, who in turn informed them that it had been shipped to them in March. A search was conducted at Redstone Arsenal without the calibration source set being found. FedEx was contacted and a search of the sort center in New Jersey, to which the shipment was traced, failed to locate the shipment. The US Army is reporting that the source set is missing, assumed lost or stolen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | AL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36971 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-05-04 13:24 | 2000-05-04 16:36 | 2000-05-04 | INADVERTENT SAFETY INJECTION ACTUATION "Harris Nuclear Plant was in Mode-5 with Reactor Vessel level at -12 inches following Mid-Loop operations. A Safety Injection Signal was actuated when Instrument Bus S-III was de-energized to return it to its normal power supply. Plant procedure MST-I0604 (Time Response Test for Channel 1 Pressurizer Pressure) was in progress. This procedure had channel 1 Pressurizer Pressure in test. When S-III was de-energized, the Low Pressurizer Pressure SI and Low Steam Generator Pressure SI Block signal (P-11) were unblocked due to Pressurizer channel III being de-energized concurrent with Pressurizer channel 1 in test. The plant was in Mode-5 with Pressurizer Pressure and Steam Generator Pressure at approximately 0 psig. Pressurizer Low Pressure SI and Low Steam Generator Pressure SI actuated the SI signal after P-11 was unblocked. Preparations to perform OST 1826 "Safety Injection: ESF Response Time, Train B 18 Month Interval test" were in progress. This test had the BIT injection valves closed with power off, which prevented ECCS discharge to the RCS. Other equipment operated as required in response to the Safety Injection Signal in these plant conditions. This actuation did not have any negative impact on RCS temperature or inventory control. The plant is currently stable in Mode-5." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36970 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2000-04-30 12:00 | 2000-05-04 09:45 | 2000-05-04 | 5000 SQUARE FOOT AREA CONTAMINATED WITH AN ESTIMATED 0.49 MILLICURIES OF PRIMARILY COBALT-60. On 05/01/2000, the licensee called to report a spill of residue inside their processing building. A 5000 square foot area was affected/contaminated with an estimated 0.49 millicuries of mixed fission/activation products (primary Co-60) when the event occurred on 04/30/00. Gross maslin smears revealed 30,000 dpm with a maximum small area smear of 6,600 dpm/100 square centimeter. There was no release of radioactive material to the environment. There were two minor personnel contamination incidents: one involving an individual's shoes and one involving an individual's hair. Both were easily decontaminated and released. There was no damage to equipment. Decontamination had already begun when reported. This event does not pose a risk to public health and safety but is reportable under 1200-2-5-141 (2)(c)1 i, ii, and iii. It required restricted access for greater than 24 hours, 0.49 millicuries is greater than 5 times the lowest ALI for Co-60, and access was restricted to allow isotopes with less than 24 half-lives to decay. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0
36969 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-03 08:00 | 2000-05-04 05:46 | 2000-05-04 | POTENTIAL FOR ACCUMULATION OF SLUDGE CONTAINING HEAVY METALS ON/IN THE LID OF TUB NRC BULLETIN 91-01 24 hour notification On 5/3/00 at 0800 hours it was discovered that a NCSA-0705_027.A003 control was not in place. The sludge tub used for accumulating heavy metal (including uranium) sludge had an unsafe/unfavorable geometry molded into the design. The unfavorable dimensions created by the raised lip is 7.75" by 37" by 2". This could have resulted in the potential accumulation, of an unsafe volume on the sludge tub lid had a leak developed In a nearby system containing uranium-bearing solution. NCSA-705_027.A003 requirement #17 states "Geometrically unfavorable containers shall not be left uncovered while unattended in the heavy metals precipitation process area or on the mezzanine in the area of the heavy metals precipitation raffinate storage (HMPRS)". This was a loss of one control (geometry/volume) in the double contingency principle for the afore mentioned NCSA. The second control (physical integrity of nearby uranium-bearing systems) was maintained throughout the event. At the direction of the Plant Shift Superintendent (PSS), the requirements for the NCS anomalous condition were initiated. At 1015 hours compliance was regained by covering the molded design SAFETY SIGNIFICANCE OF EVENTS: On May 3, 2000, it was discovered that the sludge tub used for accumulating sludge containing heavy metals (including uranium) contains an accumulation point on/in the lid. That accumulation point is created by a raised lip and has unfavorable geometric dimensions (7.75" by 37" by 2"). This is a violation of NCSA-0705_027 and NCSA-0705_076. This could have resulted in the potential accumulation of an unsafe volume of solution on/in the sludge tub lid had a leak developed in a nearby system which contain uranium-bearing solution. No uranium-bearing material was involved in the violation, since the remaining barrier to criticality (i.e., the physical integrity of nearby uranium-bearing systems) was maintained. Therefore, the safety significance of this event is low. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): If a leak had developed in a nearby uranium-bearing system such that the solution could have accumulated on/in the sludge tub lid, an unsafe geometry of solution could have resulted. If the leaking solution had contained a sufficient amount of uranium, the resulting configuration could have been sufficient for a criticality to occur. It should be noted that the allowed safe geometry and volume limits established In NCSA-0705_076 are based on potentially moderated, UO2F2 and water solution which contains uranium enriched to 100 wt%. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The parameter which was violated during this upset was the geometry of potential accumulation present in the sludge tub lid (i.e., the volume in which uranium-bearing solution could have accumulated in the event of a leak). The physical integrity of the nearby systems containing uranium-bearing material was maintained. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium bearing material was actually introduced into the lid of the sludge tub. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES NCSA-0705_076.A00 and NCSA-0705_027 take credit for the physical integrity of Systems which contain uranium-bearing material and that unsafe volume/geometry containers are either modified, covered, or oriented to prevent an unsafe configuration from resulting In the event of a leak. The lid of the sludge tub observed was not protected from a potential accumulation and it had been left unattended. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At 0800 hours, a NCS anomalous condition was initiated. At 1015 hours compliance was re-established The NRC Resident Inspector was notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36968 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-03 09:00 | 2000-05-03 23:39 | 2000-05-03 | MODERATION CONTROL LOST (NO FREE LIQUIDS) WHILE MASS CONTROL WAS MAINTAINED. NRC BULLETIN 91-01 24 HOUR NOTIFICATION On 05/03/2000 at 0954 hours a violation of a contingency control designated in NCSA-PLANT018.A02 was identified. During dry active waste (DAW) sorting operations a Chemical Operator discovered two plastic bags containing 3M cloth saturated and dripping with oil. This is in violation of NCSA-PLANT018.A02 requirement #1a, which states the following in regards to placing items in a DAW drum: "The items shall contain no free liquid (ie., not dripping or saturated with liquid)." This constituted the loss of one control of the double contingency principle. Moderation control was lost (no free liquids) while mass control (no visible uranium) was maintained. This condition was corrected under Nuclear Criticality Safety Engineering guidance when the material was removed from the DAW drum and handled per the applicable NCSA. SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is low. Two bags of 3M cloth contaminated with lube oil were found DAW drum during sorting operation. The NCSE evaluates a DAW material saturated with liquid. The drum of DAW material did not have any items in it that had visible amounts of uranium beyond fixed stains/films. Also NCSA-PLANT054.A03 has controls on lube oil and data used in the NCSE for this NCSA shows that the uranium concentration in lube oil (even lube oil spills) is less than 50ppm uranium-235. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): For criticality to occur with DAW material there would have to be visible uranium on the items placed in the DAW drum. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameters in this NCSA are moderation (no free liquids) and mass (no visible uranium). ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The highest enrichment for DAW material in the X-326 building is 100%. The form of the material in DAW is uranyl fluoride and uranyl tetrafluoride contamination. The amount of mass involved is less than 350 grams which is the safe mass value of 100% enriched uranyl tetrafluoride solution. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES The failure in this case is moderation. The NCSA requires that material that is saturated or dripping is to be disposed of in favorable geometry containers or under other specific NCSAs. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The oil saturated 3M cloth was transferred to an NCSA-PLANT054.A03 approved storage container, at which time compliance with NCSA-PLANT018.A02 was restored. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36967 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-05-03 22:15 | 2000-05-03 22:27 | 2000-05-04 | UNIT 2 TECH SPEC REQD SHUTDOWN DUE TO 2 CONTAINMENT PURGE VALVES FAILING THEIR LLRT- The licensee is shutting Unit 2 down from 100% power in accordance with Tech Spec 3.6.3.A, 12 Hour Shutdown LCO, due to containment purge valves #CPS*AOV-104 & 106 failing their local leak rate test #N2-ISP-CPS-Q001. The licensee notified the NRC Resident Inspector. * * *UPDATE ON 05/04/00 AT 0002 ET BY M. ERON TAKEN BY MACKINNON * * * Licensee exited Technical Specification 3.6.3.A at 2350 ET after manual Containment Purge Supply valve, 2CPS-V6, an upstream valve to #CPS*AOV-104 & 106 was leak tested and verified closed. Lowest reactor power level reached was 92%. R1DO (Della Greca) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36966 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2000-05-03 11:00 | 2000-05-03 16:59 | 2000-05-03 | AGREEMENT STATE REPORT- Missing Indium-111 capsules at Mayo Clinic/Medical Center, Scottsdale, AZ On 05/01/00, a standing order of three capsules, each capsule containing 100 microcuries of Indium-111, was misplaced at the Mayo Clinic/Medical Center, Scottsdale, AZ (AZ License #07-448). The missing capsules have not been located as of 1100 MST on 05/03/00, as reported to the Arizona Radiation Regulatory Agency (ARRA) by the AZ licensee's Radiation Safety Officer (RSO). The RSO is planning an investigation into the events leading to the loss and will file a report with the ARRA within 30 days. This isotope has a half-life of 67 hours. The ARRA has notified NRC Region 4, Mexico, and the states of Colorado, Nevada, Utah, New Mexico and California of this event (ARRA First Notice #00-4). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | PAR |  |  |  |  | 0
36965 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-03 12:38 | 2000-05-03 16:50 | 2000-05-03 | 4 HOUR NRC BULLETIN 91-01 REPORT - LOSS OF 1 OF 2 CONTINGENCY CONTROLS - Annual visual inspections of the cylinder wall, valve, and plug which are credited for double contingency in Nuclear Criticality Safety Evaluation (NCSE) 1493-03 have not been performed for fissile 12A (MD-type) UF6 cylinders stored in Room 144 of Building C-710. Scenario 8 of NCSE 1493-03 takes credit for the annual visual inspections required by Nuclear Criticality Safety Approval (NCSA) GEN-03 to ensure cylinder integrity is maintained. However, NCSA GEN-03 states that the inspections are required for cylinders in "cylinder storage yards". Because the cylinders are not located In the cylinder storage yards, the annual inspections were not performed for the fissile 12A MD cylinders. SAFETY SIGNIFICANCE OF EVENT: One of the controls relied upon for double contingency was not implemented. However, based on followup visual inspections, the process parameter. moderation, was not lost, POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR]: In order for a criticality to be possible, the cylinder would have to be breached and large quantities of water would have to be introduced. Upon discovery of the problem, the cylinder was inspected and determined to be acceptable. Because the cylinder was not breached, a criticality resulting from this event is not possible. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): Double contingency for this scenario Is established by Implementing two Independent controls on moderation. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): 419 pounds in the form of UF6 at an enrichment of 4.46 wt % U-235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on moderation control by prohibiting the use of water or steam to heat the fissile 12A MD cylinders. This control prevents the entry of large quantities of water into the cylinders. This control was not violated and the first leg of double contingency was maintained, The second leg of double contingency relies on a second control on moderation by crediting an annual cylinder inspection to identify corrosion and cylinder damage in order to maintain the integrity of the cylinders and prevent the introduction of moderating material. The annual cylinder inspections were credited but not performed. Therefore, double contingency was not maintained. One of the two controls on moderation credited for double contingency was not implemented, therefore double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The NCSE/A will be revised to include annual visual inspection of fissile 12A MD cylinders. The NRC resident inspector has been notified of this event. PGDP Problem Report No. ATRC-00-2499; PGDP Event Report No. PAD-2000-037 Responsible Division: Production Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36964 | 0 | GEOTECH ENVIRONMENTAL, INC |  |  |  |  | 2000-05-03 08:00 | 2000-05-03 15:24 | 2000-06-02 | STOLEN TROXLER MOISTURE DENSITY GAUGE On April 27, 2000, a technician was involved in an automobile accident in Philadelphia, PA. At that time, the gauge was stored in the trunk of the vehicle. When police arrived on the scene, the technician was arrested. The technician informed the police that the gauge was in the trunk and showed the gauge to the police officers. After the technician was arrested, the vehicle was stolen. The vehicle was recovered on April 29, 2000. The gauge was not in the trunk when the vehicle was recovered. The device contained 8 mCi of Cs-137 and 40 mCi of Am-241. * * * UPDATE AT 1402 ON 06/02/00 BY CLAIRE PANICO TO JOLLIFFE * * * The stolen Troxler moisture density gauge was found in a waste management recycling facility in Philadelphia. The undamaged gauge has been returned to Geotech Environmental, Inc. George Pangburn, NRC Region 1 has been notified. NRC Region 1 issued PNO-I-00-013A. The NRC Operations Officer Notified R1DO Dick Barkley and NMSS EO Brian Smith. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
36963 | 0 | WA DEPT OF RADIATION PROTECTION |  |  |  |  | 2000-05-02 | 2000-05-03 14:40 | 2000-05-03 | AGREEMENT STATE REPORT - POTENTIAL SKIN OVEREXPOSURE A worker was extracting a small amount of Holmium 166 from a vial containing 400 millicuries per milliliter of solution. As the syringe needle was extracted from the vial septum, small droplets were sprayed into the worker's face. Initial estimate was 0.5 microcuries of contamination on forehead, cheeks and lips. The worker was wearing safetyglasses. The worker was decontaminated on site and residual contamination was noted on forehead and right cheek (0.6 millirem per hour), lips (0.3 millirem per hour), and left cheek (0.08 millirem per hour) . Possible internal contamination was indicated by nasal and saliva samples. Worker was sent to the University of Washington Nuclear Medicine department for further assessment. An on-site investigation by the state Department of Health, Division of Radiation Protection will be conducted. Washington State incident number WA-00-016. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
36962 | 0 | VETERANS AFFAIRS |  |  |  |  | 2000-05-03 10:00 | 2000-05-03 14:06 | 2000-05-03 | RECEIPT OF A PACKAGE WITH SURFACE CONTAMINATION GREATER THAN LIMIT On May 3, 2000, at approximately 10:00 am, a box of radiopharmaceuticals containing approximately 68 mCi of Technetium-99m Sestamibi from Birmingham Central Pharmacy was received. A nuclear medicine technologist performed the procedure for incoming packages which included a wipe and survey of the box. The meter survey did not indicate any contamination, however, the wipe of the outside of the box indicated contamination of about 178 dpm/cm2. The package was emptied and surveyed again. A contaminated spot on the outside of the box was located by the meter survey. Rewipe of the area indicated 606 dpm/cm2 which exceeds the regulatory limit of 22 dpm/cm2. According to a spectrum made of the contaminated wipe sample, the radionuclide is Technetium-99m. The contamination was in an area on the side of the box away from the carrier handle. The pharmacy has been contacted. The Pharmacy wipe test data arriving with the package did not indicate contamination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | [10 empty] | NON EMERGENCY | 2 | AL | HOS | [5 empty] | 0
36961 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-05-03 10:45 | 2000-05-03 12:40 | 2000-05-16 | 1 HOUR SECURITY REPORT Unescorted protected area access granted inappropriately. Immediate compensatory measures taken. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Center for additional details * * * RETRACTION ON 05/16/00 AT 1128 ET BY BRAIN KOPETSKI TAKEN BY MACKINNON * * * After further review of this event and conversations with NRC Region 3 this event is being retracted. The event is being made a loggable because the person's access denial would not have in itself been enough to deny access. R3DO (John Madera) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) |  |  |  | 0
36960 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-05-03 08:25 | 2000-05-03 12:20 | 2000-05-03 | OUTSIDE DESIGN BASIS This notification is for San Onofre Units 2 and 3 and is being made in accordance with 10CFR5072(b)(1)(ii)(B) for the condition of the Salt Water Cooling (SWC) System and the Shutdown Cooling System potentially being outside their design basis. This condition exists for both Units 2 and 3. The SWC system consists of two separate, 100% capacity safety related cooling water trains for each unit. Each train consists of two 100% capacity pumps. The pumps aligned to the critical CCW loops are automatically started upon receipt of a safety injection actuation signal and all essential valves are aligned to their post accident positions. Although not specifically stated, the accident analyses for Unit's 2 and 3 assumes that once these valves have been placed in their safety-related positions that they would remain in that position until intentionally realigned by plant personnel. Recently, the licensee discovered that the air/trip valves for pneumatic actuators for the saltwater cooling pump discharge valves were leaking a small amount of air and questioned whether this could cause these valves to be inoperable under postulated accident conditions. The pneumatic actuators receive their air supply from the non-safety-related instrument air system, which would not be available following a Loss of Offsite Power (LOOP) event. The actuator vender indicated that under such conditions, the accumulators for the actuators would gradually loose pressure and would not forcibly hold these valves in their safety related positions. The licensee recognized that hydrodynamic forces inside the pipes could cause these valves to close. Because these valves do not have manual hand wheels and it may take some time for operators to diagnose this condition, restore instrument air, and reopen the valves, the licensee declared the valves inoperable until corrective actions were implemented. The valves were blocked open to ensure they will remain in their safety-related positions during postulated accident conditions. A similar condition exists for the pneumatic actuator for the component cooling water outlet valves for the shutdown cooling heat exchangers. The licensee restored operability to these valves by engaging manual hand wheels which lock the valves open due to increased closing drag. The Resident Inspector will be notified. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36959 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-05-03 09:46 | 2000-05-03 11:31 | 2000-05-03 | REACTOR SCRAM AND ESF ACTUATION Unit 3 auto scrammed from 100 percent power at 0946 CDT on 5/3/00. Reactor protection power supplies (120VAC) were being transferred at the time of the reactor scram. All rods fully inserted into the core. The exact cause of the scram is unknown at this time. Licensee investigation into the cause of the scram continues. All systems responded as expected. A Group 2 and Group 3 isolation signal also was received during the scram as expected. The unit is stable at hot shutdown conditions. The NRC resident inspector has been notified.- | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36958 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-05-02 07:40 | 2000-05-02 17:10 | 2000-05-23 | - 'A' TRAIN EMERGENCY SAFEGUARDS BUS UNEXPECTEDLY DEENERGIZED DURING MAINTENANCE - At 0740 CDT on 05/02/00, while electrical bus maintenance was in progress, the 'A' train emergency safeguards bus unexpectedly deenergized. DEENERGIZING the bus initiated an ESF start signal for the associated 'A' emergency diesel generator (EDG). At the time, the 'A' EDG had been removed from service for refueling outage scheduled maintenance and no EDG start occurred. In response to the loss of power to the 'A' train safeguards bus, the licensee manually started the 'B' train residual heat removal pump to reestablish decay heat removal There was no temperature rise in the primary system. The licensee is determining the cause of the bus deenergization. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/23/00 @ 1216 BY HARRINGTON TO GOULD * * * RETRACTION "For the event that occurred on May 2, 2000, there was no actual ESF equipment (pumps, valves, etc.) actuated directly as a consequence of the event. Therefore, no ESF equipment operated to mitigate the event. As such, the event would not be reportable. However, there are implications that the reporting requirements apply equally to ESF signals that are generated as part of an event, regardless of whether the event caused equipment to operate or not. For instance, NUREG-1022 contains a paragraph that states, in part, that, " [t]he Statement of Considerations also indicates that "actuation" of multichannel ESF actuation systems is defined as actuation of enough channels to complete the actuation logic." Accordingly, the May 2 event was evaluated in greater detail considering that the loss of power to the bus in itself could be understood to be an ESF actuation. "At the time of the event, work on the emergency bus relays was in process. During the work the bus was unexpectedly de-energized when the breaker providing power to the bus from the off-site power source opened. From our investigation, it appears a relay which was not being directly worked on actuated. Since power was removed from the relay, the relay appears to have been bumped or jarred which manually actuated it. The relay that was actuated was a trip relay for the breakers providing power to the affected bus. "The ESF function that could be interpreted to be actuated as a result of the relay being actuated is the loss of power to the safeguards bus start signal to the associated diesel. However, the diesel was tagged out of service and the bus voltage restoring control circuit was defeated as part of the bus work that was in progress. "In order to defeat the voltage restoring circuit the bus voltage restoring control switch was placed in "manual," and the voltage restoring relays were de-energized. With the switch in manual, a voltage search signal is not generated. As a result, the diesel does not receive a start signal if a loss of power to the bus occurs. Additionally, as part of the voltage restoring circuit, once power is lost to the bus, a power search is initiated whereby the circuit electrically seeks an available off-site power source and then would seek the diesel if no off-site source were available. With the bus voltage restoring circuit in manual there was no power source search initiated. The bus power was not automatically restored, even though the power to the bus was available. "Included in NUREG-1022 are a number of examples of situations where NRC has described reportable events. Of those that are described, all either involved equipment (pumps, valves, etc.) that actuated or the condition that generated a signal needed the ESF function to mitigate the event whether equipment actuated or not. In the event reported on May 2, no equipment operated and there was no reliance on any accident mitigation function as well as no need for any accident mitigation feature. Therefore, the event should not have been reported as an ESF actuation simply because the condition that occurred could have resulted in an ESF signal being actuated. "According to the reporting criteria, if the actuation is invalid, and the system was properly removed from service a report need not be filed. According to NUREG-1022, "[v]alid ESF actuations are those that result from "valid signals" or from intentional manual initiation, unless it is part of a preplanned test. Valid signals are those signals that are initiated in response to actual plant conditions or parameters satisfying the requirements for ESF initiation. Note this definition of "valid" requires that the initiation signal must be an ESF signal. This distinction eliminates actuations which are the result of non-ESF signals from the class of valid actuations. Invalid actuations are, by definition, those that do not meet the criteria for being valid. Thus invalid actuations include actuations that are not the result of valid signals and are not intentional manual actuations." "The ESF signal of concern for the start of the diesel generator is that which is generated in response to a loss of off-site power to the affected bus. During the subject event, off-site power was not lost. Although the off-site power was not automatically restored according to normal system operational design, it remained available. Consequently, there was no need for the diesel to supply the bus and as such no valid signal was generated. Additionally, the power restoration circuit was properly removed from service during the event; the voltage restoring switch was in manual. Therefore, no ESF signal was generated. "In summary, the event described is not reportable based on 1) there not being a need for any ESF feature to mitigate the event, and 2) the event not causing a valid (or any) ESF signal along with the related ESF equipment being properly removed from service." The NRC Resident Inspector was notified. Reg 3 RDO (Hiland) was informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36957 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2000-05-02 15:56 | 2000-05-02 16:59 | 2000-05-02 | - OFFSITE EMERGENCY NOTIFICATION SIRENS OUT OF SERVICE LONGER THAN ONE HOUR - At about 0534 on 05/02/00, the emergency phone batteries were being removed from service for planned maintenance. During the removal, the backup power supply malfunctioned. This condition required the backup power supply to be isolated. Subsequent evaluation of the as-found condition determined that the loss of normal and backup power supplies resulted in the loss of the emergency notification siren initiation capability. Upon discovery of the loss of initiation capability at about 1100, power was immediately restored using a temporary power cord. Since the siren system was out of service for longer than one hour, the licensee determined this event to be reportable to the NRC in accordance with 10CFR50.72(b)(1)(v) at 1556. The licensee plans to notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36956 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-05-02 14:00 | 2000-05-02 15:12 | 2000-05-02 | - CABLES FOR PZR PORVs & PORV BLOCK VALVES NOT SEPARATED IAW APPENDIX R EXEMPTIONS - With Unit 2 in a refueling outage, the licensee discovered during an engineering evaluation, that cabling in the Unit 2 containment for the pressurizer power operated relief valves (PORVs) and opposite train PORV block valves are not separated in accordance with the requirements of existing Appendix R exemptions. Part of the bases for the existing Appendix R exemption for containment is that redundant equipment, except pressurizer level transmitters, is separated by a minimum of 20 feet. The PORV and block valve pairs are redundant equipment for Appendix R Safe Shutdown. Field measurements indicate that cable in the open tray associated with the A-Train PORV is separated from B-Train block valve cable by 13 feet and cable in the open tray associated with the B-Train PORV is separated from A-Train block valve cable by 18 feet. These cable routing deficiencies have been evaluated and found to represent a degraded but operable condition, although at this point in the outage, the equipment is not required to be operable. This issue has been identified as Prairie Island Condition Report (CR) #20000832. An action for engineering to evaluate this issue for possible solutions has been assigned as part of CR #20000832. The licensee plans to resolve this condition prior to restarting Unit 2. The licensee plans to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36955 | 0 | R. M. WESTER & ASSOCIATES |  |  |  |  | 2000-05-02 09:00 | 2000-05-02 13:45 | 2000-05-02 | - SMASHED 80 MICROCURIE Am-241 SOURCE DISCOVERED IN A SCRAP METAL YARD IN ST LOUIS, MO - At 0900 CDT on 05/01/00, an employee at the Phillips Scrap Metal Yard, St Louis, MO, discovered two 80 microcurie Am-241 sources inside a scrap industrial air conditioning unit. One source was smashed and the other source was intact. The employee cordoned off the area and called Joe Koch, R. M. Wester & Associates, St Louis, MO, a radiation safety consulting firm possessing a general NRC license. Mr Koch responded to the scrap yard, about 34 miles away. Mr Koch leak tested the damaged source and measured 45.87 DPM (0.3 mR/hr on contact). Mr Koch packaged the sources and took possession of them and plans to send them to the manufacturer, Pyrotronics, Ceder Knolls, NJ. Phillips personnel are determining the previous owners of the air conditioning units. No persons were contaminated from these sources. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | MATL IN UNCNTRL AREA | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0
36954 | 0 | MONTANA DEPT OF TRANSPORTATION |  |  |  |  | 2000-05-01 12:02 | 2000-05-02 12:32 | 2000-05-02 | DAMAGED TROXLER MOISTURE DENSITY GAUGE Montana Dept of Transportation reported a damaged Troxler moisture density gauge containing 8 mCi Cs-137 and 41 mCi Am- 241. The gauge fell out of the back of a truck and was retrieved. The gauge case was cracked but the source was intact. The area was surveyed and a wipe test was performed with no leakage detected. The licensee presently plans to repair the damaged gauge case. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 4 | MT | OTH | GEN |  |  |  |  | 0
36953 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-05-02 07:00 | 2000-05-02 10:59 | 2000-05-08 | DEFECTIVE STEAM GENERATOR TUBES Analysis of "B" steam generator eddy current results determined that more than 1% of the Westinghouse HEJ sleeve laser weld repaired tubes were classified as defective placing the "B" steam generator in the C-3 classification per the Kewaunee Technical Specifications. Two tubes of 59 inspected contained indications in the weld repaired region. There are 288 total tubes in this population. The licensee plans to increase the population size to 100%. The NRC Resident inspector has been notified. * * * UPDATE ON 05/09/00 AT 1153ET BY TOM WEBB TAKEN BY MACKINNON * * * Analysis of "A" steam generator eddy current results determined that more than 1% of the tubes inspected in the hot leg tube sheet crevice region are classified as defective, placing steam generator "A" in the C3 category per Kewaunee Nuclear Power Plant Technical Specification. Fifteen tubes out of 833 inspected were characterized as defective. No scope expansion is necessary as 100% of the tubes for the hot leg tubesheet crevice region have been inspected. Corrective Action: 1. Plug or repair defective tubes prior to returning to operation. 2. Ensure plugging rate does not result in an unanalyzed condition. NRC R3DO (Brent Clayton) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36952 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-01 14:58 | 2000-05-02 08:58 | 2000-05-02 | 24 HOUR NRC BULLETIN 91-01 REPORT "At 1458, on 5/1/00, The Plant Shift Superintendent (PSS) was notified that the C-360 building drain configuration was found to deviate from the assumptions of Nuclear Criticality Safety Evaluation (NCSE) 3972-11. The NCSE credits the flow of water cut of the building drains during a fissile material release to be precluded from backing up and washing large quantities of uranium into the elevator and scale pits. Contrary to this assumption, a valve in the drain system closes automatically, as part of the building containment system in response to the release. This allows water supplied to an Instrument cooler to accumulate in the basement and potentially wash uranium into unfavorable geometry pits. "SAFETY SIGNIFICANCE OF EVENTS: "The conductivity cell drain system is not configured as credited for double contingency. No release has occurred and the operation has been shutdown to preclude further fissile materiel operations pending resolution of this issue. The design of the drain system as credited for double contingency is in error. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "In order for a criticality to be possible, a large release or multiple small releases, resulting In an unsafe mass of fissile material, would have to occur. "Additionally upon building containment, this material would have to be washed in sufficient quantity and concentration into an unfavorable geometry pit. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.: "Double contingency for this scenario is established by implementing mass and geometry controls. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): "There has been no release of UF6. No licensed material Is present in the unfavorable geometry pits. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The first leg of double contingency relies on system integrity to ensure that a large release or multiple concurrent small releases of fissile material are unlikely. This control was not violated and the first leg of double contingency was maintained. "The second leg of double contingency Is based on precluding the transport and accumulation of large quantities of uranium into the 0.360 scale and elevator pits, This control Is Implemented through reliance on the design of the drain system. Credit is taken for the sanitary water draining directly to the elevator pit instead of backing up on the basement floor which prevents large amounts of uranium from washing into the unfavorable geometry pits. Contrary to this assumption sanitary water from the autoclave conductivity cell will overflow tile normal drain lines and flow directly to the basement floor following building containment. Therefore, the condition required to assure safe geometry was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "Cylinder sampling and transfer operations in C-360 have been discontinued until deficiencies are corrected." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36951 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-01 10:34 | 2000-05-02 03:20 | 2000-05-02 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING NUMEROUS NUCLEAR CRITICALITY SAFETY ANALYSIS (NCSA) VIOLATIONS IDENTIFIED IN X-705 BUILDING WALKDOWN "On 4/28/00, a manager reported (PR-PTS-00-02234) a potential adverse trend with inadvertent containers (NCSA-705_076.A00) in the X-705 Building. All fissile material operations were suspended in the X-705 operation area pending assessment of PR-PTS-00-02234. "In response to PR-PTS-00-02234, a systematic walk down was performed 5/1/00 for the presence of inadvertent containers in the X-705 Building. At 1034 hours the first NCSA-705_076.A00 violation was identified. Further violations were identified throughout the day for a total of seventeen (17). All were immediately corrected with Nuclear Criticality Safety (NCS) engineer guidance. These violations could have resulted in the potential accumulation of an unsafe volume of solution had a leak developed with nearby uranium bearing systems. "Twelve (12) violations were with NCSA-705_076.A00 requirement #2 which states, 'inadvertent containers (with internal diameters greater than 5 inches) shall be controlled such that any uranium-bearing liquid that could be collected is geometrically favorable.' Some examples of these violations are: 1. Several drums had deep lids (>1.5") such that solution could accumulate in the lipped area. 2. A tray (>1.5") had no drainage holes. 3. A drain pan (>1.5") had a plugged drainage hole. 4. A section of ventilation duct was bowed inward which could allow solution collection (>1.5"). "This was a loss of one control (volume/geometry) in the double contingency principle for each violation. The second control (physical Integrity of nearby uranium bearing system) was maintained throughout this event. "One (1) violation was with NCSA-705_076.A00 requirement #3 which states, 'Flexible materials (such as plastic sheeting) shall be configured or secured such that they can not be deformed into an inadvertent container.' A rack contained several bagged items. The bagged items were oriented such that an unsafe volume could accumulate if a leak developed. This is a loss of one control (volume/geometry) in the double contingency principle. The second control (physical integrity of nearby uranium bearing system) was maintained throughout this event. "Four (4) violations were with NCSA-705_076.A00 requirement #4 which states in part, 'Absorbent materials shall be covered so that they cannot absorb uranium bearing liquids or modified such that any uranium bearing liquid could be collected is geometrically favorable.' Cheese cloth rolls and mop heads were located near areas if a leak developed could absorb solution containing uranium. This was a loss of one control (volume/geometry) in the double contingency principle for each violation. The second control (physical integrity of nearby uranium bearing system) was maintained throughout this event. No uranium bearing material was involved in any of the violations. "The safety significance of this event is low. "SAFETY SIGNIFICANCE OF EVENTS: "All of the identified problems involved the loss of geometry or volume of the inadvertent container. No uranium bearing material was involved in any of the identified problems since the remaining barrier to criticality (the physical integrity of nearby uranium bearing systems) was maintained. Therefore, the safety significance of this event is low. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "If a large leak developed in a nearby uranium bearing system, the identified inadvertent containers could have accumulated an unsafe volume/geometry of material. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.); "The parameters controlled were geometry, volume and the physical integrity of nearby uranium bearing systems. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "No uranium bearing material was involved with these problems. The nearby uranium bearing systems had various concentrations. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The inadvertent containers identified were not configured, oriented, or modified to preclude an unsafe volume/geometry from accumulating. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "Fissile material operations in the affected area have been suspended pending further investigation and subsequent corrective actions." The described violations are representative of the items identified. The investigation is ongoing. Operations informed the NRC Resident Inspector and DOE Site Representative. * * * UPDATE AT 2238 ON 05/02/00 TO PR-PTS-00-A2288 BY KURT SISLER TO JOLLIFFE * * * On 05/2/00, five additional violations of NCSA-0705_076.A00 requirements were identified while completing the X-705 facility Nuclear Criticality Safety walkdowns. All fissile operations in the X-705 facility are still suspended pending assessment and resolution of discrepancies identified during the walkdowns. All five discrepancies were corrected at the time of initial discovery. Four violations were with NCSA-0705_076.A00 requirement #2 as stated above. The violations consisted of situations in which equipment or material was oriented such that it could accumulate uranium-bearing solution or liquid in a geometrically unfavorable configuration. This constituted the loss of one control of the double control contingency (geometry/volume). The second control (physical integrity of the nearby uranium bearing systems) was maintained throughout this event. One of the violations was with NCSA-0705_076.A00 requirement #4 as stated above. A large string mop was discovered to not be controlled as required in the NCSA. This also constituted the loss of one control (geometry/volume) of the double contingency principle. The second control (physical integrity of nearby uranium-bearing systems) was maintained throughout this event. The NRC Resident Inspector and the Site DOE Representative were notified of this update. The NRC Operations Officer notified the R3DO Bruce Burgess and NMSS EO Josie Piccone (by fax). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36950 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-05-01 17:30 | 2000-05-01 22:06 | 2000-05-01 | - OFFSITE AGENCIES NOTIFIED OF FREON GAS RELEASE TO THE ATMOSPHERE FROM UNIT 3 - The licensee notified the California Office of Emergency Services, San Diego Department of Environmental Health and San Diego Air Pollution Control District that approximately 3000 pounds of freon gas had escaped into the atmosphere from a failed relief valve on a Unit 3 air conditioner (chiller). The licensee plans to notify the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36949 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-05-01 13:40 | 2000-05-01 17:34 | 2000-05-01 | NRC BULLETIN 91-01 CRITICALITY CONTROL, 4 HOUR REPORT - At 1340 on 05/01/00, it was discovered that an NCSA-0705-076.A00 control was not in place. Insulation on non-uranium bearing pipes in the vicinity of uranium bearing solution piping and systems was not sealed. The insulation could accumulate uranium bearing solution in an unfavorable geometry in the event the integrity of the nearby uranium bearing solution lines was to be lost. Geometry control specified in NCSA-0705-076.A00 was not maintained in reference to the piping insulation. The control cannot be restored within a 4 hour time frame and is therefore being submitted as a 4 hour reportable event. Operations/solution processing in the area has been secured. All fissile material operations are suspended in the X-705 operation area pending corrective actions. The loss of this control resulted in a condition in which only one control of the double control contingency was maintained. SAFETY SIGNIFICANCE OF EVENT: The insulation in use covers non-uranium bearing lines (water & steam). In addition, the insulation forms an annulus, which does not have complete cross section as compared to a cylinder. None of the nearby systems experienced a leak which could have resulted in solution entering the absorbent material. Therefore, the safety significance of this event is low. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR]: If a large leak developed in a nearby uranium-bearing system, the absorbent insulation could have accumulated a large amount of material in an unsafe geometry. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): The controlled parameters were geometry and the physical integrity of the nearby uranium-bearing systems. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium-bearing material was involved with this situation. Some of the areas which involved the insulation handles highly concentrated solutions. The high-bay area currently has a uranium-bearing concentration of 69 ppm U based on prior sampling reports. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The absorbent material was not covered or modified such that the geometry was favorable. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Fissile material operations in the affected area have been suspended pending further investigation and subsequent corrective actions. The NRC Resident Inspector and the Site DOE Representative have been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36948 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-05-01 15:20 | 2000-05-01 16:47 | 2000-05-01 | - SAFEGUARDS EXHAUST VENTILATION SYSTEM UNABLE TO FULFILL ITS SAFETY FUNCTION - While reviewing the test results of the newly revised safeguards exhaust ventilation (SEV) System discharge damper seismic air flask leakage surveillance test [1(2)-PT-77.12A(B)], the licensee determined that the test results indicate that the SEV System was in a condition that alone could have prevented the system from fulfilling its safety function. The seismic air flask equipment and damper degradations, coupled with a loss of instrument air during a loss of coolant accident, could have prevented the control of leakage of radioactive material from safeguards equipment, as well as cooling for the recirculation spray and low head safety injection pumps located in the safeguards building (residual heat removal capability). Currently, the systems have been repaired and are fully operable. JCO #00-01 has been prepared and implemented to provide additional guidance on appropriate operator actions to restore air to the seismic air flasks to assure continued system operation. The new test techniques and requirements were the result of an ongoing in-depth licensee engineering review of the North Anna plant ventilation systems. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | POT UNCNTRL RAD REL |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(C) |  |  | 0
36947 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-05-01 03:07 | 2000-05-01 06:55 | 2000-05-01 | UNIT 1 EXPERIENCED AN AUTOMATIC REACTOR SCRAM DUE TO A TURBINE TRIP/GENERATOR LOCKOUT ON ELECTRICAL FAULT "At 0307, Unit 1 Reactor automatically shutdown from 92% power. The shutdown was the result of a Turbine Trip/Generator Lockout caused by an electrical fault on the '1C' Main Transformer. All Rods fully inserted (RPS), and the plant is in Hot Shutdown (opcon 3). Level is currently at normal operating level. The following isolations were received; Main Steam and Rx Sample (1B), Reactor Water Clean-Up (3), Primary Containment Purge Supply and Exhaust (6a), Primary Containment Exhaust to REECE (6b), Drywell Sump, Suppression Pool Cleanup, and Tips (8b), and Reactor Enclosure HVAC. The isolations were received due to a NSSSS 'Reactor Level 2 - Low Low' signal during the event. All plant systems operated as designed. The cause of this event is currently being investigated by plant staff." Unit 1 will remain in Opcon 3 pending the results of the investigation. No SRVs cycled during the transient. Offsite power and EDGs are available. The extent of repairs to the main transformer has not been determined. A preliminary inspection shows a bus bar connection missing. The licensee informed state/local authorities and the NRC Resident Inspector. | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36946 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-04-30 10:00 | 2000-04-30 10:58 | 2000-05-02 | 24-HOUR CONDITION OF LICENSE REPORT INVOLVING FAILURE TO POST REQUIRED FIRE WATCH DURING MAINTENANCE DUE TO PERSONNEL ERROR. "ON 4/28/2000 AT APPROXIMATELY 1000EDT, A REACTOR BUILDING 23 FOOT ELEVATION FLOOR PLUG WAS REMOVED. AN HOURLY FIRE WATCH WAS NOT ESTABLISHED AS REQUIRED BY THE OYSTER CREEK FIRE PROTECTION PROGRAM TECHNICAL SPECIFICATIONS. THE HOURLY FIRE WATCH WAS ESTABLISHED ON 4/30/2000 AT 0900EDT WHEN THE CONDITION WAS REALIZED." THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. * * * UPDATE 1040EDT ON 5/2/00 FROM DAVID PIETRUSKI TO S. SANDIN * * * THE LICENSEE IS RETRACTING THIS REPORT BASED ON THE FOLLOWING: "Management review has determined that this event is not reportable and is retracting this notification. A. single missed fire tour is not an indication of a programmatic failure, therefore, it does nor meet the threshold for reporting." THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. NOTIFIED R1DO(DELLA GRECA). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0
36945 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-04-29 22:34 | 2000-04-29 23:38 | 2000-05-19 | UNEXPECTED ISOLATION OF CONTAINMENT PURGE A containment purge valve closed due to a loss of power to a radiation monitor. The licensee stated that the cause was deenergization of the power panel per procedures for that radiation monitor. Apparently, this was the first time this procedure had been performed since it had been revised, and there was no caution in the procedure indicating that if a purge is in effect, it would be secured. The licensee plans to change the procedures to reflect the possibility of isolation so that it can be isolated before the radiation monitor is deenergized. The licensee notified the NRC resident inspector as well as state and local authorities. * * * RETRACTION 1336 5/19/2000 FROM MYER TAKEN BY STRANSKY * * * "On 4/29/00 a Containment Purge Valve Isolation signal (CPVIS) was generated due to a loss of power to a radiation monitor. The CPVIS automatically closed the Containment Purge system supply and exhaust valves. This condition was conservatively reported as an event that resulted in an automatic actuation of an Engineered Safety Feature (ESF). "Subsequent investigation determined that the Containment Gaseous Radiation Monitor, RM-8123B, had been properly removed from service at 0801 on April 28, 2000 in accordance [with] the applicable Operating Procedure. The actuation signal from RM-8123B was the direct result of a planned loss of power to VA-30 and was not the result of a valid high radiation condition with the Containment. Therefore, the actuation signal was invalid. "The actuation only involved the automatic closure of the supply and exhaust valves within the Containment Purge system. The Containment Purge system is equivalent to 'Reactor Building Ventilation System' as defined in IEEE Std 805-1984. Therefore, the Containment Purge system is equivalent to 'Reactor Building Ventilation System' identified in 10CFR50.72(b)(2)(ii). "Section 10CFR50.72(b)(2)(ii) states that the licensee shall report any event or condition that resulted in a manual or automatic actuation of an Engineered Safety Feature (ESF) including the Reactor Protection System (RPS), except when: "(B) The actuation was invalid and " (1) Occurred while the system was properly removed from service (or), " (2) Occurred after the safety function had been already completed or " (3) Involved only the following specific ESFs or their equivalent systems iii Reactor Building Ventilation system. "Since the actuation was invalid and since the event occurred after the applicable sensor had been properly removed from service in accordance with approved plant procedures and the actuation involved only the Containment Purge system, a system which can be shown to be equivalent to the Engineered Safety Feature provided by the Reactor Building Ventilation system, this event is not reportable pursuant to either 10CFR50.72(b)(2)(ii)(B) or 10CFR50.73(a)(2)(iv)(B) and the Immediate Notification for this condition is retracted." The NRC resident inspector has been informed of this retraction. Notified R1DO (Lew). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36944 | -1 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-04-29 09:45 | 2000-04-29 12:48 | 2000-05-17 | DETERMINATION THAT DUAL INDICATION ON FEEDWATER CONTAINMENT ISOLATION VALVES (WHILE IN THE CLOSED POSITION) MAY RESULT IN THEM BEING DEGRADED The following text is a portion of a facsimile received from the licensee: "While shutting down [the] Unit 2 reactor for a refueling shutdown, leakage past the main feedwater control valves required shutting the feedwater containment isolation (CI) valves to [the] 21 and 22 steam generators (S/G) [in order] to maintain S/G level. With the CI valves in the closed position, the limit switch that provides a white status light on the containment isolation panel indicated the valves to be closed. The other limit [switches] that [provide] a red (open) and green (closed) indication for both valves were both on dual indication. S/G levels were controlled with the CI valves close. The dual indication on the CI valves while in the closed position may result in them being degraded. Containment integrity isolations per operation procedures [were] implemented. Further engineering evaluations and repairs will follow." The licensee stated that a unit cooldown was in progress as part of a refueling outage which began shortly prior to midnight. (Refer to event #36942 for additional information.) The licensee plans to notify the NRC resident inspector. * * * RETRACTED AT 1530 EDT ON 5/17/00 BY ELLISON TO FANGIE JONES * * * "Event Notification #36944 on April 29, 2000 documented a situation during unit cooldown where dual indication (both open and closed positions) on both feedwater containment isolation valves brought into doubt the actual position of the valves and their ability to perform their design bases functions. Further evaluation of the actual positions of the valves, their ability to stop flow, and their design bases functions led to the conclusion that the valves did meet the required functions at the time and were capable of meeting all design bases required functions. Therefore, Event Notification #36944 is being withdrawn." The licensee will notify the NRC Resident Inspector. The Headquarters Operations Officer notified the R3DO (John Madera). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36943 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-04-28 09:51 | 2000-04-29 05:19 | 2000-04-29 | 24 HOUR 91-01 BULLETIN - LOSS OF ONE CONTINGENCY On 4/28/00 at 0951 hours, X-705 Chemical Operation personnel discovered an NCSA-705_076.A00 noncompliance when a 55-gallon burnable waste drum was left unattended in the X-705 high-bay with it's lid ajar. This could have resulted in the potential accumulation of an unsafe volume of solution in the drum had a leak developed in the overhead storage system which contains uranium-bearing solution. This was a loss of one control(volume) in the double contingency control matrix for the aforementioned NCSA. The second control (physical integrity of the storage system) was maintained throughout this event. SAFETY SIGNIFICANCE OF EVENTS: The safety significance or this event is low because the only credible nearby source of uranium-bearing solution is that contained in the overhead storage, which is inspected on a monthly basis for evidence of leaks. Also, the solution contained in the overhead storage is typically low in uranium concentration. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): If a leak had developed in the overhead storage system such that the solution could have accumulated in the uncovered drum, an unsafe volume or solution could have accumulated, if the leaking solution had contained a sufficient amount of uranium, the resulting configuration could have been sufficient for a criticality to occur. It should be noted that the allowed safe geometry and volume limits established in NCSA-705_076 are based on optimally moderated, UO2F2, and water solution which contains uranium enriched to 100 wt% CONTROLLED PARAMETERS (MASS, MODERATION. GEOMETRY, CONCENTRATION, ETC.): The parameter which was violated during this upset was the volume of potential accumulation present in the uncovered 55-gallon drum (i.e.. the volume in which uranium-bearing solution could have accumulated in the event of a leak). The physical integrity of the system containing the uranium-bearing material was maintained. ESTIMATED AMOUNT, ENRICHMENT. FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium-bearing material was actually introduced into the uncovered drum. However, the overhead storage system does routinely contain uranium-bearing solutions of various enrichment and concentration (typically less than 500 ppm uranium concentration and less than 10 wt% enrichment, although these parameters are not controlled as NCS requirements). Data from the latest sampling of solution at first stage microfiltration (which originates from the overhead storage) indicates a maximum of 80 ppm uranium, although it should be noted that this may not be indicative of the solution concentration currently contained in the overhead storage. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: NCSA-0705_076.A00 takes credit for the physical integrity of systems which contain uranium-bearing material and that unsafe volume/geometry containers are either modified, covered, or oriented to prevent an unsafe configuration from resulting in the event of a leak. The 55-gallon drum observed in the X-705 high-bay was not protected from a potential accumulation since the cover had been dislodged and left unattended. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At 0951 hours, a NCS anomalous condition was initiated. At 1029 hours compliance was re-established. The NRC Resident Inspector and the DOE Representative were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36942 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-04-28 22:40 | 2000-04-29 00:47 | 2000-04-29 | PLANT HAD A REACTOR TRIP FROM 21.6% POWER DURING SHUTDOWN FOLLOWING A TURBINE TRIP THE UNIT 2 REACTOR TRIPPED DURING A POWER DECREASE FOR A REFUELING OUTAGE. THE SUSPECTED CAUSE IS A SPIKE ON THE 23B FEEDWATER HEATER INSTRUMENTATION GIVING A HI-HI LEVEL SIGNAL WHICH RESULTED IN A TURBINE TRIP/REACTOR TRIP. PLANT HAD LETDOWN ISOLATION, BUT THE AUX. FEEDWATER PUMPS DID NOT AUTOSTART AND WERE NOT REQUIRED TO START BASED ON THE STEAM GENERATOR LEVELS. ALL CONTROL RODS FULLY INSERTED, NO ECCS ACTUATED AND NO SAFETY RELIEF VALVES LIFTED. THEY ARE CONTINUING THE INVESTIGATION. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. | 0 | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36941 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-04-28 16:30 | 2000-04-28 18:06 | 2000-04-28 | ISOLATION OF THE CONTROL BUILDING VENTILATION SYSTEM TO THE RECIRCULATION MODE (CHLORINE MODE) The following text is a portion of a facsimile received from the licensee: "EVENT: On 04/28/00 at 1630, the control building ventilation system isolated to the recirculation mode (chlorine mode). Maintenance [personnel] had completed pressure testing the repairs that had been completed on the number 3 chlorinator with nitrogen and were venting the chlorinator. Residual chlorine with the nitrogen that was vented from the chlorinator caused the isolation. The chlorination system was isolated and under clearance in support of the scheduled maintenance activities during the event." "INITIAL SAFETY SIGNIFICANCE EVALUATION: Minimal - The control building ventilation system responded per design." "CORRECTIVE ACTION(S): The control room operators verified [that] all automatic actions occurred. Local chlorine levels were verified to be less than minimum detectable using portable chlorine monitors. Maintenance completed venting the number 3 chlorinator with no subsequent detection of chlorine. Control room ventilation was restored to the normal alignment." The licensee stated that this issue placed both units in a 12-hour to Hot Shutdown limiting condition for operation (LCO) because the control room emergency ventilation (CREV) system emergency ventilation fans are inoperable (will not operate) during the chlorine mode. The LCO has since been exited, and there was no reduction in power for either unit. The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION | TECH SPEC LCO A/S |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36940 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2000-04-27 15:30 | 2000-04-28 13:44 | 2000-04-28 | URANIUM SOLUTION MINE SHALLOW MONITOR WELL PLACED INTO EXCURSION STATUS - Crow Butte Resources shallow monitor well #SM-723 in uranium solution mine unit #7 in Crawford, NE, was placed into excursion status due to the sulfates concentration of water sample measuring at 82 PPM (upper control limit is 62 PPM). This was caused by nearby drilling activities. The well is located within the licensee controlled area. The nearest active mining well is 800 feet away. There are no public land use areas nearby. The licensee determined that there is no adverse impact or risk to people, livestock, or wildlife. The NRC Uranium Mining Expert concurred with this assessment. The licensee plans to sample the well more frequently than weekly and submit a written report to the NRC within 7 days. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 4 | NE | OTH | GEN |  |  |  |  | 0
36939 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-04-28 12:15 | 2000-04-28 13:19 | 2000-04-28 | DISCOVERY THAT A SHUTDOWN COOLING (SDC) ISOLATION VALVE WAS NOT DISABLED AS REQUIRED BY APPENDIX R FOR MODES 1, 2, AND 3 The following text is a portion of a facsimile received from the licensee: "On [04/22/00], while shutting down in Mode 3 for a planned refueling outage, it was discovered that a SDC isolation valve, 2-SI-651, was not disabled as required by the facility [Appendix] R compliance report for Modes 1, 2, and 3. Upon review and investigation of this deficiency, it was determined on April 28, 2000, that this condition could have resulted in an inability to achieve and maintain safe shutdown if a design basis fire-induced hot short of this valve had occurred." "The [Appendix] R report credits disabling this valve to ensure that a fire-induced hot short would not result in the valve damaging itself such that it could not be opened, as needed to initiate shutdown cooling. Additionally, there have been no Appendix R events during this timeframe." "A design modification was made in early 1999 (during the MP2 recovery outage) which changed the location of the coils which are removed in Modes 1, 2, and 3 to ensure the valve is disabled. When the modification was implemented, adequate guidance was not given in applicable facility procedures to ensure that the correct coils would be removed. This resulted in the valve not being disabled during the previous operating cycle." The licensee notified the NRC resident inspector as well as applicable state and local agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36938 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-04-27 10:30 | 2000-04-28 08:10 | 2000-04-28 | 24-HOUR NRC 91-01 BULLETIN REPORT INVOLVING LOSS OF ONE OF TWO CONTINGENCY CONTROLS "At 1030 hrs April 27, 2000, Chemical Operations personnel while performing decontamination operations on three forklifts in the high bay discovered slits in the seat cushion. Since these cushions are geometrically unfavorable, this was a loss of one control (geometrically) of the double contingency program for NCSA-0705__076.A00 'INADVERTENT CONTAINERS,' the second control, physical integrity of overhead piping, was maintained throughout. "At the direction of the PSS the requirements for an NCS anomalous condition were initiated. At 1130 hrs compliance was regained by repairing the seats. "1) Safety Significance of Events: "The safety significance of this event is very low. The seat cushions had dimensions of approximately 18 x 19 x 5 [inches] which is over 7 gallons of volume. The seats were damaged such that leakage of solution could readily absorb into the padding in an unfavorable geometry and the forklifts were parked directly under the overhead storage system. Although the overhead storage system can contain high concentrations of uranium at high enrichments, the current status is 69 ppm uranium. (Although enrichment is not measured, it is likely <10 wt% U-235. "2) Potential Criticality Pathways Involved (Brief scenario(s) of how criticality could occur): "If the overhead storage system contained sufficiently concentrated (>11,000 ppm U-235) uranium and if the solution leaked out of the overhead storage piping and landed on the forklift seat, the solution could achieve a critical configuration due to the volume of the cushion (>7 gallons) and the depth of the cushion (>1.5 inches). "3) Controlled Parameters (Mass, Moderation, Geometry, Concentration, Etc.): "Controlled parameters include geometry and the design of the overhead storage piping to protect against a large, uncontrolled leak. "4) Estimated Amount. Enrichment Form of Licensed Material (include process limit and % worst case of critical mass): "No uranium was involved in this event. The overhead storage system, however, can contain fully enriched uranium bearing solution at concentrations above minimum critical at volumes up to 6000 gallons. Current status of the overhead storage system is 69 ppm uranium and, although enrichment is not measured, it is likely <10 wt% U-235. "5) Nuclear Criticality Safety Control(s) or control system(s) and description of failures or deficiencies: "Nuclear criticality safety controls include geometry of the fissile material processing equipment in X-705, the design of those systems to contain the material and the prohibition against inadvertent containers in the high bay. The forklift seats have holes which can allow for the collection of solution in an unfavorable geometry." Operations staff informed the NRC Resident Inspector and the site DOE Representative. ***** UPDATE RECEIVED AT 1423 ON 04/28/00 FROM KURT SISLER TO LEIGH TROCINE ***** This update was given to provide a clarification to the initial event report. There was only one fork lift involved that did not meet the NCSA requirement. The following text is a portion of a facsimile received from the Portsmouth personnel: "On 04/27/00 at 1030 hours, X-705 Chemical Operation personnel discovered an NCSA-705_076A00 noncompliance while decontaminating three forklifts in the X-705 high bay area. One forklift seat cushion had a slit/crack failing to meet NCSA-705 076.A00 requirement #4 which states, 'Absorbent materials shall be covered so that they cannot absorb uranium-bearing liquids or modified such that any uranium-bearing liquid could be collected is geometrically favorable. Absorbent materials, which are controlled by covering, shall be elevated at least one inch so that they cannot absorb spilled uranium-bearing liquids. This requirement includes absorbent materials within containers having openings within one inch of the bottom of the container.' Since the forklift seat cushion is geometrically unfavorable, a loss of one control (geometry) occurred with the double contingency principle. The second control, physical integrity of the overhead piping, was maintained throughout the event." "At the direction of the Plant Shift Superintendent (PSS), the requirements for a NCS anomalous condition were initiated. At 1130 hours, compliance was regained by repairing the seat." "The safety significance of this event is low. The seat cushion had dimensions of approximately 18" x 19" x 5" which is over 7 gallons of volume. The seat was damaged such that leakage of solution could readily absorb into the padding in an unfavorable geometry, and the forklift was parked directly under the overhead storage system. The overhead storage system contained 69 ppm uranium during the event. Although the enrichment was not measured, it is likely less than 10 wt% uranium-235." "SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this report is very low. Only one seat cushion had unfavorable dimensions of approximately 18" x 19" x 5" which is over 7 gallons of volume. The seat was damaged such that leakage of solution could readily absorb into the padding in an unfavorable geometry, and the forklift was parked directly under the overhead storage system. Although the overhead storage system can contain high concentrations of uranium at high enrichments the current status is 69 ppm uranium. (Although enrichment is not measured, it is likely <10 wt% 235U)." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): If the overhead storage system contained sufficiently concentrated (>11,000 ppm 235U) uranium and if the solution leaked out of the overhead storage piping and landed on the forklift seat, the solution could achieve a critical configuration due to the volume of the cushion (>7 gallons) and the depth of the cushion (>1.5")." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Controlled parameters include geometry and the design of the overhead storage piping to protect against a large uncontrolled leak." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL. (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): No uranium was involved in this event. The overhead storage system, however, can contain fully enriched uranium-bearing solution at concentrations above minimum critical at volumes up to 6,000 gallons. Current status of the overhead storage system is 69 ppm uranium, and although enrichment is not measured, it is likely <10 wt% 235U." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM (S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Nuclear criticality safety controls include geometry of the fissile material processing equipment in the X-705, the design of those systems to contain the material, and the prohibition against inadvertent containers in the high bay. A forklift seat had holes which can allow for the collection of solution in an unfavorable geometry." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At 1030 hours, a NCS anomalous condition was initiated. At 1130 hours, compliance was re-established by repairing the forklift seat." Portsmouth personnel notified the NRC resident inspector. The NRC operations officer notified the R3DO (Shear) and NMSS EO (Moore). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36937 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2000-04-27 16:05 | 2000-04-27 17:03 | 2000-04-27 | LOSS OF POWER TO THE TECHNICAL SUPPORT CENTER At 1505 on 04/27/00, power was lost to the Peach Bottom Technical Support Center (TSC) as a result of breaker malfunctions during planned electrical switching. As of 1605, power had been out for greater than 1 hour constituting a loss of emergency assessment capability at the TSC. Assessment capability remains in the main control room and the Emergency Operations Facilities, and communication is still in tact between the control room and the TSC. Troubleshooting and restoration activities by maintenance and operations personnel are currently in progress, and this condition does not affect either of the operating plants. The licensee stated that power to the TSC was lost when two breakers failed to operate during performance of activities to restore power to a normal lineup following maintenance work on lines that do not normally affect the TSC. (However, when this particular lineup change is made, it realigns the power going to the TSC.) When the two breakers failed to operate, power at the TSC was lost. The licensee stated that the loss of power affected the TSC only and that no other systems of facilities were affected. The licensee plans to notify the NRC resident inspector. ***** UPDATE AT 1729 ON 04/27/00 FROM JIM KOVALCHICK TO LEIGH TROCINE ***** Power was restored to the TSC at 1710 on 04/27/00. The licensee notified the NRC resident inspector. The NRC operations center notified the R1DO (Noggle). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36936 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-04-27 10:50 | 2000-04-27 14:42 | 2000-04-27 | - STATE DEC AND U.S. COAST GUARD NOTIFIED OF SMALL OIL DISCHARGE INTO LAKE ONTARIO - The licensee notified the New York State Department of Environmental Conservation (DEC), the U.S. Coast Guard, and the NRC Resident Inspector that approximately two ounces of oil had discharged from the plant storm drains into Lake Ontario. The oil has dispersed. The cause is unknown and being investigated by the licensee. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36935 | 0 | NRC REGION 1 OFFICE |  |  |  |  | 2000-04-27 | 2000-04-27 13:48 | 2000-04-27 | DAVID BLACKMORE & ASSOCIATES REPORT TO NRC REGION 1 REGARDING A CRUSHED SOIL DENSITY GAUGE IN POTTSTOWN, PENNSYLVANIA At 1345 on 04/27/00, Joe Hughes (the radiation safety officer at David Blackmore & Associates) notified the NRC Region 1 office that a soil density gauge was crushed at a construction site in Pottstown, Pennsylvania, near Porter Road. Mr. Hughes was informed of the event and was en route to the job site at the time of this notification to the NRC Region 1 office. Mr. Hughes called the NRC Region 1 Office to ask advice and was not aware of the event specifics. The NRC Region 1 office (Noggle) subsequently notified the NRC operations center. The R1DO (James Noggle) stated that the NRC Office of Nuclear Materials Safety and Safeguards (George Pangburn and Judith Joustra) had been informed. (Call the NRC operations office for licensee contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0
36934 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 1998-05-23 06:13 | 2000-04-27 12:45 | 2000-04-27 | HISTORICAL REPORT OF THE DISCOVERY OF A FAULT CONDITION ON THREE MODULES ON THE 'X' CRITICALITY ACCIDENT ALARM SYSTEM CLUSTER DURING 1998 (24-HOUR REPORT) The following text is a portion of a facsimile received from Paducah: "At 0613 [CDT] on 05/23/98, the PSS was informed of a trouble alarm on C-337 Criticality Accident Alarm System (CAAS) 'X' cluster. Investigation of trouble alarm revealed that all three modules on [the] 'X' CAAS cluster were in a 'Fault' condition. The cluster was reset, and the Fault condition cleared. This condition was not reported as an event in which equipment required by the [Technical Safety Requirement (TSR)] is disabled or fails to function as designed as required by 10 CFR 76.120(c)(2). This event was found during the investigation of Notification Worksheet No. 36880, which occurred on 04/12/00. [The] 'X' CAAS cluster was in this 'Fault' condition from 0613 [CDT] until 0722 [CDT on 05/23/98]. During this time, an area in the Southeast corner of C-337, which contains a [Department of Energy (DOE)] Material Storage Area (DMSA) that holds 55-gallon drums of potentially fissile material, was without operable CAAS coverage." "This event should have been reported under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed." This issue was determined to be reportable yesterday afternoon. Paducah personnel notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
36933 | 0 | OFFICE OF EMERGENCY PREPAREDNESS |  |  |  |  | 2000-04-06 12:00 | 2000-04-26 16:16 | 2000-04-26 | TWO CHEMICAL AGENT MONITORS EACH CONTAINING 15 MILLICURIES OF NICKEL-63 MISSING DURING SHIPMENT FROM WINSTON-SALEM, NC TO BALTIMORE, MD VIA FEDEX On March 29, 2000, two Chemical Agent Monitors, APD-2000, each containing 15 mCi of Nickel-63 were shipped by FEDEX from Winston-Salem, North Carolina to Environmental Technology Group, Baltimore, Maryland to be wiped tested. On April 06, 2000, U.S. Public Health Service was notified that the two Chemical Agent Monitors were missing. The U.S. Public Health Service and FEDEX are unable to located the missing monitors using the FEDEX tracking number. FEDEX is still trying to locate the missing monitors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | NC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
36932 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-04-26 13:42 | 2000-04-26 16:01 | 2000-05-01 | AUXILIARY BUILDING SPECIAL VENTILATION AND CONTROL ROOM POST ACCIDENT RECIRCULATION ACTUATED DUE TO A STEAM EXCLUSION SIGNAL. At 1342 CDT on 04/26/00, the Auxiliary Building Special Ventilation and Control Room Post Accident Recirculation Systems actuated due to a steam exclusion signal. Auxiliary Building Special Ventilation and Control Room Post Accident Recirculation are Engineered Safety Features Systems. The steam exclusion signal was due to the rupture disk on Boric Acid Recovery System rupturing. Steam to the Boric Acid Recovery System was isolated. At 1425 CDT, steam exclusion was reset and the Auxiliary Building Special Ventilation and Control Room Post Accident Recirculation Systems were shutdown. All equipment operated as designed. There was no radiological release. The licensee is currently investigating why the rupture disc ruptured. Nobody was injured. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 1009EDT ON 5/1/00 FROM GARY HARRINGTON TO S. SANDIN * * * The licensee is retracting this report based on the following: "After reviewing NUREG-1022, we have identified that the steam exclusion system and the initiating signal that caused the ESF actuations is a non-valid signal. Consequently, since the signal is not valid and the ventilation systems that were affected [special ventilation system and control room post accident recirc] are those which are excluded from reporting on inadvertent actuations, we are retracting this report." The licensee informed the NRC Resident Inspector. Notified R3DO(Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36931 | 0 | DRESSER EQUIPMENT GROUP |  |  |  |  | 2000-04-25 14:00 | 2000-04-26 14:40 | 2000-06-16 | DRESSER VALVES NAME PLATE AND CODE PLATE HAVE INCORRECT SET PRESSURE INFORMATION AT HATCH. PART 21 FROM DRESSER EQUIPMENT GROUP, DRESSER VALVE DIVISION, BURLINGTON, ONTARIO, CANADA. The following noncompliance has been determined to be reportable within the requirements of 10CFR Part 21. The noncompliance involves seven safety relief valves that were purchased for the Hatch Electric Generating Plant by the Georgia Power Company through its agent, Southern Nuclear Operating Company, Inc. The valves are for use in a safely related service. The valves were purchased on Southern Nuclear Operating Company purchase order #6040304 and produced on Dresser Valve Division sales order #119588N and are further described as follows: Contract Item 002 Quantity 7 Part Number 3990C-1-S4-MS-33-SC-SC-GS produced ASME Section III Class 2 valves with the following serial numbers and required set pressures: SERIAL NO. SET PRESSURE REQD B119588-2-1 250 psig B119588-2-2 250 psig B119588-2-3 250 psig B119588-2-4 250 psig B119588-2-5 250 psig B119588-3-1 170 psig B119588-3-2 170 psig NONCOMPLIANCE SITUATION AND BRIEF HISTORY On Tuesday April 25, 2000, the customer was performing receiving inspection and noticed that the set pressure information on the Code Plates and the Name Plates do not conform to the specification requirements or the history docket testing information. The customer called the Quality Assurance Department of Dresser Valve Division to discuss the finding. It appears that the set pressure information on the plates has been interchanged. A summary of the information is as follows: SERIAL NO SET PRESSURE REQD CODE PLATE NAME PLATE B119588-2-1 250 psig 170 psig 170 psig B119588-2-2 250 psig 170 psig 170 psig B119588-2-3 250 psig 170 psig 170 psig B119588-2-4 250 psig 170 psig 170 psig B119588-2-5 250 psig 170 psig 170 psig B119588-3-1 170 psig 250 psig 250 psig B119588-3-2 170 psig 250 psig 250 psig Our investigation has begun and we have conducted a full review of our records to confirm that the valves are set correctly to the contract requirements. A notice has been given to the customer to return the affected valves to Dresser Valve Division for confirmation of the plate information and correction if required. The ANI will be involved in the investigation and corrective actions as required. We have conducted a full review of our records and confirmed that these are the only valves involved. A full review of our procedures regarding plate preparation, inspection and installation will be completed. Corrective actions will be initiated to address the internal issues, if warranted, and details will be provided in our closure reports at the completion of our investigation into the cause of this situation. * * * UPDATE 1415EDT ON 6/16/00 FROM WINFIELD TO S. SANDIN * * * The following information was received via fax: "This is a summary of the event dealing with the cause and the corrective actions implemented to prevent recurrence. "The customer returned the valves and the set pressures were confirmed to be correct to the General Arrangement Drawing (GA Dwg) requirements. New nameplates were produced, verified to the approved GA Dwg., and installed on the valves as witnessed by the ANI. "It was confirmed that the incorrect nameplate information was derived from internal work order data. The approved GA Dwg was not used as required. "Revised internal operating procedures are being implemented to ensure that engineering personnel complete nameplate forms, from data appearing only on the approved GA Dwg. Only the approved GA Dwg will be used to verify the correctness of the data." Notified R2DO(Bernhard) and NRR(Hodge). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 21.21 |  |  |  | 0
36930 | -1 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-04-25 23:42 | 2000-04-26 03:23 | 2000-04-28 | VARIOUS ESF ACTUATIONS DUE TO RPS BUS 3B DEENERGIZING AS A RESULT OF A FAILED RELAY "At 2342 CDT on 04/25/00, the RPS bus 3B deenergized causing PCIS Group 2 and Group 6 isolation valves to automatically close. A burnt relay was the initiating condition. Group 2 outboard drywell equipment drain valve and drywell floor drain valve closed. Group 6 drywell radiation monitor isolation valves closed. All other expected group isolations occurred along with the automatic starts of SBGT and CREV Systems. "Unit 3 is in Mode 5 with primary containment integrity not required. "This event is reportable under criteria 10CFR50.72(b)(2)(ii) : Any event or condition that results in manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS)." RPS bus 3B was reenergized from its alternate power supply. Electricians are currently troubleshooting the cause of the failed relay. There was no electrical maintenance or testing ongoing at the time of the relay failure. The licensee informed the NRC Resident Inspector. ***** UPDATE AT 1424 ON 04/28/00 FROM RAYMOND SWAFFORD TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "TVA is retracting this event report. TVA has reviewed the plant conditions and system alignments existing at the time of this event and has concluded that the actuation signal was invalid. Primary Containment was not required at the time of the event. The PCIS systems were either properly removed from service, were already in their ESF positions at the time of the event, or were a part of excepted systems from reporting according to NUREG-1022, Revision 1. Likewise, the control room emergency ventilation system and standby gas treatment system are excepted systems, and the actuations observed during the event are not reportable since the actuation signal was invalid. Therefore, this event is not reportable pursuant to 10 CFR 50.72(b)(2)(ii)." The licensee notified the NRC resident inspector. The NRC operations officer notified the R2DO (Fredrickson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36929 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2000-04-25 15:45 | 2000-04-25 16:21 | 2000-04-25 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE. HPCI inverter failure alarm was received at 1545ET. An operator checked the power breakers to the inverter and found them closed. The inverter reset itself at 1551 ET. HPCI was declared inoperable and a 14 day limiting condition of operation was entered per Technical Specification 3.5. Licensee investigating HPCI inverter problem. All other Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable. The NRC Resident Inspector was notified of the event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36928 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-04-25 15:00 | 2000-04-25 15:22 | 2000-04-25 | OFFSITE NOTIFICATION MADE TO THE STATE OF FLORIDA CONCERNING LOW LEVEL FIXED SURFACE CONTAMINATION FOUND ON SCAFFOLDING EQUIPMENT RECEIVED FROM A VENDOR. While performing a routine survey, Turkey Point Health Physics personnel discovered low levels of radioactivity on several pieces of scaffolding knuckles and elbows received from a vendor. The knuckles never entered the site's radiologically controlled area. These items were counted in a Small Article Monitor (SAM) and indicated low level contamination was present. In total 12 out of approximately 3,000 items surveyed indicated the presence of low level fixed activity. The highest level measured was 15,833 disintegration's per minute (DPM) when counted on the SAM and 125 net (above background) counts per minute using a standard HP-210 probe. Isotopic analysis indicates Cobalt-60 and Cesium-137. No loose surface contamination was found. The items identified with low level fixed contamination are now being held inside the Turkey Point radiologically controlled area. The NRC Resident Inspector was notified of this event notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36927 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-04-25 11:02 | 2000-04-25 13:59 | 2000-04-25 | REACTOR CORE ISOLATION COOLING (RCIC) STEAM FLOW INSTRUMENTS DECLARED INOPERABLE RCIC steam flow instruments for both Division 1 & 2 became inoperable. Inoperability of these trip units were based upon erratic indications on the trip units. RCIC was subsequently declared inoperable as a result of the required Technical Specification 3.3.2 action for the inoperability of the steam flow instrument which required the isolation of RCIC steam supply line. A 7 day Limiting Condition of Operation for RCIC was entered per Technical Specification 3.7.3 when RCIC steam supply line was isolated. Actions are being taken to correct RCIC steam flow instrument erratic indications. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
36926 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-04-24 14:03 | 2000-04-24 17:06 | 2000-04-24 | INVALID ISOLATED SIGNAL WAS GENERATED During operation of Unit 2 at 100% power, it has been determined that the inboard Primary Containment Isolation Valves associated with the Containment Radiation Monitors (CRMs) received an invalid isolation signal. During maintenance activities in the panel to change out a previously failed relay for the "A" CRM, the relay for automatic isolation was disturbed and an invalid signal was generated. The relay inputs a close signal to the inboard valves of both CRM's, and the invalid signal caused the "B" CRM to isolate. The licensee is investigating this event. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36925 | 0 | BROWNS FERRY |  | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-04-23 22:08 | 2000-04-24 17:01 | 2000-04-24 | EMERGENCY DIESEL GENERATOR "3ED" RECEIVED AND AUTOMATIC START SIGNAL. On 04/21/00 at 2208, the "3ED" Emergency Diesel Generator received an automatic start signal due to degraded voltage as a result of testing activities associated with the "3ED" 4 kv Shutdown Board. At the time the start was received, the Diesel Generator and the 4 kv Shutdown Board were considered inoperable for their Technical Specification functions, therefore the event was not deemed reportable as an Engineered Safety Feature (ESF) actuation. Further review of the event by the plant staff along with the Senior Resident Inspector concluded that this event should have been considered an ESF actuation, since the automatic start was not preplanned, and the Diesel Generator started as the result of a valid initiation signal. The NRC Resident will be notified of this event notification by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36924 | -1 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-04-24 12:53 | 2000-04-24 16:26 | 2000-04-27 | AUTOMATIC START OF THE PENETRATION ROOM FILTRATION SYSTEM DURING MAINTENANCE ACTIVITIES. Maintenance investigation of a high vibration on "1B" Spent Fuel Pool Exhaust fan resulted in the trip of the Spent Fuel Pool ventilation and subsequent autostart of the Penetration Room Filtration System. All systems operated as required. Operations restarted the Spent Fuel Pool ventilation and secured the Penetration Room Filtration System. An investigation into this event is in progress. The NRC Resident Inspector was notified of this event by the licensee. ***** UPDATE AT 1357 EDT ON 04/27/00 FROM VAUDY HOLLY, JR. TO LEIGH TROCINE ***** The licensee is retracting this event notification. The following text is a portion of a facsimile received from the licensee: "This event has been evaluated further and determined to be an invalid actuation based on 10 CFR 50.72(b)(2)(ii)(B)(3)(iv) and (v). An invalid actuation of the fuel building ventilation system or auxiliary building ventilation system is not reportable." "The accident analysis for fuel handling accidents in the spent fuel pool (SFP) credits the high radiation signal initiation of SFP ventilation isolation and penetration room filtration (PRF) system start. The low differential pressure start of the PRF system is not credited; therefore, PRF system actuation in the absence of a high radiation signal is not an [engineered safety feature (ESF)] actuation. For the purposes of 10 CFR 50.72, this is an invalid actuation." The licensee notified the NRC resident inspector. The NRC operations officer notified the R2DO (Fredrickson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36923 | 0 | SYNCOR INTERNATIONAL CORP |  |  |  |  | 2000-04-24 05:00 | 2000-04-24 15:26 | 2000-04-24 | SURFACE CONTAMINATION FOUND ON PACKAGE DELIVERED TO SYNCOR STAMFORD, CT PHARMACY. A PACKAGE DELIVERED TO THE SYNCOR STAMFORD, CT. PHARMACY FACILITY FROM NORTHERN WESTCHESTER HOSPITAL, MOUNT KISCO, NY., WAS FOUND TO HAVE OUTSIDE SURFACE CONTAMINATION LEVEL OF 645,000 DPM/100 SQUARE CENTIMETER. THE SURFACE CONTAMINATION OF THE PACKAGE WAS LIMITED TO THE TOP CORNER OF THE PACKAGE. THE HIGHEST SURFACE CONTACT RADIATION LEVEL ON THE PACKAGE WAS 0.5MR/HR (TOP CORNER OF THE PACKAGE). THE SURFACE CONTAMINATION WAS FROM Tc-99m (145KeV GAMMA EMITTER, HALF LIFE OF ABOUT 6 HOURS). THE PACKAGE WAS OPENED AND NO SURFACE CONTAMINATION WAS FOUND INSIDE THE PACKAGE. THE DRIVER OF THE VEHICLE AND THE INSIDE OF THE VEHICLE THAT TRANSPORTED THE PACKAGE WERE SURVEYED AND NO CONTAMINATION WAS FOUND. NORTHERN WESTCHESTER HOSPITAL WAS NOTIFIED BY SYNCOR OF THIS EVENT. SYNCOR NOTIFIED NRC REGION 4 (JEFF CRUZ) OF THIS EVENT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | [10 empty] | NON EMERGENCY | 1 | CT | MAT | [5 empty] | 0
36922 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2000-04-20 12:00 | 2000-04-24 15:23 | 2000-04-24 | PROJECTED DOSES TO A PATIENT MAY BE OFF BY GREATER THAN 20 PERCENT ST. JAMES HOSPITAL CALLED THE ILLINOIS DEPARTMENT OF NUCLEAR SAFETY TO REPORT A MEDICAL THERAPY EVENT. FOUR IRIDIUM-192 SEEDS (APPROX. 5mCi each) WERE INSERTED THROUGH A PATIENTS NOSE TO TREAT THE BILE DUCT ON TUESDAY. THE PHYSICIAN HAD MARKED THE TUBE AT THE NOSE AS A REFERENCE POINT. ON THURSDAY THE PHYSICIAN NOTICED THAT THE REFERENCE POINT HAD MOVED. ST. JAMES HOSPITAL PERFORMED AN X-RAY AND NOTICED THAT THE SOURCES WERE NO LONGER AT THE TREATMENT SITE. THE LICENSEE BELIEVES THAT THE DOSE TO THE INTENDED AREA WILL BE OUTSIDE THE RANGE OF THE 20% LIMIT. THE LICENSEE BELIEVES THE TREATMENT WENT AS PLANNED FOR THE FIRST 24 HOURS AND THAT THE SEEDS MOVED SOMETIME DURING THE SECOND 24 HOURS. TOTAL TREATMENT TIME WAS SUPPOSED TO HAVE BEEN 70 HOURS. THE LICENSEE IS PERFORMING A DOSE ASSESSMENT NOW AND WILL FORWARD A WRITTEN REPORT TO THE ILLINOIS DEPARTMENT OF NUCLEAR SAFETY WITHIN 15 DAYS. THE LICENSEE PLANS TO CONTINUE THE TREATMENT ONCE THEY HAVE A BETTER ESTIMATE OF DOSES TO THE TREATMENT SITE. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0
36921 | -1 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-04-23 03:35 | 2000-04-23 06:49 | 2000-05-10 | UNIT 1 TRAIN 'B' ESSENTIAL SERVICE WATER PUMP STARTED AUTOMATICALLY While setting up for testing the Solid State Protection System (SSPS) on Unit 2, the clearance permit did not anticipate the start of the Unit 1 train 'B' Essential Service Water (ESW) Pump. "To perform maintenance on the SSPS, a clearance to deenergize the SSPS cabinets in Unit 2 was written. The Unit 2 SSPS was in inhibit at this time. During the deenergization per this clearance, an automatic start of the Unit 1 East ESW Pump occurred. The ESW Pump autostart was not anticipated or described in the clearance. "A Safety Injection (SI) signal through SSPS in either Unit 1 or Unit 2 will cause the ESW Pumps in both units to autostart for the train effected. Similarly, the removal of power from the control room instrumentation distribution circuit, which is what occurred here, will cause the autostart of the ESW pumps. "There were no adverse consequences as a result of the auto pump start and the actuation was per the system design. No SI signal was generated." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1822 ON 5/10/00 BY WOODS RECEIVED BY WEAVER * * * "The original report was made regarding an automatic start of the Unit 1 East Essential Service Water (ESW) Pump during maintenance, and was conservatively reported as an automatic actuation of an Engineered Safety Feature (ESF). Subsequent reviews of the pump start event and the reportability requirements of 10 CFR 50.72 and 50.73 have confirmed that this event is not reportable. "In the case of the start of the 1 E ESW Pump, the ESF actuation slave relay never was actuated, but was deenergized and would not have actuated. No other portion of the associated ESF actuation circuitry was completed. Additionally, the ESW pump was not manually started in an emergency response to plant conditions that would have required the pump to be operating. "NUREG-1022, Revision 1, Event Reporting Guidelines: 10CFR50.72 and 50.73, Part 3.3.2, Actuation Of An Engineered Safety Feature Or The RPS, provides guidance for the reporting requirements of an ESF actuation event as listed in 10 CFR 50.72 and 50.73. The NUREG states that actuation of certain single ESF components of complex systems need not be reported. Single components of complex systems, by themselves, usually do not mitigate the consequences of significant events. "Based on the facts that this event was an inadvertent start of a single component that would not mitigate the consequences of a significant event, and that the minimum amount of ESF actuation logic, i.e., the slave relay, did not actuate, the event is not reportable under 10 CFR 50.72 or 50.73. Therefore, the 4 hour non-emergency report, event number 36921, is being retracted." The licensee informed the NRC resident inspector of this report. The Operations Center notified the R3DO (CLAYTON). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | Refueling | Cold Shutdown |  | Refueling | Cold Shutdown |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36920 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2000-04-23 00:10 | 2000-04-23 00:38 | 2000-04-23 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER During preparation for a bus transfer test, the wrong relay was energized which caused the loss of offsite power to the 'A' and 'B' 13.8 Kv busses. An Unusual Event was declared with the loss of offsite power. Only one of the offsite sources was energized at the time and the relay tripped during test setup causing the loss of that source. The 4160 volt essential busses were reenergized by their respective emergency diesel generators. The plant was defueled at the time and spent fuel pool cooling was restarted. There was no release of radioactivity and no recommended protective actions necessary. The licensee is conducting a review of the event and all testing activities are suspended until completed. The Unusual Event was terminated at 0054 EDT with the restoration of normal power configuration. The licensee notified the State of Ohio and the local counties, Ottawa and Lucas, as well as the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a)(1)(i) |  |  |  | 0
36919 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-04-22 14:28 | 2000-04-22 17:05 | 2000-04-22 | - SHUTDOWN COOLING LOST FOR 48 MINUTES; NO REACTOR VESSEL TEMPERATURE RISE - On 04/22/00, Unit 2 was in Condition 5 in a Refueling Outage with the reactor vessel cavity flooded up to higher than 20 feet 6 inches above the reactor vessel flange with the fuel pool gates removed. At 1428, shutdown cooling was lost due to a technician inadvertently pulling a wrong electrical fuse causing the Residual Heat Removal (RHR) shutdown inboard suction isolation valve #E1150-F009 to auto close. The closure of this valve was in response to an invalid reactor vessel water level three signal causing the 'A' RHR pump to trip due to loss of suction flow. At 1516, shutdown cooling was restored. No temperature rise in the reactor vessel was noted during the time that shutdown cooling was out of service. The licensee plans to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36918 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-04-22 15:06 | 2000-04-22 16:19 | 2000-04-22 | - POTENTIALLY CONTAMINATED PLANT EMPLOYEE TRANSPORTED TO OFFSITE HOSPITAL - A potentially contaminated plant employee who sustained a broken leg onsite, was transported offsite to Oswego hospital for treatment accompanied by a plant radiation technician. The licensee plans to notify the NRC Resident Inspector. * * * UPDATE AT 1712 ON 04/22/00 BY STEVE FREGEAU TO JOLLIFFE * * * The plant radiation technician determined that the plant employee was not contaminated. The licensee plans to notify the NRC Resident Inspector. The NRC Operations Officer notified the R1DO John White. | 0 | 54 | 0 | 0 | 54 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(v) |  |  |  | 0
36917 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-04-22 08:03 | 2000-04-22 11:08 | 2000-04-22 | MAIN STEAM ISOLATION VALVE FAILED TIMING TEST The licensee determined that the 'B' steam generator main steam isolation valve shut in 6 seconds during testing. The requirement is 5 seconds in the surveillance test of technical specifications and in the Updated Safety Analysis Report. The plant will remain shutdown until repairs and testing are complete. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36916 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-04-21 13:45 | 2000-04-21 18:38 | 2000-04-21 | - NOTIFICATION OF FEDERAL, STATE & LOCAL AGENCIES OF A HYDRAZINE CHEMICAL SPILL ONSITE - At 1345 CDT on 04/21/00, Unit 1 experienced a chemical spill of 38 gallons of hydrazine that had leaked from a line that leads to an onsite storage tank. The licensee isolated the leak, contained the spill onsite and is cleaning up the spill. The licensee notified the NRC Resident Inspector and is in the process of notifying the DOT National Response Center, Texas Natural Resources Conservation Commission and the Local Emergency Planning Committee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36915 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2000-04-21 11:10 | 2000-04-21 16:46 | 2000-04-21 | FITNESS-FOR-DUTY REPORT - A licensed employee was for-cause tested for the presence of alcohol and was determined not to be unfit for duty. The employee's access authorization to the plant protected area which had been suspended, was restored. The licensee notified the NRC Resident Inspector. On April 21, 2000 at approximately 11:10 MST, the Unit I Shift Manager, a licensed senior reactor operator, opened his lunch box and discovered that it contained an unopened can of beer. By approximately 11:15 MST, the shift manager completed notifications to station management and security, and isolated the alcoholic beverage. Although behavior observation by supervision detected no degradation in performance, impairment, or changes in employee performance, the shift manager's access to the protected area was suspended and he was escorted to the Palo Verde health clinic for fitness-for-duty testing. Testing for-cause, conducted in accordance with 10CFR26.24(a)(3), was negative, demonstrating that the Shift Manager was not unfit for duty due to the consumption of alcohol. Upon completion of satisfactory testing, access to the protected area was restored. The unopened can of beer has been removed from the protected area. The Shift Manager stated that the can of beer, instead of a can of soda, had been placed in the lunch box inadvertently by himself when preparing to come to work. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.73 |  |  |  | 0
36914 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2000-04-20 13:00 | 2000-04-21 15:04 | 2000-04-21 | AGREEMENT STATE REPORT: MEDICAL MISADMINISTRATION - At 1300 on 04/20/00, a 52 year old female patient received a medical misadministration of a gamma knife treatment at the University of Maryland at Baltimore (UMAB) Hospital to reduce the cancerous tumor in her head. The gamma knife is a UMAB specific license that uses 201 sealed Cobalt-60 sources of 30 curies each in a Model 23016 Leksell Gamma System for the radiation treatment of human patients. The patient received 12.6 gray to an unintended site of approximately 0.18 cubic centimeters. The unintended site was approximately 4.2 centimeters from the intended site. The medical directive for this treatment was defined as approximately 18 gray administered over six administrations. The misadministration occurred during the first administration only. The treatment planning for the patient was uneventful and was prepared and reviewed by a hospital gamma knife team of a Radiation Oncologist, a Neurosurgeon and a Medical Physicist. It appears from preliminary interviews that when two of the team members were adjusting the coordinates on the device's steriotactic frame, the Y and Z coordinates were reversed. This frame adjustment is accomplished by loosening the frame via the use of allen screws and manually adjusting it. One person calls out the coordinate and the other conducts the adjustment. According to the licensee procedures, this adjustment is to be checked for accuracy by a nurse and the Medical Physicist. Normally the coordinates are read out in a specific order. The licensee indicated that the order might have been reversed due to a specific frame orientation problem that occurs approximately once in every 20 treatments. When the licensee started to set up for the second administration, the error was noted. The treatment plan was reevaluated to include some partial dose to the tumor from the first administration and the treatment was completed in seven administrations instead of six. The patient and her referring physician have been notified of this misadministration. This misadministration constitutes no negative medical impact on the patient. A MD DOE representative requested that UMAB Hospital personnel review previous medical files to assure that this switching of coordinates has not happened before without a misadministration being identified. The gamma knife is not scheduled to be used again at UMAB Hospital until 04/25/00. On 04/24/00, a hospital management meeting has been scheduled among personnel from Hospital Administration, Oncology, Neurosurgery and the Radiation Safety Office to discuss this incident. The RSO's position at this meeting will be that all use of the gamma knife be suspended until the incident has been fully investigated and assurances are in place to prevent recurrence. A written report of this incident will be submitted to NMED within 30 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | MED MISADMINISTRATION | [8 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  | 35.33 |  |  | 0
36913 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2000-04-21 02:00 | 2000-04-21 13:59 | 2000-04-21 | AGREEMENT STATE REPORT: DAMAGED TROXLER MOISTURE DENSITY GAUGE - At 0200 on 04/20/00, an automobile struck a Banks Construction Company (License #SC-518) truck on I-26 in Charleston, SC, damaging a Troxler Moisture Density Gauge, model #4640. The 9 mCi Cs-137 and 44 mCi Am-241-Be sources were undamaged. The damaged gauge, containing its undamaged sources, was placed into its transport case and will be sent to Troxler for repairs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | DAMAGE MEASURE GAUGE | [8 empty] | NON EMERGENCY | 2 | SC | OTH | AGR |  |  |  |  | 0
36912 | 0 | ABI LABORATORY, INC. |  |  |  |  | 2000-04-20 14:00 | 2000-04-21 09:14 | 2000-04-21 | POSSIBLE OVEREXPOSURE On 04/20/00 the Radiation Safety Officer for ABI Laboratory, Inc., received a phone call from Troxler informing her that one of the film badges that they had read had a reading of 30,677 mrem (30.7 Rads). Troxler will check the film badge again on Monday, 04/24/00, since Friday is a holiday. The film badge belongs to an ABI Laboratory, Inc., employee who is currently working at a construction site located at the Philadelphia International Airport . The film badges for ABI Laboratory, Inc., are checked quarterly by Troxler. The film badge mentioned above had been used during the December 1999 through February 2000 time period. The ABI Laboratory, Inc. construction site has 2 Troxler and 2 Humboldt Density Gauges. The Density Gauges were all leak tested and radiation surveys were taken inside and around the building containing the gauges. All radiation surveys and leak tests were within expected values. From December 1999 through February 2000, the employee in question used a Density Gauge on 20 different days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2202(a)(1) |  |  |  | 0
36911 | -1 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-04-20 19:30 | 2000-04-20 20:29 | 2000-04-26 | - LICENSEE NOTIFIED NATIONAL RESPONSE CENTER AND STATE DEP OF A CHEMICAL SPILL ONSITE - The licensee notified the National Response Center and the State Department of Environmental Protection (DEP) that approximately 5 gallons of a mixture of sulfuric acid and sodium hydroxide spilled from a tank truck onto the ground after a chemical reaction took place. The spill was contained within a portable dike area onsite and is being cleaned up. The licensee plans to notify the NRC Resident Inspector. * * * UPDATE AT 0948 EDT ON 04/26/00 FROM ROY HARDING TO S. SANDIN * * * The licensee is retracting this report based on the following: "This is a retraction of the notification made on 04/20/00 at 2029 hours (Event 36911). This event was reported as a notification of another government agency [National Response Center and Pennsylvania Department of Environmental Protection (PADEP)] pursuant to 10CFR50.72(2)(b)(vi). "On April 20, 2000 at 1930 hours while Limerick Unit 1 was shutdown for refueling, 5 to 10 gallons of a dilute and partially neutralized acid (Sulfuric Acid-pH 3) was expelled from a temporary trailer tank onto asphalt and stone surface in an adjacent area outside a temporary dike. In addition, approximately 30 gallons of the acid/sludge mixture spilled into the temporary dike. The spill never threatened navigable waterways, and subsequently was cleaned up within a 24 hour period. The initial notification was conservatively reported based on information known at the time of the event. "A minor spill of this nature is not reportable to the PADEP in accordance with 40CFR112 and the Preparedness Prevention Plan for Limerick Generating Station. This spill from a temporary tank had no impact on navigable waterways and was less than the Reportable Quantity (69 gallons)." The licensee will inform the NRC Resident Inspector. The NRC Operations Officer notified the R1DO (Noggle). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36910 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2000-04-17 10:20 | 2000-04-20 17:38 | 2000-04-20 | - RCS LEAKAGE CRITERIA FOR DECLARING AN UNUSUAL EVENT EXISTED ON 04/17/00 - At 1020 on 04/17/00, St. Lucie Unit 2 was in Mode 4 in a refueling outage preparing to go on shutdown cooling. A pre-job brief was conducted and included a discussion of the potential for pressurizer level change, relief valve lifting and the need to monitor the telltale on containment spray isolation valve #MV-07-3 to determine valve leakage. The expectation was established that the operating crew would terminate the evolution if unexpected leakage was observed with the primary focus on the telltale tubing monitoring containment spray isolation valve #MV-07-3. The control room operator observed a sudden drop in pressurizer level once the last shutdown cooling isolation valve was opened (6% drop on the hot calibration indication). The valve was immediately closed and pressurizer level stabilized; the evolution duration was approximately 3 minutes. As the valve was closing, the field operator stated he was seeing leakage through the tygon tubing, which he estimated to be about 1 to 2 gpm. There was no increase in sump level and no abnormal interfacing system behavior. Operations department personnel believed the behavior observed was consistent with filling shutdown cooling lines. Subsequently, the on-shift engineer performed an inventory balance and, without adjusting for changing temperatures and pressures, estimated a 100 gpm leak had occurred. The Nuclear Plant Supervisor (NPS) did not feel the inventory balance was valid in that he knew the accuracy of the calculation was biased because of the effect of temperature and pressure and the short duration of the event. Based on the discrepancy between the calculation and field observation, the NPS had a condition report issued to determine the RCS leak rate. The NPS rationale for not entering the Emergency Plan and that RCS leakage was not greater than 10 gpm was based on the following: - his field operator's observations showed a 1-2 gpm leak, - a lack of any increase in sump level, - a lack of any abnormal plant interfacing systems behavior, and - the evolution was consistent with his understanding of the pressurizer level behavior when filling shutdown cooling piping based on his observation in the past. A subsequent activity of placing shutdown cooling on line later that same day resulted in a similar event, with significantly less inventory loss. Shutdown cooling train A was placed on line the afternoon of 04/17/00. However, based on the results of the engineering review, the pressurizer level drop was not solely due to the fill and vent evolution of the shutdown cooling system, as originally concluded. Two hundred (200) gallons of RCS inventory was transferred inter-system during this event. FPL has concluded that this short duration, operator-terminated event met the procedural requirements for entering the emergency plan. However, it is clear upon review of the context and intent of the emergency plan that at no time did an actual emergency or threat thereof exist. As provided for in NUREG 1022, "a licensee may discover that an event or condition had existed which met the emergency plan criteria, but that no emergency had been declared and the basis for the emergency class no longer exists at the time of discovery". Based on an engineering review, FPL concludes that while initiating shutdown cooling on the A train on 04/17/00, an RCS inventory transfer occurred to interfacing systems in the 2-3 minute periods associated with starting shutdown cooling. The initial attempt to place shutdown cooling on line, and possibly a second attempt later the same day, resulted in leakage exceeding the Technical Specification threshold and would constitute entry into a Notification of Unusual Event. Although the criteria was met, FPL is not declaring an emergency for the following reasons: 1. The event was the result of a planned activity and the greater than expected pressurizer level drop was quickly compensated for by operator actions. 2. The event was of very short duration and at no time challenged the ability for decay heat removal or posed a threat to the health and safety of the public or plant personnel. 3. The circumstances associated with determining the appropriate classification of the event required three days of engineering evaluation. State and local county officials and the Senior NRC Resident Inspector are being informed of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0
36909 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-04-20 09:30 | 2000-04-20 14:02 | 2000-04-20 | - UNIT 2 S/Gs PRIMARY-TO-SECONDARY DESIGN DIFFERENTIAL PRESSURE OUTSIDE DESIGN BASIS - Indian Point Unit 2 received a letter from Westinghouse (the NSSS Supplier) which stated that Westinghouse is in the process of completing a Nuclear Safety Advisory Letter regarding the primary-to-secondary design pressure differential in the steam generators. The current design pressure listed in the equipment Specification is 1550 psid. With an anticipated steam generator outlet pressure in the 650 to 660 psia range, this design pressure will be exceeded. However, Indian Point Unit 2 has an analysis that determined that the limiting structure within the steam generator, the tube sheet, can withstand a pressure differential of 1750 psid. This issue may be addressed by updating the design pressure and stress reports demonstrating compliance with the ASME Code as governed by Section IWA-4312, Re-rating, of Section Xl of the ASME Code. The licensee plans to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36908 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-04-20 07:45 | 2000-04-20 11:43 | 2000-04-20 | - HPSI, LPSI & CS SYSTEMS OUTSIDE THEIR DESIGN BASIS DUE TO LACK OF INSTALLED INSULATION - The following is the text of a fax received from San Onofre: This notification from San Onofre Units 2 and 3 is being made in accordance with 10CFR50.72(b)(1)(ii)(B) for the condition of the High Pressure Safety Injection (HPSI), Low Pressure Safety Injection (LPSI) and Containment Spray (CS) Systems being outside their design basis. This condition exists for both Units 2 and 3. On 04/19/00, during an NRC inspection, it was discovered that portions of the ECCS piping were not insulated as assumed in design calculations. Affected lines are the suction and discharge piping for the HPSI Pumps #P017, P018 & P019, LPSI Pumps #P015 & P016, and CS Pumps #P013 & P014. The consequence of the missing insulation is that the heat loads in the ECCS pump rooms will be higher than assumed in the plant accident analyses. At 0745 PDT on 04/20/00, SCE concluded that ECCS pump room temperatures during certain accident scenarios may not remain below their design basis room temperatures of 104°F. However, the equipment in the pump rooms continues to be operable at the calculated higher post-accident temperatures. That is, even with the higher than expected ECCS pump room temperatures, the affected equipment would continue to be able to perform its intended safety function. SCE has installed some temporary insulation and will take actions to install permanent insulation on the affected piping. SCE's investigation of this occurrence is ongoing; the cause of this condition will be reported in the followup 30 day licensee event report. At the time of this discovery, both Units 2 and 3 were operating at about 100% power: Unit 1 remains permanently defueled. SCE plans to notify the NRC Resident Inspectors about this issue and will provide them with a copy of this event report. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36907 | -1 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-04-19 18:16 | 2000-04-19 21:36 | 2000-05-18 | FILTERED EXHAUST FANS CANNOT BE OPERATED IN PARALLEL "Based on Unit 1H and 1J emergency bus logic testing performed on 4/18/00 and 4/19/00 in accordance with 1-OPT-ZZ-001 and 1-OPT-ZZ-002, it has been concluded that the Cat 1 Filtered Exhaust Fans, 1-VS-F-58A & B, will not operate in parallel without tripping one or both fans. As a result, an event or condition that alone could have prevented the fulfillment of a safety function of structures or systems that are needed to control the release of radioactive material, or mitigate the consequences of an accident exists for Surry Units 1 and 2. This condition is reportable in accordance with 10 CFR 50.72(b)(2)(iii). "Both fans have been tested by operating the fans individually. This testing has determined that operation and performance of each fan is entirely satisfactory when operated independently. "The current system alignment is that one of the two fans is in the pull-to-lock position, and the other fan is in automatic stand-by. In this configuration, one fan is operable, and fully capable of performing its required functions. Unit 2 entered a 7 day Technical Specification 3.22.B action statement on 4/18/00 at 1240 hours as a result of this condition. "The Surry Emergency Operating Procedures provide required directions to place a Cat 1 Filtered Exhaust Fan in service, if the fans fail to automatically start upon initiation of a Safety Injection. In the current configuration, if the operable Cat 1 Filtered Exhaust fan fails to start, the fan that is currently in PTL can be immediately placed in service." The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE ON 5/18/00 @ 1243 BY HARROW TO GOULD * * * RETRACTION NUREG 1022, Event Reporting Guidelines for10CFR50.72 and 50.73. states that "Reasonable operator actions to correct minor problems may be considered; however, heroic actions and unusually perceptive diagnoses, particularly during stressful situations should not be assumed." Both CAT 1 FiItered Exhaust Fans were proven to operate satisfactorily when tested individually, and only one fan is needed to meet the system design requirements. If both fans had tripped after automatically starting from a Safety Injection signal, the Emergency Operating Procedures (EOP's) would direct that one fan be started. This is accomplished from the control room, and does not require unusual actions from the operator. The Surry DBA Dose Analysis assumes that filtration of ECCS leakage begins 30 minutes post-accident, which is ample time to perform the EOP action of starting a Filtered Exhaust Fan if none are running. Based on the above review of the event and the information in NUREG 1022, it has been determined that this event was not immediately reportable, as existing Emergency Operating Procedures would ensure that at least one fan is running within the required time after a Safety Injection signal is received. This notification is being made to retract the report made on 4/19/00 based on the above discussion. The NRC Resident Inspector was notified. Notified the Reg 2 RDO(Wert). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iii)(C) | 50.72(b)(2)(iii)(D) |  |  | 0
36906 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-04-19 15:55 | 2000-04-19 19:50 | 2000-04-19 | NRC BULLETIN 91-01 4 HOUR REPORT "At 1555 hrs April 19, 2000, laboratory personnel were preparing samples when they discovered that 8 uranium bearing samples (16-40 ml vials) were in an Environmental Safety & Health (ES&H) Analytical Laboratory without having had a gamma scan performed to determine total uranium. NCSA-0710_015.A02 administrative control #1, states in part, "Any sample containers that are postulated to contain uranium contamination >=100 ppm uranium based on their origin shall be gamma scanned for total uranium." Control #1 of the NCSA was lost, leading to a possible error in the mass tally for the high concentration containers. The total volume of the containers was 640 ml, and the concentration of the containers was subsequently determined to be 500 ppm U-235. Mass control was lost for the high concentration containers. Mass control for low concentration containers and volume controls for process waste were maintained. "At the direction of the Plant Shift Superintendent (PSS) the requirements for an NCS anomalous condition were initiated. At 1920 hrs compliance was regained by scanning the samples and properly logging them into the container mass inventory. "At the direction of the PSS the X-710 management staff will conduct briefings with the respective personnel to prevent re-occurrence." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36905 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-04-19 14:33 | 2000-04-19 17:55 | 2000-04-19 | INADVERTENT AFW ACTUATION FOLLOWING TESTING "At about 1433 hours on 19 April 2000, there was an inadvertent actuation of 32 Auxiliary Boiler Feedwater Pump (ABFP). The actuation occurred following the completion of the required monthly test of 32 Emergency Diesel Generator (EDG), when the diesel output breaker was opened. Normally the 'Non-SI Blackout Logic' circuitry prevents automatic starting of equipment until manually reset. For some reason, currently under investigation, this circuitry automatically reset when the EDG output breaker was opened. The cause of the automatic reset of the Non-SI Blackout Logic, and the automatic start of 32 ABFP is under investigation. 32 EDG was inoperable prior to this event for planned testing, and remains inoperable while the investigation continues. 32 EDG is currently available and aligned for automatic start. There were no plant conditions requiring operation of 32 ABFP and the automatic start sent no water to any steam generator (since this requires additional manual action). Immediate corrective action taken was to secure 32 ABFP." The NRC resident inspector has been informed of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36904 | 0 | HONEYWELL SENSOR AND GUIDANCE PRODS |  |  |  |  | 2000-03-23 | 2000-04-19 16:09 | 2000-04-19 | MISSING AIR IONIZER A generally licensed NRD model P-2021-3000 air ionizer (s/n 115737) was discovered missing from a clean room at the Honeywell SGP facility in Minneapolis. The device had an initial activity of 10 mCi of Po-210, but the caller did not know the current activity. The device was declared lost on 3/23/00 after repeated searches of the facility and interviews of employees did not lead to its recovery. Honeywell has contacted the vendor regarding this matter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36903 | 0 | ST. LUKE'S REGIONAL MEDICAL CENTER |  |  |  |  | 2000-02-25 | 2000-04-18 12:21 | 2000-04-18 | MEDICAL MISADMINISTRATION On 2/25/2000, an individual was implanted with 58 I-125 seeds for prostate treatment. However, the activity of the seeds implanted (0.354 mCi/seed) was higher than prescribed (0.27 mCi/seed). The licensee reported that, although the actual dose to the prostate was similar to the planned treatment dose, since the activity of the implanted seeds exceeded the prescribed activity by more than 20%, this occurrence was being treated as a misadministration. The misadministration was discovered during a review performed on 4/17/2000. The licensee reported that an error occurred when the seeds were being ordered, and that additional steps would be added to the procedure to prevent recurrence. The radiation oncologist has been notified, and he will inform the patient of the incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 4 | ID | HOS |  | 35.33 |  |  |  | 0
36902 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-04-17 14:40 | 2000-04-17 16:02 | 2000-04-17 | SOURCE RANGE NEUTRON MONITOR COULD BE AFFECTED BY 10 CFR PART 50, APPENDIX R ISSUE "The cabling for Unit 2 source range monitor 2N-32 was found to be impacted by a postulated fire in either the CCW pump room or the Unit 2 MCC room in the 8' PAB. Per 10 CFR 50 Appendix R at least one nuclear instrument (2N-31, 2N-32 or 2N-40) must be available to monitor source range flux while shutting down the unit. [Monitor] 2N-32 is relied upon for a fire in [fire zone] FZ 142 and 166 due to cable losses on the 2N-31 and 2N-40 instruments. Loss of 2N-32 will cause a total loss of SR monitoring capability which places the plant outside the Appendix R design basis." The NRC resident inspector will be informed of this notification by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36901 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-04-17 13:09 | 2000-04-17 15:56 | 2000-04-17 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM "At 13:04 on 4/17/00, BVFS Unit 1 experienced a loss of the turbine auxiliary steam header pressure. The loss of auxiliary steam pressure resulted in a decrease in condenser vacuum, rapidly approaching the low-low vacuum turbine trip setpoint. At 1309, the reactor was tripped manually. Steam Generator 1C feed valve FCV-1FW-498 was isolated during recovery due to minor leakby. Auxiliary Feedwater and all other equipment responded as expected. The initial problem was caused by a failure of the auxiliary steam supply pressure control valve air diaphragm packing. This valve is air to open and spring operated to close. Air pressure was lost through the failed packing causing the valve to fail in the closed position. Auxiliary steam was restored during plant stabilization. The plant is in Hot Standby and all systems are functioning properly. Heat removal is via the normal condenser steam dump system." The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36900 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-04-16 12:00 | 2000-04-17 12:35 | 2000-04-17 | OFFSITE NOTIFICATION REGARDING DISCOVERY OF SEA TURTLE IN PLANT INTAKE CANAL "At approximately 12:00 on 4/16/00, a loggerhead sea turtle was recovered from the plant's intake canal. The turtle was alive, but in need of rehabilitation, and was subsequently sent to a facility at Sea World. As required by the plant's sea turtle permit, the Florida Department of Environmental Protection (DEP) was notified of the event. The notification of the DEP necessitates a four (4) hour phone call to the NRC. "The licensee recognizes that this notification is being made outside the allotted four (4) hour window. The root cause will be investigated through the Condition Report process." The NRC resident inspector has been informed of this notification by the licensee. | 100 | 68 | 0 | 100 | 68 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36899 | 0 | INTERNAT. RAD & INSPECT. SVCS. INC. |  |  |  |  | 2000-04-14 11:30 | 2000-04-17 11:44 | 2000-04-17 | SOURCE DISCONNECT ON CAMERA OWNED BY INTERNATIONAL RADIOGRAPHY & INSPECTION SERVICES INC. A radiography camera being used for an inspection by International Radiography & Inspection Services Inc. at the Matrix Fabrication Division site in Catoosa, Ok. had a source disconnect while being cranked out. The source, which contained 72 curies of Iridium-192, was manufactured by AEA Technologies and mounted in a SPEC camera. During the time of the source disconnect, the area around the camera was secured. The licensee RSO went to the site, did a source recovery and returned the camera to their facility. There were no exposures >40 mrem. The licensee has packaged the equipment and will FedEx it to AEA Technologies for their analysis of the problem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 4 | OK | OTH | GEN | 30.50(b)(2)(ii) |  |  |  | 0
36898 | 0 | COMMUNITY HOSPITAL OF LANCASTER |  |  |  |  | 2000-04-16 14:30 | 2000-04-17 09:48 | 2000-04-17 | RECEIPT OF A PACKAGE WITH SURFACE CONTAMINATION GREATER THAN THE 2,000 DPM/100 cm² LIMIT On 04/16/00, a package arrived from Syncore (a pharmacy located in Harrisburg, Pennsylvania), and calculations following a wipe test of the package revealed surface contamination of 13,600 DPM/cm². This was discovered at 0230 on 04/16/00. The licensee reported that the package contained technetium-99m and that the licensee normally receives 50 mCi in each package. At the time of this event notification, the package had not been opened, and there was no report of a breach. The licensee quarantined the package in a storage area and notified Syncore at 0245 on 04/16/00. The licensee reported that the contamination is more likely to be around 2,400 DPM/cm² because the efficiency of the well counter is based on cesium and the isotope involved was identified to be technetium-99m. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | [10 empty] | NON EMERGENCY | 1 | PA | HOS | [5 empty] | 0
36897 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-04-17 02:51 | 2000-04-17 04:57 | 2000-04-17 | CLOSURE OF A RESIDUAL HEAT REMOVAL (RHR) SHUTDOWN COOLING OUTBOARD ISOLATION VALVE RESULTING IN LOSS OF AN RHR PUMP AND SUBSEQUENT LOSS OF SHUTDOWN COOLING FOR 21 MINUTES The following text is a portion of a facsimile received from the licensee: "At 0251 on 04/17/00, the E1150-F008 'RHR Shutdown Cooling (SDC) Outboard Isolation Valve' closed causing the RHR 'B' pump to trip due to loss of suction flow path. At the time of the trip, the RHR 'B' pump was in operation for [SDC]." "[SDC] was restored at 0312. During the event, Unit 2 was in Mode 5 -- Refueling -- with the vessel cavity flooded up to greater than 20' 6" above the vessel flange with the fuel pool gates removed. No temperature rise in the vessel was noted during the time SDC was out of service. No core alterations were in progress at the time." "Prior to the closure of the E1150-F008 valve, [the] Division 2 core spray system was being tagged out of service for [refueling] outage maintenance. Part of the tag-out was to remove fuses for the core spray AC/DC inverter. Upon removing power to the inverter, a reactor high pressure signal caused a trip system B, group 4 -- Shutdown Cooling/Head Spray Isolation, which closes the E1150-F008 valve. After the isolation, the core spray AC/DC inverter was returned to service, the E1150-F008 valve opened, and RHR 'B' pump was placed back into [the] SDC mode." "This event is being reported under 10CFR50.72(b)(2)(ii), any event or condition that results in the manual or automatic actuation of any engineered safety feature." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36896 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-04-16 07:34 | 2000-04-16 13:28 | 2000-04-16 | OFFSITE NOTIFICATION MADE TO THE NATIONAL MARINE FISHERIES The licensee made an offsite notification to the National Marine Fisheries that a green sea turtle was found inside their intake structure. The licensee will take the sea turtle out to sea and release it . As a courtesy the licensee will notified state and local officials. The NRC Resident Inspector was notified of this offsite notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36895 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-04-16 04:20 | 2000-04-16 05:45 | 2000-04-16 | MANUAL REACTOR TRIP WITH ROD MOTION DUE TO A DIFFERENCE BETWEEN SHUTDOWN BANK 'B' GROUP DEMAND AND DIGITAL ROD POSITION INDICATION (DRPI) FOR ROD G-13 The following text is a portion of a facsimile received from the licensee: "At 0420 CDT, the Unit 2 reactor trip breakers were opened while withdrawing the shutdown banks. Shutdown bank 'B' was at 17 steps by group demand and indicated (rod G-13) 210 steps by DRPI. [Technical Reference Manual (TRM)] 3.1.g required [the reactor] trip [breakers] to be opened immediately. The unit is stable in Mode 3. All rods indicated on the bottom." The licensee stated that there was nothing unusual or not understood and that all systems functioned as required. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36894 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-04-15 20:45 | 2000-04-15 23:28 | 2000-04-15 | STEAM GENERATOR BLOWDOWN AND BLOWDOWN SAMPLE ISOALTION VALVES CLOSED DUE TO RADIATION MONITOR R-15 FAILURE. Radiation Monitor R-15 air ejector exhaust failed indicating a detector no count failure. This failure caused steam generator blowdown isolation valves and steam generator blowdown sample isoaltion valves isolations to close. These valves have a containment isolation function for a main steam line rupture within containment. Their post Loss Of Coolant Accident function is to provide steam generator isolation. HS-17-1, Humidification steam inlet CV to office/warehouse ventilation also closed as designed. Offsite Dose Calculation Manual compensatory measures have been implemented. Instrument and control personnel have been called in to begin failure investigation. Chemistry Department personnel have been contacted concerning the steam generator blowdown isolation. Licensee thinks that Radiation Monitor R-15 air ejector exhaust failed because its chart recorder indicates erratic downscale counts for approximately 20 minutes. Per Radiation Monitor Logic a failure of the monitor will occur if no counts are detected for 5 minutes. The licensee also stated they have been having problems with this detector in the past and it had been recently replaced. The NRC Resident Inspector was notified of this event by the licensee. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36893 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-04-15 17:14 | 2000-04-15 19:22 | 2000-04-15 | AUTOMATIC REACTOR TRIP ON NEGATIVE FLUX RATE TRIP - DROPPED ROD. At 1714 CT Unit 2 tripped from a Nuclear Instrumentation (from all 4 Power Ranges) negative rate (coincidence with 2 of 4 Power Range Rate change of 5% in 2 seconds) signal. The initiating event appears to have been a dropped rod. Control Bank "B" P-10 Stationary Gripper Fuse has been found blown. Following the trip the Motor Driven and the Diesel Driven Auxiliary feedwater pumps actuated on low steam generator water level signals from all 4 steam generators. A P-14 (high 2 on 2 of 4 steam generator levels for Steam Generator "2C") was processed during the first second of the reactor trip. This is an ESF actuation but is considered an invalid signal, because Steam Generator "2C" did not have a high water level, but is reportable. All rods fully inserted into the core. The Unit is stable in Hot Standby with heat being removed via the steam dumps to the main condenser and main feedwater is being supplied to maintain proper steam generator water levels. Offsite power is available. Steam Generator atmospheric valves may have opened but there are no leaking steam generator tubes. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36892 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-04-15 12:26 | 2000-04-15 14:22 | 2000-04-16 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL (RVWL) DUE TO 1 OF 2 REACTOR FEED PUMPS (RFP) TRIPPING. HPCI & RCIC INJECTED INTO THE REACTOR VESSEL FOR LESS THAN ONE MINUTE. Unit 3 was in coastdown planning to enter its scheduled refueling outage on 04/16/00. Reactor power level had been reduced from 82% to 70% to place RFP "3A" in service and remove RFP "3C" from service to investigate the pumps high EHC oil filter pressure. RFP "3C" tripped unexpectedly causing an automatic reactor scram on low RVWL. Two rods did not indicate fully inserted (digital indication for rods 22-47 & 18-47 indicated that they were not fully inserted but both rods had a green background indication on the scram pattern indicating that they were fully inserted) and the appropriated Emergency Operating Instructions EOIs ( 1& C5) were entered. An Alternate Rod Insertion (ARI) was initiated per the EOIs after which both rods indicated that they were fully inserted into the core. Due to low RVWL both Recirculation Pumps Tripped (RPT trip) and High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) automatically actuated and discharged into the Reactor Vessel for less than one minute before they were secured. Primary Containment Isolation Systems Group 2 (Rad Waste), 3 (Reactor Water Cleanup), 6 (Containment) & 8 (Traversing in-core probe) were also received along with the auto start of the Control Room Ventilation System (CREVS) and the Standby Gas Treatment System (SBGT) as expected. All other system operated properly. The licensee is investigating why RFP "3C" tripped and why the digital rod position for rods 22-48 & 18-47 indicated that they had not fully inserted into the core. No work was being performed on RFP "3C" when it tripped. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 04/16/00 AT 1538 ET BY DON SMITH TAKEN BY MACKINNON * * * On 04/15/00, Browns Ferry Nuclear Plant reported that two control rods (22-47 and 18-47) did not indicate being fully inserted following the low Reactor water level scram at 1226 CT. This is corrected by this update as control rods 22-47 and 22-15. Subsequent review of process computer control rod data has confirmed that the two rods (22-47 and 22-15) did fully insert at the time if the scram as expected. R2DO (Chris Christensen) notified. The NRC Resident Inspector was notified of this event update by the licensee. | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | -1 | N | N | A/R | Power Reactor | ECCS INJECTION | RPS ACTUATION | ESF ACTUATION |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(1)(iv) | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  | 0
36891 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-04-14 17:41 | 2000-04-14 19:58 | 2000-04-19 | BURNT SMELL FROM HIGH PRESSURE COOLANT INJECTION (HPCI) STEAM SUPPLY VALVE BREAKER. HPCI DECLARED INOPERABLE AND 14 DAY LIMITING CONDITION OF OPERATION ENTERED PER TECHNICAL SPECIFICATION. An undervoltage alarm was received in control room from HPCI Direct Current Motor Control Center (DCMCC) D312 which is located in the HPCI room. An operator was immediately dispatched to investigate the undervoltage condition on D312. The operator discovered that HPCI Steam Supply Valve, ( MOV-2036), breaker, (D31206), had a burnt smell. The breaker was opened and HPCI Steam Supply Inboard Isolation Valve was closed. HPCI was declared inoperable and a 14 day Limiting Condition of Operation was entered per their Technical Specification. Emergency Core Cooling Systems and Reactor Core Isolation Cooling are fully operable if needed. Their was no fire and the licensee is investigating. The NRC Resident Inspector will be notified of this event by the licensee. * * * RETRACTION 1717 4/19/2000 FROM BISTODEAU TAKEN BY STRANSKY * * * "This notification retracts a notification made 4/14/00 for HPCI being declared inoperable due to a suspected electrical problem in a DC motor control center (MCC). An undervoltage alarm was received, and a burnt smell near the MCC was observed. The HPCI system was isolated per procedure. Investigation revealed a low voltage monitoring coil had failed The coil was replaced and successfully tested. The system was returned to its normal standby condition. "This coil performs a monitoring function only. Failure of the coil, or any effects of the failure would not have prevented the MCC or HPCI system from performing their required safety function. The HPCI system was fully operable until removed from service to investigate the condition and replace the coil." The NRC resident inspector has been informed of this retraction. Notified R3DO (Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36890 | 0 | DRESSER EQUIPMENT GROUP, INC. |  |  |  |  | 2000-04-11 12:00 | 2000-04-14 15:48 | 2000-04-14 | VALVE BONNETS PRODUCED FROM IMPROPERLY UPGRADED CASTINGS. The following noncompliance has been determined to be reportable within the requirements of 10 CFR Part 21. The noncompliance situation involves the delivery of two Safety Relief Valves to Nuclear Utilities for Nuclear Safety Related service that had Valve Bonnets produced from improperly upgraded castings. The valves affected by this situation are as follows: 1) Safety Relief Valve, SN TL-89763 - 1" 1970-2 (1-1-1-2)-XNC3116 (Code Stamped as Section VIII, Safety Related Service) This valve was supplied to Commonwealth Edison Company per their Purchase Order 42I091(Dresser S0 18-56188-0) for their Quad Cities Station #4 in October 1999. 2) Safety Relief Valve, SN TL-66815-1" 1970-2(3-1-3-2)-XFL9-NC3090 (Code Stamped as Section III, Class 2) This valve was supplied to Duke Energy Corporation per their Purchase Order MN39136 (Dresser SO 18-45913-0) for their McGuire Nuclear Station in April 1999. Noncompliance Situation and Brief History On Monday afternoon, April 10, 2000, during the review of documentation for a Nuclear Safety Related valve in process at our facility, we discovered that our casting supplier did not properly upgrade the bonnet staged for assembly of this valve. The mechanical properties of the steel were not verified after the heat treatment phase of the upgrading process. We began our investigation and found the following circumstances that contributed to this situation: 1) The supplier of these castings approved for producing and upgrading castings for Nuclear Safety Related Service quit producing castings by the shell molding process and the casting patterns were transferred to a commercial foundry. 2) Commercial castings were then sent by the Dresser Valve Division, Alexandria facility to the supplier approved for producing and upgrading Nuclear Safety Related Castings with instructions for the castings to be upgraded. 3) The purchase orders for these castings did not reflect instructions for upgrade, but rather read as if we were buying the Nuclear Class castings from this supplier. The castings used for this effort were not certifiable as being free of weld repairs nor were they supported by test bars for use in verifying the mechanical properties after final heat treatment. 4) The Alexandria Inspection department received and inspected the castings but failed to detect the discrepancy during the production operations prior to Monday, April 10, 2000. 5) On Tuesday, April 11, 2000, we determined that two valves referenced earlier in this report had been processed using these castings and were delivered to customers for use in Nuclear Safety Related Service. At this point, we opened an investigation per the requirements of US Code of Federal Regulations, Title 10 CFR, Part 21. We have conducted a full review of our records and have determined that this situation is isolated to the two valves referenced earlier in this report and have contacted the customers and are initiating recall actions as of this writing. Both valves in question were still in the customer's warehouses and had not been installed in the Safety Related Service applications. Corrective actions are being initiated to address the internal and external issues and the details will be provided in our closure report due upon completion of our investigation into the causes of this situation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | LA | OTH | PAR | 21.21 |  |  |  | 0
36889 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-04-13 16:10 | 2000-04-13 17:54 | 2000-04-13 | BOTH STEAM GENERATOR PRESSURE TRANSMITTERS WOULD NOT BE AVAILABLE AS A RESULT OF A POSTULATED FIRE. It was discovered that the 2A Steam Generator pressure transmitter 2PT-469 would not be available as a result of a postulated fire event in the North Section of the Primary Auxiliary Building, 26 foot elevation. 2PT-469 is a redundant Appendix R instrument to 2PT-483, 2B Steam Generator pressure transmitter. 2PT-483 was already known to be lost due to this postulated fire event. The loss of both pressure transmitters places the plant outside the design basis for Appendix R. This was discovered during the Appendix R Rebaselining Project review. Compensatory actions include a fire watch in the appropriate fire zone within one hour of discovery and twice per shift thereafter. As a long term corrective action Point Beach is already pursuing a plant modification to re-route pressure transmitter 2PT-483 cables. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36888 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-04-13 15:35 | 2000-04-13 17:13 | 2000-05-25 | FEEDWATER ISOLATION VALVES MAY CLOSE FASTER THAN 1.5-SECOND DESIGN BASIS LIMIT. On March 21, 2000, Waterford Unit 3 determined that, based on a new calculation methodology and the latest stroke time data, the Feedwater Isolation Valves (FWIVs) FW-184 A (B) may close faster than the 1.5-second design basis limit. The physical plant was determined to be operable and the FWIVs would have performed their intended safety function at the time the condition was identified. An initial operability evaluation was made in accordance with procedure W4.101, which determined that the valves were operable at the time the evaluation was conducted. This was based on an engineering evaluation that determined that the faster closure of the FWIVs would not result in water hammer loads that would prevent the FWIVs and their associated penetrations from performing their required safety function. The engineering evaluation determined that the analyzed increase in fast valve closure (FVC) load is 57% for FW-184A and 52.9% for FW-184B. A subsequent evaluation was performed for FW-184A (B) to determine if at any time in the last two years the increase in FVC load may have exceeded the allowable loads determined by the engineering evaluation for W4.101. That evaluation determined on one occasion for FW-184A and six occasions for FW-184B, the percent increases for the FWIVs and subsequent stroke times exceeded the values provided in the operability determination On these occasions in question, closure of FW-184A (B) in response to the most adverse accident scenario could have potentially produced water hammer that may have exceeded the capability of piping supports in the FW system between the SGs and FW-184A (B). This may have resulted in the subsequent loss of containment isolation function of FW-184A (B). The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 05/25/00 AT 1630 ET BY CHRIS PICKERING TAKEN BY MACKINNON * * * Entergy is revising this event notification. The event was initially reported under 10CFR50.72(b)(2)(iii) as a condition that alone could have prevented fulfillment of a safety function. Based upon further review of the condition, Entergy has determined the condition is reportable under 10CFR50.72(b)(1)(ii)(B) as a condition that was outside the design basis of the plant. Evaluation of the event determined that the potential impact on containment integrity as a result of this condition does not affect the results of the currently analyzed MSLB event's radiological consequences. Further, the possibility of containment integrity loss due to excessive waterhammer loads during a FWLB remains bounded by the MSLB with respect to dose consequences. The FWLB event radiological consequences are bounded by the MSLB event, which is predicted to be within 10CFR100 limits. This event posed a containment integrity condition that was outside the design basis of the plant. An evaluation determined that the FWIVs could have potentially closed faster than their design basis minimum limit on seven occasions, six instances for FW-184A and one instance for FW-184B. The original event notification (above) incorrectly noted that there was one instance for FW-184A and six instances for FW-184B. The faster valve closure times could have placed increased loads on the piping and piping supports in the FW system between the steam generators (inside containment) and the FWIVs (outside containment). These increased loads were not accounted for in the design basis of the system. Based on this information, the event is reportable under 10CFR50.72(b)(1)(ii)(B) as a condition that was outside the design basis of the plant. The NRC Resident Inspector was notified of the event revision by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | OUTSIDE DESIGN BASIS |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(C) | 50.72(b)(1)(ii)(B) |  |  | 0
36887 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-04-13 10:04 | 2000-04-13 14:19 | 2000-04-13 | UNEXPECTED REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM ISOLATION DURING SURVEILLANCE TESTING "At 1004 on 04/13/00 during the performance of I&C STP 207-4539 (RCIC Isolation - RCIC steam supply pressure low channel functional test on E31 N685B) received a Division II isolation of the RCIC system. The isolation appears to be invalid. E51-F063 (RCIC Steam Supply Inboard Isolation Valve) and RCIC Trip and Throttle Valve went from open to closed as designed. Investigation is ongoing to determine the cause." RCIC was declared inoperable placing the unit in a 14-day LCO A/S. The licensee informed the NRC Resident Inspector. | 78 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36886 | 0 | MALLINCKRODT INC. |  |  |  | NUCLEAR PHARMACY | 2000-03-31 12:00 | 2000-04-13 13:59 | 2000-04-13 | EVENT THREATENS TO CAUSE A SHALLOW-DOSE EQUIVALENT TO THE LEFT HAND OF 250 RADS (2.5 Gy). The Mallinckrodt Radiation Safety Officer called in an immediate notification under 10 CFR 20.2202(a)(1)(iii). A Ring Badge from the right index finger of an employee had a reading of 5685 mrem. On 03/31/00 a Mallinckrodt employee working in the generator manufacturing line facility handled a column containing 19 curies of Mo-99 with his left hand. The individual was supposed to use forceps to manipulate needles inside the generator but instead used his fingers. The calculated dose to his right index finger tip is 31 rem at 1.5" from the source of activity. The employee recreated the event from which the licensee concluded that the finger tips of the left hand were intermittently in contact with the Mo-99 generator column over a span of 30 minutes. At this time the Radiation Safety Officer postulates that the dose to the fingers of the individual's left hand may exceed 250 rads. The individuals whole body dose has not been calculated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 3 | MO | FUE |  | 20.2202(a)(1) |  |  |  | 0
36885 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-04-12 13:47 | 2000-04-13 03:08 | 2000-04-13 | NRC BULLETIN 91-01, 24 HOUR REPORT The following is quoted from the licensee's report: 1-kg cylinders were discovered in the C-710 Isotopic Lab that violate the wall thickness design specification of NCSE 1493-03. The wall thickness credited in the NCSE is 0.109". Wall thicknesses of some cylinders were discovered as low as 0.065". The wall thickness is credited in the criticality safety calculations to demonstrate double contingency. SAFETY SIGNIFICANCE OF EVENTS: A design feature limitation credited to ensure double contingency was exceeded. Calculations demonstrate that greater than 240 cylinders using a wall thickness of 0.065" of optimally moderated UO2F2 solution are safe. There are a total of 95 1-kg cylinders in the three storage cabinets in the Isotopic Lab. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, the batch limitation would have to be exceeded by more than a factor of three. Additionally, the 1-kg cylinders would have to be filled with optimally moderated UO2F2 solution instead of the existing UF6. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing interaction and geometry controls. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): There are 95 1-kg cylinders in C-710 only some of which have been determined to have inadequate wall thickness. The assay of these cylinders varies from less than 1% U235 to approximately 4.6% U235. The material contained in these cylinders is UF6. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on interaction control through the application of batch limits. This control was not violated and the first leg of double contingency was maintained. The second leg of double contingency is based on geometry control. This is controlled through implementation of design specifications for the 1-kg cylinder. The actual wall thickness was discovered to be less than that credited in the design features. Therefore, the geometry process parameter limit was exceeded. The geometry process parameter was violated, therefore double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: This area is being controlled to ensure that no fissile material is moved within two feet of this storage area. NCS is in the process of developing a remediation plan to correct this condition. NUCLEAR CRITICALITY SAFETY CONTROLS INVOLVED AND THEIR IMPACT ON DOUBLE CONTINGENCY: Double contingency for this scenario is established by implementing interaction and geometry controls. The first leg of double contingency relies on interaction control through the application of batch limits. This control was not violated and the first leg of double contingency was maintained. The second leg of double contingency is based on geometry control, This is controlled through implementation of design specifications for the 1-kg cylinder. The actual wall thickness was discovered to be less than that credited in the design features. Therefore, the geometry process parameter limit was exceeded. The geometry process parameter was violated therefore double contingency was not maintained. POTENTIAL CRITICALITY PATHWAYS INVOLVED; In order for a criticality to be possible, the batch limits would have to be exceeded by more than a factor of three. Additionally, the 1-kg cylinders would have to be filled with optimally moderated UO2F2 solution instead of the existing UF6. SAFETY SIGNIFICANCE OF INCIDENT: A design feature limitation credited to ensure double contingency was exceeded. Calculations demonstrate that greater than 240 cylinders using a wall thickness of 0.065" of optimally moderated UO2F2 solution are safe. There are a total 95 1-kg cylinders in the three storage cabinets in the Isotopic Lab. EXCLUSION ZONE AND POSTINGS: Post the area as follows in accordance with CP2-EG-NS1031. Ensure all four sides including areas on opposite sides of adjacent walls less than 2-feet from the storage cabinets. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36884 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2000-04-12 14:30 | 2000-04-12 18:46 | 2000-04-12 | POTENTIAL TO CAUSE AN OVEREXPOSURE This report is based on the potential to cause an exposure in excess of 25 REM. No actual over-exposure occurred. The licensee moved fuel into the fuel pool. This caused a high radiation alarm to be sounded in a room adjacent to the fuel pool. The licensee investigated and determined that the cause of the alarm was that some concrete shielding had been removed from the side of the pool. The shielding had been removed so that an inspection of the fuel pool liner could be performed. A 2 foot by 2 foot piece of shielding was removed from the wall, which is four feet thick. After verifying that the room was not occupied, the licensee moved the fuel to a safe portion of the pool The licensee reported radiation measurements of 200 R/HR in the area where the shield was removed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 3 | MO | NPR |  | 20.2202(a)(1) |  |  |  | 0
36883 | -1 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2000-04-12 14:10 | 2000-04-12 17:57 | 2000-04-18 | LEAK IN THE HPCI TEST RETURN HEADER TO THE CONDENSATE STORAGE TANK On 4/12/2000, at 14:10 while performing 2-SR-3.5.1 .7, HPCI Main and Booster Pump Set Developed Head and Flow Rate Test at Rated Reactor Pressure, the Unit Operator (UO)observed unstable HPCI suction pressure, followed by an auto swap of the suction from the Condensate Storage Supply to the Suppression Pool. The UO then observed annunciator, 'HPCI PUMP SUCT CONDENSATE HDR LEVEL LOW'. HPCI was tripped and declared inoperable. Subsequently a leak was discovered on the HPCI Test Return header to the CST. The leak has been isolated. Unit conditions are stable. The licensee notified the NRC resident inspector. * * * RETRACTION 1815 4/18/2000 FROM TIM GOLDEN TAKEN BY BOB STRANSKY * * * "TVA is retracting this report. Subsequent investigation into the cause of this event determined that the source of the leak was a separated weld in a non-safety related portion of the test return flowpath to the condensate storage tank. Testing and engineering analyses performed after the event demonstrated that the conditions which caused the event would not have prevented HPCI from performing it's safety function if required. Specifically, if HPCI had been called upon to mitigate an actual event, automatic closure of the test return control valve would have isolated the leak, thereby establishing a safety injection flow path to the reactor vessel. Therefore, this event is not reportable with respect to 10CFR50.72(b)(2)(iii) and is hereby retracted. The senior NRC resident inspector has been informed." Notified R2DO (Boland). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(C) | 50.72(b)(2)(iii)(D) |  | 0
36882 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-04-12 10:54 | 2000-04-12 12:58 | 2000-04-12 | REACTOR TRIP "At 1054, a manual reactor trip was performed due to a turbine runback due to the Valve Position Limiter (VPL) going down outside of the Operators' control. The trip was performed when a previously identified limit on turbine load was reached. An Electrohydraulic Control (EHC) card was being replaced at the time of the runback in accordance with SC.IC-GP.EHC.0002(Z), General Troubleshooting for Main Turbine EHC System as an Infrequently Performed Test or Evolution (IPTE). This card was being replaced to fix a previously identified slow drift downward of the VPL. An Aux Feedwater (AFW) Autostart signal was received due to low S/G level due to normal shrinkage of S/G levels for normal post trip response. All safety systems performed as designed. Source Range Nuclear Instrument (SRNI) N-31 and 14 Service Water Pump were out of service prior to the trip, SRNI N-32 performed as designed. At this time, the unit is stable in Mode 3." All control rods fully inserted following the trip. The main condenser remains in service with decay heat being removed via the bypass valves. The licensee informed Lower Alloways Creek (LAC) Township and the NRC Resident Inspector and will inform the state of New Jersey. | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36881 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2000-04-11 13:00 | 2000-04-12 11:36 | 2000-04-12 | AGREEMENT STATE REPORT - STOLEN TROXLER ROOF MOISTURE GAUGE The Illinois Department of Nuclear Safety reported the theft of a Troxler roof moisture gauge, model # 3216 (serial # 140) from a state licensee. It was stolen from a locked vehicle at 6929 S. Crandon in Chicago, Illinois. The gauge contains 40 mCi of Am-241/Be. The licensee is in contact the Chicago police department. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36880 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-04-10 09:47 | 2000-04-10 21:03 | 2000-04-10 | SAFETY EQUIPMENT FAILURE (CRITICALITY ALARM SYSTEM TROUBLE) "At 0947 CDT on 04/10/00, the Plant Shift Superintendent was informed of a trouble alarm on the C-337A Criticality Accident Alarm System (CAAS) cluster. Investigation of trouble alarm revealed that all three modules on the 'N' CAAS cluster were in a 'Fault' condition. With all three modules in this condition, the system was unable to perform its intended safety function, rendering the system inoperable. The system is required to be operable according to TSR 2.2.4.3 for the current mode of operation in twelve rad areas covered by CAAS systems. Overlapping coverage for the C-337A facility was provided by the C-337 'X' and 'V' CAAS clusters. However, the C-360/C-337 tie line CAAS coverage is provided by the 'N' cluster. The system was inoperable for approximately seven minutes until it could be reset per procedure. A portion of the C-337/C-360 tie line was without CAAS coverage as required by TSR 2.2.4.3 during the time of cluster inoperability." The NRC Senior Resident Inspector has been notified of this event. (Refer to event #36934 for an event discovered during investigation of this issue.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
36879 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-04-10 14:00 | 2000-04-10 20:57 | 2000-04-10 | NRC BULLETIN 91-01, 24 HOUR REPORT "AT 1400 HOURS ON APRIL 10, 2000, X-710 LABORATORY PERSONNEL WERE CONDUCTING A SELF ASSESSMENT REVIEW OF NCSA-710-025.A00 (HANDLING AND STORAGE OF SAMPLES FROM ES&H ANALYTICAL LABS) WHEN THEY DISCOVERED THAT REQUIREMENT #4 (SPACING) WAS NOT BEING MAINTAINED IN A SPECIFIED STORAGE AREA WITHIN THE FACILITY. REQUIREMENT #4 STATES: 'A MINIMUM SPACING OF TWO FEET SHALL BE MAINTAINED BETWEEN GROUPS OF SAMPLES, EXCLUDING EXEMPTED SAMPLES.' THE FACT THAT THIS REQUIREMENT WAS NOT BEING MAINTAINED RESULTED IN A LOSS OF ONE CONTROL (SPACING). THIS CONSTITUTES A LOSS OF CONTROL 'A' (SPACING) AS IDENTIFIED IN THE DOUBLE CONTINGENCY MATRIX A/B.7.1. CONTROL 'B' (MASS + VOLUME + ENRICHMENT) WAS MAINTAINED THROUGHOUT THIS EVENT. "AT THE DIRECTION OF THE PLANT SHIFT SUPERINTENDENT, THE REQUIREMENTS FOR AN ANOMALOUS CONDITION WERE ESTABLISHED PER PLANT PROCEDURES. AT 1630 HOURS ON 04/10/2000, DOUBLE CONTINGENCY CONTROLS WERE REESTABLISHED (SPACING) UNDER THE DIRECTION OF ONSCENE NUCLEAR CRITICALITY SAFETY PERSONNEL. "AT THE DIRECTION OF THE PLANT SHIFT SUPERINTENDENT, THE X-710 MANAGEMENT STAFF WILL CONDUCT BRIEFINGS WITH THE RESPECTIVE PERSONNEL TO PREVENT RECURRENCE." THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. SAFETY SIGNIFICANCE OF EVENT: The safety significance of this event is very low. The group involved contained a maximum of 82 grams of U235 which is less than 11% of minimum sub-critical mass at 100% enrichment. Groups of samples with or > or += 500 ppm U235 are supposed to be controlled in separate safe mass groups spaced apart from the samples with < 500 ppm U235. In this event two groups were not spaced as required. POTENTIAL CRITICALITY PATHWAYS INVOLVED BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Additional mass would be required and/or additional spacing violations would be required before a criticality would be possible. A mass of 760 grams U235 of sub-critical with optimum moderation, optimum geometry, and reflection according to ANSI/ANS-8.1 CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Mass and spacing were the controlled parameters. The spacing control was lost when the group of samples containing the > or = 500 ppm U235 sample was stored too close to a group of samples with < 500 ppm U235. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED ,MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The amount of material is approximately 82 grams U235 based on a very conservative estimate for U235 mass. This represents 11% of the minimum sub-critical mass. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Mass and spacing are the applicable controls. The spacing control was lost when two sample groups were stored without the required 24" minimum spacing. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Under the direction of the Nuclear Criticality Safety Staff control was re-established (spacing) at 1630 hours. Plant Shift Superintendent directed facility management to conduct crew briefings prior to restart of operations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36878 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-04-09 10:00 | 2000-04-09 12:32 | 2000-04-10 | LOSS OF BOTH VITAL BUSES DURING 'B' TRAIN LOAD SHED TESTING At 1000 CDT, during Unit 1 'B' train load shed testing (performed every 18 months during a refueling outage), the 'A' startup transformer tripped, resulting in a loss of offsite power to both trains of Unit 1 vital buses, the autostart of 'A' train emergency diesel generators (EDGs) which reenergized the 'A' train buses, and the sustained deenergization of the 'B' train vital buses. At the time of this event, Unit 1 was defueled, with the 'B' train service water system out of service and the 'B' train EDG unavailable to Unit 1. Both trains of Unit 1 vital power were aligned to the '1A' startup transformer as part of the load shed test that was in progress. The loss of the '1A' startup transformer coincided with, and appears to be associated with, the removal of a jumper from a 'B' train sequencer relay. Investigation of this apparent cause is continuing. The 'A' train vital buses were immediately restored to service by the 'A' train EDGs. At 1018 CDT, spent fuel pool cooling was manually restored. Spent fuel pool temperature remained at 98°F throughout this event. At 1019 CDT. the 'B' train buses were manually reenergized from the '1B' startup transformer. At 1053 CDT, the 'A' train buses were transferred from the EDGs to offsite power. Unit 2 remains at 100% power and is unaffected by this event. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1615 ON 4/10/00, BY COLLINS RECEIVED BY WEAVER * * * The following is an update to the above non-emergency report: The purpose of this emergency notification is to retroactively declare and terminate a Notice of Unusual Event (NOUE) that occurred on April 9, 2000. As of 1000 CDT on April 9, 2000, a NOUE was declared due to a loss of offsite power to the Unit 1 vital buses. The emergency declaration was terminated at 1019 CDT on April 9, 2000 at which time one train of vital power was reestablished from offsite power supply. During this event, one train of vital power was automatically supplied from an EDG. At the time of the event, Unit 1 was defueled. The 'B' train EDG was not available due to routine outage activities and the Unit 1 'A' startup transformer was supplying both trains of vital buses from offsite power. At 1000 CDT on April 9, 2000, the Unit 1 'A' startup transformer tripped for unknown reason, resulting in a loss of power to both trains of vital electrical buses. Both 'A' train EDGs automatically started and reenergized the Unit 1 'A' train vital buses within seconds. The Unit 1 'B' train vital buses remained deenergized for about 19 minutes until the Unit 1 'B' startup transformer was aligned by the operators to supply power to them. The cause of the Unit 1 ' A' startup transformer trip is unknown and being investigated. This event resulted in a brief loss of spent fuel pool cooling. Spent fuel pool cooling was restored by the operators at 1018 CDT on April 9, 2000 in accordance with plant procedures. The temperature of the spent fuel pool remained constant at 98°F throughout this event. Following a walkdown for faults, the Unit 1 'B' train vital buses were reenergized from offsite power at 1019 CDT from the Unit 1 'B' startup transformer. Offsite electrical power was restored to the 'A' train vital buses at 1053 CDT and the EDGs were secured and returned to normal standby alignment. The operations shift crew evaluated this event and reported it to the NRC as a four hour non-emergency report per 10CFR50.72. The operations shift crew recognized the momentary loss of power to the vital buses but after reviewing the emergency implementation procedures and Technical Specifications concluded that a loss of both trains of offsite power had not occurred. That was concluded since the operators were readily able to align the Unit 1 'B' startup transformer to supply the 'B' train vital buses. Further evaluation of the event on April 10, 2000, concluded that a NOUE was appropriate since offsite power was momentarily lost to the vital electrical buses. Unit 2 remained at 100% power during this event and was unaffected by this event. The licensee informed the NRC resident inspector of this notification. The NRC Operations Officer notified the R2DO (Cahill), NRR EO (Marsh), IRO (Giitter) and FEMA (Steindruff). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | ESF ACTUATION |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a)(1)(i) | 50.72(b)(2)(ii) |  |  | 0
36877 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-04-07 15:33 | 2000-04-07 19:11 | 2000-04-07 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO A DROPPED CONTROL ELEMENT ASSEMBLY (CEA). On April 7, 2000, around 1319 PDT, an alarm was received for a control element drive mechanism control system timer. In response to this alarm, plant operators began moving control rod subgroup 20 to the "hold" bus (4 rods on the hold bus). Shortly thereafter, CEA #84 (a full length CEA and part of shutdown bank B) dropped into the reactor core. Technical Specification (TS) 3.1.5, "Control Element Assembly Alignment" requires all full length CEAs to be aligned to within 7 inches of all other CEAs in its group. If this requirement can not be met within 2 hours, Action B of TS 3.1.5 requires Southern California Edison to initiate a plant shutdown. Plant operators initiated actions to realign CEA #84 with the remainder of its group. However, to minimize potential adverse affects to the fuel, reactor engineers have recommended a CEA withdrawal rate which will not allow CEA #84 to be realigned with the remainder of its group within 2 hours allowed by TS 3.1.5. Consequently, at 1533 PDT, Southern California Edison initiated a power reduction of San Onofre Unit 3. At 1557 PDT, CEA #84 was realigned to within 7 inches of the remainder of its group before completion of plant shutdown. Southern California Edison believes there is no safety significance to this event as all system operated as required. The cause of this event is under investigation. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 74 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36876 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-04-07 10:14 | 2000-04-07 18:07 | 2000-04-07 | POWER EXCURSION TO 104% OF THERMAL RATED POWER Power excursion to 104% occurred when a deaerator level channel was improperly removed from service for calibration and caused a loss of deaerator level and pressure control. This resulted in an increase in feedwater and steam flow to the deaerator, which in turn caused reactor power to increase above rated values. Operators took action to terminate the transient and stabilized Unit 2 at 99% power. The length of the excursion was approximately 3 minutes. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
36875 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-04-07 14:05 | 2000-04-07 17:54 | 2000-04-07 | BLOWN FUSE CAUSED A PARTIAL SYSTEM ISOLATION A partial system isolation occurred on the containment instrument gas system and the drywell chilled water system. The cause of the partial isolation is a blown fuse. At the time of this event, Unit 1 was in Operational Condition 5 undergoing refueling. There was no release of radiation or loss of vessel inventory or shutdown cooling. Proper system response is being verified. The fuse will be replaced and all valves will be placed back in their proper position. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36874 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-04-07 16:15 | 2000-04-07 17:56 | 2000-04-07 | RECEIVED PARTIAL GROUP 1 (MSIVs) AND GROUP 2 (Primary Containment) OUTBOARD ISOLATIONS. Received a partial Group 1 and Group 2 outboard isolation which caused 13 outboard isolation valves to close. The following outboard isolation valves closed: 4 hydrogen and oxygen sample valves, 3 Fission Product Monitor sample valves, Drywell floor drain valve, Drywell equipment drain valve, Drywell Air Purge and Vent line valves, Primary Coolant Sample line valve, and a Main Steam Line drain valve. All the outboard valves belong to Group 1 except for the last two listed which belong to Group 2. Electricians were replacing covers on divisional separation wiring trays in the outboard isolation panel 2H11-P623. Insulation on a wire was damaged causing a fuse to blow. An evaluation is in progress to determined if the wire can be tapped or a new wire will be installed. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36873 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-04-07 14:00 | 2000-04-07 17:15 | 2000-04-13 | "C" MAIN STEAM LINE FAILS LOCAL LEAK RATE TEST DUE TO EXCESSIVE LEAKAGE During Local Leak Rate Testing (LLRT) of the "C" Main Steam Line, the as-found leakage could not be quantified. Technical Specification surveillance requirement, SR 3.6.1.3.12 limit of less than 100 scfh combined MSIV leakage rate for all four main steam lines when tested at greater than 25 psig was exceeded. Fermi 2 Main Steam Lines are equipped with a Main Steam Line Isolation Valve Leakage Control System (MSIVLCS) which is designed to maintain pressure between the MSIVs slightly above that of primary containment. Since the leakage could not be quantified, it could not be demonstrated that the leakage did not exceed the capacity of the MSIVLCS. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 04/07/00 AT 1836 EDT BY S. MAREK TAKEN BY MACKINNON * * * During LLRT of the "D" Main Steam Line, the as-found leakage could not be quantified. Technical Specification surveillance requirement, SR 3.6.1.3.12 limit of less than 100 scfh combined MSIV leakage rate for all four main steam lines when tested at greater than 25 psig was exceeded. Fermi 2 Main Steam Lines are equipped with a MSIVLCS which is designed to maintain pressure between the MSIVs slightly above that of primary containment. Since the leakage could not be quantified, it could not be demonstrated that the leakage did not exceed the capacity of the MSIVLCS. The "A" & "B" Main Steam Lines passed their LLRT. The NRC Resident Inspector was notified of this update by the licensee. R3DO (T. Kozak) was notified. * * * UPDATE AT 0931 ON 4/12/2000 FROM S. MAREK TAKEN BY STEVE SANDIN * * * "During Local Leak Rate Testing (LLRT) of Main Steam Line drain valve, B2103F019, the as found leakage was 232.7 SCFH, the allowable leakage is 1.00 SCFH. "The leakage through this penetration X-8 of 232.7 SCFH exceeds Technical Specification surveillance requirement, SR 3.6.1.3.11 Bypass Leakage Total limit of less than 0.04 La, (11.9) SCFH. The total containment leakage is 274.62 SCFH. which is less than 1.0 La of 297.30 SCFH. "This report is being made in accordance with 10CFR 50.72(b)(2)(i), any event or condition found while the reactor is shutdown that, had it been found while the reactor was in operation, would have resulted in the nuclear plant, including its principal safety barriers, being seriously degraded or being in an unanalyzed condition that significantly compromises plant safety." The NRC resident inspector has been informed of this update by the licensee. Notified R3DO (Hiland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36872 | -1 | ST LOUIS UNIVERSITY HOSPITAL |  |  |  |  | 2000-04-06 17:36 | 2000-04-07 16:42 | 2000-04-10 | MEDICAL MISADMINISTRATION A patient on a ventilator was being treated with a High Dose Radiation Remote Afterloader when the patient intervened causing a jarring motion which caused the patient's catheter to come part way out. The catheter came part way out after 13 of 14 dwell positions had been completed. Just before the commencement of the 14th dwell position the catheter was pulled out and the physicist immediately intervened and retracted the source such that the 14th dwell position was underdosed between 10 and 60%. The worst case is that the 14th dwell position, which was outside of the tumor volume, would have received as little as 40% of the original planned dose at that location. NRC Region 3 (Kevin Null) was notified of this event by the licensee. * * * UPDATE AT 1215 ON 04/10/00 BY DAWSON RECEIVED BY WEAVER * * * The licensee has requested that this event be retracted after discussions with NRC Region III. The dose did not deviate by greater than 20% from the intended dose and no dose was delivered to unintended sites. The NRC Operations Officer notified the R3DO (Hiland) and NMSS (Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.33 |  |  |  | 0
36871 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-04-06 12:05 | 2000-04-06 14:02 | 2000-04-06 | SPENT FUEL POOL STORAGE RACKS BORAFLEX DEGRADING. An evaluation of a preliminary report on the Spent Fuel Pool storage racks Boraflex testing determined that degradation is occurring. Some racks might not be able to receive fuel and ensure the Technical Specification requirement of maintaining Keff <= to 0.95 with un-borated water could be assured. Administrative controls will ensure that Keff is maintained <= to 0.95. The design of the fuel racks was to allow full core off-loads for the term of the license. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36870 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-04-06 10:00 | 2000-04-06 12:38 | 2000-04-06 | GROUP 1 ISOLATION OCCURRED DURING MAIN TURBINE CONTROL TESTING WHICH CAUSED THE REACTOR COOLANT SAMPLE VALVES TO CLOSE. During performance of Main Turbine Control testing, a Group 1 isolation occurred which caused Reactor Coolant sample valves 2B31 F019 & F020 (0.75" line; 1.0" valves) to close. One of the jumpers installed during the Main Turbine Control test made the Main Turbine Logic think that the generator was tied to the line. This caused the Main Turbine speed control to go to 1800 RPM because the main turbine speed control was selected to 1800 RPM instead of all valves closed. When the operator reset the Main Turbine, all 4 Main Turbine Stop Valves opened as a result of the speed control being selected to 1800 RPM. A Group 1 isolation occurred due to the Main Turbine stop valves opening coincident with a low Main Condenser Vacuum. Only the Reactor Coolant Sample Valves closed. Main Steam Isolation valves and the Main Steam line drain valves remained closed during the Group 1 isolation. The licensee is continuing the Main Turbine Control Test. The NRC Resident Inspector was notified of the event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36869 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-04-05 12:52 | 2000-04-05 14:38 | 2000-04-05 | 1 HOUR SECURITY REPORT Unescorted protected area access granted inappropriately. Immediate compensatory measures taken. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Center for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 0
36868 | 0 | U.S. NAVY |  |  |  |  | 2000-04-04 15:30 | 2000-04-05 13:00 | 2000-04-06 | STRONTIUM/YTTRIUM SOURCE LOST TO LANDFILL A generally licensed strontium/yttrium source, 500 mCi, from an 'In Flight Blade Inspection System' was improperly placed in a dumpster which in turn was dumped at a regular land fill. The U.S. Navy is investigating the incident and trying to determine where and how deep the source is in the land fill. The U.S. Navy notified NRC Region 2 (M. Fuller) and intends to notify the State of Arizona. ****************** UPDATE AT 0814 ON 04/06/00 FROM GARY HIGGINS TO LEIGH TROCINE ****************** The licensee called to provide the following correction to the original report: The licensee reported that they were provided with an incorrect activity for the missing source. They were originally informed that the activity was 500 mCi when in fact the actual activity was 500 µCi. The licensee notified the NRC Region 2 office (Mike Fuller). The NRC operations officer notified the R2DO (Cahill), R4DO (Jones), and NMSS EO (Sturz). (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AZ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36867 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-04-05 09:38 | 2000-04-05 12:30 | 2000-04-05 | TWO CONTAINMENT ISOLATION VALVES CLOSED DUE TO BLOWN FUSES The Nuclear Safety and Compliance Group notified Operations today that a report of ESF activation should be made to the NRC. The group noted that during the review of a logic system functional testing on diesel generator 2R43-S001A, a logic power fuse (2A71-F21A) blew closing two primary containment isolation valves (2G11-F003 & 2G11-F019). These valves are the inboard drywell sump isolation valves. This occurred on 4/2/00 at 0030 EDT. The system was checked, fuses replaced, and the valves opened. The valves are fully operational. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36866 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-04-04 16:30 | 2000-04-04 18:23 | 2000-04-04 | CALIBRATION CONSTANT INACCURACY MAY HAVE CAUSED THE UNIT TO EXCEED LICENSED LIMIT During calibration of main feedwater flow instruments, the licensee determined that a calibration constant that converts differential pressure to flow was not updated when the unit was re-rated in October 1998. The result of the change not being made may have resulted in a power determination such that actual power exceeded the licensed thermal limit by approximately 3.5 megawatts thermal. An investigation is ongoing to determine the full implications of the inaccurate calibration constant. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36865 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-04-04 15:45 | 2000-04-04 16:17 | 2000-04-04 | LICENSEE RECEIVED NOTICE FROM THE NEW YORK STATE DEPARTMENT OF ENVIRONMENTAL CONSERVATION OF A VIOLATION OF THE "STATE POLLUTANT DISCHARGE ELIMINATION PERMIT" The licensee received a fax notification of a violation of their 'State Pollutant Discharge Elimination Permit' from the New York State Department of Environmental Conservation. On 3/27/00, during maintenance on yard drains, a vacuum truck was used to suck water from one drain and discharged to another drain. The 'Permit' requires that the water be treated before discharge to a drain. The licensee intends to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0
36864 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-04-04 11:48 | 2000-04-04 12:25 | 2000-04-05 | LOSS OF RESERVE STATION TRANSFORMER CAUSED LOSS OF REACTOR COOLANT PUMP WHICH REQUIRED A REACTOR TRIP The 'C' reserve station transformer (RST) deenergized which resulted in a loss of the Unit 2 'C' reactor coolant pump (RCP). The Unit 2 loss of RCP 'C' required a reactor trip, which was initiated manually, all rods fully inserted and the plant is stable in Hot Standby. Unit 2 was on the steam dumps to the condenser and main feedwater at the time of the trip and continue on them. Unit 1 '1H' emergency bus was lost due to the problem with the 'C' RST and the failure of the '1H' emergency diesel generator (EDG) to start. The loss of the '1H' bus caused the loss of the 'C' RCP and 'A' Residual Heat Removal (RHR) pump, which led to the loss of core cooling circulation, but was restored in less than 2 minutes by starting the 'B' RHR pump. The 'C' RST and the '1H' EDG problems are being investigated, the cause of the problems are unknown at this time. Unit 2 will remain in Hot Standby until all problems are corrected. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1503 EDT ON 4/5/00 BY JIM CROSSMAN TO FANGIE JONES * * * The licensee made a correction to the reporting criteria. Removed the original criteria of 10 CFR 50.72(b)(1)(ii) Degraded Condition During Operation, this was for Unit 1 which was shutdown at the time. Added the criteria 10 CFR 50.72(b)(2)(ii) ESF Actuation, due to a real start signal to two of the emergency diesel generators. The licensee notified the NRC Resident Inspector. Notified R2DO (Steve Cahill). | 0 | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION | ESF ACTUATION |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Hot Standby |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(1)(i)(A) | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  | 0
36863 | 0 | PALISADES | 1 |  |  | [1] CE | 2000-04-04 06:32 | 2000-04-04 10:10 | 2000-04-04 | MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEEDWATER While racking out the emergency diesel generator (EDG) 1-1 output breaker, the breaker was inadvertently closed, motorizing the 1-1 EDG and causing a momentary undervoltage condition on emergency busses 1C and 1D. The undervoltage condition caused both EDGs to automatically start, and caused the instrument AC bus to transfer to an alternate source. During the transfer, the cooling tower pumps and heater drain pumps tripped. Loss of the heater drain pumps caused the main feedwater pumps to trip. Reactor coolant pumps remained running throughout the event. Operators manually tripped the reactor, and all control rods inserted completely. The auxiliary feedwater system automatically started following the trip due to low steam generator water levels. The unit is currently stable in Hot Standby, with decay heat being removed using the steam generator (S/G) atmospheric dump valves, and S/G levels being maintained using the auxiliary feedwater system. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36862 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-04-04 07:24 | 2000-04-04 09:31 | 2000-04-04 | NONESSENTIAL SERVICE WATER SYSTEM ISOLATION At 0724, valves associated with the nonessential portion of the Division I service water system closed unexpectedly. Less than a minute later, three of the four running service water pumps tripped due to low flow. The running pump provides sufficient flow for required safety related loads. Plant operators entered procedures appropriate for nonessential service water system header isolation. Initial walkdowns of the Division I service water piping and electrical systems did not reveal any obvious problems with the system. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36861 | 0 | PPG ARCHITECTURAL FINISHES, INC |  |  |  |  | 2000-04-03 | 2000-04-03 13:20 | 2000-05-03 | 10 CFR PART 21 REPORT "This notification is being made by PPG Architectural Finishes, Inc (PPG) concerning relatively small quantities of a silicon stainless steel enamel coating used inside primary containment supplied to a single utility which is a NRC nuclear power plant licensee. The coating was not appropriately controlled such that its formulation changed from that which was originally supplied. The utility has been informed and is working with PPG. Further investigation is being conducted which may result in the withdrawal or modification of this notification. Written notification in accordance with 10 CFR § 21.2 1(d)(3)(ii) will follow." * * * UPDATE AT 1640 ON 05/03/00 BY JOSEPH M. KARAS, PPG INDUSTRIES, INC TO JOLLIFFE * * * Exterior silicone stainless steel enamel coating #8674 qualified for Coating Service Level I Exposure in 1980 by PPG Industries, Inc, Keeler & Long Division, was supplied as a commercial grade item (not included in the supplier's Quality Assurance Program) to Duke Energy Company Nuclear Facilities, Catawba, McGuire and Oconee. This coating is being used inside containment on piping that is contained by mirror insulation which should minimize the potential for paint chip fouling of sump pumps thereby interfering with the operation of Emergency Core Cooling Systems in the event of a DBA incident. The NRC Operations Officer notified the R2DO Bob Haag and NRR Vern Hodge (by fax). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0
36860 | 0 | GE PLASTICS |  |  |  |  | 2000-03-29 | 2000-04-03 13:28 | 2000-04-03 | MISSING 15 mCi NICKEL-63 SOURCE The licensee discovered that a HP model 5890 Gas Chromatograph (serial # 2541A06448), containing a 15 mCi Ni-63 source, was missing from the excess equipment storage on site. The source is contained within an electron capture detector. A search of the entire site was completed on 3/29/00 without finding the device. A written report will be made within thirty days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
36859 | 0 | GEORGIA INSTITUTE OF TECHNOLOGY |  |  |  | 5000 KW RESEARCH HW | 2000-04-03 09:49 | 2000-04-03 10:49 | 2000-04-05 | SAFEGUARDS SYSTEM DEGRADATION RELATED TO DETECTION/MONITORING/ALARM FUNCTIONS.. COMPENSATORY MEASURES TAKEN IMMEDIATELY UPON DISCOVERY. CONTACT THE OPERATIONS CENTER FOR ADDITIONAL INFORMATION. * * * UPDATE AT 1507 EDT ON 4/5/00 BY ROD ICE TO FANGIE JONES * * * Normal safeguards systems are restored. Notified R2DO (Steve Cahill) and NRR (Ed Goodwin). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | GA | NPR |  | 73.71(b)(1) |  |  |  | 0
36858 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-04-03 08:45 | 2000-04-03 10:43 | 2000-04-17 | HIGH ENERGY LINE BREAK ANALYSES (HELB) REQUIRE DOORS IN AREAS CONTAINING MAIN STEAM LINES NOT BE BLOCKED OR OBSTRUCTED "DOORS 155/177 OBSTRUCTED BY SCAFFOLDING CAUSING DOORS TO BE PARTIALLY BLOCKED. DUE TO HELB CONSIDERATIONS, DOORS NEED TO BE ABLE TO SWING OPEN FULLY. SCAFFOLDING WAS MOVED AT 0925 CDT." THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. * * * RETRACTED AT 1130 EDT ON 4/17/00 BY WILLIAM MATHER TO FANGIE JONES * * * "Northern States Power Company's Nuclear Analysis Department (NAD) completed calculations based on the doors being blocked and as a result of these calculations is withdrawing the Event Notification #36858." The analysis indicates that there is no significant effect on peak pressure during the analyzed event. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO (Patrick Hiland). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36857 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-04-03 08:57 | 2000-04-03 10:02 | 2000-04-03 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP DUE TO STATION SERVICE TRANSFORMER FAULT "REACTOR TRIP CAUSED BY LOSS OF 'C' STATION SERVICE TRANSFORMER DUE TO A FAULT. THE AUXILIARY FEEDWATER SYSTEM ACTUATED AS DESIGNED." THE LICENSEE'S PRELIMINARY EVAULATION OF THE TRANSFORMER FAULT INDICATES INSULATION FAILURE. FOLLOWING THE TRIP, NO PRIMARY/SECONDARY SAFETIES OR RELIEFS LIFTED. ALL CONTROL RODS FULLY INSERTED. ALL (3) AFW PUMPS STARTED AS DESIGNED SUPPLYING MAKEUP TO THE STEAM GENERATORS. THE MAIN CONDENSER IS IN SERVICE ACTING AS A HEAT SINK FOR DECAY HEAT REMOVAL. ALL ELECTRICAL LOADS REMAINED ENERGIZED WITH OFFSITE POWER SUPPLIED THROUGH THE RESERVE STATION TRANSFORMER. THE EMERGENCY DIESEL GENERATORS ARE AVAILABLE, IF NEEDED. UNIT 2 WILL REMAIN IN MODE 3 PENDING THE RESULTS OF THE INVESTIGATION INTO THE TRANSFORMER FAULT. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. * * * UPDATE 1052EDT ON 4/3/00 FROM MUNDEN TO S.SANDIN * * * "AUXILIARY FEEDWATER SYSTEM AUTOMATIC ACTUATION [1014EDT] FOLLOWING SECURING DUE TO LOW-LOW LEVEL IN 'C' STEAM GENERATOR." THE AFW SYSTEM HAS BEEN SECURED WITH MAIN FEED IN SERVICE USING THE BYPASS VALVES. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. NOTIFIED R2DO (JULIAN). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36856 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-04-02 09:17 | 2000-04-02 09:38 | 2000-04-02 | UNUSUAL EVENT DECLARED DUE TO LOSS OF THE EMERGENCY RESPONSE FACILITY INFORMATION SYSTEM (ERFIS) FOR GREATER THAN 4 HOURS AT 0917EDT THE LICENSEE DECLARED AN UNUSUAL EVENT BASED ON EMERGENCY ACTION LEVEL (EAL) 6-2-1, "INABILITY OF ERFIS TO PERFORM ITS INTENDED FUNCTION FOR A CONTINUOUS PERIOD OF 4 HOURS." BOTH THE "A" AND "B" PLANT PROCESS COMPUTERS WHICH SUPPLY INPUT DATA TO ERFIS WOULD NOT REBOOT FOR REASONS UNKNOWN. ADDITIONAL INFORMATION TECHNOLOGY (IT) STAFF HAS BEEN BROUGHT IN TO RESOLVE THE FAILURE. THE LICENSEE HAS IMPLEMENTED MONITORING ON REDUNDANT EQUIPMENT IN ACCORANCE WITH TECH SPEC REQUIREMENTS. THE UNIT IS CURRENTLY STABLE AT 100% POWER. THE LICENSEE INFORMED STATE AND COUNTY AGENCIES AND WILL INFORM THE NRC RESIDENT INSPECTOR. * * * UPDATE AT 1644 ON 4/2/00, BY LOWE RECEIVED BY WEAVER * * * The licensee terminated the Unusual Event at 1630 after having repaired and tested the ERFIS system. The licensee informed the NRC resident inspector as well as state and county agencies. The Operations Center notified the RDO (Julian), EO (Zwolinski) and FEMA (Cegielski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a)(1)(i) |  |  |  | 0
36855 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-04-02 05:05 | 2000-04-02 07:25 | 2000-04-05 | 1 HOUR SECURITY REPORT UNESCORTED PROTECTED AREA ACCESS GRANTED INAPPROPRIATELY. IMMEDIATE COMPENSATORY MEASURES TAKEN. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. CONTACT THE HEADQUARTERS OPERATIONS CENTER FOR ADDITIONAL DETAILS. * * * UPDATE 0955EDT ON 4/2/00 FROM VINCE MURPHY TO S.SANDIN * * * THE LICENSEE PROVIDED ADDITIONAL SPECIFIC INFORMATION. A REVIEW WILL BE PERFORMED ON MONDAY 4/3 TO DETERMINE REPORTABILITY. NOTIFIED R2DO (JULIAN). * * * RETRACTED AT 1420 EDT ON 4/5/00 BY VINCE MURPHY TO S. SANDIN * * * After review of the incident, it was determined that there was no improper unescorted protected area access granted, thus this event notification is retracted. The licensee notified the NRC Resident Inspector. Notified R2DO (Steve Varley). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 0
36854 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-04-01 19:15 | 2000-04-01 22:28 | 2000-04-01 | REACTOR SCRAM On Saturday 4/1/2000, at 1200 hours, control room operators commenced a planned unit shutdown in preparation for refueling outage number 7. At 1815 hours, the 'A' Reactor Recirculation Pump exhibited speed fluctuations and was tripped. The crew conducted an evaluation to determine existing procedure guidance for operation at low power and low flow in a single loop configuration, and conservatively decided to shut down the reactor. At 1915 hours, the Reactor Operator placed the Reactor Mode Switch in Shutdown inserting a manual scram from 23% reactor power. All control rods fully inserted. All systems operated as expected, no safety/relief valves opened and no ECCS systems initiated/actuated. The lowest reactor water level observed was 163 inches, normal operating band is 196 inches, all level three isolations (173 inches) came in as expected. At present, reactor water level is operating in normal operating band and is being maintained on the startup level control valve. No steam leaks noted. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36853 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-04-01 17:38 | 2000-04-01 21:04 | 2000-04-01 | REACTOR SCRAM During a planned power reduction, the recombiner was removed from service. The recombiner bypass valve shut, reason unknown, isolating all off gas flow. Vacuum decayed as a result. The main turbine was manually tripped, followed by an automatic reactor scram. Three rods did not indicate fully inserted immediately after the trip, but were later verified to be full in. The recirculating pumps are running and steam is being dumped to the main condenser (vacuum was restored) to remove decay heat. The licensee informed the NRC resident inspector and will make a press release. | 0 | 0 | 0 | 26 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36852 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2000-04-01 09:20 | 2000-04-01 11:02 | 2000-04-19 | TECH SPEC REQUIRED SHUTDOWN DUE TO EMERGENCY FEEDWATER STORAGE TANK LEVEL DECREASING BELOW TECH SPEC LIMIT THE PLANT ENTERED ABNORMAL OPERATING PROCEDURE (AOP) 30, "EMERGENCY FILL OF EMERGENCY FEEDWATER STORAGE TANK," AS A RESULT OF THE EMERGENCY FEEDWATER STORAGE TANK LEVEL FALLING BELOW TECH SPEC LOW LIMIT OF 91%. THIS RESULTED IN ENTRY INTO TECH SPEC 2.0.1 WHICH DIRECTS PLACING THE PLANT IN HOT SHUTDOWN WITHIN 6 HOURS, LESS THAN 300 DEGREES F IN ANOTHER 6 HOURS AND IN COLD SHUTDOWN IN 30 HOURS. AT THE TIME OF ENTRY INTO THIS TECH SPEC THE PLANT WAS ALREADY IN HOT SHUTDOWN. ACTIONS TO REFILL THE EMERGENCY FEEDWATER STORAGE TANK WERE TAKEN BY OPENING THE CONDENSATE FILL LINE AND EMERGENCY FILLING. FILLING WAS IN PROGRESS BEFORE GOING BELOW 91%, HOWEVER, SYSTEM DEMAND WAS GREATER THAN THE MAKEUP ABILITY OF THE DEMINERALIZED WATER SOURCE (STEAM GENERATOR WATER SUPPLY SWAPOVER). LEVEL WAS ABOVE 91% AT 0944CST AT WHICH TIME AOP 30 AND TECH SPEC 2.0.1 WERE EXITED. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. * * * UPDATE AT 1007 ON 4/19/00 BY MATZKE RECEIVED BY WEAVER * * * EVENT RETRACTION On April 1, 2000, at 1102 EDT, Fort Calhoun Station made a 1-hour notification of entry into a shutdown-required Technical Specification Limiting Condition for Operation (LCO) to the NRC Operations Center under 10CFR50.72(b)(1)(i)(A). At the time the plant had completed a normal shutdown to hot standby per plant procedures. While maintaining the plant in Hot Standby (Mode 3), the indicated level in the Emergency Feedwater Storage Tank (EFWST), FW-19, appeared to fall below the Technical Specification (TS) minimum level of 55,000 gallons. Operators conservatively entered TS 2.0.1 (equivalent to standard TS 3.0.3). This LCO would have required the plant to be placed in Cold Shutdown (Mode 4). The tank level was quickly recovered and the TS exited. Subsequent investigation determined that the TS for EFWST level had not been violated and TS 2.0.1 not entered. Therefore, the notification of April 1, is being withdrawn. The Resident Inspector was notified. Reg 4 RDO(Powers) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36851 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-03-31 14:48 | 2000-03-31 15:40 | 2000-04-11 | A CONTRACT EMPLOYEE WAS INAPPROPRIATELY GRANTED UNESCORTED ACCESS. ACCESS HAS BEEN SUSPENDED PENDING FURTHER INVESTIGATION. THE LICENSEE WILL NOTIFY THE NRC RESIDENT INSPECTOR. ADDITIONAL DETAILS ARE AVAILABLE FROM THE NRC OPERATIONS CENTER. * * * UPDATE AT 1527 ON 4/11/00 BY JERNIGAN RECEIVED BY WEAVER * * * The licensee has reviewed this event and determined that the event is loggable but not reportable. NRC employees may obtain the details of this retraction by contacted the NRC operations center. The licensee notified the NRC resident inspector, the operations center notified the R2DO(Christensen). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 0
36850 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-30 15:58 | 2000-03-31 15:10 | 2000-04-03 | CRITICALITY ACCIDENT ALARM SYSTEM FAILURE DURING A TEST At 1845 on 03-30-2000, during functional testing of C-746Q Criticality Accident Alarm System (CAAS), it was discovered that temperature control system on cluster "AD" was unable to perform the ability to maintain the system above the manufacturer's fourteen degree Fahrenheit recommendation due to failure of a temperature switch. The system was last tested on 12-30-99 and was determined to be functional at that time. In January of this year there were several days were outside ambient temperature dropped below fourteen degrees Fahrenheit and operability of system at those times cannot be reasonably determined. Even though the failure was discovered during testing, it is possible that the system would not have performed its intended safety function if it had been required to since the last surveillance on 12-30-99. This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. The NRC Senior Resident Inspector has been notified of this event. * * * Update 1155EDT on 4/3/00 from Underwood to S.Sandin * * * Corrected event date and time. Operations informed the NRC Resident Inspector. Notified R3DO (Kozak). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
36849 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-03-31 | 2000-03-31 07:31 | 2005-02-25 | AGREEMENT STATE REPORT - STOLEN MOISTURE/DENSITY GAUGE The Florida Bureau of Radiation Control reported the theft of a Troxler Model 3430 moisture/density gauge (Serial Number 2904-1) from a state licensee. The theft occurred sometime between 0000 and 0600 on 3/31/2000 from the parking lot of a motel in Jacksonville, FL. The gauge was stored in its case, which was chained to the bed of a pickup truck. The chain was cut, and both the gauge and case were taken. The theft has been reported to the Jacksonville Police Department. The state has requested that the licensee post a reward for the return of the gauge, and is helping the licensee to prepare a press release regarding this incident. * * * UPDATE FROM CHARLES ADAMS TO W GOTT ON 2/25/05 * * * The following was submitted via e-mail from the Florida Bureau of Radiation Control: "[The] gauge was recovered in Blackshear, GA. Georgia Radiation will provide a more detailed report on the recovery events. J.B. Coxwell Construction has since sold the gauge business to ATC Group Services. This gauge will be returned to ATC Group Services in Florida. [The] gauge appears intact and undamaged." Notified R1DO (P. Henderson) and NMSS EO (S. Moore) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  |  |  |  | 0
36848 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-03-30 16:20 | 2000-03-30 18:54 | 2000-03-30 | OFFSITE NOTIFICATION A DEAD LOGGERHEAD SEA TURTLE WAS RECOVERED FROM THE INTAKE CANAL AT APPROXIMATELY 1600. THE FLORIDA FISH AND WILD LIFE CONSERVATION COMMISSION WAS NOTIFIED AT 1620. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36847 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2000-03-30 | 2000-03-30 16:48 | 2000-04-04 | AGREEMENT STATE REPORT A 100 mCi Cs-137 source was found at the Southern Scrap Yard in Baton Rouge, LA. The source was part of a level gauge used by Formosa Plastics. The source was unopened and there was no spread of contamination. The manufacturer of the source, Texas Nuclear Technologies, will recover the source. The source is currently in a roped off area at the scrap yard. The State is investigating how the source ended up in the scrap yard. * * *UPDATE 0928EDT ON 4/3/00 FROM PAT LARKINS TO S.SANDIN * * * THE FOLLOWING INFORMATION WAS FAXED TO THE NRC OPERATIONS CENTER ON 4/3/00 BY THE NRC OFFICE OF STATE PROGRAMS: "APPROXIMATELY 1220 [HOURS] THURSDAY 3/30/00 LDEQ RECEIVED A CALL FROM THE NATIONAL RESPONSE CENTER DIRECTING US TO SOUTHERN SCRAP LOCATED ON SCENIC HWY IN BATON ROUGE, LA, CONCERNING A SOURCE DISCOVERED ON THEIR YARD. THE ATTACHMENT PLATE ON THE Cs-137 LEVEL GAUGE WAS DAMAGED BY A SHREDDER AT SOUTHERN SCRAP. THIS ACTION EXPOSED THE SOURCE LEADING TO ITS DISCOVERY. SOUTHERN SCRAP WAS ABLE TO DETERMINE FROM LABELING THAT THE SOURCE WAS A 100 mCi Cs-137 SOURCE MANUFACTURED IN 1991 BY TN TECHNOLOGY AND BELONGED TO FORMOSA PLASTIC. THE SOURCE WAS A MODEL 5200 LEVEL GAUGE, S/N B2209. AT 1430 [HOURS] A MEETING WAS HELD WITH FORMOSA PLASTIC TO TRY TO DETERMINE HOW THE SOURCE ESCAPED THEIR POSSESSION. AT THIS TIME NO MEANS COULD BE DETERMINED. AT 2000 [HOURS] 3/30/00 A TN TECHNOLOGY REPRESENTATIVE RECOVERED THE SOURCE. FOUR WIPE TEST[S] WERE PERFORMED ON THE SOURCE, ALL RESULTING IN THE SOURCE NOT LEAKING. THERE WAS NO CONTAMINATION OF THE AREA. ON 3/31/00, JIM ALDREDGE CONTACTED LDEQ STATING THAT THE SHUTTER WAS NOT SHEERED OFF AND THE GAUGE WAS RETURNED TO THE LOCKED POSITION. MR ALDREDGE ALSO STATED THAT THE GAUGE WAS TO BE RETURNED TO FORMOSA PLASTIC ON 3/31/00." THE NRC OPERATIONS OFFICER NOTIFIED R4DO (JONES) AND NMSS (HICKEY). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0
36846 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-03-30 12:04 | 2000-03-30 15:45 | 2000-03-30 | ESF ACTUATION "At 1204 on March 30, 2000, an 18 month automatic-load sequencing operational surveillance test was being conducted on the No. 1 Emergency Diesel Generator (EDG) during a refueling at the Beaver Valley Power Station (BVPS) Unit No. 1. The power to the 4KV 1AE Emergency Bus was being supplied by the operating No. 1 EDG and the Emergency Bus 4KV-1AE was separated from offsite power sources. The EDG output breaker E9 unexpectedly opened and re-closed three times before the breaker remained open, deenergizing the 4KV-1AE Emergency Bus. The cause of this event is not currently known and is being investigated. Power was restored to the 4KV 1 AE Emergency Bus at 1228 from the offsite power source. The No.1 EDG was subsequently shutdown and remains out of service. The redundant train reactor decay heat cooling and spent fuel pool cooling remained in service throughout this event. Reactor coolant temperature and spent fuel pool temperature remained constant. The redundant 4KV 1DF Emergency Bus and No. 2 EDG remained unaffected by this event. "This condition is being reported pursuant to 10CFR50.72(b)(2)(ii) as an event that resulted in an automatic actuation of an Engineered Safety Feature. De-energizing the 1 AE Emergency Bus actuated an automatic EDO signal and output breaker E9 closure. The EDG had been running, however, and the output breaker opened and re-closed three times before remaining open." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36845 | 0 | GE PLASTICS |  |  |  |  | 2000-03-30 09:30 | 2000-03-30 14:30 | 2000-03-30 | LOST SOURCE The licensee reported the loss of a 15 mCi nickel-63 source from their Washington, WV facility. Ni-63 is a low energy beta emitter and has no gamma. The source is used in an electron capture device and was last seen in July of 1999 in the licensee's laboratory. Contact information is available from the Operations Center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
36844 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-03-30 08:50 | 2000-03-30 09:46 | 2000-03-30 | COMPONENT COOLING WATER SYSTEM OUTSIDE OF DESIGN BASIS "At approximately 0850 hours on March 30th, 2000, it was determined that one loop of the Component Cooling Water (CCW) system piping located in the Spent Fuel Storage Building (FSB) was not in compliance with FSAR design criteria. The FSAR says that CCW is protected from tornadoes and tornado generated missiles by structures designed to withstand such loading. The CCW piping located in the FSB is not protected by the structure. This was identified as an issue and addressed as part of the 10CFR50.54(f) program at Indian Point 3. The issue was not considered reportable when first identified because tornado protection from the effects of missiles can be provided by redundancy. An evaluation has shown that the CCW piping can sustain limited damage from a tornado missile and that the design function of the system can be performed with this damage. Operator action is depended upon to initiate makeup water to the CCW system, a current design basis. When a 10CFR50.59 evaluation determined that the criteria for the CCW tornado protection could not be changed without prior NRC approval, the issue was determined to be reportable because the CCW system could not be shown to be in accordance with FSAR design basis. No corrective actions were immediately required because current administrative controls are sufficient to assure system operability." The NRC resident inspector has been informed of this report by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36843 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-03-29 02:00 | 2000-03-29 02:38 | 2000-03-29 | EXCESSIVE LEAKAGE THROUGH CONTROL ROD DRIVE CHECK VALVES "During the Unit 1 Refuel and Inspection Outage, it has been determined that the CRD check valves (CRD Seismic Island) exceeded the as-found minimum path leakage limit of 508 ml/hr. This failure is a degraded condition found while the plant is shutdown, and requires a 4 hour ENS notification under 10CFR50.72(b)(2)(i)." The NRC resident inspector will be informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36842 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-03-27 15:30 | 2000-03-28 22:33 | 2000-03-28 | - ESF ACTUATION OF REACTOR WATER CLEANUP SYSTEM DURING DRAINING EVOLUTIONS - During the Unit 1 Refueling and Inspection Outage, the licensee determined that the Reactor Water Cleanup System received an ESF Actuation signal during draining evolutions. The potential for an ESF Actuation is identified in the draining procedure, however after review, the licensee determined that the actuation signal was not part of the planned evolution due to the system not being properly removed from service. An actual isolation did not occur due to the isolation valves being bypassed per the draining procedure. This event has no effect on Unit 2 which is at 100% power. The licensee is investigating this event and determining corrective actions. At 2030 on 03/28/00, while reviewing this event, the licensee determined that this event is reportable to the NRC. This failure requires a four hour ENS notification under 10CFR50.72(b)(2)(ii). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36841 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-28 10:30 | 2000-03-28 18:54 | 2000-03-28 | NRC BULLETIN 91-01, 4 HOUR REPORT - At 1030 on 03/28/00, a box containing uranium oxide standard vials was discovered under a workbench in building X-710 room 117, The applicable Nuclear Criticality Safety Approval/Evaluation (NCSA/E-0710-011) does not analyze storing uranium oxide vials in this area of the X-710 building. The uranium oxide vials were transported to an area designated for storage of such materials under applicable approved NCSAs. The material was non-destructive assay (NDA) tested. The combined mass of all of the uranium oxides in all the standard vials was 18 +/- 9 grams U-235 with an average enrichment of 18 wt% U-235, SAFETY SIGNIFICANCE OF EVENTS: The uranium oxide vials were stored at least two feet edge-to-edge from any other fissile material. The combined mass of all of the uranium oxides in all the standard vials was determined by NDA to be 18 +/- 9 grams U-235 with an average enrichment of 18 wt% U-235. Due to the low mass and absence of moderation, the safety significance is low. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR]: Additional mass and a spacing violation would have been required before a criticality would be possible. Without moderation, much more than the safe mass of 350 grams of U-235 would have to be present before a criticality could be possible. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): This was an unanalyzed condition. Although not specifically controlled, the combined mass of all the uranium oxides in all the standard vials was less than a safe mass, moderation was not present, and the uranium oxide vials were spaced at least two feet from any other fissile material. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDING PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): NDA shows the combined mass of all of the uranium oxides in all the standard vials to be 18 +/- 9 grams of U-235 with an enrichment of 18 wt% U-235. The material is in the form of dry oxides. For a spherical system at optimum moderation, full water reflection, and 100 wt% enrichment, the safe mass is 350 grams U-235. NUCLEAR CRITICALITY SAFEEY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The request failed to identify the presence of uranium oxide vials in the room resulting in an unanalyzed condition. The uranium oxides are less than a safe mass and other uranium bearing material was spaced at least two feet edge-to-edge from the uranium oxides. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The uranium oxide vials were removed from the X-710 room 117 under applicable plant approved NCSAs. Total mass of material in X-710 room 117 is currently less than 15 grams U-235. The NRC Resident Inspector and the site DOE Representative were notified. PTS-2000-038; PR-PTS-00-01697. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36840 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-03-28 12:41 | 2000-03-28 15:21 | 2000-04-21 | PRIMARY COMPONENT COOLING WATER SYSTEM INOPERABLE DUE TO THE AREA VENTILATION SYSTEM INCAPABLE OF PERFORMING ITS SAFETY FUNCTION "On 03/26/00 Seabrook Station entered Tech Spec (TS) 3.0.3 due to both trains of the Primary Component Cooling Water (PCCW) system being declared inoperable. Both trains of PCCW were declared inoperable because the PCCW Area Ventilation System was determined to be incapable of performing its intended function. "The PCCW system is a two train closed loop cooling system used to remove heat from plant components during plant operation, plant cooldown and during various phases of an accident. The PCCW pumps are located within the Primary Auxiliary Building (PAB). The operation of the PCCW pumps is supported by the PCCW Area Ventilation system. This ventilation system has redundant, automatically controlled auxiliary supply fans and associated dampers to ensure that the temperature in this area does not exceed design limits should the normal PAB ventilation system fail. "During surveillance testing of the PCCW Area Ventilation system, an exhaust damper (PAH-DP-357) failed to open as required. During a subsequent local investigation by the Shift Manager and Unit Supervisor it was determined that recent painting activities may have affected both PAB Exhaust Dampers (PAH-DP-357 and PAH-DP-358). A subsequent test of PAH-DP-358 indicated that it also failed to open as required. TS 3.0.3 was entered on 03/26/00 at 0346. TS 3.0.3 was subsequently exited at 0425 on 03/26/00 after plant personnel reestablished operability for PAH-DP-358. The subject dampers automatically open to provide an exhaust flow path for the PCCW Pump Area ventilation system which supports operation of the PCCW pumps. An initial review of this condition concluded that a report pursuant to the requirements of 10CFR50.72 was not required. A subsequent review of this event determined that it is reportable pursuant to the requirements of 10CFR50.72(b)(2)(iii) as a condition that alone could have prevented the fulfillment of a safety function." The licensee will inform the NRC resident inspector. HOO Note: The event time was the time the licensee determined this condition to be reportable to the NRC. * * * RETRACTION ON 04/21/00 AT 1330 HOURS BY M. KILEY TAKEN BY MACKINNON * * * Upon further Engineering review, North Atlantic has determined that the PCCW system remained capable of performing its intended function during the period when the PAB Exhaust Dampers (PAH-DP-357 and PAH-DP-358) were painted between March 12, 2000 and March 26, 2000 when the condition was corrected. North Atlantic analyzed the area heat-up conditions as they pertain to the operation of the PCCW system and other associated safety-related equipment and concluded that the PCCW system would have performed its intended function even with the subject dampers isolated. Therefore, this condition is not reportable pursuant to the requirement of 10 CFR 50.72(b)(2)(iii) as a condition that alone could have prevented the fulfillment of a safety function. R1DO (John White) notified. The NRC Resident Inspector has been notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36839 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-03-28 | 2000-03-28 12:27 | 2000-03-28 | AGREEMENT STATE REPORT - STOLEN / RECOVERED TROXLER NUCLEAR GAUGE IN ARLINGTON, TX Texas Licensee #TX-L-05082, Fugro-McClelland (Southwest), Inc., Fort Worth, Texas, reported to Texas Department of Health, Bureau of Radiation Control, the theft of a nuclear gauge from it's unsecured transport box sitting near a work site at the General Motors Plant in Arlington, Texas. The gauge was unsecured and the source rod was not locked, as the operator was going to use the gauge after a short discussion approximately 100 feet from the transport box. Gauge Manufacturer: Troxler, Model: 3411-B, Serial Number: 10390. Two sealed sources: 1) Cs-137 with nominal activity of 10 millicuries and 2) Am-241/Be, nominal activity 40 millicuries. The stolen gauge was discovered along a local street several blocks from the GM Plant and in a damaged condition - the source rod was extended and broken. The gauge was recovered by a passerby who thought the damaged gauge may be of value and took it to a local equipment rental facility to ascertain the value. He was warned of the radiation hazard but reportedly departed the facility with the broken gauge. He evidently changed his mind and notified the City of Arlington, who arrived and recovered the gauge. The gauge was turned over to the Troxler Service Facility in Arlington where a leak test was performed and indicated that the sealed sources were still intact. However, the gauge would require repair before being placed back into service. The Texas Licensee was notified of the recovery. The gauge is being maintained by the Troxler facility until release by this agency for repairs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36838 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-03-27 10:08 | 2000-03-27 14:43 | 2000-03-27 | FITNESS FOR DUTY EVENT - A temporary employee foreman tested positive for illegal drugs during a random drug test. The licensee terminated the employee's plant access authorization. Contact the NRC Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 26.73 |  |  |  | 0
36837 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-03-27 | 2000-03-27 10:00 | 2000-03-27 | AGREEMENT STATE REPORT INVOLVING RECOVERED TROXLER GAUGE "Citizen found troxler gauge [containing 8mCi Cs-137 and 40mCi Am-241:Be] along road and took it to the Royal Palm Beach PD. Owner notified this office of missing gauge, was told of it's location [Intersection of 41 & 67 in Royal Palm Beach], and then took possession. There was no damage to the gauge which was in a locked case. Owner said that the operator failed to secure the gauge to the truck when leaving a work site. Florida is investigating the incident [Florida Incident #FL00-054]." The licensee lost the device on the morning of 3/27/00 when it fell off his truck due to not being properly secured. Call the Headquarters Operations Center for contact information. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36836 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-03-27 08:00 | 2000-03-27 09:17 | 2000-03-27 | FAILURE OF LOCAL LEAK RATE TEST. DURING LOCAL LEAK RATE TESTING(LLRT) OF THE "2G11-F004", DRYWELL FLOOR DRAIN SUMP PRIMARY CONTAINMENT ISOLATION VALVE, IT WAS DETERMINED THAT THE VALVE LEAKS AT A RATE GREATER THAN 30,000 ACCM(ACTUAL CUBIC CENTIMETERS/MIN) WHICH IS GREATER THAN THE PROCEDURAL LIMITS. THIS IN COMBINATION WITH ITS COMPANION( IN SERIES) ISOLATION VALVE(2G11-F003) WHICH HAD FAILED A PREVIOUS LLRT AND WAS REPAIRED, BUT FAILED ITS RETEST, RESULTED IN THE TECH SPEC LIMIT FOR 0.009L-SUB-A BEING EXCEEDED FOR BYPASS LEAKAGE. THE TEST WAS PERFORMED ON 3/26 AND WAS EVALUATED THIS MORNING. THE RESIDENT INSPECTOR WAS NOTIFIED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36835 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-03-26 17:34 | 2000-03-26 21:06 | 2000-03-26 | STATE OF FLORIDA NOTIFICATION INVOLVING LOGGER HEAD SEA TURTLE An endangered Logger Head Sea Turtle was discovered at the Crystal River (CR-3) intake area. The turtle which appeared to have been struck by a boat propeller died from injuries . The Florida Department of Environmental Protection will be notified on Monday, 3/27/2000. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36834 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-02-08 12:00 | 2000-03-24 17:25 | 2000-04-14 | AGREEMENT STATE REPORT - STOLEN / RECOVERED CPN NUCLEAR GAUGE IN HOUSTON, TX The following text is from the facsimile received from the Texas Department of Health: "Theft/Recovery of a nuclear gauge - licensee notified the agency [Texas Department of Health] Feb 8, 2000. Reports lost in mail. Faxed information today at request of Incident Investigation. Gauge recovered intact Feb 14, 2000. Leak tested Feb 15, 2000 was fully satisfactory." * * * UPDATE AT 1255 ON 03/28/00 BY JAMES OGDEN TO JOLLIFFE * * * The following is a more detailed version of the above Agreement State Report: Texas Licensee #TX-L-02757, HTS, Inc. Consultants, Houston, Texas, reported to Texas Department of Health, Bureau of Radiation Control, the theft of a nuclear gauge in it's transport box from the bed of a company pickup truck on February 8, 2000. Gauge Manufacturer: CPN, Model: MC-3. Serial Number: M35116369. Two sealed sources: 1) Cs-137, maximum activity 10 millicuries and 2) Am-241/Be, maximum activity 50 millicuries. The gauge was stolen between 5:45 a.m. and 1:45 p.m. from a jobsite. Incident Report Number 16656300-H was filed with the Houston Police Department on February 8, 2000. Ten local pawn shops were notified by the licensee. The stolen gauge was discovered in a lot adjacent to Hemmi Autoworks, Houston, TX by the facility owner, Richard "Butch" Hemmi and reported to the City of Houston, Bureau of Occupational Health and Radiation Control. This organization recovered all components of the gauge intact on February 14, 2000 (Gauge, Transport box, Calibration Block, Guide Pin, Guide Plate, and paperwork of the last leak test.) The gauge was satisfactorily leak tested on February 15, 2000. The gauge was returned to storage and to service with the Texas licensee. The NRC Operations Officer notified the R4DO Kriss Kennedy and NMSS EO Brian Smith. * * * UPDATE AT 1206 ET ON 04/14/00 BY HELEN WATKINS TO MACKINNON * * * The licensee does not believe rad exposures to the public occurred. The Agency (BRC) is investigating the incident to obtain further information. R4DO (Chuck Paulk) & NMSS EO (Brian Smith) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36833 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-03-24 13:00 | 2000-03-24 16:18 | 2000-03-24 | ONE EMERGENCY SIREN INADVERTENTLY INITIATED "One (1) emergency siren inadvertently initiated on 03-24-00 at 1300. At 1310. the West Feliciana parish BOC Director called to advise RBS personnel that one of our sirens in East Feliciana parish had sounded. Telephone calls with East Feliciana personnel corroborated the information. Siren control computer records indicate that beginning at 1230, siren #6 had attempted unsuccessfully to power up several times. At 1300, it succeeded in powering up and sounded for about two minutes. There was no event or maintenance activity in progress to initiate this siren. The siren is communicating with the RBS LOF communications room but the siren was not initiated from that center. The cause of the activation is not known at this time. Technicians are en route to the siren to investigate. All other sirens are fully operable. The Louisiana Office of Emergency Preparedness (State Agency) and the RBS NRC site Senior Resident Inspector (T. Pruitt) have been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36832 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-03-24 11:30 | 2000-03-24 12:58 | 2000-03-24 | COMPLETE LOSS OF COMMERCIAL AND DEDICATED PHONE LINES The plant has lost all normal offsite communications, commercial and FTS. This is an area problem, not just a plant problem. Bell South has been contacted and is troubleshooting the problem. The plant still has its communication link to load dispatch as well as radio communication. Also, the control room has a satellite phone which was used to make this notification. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2148 EST ON 3/24/00 BY CHRIS MILLER TO FANGIE JONES * * * The FTS and commercial phones have been restored. The NRC Resident Inspector and R4DO (Lawrence Yandell) have been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ENS INOPERABLE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36831 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-23 10:00 | 2000-03-24 09:42 | 2000-03-24 | - NRC BULLETIN 91-01, 24 HOUR REPORT - During chemical cleaning of motor brake pads in the C-400 alkali tank, it was discovered that the brake pads were placed in the alkali tank before being verified to meet unconditional release limits, in violation of NCSA 400.011. Compliance with unconditional release limits requires both a removable contamination smear and a fixed uranium contamination survey. The fixed contamination survey was omitted. Compliance with unconditional release limits and a visual inspection for uranium contamination are used to ensure that unknown quantities of fissile material do not enter the alkali tank. The visible inspection required was properly performed. A determination that assay was 5.5 wt% is also required and was performed and documented. However, the determination was documented on the C-400 Chemical Cleaning Log sheet, instead of the form required by CP2-EG-NS1O33. SAFETY SIGNIFICANCE OF EVENTS: The visual inspection of the brake pads showed no uranium contamination and this equipment is not directly in contact with process UF6. The potential for introduction of U-235 into the alkali tank from the brake pads is extremely low, a control relied upon for criticality safety was violated. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCEANARIO(S) OF HOW CRITICALITY COULD OCCUR]: In order for a criticality to be possible, the accumulation of fissile material involving an unsafe mass and geometry would have to occur. However, since the visual inspection showed no contamination, an accumulation of U-235 above assumed limits did not occur. These limits are a small fraction of the unsafe mass value, CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for this scenario is established by implementing two independent controls on mass. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITCAL MASS): No visible contamination. Therefore, the mass is zero grams. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on a visual inspection of all internal and external surfaces for uranium contamination to verify no visual contamination. Verification of no visual contamination ensures the mass limit is maintained for assays </= 5.5 wt%. This control was not violated. The second leg of double contingency is based on meeting health physics unconditional release criteria in order to meet the mass limit for assays </= 5.5 wt%. Compliance with the unconditional release criteria was not established. This control was violated when the brake pads were placed in the tank without verification that the unconditional release criteria were met. One of the two controls on mass was violated, therefore double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Sample the alkali tank and verify that the assay is less than 1 wt% U-235 and uranium concentration is less than 1.0 g U/I. The NRC Resident Inspector has been notified of this event. PGDP Problem Report #ATRC-OO-1758; PGDP Event Report #PAD-2000-023. Responsible Division: Chemical Operations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36830 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-03-24 05:37 | 2000-03-24 06:32 | 2000-03-24 | - CONTROL ROD DROPPED INTO THE CORE DURING CONTROL ROD MOTION TESTING - While performing control rod motion testing, plant technicians were checking the control rod fuses and caused a fuse to blow which caused control rod #48 to drop into the core. Plant operators reduced power from 100% to 70% and are in the process of retrieving the dropped control rod and are investigating the cause of the blown fuse. The licensee notified state and local officials and the NRC Resident Inspector. | 0 | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36829 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-03-24 04:45 | 2000-03-24 05:56 | 2000-03-24 | - 'C' INBOARD MAIN STEAM ISOLATION VALVE FAILED ITS LOCAL LEAK RATE TEST - During the performance of a local leak rate test of the 'C' main steam isolation valves (MSIVs) with Unit 1 in a refueling outage, the inboard MSIV #HV141-F022C was unable to hold pressure. This constitutes a failure of the maximum path leak rate required by Tech Spec 3.6.1.3. This condition constitutes a degraded condition of a principal safety barrier found while Unit 1 was shutdown. No other adverse conditions were identified. Unit 1 remains safely shutdown and the licensee is conducting an investigation to determine the cause of the failure. The licensee plans to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36828 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-03-23 21:40 | 2000-03-23 23:27 | 2000-03-23 | FULL REACTOR SCRAM SIGNALS GENERATED DURING TESTING WHILE REACTOR IS SHUTDOWN With Unit 2 in a refueling outage, control room operators were performing a Reactor Protection System scram discharge volume (SDV) high water level bypass switch (rod block) functional test. During performance of the test, control room operators placed the SDV high water level bypass switch #2C71-54 in the bypass position and the reactor mode switch in the shutdown position. This action caused the generation of a full reactor scram signal. The Control Rod Drive System had already been deenergized and all control rods were already fully inserted into the reactor core. Control room operators reset the reactor scram signal to normal and placed the bypass switch in the normal position in accordance with the test procedure. However, the bypass switch was placed in the normal position before the SDV had time to drain down. With the SDV water level above the high level alarm setpoint, a second full reactor scram signal was generated. The licensee restored all systems to normal and is investigating this situation, including reviewing the test procedure. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36827 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-03-21 06:30 | 2000-03-23 16:46 | 2000-03-24 | AGREEMENT STATE/TRANSPORTATION EVENT INVOLVING A BURNED FEDERAL EXPRESS TRUCK CARRYING A GAUGE WITH A SMALL SOURCE IN IT On 3/21/00 at about 6:30 AM in Oxnard CA, a Federal Express truck burned due to an unknown cause. It was discovered today, 3/23/00, that a thickness gauge from NDC of Irwindale, CA was on the truck. The gauge contains a special form source of Curium-244, 100 mCi. The source is thought to be able to survive the fire and is being sought. Dr. Roy Parker, the Federal Express Safety Officer, is on the scene and following up on the incident. The National Response Center report number is 523952. (Call the HOO for contact numbers) * * * UPDATE AT 1715 EST ON 3/24/00 BY DONALD BUNN TO FANGIE JONES * * * The source has been recovered intact from the fire debris, there has been no release. Notified the NMSS EO (Larry Camper), R4DO (Lawrence Yandell), IRO (Frank Congel), DOT (Matt Robertson), and DOE (Mike Wyatt). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | TRANSPORTATION EVENT | [8 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
36826 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-03-23 08:30 | 2000-03-23 13:17 | 2000-03-23 | THREE FUEL ASSEMBLIES DETERMINED TO BE IN WRONG POSITIONS IN THE SPENT FUEL POOL Unit 1 personnel determined that three fuel assemblies, in the Unit 1 Spent Fuel Pool (SFP), were in positions inconsistent with the Technical Specifications (TS). Preliminary assessment indicates that the Keff limit of 0.95 (TS 3.7.15) for the SFP would have still been met. This condition existed for ten days, since the last Unit 1 core offload. The assemblies have been returned to the positions allowed by TS. An investigation is in progress to determine the cause of this event and to determine if the Keff limit was exceeded. There will be a 30 day written report submitted. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW | [5 empty] | 0
36825 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-03-23 12:00 | 2000-03-23 13:11 | 2000-03-31 | C-3 DEFECTS DETECTED DURING EDDY CURRENT INSPECTION OF STEAM GENERATORS Indian Point 2 is conducting eddy current testing of 100% of the steam generator (SG) tubes. With about 90% of the inspection complete, SG-21 and SG-24 tubes have defects in greater than 1% of the tubes inspected. SG-22 and SG-23 have defects in much less than 1% of the tubes inspected. The majority of the defects are at the support plate intersections and in row 2 U-bends. There are 41 indications in SG-21, 40 at the support plate and 1 in the U-bend. There are 39 indications in SG-24, 36 at the support plate and 3 in the U-bend. In accordance with Technical Specification 4.13, these defects result in a C-3 classification. The testing will continue until 100% of the tubes are inspected. The licensee notified the NRC Resident Inspector. UPDATE ON 3/31/2000 BY LAMB, RECEIVED BY WEAVER * * * This report is being made as a follow up to previously reported event number 36825. At approximately 1500 today, the tube at Row 2 Column 69 in steam generator 24 failed the three delta pressure requirement during in-situ pressure testing being performed in accordance with NEI 97-06 guidelines to meet Technical Specification requirements. The three delta pressure value was calculated to be 5118 psi, and with uncertainties applied, the test pressure was specified at 5173 psi. Shortly after achieving 5173 psi for the required two seconds specified in the test, pressure was noted to rapidly drop indicating leakage. No leakage was observed at a steam line test pressure of 2841 psi. Therefore, that performance criterion was met. The licensee notified the NRC resident inspector. The operations center notified the R1DO (Evans). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36824 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2000-03-22 | 2000-03-22 15:07 | 2000-03-22 | AGREEMENT STATE REPORT "During a routine license inspection it was noted a fluoroscopy technologist had received a reported film badge exposure of approximately 8 rem during 1999. It was also noted this same individual had an exposure reported during one month of 1999 exceeding 116 rem. A subsequent evaluation by the licensee and the dosimetry processor indicated the 116 rem exposure was probably an anomaly and therefore was taken off the individual's exposure record. This was based on a review of past exposures and a review of the film which showed no discernable filter patterns. "The annual exposure of approximately 8 rem is currently unexplained and is being investigated by the licensee. The licensee requested the individual be given blood tests to confirm the potential exposure. The individual refused the blood tests. "Neither of these exposures reported to the licensee by the dosimetry processor was reported to the State Radiation Control Program as required." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0
36823 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-03-21 21:36 | 2000-03-22 00:48 | 2000-03-22 | - SERVICE WATER SYSTEM NONESSENTIAL VALVES ISOLATED DURING MAINTENANCE ACTIVITIES - During performance of preplanned Division I Service Water System (SWS) logic circuitry relay replacement activities, an installed electrical jumper failed to maintain contact within the circuit causing a fuse to blow and the subsequent automatic isolation of the Division II SWS nonessential valves. This potential failure had been discussed in preevaluation briefings as a distinct possibility and a contingency was in place. Maintenance technicians replaced the fuse and restored flow to the nonessential headers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36822 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2000-03-21 18:50 | 2000-03-21 23:12 | 2000-03-21 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE "During performance of Unit One HPCI System Logic Functional Test, the HPCI Auxiliary oil pump would not stay running and the turbine stop valve did not open on receipt of a simulated auto initiation signal. The Auxiliary oil pump was subsequently taken to manual, at which time the pump stayed running and the turbine stop valve opened. HPCI is inoperable with Engineering and Maintenance troubleshooting possible pressure switch problems." The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36821 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-21 13:50 | 2000-03-21 16:44 | 2000-03-21 | 4-HOUR NRC BULLETIN 91-01 REPORT "Valves being dispositioned as part of the transfer of material storage areas from DOE to USEC in C-331 were incorrectly handled as NCS exempt equipment in violation of NCSA GEN-20. NCSA GEN-20 requires that the equipment be characterized prior to movement/transportation. Valves located in former DMSAs were incorrectly labeled as exempt from NCS controls based on invalid assay smear results. The smears contained less than a measurable quantity of uranium and valid assay results could not be obtained. Assay smears with uranium below a measurable quantity cannot provide an accurate measurement of assay. The smear analysis results were incorrectly used to determine that the equipment assay was below 1%. "SAFETY SIGNIFICANCE OF EVENTS: "Assay smears taken to determine the assay of the valves did not contain sufficient uranium for analysis. The smears included valve internal surfaces, but all internal surfaces were not visible. The items have been decontaminated and holdup of uranium in the internal surfaces is highly unlikely. In addition, many of the equipment items were not used in UF6 service, however, the assay exemption process is not allowed unless valid sample analysis results can be obtained. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: "In order for criticality to be possible, the accumulation of fissile material involving an unsafe mass and geometry would have to occur. A significant amount of uranium is not believed to be present but no valid quantification of mass has been made. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY CONCENTRATION ETC.): Double contingency for this scenario is established by implementing two independent controls on assay. "ESTIMATED AMOUNT, ENRICHMENT FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITCAL MASS): "Unknown due to DOE previously controlling areas. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "No NCS controls (other than providing 10 foot buffer zone) were in place. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "All equipment which has been improperly characterized will be identified and characterized with proper independent verification of assay and mass. The issue of inadequate procedures and/or training for the performance of independent assay verification will be corrected by retraining of personnel and/or revision of the applicable procedure prior to the performance of any further independent assay verifications." The NRC resident inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36820 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2000-03-21 08:50 | 2000-03-21 09:48 | 2000-03-21 | OFFSITE NOTIFICATION INVOLVING MINOR OIL RELEASE TO DISCHARGE CANAL During demolition of a building, a hydraulic line was severed causing an approximate 1-2 gallon spill of oil. A small portion of the spill reached the discharge canal creating a sheen on the water. The licensee notified the State of Connecticut Department of Environmental Protection (DEP), the USCG and the National Response Center (NRC). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36819 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-03-21 04:40 | 2000-03-21 06:15 | 2000-03-21 | TURBINE TRIP - REACTOR TRIP An electrical fault on the main generator caused a turbine trip and an anticipatory reactor trip. All rods fully inserted and the plant response to the trip was as expected. Decay heat is being removed by dumping steam to the main condenser. Auxiliary Feedwater started as expected. Reactor coolant pumps are running. Offsite power and the emergency diesel generators are operable. The licensee is investigating the cause of the turbine trip. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36818 | 0 | TEMPLE UNIVERSITY |  |  |  |  | 2000-03-20 12:00 | 2000-03-20 17:07 | 2000-03-20 | PACKAGE RECEIVED WITH EXTERNAL RADIAITON READING GREATER THAN LIMIT A shipment of phosphorus-32 from New England Nuclear was received with an external radiation reading in excess of that permitted by the shipping label. The package was labeled with a Radioactive White I placard, but the licensee obtained a radiation reading of 225 mrem/hr on contact, using an ionization detector with the beta window uncovered. No external contamination was observed, although some contamination of the vial within the lead shield was found. The licensee believes that the shipment contains more than the specified 1 mCi of P-32, and that the high radiation reading is the result of bremsstrahlung. The shipment is being returned to the vendor. The licensee has already contacted NRC Region I regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | [10 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0
36817 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-03-20 15:05 | 2000-03-20 17:03 | 2000-03-27 | SECURITY REPORT A contact employee attempted to bring contraband into the Protected Area. Immediate compensatory actions were taken upon discovery. The licensee notified the NRC resident inspector. Contact the NRC Operations Center for additional details. * * * UPDATE AT 1513 ON 03/27/00 FROM KIM AITKEN TO JOLLIFFE * * * Further licensee investigation revealed that there was no significant threat to River Bend Station or the public and that the vendor employee had no malevolent intent. After review of Reg Guide 5.62, NUREG 1304, and Generic Letter 91-03, the licensee has determined that this event is not reportable under 10CFR26, 10CFR50.72, 10CFR73.71, or 10CFR73, Appendix G.l.d criteria and thus, the licensee desires to retract this event. The licensee has discussed this event with Region IV security personnel and the NRC Resident Inspector. The NRC Operations Officer notified the R4DO Kriss Kennedy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 0
36816 | 0 | GARDEN STATE CANCER CENTER |  |  |  |  | 2000-03-20 | 2000-03-20 11:55 | 2000-03-20 | MEDICAL MISADMINISTRATION INVOLVING TREATMENT PROTOCOL IN DECEMBER 1999 A FEMALE PATIENT UNDERGOING A CANCER TREATMENT REGIME WAS PRESCRIBED A THERAPEUTIC DOSE OF 20 mCi Y-90 (YTTRIUM). THE COVERING PHYSICIAN TERMINATED THE TREATMENT AFTER 2 mCi WAS ADMINISTERED DUE TO A PROTOCOL ISSUE THAT REQUIRED THE PHYSICIAN VERIFY "MIRROR IMAGING" OF THE TREATMENT SITE WITH THE CAT SCANS. NO ADVERSE HEALTH EFFECTS WERE EXPERIENCED BY THE PATIENT. THE PATIENT SUBSEQUENTLY RECEIVED THE PRESCRIBED DOSE. THE LICENSEE HAD DISCUSSIONS WITH REGION I (JIM DWYER) CONCERNING THIS REPORT. CALL THE HEADQUARTERS OPERATIONS CENTER FOR CONTACT INFORMATION. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.33 |  |  |  | 0
36815 | -1 | CARDIOLOGY ASSOC OF FAIRFIELD CO. |  |  |  |  | 2000-03-20 | 2000-03-20 09:44 | 2000-03-21 | EXTERNAL RADIATION LEVELS EXCEEDING THE LIMITS OF 10 CFR 71.47 CARDIOLOGY ASSOCIATES OF FAIRFIELD COUNTY LOCATED AT 40 CROSS STREET IN NORWLAK, CT, RECEIVED A PACKAGE FROM SYNCOR INTERNATIONAL IN STAMFORD, CT, LABELED WHITE I WHICH MEASURED 40 mR/HR (EXTERIOR SWIPE READ 38 DPM). THIS EXCEEDS THE EXTERNAL RADIATION LEVELS ALLOWED FOR WHITE I. THE PACKAGE CONTAINED SEVERAL LEAD PIGS OF TECHNETIUM-99m , ONE OF WHICH WAS CONTAMINATED READING 5652 DPM USING A SWIPE. THE LICENSEE NOTIFIED THE SYNCOR INTERNATIONAL AND THE NRC REGION I OFFICE (SHANBAKY). * * * UPDATE 1116EST ON 3/21/00 BY S.SANDIN * * * THE LICENSEE IS RETRACTING THIS REPORT AFTER FURTHER REVIEW AND DISCUSSIONS WITH REGION I (DARDEN). NOTIFIED R1DO (MANNING). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | [10 empty] | NON EMERGENCY | 1 | CT | HOS | [5 empty] | 0
36814 | 0 | COMBUSTION ENGINEERING INC. |  |  |  | URANIUM FUEL FABRICATION | 2000-03-19 07:50 | 2000-03-20 08:46 | 2000-03-20 | 24 HOUR BULLETIN 91-01 REPORT At approximately 0750 on 03/19/2000, a water leak was discovered above and adjacent to the Erbia master blender. The water leak was from the building outer roof and around an I-beam that penetrates the secondary roof. The blender was undergoing maintenance and was emptied of Special Nuclear Material (SNM). An open filter housing on the blending was immediately covered with plastic. The blender was currently empty and visually verified to contain less than a safe mass of uranium. Furthermore, no water was detected inside the blender. Thus, no unsafe condition existed. However, the blender will remain out of service until the moderation barriers are reestablished. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: If the blender contained greater than a safe mass of uranium and greater than 11 liters of water entered the blender. CONTROLLED PARAMETERS: Moderation is the primary controlled parameter. Normally, there are at least three barriers to isolate the contents of the blender from moderators: two independent overhead roofs and the closed blender vessel. In this case the blender was empty (<5 kg) and shutdown for maintenance. Therefore, mass control was also in place for the blender. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSE MATERIAL: Approximately 5 kg of residual U02 powder was present in the filter housing of the blender. The maximum enrichment was 4.0% U-235 and the corresponding safe mass is 24 kg U02. The contents were poisoned with approximately 8% erbium. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: The system will remain out of service with less than a safe mass until the event investigation is completed and the overhead barriers are successfully repaired. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | MO | FUE | [5 empty] | 0
36813 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-03-20 04:15 | 2000-03-20 05:02 | 2000-03-20 | OFFSITE TRANSPORTATION OF A POTENTIALLY CONTAMINATED WORKER "A vendor support employee was injured due to a fall (approximately 6 to 8 feet) in Unit 2 lower containment. The individual was supporting reactor coolant pump work. Due to injuries, the individual could not be fully frisked for contamination. Until further determination, individual is considered potentially contaminated and is being transported offsite to the local medical facility." The licensee will notify the NRC resident inspector. * * * UPDATE AT 0930 ON 3/20/00, BY BREWER RECEIVED BY WEAVER * * * This is a follow-up pertaining to the notification of 0500 today concerning the transport of a potentially contaminated worker to an off-site medical facility. The injured individual was NOT contaminated, however the harness and nylon choker used to lift the injured man has some low level fixed contamination. This material has been transported back to the site and all areas of the hospital and the transport vehicle have been surveyed clean. The licensee informed the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(v) |  |  |  | 0
36812 | -1 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-03-19 20:00 | 2000-03-19 23:31 | 2000-03-21 | DISCOVERY OF REACTOR COOLANT SYSTEM LEAKAGE ON THE WITHDRAWAL LINE WELDS OF THREE CONTROL ROD DRIVE MECHANISMS DURING HYDRO TESTING The following text is a portion of a facsimile received from the licensee: "EVENT: During [the performance of procedure] OPT-80. 1, Reactor Pressure Vessel ASME Vessel ASME Section XI Pressure Test, reactor coolant system (RCS) pressure boundary leakage was observed on the withdrawal line welds of three control rod drive mechanisms (CRDM). The following CRDMS were noted with leakage: CRDM 06-15 (10 drops/minute at 1030 psig), CRDM 30-15 (20 drops/minute at 1030 psig) and CRDM 14-19 (20 drops/minute at 1030 psig). This leakage is outside the acceptance standard of zero leakage per ASME Section XI, Table IWB-3410-1." "INITIAL SAFETY SIGNIFICANCE EVALUATION: Minimal; the leakage is well within the capacity of available injection systems." "CORRECTIVE ACTION(S): The CRDMs will be removed, and the affected areas repaired prior to reactor startup." The licensee notified the NRC resident inspector. * * * RETRACTION 1522 3/21/2000 FROM MARK TURKAL TAKEN BY BOB STRANSKY * * * "Upon further inspection and evaluation, CP&L had determined that the previously reported leaks from control rod drive mechanisms (CRDMs) 06-15, 30-15, and 14-19 do not represent a serious degradation of a principal safety barrier. "Based on the location of the leaks, it was conservatively assumed to be pressure boundary leakage coming from the withdrawal line welds to the CRD housing flange; which was outside the acceptance criteria of zero leakage per ASME Section XI, Table IWB-3410-1. CP&L notified the NRC at 23:31 EST (i.e., Event Number 36812), in accordance with 10 CFR 50.72(b)(2)(i), that a condition on Unit 1 had been identified that had it been found while the reactor was in operation, would have resulted in the nuclear power plant, including its principal safety barriers, being seriously degraded. "Subsequently, repressuization of the Unit 1 reactor pressure vessel was performed and the leaks were observed using advanced video inspection techniques. Based on this re-inspection, it was determined, on March 21, 2000, that the leakage was from the CRDM flange bolting and not the withdrawal line welds. As such, this is not pressure boundary leakage and the zero leakage acceptance criteria of ASME Section XI, Table IWB-3410-1 is not applicable. This condition does not represent a serious degradation of a principal safety barrier. "CP&L has evaluated and dispositioned the observed leakage, in accordance with Code Case N-566-1, 'Corrective Action For Leakage Identified at Bolted Connections,' and determined it to be insignificant leakage, which is expected to seal during plant heatup." The NRC resident inspector has been informed of this retraction. Notified R2DO (Decker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36811 | -1 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2000-03-17 17:30 | 2000-03-17 20:26 | 2000-04-07 | DISCOVERY OF NON-CONSERVATIVE RODDED RADIAL PEAKING FACTORS IN THE CORE PROTECTION CALCULATORS AND CORE OPERATING LIMIT SUPERVISORY SYSTEM FOR GROUPS 5 AND P The following text is a portion of a facsimile received from the licensee: "On 03/17/00 at approximately 1730 MST, Palo Verde Engineering determined that Non-conservative Rodded Radial Peaking Factors were installed in the Unit 1 Core Protection Calculators (CPC) and Core Operating Limit Supervisory System for Group 5 and Group P. During the course of normal operations, Group 5 could be inserted into the core in order to compensate for Axial Shape Index. With the current values of Rodded Radial Peaking Factors, Group 5 may be outside of its design basis. Control room operators have been briefed on contingency actions to prevent the unit from operating outside the design basis. At this time, only Unit 1 is impacted, and the investigation is continuing." The licensee plans to notify the NRC resident inspector. * * * UPDATE AT 0009 ON 3/18/00, BY BANKS RECEIVED BY WEAVER * * * "On 3/17/00 at 2122, conservative Rodded Radial Peaking Factors were installed in unit 1, Core Protection Calculators (CPCs) channels A, B, & C and Core Operating Limit Supervisory System for Group 5 and Group P. CPC channel D remains out of service for an unrelated issue, however, before the channel is placed back into service, the new conservative Rodded Radial Peaking Factor will be installed." The licensee informed the NRC resident inspector of this update. The Operations Center notified the R4DO (Graves). * * * RETRACTION ON 04/07/00 AT 1627 EDT BY DAN MARKS TAKEN BY MACKINNON * * * On 04/06/00, Palo Verde Engineering personnel completed an analysis of the impact of the non-conservative Rodded Radial Peaking Factors and concluded that sufficient margin existed such that the Core Operating Limit Supervisory System and Core Protection Calculators would have maintained their safety system function and would have tripped/alarmed as required to maintain the plant within its design basis. The evaluation demonstrated that sufficient margin would exit throughout the current operating cycle such that the specified acceptable fuel design limits would not have been violated. The NRC Resident Inspector was notified of this retraction by the licensee. R4DO (Jeff Shackelford) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36810 | -1 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-03-17 15:15 | 2000-03-17 16:52 | 2000-04-12 | AS-FOUND TEST VALUES FOR 8 OF 20 MAIN STEAM SAFETY VALVES WERE OUT OF TOLERANCE HIGH. The preliminary results on the analysis of testing of the main steam safety valves indicates that the plant was operating outside the design bases. A hypothetical turbine trip and loss of load accident would have exceeded the design limit for secondary side pressure. The limit for pressure is 1318.5 psig, and preliminary analysis shows a pressure of 1354 psig. The main steam safety valves have since been set to within 1% of the tolerance of the required setpoints for all 20 valves. This action of resetting the valves returned the plant to within the design basis. The licensee notified the NRC resident inspector. * * * UPDATE AT 1630 ON 4/12/00, BY ROCHA RECEIVED BY WEAVER * * * Following the preliminary analysis, the Nuclear Fuel Management Department performed a detailed evaluation of LOCA Analyses and Non-LOCA and Containment Analyses using the test data from the MSSV testing. The limiting event is the LOL/TT (Loss of Load/ Turbine Trip) event, which is part of the Non-LOCA Analyses. For the LOL/TT event, the detailed evaluation utilized certain cycle specific parameters, uncertainty values and instrument response times in place of the conservative analysis of record assumptions. The results of each of the evaluations indicated the acceptance criteria for each of these events were not exceeded, with a calculated peak secondary side pressure of 1308.2 psia. The pressure limit is 1318.5 psia. Therefore, the plant was not outside of the design basis as a result of the high relief setpoints for the MSSVs. The licensee notified the NRC resident inspector. The operations center notified the R3DO(Hiland). | 66 | 0 | 0 | 66 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36809 | 0 | U.S. ARMY |  |  |  |  | 2000-03-17 12:00 | 2000-03-17 15:53 | 2000-04-27 | DISCOVERY THAT AN M43A1 CHEMICAL AGENT DETECTOR CELL MODULE CONTAINING 250 µCi OF AMERICIUM-241 HAD BEEN MISSING FROM FT. BRAGG (NORTH CAROLINA) SINCE APRIL 1996 Late yesterday afternoon (03/16/00), representatives from Ft. Bragg, North Carolina, requested the U.S. Army in Rock Island, Illinois, to help trace files for documentation regarding a cell module that was discovered to be missing from an M43A1 chemical agent detector. (The cell module contained 250 µCi of americium-241.) The most recent documentation found related to the missing cell module indicated that it was last seen at Ft. Bragg in April of 1996. More recent paperwork has not yet been found. The licensee determined this event to reportable at approximately 1200 CST today (03/17/00). The licensee hypothesized that the M43A1 chemical agent detector may have been turned into a maintenance unit at some point. If the device tested with bad air flow, the maintenance unit could have replaced several items including the cell module. At this time, it is believed that the cell module in question may have been removed (without any paperwork) and that the device may have been returned without a replacement cell module installed. The licensee stated that there does not appear to be any likelihood that the general public will get involved with this issue. The licensee plans to submit a 30-day written report to the NRC Region 3 office. (Call the NRC operations officer for licensee contact information.) * * * UPDATE AT 1420 ON 03/30/00 BY MOHS RECEIVED BY WEAVER * * * The module was found on March 23, 2000. The Operations Center notified the R3DO (Gardner) and R2DO (Caudle) and NMSS (Sherbini). ***** UPDATE AT 1631 ON 04/27/00 FROM JEFF HAVENNER TO LEIGH TROCINE ***** Based on a paper trail, the missing item was located at a Defense Logistics Agency (DLA) facility in Anniston, Alabama. The M43A1 chemical agent detector cell module was non-functional and had been removed during maintenance. It was then turned in through channels and sent to this depot facility. The NRC operations officer notified the R3DO (Shear), R2DO (Fredrickson), and NMSS EO (Cool). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36808 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-03-17 10:20 | 2000-03-17 14:15 | 2000-03-17 | LOSS OF TWO DIVISION 2 SERVICE WATER SYSTEM (SWP) PUMPS WHILE ONE DIVISION 1 PUMP WAS OUT OF SERVICE The following text is a portion of a facsimile received from the licensee: "At time 1020 hours on 03-17-00, Nine Mile Point Unit 2 entered Special Operating Procedure (SOP) N2-SOP-11 for loss of service water. Specifically, the Division 2 SWP pumps 2SWP*P1B [and] 2SWP*P1D tripped due to a low flow condition. Operations personnel were restoring the Service Water System (SWP) in accordance with procedure N2-PM-@12, attachment 2, to align Division 1, following the Division 1 AC electrical bus outage. A lead was re-landed in the Division 1 SWP logic. A failed component in this Division 1 SWP logic caused the safety-related to non-safety-related isolation valves to isolate. 2SWP*P1C remained in service when the Division 2 pumps tripped. Subsequently, [the] SWP system was restored to a [one] pump per division line-up. Investigation of the failed Division 1 logic component continues at this time." The licensee stated that 2SWP*P1D was restored to service within approximately 20 minutes and that no fuel moves (as part of a fuel shuffle) were ongoing at the time of the event. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36807 | 0 | THE FOXBORO COMPANY |  |  |  |  | 2000-03-17 | 2000-03-17 09:46 | 2000-03-17 | PART 21 REPORT - LOSS OF GASKET SEAL INTEGRITY ON FOXBORO TRANSMITTER DISPLAY COVERS The Foxboro Company has identified a potential defect with certain Foxboro transmitter display covers manufactured between August 1997 and June 1999. These display covers may not be in compliance with the requirements of leech 1P65 nor NEMA Type-4 Environmental Protection, CENELEC (flameproof), CSA and FM (explosion proof) electrical classification requirements are also affected. A Foxboro investigation was initiated upon the return of a commercial grade display cover which was reported to have lost seal integrity. This investigation found that an unauthorized manufacturing process change occurred between August 4, 1997 (date code 9732) and March 12, 1999 (date code 9911) which allowed an interrupted seal on some portion of the covers manufactured, compromising the environmental and electrical protection requirements. Foxboro is taking immediate action to notify all customers who purchased this product from The Foxboro Company during the time period affected and to provide replacement covers. Indian Point Unit 3 and Cook Units 1 and 2 may be affected by this problem. Foxboro plans to submit a written report to the NRC on this 10 CFR Part 21 Report. (Call the NRC operations center for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21 |  |  |  | 0
36806 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2000-03-16 14:00 | 2000-03-16 18:05 | 2000-03-17 | STATE NOTIFICATION REGARDING A PERSONNEL MEDICAL EMERGENCY The following text is a portion of a facsimile received from the licensee: "Arkansas Nuclear One Unit 1 declared a personnel emergency at 1400 [CST] on 03/16/00 due to a contract employee becoming disoriented while performing a routine task on top of an overhead crane that is located outside of the power block. The individual had performed this task previously without incident. The on-site Emergency Medical Team was activated to provide assistance, and the Pope County Emergency Rescue was requested via 911 to provide assistance in the safe removal of the individual from the crane. The individual was subsequently transported to St. Mary's Regional Medical Center for evaluation via local ambulance service. The individual was conscious and in a stable condition following removal from the crane. This event may result in news coverage." The licensee notified the State and the NRC resident inspector. HOO NOTE: This report was updated to reflect notification of the State of Arkansas. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36805 | 0 | USAF RADIOISOTOPE COMMITTEE |  |  |  |  | 2000-02-16 11:45 | 2000-03-16 16:03 | 2000-03-16 | LOSS OF TWO AMERICIUM-241 SOURCES (4 µCi EACH) DUE TO THE CRASH OF AN F-16 NEAR DONALDSONVILLE, GEORGIA The following text is a portion of a facsimile received from the USAF Radioisotope Committee: "[...] Date [and] Time of Occurrence or Discovery: 16 Feb 2000/1145 [hours]" "[...] Organization Possessing Source(s): 347CRS/LGMVS Moody AFB, GA" "[...] What Happened: [An] F-16 carrying a Low Altitude Navigation Targeting Infrared for Night (LANTIRN) pod crashed (16 Feb 00) in a rural area approximately 10 miles north of Donaldsonville, GA. The Disaster Control Group (DCG) at the scene of the crash confirmed that the F-16 was not [equipped] with a LANTIRN pod. 347CRS/LGMVS, who maintains the pods, notified Lt. Nikel that a pod was on this F-16 and that the DCG had made an error (347CRS notified Lt. Nikel 16 Mar 2000)." "[...] Radioisotope(s) Involved: Am-241 Activity: 2 sources/4 [µCi] each" "[...] Sealed Source Model/Serial No.: Model AMM.7 Amersham, Inc." "[...] Actions Taken to Correct or Abate: The DCG moved all aircraft material from the crash site to Moody AFB, GA. Lt. Nikel will take a team to the DCG storage areas and attempt to search for the pod in the debris." "[...] Additional Actions Planned and Estimated Time to Complete: An interim or final report will be provided to [the] NRC by 11 April 2000 on disposition of the sources. An investigation will be performed to try and determine why the DCG failed to identify that the F-16 was carrying a LANTIRN pod." "[...] Additional/Follow-up Information: Sealed Source Device Registry No. NR-136-S-208-S." (Call the NRC operations officer for contact information.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | GA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36804 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-03-16 13:32 | 2000-03-16 15:57 | 2000-03-16 | STEAM GENERATOR BLOWDOWN DUE TO FAILURE OF A RADIATION MONITOR The following text is a portion of a facsimile received from the licensee: "Radiation monitor R-15 air ejector exhaust detector failed low resulting in [a] steam generator blowdown isolation. [The] failure occurred at 1332 [CST] on 03/16/2000. The detector had been replaced earlier in the day and had been returned to service at 1105 [CST]. All systems responded as designed including steam generator blowdown isolation, steam generator blowdown sampling isolation, and isolation of heating steam to the warehouse annex. [The] cause is unknown, and an investigation has been initiated. [Offsite Dose Calculation Manual (ODCM)] compensatory measures have been implemented. Health Physics has been directed to obtain grab samples of the air ejector discharge as least once per 12 hours and analyze the samples for gross activity within 24 hours." The licensee notified the NRC resident inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36803 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2000-03-15 02:15 | 2000-03-16 15:22 | 2000-03-22 | LICENSEE SUPERVISOR ARRESTED AND CHARGED WITH FELONY POSSESSION OF A CONTROLLED SUTSTANCE The following text is a portion of a facsimile received from the licensee: "[At 0215 CST on 03/15/00, a] licensee supervisor was arrested and charged with felony possession of a controlled substance. The individual's unescorted access was immediately revoked upon discovery of the event [at] 1510 [CST] on [03/15/00]. A licensee investigation has been initiated to obtain additional details related to this off-site event." "The NRC [resident inspectors] and licensee senior management [have] been informed." Call the NRC operations officer for additional details. * * * UPDATE 1714 3/22/2000 FROM DAVID HANKS TAKEN BY BOB STRANSKY * * * The individual tested positive for drug use after being administered a for-cause test by the licensee following the arrest. The individual's unescorted access remains suspended. The licensee is currently reviewing work performed by this individual. The NRC resident inspector has been informed of this update by the licensee. Notified R4DO (Yandell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.73 |  |  |  | 0
36802 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-03-14 13:41 | 2000-03-16 12:12 | 2000-03-16 | MECHANICAL BINDING OF FIRE DAMPERS DURING SURVAILLANCE TESTING At 1341 on 03/14/00 during performance of a main transformer deluge test, three of eight fire dampers in the cable spreading room failed to drop. They were mechanically bound because of improper installation of the fusible links which were installed on 12/23/99. The licensee stated that all other systems functioned as required. An extent of condition review is currently in progress. This event was determined to be reportable at 1205 on 03/16/00. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36801 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-03-15 21:15 | 2000-03-15 22:38 | 2000-03-15 | PLANT HAD ESF ACTUATION DUE TO A HIGH RADIATION ALARM While performing fuel sipping in the unit 1 spent fuel pool, rad monitors R25A and R25B upscaled with R25B going into high alarm. The alarm activated both trains of the penetration room filtration system and secured the spent fuel pool ventilation system. The alarm was valid due to a leaking fuel assembly that was discovered during the fuel sipping activity. There was no indication of any radiation release, fuel sipping operations were suspended and evacuation of the spent fuel pool was initiated. They have not yet secured all of the actuations. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36800 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-03-15 15:32 | 2000-03-15 17:03 | 2000-03-15 | OFFSITE NOTIFICATION MADE TO THE MICHIGAN DEPARTMENT OF ENVIRONMENTAL QUALITY(MDEQ) Cooling tower water was identified to be leaking from the south cooling tower to the ground. The water accumulated and ran over land to the overflow canal which lead to the Swan Creek. Samples were obtained to determine if chlorine could be detected in the water flowing to the overflow canal. Communication was made with Corporate Environmental and it was determined that this event is reportable to the State of Michigan. The spill reaching the surface water was discovered at 1150 on 03/15/00. Temporary earthen dikes have been installed to stop flow to the overflow canal. Initial studies indicated that no detectable chlorine reached the surface water. Follow-up samples will be obtained from the overflow canal and near the point where the overflow canal meet Swan Creek. A temporary deflector is being installed to route the water back into the tower instead of allowing it to flow to the ground. A permanent fix will be installed in April 2000 during the refueling outage. The State MDEQ was contacted at 1532. The NRC Resident Inspector was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36799 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-03-15 15:11 | 2000-03-15 16:58 | 2000-03-15 | SAFEGUARD SYSTEM VULNERABILITY DUE INABILITY TO RESPOND TO PERIMETER ALARMS AROUND THE PROTECTED AREA BECAUSE OF ADVERSE WEATHER CONDITIONS. IMMEDIATE COMPENSATORY MEASURES NOT TAKEN UPON DISCOVERY; HOWEVER, THEY ARE NOW FULLY IMPLEMENTED. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED. CONTACT THE NRC OPERATIONS CENTER FOR ADDITIONAL DETAILS. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 0
36798 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 1999-12-27 19:52 | 2000-03-15 15:55 | 2000-03-15 | PLANT HAD ACTUATION OF THEIR STANDBY GAS TREATMENT AND ANNULUS MIXING SYSTEMS On December 27, 1999, at 1925 (CST), an unplanned automatic actuation of the standby gas treatment and annulus mixing systems occurred. The initiating signal originated in radiation monitor 11B, which monitors the reactor building annulus for gaseous activity. Grab samples of the annulus atmosphere were taken, and were found to be normal. The 11A radiation monitor in the same process stream likewise indicated no presence of radioactivity. The filter cartridge in the 11B radiation monitor was changed, and its indication returned to normal. The standby gas treatment and annulus mixing systems were returned to their normal lineup. This event is being reported in accordance with 10CFR50.72(b)(2)(ii) as an event that resulted in the automatic actuation of an engineered safety feature. An investigation of the event found that the filter cartridge in the 11B radiation monitor was incorrectly installed, such that particulate matter could reach the sample chamber. The monitor is designed to detect gaseous radioactivity, and the purpose of the filter assembly is to keep particulate matter out of the sample chamber. There is a charcoal cartridge in the upstream of the filter to remove iodine. The detector in the sample chamber was determined to be responding correctly, and it is postulated that a transient particle from the charcoal cartridge bypassed the filter element, and was detected in the sample chamber. The event was not reported within the timeframe required by 10CFR50.72, because there was no corroborating evidence that radioactivity sufficient to actuate the ventilation process monitors was present in the annulus. Subsequent discussion with the NRC has determined that this event was reportable on 3/15/00 @ 1450 CST. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36797 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-03-15 10:36 | 2000-03-15 14:15 | 2000-03-15 | THE PLANT ENTERED A 72 HOUR LCO ACTION STATEMENT DUE TO AN INOPERABLE HIGH PRESSURE COOLANT INJECTION SYSTEM. On 3/15/2000 at 1036 hours, the High Pressure Coolant Injection System (HPCI) Reactor Vessel Water Level 8 turbine trip was inadvertently received while performing surveillance 44.030.254, ECCS - Reactor Vessel Water Level (Levels 1, 2, and 8) Division 2 Channel D Functional Test. The ability for HPCI to add water to the reactor vessel at Level 2 may have been inhibited with the Level 8 HPCI turbine trip initiated. This may have made the HPCI system inoperable. The cause of the problem is currently under investigation. The Level 8 HPCI turbine trip was reset at 1112 hours. Technical Specifications 3.5.1.E, emergency core cooling systems, and 3.3.5.1.C, emergency core cooling system instrumentation, were entered. The plant has 72 hours to return HPCI to operable condition or be in hot shutdown within the following 12 hrs. This report is being made in accordance with 10 CFR 50.72 (b)(2)( iii)( D), any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems necessary to mitigate the consequences of an accident. The NRC Resident Inspector will be informed. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(iii)(D) |  |  | 0
36796 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-03-14 22:45 | 2000-03-15 00:58 | 2000-03-15 | - ESF ACTUATIONS DURING A RELAY REPLACEMENT CAUSED BY AN ELECTRICAL SHORT - While replacing the relay for TIP withdrawal & RHR valve #2A71B-K5C in Reactor Protection System relay panel #2H11-P609, an electrician caused an electrical short which resulted in the following: - Units 1 & 2 Standby Gas Treatment System actuation (1A, 1B, 2A and 2B trains/fans started) - Units 1 & 2 Outboard [B] Reactor Building Ventilation System isolation - Units 1 & 2 Outboard [B] Refueling Floor Ventilation System isolation - Discovered Group 2 Outboard Post Accident Sampling Isolation Valve #2E41-F121 closed - Discovered Group 2 Outboard Fission Product Monitor Valve #2D11-F072 closed The licensee is investigating the cause of this event. The licensee plans to return the above systems and components to normal status as soon as possible. The licensee plans to notify the NRC Resident Inspector. Refer to related event #36795. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36795 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-03-14 13:18 | 2000-03-14 16:12 | 2000-03-14 | THE PLANT HAD AN ESF ACTUATION WHILE PERFORMING A LEAK RATE TEST. While performing leak rate testing on 2E11-F041D, Drywell Pressure Sensing Line Isolation Valve, a High Drywell Pressure Signal was received resulting in the following actuations: Reactor Scram Signal (RPS),(no rod motion) Unit 1 and Unit 2 Standby Gas Treatment System actuation, Unit 1 Reactor Building Ventilation isolation. Group 2 Isolation of: Drywell Sump Isolation Valve (2G11-F004), Post Accident Sampling Valve (2E41-F121), Fission Product Monitor Valve (2D1 l-F072), and Unit 1 and Unit 2 Refueling Ventilation Isolation. Other valves did not activate on the Group 2 Isolation signal from High Drywell Pressure because they were out of service for refueling outage maintenance activities. Investigation is ongoing as to the cause of this event. All systems have been returned to normal status. The NRC Resident Inspector will be notified. Refer to related event #36796. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36794 | 0 | DEPARTMENT OF THE ARMY |  |  |  |  | 2000-03-13 12:00 | 2000-03-14 14:52 | 2000-03-14 | THE DEPARTMENT OF THE ARMY REPORTED A CHEMICAL AGENT DETECTOR (CAD) WAS LOST AT FT. HOOD, TX. A M43A1 CAD CONTAINING 250 MICROCURIES OF AM-241 WAS LOST FOLLOWING A FIELD TRAINING EXERCISE AT FT. HOOD, TX. THE DEVICE WAS RUN OVER BY A VEHICLE ON 3/1/00 AND UPON RETRIEVAL, THE PIECES WERE PLACED IN TWO OPAQUE PLASTIC BAGS AND TAKEN BACK TO THE INSTALLATION WHERE IT WAS DETERMINED (ON 3/7/00) THEY HAD BEEN LOST. IT IS BELIEVED THAT THE TWO BAGS WERE DISCARDED WITH THE TRASH IN THE ON-POST LANDFILL. A SEARCH OF THE LANDFILL WAS IMPLEMENTED, BUT THE BAGS COULD NOT BE FOUND. SINCE THE GENERAL PUBLIC DOES NOT HAVE ACCESS TO THIS LANDFILL, THE ARMY HAS TERMINATED ITS SEARCH. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
36793 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-13 22:25 | 2000-03-14 08:40 | 2000-03-14 | 24-HOUR NON-CFR REPORT INVOLVING ACTUATION OF A SAFETY SYSTEM DUE TO A VALID SIGNAL "At 2225 on 03/13/00, the PSS office was notified that a primary condensate alarm was received on the C-333A position 2 North autoclave Water Inventory Control System (WICS). The WICS system is required to be operable while heating in mode 5 according to TSR 2.2.4.2. The autoclave was checked according to the alarm response procedure, removed from service and the Water Inventory Control System was declared inoperable by the Plant Shift Superintendent. Troubleshooting was initiated and is continuing in order to determine the reason for the alarm. "The safety system actuation Is reportable to the NRC as required by Safety Analysis Report, section 8.9, table 1 criteria J.2, Safety System actuation due to a valid signal as a 24-hour event notification. "The NRC resident inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36792 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-03-14 00:35 | 2000-03-14 04:01 | 2000-03-14 | MANUAL PHASE "A" AND CONTAINMENT VENT ISOLATION INITIATED DUE TO SHUTDOWN LOSS OF COOLANT ACCIDENT (LOCA). "Unit 1 was in Mode 5 with Cycle 10 refueling outage in progress. At 0017 on 3/14/00 with RCS temperature at 145 F and RCS pressure at 330 psig. Unit 1 entered Abnormal Operating Procedure R.02 (Shutdown LOCA) due to decreasing pressurizer level. A manual Phase A and Containment Vent Isolation were initiated at 0035 as required by procedure. The loss of RCS coolant was initially contained in the Pressurizer Relief Tank (PRT) until the PRT rupture disc ruptured. At 0125, AOP R.02 was completed and plant conditions were stabilized with RCS temperature at 156 F and RCS pressure at 145 psig. At present there is no RCS leakage, plant conditions are stable, and suspected cause is the RHR suction or discharge piping relief valve. Investigation is in progress." The transient lasted approximately 30 minutes. The licensee suspects that when RCS pressure was lowered per the AOP, the relief valve reseated. There is no estimate of the lost RCS inventory at this time. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36791 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2000-03-14 00:05 | 2000-03-14 03:11 | 2000-03-14 | UNIT 1 MANUALLY TRIPPED FOLLOWING A FAILURE OF THE MAIN TURBINE GOVERNOR VALVES CONTROL SYSTEM "The Unit 1 Reactor was manually tripped following a failure of the main turbine governor valves control system. This failure resulted in the main turbine governor valves inadvertently going closed. At the time of the event, Unit 1 was at 82% power and proceeding to 100% power following the completion of maintenance outage 1P-00-2. "Unit 1 has been stabilized in Hot Shutdown (550 degrees F, 2125 psig, and the reactor is subcritical). No radioactive releases have occurred nor are any planned." Prior to the transient the turbine governor valve position limit was acting erratically. All control rods fully inserted. Following the trip, primary pressure increased to 2300 psig. Three(3) of eight(8) mainsteam (MS) safeties lifted and reseated on each MS header. Also, Bus "1H1" which supplies power to two Reactor Coolant Pumps (RCPs) was slow in transferring to the startup transformer. This resulted in both "P32A" and P32C" RCPs tripping. The 1H1 bus remained energized during the transient. Unit 1 is currently removing decay heat using RCPs "P32B" and P32D" (one operating in each reactor coolant loop) with steam discharging to the Main Condenser. All safety-related equipment including the Emergency Diesel Generators (EDGs) is available, if needed. I&C is investigating the cause of the governor valves' control system failure and the Relay Department is evaluating the slow bus transfer. The licensee informed the NRC Resident Inspector and the State of Arkansas. | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(vi) |  |  | 0
36790 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-13 19:57 | 2000-03-13 22:00 | 2000-03-13 | 4 HOUR 91-01 BULLETIN RESPONSE The Plant Shift Superintendent(PSS) was notified of two seal test buggies on the cell floor of the X-333 facility containing a vacuum pump whose oil reservoir volume was greater than the NCSA PLANT 069.A00 requirement of a 1 quart reservoir. Boundaries were placed around the buggies and the buggies were made inoperable to prevent use. The NCSE allows 3 quarts for normal operations and an analyses for 5 quart reservoir for "abnormal operations." Therefore, the safety significance is low since the pumps supplied by the manufacturer have a reservoir volume of more than 3 quarts due to a design modification. The site only had 4 pumps (two installed and two on the shelf) with this design modification. SAFETY SIGNIFICANCE OF EVENTS: The safety significance of this event is low. The NCSE evaluates a pump filled to a capacity of 5 quarts and shows the system to remain subcritical. NCSE- PLANT 031 .E03, for similar carts, modeled a cart with a 5 quart vacuum pump adjacent to another cart and found that the system to be subcritical with a Keff +2q (sigma) of 0.841. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): The Kinney model vacuum pump has a volume capacity of less than 4 quarts. For a criticality to occur, a cart with a pump with a capacity of 5 quarts would have to be used. The chemical traps in front of the pump would have to be empty or saturated such that the pump oil becomes saturated with uranium, and a spacing violation would have to occur. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The controlled parameters in this NCSA are volume and interaction. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The carts are approved for use with 100% enriched material. The form of the material is uranium in oil. This system has been modeled and the Keff +2q(sigma) determined to be 0.841 for this upset. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The pump has been modified by the manufacturer to hold more than 3 quarts CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Established conditions as required by the Anomalous Condition procedure. The double contingency cannot be established within 4 hours and is reportable. The NRC Resident Inspector and DOE Representative were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36789 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-03-12 04:49 | 2000-03-12 05:41 | 2000-03-12 | UNIT 1 COMMENCED A TECH SPEC REQUIRED SHUTDOWN AFTER DECLARING THE REFUELING WATER STORAGE TANK (RWST) INOPERABLE DUE TO THE INABILITY TO CLOSE A MANUALLY OPERATED RWST VALVE. "At 0230 hours, on 3/12/00, it was noted that a Surry Power Station Unit 1 Refueling Water Storage Tank (RWST) suction valve (1-CS-27) that was being used for purification purposes, could not be closed. The valve had been opened under administrative control, as allowed by procedure. The Unit 1 RWST was declared inoperable, and a 1 hour LCO was entered in accordance with Technical Specifications. The 1 hour LCO expired at 0330 hours on 3/12/00, and a 6 hour LCO to hot shutdown was entered in accordance with Technical Specifications. "At 0449 hours, Surry Power Station Unit 1 initiated a plant shutdown from 96% power as required by Technical Specifications, in order to meet the 6 hour LCO. The ramp was stopped at 0459 hours at 93% power, after the valve was mechanically closed. An evaluation of the valve is currently being pursued. "This report is being made pursuant to 10CFR50.72(b)(1)(i)(A), Power Mode Reduction Required by Technical Specifications." The valve involved is a manual grinnel diaphragm valve which appears to have the spindle threads stripped. Maintenance personnel closed the valve by jacking it shut. This particular valve is used for sampling and purification of the RWST and does not interfere with the main suction path used for ECCS. The licensee informed the NRC resident inspector. * * * UPDATE 0945EST ON 3/12/00 FROM DARLENE BROCK TO S.SANDIN * * * The licensee provided the following information as an update: "This is an update to Event #36789. At 0551 hours, on 3/12/00, 1-CS-27 was closed using a Jacking device. In addition, 1-CS-31 and 1 -CS-28 (suction isolation valves on the recirculation pumps) were closed. At 0657 hours the Unit 1 Refueling Water Storage Tank was considered operable. The 6 hour LCO to hot shutdown was exited at 0657 hours on 3/12/00 with the Unit stable at 93% power. Surry Power Station Unit 1 was ramped down from 96% power to 93% power during the 6 hour LCO. At 0900 hours, on 3/12/00, a ramp was commenced to return power on Unit 1 to 96%." The licensee informed the NRC resident inspector. Notified R2DO (McAlpine). | 93 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36788 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2000-03-11 14:30 | 2000-03-11 16:07 | 2000-03-22 | DEFECT DETECTED DURING EDDY CURRENT INSPECTION OF STEAM GENERATOR "Turkey Point is performing eddy current testing of the Unit 3 steam generators in accordance with Plant Technical Specifications and Industry Guidance. A 20% inspection was planned for the top of tubesheet expansion transition region in the hot leg of each steam generator. This total planned sample was divided into 1st, 2nd and 3rd samples to address the progressive inspection process of the Technical Specifications Table 4.4-2. The 1st sample of 96 tubes in the 3B steam generator resulted in detection of 1 defect near the top of the tubesheet. In accordance with Technical Specification 4.4.5.5c, this defect results in a C-3 Classification for the 1st sample. "A small number of additional indications near the top of the tubesheet have also been detected in this steam generator, and the inspection is ongoing. The inspection will be expanded to 100% of the tubes in the 3B steam generator. "Eddy current results indicate the defects are shallow volumetric or pit-like in nature. A preliminary structural evaluation indicates that all indications detected to date meet the structural and leakage integrity performance criteria of NEI 97-06, 'Steam Generator Program Guidelines.'" The NRC resident inspector has been informed of this notification by the licensee. * * * UPDATE 1537 3/22/2000 FROM MOWREY TAKEN BY STRANSKY * * * "The steam generator inspection effort at Turkey Point Unit 3 was completed on March 16, 2000. The scope of inspection was expanded to 100% of the hot leg top of tubesheet for all three steam generators. Scope expansion for the 3B steam generator was driven by Technical Specification requirements. Scope expansion for the 3A steam generator was driven by the performance criteria contained in NEI 97-06, 'Steam Generator Program Guidelines.' Scope expansion in the 3C steam generator was pursued as a prudent measure due to the results in the 3A and 3B steam generators. "The total number of tubes plugged during this inspection were as follows: "3A SG: 7 tubes for ID circumferential indications, 3 tubes for OD circumferential indications, 13 tubes for OD volumetric indications and 2 tubes for wear indications. Total of 25 tubes plugged. "3B SG: 2 tubes for ID circumferential indications, 3 tubes for OD circumferential indications, 22 tubes for OD volumetric indications and 1 wear indications. Total of 28 tubes plugged. "3C SG: 6 tubes for ID circumferential indications, 2 tubes for OD circumferential indications, 6 tubes for OD volumetric indications and 2 wear indications. Total of 16 tubes plugged. "An investigation has been conducted to determine the cause of the tube degradation identified during this inspection. This investigation included a review of the steam generator design features, manufacturing information, inspection techniques, and historical and current chemistry programs. Due to the lack of prior inspection data, and the limited number of defects identified by the industry for thermally treated alloy 600 tubing, the results are inconclusive for the circumferential and volumetric indications. The potential causes for these mechanisms are suspected to be original manufacturing anomalies, inspection anomalies, or corrosion attack. The number of indications found is attributed to an inspection transient resulting from first time extended use of rotating probe technology at Turkey Point. "The corrective measures taken to prevent recurrence of the potential causes of degradation are as follows: "* The inspection was expanded to cover 100% of the hot leg areas affected by the circumferential and volumetric indications in order to provide a complete baseline with the rotating probe technology. "* The chemistry program is continually reviewed for enhancement opportunities and compliance with the latest industry guidance. Turkey Point has initiated the addition of ethanolamine (ETA) to reduce iron transport to the steam generators. "* Aggressive sludge removal techniques have been incorporated including high volume bundle flushing. "* The latest industry inspection guidelines will continue to be implemented, to ensure adequate inspections are conducted. "Mechanical wear indications have been tracked for Turkey Point Unit 3 since the fourth cycle of operation for the current steam generators (1990). The cause of this type of degradation is a well understood design issue. Tubes with wear indications were plugged based on qualified sizing techniques. Tubes plugged for mechanical wear were not the cause of the 10CFR50.72 notification." The NRC resident inspector has been informed of this update by the licensee. Notified R2DO (Decker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36787 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-03-10 11:48 | 2000-03-11 08:24 | 2000-03-11 | ELECTRICAL SEPARATION REQUIREMENTS WERE VIOLATED This event notification was called under License Condition 2.G. - 24 hour License Notification On Monday, March 6, 2000 defueling operations were ongoing at South Texas Project Unit 1 to support the current refueling outage. A temporary modification was installed on that date in a Safety Related "B" Train Load center to supply non-class power to one of the two spent fuel pumps. This modification was installed to ensure "B" train related pump remained available while fuel was being loaded into the spent fuel pool. The other pump was supplied with Class 1E power and was backed up by a diesel. The modification involved running non-class cables in and around the Class 1E load center. On March 10th it was determined that since electrical separation requirements [class to non-class] were violated the load center was rendered inoperable as well as the electrically supported equipment. One component affected was the "B" Train containment isolation valve for normal purge. If the valve is inoperable Technical Specification 3.9.9, Containment Ventilation Isolation System, requires that the normal purge penetration be closed during core alterations. During the time frame that the valve was inoperable fuel movement took place with the normal purge in operation (I.e., the penetration was open). This is in violation of Technical Specification requirements. The NRC Resident Inspector will notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
36786 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-03-10 18:45 | 2000-03-10 20:05 | 2000-03-10 | POTENTIAL TO DAMAGE EDG WHEN PARALLELED TO OFFSITE POWER SOURCE "It has been determined that there exists the potential for an unanalyzed interaction between the Static VAR Compensators and a diesel generator when paralleled with an offsite power source. This unintended interaction has been determined to constitute an event or condition during operation that results in the nuclear power plant being in a condition that is outside the design basis of the plant. This condition has been documented in a Condition Report and entered into the plant corrective action program. "Discussion: "Static VAR compensators (SVCs) are installed on the secondary side of the reserve auxiliary transformer (RAT) and the emergency reserve auxiliary transformer (ERAT) to address potentially inadequate grid voltage conditions assuming a loss of coolant accident (LOCA) and unit trip. One SVC is installed on the secondary (4.16 kV) side of the RAT and one SVC is installed on the secondary side (4.16 kV) side of the ERAT. The RAT is associated with the offsite 345 kV transmission system and the BRAT is associated with the offsite 138 kV transmission system. These two transmission systems constitute the two required offsite electrical power sources for the plant's three Class 1E 4.16 kV buses, Each Class 1B 4.16 kV buses is also capable of being supplied by a dedicated diesel generator. "The design of the SVC is described in a Design Report that was included as Attachment 5 to the CPS license amendment submittal dated May 4, 1998 (letter U602972). During parallel operations between the diesel generator and the offsite power source via either the RAT or the ERAT, the SVCs are designed to 'freeze' such that their design function of regulating voltage on the secondary side of the RAT and the BRAT does not result in detrimental interaction between its control circuits and the control circuits of the diesel generator. The action of freezing the SVC control circuit ensures that the SVCs do not attempt to counter bus voltage transients inherent in the process of synchronizing the diesel generator to its respective Class 113 bus. The freeze signal is derived from auxiliary contacts on die diesel generator output breaker and the Class 1E bus feeder breakers. "During the root cause investigation into the damage incurred by the Division III diesel generator during a routine surveillance (apparently involving a synchronization attempt with an out-of-synchronization condition), it was determined that a small time delay inherent in the electrical interlock circuitry for the freeze signal allowed the SVC to detrimentally interact with the diesel generator since the SVC freeze condition is not immediately effected upon closure of the diesel generator output breaker. The damage to the Division III diesel generator was previously reported in event number 36736. Although the potential for interaction had been recognized and compensated for in the design, the effect of the longer than expected time delay had not been recognized. Therefore, the effects of the unanalyzed time delay introduced an increased probability of malfunction of equipment important to safety resulting in a design configuration that constitutes an unreviewed safety question as defined in 10 CFR 50.59. "This configuration has been determined to constitute a condition that is outside the design basis of the plant. The design requirement for the SVCs is to assist in maintaining secondary side voltages on the RAT and ERAT within acceptable values consistent with the offsite source 'capacity and capability' requirements of General Design Criterion (GDC) 17. A second requirement was that the SVCs not negatively impact plant structures, systems, and components such that an increase in the probability of a malfunction of equipment important to safety exists. Contrary to the above requirements, the current design of thc SVC controls is such that during synchronization of the diesel generator to its Class 1E bus the potential exists for the SVC to negatively impact bus voltage. As a consequence of the adverse voltage control during the diesel generator synchronization, the potential exists for the SVC response to degrade or impair the function of the diesel generator resulting in an increased probability of malfunction of equipment important to safety. "This design deficiency exists only under the limited circumstances during the conduct of diesel generator surveillances in which the diesel is paralleled with the offsite power source. The postulated duration of the unanalyzed condition is a fraction of a second following the closure of the diesel generator output breaker. This is the approximate length of time required for the SVC control circuits to enter the freeze mode after closure of the diesel generator output breaker. Prior to the breaker closure and following the small time period of the unanalyzed condition, the diesel generators and the offsite power circuits are capable of performing their intended design functions during parallel operations. The Onsite AC Sources Limiting Conditions for Operation (LCO) specified in Technical Specifications 3.8.1 and 3.8.2 are satisfied. "AmerGen is currently pursuing a plant modification to resolve this design deficiency as soon as possible to support testing of the diesel generators." The NRC resident inspector will be informed of this notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36785 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-03-10 16:20 | 2000-03-10 18:13 | 2000-03-10 | SHIELD BUILDING VENTILATION FILTER TRAIN FLOW OUTSIDE OF SPECIFICATION While performing an administrative review of the results of surveillance test SP 24-122, "Shield Building Vent Filter Testing," performed on 7/27/1999, the licensee determined that train "B" was outside of specification for fan flow rate. The required flow rate is 6200 SCFM +/- 10%, while measured flow was 5427 SCFM. The Updated Final Safety Analysis Report (UFSAR) assumes a flow rate of 5000 SCFM. Shield building vent train "B" was declared inoperable at 1620 on 3/10/2000, and the unit entered 7-day Technical Specification Limiting Condition for Operation (LCO) 3.6.b.1. The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRAD COND DURING OP | UNANALYZED COND OP |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii) | 50.72(b)(1)(ii)(A) |  |  | 0
36784 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-03-09 22:57 | 2000-03-10 17:58 | 2000-03-10 | COURTESY NOTIFICATION REGARDING ONSITE FATALITY At 2357 on 3/9/2000, a Duke temporary employee was pronounced dead at the Piedmont Medical Center. The individual had collapsed at the site, and attempts to resuscitate the individual were unsuccessful. The licensee made a courtesy notification to the Occupational Safety and Health Administration (OSHA) regarding this occurrence. The NRC resident inspector has been informed of this notification by the licensee. | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0
36783 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-03-09 14:30 | 2000-03-10 13:01 | 2000-03-10 | NOTIFICATION TO FEDERAL ENERGY REGULATORY COMMISSION The licensee notified the Federal Energy Regulatory Commission (FERC) regarding the inoperability of the spillway diesel generator. The diesel generator was inoperable while batteries were being replaced. The diesel generator is now fully operable. The NRC resident inspector has been informed of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36782 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-09 03:32 | 2000-03-09 17:04 | 2000-03-11 | 24-HOUR NRC BULLETIN 91-01 REPORT "At 0332 hours on 03/09/2000, it was identified that an error had been made in connecting a cell calibration test buggy, covered by NCSA-PLANT069, at X-330 building cell 31-3-9. The cell was connected to the HI DAT (HI DATUM) port instead of the PROCESS inlet port. The NCSA identifies installed chemical traps on the test buggy as a passive design characteristic relied upon to prevent an accumulation of uranium in the vacuum pump oil. The installed traps are also a control contingency in preventing back flow of vacuum pump oil to the cell manifold. Connection of the process system to the HI DAT port bypassed these chemical traps and provided a direct flow path between the process gas system and vacuum pump. "Establishing a connection between the vacuum pump and cell process gas manifold constitutes a loss of one control of the double contingency control principle. The cell calibration buggy was disconnected and it was determined that no oil from the vacuum pump had migrated through the buggy to the cell manifold. The potential for a criticality to occur is precluded based on the amount of oil contained in the vacuum pump and by the assay of the material at that point of the cascade. Pull compliance with NCSA-PLANT069 was regained when the calibration buggy was disconnected from the cell manifold. "There was no loss of hazardous/radioactive material or radioactive/radiological contamination exposure as a result of this event. "SAFETY SIGNIFICANCE OF EVENTS: "This event has a low safety significance. Due to operator error, the cell was connected to the wrong inlet port This allowed the possibility that process gas could bypass the chemical trap(s) and then collect in the oil reservoir of the vacuum pump. The oil reservoir (limited to <= one quart) is sized such that it is safe for 100% enriched material. The process gas that may have entered the oil reservoir of the pump is approximately 2.25% enriched. There is insufficient oil In the vacuum pump for a criticality to occur. Additionally the test buggy has been disconnected from the cell. Thus, there is no possibility of adding additional uranium to the oil reservoir of the vacuum pump. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "For a criticality to occur, sufficient UF6 would need to collect in the oil reservoir of the vacuum pump and the vacuum pump would need to be replaced with a different model such that the oil reservoir is large enough (greater than 3 quarts) for a criticality to occur. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "This NCSA relied on preventing the accumulation of process gas from collecting in the vacuum pump oil by placing a chemical trap upstream of the vacuum pump. This control was lost. The second control was to limit the amount of oil in the vacuum pump to less than 1 quart, which is less than the minimum volume of oil required for a criticality at 100% U235. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "At this time it is not known if any UF6 reached the oil reservoir for the vacuum pump. Enrichment in cell 31-3-9 is estimated to be 2.25% U-235. If process gas reached the oil reservoir, it would be in the form of UF4/oil mixture. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "Nuclear criticality safety is maintained by two controls, the first Is the placement of chemical traps upstream of the vacuum pump. This control was lost. The second control was on the allowed volume of oil in the reservoir of the vacuum pump. This control was maintained throughout the event. Thus, one control relied on for double contingency was lost." The NRC resident inspector has been informed of this notification. * * * UPDATE ON 03/11/00 AT 0128 ET FROM ERIC SPAETH TAKEN BY MACKINNON * * * It was discovered that the internal volume of the oil reservoir in the vacuum pump was greater than the NCSA control limit of less than or equal to one quart. The actual volume of the reservoir is approximately one and one third quart (The manufacturer recommends that the vacuum pump oil level should be 1.33 quarts). At the time of the initial notification, it was not known that the oil reservoir was greater than the NCSA controlled limit. However, this volume is still within the three quart volume analyzed in the NCSE for the normal case condition. Therefore, the safety significance of this event remains low. The Certificate holder said that the NCSA limit for oil will be increased. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The second control parameter was also lost which was to limit the oil level in the vacuum pump to less than one quart. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The second control was lost (oil level greater than one quart) when it was discovered that the volume of the oil reservoir exceeded the allowed volume in the NCSA. Even though the volume of the reservoir exceeded the allowed amount it was still within the three quart limit analyzed in the NCSE for the normal case condition. R3DO (Roger Lanksbury) and NMSS (Tom Essig) notified. The NRC Resident Inspector was notified of this event update by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36781 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-03-09 09:18 | 2000-03-09 14:56 | 2000-03-09 | CONTROL ROOM VENTILATION PLACED IN PRESSURIZATION MODE DUE TO SMOKE At 0906 PST, rod drive motor/generator set 1-2 tripped due to overcurrent. Heavy smoke from burnt insulation was observed in the vicinity. In order to prevent the smoke from entering the control room, the shift foreman directed operators to manually place the control room ventilation system in pressurization mode (mode 4). The NRC resident inspector will be informed of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36780 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-03-09 13:47 | 2000-03-09 14:54 | 2000-03-09 | UNITS OUTSIDE OF DESIGN BASIS DUE TO 10 CFR PART 50, APPENDIX R ISSUE Following is the abstract of an engineering document submitted to the NRC Operations Center: "As part of the continuing resolution of fire protection program issues identified during a Follow-up Fire Protection Functional Inspection at St. Lucie in December 1999, a detailed review of Appendix R circuit separation and protection for the Units 1 & 2 containment was performed. This review considered the design and licensing basis for these features as described in the Unit 1 & 2 Updated Final Safety Analysis Reports (UFSARs), associated NRC Safety Evaluation Reports (SERs), Appendix R requirements and guidance provided in Generic Letter 86-10. The review has identified a number of separation issues for various safe shutdown circuits and/or components credited for post-fire safe shutdown operations following a fire in containment. The affected equipment is hi/lo pressure interface equipment along with control and indication equipment associated with the reactor coolant system." The discrepancies noted in the report affect the power operated relief valves (PORVs), as well as pressurizer pressure and level instrumentation. The licensee has determined that the conditions do not affect operability of the affected equipment due to the low combustible material loading inside the containment and the low probability that a fire would occur inside the containment. The NRC resident inspector has been informed of this report by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36779 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2000-03-09 10:54 | 2000-03-09 12:42 | 2000-03-09 | CONTROL ROOM DOSE RATE EXCEEDS STANDARD REVIEW PLAN LIMIT "The Fort Calhoun Station is in the process of revising and reanalyzing the radiological consequences analysis for the plant as a result of corrective actions for LERs 1998-012 and 1998-013. In the process it has been determined that some of the assumptions made when the plant was constructed in the early 1970s, about 30 years ago, need to be validated. An important assumption that was brought into question was that the Control Room has zero (0) standard cubic feet per minute (SCFM) unfiltered inleakage. The control room envelope was recently tested and the unfiltered inleakage was determined to be very small at 8 SCFM. This level of leakage leads to a thyroid dose to the operators of about 32 rem. The Fort Calhoun Station USAR commits the station to NRC Standard Review Plan (SRP) section 6.4 which states that the thyroid dose to the operators shall be no higher than 30 rem. Higher thyroid doses have been approved for other plants and the dose projected certainly would not incapacitate an operator. The calculated dose is in excess of the current plant design basis. "Plant actions to date have included putting in place an Safety Analysis for Operability (SAO) (similar to a Justification for Continued Operation [JCO]) to allow the plant to continue operating in this condition. The plant has been in communication with the NRC staff on the progress of this radiological consequences reanalysis." The NRC resident inspector has been informed of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36778 | 0 | PUBLIC SERVICE ELECTRIC AND GAS CO. |  |  |  |  | 2000-03-09 | 2000-03-09 12:15 | 2000-03-09 | 10 CFR PART 21 REPORT Replacement emergency diesel generator (EDG) air start motors were supplied to PSE&G with grease on the bendix drive shafts. This did not meet the requirements of the purchase order which stated: "Do not grease the bendix drive: as per the vendor manual this is to be lubricated with SAE 10 oil." Excessive grease on the bendix shaft could harden and prevent the drive pinion from engaging the ring gear on the EDG flywheel during starting. The air start motors were supplied by: BFGoodrich Company (formerly Coltec Industries) Fairbanks Morse Engine Division 701 White Avenue Beloit, WI 53511 Affected FMED Part #s: 21800136-1, 21800145, 21800146 and 21800147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21 |  |  |  | 0
36777 | 0 | INSPECTION SERVICES COMPANY |  |  |  |  | 2000-03-09 10:30 | 2000-03-09 11:40 | 2000-03-09 | STOLEN MOISTURE DENSITY GAUGE INSPECTION SERVICES CO. REPORTED THAT A HUMBOLDT MOISTURE DENSITY GAUGE MODEL 5001 SERIAL # 2996 WAS STOLEN FROM THEIR PICKUP TRUCK WHILE IT WAS PARKED IN THEIR FACILITY PARKING LOT IN PLYMOUTH, MI. THE GAUGE WAS BOLTED TO THE TRUCK AT THE TIME OF THE THEFT. THE DEVICE CONTAINED 8 MILLICURIES OF Cs-137 AND 40 MILLICURIES OF Am-241. THE LOCAL POLICE WERE NOTIFIED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
36776 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2000-03-09 10:35 | 2000-03-09 11:16 | 2000-03-09 | TECH SPEC REQUIRED SHUTDOWN - LOSS OF CONTROL ROOM AIR CONDITIONING The licensee has two control room chillers. The 'A' chiller tripped because of low freon. The 'B' chiller was started and then tripped on two occasions. Based on the unreliability of the 'B' chiller, the licensee considered both chillers inoperable and entered Tech Spec 3.0.3 as a result. The licensee will start reducing power of all three units at 1 percent per hour at 1130. However they expect that they will have one chiller back in service prior to reaching the 2235, the time the units need to be in mode 3. The licensee notified the NRC resident inspector. * * * UPDATE ON 3/9/00 @ 1329 BY CLARKSON TO GOULD * * * Actions were undertaken to restore the 'B' Chilled water train to operable status. At 1246 hours, on March 9, 2000, the 'B' Chilled Water train was returned to operable status and Technical Specifications 3.0.3 and 3.7.16, Condition E were exited. The shutdown of all three Oconee units was also halted at approximately 98% power and the units are being returned to 100%. The NRC Resident Inspector was informed. The Reg 2 RDO (McAlpine) was notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | TECH SPEC LCO A/S |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36775 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-03-08 12:00 | 2000-03-08 18:12 | 2000-03-08 | 10CFR Part 21 Report - On 03/08/00, Clinton Power Station (CPS) officials notified the NRC of the failure of two hydramotors prior to installation in the plant. The hydramotors failed to meet fail safe return time test acceptance criteria and recycle criteria during bench testing due to the malfunction of hydramotor pump assemblies manufactured and supplied to CPS by ITT Barton. Reference CPS Letter #U-603341 dated 03/08/00. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS/NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 21.21(c)(3)(i) |  |  |  | 0
36774 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2000-03-08 15:50 | 2000-03-08 18:00 | 2000-03-08 | - REVERSE OSMOSIS UNIT BRINE EFFLUENT pH OUT OF NPDES PERMIT SPECIFICATION - During the monthly National Pollutant Discharge Elimination System (NPDES) sampling, the reverse osmosis unit brine effluent pH was determined to be out of specification. The effluent pH was determined to be 5.85 which was below the normal pH range of 6.5 to 9.0. The reverse osmosis unit was just coming out of an acid cleaning, and apparently did not have the sodium hydroxide neutralization injection feed rate set properly. This event resulted in a NPDES permit noncompliance for NPDES Point No. 002. Licensee chemistry department personnel are in the process of sampling the reverse osmosis unit brine effluent pH and the river outfall. (NPDES Points No. 001 and 002). The brine effluent is directed into the plant discharge tunnel and being diluted by 360,000 gallons of water. The licensee notified the Nebraska Department of Environmental Quality and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36773 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-03-08 15:30 | 2000-03-08 16:20 | 2000-03-08 | - PRIMARY AND SECONDARY METEOROLOGICAL TOWER WIND SPEED INDICATORS INOPERABLE - With the primary meteorological tower wind speed indicator inoperable, the backup meteorological tower wind speed indicator was determined to be inoperable at 1530 on 03/08/00. This condition constitutes a major loss of emergency capability in accordance with the licensee emergency plan. The licensee is repairing the wind speed indicators and developing a contingency plan to obtain wind speed readings from the National Weather Service during a declared emergency. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36772 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2000-03-08 12:00 | 2000-03-08 12:42 | 2000-03-08 | - SHIPMENT OF THREE 100 MILLICURIE Fe-55 SOURCES MISSING IN SOUTH KOREA - Bob Gallaghar, Massachusetts Department of Public Health, reported that on 02/04/00, Hanmi Express Company, Jamaica, NY, shipped an excepted package containing three 100 millicurie Fe-55 sources from AEA Technology QSA Inc (formally Amersham), Burlington, MA, to Shin-Ho Paper & Manufacturing Company, Jin-Ju City, South Korea. The freight forwarder (Hanmi Express) apparently opened the shipping container and added electronics parts that were destined for Shin-Ho and resealed the container. On 03/07/00, Shin-Ho reported that they had received a box of electronics components; the South Korean customer for which the electronics components were intended had received an empty box. Chris Martel, AEA Technology, is investigating this incident. Bob Gallaghar plans to notify New York State representatives. * * * UPDATE AT 1421 ON 03/08/00 FROM BOB GALLAGHAR TO JOLLIFFE * * * The package of missing sources has been located in a warehouse in South Korea and is being shipped to Shin-Ho. Bob Gallaghar plans to notify New York State representatives. The NRC Operations Officer notified the R1DO Greg Cranston, NMSS EO Susan Greene, and IP Ron Hauber. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0
36771 | -1 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-03-07 13:00 | 2000-03-08 12:18 | 2000-03-27 | 24-HOUR CONDITION OF LICENSE REPORT INVOLVING TECH SPEC REQUIREMENTS "On February 9, 2000, it was discovered that the Flux Multiplication Alarm (which is used to mitigate boron dilution accidents) was not functional. It was not recognized at that time that this caused the associated extended range neutron detector to be inoperable. If an extended range detector is inoperable in Modes 3, 4, and 5 the Technical Specifications requires that operations be suspended involving positive reactivity changes. "On March 1, 2000 at 0017 hours Unit 1 entered Mode 3 as part of a shutdown to support refueling activities. Immediately following Mode 3 entry testing was performed which involves raising control rods to perform drop testing. Raising control rods constitutes positive reactivity which is contrary to requirements of the Technical Specifications. "This notification is being made pursuant to Operating License NPF-76 Condition 2.G for operation or condition prohibited by Technical Specifications." The licensee will inform the NRC resident inspector. * * * UPDATE AT 1417 ON 03/27/00 BY KEN TAPLETT TO JOLLIFFE * * * Further licensee review determined that the extended range neutron detector in question had been operable during the positive reactivity change activity. During the time of the original notification, the Flux Multiplication Alarm was thought to be non-functional. A non-functional Flux Multiplication Alarm causes the associated extended range neutron detector to be inoperable. It was determined that the Flux Multiplication Alarm was actually functional at the completion of surveillance testing conducted on February 9, 2000. The surveillance procedure requires an alarm reset prior to exiting the surveillance test which arms the Flux Multiplication Alarm circuit thus making it functional. Although this step was performed on February 9, 2000, the performers did not recognize at the time that this corrected the perceived loss of alarm function. Prior to the February 9, 2000 surveillance test, the last satisfactory performance of the Flux Multiplication Alarm surveillance was conducted on November 16, 1999 with a grace period to March 10, 2000. Unit 1 entered Mode 6 (where the requirement was no longer applicable) on March 3, 2000 and has remained in that mode for a refueling and steam generator replacement outage. A satisfactory surveillance test was conducted on March 16, 2000. The licensee plans to revise the test procedure to preclude recurrence of this event. Based upon the above justification, the licensee desires to retract this event. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R4DO Kriss Kennedy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
36770 | 0 | CROW BUTTE RESOURCES |  |  |  |  | 2000-03-08 08:40 | 2000-03-08 10:49 | 2000-03-08 | MONITOR WELL IN EXCURSION STATUS A MONITOR WELL AT MINE UNIT 6 NEAR CRAWFORD, NE WAS DECLARED IN AN EXCURSION STATUS BASED ON EXCEEDING THE UPPER CONTROL LIMIT (UCL) FOR CHLORIDES. THE UCL IS 19 PPM AND THE CONCENTRATION MEASURED WAS 20 PPM. THE LICENSEE BELIEVES THIS IS A NORMAL VARIATION IN THE CHLORIDE LEVEL AND INTENDS TO INCREASE THE SAMPLE FREQUENCY. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LICENSEE 24 HR REPORT | [9 empty] | NON EMERGENCY | 4 | NE | MAT | [5 empty] | 0
36769 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-07 14:10 | 2000-03-08 08:01 | 2000-03-08 | BULLETIN 91-01 24 HOUR REPORT On March 7, 2000 at 1410 hours, it was discovered that a plastic 55 gallon laundry drum (containing used rubber totes) was left unattended in the X-705 Decontamination Building High Bay Area with the lid ajar. Following correction, the condition was identified again at 1508 hours. This violates requirement #5 of NCSA-0705_076.A00 which requires modification or covering of containers to prevent geometrically unfavorable accumulation of uranium bearing solution. This constitutes the loss of Control A (Volume) of the double contingency principle. Control B (primary integrity or the overhead piping) was maintained throughout the event. Each of the two non-compliances identified was corrected within thirty minutes of discovery under the direction of plant Nuclear Criticality Safety personnel. Following discovery of the repeat occurrence, a facility stand down was initiated in X-705 to conduct crew briefings and determine appropriate follow-up. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36768 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-03-08 03:30 | 2000-03-08 07:27 | 2000-03-15 | ESF ACTUATION - CONTROL ROOM VENTILATION SYSTEM Moving the Unit 2 dryer during refueling operations set off an area radiation alarm. The alarm caused the control room ventilation system to shift into pressurization mode. The radiation alarm cleared as the dryer was placed in its storage location. The trip has been reset and the control room ventilation has been returned to its normal lineup. The licensee will notify the NRC resident inspector. * * * UPDATE ON 3/15/00 @ 1625 BY URQUHART TO GOULD * * * RETRACTION Upon further investigation the licensee has determined that the control room ventilation shifted to the pressurization mode as a result of an invalid signal. Since the originating signal is not identified as an ESF, no notification is required, therefore the licensee is retracting this event. The NRC Resident Inspector will be notified. Reg 2 RDO (Belisle) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36767 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-07 10:38 | 2000-03-08 02:37 | 2000-03-08 | BULLETIN 91-01 24 HOUR REPORT At 1038 hours on 3/7/00, it was discovered that a 5 gallon bucket containing used, potentially contaminated oil was spaced less than 2 feet from another like container. The two containers were 23 inches apart rather than the minimum 24 inches required by NCSA-PLANTO45.AO1 Requirement #5. This spacing violation constitutes the loss of one control of the double contingency principle. The spacing violation was corrected at 1055 hours. A walk-down of the affected area verified that no other spacing issues exist. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36766 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-07 02:32 | 2000-03-07 20:33 | 2000-03-07 | - C-333A AUTOCLAVE WATER INVENTORY CONTROL SYSTEM PRIMARY CONDENSATE ALARM RECD - At 0232 CST on 03/07/00, the Plant Shift Superintendent (PSS) was notified that a primary condensate alarm was received on the C-333A Position 2 South autoclave Water Inventory Control (WIC) System. The WIC System is required to be operable while heating in Mode 5 according to TSR 2.2.4.2. The autoclave was checked according to the alarm response procedure, removed from service, and the WIC System was declared inoperable by the PSS. Troubleshooting was Initiated and is continuing in order to determine the reason for the alarm. The safety system actuation is reportable to the NRC as required by Safety Analysis Report, Section 6.9, Table 1, Criterion J.2, Safety System Actuation due to a valid signal as a 24-hour event notification. The NRC resident Inspector has been notified of this event. PGDP Problem Report No, ATR-00-1340; PGDP Event Report No, PAD-2000-020. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36765 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-03-07 14:22 | 2000-03-07 19:47 | 2000-03-07 | - NEWS RELEASE REGARDING THE RETRIEVAL OF BOXES OF RADIOACTIVE WASTE - The following news release was issued by the licensee to the general public at 1422 PST on 03/07/00 regarding the retrieval of boxes of radioactive waste that also may contain a hazardous substance: "Energy Northwest retrieves low-level radioactive waste shipment - RICHLAND, WA -- Acting on its own initiative, Energy Northwest has retrieved four boxes of low-level radioactive waste from US Ecology Inc. because the boxes possibly also contain what is classified as a hazardous substance. The combination of radioactive and hazardous wastes is considered mixed waste. US Ecology operates the commercial low-level radioactive waste disposal site at Hanford. US Ecology is not licensed to accept mixed waste. Energy Northwest discovered this potential problem internally and notified US Ecology, the state departments of Health and Ecology, the Nuclear Regulatory Commission and other interested parties. Energy Northwest owns the Northwest's only commercial nuclear power plant, which produces enough electricity to serve a city the size of Seattle with power at a competitive price. The plant is located about 10 miles north of Richland. During the plant's last refueling outage, which ended in October, Energy Northwest used a specialized process to clean and coat the interior of certain steam lines that had become somewhat corroded during 15 years of operation. The pipe was cleaned with blasting grit that became slightly radioactive. The grit and the corrosion deposits removed from the pipe are considered to be low-level waste. Immediately after cleaning, a metal coating was sprayed onto the inside of the piping. The spray was created by melting a nickel-chromium wire in an electrical arc, creating fine particles that coated the walls of the piping. Some of these fine particles possibly mixed with some of the used grit. The nickel-chromium wire is made of materials very much like those used to make kitchen cookware. However, under certain conditions nickel-chromium could be considered to be hazardous waste. When the pipe cleaning-coating operation was under way, it wasn't clear to Energy Northwest officials that the final waste could be classified as mixed waste. In October, waste from the pipe operation was gathered and placed in four metal boxes, each four feet by four feet by six feet. In December, the boxes were taken to the US Ecology disposal site on the Hanford Nuclear Reservation. The US Ecology site is licensed for low-level radioactive waste, such as that from medical clinics. In January, an Energy Northwest employee questioned whether the mixture of arc-spray residue and grit might possibly be classified as mixed waste, rather than low-level waste. Energy Northwest then told US Ecology it would retrieve the boxes. The boxes had not yet been buried. Energy Northwest retrieved the boxes in late February. A plan to sample and analyze waste is being prepared. The material will be tested to determine if the waste should be classified as mixed waste. If not, the boxes will be returned to US Ecology. If the waste is classified as mixed waste, Energy Northwest will explore other storage and disposal options." The licensee notified Washington State Officials and plan to notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36764 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-03-07 15:04 | 2000-03-07 15:45 | 2000-03-07 | - TEN OFFSITE EMERGENCY SIRENS INOPERABLE FOR 19 MINUTES - At 1504 on 03/07/00, the licensee notified Brunswick County Officials that ten offsite emergency sirens for Brunswick County were inoperable from 1444 to 1503 on 03/07/00. Alternate offsite notification mechanisms were available during this 19 minute period. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP | OFFSITE NOTIFICATION |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) | 50.72(b)(2)(vi) |  |  | 0
36763 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-03-06 21:42 | 2000-03-07 14:23 | 2000-03-07 | - X-342 BUILDING EVACUATED DUE TO A VALID ACTUATION OF A "Q" SAFETY SYSTEM - At 2142 on 03/06/00, X-342 building feed and sampling operations personnel viewed smoke escaping from the pigtail (female) to manifold (male) fitting for a cylinder in autoclave #2. The release started when the cylinder valve was opened. The building personnel evacuated the building and remotely placed the autoclave in containment shutdown. Placing the autoclave in containment shutdown by design resulted in closure of the pigtail line isolation/safety valve and a manual actuation of that particular safety system. The safety system was actuated while the autoclave was in an applicable TSR mode (TSR 2.1.3.13). The plant emergency response process and procedures were implemented. Results of all surveys performed during the emergency response were less than detectable. Plant personnel plan to inspect the subject area and repair/replace damaged parts. This event is reportable to the NRC as a valid actuation of a "Q" Safety System in accordance with Safety Analysis Report, Section 8.9 (24-Hour Report). There was no loss of hazardous or radioactive material nor radioactive or radiological contamination exposure as a result of this event. Plant personnel notified the NRC Resident Inspector and the Site DOE Representative. PTS-2000-026, PR-PTS-00-01308. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36762 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-03-06 12:00 | 2000-03-07 12:39 | 2000-03-07 | - CESIUM-137 SOURCE LOCATED IN A LOAD OF SCRAP STEEL IN A SCRAP YARD IN UTAH - On 03/06/00, Ed Johnson of Rocky Mountain Consultants notified California Radiologic Health Branch (RHB) that he had discovered a 10 millicurie Cs-137 source in a load of scrap steel that originated from California. The source was in a train car of scrap steel that set off the radiation monitor at Nucor Steel Company, Utah. Mr Johnson searched the load and discovered a Cs-137 source that had been removed from the body of a CPN portable gauge. The source appeared to have been through a shredder but the serial number was visible. The source manufacturer, Amersham, said it was delivered to CPN who said they installed it in a MC-1 gauge, serial number M-19089075. The gauge was sold to Petra Geotechnical Company, license #2933 in 1989. This gauge was reported stolen on 12/12/94 and an investigation was conducted at that time. Mr Johnson said the source will be shipped to CPN who will dispose of it. The Am-241 neutron source was not located in the load of scrap steel. RHB-LA plans to go to Williams Recycling Company, Los Angeles, where the load originated, and survey their facility to try to locate it. The scrap yard operator had installed a $30,000 Bicron gate monitor system three years ago to keep unwanted radioactive material out of the scrap yard, but apparently this did not work. A 5010 has been opened and assigned to RHB-LA & Brea to investigate. RBH plans to notify NRC of this incident after results of the survey at Williams Recycling Company are known. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>10X | [8 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  | 20.2201(a)(1)(ii) |  |  | 0
36761 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-02-29 12:00 | 2000-03-06 16:05 | 2000-03-06 | AGREEMENT STATE REPORT - RADIOGRAPHER RECEIVED ANNUAL EXPOSURE OF 5.205 Rem IN 1999 - On 02/29/00, Texas Department of Health Bureau of Radiation Control received notification from GCT Inspection, Inc, South Houston, TX, that a radiographer had received an annual exposure of 5.205 Rem during 1999. 3.34 Rem had been received in the 09/15/99 - 10/14/99 monitoring time period. TX Department of Health Bureau of Radiation Control personnel are requesting additional information and investigating this incident. TX Incident #7574. (Call the NRC operations officer for a state contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0
36760 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-03-06 11:45 | 2000-03-06 13:38 | 2000-03-06 | - TECH SPEC REQUIRED PLANT SHUTDOWN DUE TO SMALL UNISOLABLE LEAK IN THE CVC SYSTEM - At 1145 CST on 03/06/00, the licensee entered Tech Spec 3.0.3 due to visually observing a small crack (approximately 1/4 inch long) located at a welded joint in the suction line of the 'A' Charging and Volume Control (CVC) pump, leaking approximately 1 drop every 2 minutes. This rendered the entire CVC System inoperable. The leaking weld is unisolable from the entire charging header. Tech Spec 3.1.2.4 requires at least two charging pumps to be operable in Modes 1, 2, 3, and 4. With only one charging pump operable, restoration of at least two charging pumps to operable status within 72 hours is required. Currently, the leakage is not preventing the system from performing its design function. The most closely affected charging pump has been secured to limit the line vibration, which is the apparent cause of the leak. At 1222 CST on 03/06/00, the licensee commenced a plant shutdown from 100% power. Tech Spec 3.0.3 requires the plant to be in Hot Standby Mode within 6 hours. The licensee plans to cool the plant down to repair the leaking weld. The licensee notified the NRC Resident Inspector. | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36759 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2000-03-01 | 2000-03-06 09:08 | 2000-03-06 | AGREEMENT STATE REPORT INVOLVING AN IODINE-131 SPILL AT CLINICAL PHARMACY SERVICES LOCATED IN GRAY, TENNESSEE The following text is a portion of a facsimile received from the State of Tennessee, Department of Environmental Conservation, Division of Radiological Health (DRH): "Event Report ID No.: TN-00-038" "Event date and time: March 1, 2000" "Event location: Gray, Tennessee" "Event type: Contamination event" "Event description: DRH was notified on 03/03/00 by a representative from Clinical Pharmacy Services of an iodine-131 spill in the pharmacy on 03/01/00. When moving a pig with syringe from one hood to another for dose calibration, the end of the syringe plunger caught on part of the hood and was pulled out. Most of the 150 millicuries of I-131 was lost and contaminated the area. The area read 150 mR/hr. This was shielded to 50 mR/hr with lead. The area was cleaned and covered to an extent, but this was discontinued when clothing and badges became contaminated. They have discontinued work in the room and I-131 preparation. They will distribute unit commercial doses for now. They have a hood in another room for their other work. The unrestricted air concentration was 10,000 times the limit. The occupational dose was 72% of the limit. Bioassays were performed. A written report will be submitted." (Call the NRC operations officer for a State of Tennessee, Department of Environmental Conservation, Division of Radiological Health, contact name and telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | TN | OTH | AGR |  |  |  |  | 0
36758 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-03-05 22:00 | 2000-03-06 02:39 | 2000-03-06 | FAILURE TO MEET DRYWELL-TO-SUPPRESSION CHAMBER LEAKAGE TEST ACCEPTANCE CRITERIA The following text is a portion of a facsimile received from the licensee: "The acceptance criteria specified for the DRYWELL-TO-SUPPRESSION CHAMBER LEAKAGE TEST was not met. The as-found value of 0.51 [inches] H2O/Min exceeded the operability value of <= 0.2 [inches] H2O/Min. Based on this, the operability of the drywell-to-suppression chamber vent pipes, vent header downcomers, and vacuum breakers cannot be assumed. Primary containment was declared inoperable based on a failure to meet the requirements of [surveillance requirement (SR)] 3.6.1.1.2, Verify drywell to suppression chamber bypass leakage is equivalent to a hole < 1.0 inch in diameter." "[The unit] entered [limiting condition for operation (LCO)] 3.6.1.1, Condition A, requiring the restoration of primary containment to an operable status within 1 hour. If this required action is not met, Condition B.1 requires having the reactor in Mode 3 within 12 hours and B.2 requires having the reactor in Mode 4 within 36 hours." "Currently[, the unit is] in Mode 3 for commencing [a] planned refueling outage." "Engineering evaluation of test results is continuing, and the resident inspectors will be kept apprised." The licensee notified the NRC resident inspectors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iii)(D) |  |  | 0
36757 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-03-04 08:45 | 2000-03-04 11:05 | 2000-04-12 | DISCOVERY OF A REACTOR CORE ISOLATION COOLING (RCIC) FLOW CONTROL IRREGULARITY DURING THE PERFORMANCE OF SURVEILLANCE TESTING The following text is a portion of a facsimile received from the licensee: "A RCIC flow control irregularity was identified during quarterly RCIC surveillance testing. Upon reaching the required flow rate of 400 gpm, RCIC flow dipped to approximately 360 gpm for 1 - 2 minutes before stabilizing at 400 gpm. Engineering is evaluating this condition. In the interim, the RCIC system has been declared inoperable. The plant is in a 7-day [technical specification limiting condition for operation (LCO)]." The licensee plans to notify the NRC resident inspector. * * * UPDATE AT 1357 ON 4/12/00, BY ABRAMSKI RECEIVED BY WEAVER * * * The plant's licensing department has reviewed this event and determined that it is not reportable. The RCIC system is not required by the plant accident analysis. The licensee notified the NRC resident inspector. The operations center notified the R1DO (Reber). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(B) |  |  |  | 0
36756 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-03-04 00:18 | 2000-03-04 02:37 | 2000-03-04 | UNEXPECTED AUTOMATIC AUXILIARY FEEDWATER PUMP START While passing through Mode 2 in the process of shutting down Unit 1 to enter refueling outage #16, the last running feedwater pump was secured without defeating the automatic start defeat switch on the balance of plant. This resulted in the automatic start of the 'B' motor-driven auxiliary feedwater pump. The other auxiliary feedwater pump was already running. The licensee stated that a procedure step was missed and that an occurrence report has been initiated to determine why the procedure step was missed. The licensee also stated that all systems functioned as required and that there was nothing unusual or not understood. The unit is currently in Mode 3 (Hot Standby). The licensee notified the NRC resident inspector who was at the site observing the unit shutdown. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36755 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-03-03 16:30 | 2000-03-03 17:42 | 2000-03-03 | THE LICENSEE DETERMINED A CONDITION FOUND WHICH COULD HAVE RESULTED IN THE PLANT BEING SERIOUSLY DEGRADED. As a result of an Engineering evaluation of all safety-related large bore piping, a number of as-built discrepancies were found with portions of the Unit 2 Residual Heat Removal, Safety Injection and Containment Spray piping systems. This analysis has concluded that these piping systems deviate from the design criteria USAS 831.1-1967, which is the code of record for the Cook Nuclear Plant. As the design and construction of the corresponding systems in Unit 1 are similar, this notification is being made for both units despite the fact that the Unit 1 review effort has not been completed. Though informal evaluations have concluded that the piping is unlikely to fail in a postulated seismic event, no formal analysis exists to support this conclusion. The engineering efforts to evaluate and resolve these issues are ongoing. Both units are currently in no Technical Specification Operating mode with both cores unloaded. The Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | Refueling | Refueling |  | Refueling | Refueling |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36754 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-03-03 11:15 | 2000-03-03 17:34 | 2000-03-03 | ISOLATION CONTROLS FOR THE TIP GUIDE TUBE ARE NOT DESIGNED/QUALIFIED FOR SAFETY RELATED SERVICE. The Transverse Incore Probe (TIP) guide tube primary containment isolation controls are not designed or qualified for safety-related service. This could result in a condition outside the Design Basis of the plant because multiple failures could cause the undesirable opening of the TIP ball valves during a Design Basis Accident. However, the TIP valve and TIP Shear Valve Actuation circuits remain operable and continue to be capable of operating as containment isolation valves. The TIP Ball Valve power source is through the TIP Drive Mechanism. The TIP Ball Valves will be disabled by removing the power source from the drive Mechanism when the TIP system is not in use. The drive Mechanism power will be restored, under administrative controls, when the TIP system is required to be used. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36753 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-03-03 14:17 | 2000-03-03 15:56 | 2000-03-03 | MANUAL REACTOR SCRAM FOLLOWING A LOSS OF FEEDWATER SEAL INJECTION FLOW DURING PLANT SHUTDOWN "WHILE PERFORMING A NORMAL SHUTDOWN, THE REACTOR WAS MANUALLY SCRAMMED AT 1417EST DUE TO A LOSS OF SEAL WATER TO THE OPERATING FEEDWATER PUMP AND ITS POTENTIAL FAILURE. ALL RODS FULLY INSERTED. SUBSEQUENT TO THE MANUAL SCRAM, AN AUTOMATIC SCRAM WAS RECEIVED ON REACTOR WATER LEVEL 3. AN ATTEMPT WAS MADE TO MANUALLY INITIATE REACTOR CORE ISOLATION COOLING TO ASSIST WITH REACTOR WATER LEVEL CONTROL. THE RCIC SYSTEM FAILED TO INITIATE DUE TO A TRIPPED TRIP THROTTLE VALVE. AT 1420EST THE RCIC SYSTEM WAS DECLARED INOPERABLE. THE RCIC SYSTEM HAS BEEN RESTORED TO STANDBY. THE OPERATING FEEDWATER PUMP CURRENTLY REMAINS IN SERVICE AND SCRAM RECOVERY PROCEDURE AND REACTOR COOLDOWN ARE IN PROGRESS." FOLLOWING THE SCRAM MINIMAL SEAL INJECTION FLOW WAS AVAILABLE TO THE OPERATING FEEDWATER PUMP. DECAY HEAT IS CURRENTLY BEING REJECTED TO THE MAIN CONDENSER. THE NRC RESIDENT INSPECTOR WAS INFORMED. | 0 | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) | 50.72(b)(2)(iii)(D) |  | 0
36752 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-03-03 13:57 | 2000-03-03 14:29 | 2000-03-03 | REACTOR SHUT DOWN DUE TO ENTERING TS 3.0.3. LCO ACTION STATEMENT - (REFER TO EVENT #36750 AND EVENT #36751 FOR ADDITIONAL INFORMATION.) At 1300 hours, Unit 2 entered Technical Specification 3.0.3 due to the loss of diesel generator #2 while two off-site AC circuits were inoperable as required by Limiting Condition of Operation 3.8.1, Condition I. The loss of AC power and the diesel generator failure were previously reported in ENS #36751. At 1357 hours, Unit 2 reactor shutdown commenced from 100% power. INITIAL SAFETY SIGNIFICANCE EVALUATION: The significance of this occurrence is minimal. Sufficient redundant equipment remains operable such that no safety functions have been lost. Plant conditions are stable at this time. CORRECTIVE ACTION(S): Efforts to restore the inoperable equipment are in progress. Reference ENS # 36751 The NRC Resident Inspector was notified. * * * UPDATE ON 3/3/00 @ 2008 BY BELLER TO GOULD * * * PLANT EXITED THE 3.0.3 LCO AT 1756 WHEN THE UNIT 1 STARTUP AUX TRANSFORMER WAS USED TO POWER THE EMERGENCY BUSSES. THEY ARE STILL IN A 12-HOUR LCO ACTION STATEMENT TO RESTORE UNIT 1 UNIT AUXILLARY TRANSFORMER TO SERVICE OR BE IN HOT SHUTDOWN IN THE FOLLOWING 12 HOURS. POWER HAD BEEN REDUCED TO APPROXIMATELY 60%. THE NRC RESIDENT WAS INFORMED BY THE LICENSEE. THE NRC OPERATIONS OFFICER NOTIFIED THE R2DO (WERT). | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36751 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-03-03 09:31 | 2000-03-03 13:25 | 2000-03-03 | THE PLANT HAD ESF ACTUATION DURING THE LOSS OF OFFSITE POWER EVENT - (REFER TO EVENT #36750 AND EVENT #36752 FOR ADDITIONAL INFORMATION.) With Brunswick Unit 1 shutdown for refueling at approximately 09:31 on 3/3/00 while performing procedure TM-TTBUS1A (Trip Testing of 230KV Bus 1A) a loss of power to the Unit 1 BOP 4160 and emergency busses occurred. This caused an automatic start of 4 diesel generators with diesels number 1 and 2 loading and restoring power to their respective emergency busses. Unit 1 received a group 8 isolation signal that caused a loss of shutdown cooling. Core alterations were secured and shutdown cooling was reestablished at 09:52. A small rise in reactor coolant temperature occurred (89°F was the maximum) and the coolant system did not approach boiling temperatures. Six group isolation signals occurred with various valves closing depending on initial (pre-event) position. The following actuations occurred: 4 Diesel generators started, Reactor Building HVAC isolated, Standby Gas trains started, and an RPS trip occurred (no rod motion occurred due to all rods being inserted). Systems and components performed as designed based on initial assessment of the event. An Unusual Event was declared at 09:50 (event #36750) due to a loss of offsite power to the emergency busses. At approximately 12:00 an actuation of the diesel building fire protection halon system occurred with an isolation of the control building ventilation system. A subsequent loss of emergency bus E2 occurred due to a trip of DG#2, which resulted in a second loss of shutdown cooling on Unit 1. Group isolations similar to those occurring initially also occurred. Shutdown cooling was reestablished at 12:18. The plant is stable and investigation into the cause of the DG trip is underway. The plant fire brigade responded and found no immediate evidence of a fire. The NRC Resident Inspector was notified along with state and local officials. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION | POT RHR INOP | OFFSITE NOTIFICATION |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(vi) |  | 0
36750 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-03-03 09:50 | 2000-03-03 10:38 | 2000-03-03 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER TO 4 kV EMERGENCY BUSES - (REFER TO EVENT #36751 AND EVENT #36752 FOR ADDITIONAL INFORMATION.) At 0950 on 03/03/00, with Unit 1 in a refueling outage, the licensee declared an Unusual Event due to a loss of offsite power to 4 kV emergency buses E-1 and E-2 due to a mispositioned switch during relay testing. All four emergency diesel generators (two for each unit) started; both Unit 1 EDGs are in operation powering buses E-1 and E-2. Shutdown cooling was lost but has been restored; spent fuel pool temperature is normal at 83°F. The licensee has suspended all fuel movement and is restoring power to systems that lost power. Unit 1 is stable. Unit 2, which is at 100% power, is unaffected by this event. The licensee notified the NRC Resident Inspector and state and local officials. * * * UPDATE ON 3/3/00 @ 1226 BY HILL TO GOULD * * * WHILE ATTEMPTING TO COME OUT OF THE LOSS OF OFF SITE POWER CONDITION, THE PLANT HAD AN OVERCURRENT ALARM ON THE D/G-2, AND THEY LOST POWER FROM THE NORMAL AND EMERGENCY POWER SOURCES TO THE E-2 BUS AT 1200. THIS IN TURN RESULTED IN THE LOSS OF SHUT DOWN COOLING. SHUTDOWN COOLING WAS RESTORED AT 1218 WITH MINIMAL TEMPERATURE INCREASE. THEY ALSO HAD THE HALON SYSTEM ACTUATION IN THE D/G BASEMENT AREA. THE CAUSE OF THIS MAY HAVE BEEN RELATED TO THE GROUND ON THE E-2 BUS. THE RESIDENT INSPECTOR WAS NOTIFIED. THE REG 2 RDO(WERT), NRR EO(HANNON), AND IRO(CONGEL) WERE NOTIFIED. * * * UPDATE ON 3/3/00 @ 1615 * * * COMMISSIONER'S ASSISTANTS BRIEF MALLETT(BRIEFER), MARSH(NRR EO), REYES(RA), EASLICK(RI), COLLINS(NRR), MILLER(IRO), WERT(RDO), WIENS(NRR), BEECHER(PA), LOHAS(SP), FAULKNER(IP), SATORIUS(EDO), BATES(SECY), CHAN(CHAIRMAN MESERVES' ASST), OLENCZ(COMM. DICUS' ASST), SHARFEY(COMM. MCGAFFIGAN'S ASST), CASTLEMAN(COMM. DIAZ'S ASST), AND McCABE(COMM. MERRIFIELD"S ASST). * * * UPDATE ON 3/3/00 @ 1844 FROM JOLICOEUR TO GOULD * * * NOUE TERMINATED AT 1840 DUE TO RESTORING POWER FROM NORMAL OFF-SITE SOURCES TO THE E-1 AND E-2 BUSSES. The NRC Resident Inspector was notified. REG 2 RDO(WERT), NRR EO(HANNON), IRO(CONGEL), AND FEMA(STEINDURF) WERE NOTIFIED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | COMM ASST BRIEF |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a)(1)(i) |  |  |  | 0
36749 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-03-02 16:30 | 2000-03-02 19:25 | 2000-03-02 | LICENSEE DID NOT COMPLY WITH LCO ACTION STATEMENTS On March 1, 2000 at 1008 hours, 125 VDC Battery System E1A11 was declared inoperable. Subsequently, in accordance with Technical Specifications 3.8.2.2, "D. C. Sources," and 3.8.3.2, "Onsite Power Distribution - Shutdown," Nuclear Instrumentation Source Range Detector 31 should have been declared inoperable or actions should have been initiated to suspend operations involving positive reactivity changes. Contrary to these requirements, Source Range Detector 31 was not declared inoperable, and at 0027 hours on March 2, 2000, control rods were moved as part of rapid refueling rod holdout operations. The rods were cycled 18 steps 3 times between the hours 0027 and 0400 @ 3/2/00. No movements have taken place since then. Detector 31 has been declared inoperable and is still inoperable. The NRC Resident Inspector has been notified. This notification is being made pursuant to Operating License NPF-76 Condition 2.G for operation or condition prohibited by Technical Specifications. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | TECH SPEC LCO A/S | LICENSEE 24 HR REPORT |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
36748 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-03-02 18:00 | 2000-03-02 18:18 | 2000-03-02 | THE LICENSEE DISCOVERED NON-CONSERVATISM IN CRITICALITY CALCULATIONS FOR FUEL POOL STORAGE REQUIREMENTS. It was determined that certain assumptions may result in a K-effective (K-eff) in excess of 0.95 at 0 ppm boron concentration in the spent fuel pool. The Design Basis of the plant is that the fuel stored in the fuel pool will remain less than or equal to 0.95 K-eff when fully flooded with unborated water. As such the Licensee is reporting this as a condition outside the design basis of the plant in accordance with 10CFR50.72(b)(1)(ii)(B). Currently each spent fuel pool has boron concentrations in excess of 2675 ppm as required by Technical Specifications. Under these conditions, with routine monitoring of boron concentration as required by Technical Specifications, the plant will not require any compensatory measures to remain operable in the fuel pool. Duke will continue to evaluate the models to further evaluate this condition. The NRC Resident Inspector was informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36747 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2000-03-01 07:49 | 2000-03-01 19:25 | 2000-03-01 | FITNESS FOR DUTY EVENT A LICENSED OPERATOR TESTED POSITIVE FOR ALCOHOL DURING A FOR CAUSE TEST. THE OPERATOR'S PROTECTED AREA ACCESS HAS BEEN SUSPENDED. CONTACT THE OPERATIONS CENTER FOR ADDITIONAL DETAILS. THE LICENSEE NOTIFIED THE NRC RESIDENT INSPECTOR. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.73 |  |  |  | 0
36746 | 0 | RESTON HOSPITAL CENTER |  |  |  |  | 2000-02-28 08:00 | 2000-03-01 14:22 | 2000-03-01 | LOST I-125 SEED A 0.401 mCi I-125 seed was lost on 2/28/2000, at Reston Hospital Center in Reston, VA. The technician working with the seed believes the seed was lost in the hot lab while preparing the seeds for use. The hot lab was searched but the seed could not be found. The technician frisked herself prior to leaving the hot lab, so the licensee does not believe the seed is outside of the lab. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | VA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0
36745 | -1 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2000-03-01 12:35 | 2000-03-01 13:56 | 2000-03-07 | UNANALYZED CONDITION - USING THE AUXILIARY FEEDWATER PUMP TO FEED THE STEAM GENERATORS VIA THE MAIN FEEDWATER SYSTEM IS UNANALYZED. ANO engineering has determined that using the Auxiliary Feedwater (AFW) pump to feed steam generators (S/Gs) via the Main Feedwater (MFW) System is unanalyzed. The ability of the MFW block valves to shut and isolate the affected S/G on a Main Steam Line Break (MSLB) has not been fully evaluated. Preliminary evaluation indicates that the valves may not shut under worst case conditions (low voltage supplied to the MOV and high D/P across the valves). This condition is only applicable during low power operations with AFW feeding via the MFW piping. AFW is not an Engineered Safety Feature at ANO Unit 2. The plant has a separate Emergency Feedwater (EFW) System which is not affected by this problem. The licensee will notify the NRC resident inspector. * * * UPDATE AT 1336 ON 03/07/00 BY TOM SCOTT TO JOLLIFFE * * * A licensee engineering review has determined that the consequences of the above event would have had no safety significance. Review of the Hot Zero Power (HZP) Containment Analysis for a MSLB showed that consequences of a small amount of additional AFW would be bounded by the current limiting MSLB containment analysis for Hot Full Power. A previous sensitivity analysis of the effects of isolating EFW to the S/Gs indicated no significant impact due to continued flow for the HZP Nuclear Steam Supply System MSLB analysis. Since the consequences of having operated in an unanalyzed condition have been determined not to have significantly compromised plant safety, reporting to the NRC per 10CFR50.72(b)(1)(ii) is not applicable. Thus, the licensee desires to retract this event. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R4DO Dave Loveless. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED COND OP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(1)(ii)(A) |  |  |  | 0
36744 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-03-01 10:58 | 2000-03-01 13:20 | 2000-03-01 | REACTOR MANUALLY SCRAMMED DUE TO A LOSS OF 3 OF 5 RECIRCULATION PUMPS. STARTUP TRANSFORMER "A" WAS BEING USED TO FEED ELECTRICAL POWER TO 4.16 kV NON- VITAL BUS "A" AND VITAL BUS "C". EARLIER IN THE DAY THE REACTOR HAD BEEN TAKEN OFF LINE SO THAT AUXILIARY TRANSFORMER "M1A" COULD BE PLACED BACK IN SERVICE. AUXILIARY TRANSFORMER "M1A" WAS REPAIRED OVER THE PAST FEW WEEKS. WHEN AUXILIARY TRANSFORMER BREAKER "1A" WAS CLOSED TO TRANSFER STATION ELECTRICAL LOADS FROM THE STARTUP TRANSFORMER TO THE "M1A" AUXILIARY TRANSFORMER, STARTUP TRANSFORMER "A" BREAKER "S1A" OPENED AS EXPECTED BUT "1A" BREAKER DID NOT CLOSE. THE FAILURE OF BREAKER "1A" TO CLOSE RESULTED IN A LOSS OF ELECTRICAL POWER TO BOTH NON-VITAL BUS "A" AND VITAL BUS "C". THE LOSS OF NON- VITAL BUS "A" CAUSED THREE OF FIVE REACTOR RECIRCULATION PUMPS TO TRIP. THE OPERATORS MANUALLY SCRAMMED THE REACTOR IN ACCORDANCE WITH PROCEDURES. ALL CONTROL RODS FULLY INSERTED INTO THE CORE. LOSS OF ELECTRICAL POWER TO VITAL BUS "C" CAUSED A LOSS OF POWER TO 1/2 OF THE REACTOR PROTECTION SYSTEM. THIS RESULTED IN VITAL BUS EMERGENCY DIESEL GENERATOR #1 TO AUTOMATICALLY START AND LOAD ONTO THE BUS. THE MAIN STEAM ISOLATION VALVES CLOSED WHEN REACTOR VESSEL PRESSURE DECREASED BELOW 850 PSIG. AT THE PRESENT TIME THE ISOLATION CONDENSER IS BEING USED TO COOL THE REACTOR VESSEL DOWN. WHEN REACTOR PRESSURE DROPS BELOW 100 PSIG THE MAIN STEAM ISOLATION VALVES CAN BE REOPENED. OFFSITE POWER HAS BEEN RESTORED TO NON- VITAL BUS "A" AND VITAL BUS "C" VIA STARTUP TRANSFORMER "A." EMERGENCY DIESEL GENERATOR # 1 IS BEING PROPERLY SECURED. DURING THIS INCIDENT BOTH NON-VITAL BUS "B" AND VITAL BUS "D" REMAINED IN SERVICE. THE LICENSEE IS INVESTIGATING WHY "1A" BREAKER DID NOT CLOSE. THE NRC RESIDENT INSPECTOR WAS NOTIFIED OF THIS EVEN BY THE LICENSEE. | 0 | 0 | 0 | 24 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36743 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2000-03-01 12:15 | 2000-03-01 13:06 | 2000-03-01 | OUTSIDE DESIGN BASIS - NON CONSERVATIVE LIMITING CONDITION FOR OPERATION On March 1, 2000, at 1215 hours, resulting from evaluations performed in response to the McGuire Station Notification (02/04/2000, event # 36659), Virgil C. Summer Nuclear Station has determined that a condition outside of design basis may have existed during past plant operation. The specific condition is a deficiency in the current Limiting Condition for Operation for Engineered Safety Feature Actuation System (ESFAS) instrumentation. For one inoperable channel (in the Emergency Feedwater suction swap over on low suction pressure, RWST [Reactor Water Storage Tank] swap over to RB [Reactor Building] Sump on low level, and/or Containment Spray actuation on High-3 pressure) the Technical Specification (TS) action is to place the channel in bypass with no Allowed Outage Time (AOT) limit. These are energize to actuate functions. At this point the actuation logic changes from 2 out of 4 to 2 out of 3. Because of the indefinite period of time that this condition is permitted to remain in effect, this condition cannot be considered a single failure during a design basis accident. During a design basis accident, a single failure involving a loss of power to the opposite train instrumentation, while one or more of these functions were in bypass, would prevent the safety function from automatically occurring. Manual operator action is specified in the station Emergency Operating Procedures. Currently all four channels for each of the above functions are OPERABLE. Therefore, Summer is not operating with a single failure vulnerability at this time. A preliminary PRA [Probability Risk Assessment] assessment shows the change in Core Damage Frequency to be 2.4 E-8 for placing one channel from each of these functions in bypass indefinitely. Administrative controls have been developed to limit the AOT for these particular channels to be in bypass until such time as a TS change request can be submitted and approved. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36742 | 0 | ALLEGHENY GENERAL HOSPITAL |  |  |  |  | 2000-03-01 10:30 | 2000-03-01 11:38 | 2000-03-01 | AMERICIUM-241 SEALED SOURCE DISCOVERED TO BE MISSING FROM ALLEGHENY GENERAL HOSPITAL LOCATED IN PITTSBURGH, PENNSYLVANIA. At approximately 1030 on 03/01/00, representatives at Allegheny General Hospital located in Pittsburgh, Pennsylvania, discovered that a 14-millicurie, americium-241, sealed source was missing from a stationary gamma camera. The licensee reported that the source was last seen at 1130 on 02/29/00. The licensee stated that the source is a relatively low level source with longevity which is used to mark images. It is about the size of a pencil eraser, and it is typically glued into a holder on the gamma camera. The licensee currently believes that the source may have become dislodged from the holder and that it may have fallen to the floor. If that occurred, the source may have been placed in the trash when the room was cleaned the on the evening of 02/29/00. The licensee's investigation is ongoing, and surveys are underway. The licensee plans to notify the state inspector. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0
36741 | -1 | US ARMY (ACALA) |  |  |  |  | 2000-02-17 12:00 | 2000-03-01 10:36 | 2000-03-02 | - M1A1 COLLIMATOR WAS OVERPRESSURIZED AND RUPTURED - On 02/17/00, while the Third Army Corp Maintenance Unit from Fort Wainwright, AK, was performing a purge for Fort Hood units during training at Fort Irwin, CA, an M1A1 collimator containing 10 curies of tritium was overpressurized and ruptured. The M1A1 collimator was double bagged but not reported to the Fort Irwin Radiation Safety Officer. On 02/29/00, when the military van containing the M1A1 collimator was being readied for shipment back to Fort Wainwright, the broken M1A1 collimator was noted and surveyed. The survey came back contaminated (as high as 255,000 dpm). The military van is being held at Army/Marine Base, Yermo Annex, Barstow, CA, by Fort Hood personnel. Results are pending. The two individuals who performed the purge are being bioassayed. Results are pending. Further investigation of what happened and surveys to determine contamination status are ongoing. Army Incident #00-12. * * * UPDATE AT 1040 ON 03/02/00 FROM TIM MOHS TO JOLLIFFE * * * The results of the bioassays indicated that no dose was received by either individual. No personnel were contaminated. Radiation levels inside the van were less than release limits. Thus, the licensee desires to retract this event. The NRC Operations Officer notified the R3DO Mike Jordan and NMSS EO Brian Smith. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | MATL >5X LOWEST LIMIT | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 30.50(b)(1)(ii) |  |  |  | 0
36740 | 0 | FL BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-01-31 12:00 | 2000-03-01 08:58 | 2000-03-01 | - MEDICAL MISADMINISTRATION EVENT IN AN AGREEMENT STATE - On 01/31/00, during the second of three applicator treatments of 3.43 curies of Ir-192 at Halifax Medical Center, Daytona Beach, FL, the hospital therapist switched the location numbers and the patient was treated at a location of 898 mm instead of 989 mm. The result was that the majority of the dose went to the wrong treatment site. The maximum dose received was 1600 Rads. The doctor and the patient have been notified. No damage to the patient is expected. The patient has since completed the full course of treatments which were compensated for the error. A written report has been filed with Florida. This incident is still under investigation by Florida. Florida Incident Number FL00-018. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | MED MISADMINISTRATION | [8 empty] | NON EMERGENCY | 2 | FL | HOS |  |  | 35.33 |  |  | 0
36739 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2000-03-01 05:30 | 2000-03-01 06:27 | 2000-03-01 | - OVERDUE SHIPMENT OF NEW FUEL - The licensee reported that a shipment of new fuel from General Electric was due to arrive onsite at 0500 on 03/01/00. The shipper (Kindrick Trucking Company) was contacted and the shipment was located in Canton, Ohio, at 0550 on 03/01/00. The new expected arrival time is 0900 on 03/01/00. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0955 ON 03/01/00 BY PAT FALLON TO JOLLIFFE * * * General Electric notified the licensee that the reason for the delay was that a tarp on the nuclear fuel truck blew off and is being recovered and reinstalled on the truck. Estimated time of arrival onsite now is 1300 on 03/01/00. The licensee plans to notify the NRC Resident Inspector. The NRC Operations Officer notified R3 IAT Jim Creed, R3DO Mike Jordan, NRR IAT Dick Rosano, NRR EO Chris Grimes, NMSS IAT Mike Weber, NMSS EO Brian Smith, and IRO Frank Congel. * * * UPDATE AT 1254 ON 3/1/2000 BY COSEO TAKEN BY WEAVER * * * The licensee is retracting this event. "10 CFR 73.67(g)(3) states that each licensee, either shipper or receiver, who arranges for the physical protection of special nuclear material of low strategic significance while in transit or who takes delivery of such material free on board (f.o.b.) the point at which it is delivered to a carrier for transport shall: conduct immediately a trace investigation of any shipment that is lost or unaccounted for after the estimated arrival time and notify the NRC Operations Center within one hour after the discovery of the loss of the shipment and within one hour after recovery of or accounting for such lost shipment in accordance with the provisions of 10 CFR 73.71. In accordance with a General Electric (GE) letter to Detroit Edison, dated August 12, 1992, GE stated that they are responsible for in-transit physical protection of fuel shipments from Wilmington to the Fermi 2 site. Therefore, the notification to the NRC regarding lost or unaccounted for special nuclear material of low strategic significance while in transit should have been completed by GE. "However, further evaluation of the event revealed that communication between GE and the truck driver regarding the trucks location and problem, did occur. Therefore, the truck was never lost or unaccounted for by GE. The delay in the estimated arrival time was apparently due to problems with the truck during the transit. Based on the above information and the fact that the shipment was never lost or unaccounted for, the reporting requirements of 10 CFR 73.71 do not apply in this event. Therefore, Detroit Edison is retracting the 1-hour notification." The licensee notified the NRC resident inspector and the Operations Center notified the RDO (Jordan), EO (Smith), IRO (Congel). | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0
36738 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-02-29 08:03 | 2000-02-29 08:28 | 2000-02-29 | OFFSITE NOTIFICATION TO THE FEDERAL ENERGY REGULATORY COMMISSION (FERC) REGARDING FAILURE OF SPILLWAY EMERGENCY DIESEL GENERATOR TO START DURING TESTING "THE NORTH ANNA SPILLWAY DIESEL FAILED TO START DURING THE PERFORMANCE OF THE PERIODIC SURVEILLANCE (1-PT-1). THIS EVENT IS REPORTABLE TO THE FERC REGIONAL ENGINEER, THEREFORE, THE NRC MUST BE NOTIFIED WITHIN 4 HOURS. MAINTENANCE IS INVESTIGATING. THE SPILLWAY HAS NORMAL POWER AVAILABLE. THIS IS THE EMERGENCY DIESEL GENERATOR AT THE DAM AND IS A SAFETY DEVICE PER FERC REGULATIONS." THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 72 | 100 | 0 | 72 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36737 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-02-28 23:09 | 2000-02-28 23:29 | 2000-03-31 | TECH SPEC REQUIRED SHUTDOWN - BACKLEAKAGE FROM THE S/G TO THE AUXILIARY FEEDWATER SYSTEM. Check valve leakage from the # 1 Steam Generator caused a rise in temperature in the discharge piping of the "A" auxiliary feedwater pump. The maximum allowed temperature is 190 degrees F. The maximum temperature reached was 300 degrees F. The licensee entered Tech Spec 3.0.3 at 1209 and started slowly lowering power. Injection with the "A" AFW pump reduced the temperature in the line below the limit. The licensee is waiting to determine if the check valve has reseated. The licensee notified the NRC resident inspector, the town of Waterford and the state of Connecticut. * * * UPDATE 0026 2/29/2000 FROM JOHN CLAIR TAKEN BY BOB STRANSKY * * * TS 3.0.3 was exited at 2338 2/28/2000. The unit is returning to rated power. The NRC resident inspector will be informed of this update by the licensee. Notified R1DO (Trapp). * * * RETRACTION 0833 3/31/2000 FROM KENNETH TRUSDALE TAKEN BY STRANSKY * * * "This call is to retract a call made on 2/28/2000 under 10 CFR 50.72 regarding entry into Tech Spec Action Statement 3.0.3, as the plant was in a condition prohibited by the Tech Specs. The original notification was made because the Shift Manager had indication that the auxiliary feedwater piping temperature was above normal, and he did not have enough information or guidance at that time to determine that the auxiliary feedwater system was operable. As operability was indeterminate, the Shift Manager conservatively assumed the auxiliary feedwater system was inoperable, which is a condition prohibited by the plant Technical Specifications. Subsequent research and investigation determined that the auxiliary feedwater system was operable throughout the event and the plant was not in a condition prohibited by the Technical Specifications. "As the plant was not in a condition prohibited by the Technical Specifications, there was no requirement to enter Action Statement 3.0.3. The notification made on 2/28/2000 is withdrawn." The NRC resident inspector has been informed of this retraction by the licensee. Notified R1DO (Evans). | 0 | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36736 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-02-28 14:15 | 2000-02-28 18:24 | 2000-03-02 | HIGH PRESSURE CORE SPRAY INOPERABLE High Pressure Core Spray was declared INOPERABLE following an overvoltage condition on the Division Three AC Power Distribution System. During performance of CPS 9080.02 Division Three Diesel Generator Operability Surveillance, the Division Three Diesel Generator was synchronized with the AC bus. Following synchronization, bus voltage went to approximately 4360V, which is above the limit of 4300V. The high voltage condition remained for approximately 3 1/2 minutes, until the Diesel Generator output breaker was opened and voltages returned to less than 4300V. The Division Three AC Power Distribution System was declared INOPERABLE due to being above 4300V pending an Engineering evaluation of the overvoltage condition. CPS Improved Technical Specification 3.8.9, Action E.1 requires High Pressure Core Spray to be declared INOPERABLE with the Division Three AC Power Distribution System INOPERABLE. The Division Three Diesel Generator was also declared INOPERABLE. The cause of the overvoltage is not known and is being investigated at this time. NRC Resident Inspector C. Brown was notified. * * * UPDATE ON 3/2/00 @ 1441 BY FUNCKHOUSER TO GOULD * * * All portions of the Division Three AC Distribution System were initially declared INOPERABLE. The Division Three AC Distribution System has had an Engineering Evaluation performed and restored to an OPERABLE status. At this time the High Pressure Core Spray (HPCS) System was restored to an OPERABLE status. The Division Three Diesel Generator is being worked to restore it to an OPERABLE status, subsequent to the abnormal conditions experienced during the Division 3 Diesel Generator run on Monday, February 28, 2000. The plants Technical Specifications Limited Condition for Operation (LCO) section 3.8.1, AC Sources Operating, does not require the Division 3 AC electrical power sources to be OPERABLE when the HPCS System is inoperable and it allows the use of the HPCS LCO in lieu of the Division 3 Diesel Generator. Thus, the High Pressure Core Spray (HPCS) System has been declared INOPERABLE at approximately 1000 on March 2, 2000 in lieu of the Division 3 AC Source (Division 3 DG). This is allowed by the LCO 3.8.1 Bases, Applicability section. The HPCS System LCO is covered in Technical Specifications section 3.5.1. At 1000 on 3/2/00 the plant exited LCO 3.8.1 and entered LCO 3.5.1. The NRC Resident Inspector was informed. The Reg 3 RDO(Jordan) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36735 | 0 | NEW YORK CITY DEPARTMENT OF HEALTH |  |  |  |  | 2000-02-09 | 2000-02-28 10:40 | 2000-02-28 | AGREEMENT STATE REPORT On 2/9/2000, Columbia University discovered that a graduate student in the biology department had contamination (phosphorus-32 and sulfur-35) of her hair and fingers. A radiological survey also discovered contamination in her apartment, which is owned by the university. An assessment based upon urinalysis indicated a dose of several millirem to the student. An investigation by the university and NYC Department of Health determined that the contamination was intentionally self-inflicted by the student. The university is currently determining whether to expel the student. The student is a foreign national living in the United States on a student visa. The NYC Department of Health has already contacted NRC Region I (Duncan White) regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0
36734 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-02-28 05:45 | 2000-02-28 06:34 | 2000-03-07 | OVERDUE SHIPMENT OF NEW FUEL The licensee reported that a shipment of new fuel from ABB was due to arrive onsite at 0530 2/28/00. At the time of the report, the shipment had not yet arrived. The licensee is attempting to contact the shipper. The NRC resident inspector will be informed of this event by the licensee. * * * UPDATE 0809 2/28/00 FROM PARKER TAKEN BY STRANSKY * * * The fuel shipment arrived onsite at 0735 2/28/00. The shipper (Roberts Express) believed that the scheduled delivery time was 0700. The licensee plans to investigate the discrepancy in the delivery schedule. The NRC resident inspector will be informed of this update by the licensee. Notified R1DO (White), NRR IAT (Skelton), NMSS IAT (Davidson), NRR EO (Beckner), and NMSS IAT (Brach). * * * UPDATE 1012EST ON 3/7/00 FROM ERV PARKER TO S.SANDIN * * * "On 02/28/00, at 0634, Hope Creek made a one hour notification (NRC event #36734). This notification stated 'Hope Creak Generating Station expected a new fuel receipt to arrive on site at approximately 0530 this morning. As of this time the shipment has not arrived. Station personnel are attempting to contact the shipping vendor. Our information indicates that the truck was dispatched at 1040 on Saturday and should have arrived by now.' The shipment subsequently arrived on February 28, 2000, at 0735. This information was provided to the NRC at 0805. This notification was made in accordance with 10CFR73.71, Reporting Of Safeguards Events, as a lost fuel shipment. The shipment was reported as lost because the Control Room expected the shipment to arrive at 0530, and it did not. The cause of the shipment not arriving at 0530 has been determined to be miscommunication. Due to this miscommunication, the trucking company believed that the shipment was expected at 0800. While conducting the investigation, plant staff determined that the truck was continually being tracked via satellite and the dispatcher was aware of its location at all times. Therefore, the fuel truck was not lost and this event is not reportable in accordance with 10CFR73.71. As a result, the notification is being retracted." The licensee will inform the NRC resident inspector. Notified R1DO(Cranston). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | LOST/STOLEN LNM>1000X |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) | 20.2201(a)(1)(i) |  |  | 0
36733 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-02-27 16:30 | 2000-02-27 17:02 | 2000-02-27 | HIGH PRESSURE CORE INJECTION (HPCI) DECLARED INOPERABLE DUE TO WATER INTRUSION INTO THE HPCI PUMP OIL RESERVOIR During a routine surveillance for operability, the HPCI bracket drain clogged causing seal leakoff to spill into the HPCI oil reservoir. The bracket drain line collects seal leakoff and directs the flow to the floor drain system. HPCI was declared inoperable per Tech Spec 3.5.1 placing Unit 2 in a 14-day LCO. The licensee estimates that the oil will be changed and HPCI restored by approximately 2400 hours on 2/27/00. The licensee will inform the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36732 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-02-26 13:55 | 2000-02-26 15:19 | 2000-02-26 | NEW YORK STATE DEPARTMENT OF ENVIRONMENTAL CONSERVATION (NYSDEC) NOTIFIED REGARDING MINOR SEWAGE SPILL ONSITE WITH RELEASE TO THE DISCHARGE CANAL AND HUDSON RIVER "At 1205 hrs on 2/26/00 the Control Room was notified that a sewage line was leaking in to the yard area north of the Turbine Bldg. Investigation revealed that a clean out plug had broke causing the spill. At 1220 hrs the leakage was isolated by installation of a temporary plug. An estimated 15 gallons total spilled with a conservative estimate of 5 gallons to a near by storm drain. Miller Environmental contractor service has been notified for clean up and NYSDEC has been notified due to leakage to the discharge canal." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36731 | -1 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2000-02-26 00:48 | 2000-02-26 02:55 | 2000-02-28 | SECURITY REPORT Fitness for duty of security personnel questioned due to inattentiveness. Immediate compensatory measures taken upon discovery. The NRC resident inspector has been informed of this event by the licensee. Contact the NRC Operations Center for additional details. * * * UPDATE 1458EST ON 2/27/00 FROM BOB FRANSSEN TO S.SANDIN * * * The licensee provided clarification to the initial report. Contact the NRC Operations Center for additional details. The NRC resident inspector has been informed of this update by the licensee. Notified R1DO (White). * * * UPDATE AT 1550 ON 2/28/2000 BY BECK RECEIVED BY WEAVER * * * The licensee has retracted this event. Contact the NRC Operations Center for additional details. The NRC resident inspector has been informed of this update by the licensee. Notified R1DO (Trapp). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 0
36730 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-02-26 01:06 | 2000-02-26 01:33 | 2000-02-26 | OFFSITE NOTIFICATION The licensee notified the Federal Aviation Administration (FAA) office in Bangor, ME that a navigational hazard beacon on one of the onsite cranes was not illuminating. The licensee will inform the NRC resident inspector of this notification. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36729 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2000-02-25 | 2000-02-25 15:40 | 2000-02-25 | AGREEMENT STATE REPORT INVOLVING A RADIOLOGIST (OCCUPATIONAL WORKER) WHO RECEIVED > 5 REM DURING CALDENDER YEAR 1999 ON 2/25/00 THE KANSAS DEPARTMENT OF HEALTH & ENVIRONMENT WAS NOTIFIED THAT A RADIOLOGIST PERFORMING INTERVENTIONIST RADIOLOGY AT THE UNIVERSITY OF KANSAS MEDICAL CENTER IN KANSAS CITY, KS, HAD RECEIVED 5.29 REM WHOLE BODY IN 1999 (CUMMULATIVE). THIS WAS DISCOVERED IN A REVIEW OF RECORDS PERFORMED BY THE UNIVERSITY. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | PERS OVEREXPOSURE/TEDE >= 5 REM | [8 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  | 20.2202(b)(1) |  |  | 0
36728 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-25 08:35 | 2000-02-25 14:40 | 2000-02-25 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING THE LOSS OF ONE CRITICALITY CONTROL DURING MAINTENANCE ACTIVITIES "At 0835 hours on 02/25/00, a Nuclear Criticality Safety (NCS) anomalous condition was identified by X-333 Operations personnel, when it was discovered that a process piping opening was not completely covered nor was it being manned by maintenance personnel as required by NCSA-PLANT062.A02. Maintenance Activity at this location had been terminated at approximately 0600 hours, 02/25/00. "This violated requirement #4 of NCSA-PLANT062.A02 which states; 'Openings/Penetrations made during, or as a result of, maintenance activities will be covered to minimize the potential for moderator collection and moist air exposure when unattended.' This constitutes the loss of one NCS control (moderation) with mass and interaction controls maintained throughout this event. "Moderation control was reestablished at 1055 hours by covering the openings under the direction of the Nuclear Safety Engineer. "This is reportable under NRC Bulletin 91-01; 24-hour criticality control. "There was no loss of hazardous/radioactive material or radioactive/radiological exposure as a result of this event. "SAFETY SIGNIFICANCE OF EVENTS: "The safety significance of this event is extremely low. The limited amount of time the flanges were uncovered and unattended did not allow any more moisture to enter than if work had continued and the equipment had been attended for the entire period. Lack of attending personnel during the 'see & flee' simply removed the ability to mitigate an unlikely event involving the entrance of liquid water (or other moderator) into the equipment. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "If the equipment had been mis-categorized and actually contained greater than the minimum Critical mass of uranium (more than 3400 pounds U02F2 at 1.44 wt% enrichment) and liquid water entered the exposed openings, a critical configuration might have formed inside the cascade equipment. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Controlled parameters include mass and moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): "The exact amount is unknown, however, the cell was categorized as 'uncomplicated handling' which means the cell has less than the safe mass (approximately 1500 pounds U02F2 at 1.44 wt% enrichment). The form would be U02F2. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "By leaving the exposed flanges unattended, control #4 of NCSA-PLANT062.A02 which requires 'Opening/penetration made during maintenance activities shall be covered to minimize the potential for moderator collection and moist air exposure when unattended.' "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "Moderation control was reestablished at 1055 hours, 02/25/00, under the direction of the Nuclear Safety Engineer, by covering the opening." Operations personnel informed both the DOE Site Representative and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36727 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2000-02-25 11:00 | 2000-02-25 13:51 | 2000-02-25 | CONTAMINATION LEVELS FOLLOWING URANYL NITRATE SPILL (LOW LEVEL ENRICHED URANIUM) EXCEED ALLOWABLE LIMITS "Westinghouse is making this notification in accordance with 10CFR70.50(b)(1), 'Domestic Licensing of Special Nuclear Material'. "On February 8, 2000, contamination was discovered on a small portion (less than approximately 10%) of a 20 feet x 50 feet outside concrete pad, located adjacent to the Columbia Plant Manufacturing Building (between the building and the Uranyl Nitrate Tank Storage Pad). The contamination resulted from leakage of aqueous material through the wall of the Manufacturing Building from a spill of uranyl nitrate material in the UF6 Bay, near the HF Spiking Station, which occurred on 2/7/00. The leakage of aqueous material outside the building was identified after the inside spill was decontaminated. "The concrete pad was roped off, and decontamination efforts were begun. Based upon initial contamination survey results, the event was not deemed notifiable because contamination levels did not exceed the limit in 10CFR70.50(b)(1)(ii). Decontamination efforts were hampered by the presence of soil on the concrete pad, which had accumulated over the years. As these materials were removed, on February 25, 2000, additional radioactive materials were discovered, making this event reportable under 10CFR70.50(b)(1). Contamination levels measured on 2/25/00 averaged approximately 133 dpm/100 cm2 alpha removable and approximately 6,000 dpm/100 cm2 non-removable alpha. " The area remains roped off, and a decontamination plan is being formulated. As indicated above, the contamination surveys on 2/25/00 reveal that the majority of the contamination is fixed in the concrete. " The decontamination plan will address removal of any loose material on the surface of the concrete, decontamination of the concrete, evaluation of the potential for further movement of material through the walls of the Plant, and an assessment of any movement of radioactive material into the soil." The licensee discussed the above report with NRC staff in Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MATL >5X LOWEST LIMIT | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 70.50(b)(1)(ii) |  |  |  | 0
36726 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-02-25 09:30 | 2000-02-25 11:35 | 2000-02-25 | OFFSITE NOTIFICATION TO THE STATE OF FLORIDA REGARDING A SEA TURTLE RESCUE FROM THE PLANT INTAKE AREA "RESCUED STRANDED KEMPS-RIDLEY TURTLE AT CRYSTAL RIVER UNIT 3 INTAKE AREA. FLORIDA POWER CORPORATION ENVIRONMENTAL REPRESENTATIVE WILL NOTIFY STATE OF FLORIDA." THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36725 | 0 | US STEEL, GARYWORKS |  |  |  |  | 2000-02-25 01:58 | 2000-02-25 09:15 | 2000-02-25 | DAMAGED INDUSTRIAL THICKNESS GAUGE An NDS Model 200 thickness gauge containing 2.001 Ci of Am-241 was damaged when it was struck and dislodged by a break in the continuous strip passing through the thickness gauge measuring area. The location of the gauge is located on the #6 line in the east galvanizing line of the sheet products division. The area was immediately isolated. Their outside consultant was called in to survey and wipe test the gauge. The shutter was in the closed position, there were no indications of a leak or higher than normal radiation readings, and the wipes came back negative for source leakage. There were no personnel injuries due to this event. US Steel has contacted the manufacturer, who will send someone out to retrieve the source and determine if it can be reused or needs to be replaced. US Steel intends to submit a written report to the NRC within thirty days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DAMAGE MEASURE GAUGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT | [5 empty] | 0
36724 | 0 | ARKANSAS DEPT OF HEALTH |  |  |  |  | 2000-02-23 12:00 | 2000-02-24 14:49 | 2000-02-24 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE AT APPROXIMATELY 1200 CST ON 2/23/00, A TROXLER MOISTURE DENSITY GAUGE WAS STOLEN FROM A MATERIALS TESTING OF ARKANSAS, INC., TRUCK PARKED AT A WALMART STORE IN LITTLE ROCK, AR. THE GAUGE WAS A MODEL #3430, S/N 26636 CONTAINING TWO RADIOACTIVE SOURCES; 8 mCi Cs-137 AND 40 mCi 241- AmBe. LOCAL POICE WERE INFORMED AND THE GAUGE WAS RECOVERED ABOUT 2 HOURS LATER ABANDONED ROADSIDE. THERE WAS NO DAMAGE OR INDICATION OF TAMPERING. THE ARKANSAS DEPT. OF HEALTH ISSUED A PRESS RELEASE AND WILL CONTACT THE NRC REGION IV OFFICE. CONTACT THE HEADQUARTERS OPERATIONS OFFICER FOR THE LICENSEE'S ADDRESS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36723 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-02-24 08:49 | 2000-02-24 09:47 | 2000-02-24 | DUE TO A LOCAL POWER OUTAGE ALL 5 OFF-SITE SIRENS FOR NEW HANOVER COUNTY ARE INOPERABLE. On 02/24/00 at 0856 ET the Brunswick Plant Shift Superintendent was notified that off-site sirens for New Hanover County were inoperable. These sirens lost power and became inoperable at 0849 ET. New Hanover County Emergency Operations Center has been contacted and alternate notification mechanisms are pre-established and available. Investigation into the condition is in progress. All but one siren has been returned to service as of 0907 ET on 02/24/00. The NRC Resident Inspector was notified of this event by the licensee. | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) | 50.72(b)(2)(vi) |  |  | 0
36722 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-02-24 02:10 | 2000-02-24 02:48 | 2000-02-24 | EMERGENCY RESPONSE DATA ACQUISITION AND DISPLAY SYSTEM (ERDADS) INOPERABLE GREATER THAN 30 MINUTES. ERDADS LOCKED UP FOR GREATER THAN 30 MINUTES. PERSONNEL HAVE BEEN CALLED OUT TO REPAIR ERDADS. ALL OTHER SYSTEMS OPERATING PROPERLY. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED OF THIS EVENT BY THE LICENSEE. * * * UPDATE ON 02/24/00 AT 0515 ET BY MR. MORRIS TAKEN BY MACKINNON * * * ERDADS RETURNED TO SERVICE AT 0400 ET. R2DO (CHARLES OGLE) NOTIFIED. THE NRC RESIDENT INSPECOTR WILL BE NOTIFIED BY THE LICENSEE OF THIS EVENT UPDATE. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36721 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-23 08:35 | 2000-02-23 19:11 | 2000-03-10 | - Emergency response procedures implemented due to a smoke head alarm and high pressure vent actuation - At approximately 0835 on 02/23/00, Portsmouth operations personnel received a smoke head alarm for extended range product (ERP) compressor W-3 in Area Control Room (ACR)-4. At the same time, another operator in ACR-4 looked at the TV monitor for the ERP compressors and saw a "puff" of smoke around compressor W-3. The plant's "SEE & FLEE" emergency procedures were immediately implemented. The ERP stations' high pressure vent actuated taking the station below atmospheric pressure. Results of all surveys performed during the emergency response were less than minimum detectable activity. At 0949, the emergency response was cancelled. The ERP station was made inoperable to allow for testing of the system by operations and engineering personnel. Portsmouth is reporting this alarm as a valid actuation of a "Q" Safety System. This event is reportable to the NRC as a valid actuation of a "Q" Safety System in accordance with Safety Analysis Report, Section 6.9 (24-HOUR REPORT). There was no loss of hazardous or radioactive material nor radioactive or radiological contamination exposure as result of this event. The NRC Resident Inspector and DOE site representative were notified of this event. PTS-2000-020 PR-PTS-00-01079 * * * RETRACTION 1501 3/10/2000 FROM HALCOMB TAKEN BY STRANSKY * * * "After further investigation, it has been determined that a 'Q' safety system actuation did not occur. The Pyrotronic smoke detectors and the ERP station high pressure vent are not classified as 'Q' safety systems. The CADP smokeheads, which are classified as 'Q' safety systems, did not actuate. Since there was no safety system actuation, this event has been determined to be not reportable to the NRC and is being retracted." The NRC resident inspector has been informed of this retraction. Notified R3DO (Lanksbury). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36720 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-02-23 14:00 | 2000-02-23 18:00 | 2000-02-23 | - Discovery of unfiltered leak path from Secondary Containment to outside atmosphere via the SBGT System - During Standby Gas Treatment (SBGT) System testing, the pressure in the room containing the SBGT System was found to be at a lower pressure than Secondary Containment (SC). The SBGT System draws a negative pressure on the SC during accident scenarios. The SBGT System room is located outside SC. With the SBGT System room being at a lower pressure than SC, a possible leakage path is created from SC into the SBGT System room, into the SBGT System (downstream of the filters) and out the plant stack. This path bypasses the SBGT System filtering assumed in the offsite dose analysis. This leakage path is small, but is not currently assumed in the accident analysis. The licensee is determining corrective actions and plans to resolve this issue prior to restarting the plant. The licensee notified state and local officials and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
36719 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-21 23:45 | 2000-02-22 23:29 | 2000-02-23 | HIGH DISCHARGE ALARM FOR THE W-2 COMPRESSOR. LEAK TESTING OF THE W-2 COMPRESSOR INDICATE A SEAL FAILURE WITH POTENTIAL FOR URANIUM HEXAFLUORIDE OUT GASSING. At approximately 2347 hours, 02/21/00, operations personnel received a Cascade Automatic Data Processing (CADP) smoke head alarm for Extended Range Product (ERP) W-2 withdrawal station compressor. Operations personnel had responded to a High Discharge Alarm for the W-2 compressor and upon arrival discovered the compressor shutdown and the CADP smoke head in alarm. No smoke was discovered during the investigation of the alarm, however the smoke head is located inside a heated housing not readily accessible to operations personnel. Leak testing of the W-2 compressor indicated a seal failure with potential for uranium hexafluoride outgassing. Operations and engineering personnel are continuing to investigate the cause of the smoke head alarm, but have not provided evidence at this time to invalidate the alarm. PORTS is reporting this alarm as a valid actuation to a "Q" Safety System. There was no loss of hazardous/radioactive material or radioactive/radiological contamination exposure as a result of this event. The NRC Resident Inspector was notified of this event by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36718 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2000-02-22 22:05 | 2000-02-22 22:59 | 2000-02-28 | Plant Physical Security Event - Vital area door keys inadvertently removed from the site. Compensatory measures were not fully implemented in the required time but are now fully implemented. The licensee plans to notify the NRC Resident Inspector. Contact the NRC Operations Officer for additional details. * * * UPDATE AT 1455 ON 2/28/2000 BY GROFF RECEIVED BY WEAVER * * * The licensee retracted. The details are available from the NRC Operations Center. The licensee notified the NRC resident inspector. The HOO notified the R3DO (Jordan). | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 0
36717 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-22 12:00 | 2000-02-22 15:54 | 2000-02-22 | NRC BULLETIN 91-01, 4 HOUR REPORT - At 1200 on 02/22/00, the Plant Shift Superintendent (PSS) was notified by the Nuclear Criticality Safety staff that there was a Fissile Material Operation (FMO) for which no Nuclear Criticality Safety Approval (NCSA) existed. While reviewing NCSAs to determine the requirements for moving cylinders into the X-710 laboratory building, it was discovered that the transportation or movement of a five inch diameter cylinder in the X-710 laboratory building hallways was not addressed in any current NCSA. Activities involving the use of five inch diameter cylinders in the X-710 laboratory are addressed by NCSA-0710-006 (Uranium Sampling Laboratory). The laboratory extracts samples from process sampling cylinders, empties, decontaminates and prepares cylinders for reuse in the process facilities. NCSA-0710-006 failed to specifically identify and analyze the movement of five inch diameter cylinders in the X-710 building hallway as an activity to be evaluated. SAFETY SIGNIFICANCE OF EVENTS: Since there is an issue of non-coverage of an FMO, this event is being reported as a Level 2 event - Loss of all double contingency controls applicable to an FMO. However, in practice, the requirements of NCSA-0710-006 are followed. The only time a five inch diameter cylinder is moved out of the Uranium Sampling Laboratory (and into the hallway) is to load them into a PLANT043 transport vehicle. There are also spacing requirements associated with this NCSA. All of the spacing requirements have been met while transporting five inch diameter cylinders through the X-710 building hallway. Therefore, the safety significance is very low. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICAUTY COULD OCCUR]: If a cylinder was not spaced 24 inches from other uranium-bearing material, the chance of a criticality would be increased. Since the cylinders from the Uranium Sampling Laboratory are limited to 5% U-235 enrichment, multiple cylinder spacing upsets would be required before a criticality would be possible (since the evaluation performed in PLANT043 considers two eight inch diameter cylinders in contact at 97.65% U-235 and determines that they would be subcritical). CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, etc): The parameters controlled are the geometry of the five inch diameter cylinder, the enrichment of the cylinder, and spacing between uranium-bearing material and a five inch diameter cylinder. All controls on parameters were maintained. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE OF CRITICAL MASS): The five inch diameter cylinders have a favorable geometry for any enrichment, but are limited to 5% U-235 by an administrative control. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The NCS controls on cylinder geometry, enrichment, and spacing were maintained. A failure has occurred in that the boundaries for NCSAs are unclear as written in their process descriptions. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At the direction of the PSS, the requirements for an NCS Anomalous Condition were initiated. A "Stop Work Notice" was implemented with the following requirements: 1) No movement of five inch diameter cylinders in hallways of the X-710 building. 2) No movement of five inch diameter cylinders into or out of the X-710 building. There was no loss of hazardous or radioactive material nor radioactive or radiological contamination exposure as a result of this event. The NRC Resident Inspector has been notified of this event. PTS-2000- 018 PR-PTS-00-01046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36716 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2000-02-22 10:15 | 2000-02-22 12:16 | 2000-02-22 | - UPS is searching for an overdue shipment of a box of 10 fire exit signs which contain tritium gas - At 1015 on 02/22/00, Lee Cox, North Carolina Division of Radiation Protection (NC DRP), was notified that 1 of 10 cardboard boxes of fire exit signs did not arrive at the intended destination. The missing box contains 10 model #B-100 fire exit signs; each sign contains 17 curies of tritium gas. The signs were shipped via UPS from SRB Technologies Company (NC Licensee), Winston-Salem, NC on 01/27/00 and were scheduled to arrive at DMA Company, Salt Lake City, UT on 02/03/00. On 02/07/00, the shipper, SRB Technologies Company, was notified by the receiver, DMA Company, that 1 of the 10 boxes of signs had not arrived in Salt Lake City. On 02/22/00, the shipper notified NC DRP of the missing box of signs and that UPS is searching for the missing box of signs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | OTH | GEN |  |  |  |  | 0
36715 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-02-21 17:00 | 2000-02-21 19:50 | 2000-02-21 | - Condensate System HELB could disable Div 1 125-vdc breaker control power in Div 1 4-kv switchgear room - Based on the results of a UFSAR review with the plant on cold shutdown condition in a refueling outage, the licensee performed a reevaluation to determine the effect of a high energy line break (HELB) in the condensate system on the Division 1 switchgear. The licensee determined that the flood level in the Division 1 4-kv switchgear room could rise high enough to disable Division 1 125-vdc breaker control power; thus, the Division 1 4-kv switchgear would have been inoperable for this HELB event. The licensee is determining corrective actions. The licensee plans to notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36714 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-02-18 21:30 | 2000-02-21 17:00 | 2000-02-21 | - 24-hour Report, Violation of Operating License, condition existing longer than permitted by Plant Tech Specs - During Unit 1 plant coastdown operations in preparation for a refueling outage, Charging Header Pressure - Low Channel [Plant Technical Specification 3.3.2, Table 3.3.3.3.d.(2)] failed at 2130 CST on 02/18/00. The licensee discovered the failure at 0600 CST on 02/19/00. The licensee placed the instrument in a tripped condition at 0615 CST on 02/19/00 in compliance with Action #16 of the Limiting Condition for Operation. LCO Action #16 requires placing an inoperable Charging Header Pressure Channel in the tripped condition within one hour. The Charging Header Pressure Channel had been inoperable for 8 hours and 45 minutes before the licensee placed it in a tripped condition. The licensee restored the channel to operable status at 1431 CST on 02/19/00. This notification is being made pursuant to Operating License NPF-76, Condition 2.G for operation or condition prohibited by Plant Technical Specifications. The licensee plans to notify the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
36713 | -1 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-02-21 08:40 | 2000-02-21 16:16 | 2000-02-23 | - 24 hour Report, Violation of Operating License, condition existing longer than permitted by Plant Tech Specs - Carbon samples obtained from Fuel Handling Building Exhaust Filtration Unit Train A failed laboratory tests. The Plant Technical Specification 4.7.8.a.2 limit of less than 1% methyl iodide penetration was exceeded. The as-found methyl iodide penetration results were 1.07%. This resulted in the Train A Fuel Handling Exhaust Filtration Unit being inoperable since the time that the carbon samples were obtained at 0900 CST on 02/17/00. This results in the system being inoperable for longer than 7 days which is a violation of Technical Specification 3.7.8. Action a. The sample results were obtained at 0840 CST on 02/21/00. This notification is being made pursuant to Operating License NPF-76, Section 2.G for operation or condition prohibited by Plant Technical Specifications. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1604 ON 02/23/00 BY GREG JANAK TO JOLLIFFE * * * Plant Technical Specification Surveillance Requirement 4.7.8 (b) requires that periodic samples be taken from charcoal beds and analyzed within 31 days after removal. These requirements were met and action to declare that train inoperable was taken upon notification of unsatisfactory results. Based on previous practice, a 24-hour report for a violation of the operating license was made to the NRC as a result of this failure. While onsite for an inspection of the Effluents Program, an NRC inspector questioned the reportability of this event. After further investigation into the issue, and input from both Region IV and NRR on this issue, the licensee has determined that this event is not reportable to the NRC as long as the charcoal in question is replaced within the allowed outage time, as specified in the Plant Technical Specifications. Based on the above, the licensee retracted this event. The licensee plans to notify the NRC Resident Inspector. The NRC Operations Officer notified the R4DO Charles Marschall. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
36712 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-21 10:00 | 2000-02-21 12:22 | 2000-06-26 | NRC BULLETIN 91-01, 4 HOUR REPORT - Material storage areas transferred from DOE to USEC contain uncharacterized potentially fissile material that does not comply with USEC NCS program requirements. The stored material also does not meet DOE NCS requirements. Responsibility for the storage areas was transferred to USEC for more rapid remediation of the non-conforming conditions, in part to support the Seismic Upgrade Project in C-331 and C-335, and to improve overall site safety. SAFETY SIGNIFICANCE OF EVENTS: The DOE material storage areas were located within the boundaries of USEC leased space. Transfer to USEC control allows more timely remediation to establish double contingency controls on the material. Timely remediation will improve overall site safety. The material is in a stable condition and double contingency will be established using USEC procedures. These procedures ensure that safety is not degraded during the remediation actions. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCEANARIO(S) OF HOW CRITICALITY COULD OCCUR]: In order for a criticality to be possible, more than a critical mass would need to be accumulated in an unsafe geometry. The stored material is primarily equipment items in which the fissile material is deposited in small quantities widely dispersed over large surface areas. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY CONCENTRATION, etc): Since no NCS controls were applied to the equipment, double contingency can not be demonstrated. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Unknown due to DOE previously controlling areas. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: No NCS controls (other than providing 10 feet buffer zone) where in place. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Areas are to be remediated in accordance with NCS program requirements. The NRC Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-OO-1009: PGDP Event Report No. PAD-2000-017. * * * UPDATE 1232 4/18/2000 FROM PITTMAN TAKEN BY STRANSKY * * * An additional area, DMSA 30 in C-337, was transferred from DOE to USEC on 4/18/2000 at 1000 CST. The NRC resident inspector has been informed of this update. Notified R3DO (Ring), NMSS (Sturz). * * * UPDATE 1640EDT ON 6/26/00 FROM MIKE UNDERWOOD TO S. SANDIN * * * Assay results identified three converters each containing >400 grams U-235. This amount of material is beyond the scope of the NCS program. Corrective actions have not been identified. The assay results are as follows: 956 gms U-235 assay 42.65% 973 gms U-235 assay 57.45% 1230 gms U-235 assay 29.75% The NRC Resident Inspector has been informed. Notified R3DO(Leach) and NMSS(Piccone). The following UPDATE information was received via fax: EVENT DESCRIPTION: UPDATE 6-26-00: Three equipment items were discovered that contained greater than 5.5 wt. % enrichment and greater than 400 grams 235U. There are no actions specified in NCSA GEN-20 which will result in the ability to establish double contingency. Three items were discovered in DMSA-331-09 containing 956 grams 235U at 42.65 wt. %, 973 grams 235U at 57.45 wt. %, and 1230 grams 235U at 29.75 wt. %. SAFETY SIGNIFICANCE OF EVENTS: UPDATE 6-26-00: Three equipment items have been identified that contain greater than the minimum critical mass. The minimum critical mass Is based on optimum geometry, moderation, and reflection conditions. The material contained within the subject equipment is expected to be distributed throughout the equipment. Due to process nature and equipment design, there are no credible mechanisms for accumulation of material in an optimum geometrical configuration. The subject equipment openings are covered to preclude intrusion of fire sprinkler water and optimum moderation conditions are not credible. A minimum 10-foot exclusion zone has been established around the three equipment items to preclude Increased reflection effects due to equipment/ personnel in the immediate vicinity. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: UPDATE 6-26-00: Three equipment items were identified as containing greater than the minimum critical mass. Since the three items contain approximately 105, 112, and 120% of the estimated minimum critical mass at their respective enrichments, the mass would have to exist in a near optimum geometry, moderation, and reflection before a criticality could occur. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Unknown due to DOE previously controlling areas. UPDATE 6-26-00: The three subject equipment items respectively contained 956 grams 235U at 42.65 wt. %, 973 grams 235U at 57.45 wt. %, and 1230 grams 235U at 29.75 wt. %. Limits as established in NCSA GEN-20 are 400 grams 235U at 5.5 wt. %. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: UPDATE 6-26-00: In addition to the 10-foot buffer zone, an exclusion zone shall [be] established around the three equipment items located in DMSA-331-09 which contain greater than the minimum critical mass. The exclusion zone shall be posted with a minimum 10-foot boundary from the edge of the subject equipment. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: UPDATE 6-26-00: In addition to the 10-foot buffer zone, an exclusion zone shall be established around the three equipment items located in DMSA-331-09 which contain greater than the minimum critical mass. The exclusion zone shall be posted with a minimum 10-foot boundary from the edge of the subject equipment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0
36711 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-02-21 10:50 | 2000-02-21 10:50 | 2000-02-21 | THE LICENSEE DETERMINED A CONDITION OUTSIDE DESIGN BASIS INVOLVING ECCS LEAKAGE OUTSIDE CONTAINMENT. On February 21, 2000 plant personnel determined that a condition outside the design basis of the plant has occurred on Unit 1 & Unit 2 due to defeating part of a compensatory action for monitoring potential emergency core cooling system (ECCS) leakage outside containment. This is reportable per 10 CFR 50.72(b)(1)(ii)(B). On February 10, 2000 Unit 1 Operations noted that no alarms were received when the residual heat removal (RHR) and containment spray (CS) sump pumps automatically started to pump down their respective sumps. Further investigation determined that the computer point to initiate the alarms had been deleted from processing on 8/30/99 for sump level switch work. This computer point was part of a corrective action for an event reported in LER 413-98-016. The LER dealt with an issue where leakage from ECCS components outside containment may not be detected in the time frame specified in the UFSAR for a LOCA. This was reported in the LER as a condition outside the design basis of the plant. Upon discovery, the computer point was returned to service. In addition the security level of the computer point has been increased to require Operations permission prior to modifying the point in any manner. On February 16, 2000, the same computer point was taken out of service without Operations permission for maintenance work. Upon discovery the computer point was returned to service. These events have been entered into the plants corrective action program for determination of the cause of these events and appropriate corrective actions. The cause of this event was due to personnel error. The Resident Inspector will be notified. HOO NOTE: SEE EVENT #34936 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36710 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-02-19 12:04 | 2000-02-19 14:53 | 2000-02-19 | OFFSITE NOTIFICATION 0F A SMALL GASOLINE SPILL IN THE CEDAR RIVER The licensee notified the Iowa Department of Natural Resources, Linn County Sheriff, and the US National Response Center of a reportable spill of gasoline into the Cedar River. While clearing snow at the intake structure, a snow blower fell into the river. During the recovery a small sheen was observed on the river. The snow blower has been recovered. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36709 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-18 13:25 | 2000-02-19 09:52 | 2000-03-13 | 24 HOUR NOTIFICATION - FAILURE OF THE UF6 RELEASE DETECTION SYSTEM At 1325 CST, on 2/18/00, the Plant Shift Superintendent (PSS) was notified of an air leak on the C-310 Cylinder Valve Closure System. The function of this system is to close the cylinder valve in the case of an actuation of the UF6 Release Detection and Isolation System Low Voltage ("New") System at the UF6 Withdrawal Stations. TSR 2.3.4.1 requires this system to be operable while operating in mod 2. At the time the leak was discovered, the air pressure on the Cylinder Valve Closure System was being maintained within allowed parameters. However due to the size of the leak, it was questionable as to if the system could maintain enough air pressure to perform its intended safety function, if it were called upon. After discussing with the C-310 building System Engineer, the PSS could not be provided with reasonable assurance of operability. The UF6 Release detection System was declared inoperable by the PSS, and repair of the system was initiated. TSR required LCO actions were implemented. Repair of the air leak was completed, and the UF6 Release Detection System was returned to Operable status at 1706 CST, on 2/18/00. This event is reportable under 10 CFR 7B.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. The NRC Senior Resident inspector has been notified of this event and the DOE on site representative was also informed. * * * UPDATE ON 3/13/00 @ 1438 BY WALKER TO GOULD * * * RETRACTION THIS EVENT HAS BEEN RETRACTED. Engineering Evaluation EN-C-826-00-018 concluded that the capacity of the backup nitrogen supply regulator was sufficient to provide for this backflow and loss of system air, and still capable of providing flow to close two cylinder valves simultaneously. Thus, the system was capable of performing its intended safety function using nitrogen had it been called upon during the time of the subject event and the 10CFR76.120 reporting criteria were not met. Given the results of this Engineering Evaluation, this event is being retracted. The NRC Resident Inspector was informed and the Reg 3 RDO(Jacobson) and NMSS EO(Smith) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
36708 | 0 | NINE MILE POINT UNIT TWO |  |  |  |  | 1999-12-17 12:00 | 2000-02-18 14:24 | 2000-02-18 | PART 21 - NON-CONSERVATISM IN ENVIRONMENTAL QUALIFICATION (EQ) CALCULATIONS 1-. Affected unit: Nine Mile Point Unit 2 2- Components that contain defect/deviation: Miscellaneous components (limitorque operators electrical cables etc.) in environmental qualification (EQ) program 3- Firm supplying components/activity: Stone and Webster Engineering Corporation (SWEC) 4- Nature of defect/deviation: non-conservatism in EQ calculations (lowest expected ambient temperatures used instead of normal expected ambient temperatures for winter periods). About 30 components will have qualified lives reduced from greater than 40 years to less than 40 years, when non-conservatism is removed. Several hundred other components will have qualified lives reduced but not to less than 40 years. 5- Date on which information was obtained (discovery date): December 17. 1999 6- Number and location of components: potentially numerous components in multiple systems at multiple locations. 7- Corrective actions: EQ calculations and Environmental Qualification Engineering Design Criteria document, which was source of erroneous data for the EQ calculations, will be corrected prior to expiration of actual qualified lives of affected EQ components i.e., within a few years. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0
36707 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-18 | 2000-02-18 14:03 | 2000-03-03 | At 1335 hours on 02/17/00 a see and flee emergency was initiated at the X-330 building Tails position #1. The see and flee was Initiated as a result of a process gas release from the pigtail on Tails position #1. The release was large enough to exceed the capacity of portable mini-gulper staged In the area. The mini-gulper is used to divert and contain any small releases that may occur during pigtail connect/disconnect operations. The release of process gas caused a valid actuation of the pyrotronics smokehead safety system. The pyrotronics smokeheads and pigtail line isolation safety systems operated as designed during this event. UPDATE AT 1445EST ON 3/300 FROM KURT SISLER TO S.SANDIN * * * The Regulatee is retracting this report based on the following: "Nuclear Regulatory Affairs has reviewed the basis for Portsmouth Event Report Notification PTS-2000-017, 'X-330 Tails Withdrawal, Pyrotronics Smokehead Actuation due to PG Release Exceeding the Capacity of the Gulper', and determined that the event should be retracted. (Reference problem report PR-PTS-00.-0096S). "On February 17, 2000 at 1335 hours, an outgassing occurred during the connection of an empty cylinder at Tails position 1. The outgassing was attributed to pressure inside the evacuation manifold due to a cylinder burping operation which had just been completed at Tails position 3. When position 3 was burped, the 1-inch diameter evacuation piping and the position 1 pigtail, which was valved into the evacuation header, would have been exposed to UF6 at above atmospheric pressure. When the burping operation was completed, the position 3 evacuation was valved off and UF6 withdrawal was restarted. "The operator proceeded to complete the connection of a new cylinder at position 1. The operator, who was wearing appropriate personal protective equipment, cracked open and closed the pigtail safety valve per procedure, to evacuate the small space between the cylinder safety valve and the pigtail safety switch, which plugs the safety valve when it is not connected to a cylinder This exposed the space to UF6. As the operator began to remove the pigtail safety switch, he observed smoke which was contained by the gulper. The operator closed the valve and attempted to tighten fittings. When the pigtail safety valve was again cracked open and closed to evacuate the line, smoke exceeded the capacity of the gulper to contain the release and set off both Pyrotronics smokeheads above position 1. The pigtail safety valve was already closed and the Pigtail Line Isolation System closed the manifold safety valve at position 1 automatically. The event was initially determined to be reportable as a Safety System actuation of the Pigtail Line Isolation System in accordance with the Safety Analysis Report Section 6.9, Table 6.9-1, J.2. "The TSR 2.5.3.4 Basis Statement indicates that the purpose of the Pigtail Line Isolation System is to minimize a release of liquid UF, due to pigtail failure during a withdrawal (Modes II and III). Since the pigtail was isolated from the liquid UF, system while the cylinder was being connected, Tails Withdrawal position 1 was in preparation mode (Mode I) and the Pigtail Line Isolation System safety function was not required. "The reporting criteria in Table 6.9-1, J.2 states that an actuation is reportable for events having the potential for significant impact on the health and safety of personnel. Events having the potential for significant impact are those events where actual plant conditions existed that the system was designed to protect against. Since position 1 was not in a Mode for which the safety system was required to be operable, this event has been determined to not be reportable to NRC. Accordingly, this was not a valid actuation of a safety system. The event notification PTS-2000-017 may be retracted." Operations informed the NRC Resident Inspector and the DOE Site Representative. Notified R3DO(Jordan) and NMSS(Cool). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36706 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-16 16:00 | 2000-02-17 13:23 | 2000-02-18 | NRC BULLETIN 91-01 RESPONSE (24-HOUR REPORT) The following text is a portion of a facsimile received from Portsmouth personnel: "On 02/18/00 at 1600, the Plant Shift Superintendent (PSS) was notified of a loss of one control parameter, geometry, in NCSA-0705_100.A01 for the X-705 decontamination facility. During a boroscope inspection of the 'A' pre-evaporator loop condenser/condenser tubing, a problem with three tubes were observed. Two tubes have sections missing below the tube sheet, and one tube was crimped such that it did not make a seal against the tube sheet. After discovery of the problem, the pre-evaporator condenser was isolated for repair." "The second control parameter of NCSA-0705_100.A01, volume, was maintained throughout the inspection." "There was no loss of hazardous/radioactive material or radioactive radiological contamination exposure as a result of this event." "SAFETY SIGNIFICANCE OF EVENTS: "During a boroscope inspection of the 'A' pre-evaporator loop condenser/condenser tubing, a problem with three of the tubes was observed. Two of the tubes had sections missing below the tube sheet, and one of the tubes was crimped such that it did not make contact with (seal against) the tube sheet. Per discussion with the system engineer, these failures indicate that the integrity of the tubes could no longer be assured. This is a loss of passive barrier 2(PB2) counted upon in NCSA-0705_100.AOI to maintain double contingency. Since there is no indication that the verification of the cooling water flow was lost, any intermixing of the solutions would have resulted in water entering the tube side of the condenser and getting pumped with condensed solution to overhead storage. Since the downstream components from the tube side of the condenser are evaluated for uranium-bearing solutions, the addition of water to the solution would be bounded by the original solution (i.e., the original solution would be diluted by the water). Therefore, the safety significance of the event is low." "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Given the failure of the condenser tubes integrity, if the pressure of the shell side had been lower (water not valved in) the condensed gas (uranium-bearing solution) could have been discharged along with the pathway that the process water normally takes. This stream leads to the storm sewer system, which has not been analyzed for an accumulation of uranium-bearing material. If the material had settled out/been deposited in an unfavorable location in the sewer system, a criticality could have resulted." "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): The parameters being controlled under this NCSA were geometry and volume. By taking credit for the integrity of the condenser tubes and verifying the flow of the cooling water on the shell side, the resulting condensed uranium-bearing solution is maintained in a safe geometry environment. Loss of condenser tube integrity meant only the pressure differential of the cooling water prevented the uranium-bearing solution from entering a system not designed for handling that material." "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST): The system is analyzed for up to 100 wt% U235. Since the secondary control for keeping the uranium-bearing solution in a geometrically favorable system was maintained, (the check on the cooling water), no material was actually introduced into the storm sewer system." "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Based on the visual inspection of the tube/tube sheet interface, at least three tubes appear to have failed such that intermixing of the solution is possible. This represents a loss of a passive barrier (P82 in the NCSA) credited for meeting the double contingency principle for the operation." "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: At 1730, [the] A, B, and C post-evaporator condensers and 'A' pre-evaporator condenser are tagged out of service. Water and steam are isolated from the condensers." Portsmouth personnel notified the NRC resident inspector and Department of Energy site representative. * * * UPDATE AT 1335 ON 2/18/2000, BY SPAETH RECEIVED BY WEAVER * * * This update is being provided to clarify the controlled parameter associated with the NCSA applicable to this event. The NCS parameter being controlled for this event is geometry. Although volume is a parameter identified in the NCSA for this operation, volume is not relevant to this event. Two controls are in place to maintain the geometry parameter, tube integrity and water pressure differential. By taking credit for the integrity of the condenser tubes and verifying the flow of the cooling water on the shell side, the resulting condensed uranium-bearing solution is maintained in a safe geometry environment. Loss of condenser tube integrity meant only the pressure differential of the cooling water prevented the uranium bearing solution from entering a system not designed for handling that material. The licensee notified the NRC resident inspector. The operations center notified the R3DO(Jorgensen) and NMSS EO (HICKEY). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36705 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-02-17 10:00 | 2000-02-17 11:30 | 2000-02-17 | DISCOVERY OF CABLING NOT ROUTED IN ACCORDANCE WITH APPENDIX 'R' REQUIREMENTS The following text is a portion of a facsimile received from the licensee: "During the Appendix 'R' rebaselining project, it was discovered that in both units' containment's redundant [safety-related] instrumentation cabling was routed [within] 20 [feet] of each other. This is not in accordance with Appendix 'R' requirements as described in Section iii.g.2. Due to strict administrative controls, there is minimal fire risk in these areas." The licensee notified the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36704 | 0 | NC DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-02-04 | 2000-02-17 10:55 | 2000-02-17 | TROXLER MOISTURE DENSITY GAUGE LOST DURING SHIPPING The following information was submitted by the State of North Carolina via facsimile: "Froeling & Robertson, Inc (F&R). (N.C. License No. 092-0353.6) shipped one Troxler Model 3411-B nuclear gauge (s/n 9220) from the Raleigh, NC office to their Chesapeake, VA. Office (NRC License No. 45-08890-02) on 04 February 2000 via FedEx. As of today's date, the gauge has not been delivered to the Chesapeake office. "FedEx is conducting a search of the Raleigh, NC, hub, as well as tracking the package at other FedEx hubs in the area. F&R has notified all of its branch offices of the occurrence. "North Carolina has assigned log number ICD-00-03 to this incident." *************** UPDATE AT 1341 ON 02/17/00 FROM J. MARION EADDY TO LEIGH TROCINE *************** The following text is a portion of a facsimile received from the North Carolina Division of Radiation Protection: "UPDATE on Loss of a Troxler Model 3411-B Moisture/Density Gauge NC Log No. ICD-00-03." "[The] North Carolina Division of Radiation Protection received a call from the Radiation Safety Officer for FedEx this afternoon. The gauge (Troxler Model 3411-B s/n 9220) was located at Troxler Electronic Laboratories Research Triangle Park Office." "North Carolina is continuing to investigate this incident." The NRC operations officer notified the R2DO (Barr) and NMSS EO (Piccone). Call the NRC operations officer for a contact telephone number | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | NC | MAT | [5 empty] | 0
36703 | -1 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-02-16 07:59 | 2000-02-17 10:39 | 2000-03-17 | LICENSEE 24-HOUR REPORT DUE TO EXCEEDENCE OF LICENSED POWER LIMIT "On February 16, 2000, at 0759 PST Diablo Canyon Power Plant (DCPP) exceeded the Operating License reactor core power of 3411 megawatts by greater than 2 percent. At 0757 PST with Unit 2 at nominal full reactor power a load transient bypass (LTB) signal was initiated diverting main feedwater around the normal feedwater heaters into the steam generators. During the resultant sudden temperature decrease, reactor power peaked at 103.8% and exceeded the nominal full power for a total of six minutes. "The transient was initiated by utility maintenance personnel during the scheduled performance of instrumentation calibration of circuits associated with the LTB. Technicians performing a calibration inadvertently disturbed an input circuit creating an invalid LTB initiate signal. "The feedwater temperature was rapidly reduced approximately 45 to 50 degrees F. The Final Safety Analysis Report Update Chapter 15, 'Accident Analyses,' Condition II, 'Faults of Moderate Frequency,' Section 15.2.11, 'Sudden Feedwater Temperature Reduction,' provides bounding analysis for this event. The FSAR Update concludes that for temperature drops of less than 73 degrees F that the reactor will remain in operation and the reactor will not go below the minimum DNBR. FSAR Update Section 15.2.11.1 analysis specifically identifies the inadvertent actuation of the LTB as an initiating event bound by the analysis.) "The DCPP Unit 2 Operating License DPR-82, Condition 2.C(1) authorizes PG&E to operate Unit 2 at reactor core power levels not in excess of 3411 megawatts thermal (100% rated power). DPR-82, Condition 2.G, 'Reporting,' requires Emergency Notification System reporting within 24 hours and a written followup report within 30 day in accordance with the procedures described in 10 CFR 50.73(b), (c), and (e). This event will be reported as Licensee Event Report (LER) 2-00-001." ************** UPDATE AT 1328 EST ON 03/17/00 FROM RICH LUCKETT TO LEIGH TROCINE ************** The licensee is retracting this event notification because the NRC had rescinded the requirement to make this report and because the licensee had not received it. On 02/24/00, the NRC issued a letter identifying that Operating License DPR-82, as modified by License Amendment No. 120 on 02/03/00, was not properly issued to the correct license. Consequently, the reporting requirement identified was incorrect, and a report was not required. The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Graves). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0
36702 | 0 | U.S. ARMY |  |  |  |  | 2000-02-02 | 2000-02-17 09:48 | 2000-02-17 | LOSS OF SEALED SOURCE CONTAINING 30 mCi OF TRITIUM The licensee reported the loss of a small tritium source from a mortar system assigned to the U.S. Marine Corps School of Infantry at Camp Le Jeune, NC. A scale index lamp (a plastic arrow containing 30 mCi of tritium) became detached from an M-64 mortar sight unit while the mortar unit was being used on a firing range. The source was discovered to be missing after the unit had been moved from the firing range. The licensee stated that the source could not be located. This source poses no threat to the public as access to the firing range is controlled. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | NC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
36701 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-16 12:00 | 2000-02-17 09:19 | 2000-02-17 | NRC BULLETIN 91-01 REPORT "On 2/16/00 at 1200 Plant Shift Superintendent (PSS) was notified of a loss of one control spacing, in NCSA-0710_006.A01 for the X-710 laboratory facility. During a walk down of proposed revision to the NCSA laboratory personnel discovered that a vertical spacing requirement for storage racks was not being maintained. This was a violation of one control of the double contingency controls established by this NCSA. The other control geometry was maintained through. To regain compliance the containers stored in the affected storage racks were removed and the storage racks were tagged out of service by 1530 hrs. "SAFETY SIGNIFICANCE OF EVENTS: "The safety significance of this event is very low. The smallest actual spacing between storage clusters was approximately 11.25 inches. Since each storage bin is 5"x 5", and the tallest arrangement of containers in a bin is approximately 4 inches, the extra inch gap results in adequate spacing between the containers. Also, the enrichment of the containers stored in the bins is limited by PORTS certification to less than 20% versus the 100% enrichment analyzed in the NCSE. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "If all the bins were over loaded with containers and the bins were adjacent and all the containers were filled with the analyzed limit of 100% enriched material, a spacing violation with a person carrying a polybottle might cause a criticality. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "Geometry and Spacing were the controlled parameters. The spacing control was lost when the vertical distance between storage bins was found to be less than 12 inches. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST): "The amount of material is variable depending on whether 2S, 1S or 990 cold traps are considered. The enrichment is analyzed to 100%, although the PORTS' operating certificate limits the cascade to 20%. The form of the material in the containers is UF6. The percent worst case of critical mass is not known, however, at 100% enrichment a single 2S cylinder can contain more than the minimum critical mass. In reality, at 5% enrichment, it would require over 20 25 cylinders to have more than minimum critical mass. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Geometry and spacing were controlled. The spacing control was lost because the storage bins were not the correct vertical distance apart. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "At 1530 hrs, all controls were regained." The NRC resident inspector has been informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36700 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-02-16 17:55 | 2000-02-16 19:19 | 2000-02-16 | TEMPORARY FIRE PENETRATION IN THE CABLE SPREADING ROOM WAS FOUND TO BE POTENTAILLY OUTSIDE THE PLANTS DESIGN BASIS. A condition was discovered which is potentially outside the plants design basis. Engineering review of a temporary fire penetration in the cable spreading room determined that it would not withstand a high energy line break event. This may result in the temperature in the cable spreading room exceeding the design basis temperature for equipment located in the room. The temporary fire penetration has been sealed and is now fully operable. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36699 | 0 | ONCOLOGY INST. OF GREATER LAFAYETTE |  |  |  |  | 2000-02-16 15:00 | 2000-02-16 16:12 | 2000-02-16 | UNINTENDED SITE IRRADIATED While performing high dose rate (HDR) endobronchial brachytherapy, it was discovered that unintended sites in a patient had been irradiated. The licensee uses a Nulceatron Micro Selection HDR #31024, controlled by an IBM G50 computer. It was discovered that after the dwell time was entered into the computer, if the enter key is pushed twice instead of once, the distance that the source moves is increased by 100% without warning the operator that the distance had changed. (If the source is supposed move 4 centimeters and you push the enter key twice that source will move 8 centimeters). A patient received three unintended site radiation treatments to his bronchial tube before the problem was discovered. An NRC Region 3 Inspector was at the facility when this incident occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0
36698 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2000-02-16 13:52 | 2000-02-16 14:41 | 2000-02-16 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO AN UNISOLABLE REACTOR COOLANT PRESSURE BOUNDARY LEAKAGE. At 1305 EST on 02/16/00 a small leak ("weeping steam") was discovered in the reactor coolant system pressure boundary on a 1.5 inch (ID) post accident sampling system line. The leak is estimated to be 0.03 gpm based on historical trending of the reactor building normal sump. The leak was discovered during a reactor building entry to investigate reactor coolant pump seal indications. At 1352 EST on 02/16/00 shutdown was commenced. Unit 1 must be in Mode 3 (Hot Standby) by 02/17/00 at 0105 EST and in Mode 5 (Cold Shutdown) by 02/18/00 at 0105 EST per Technical Specification 3.4.13, "Reactor Coolant Operational Leakage." The post accident sampling line connects to the coolant cold leg piping between the "B" once through steam generator and the suction side of reactor coolant pump "1B2". The leak is coming from the area of a 90 degree elbow where the sampling line passes near the containment floor. All emergency core cooling systems and the Keowee system are fully operable. The electrical grid is also stable. The NRC Resident Inspector was notified of this event by the licensee. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(i)(A) |  |  |  | 0
36697 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2000-02-15 20:58 | 2000-02-16 00:21 | 2000-02-18 | FLAWED WELD DISCOVERED DURING PLANT OUTAGE "At 2058 CST on 2/15/2000, a flawed weld was identified on an instrument connection to the Reactor Coolant System Loop 'A' Hot Leg Piping. The subject flaw was identified by Non-Destructive Examination (NDE) at the connection of Level Instrumentation to the RCS Hot Leg Piping. Unit 1 was taken offline at 0010 on 2/5/2000 for scheduled maintenance. Boron buildup was identified on 2/15/00 at the subject connection while the plant was at cold shutdown condition. The accumulated boron indicates the leakage through the weld flaw is classified as very small weepage. The unidentified RCS leak rate prior to thc scheduled outage was 0.093 GPM. No unexplainable changes in RCS leak rate exist for cycle 16 operation. Due to the physical location of the connection, major scaffolding was required to access the area. At 2058 on 2/15/2000, NDE was complete identifying the reportable condition. Further investigation by Plant Staff is in-progress to characterize the flaw morphology and cause. This report is being performed to comply with the requirements of 10CFR50.72(b)(2)(i)." The NRC resident inspector has been informed of this event by the licensee. * * * UPDATE AT 1352 ON 2/18/2000, BY DAVENPORT RECEIVED BY WEAVER * * * Unit 1 was taken off-line at 0010 CST on February 5, 2000, for scheduled maintenance and is currently in a cold shutdown condition. Boron buildup was identified at 5 additional level instrumentation connections on the RCS A and B Hot Leg piping. The accumulated boron indicates the leakage through the weld flaws is very small weepage. Due to the physical locations of the connections, major scaffolding was required to access the areas. NDE was performed to confirm the initial nozzle leak found on 2/15/2000. Due to radiological conditions, as-found NDE will not be performed on the remaining leaking nozzles as planned. The visual inspections already performed are sufficient to determine past leakage. None of the identified flaws are actively leaking with the reactor in cold shutdown. The unidentified RCS leak rate prior to the scheduled outage was 0.093 gpm. No unexplainable changes in the RCS leak rate existed for the Cycle 16 operation. Further investigation by Plant Staff is in-progress to characterize the flaw morphology and cause. The licensee notified the NRC resident inspector, the Operations Center notified the R4DO (Tapia). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36696 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-02-15 19:40 | 2000-02-15 20:35 | 2000-02-16 | UNIDENTIFIED LEAKAGE 1.1 GALLONS PER MINUTE "Elevated reading noted on Unit 2 Plant Vent Radiation Monitor (2R41D) concurrent with slowly lowering Volume Control Tank (VCT) level. Plant was operating at 100% reactor power. Investigation by on-shift personnel estimated unidentified RCS leakage at 1.1 gpm. This value exceeds the Tech Spec limit of 1 gpm unidentified (Reference Tech Spec 3.4.7.2). The Unit 2 Reactor Coolant Filter had been replaced on dayshift. Operators isolated the Reactor Coolant Filter at 2010 and the leakage appears to be stopped. This report is being made for RCS leakage outside containment which may result in exceeding GDC-19 criteria for Control Room habitability." The leak appears to have started at 1638 EST and was stopped at 2010 EST. The volume that was lost is estimated at 160 gallons, the leak was through a hard pipe directly to a radiation waste tank. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 02/16/00 AT 1647ET BY S. SAUER TAKEN BY MACKINNON * * * Further review of the above event report for reactor coolant leakage outside containment, which may have resulted in exceeding GDC-19 criteria for control room habitability has identified that this leakage flow path is not part of the post accident recirculation flow path in communication with the containment sump. Leakage from systems that are isolated from the recirculation flow path or that can be isolated from it, without degrading the ability to recirculate the reactor coolant system are not included in leakage requirement of the USFAR. R1DO (F. Costello) notified. The NRC Resident inspector was notified of this event retraction by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRAD COND DURING OP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(ii) |  |  |  | 0
36695 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-02-15 19:29 | 2000-02-15 20:07 | 2000-02-16 | REACTOR MANUALLY TRIPPED DUE TO INDICATION OF A STEAM GENERATOR TUBE RUPTURE ON STEAM GENERATOR # 24. The licensee was at 99% power when they received indication of a steam generator tube rupture on steam generator #24. The steam generator tube rupture was initially estimated to be approximately 90 gallons per minute. At 1929, the reactor was manually tripped, and all rods fully inserted into the core. The faulted steam generator was isolated. Currently, reactor coolant system pressure is 2243 psig, temperature is 547 °F and pressurizer level is being maintained at 35%. The licensee declared an Alert classification at 1929 per EAL 3.1.2 (large amount of water out of the reactor coolant system). The NRC entered Standby at 2049 EST. The NRC response was deescalated to Monitoring at 2335 EST. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1000 @2/16/00 * * * COMMISSIONER'S ASSISTANTS BRIEFING GIVEN BY RANDY BLOUGH ON THE INDIAN PT 2 ALERT. The following persons participated in the briefing: Region 1 RA (Hub Miller), R1 PAO(Diane Screnci), R1 (Jennifer England), RI (Pete Habighorst), R1DO (F. Costello), IRO (F. Congel), EDO (Bill Travers), DEDR (Frank Miraglia), NRR (Sam Collins), EDO Staff (Mike Tschiltz), Chairman's Office (Terence Chan), Comm. Dicus' (Thomas Hiltz), Comm. McGaffigan's (Jeff Sharkey), Comm. Diaz's (Roger Davis), Comm. Merrifield's (Brain McCabe), NRR PD (Jim Clifford), PM (Jeff Harold), NRR EO (Tad Marsh), PA (Sue Gagner), State Programs (Paul Lohaus), IP (Howard Faulkner), and CAO (Tom Madden). DEDMRS Staff and SECY did not participate. * * * UPDATE AT 1922 @ 2/16/00 BY SPALL TAKEN BY MACKINNON * * * As of 1657 hours, Unit 2 attained a cold shutdown condition. Leakage from the reactor coolant system into # 24 steam generator has stopped. Indian Point 2 is terminating the alert classification as of 1850 hours and will be entering the Recovery Phase. At 1915 hours NRC exited Monitoring mode and returned to normal operations. NRC Resident Inspectors notified. R1DO (F Costello), NRR EO(D Wessman) and IRO (Joe Giitter) notified. FEMA (Eaches), DOE (Bob Young), USDA (Corley), HHS (Pamela), and EPA (Garneau) notified that Indian Point Unit 2 exited their Alert classification at 1850 hour and entered Recovery Phase and were also notified that the Nuclear Regulatory Commission exited Monitoring Mode at 1915 hours. | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | COMM ASST BRIEF |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | ALERT | 1 | NY | POW |  | 50.72(a)(1)(i) |  |  |  | 0
36694 | 0 | INEEL |  |  |  |  | 2000-02-15 13:25 | 2000-02-15 17:36 | 2000-02-15 | THREE MILE ISLAND UNIT 2 SPENT FUEL STORAGE CONFINEMENT SYSTEM IN USE HAS A POTENTIAL FOR A SIGNIFICANT REDUCTION IN EFFECTIVENESS. THIS IS NOT A SAFETY ISSUE. At 1325 MST, 15 FEB 2000, a determination was made that a spent fuel storage confinement system in use has a potential for a significant reduction in effectiveness. This conclusion is based on an engineering evaluation of plugs in the Three Mile Island Unit 2 (TMI-2) core debris Canisters. These plugs are approximately 2" diameter and there are two plugs in each TMI-2 Canister. There are eight TMI-2 Canisters in the Dry Storage Canister (DSC) currently in storage at the TMI-2 ISFSI. The TMI-2 ISFSI Safety Analysis Report takes credit for the plugs being in place for the design function of the confinement of radioactive material. The DSC containing the eight TMI-2 Canisters continues to provide an intact outer confinement boundary. The condition described above exists at the TMI-2 ISFSI at the Idaho National Engineering and Environmental Laboratory. The affected DSC contains eight TMI-2 Canisters containing TMI-2 core debris. The U-235 inventory is conservatively estimated to be significantly less than 1 kilogram for the entire DSC. There are no potential for personnel radiation exposure associated with this condition. There is no potential for release of radioactive material from the DSC associated with this condition. NRC Region IV has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SPENT FUEL CASK EVENT | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 72.75 |  |  |  | 0
36693 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2000-02-15 11:31 | 2000-02-15 15:31 | 2000-02-15 | BUILDING FF (OSO BUILDING) WITHOUT CRITICALITY ALARM COVERAGE FOR APPROXIMATELY 7 HOURS. On 2/12/00, at approximately 1320, a short circuit in one of the circuits in the plant uninterruptable power system (UPS) caused a fuse to blow which de-energized the circuit. This caused a loss of power to several of the Security Data Gathering Panels (DGPs). Appropriate security compensatory measures were taken and repairs to the DGPs completed by approximately 2015 on 2/12/00. During the course of the investigation it was discovered on 2/15/00 that the criticality monitoring system and the evacuation howlers at Building FF (OSO Building), which is used to store uranium enriched to no greater than 5 %, are also powered by the UPS circuit that was affected. When the UPS circuit was broken, the criticality monitoring system and the evacuation howlers for Building FF were not functional. The two other criticality monitoring systems (NNFD Main Plant and LRC) remained functional since they are not on the affected UPS circuit. The Security DGPs are also used to monitor the performance of the criticality monitoring systems at the site. The uninterruptable power supply circuit which feeds the Building FF criticality system also feeds the DGP monitoring the criticality system. When UPS power was lost, the DGP did not provide warning that the criticality monitoring system had failed and appropriate compensatory actions were not implemented. Therefore, for approximately 7 hours, Building FF was without criticality monitoring as required. Normally this facility is unoccupied on weekends. No SNM operations were being conducted during this 7-hour period, however, they are still investigating when and if personnel could have been present in the building. Immediate actions are being taken to assure safety management is immediately notified of any failures of DGP or UPS systems so that appropriate compensatory actions can be taken. As the investigation proceeds, additional actions will be taken as appropriate. All criticality monitoring and evacuation alarm systems have been operating normally since the incident and are presently fully functional. The NRC Licensing Project Manager for NNFD and the NNFD Resident Inspector who are onsite at NNFD have been briefed on this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 70.50(b)(2)(ii) |  |  |  | 1
36692 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-14 17:00 | 2000-02-15 00:30 | 2000-02-15 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING LOSS OF GEOMETRY/VOLUME CRITICALITY CONTROL IN THE X-705 DECONTAMINATION FACILITY "On 2/14/00 the Plant Shift Superintendent (PSS) was notified of the loss of one control parameter, geometry/volume in the X-705 decontamination facility. A vinyl covered foam padded chair was found in the high bay area with the vinyl covering worn open. This is a violation of NSCA-0705_076 inadvertent containers. The foam padding thickness was greater than the requirement for absorbent material described in NCSA-0705_076. "The system integrity of nearby uranium-bearing pipes was maintained. Therefore, no solution was actually present to accumulate on/in the padding of the chair. "The chair was moved to an area in the high bay not covered by the above described NCSA. Compliance with NCSA--0705_076 is restored "THERE WAS NO LOSS OF HAZARDOUS/RADIOACTIVE MATERIAL OR RADIOACTIVE/RADIOLOGICAL CONTAMINATION EXPOSURE AS A RESULT OF THIS EVENT. "SAFETY SIGNIFICANCE OF EVENTS: "A padded chair (seat dimensions approximately 17.5" x 21" x 3.5") was used near a uranium solution transfer line. The vinyl on the seat was damaged to the point that any solution if splashed in to the chair could have accumulated in the padding. The padding is an unsafe height > 1 .5") and has a total volume >20 liters, which is well above the allowed limit of 4.8 liters. The transfer line near this seat can contain high concentrations of HEU solution. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO[S] OF HOW CRITICALITY COULD OCCUR): "If the solution line had failed, uranium-bearing solution could have splashed/sprayed onto the seat padding and accumulated. Since the total volume of the padding was greater than the allowed 4.8 liters and the height (excluding and swelling of the material) was greater than the allowed 1.5" an unsafe condition would have resulted and a criticality could have resulted. "CONTROLLED PARAMETERS (MASS, MODERATION. GEOMETRY, CONCENTRATION, ETC.): The parameter lost was the geometry/volume of the absorbent material on the chair. The physical integrity of the transfer line was maintained. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST "No material accumulated on/in the chair padding. The transfer line near the chair can contain HEU solutions with high uranium concentrations. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "Requirement #4 requires that absorbent material be covered or modified to prevent an unfavorable accumulation in the event of a solution leak in a nearby system. The chair padding was absorbent and the vinyl covering had degraded to the point that solution hitting the chair could accumulate in the padding. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: "Compliance was regained when the chair was moved to an area not covered by NCSA-0705_076. Crew briefing are being conducted shiftily and the chair in question is caution boundaried." Operations personnel notified both the DOE Site Representative and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36691 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2000-02-14 11:30 | 2000-02-14 15:40 | 2000-02-14 | 4-HOUR NRC BULLETIN 91-01 REPORT INVOLVING LOSS OF MASS CONTROL At approximately 1145 on February 14, 2000, nuclear safety confirmed that 55 cans of grinder swarf material (grindings from making fuel pellets) was stored at pad storage in violation of the established mass limit for heterogeneous material. The mass limit used to determine each can's allowable weight was incorrectly assigned. The storage of these cans at this location resulted in a loss of mass control. Geometry control on spacing remained intact, thus no unsafe condition existed. Relocation of affected cans to approved storage locations is in progress and is expected to be completed within 90 minutes of this report. Scrap material movement from the Gadolinium Shop to Fuel Support pad storage has been suspended pending investigation and implementation for corrective actions. SAFETY SIGNICANCE OF EVENTS: Low safety significance - fixed geometry/spacing control on heterogeneous scrap storage remained intact. POTENTIAL CRITICALITY PATHWAYS INVOLVED: Multiple failure modes required before a criticality accident could occur. CONTROLLED PARAMETER(S) (MASS, MODERATION, GEOMETRY, CONCENTRATIO, ETC.) Geometry/Spacing: single-planar array of 3-gallon heterogeneous scrap demonstrated safe optimally moderated, 12-inches edge-to-edge spacing provided by treated wooden storage racks. Mass: mass of 3-gallon heterogeneous scrap material limited to 16.5 kgs (gross) weight per can. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL : Affected 3-gallon gadolinium grinder scrap cans contained approximately 25 kgs of Uranium Dioxide versus limit of 16.5 kgs gross weight. At a 12-inch edge-to-edge spacing, single planar array storage configuration is demonstrated safe for "optimally moderated" heterogeneous Uranium Dioxide plus water mixture. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTATION OF THE FAILURES OF DEFICIENCIES: Administrative mass control on gadolinium grinder swarf. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. All gadolinium scrap movement to fuel support suspended. 2. Relocated affected cans to approved storage locations under NSE direction. 3. Investigation and implementation of corrective actions pending. The Licensee will inform NRC Region 2, State and Local officials of this event notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0
36690 | 0 | LESTER E. COX MEDICAL CENTER |  |  |  |  | 2000-02-03 12:00 | 2000-02-14 12:35 | 2000-02-14 | 15 MILLICUIRE NICKEL-63 SOURCE USED IN A HP GAS CHROMATOGRAPHY MISSING Today at 0930 CT the Radiation Safety Officer for Cox Health System was informed by the Chief of Safety for Lester E. Cox Medical Center - North, located in Springfield, Mo., that a 15 millicurie Ni-63 source for a HP Gas Chromatography was missing and is now believed to be buried in a local land fill. The source was initially purchased on July 30. 1982 and it was last used in 1990. Since 1990 the source had been in a storage room located in the toxicology lab at Lester E. Cox Medical Center - North, Springfield, Mo. The items stored in the storage room were moved earlier this year to another location in the Lester E. Cox Medical Center - North. The left over items in the storage room were discarded into a BFI Dumpster at their facility and it is believed that the Ni-63 source was discarded to the BFI Dumpster. On 02/03/00 BFI hauled the contents of the dumpster to a local land fill. At this time the licensee is trying to find out if it is necessary to recover the Ni-63 source. Ni-63 is a pure Beta emitter and the energy of the Beta particles is 17 Kev. HP registry number for the Gas Chromatography is NR-348-D-804-B. Call the Headquarters Operation Officer for address and phone number. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0
36689 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-02-14 10:30 | 2000-02-14 12:19 | 2000-02-22 | THREE CONTAINMENT NITROGEN MAKEUP FOR TORUS AND DRYWELL VALVES ARE NOT CAPABLE OF CLOSING DURING A DESIGN BASIS ACCIDENT. Control Room was notified by system engineering that design basis review calculations have determined that Air Operated Valves CV4311, CV4312, and CV4313 (containment nitrogen makeup for torus and drywell) are not capable of closing during a design basis accident. The spring closing force is borderline such that the spring force may not be large enough to close the valve when the containment is at its maximum pressure during a design basis accident. CV4311, CV4312, and CV4313 have been declared inoperable. The licensee entered Technical Specification 3.6.1.3 condition B to isolate the affected penetrations within one hour. The valves have been closed and at this time the licensee is de-energizing the power to the valves. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1137 ON 02/22/00 BY BRIAN HUPKE TO JOLLIFFE * * * After testing the above valves and reviewing the margins in the analysis used, the licensee has concluded that the valves were actually capable of performing their intended containment isolation function. The licensee declared these valves operable at 1619 CST on 02/17/00. Since this event is no longer reportable to the NRC, the licensee desires to retract this event and does not plan to submit an LER on this event. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO Jim Creed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36688 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-02-14 11:33 | 2000-02-14 12:12 | 2000-02-14 | SPDS DECLARED INOPERABLE THE PLANT NOTICED A FAILURE OF THEIR SPDS PORTION OF THE EMERGENCY RESPONSE FACILITY COMPUTER SYSTEM (ERFCS) AT 1133 EST. HOWEVER ,THE SYSTEM WAS RETURNED TO OPERABLE CONDITION AT 1140 HOURS. THIS CONDITION WAS DUE TO SYSTEM TIME NOT UPDATING. THE ERFCS WAS REBOOTED SATISFACTORILY AND ALL PORTIONS OF THE SYSTEM WERE NOTED TO BE FUNCTIONING CORRECTLY AT 1140 HOURS. INSPECTION OF THE SYSTEM ALARM SUMMARY INDICATED THAT THE LAST TIME A VALID SYSTEM TIME UPDATE OCCURRED WAS 1013 HOURS. THE RESIDENT INSPECTOR WILL BE NOTIFIED. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36687 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2000-01-28 10:00 | 2000-02-14 11:15 | 2000-02-14 | FLORIDA AGREEMENT STATE REPORT INVOLVING MEDICAL MISADMINISTRATION DURING GAMMA KNIFE TREATMENT "Patient was being treated with Gamma knife for brain lesions. On Tuesday, Jan 25, patient was supposed to have lesions #44-49 treated. A mistake in site location resulted in lesion #16 being retreated instead of lesion #47. This mistake was discovered at approximately 10:00 am on Friday, Jan 28 by Dr. Coy. NRC Region II was notified of this incident on 1-31-00 and agreed that the investigation should be completed before NRC Ops [Center] notification to make sure it was an abnormal occurrence. Investigator found no violations of the license or regulations. The licensee's quality assurance program found the error. The licensee had the wrong site set in the computer when the procedure was performed. The additional dose to this site has not caused any harmful effects in the patient." The maximum dose received was 12 gray from a Gamma knife loading of 201 rods each containing 36 Curies Co-60 activity/rod. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | MED MISADMINISTRATION | [8 empty] | NON EMERGENCY | 2 | FL | OTH | AGR |  | 35.33 |  |  | 0
36686 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-02-13 18:32 | 2000-02-13 19:56 | 2000-02-13 | AUTOMATIC REACTOR TRIP DUE TO A TURBINE TRIP FOR UNKNOWN REASONS The following text is a portion of a facsimile received from the licensee: "Unit 1 reactor trip occurred at 1832 hours on 02/13/2000. Control room annunciators indicate that the cause of the reactor trip was a turbine trip. At this time, the cause of the turbine trip is unknown. All systems and plant responses to the reactor trip were normal." The licensee stated that all control rods fully inserted and that all support systems functioned correctly. None of the primary or secondary system safety relief valves lifted. There were no emergency core cooling system actuations, and none were required. The following three engineered safety feature actuations occurred: turbine trip (for unknown reasons), feedwater isolation, and auxiliary feedwater automatic start. Feedwater isolated and auxiliary feedwater automatically started as designed. The cause of the turbine trip is unknown but is currently believed to be electrical in nature. There were no related maintenance or surveillance activities ongoing at the time of the event. The unit is currently stable in Mode 3 (Hot Standby). Normal charging and letdown, pressurizer heaters and sprays, and the reactor coolant pumps are being utilized at this time for primary system level, pressure, and transport control. Auxiliary feedwater is supplying water to the steam generators, and secondary steam is being dumped to the condenser. The electrical grid is stable. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36685 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2000-02-13 07:34 | 2000-02-13 11:11 | 2000-02-13 | AUTOMATIC REACTOR TRIP ON LOSS OF REACTOR COOLANT SYSTEM (RCS) FLOW THE UNIT EXPERIENCED AN AUTOMATIC REACTOR TRIP-TURBINE TRIP FROM 100% POWER DUE TO THE LOSS OF RCS FLOW CAUSED BY THE TRIP OF THE REACTOR COOLANT PUMPS (INITIALLY "B" RCP FOLLOWED BY THE "A", "C" AND "D"). FLUCTUATING GRID VOLTAGE DUE TO AN ELECTRICAL PROBLEM IN SOUTHEAST MISSOURI CAUSED THE LOSS OF THE RCPs AND THE OPERATING CIRCULATING WATER (CW) PUMPS. DURING THE PERIOD TIME BEFORE THE RCPs WERE RESTARTED, RCS PRESSURE INCREASED CAUSING ONE (1) PRESSURIZER PORV TO LIFT AND RESEAT (SETPOINT 2335 PSIG - PRIMARY SAFETY SETPOINT IS 2485 PSIG). A SLIGHT INCREASE IN THE PRESSURIZER RELIEF TANK PRESSURE WAS OBSERVED. A FEEDWATER ISOLATION SIGNAL OCCURRED WITH ALL SYSTEMS FUNCTIONING AS EXPECTED INCLUDING AUTOSTART OF ALL AUXILIARY FEEDWATER PUMPS (BOTH MOTOR-DRIVEN AND THE TURBINE-DRIVEN PUMPS). CONDENSER VACUUM WAS LOST AS A RESULT OF THE CW PUMP TRIPS. HOWEVER, TWO (2) CW PUMPS WERE RESTARTED AND THE MAIN CONDENSER PLACED BACK IN SERVICE AS THE HEAT SINK. THE LICENSEE ESTIMATES THAT THE STEAM GENERATOR ATMOSPHERIC DUMPS WERE USED FOR NO MORE THAN 20 MINUTES DURING THE PERIOD OF TIME WHEN THE MAIN CONDENSER WAS NOT AVAILABLE. THERE IS NO INDICATION OF ANY PRIMARY-SECONDARY LEAKAGE PRIOR TO THIS EVENT. THE PLANT IS CURRENTLY STABLE WITH OPERATORS RESTORING MAIN FEEDWATER. BOTH EMERGENCY DIESELS ARE IN STANDBY AND AVAILABLE, IF NEEDED. THE UNIT WILL REMAIN IN MODE 3 PENDING THE OUTCOME OF THE INVESTIGATION INTO THE GRID ELECTRICAL TRANSIENT. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36684 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-02-11 17:07 | 2000-02-11 20:13 | 2000-02-11 | - Nebraska Game and Parks Department notified of a dead American Bald Eagle found onsite - At 1707 CST on 02/11/00, a licensee employee found an American Bald Eagle under a 345 kV line on licensee property. The licensee notified the Nebraska Game and Parks Department. A Nebraska Game Warden reported to the site and took possession of the eagle. The warden stated that the eagle had been dead for some time. The warden plans to notify the Fish and Wildlife Service of this incident and to send the bird to them. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36683 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-10 23:30 | 2000-02-11 16:27 | 2000-02-11 | NRC Bulletin 91-01, 24 Hour Report - Loss of 1 of 2 Controlled Parameters (Geometry) - At 2330 on 02/10/00, the Plant Shift Superintendent (PSS) was notified that a Nuclear Criticality Safety Approval (NCSA) requirement was not being maintained in the X-705 decontamination facility. While performing an NCS Self Assessment, facility personnel noticed an operation where requirements for the control of "Inadvertent Containers" was not being met. The Inadvertent container was a rectangular support structure for a ventilator that was approximately 5.5 inches deep and did not have any holes or slots to provide drainage. The critical height dimension is 1.5 inches from the bottom of the container. Requirement #5 of NCSA-0705-076.A00 states, in part that modifications to inadvertent containers, where practical, shall be accomplished by drilling holes or making slots in the container to provide drainage. This structure, not having drainage holes, was a loss of one control (geometry). The other control (concentration) was maintained. At the direction of the PSS, the requirements for an NCS anomalous condition were established per plant procedures. At approximately 0130 on 02/11/00, double contingency controls were reestablished. SAFETY SIGNIFICANCE OF THE EVENT: The safety significance of this event is low. The inadvertent container is an iron support structure for a ventilator that is approximately 5.5 inches deep by 24 inches wide and just over 60 inches long. This structure is in the high bay of the X-705 building bolted to the floor under the overhead storage system. However, there were no indications that any solution had collected in the container or that any leakage had occurred from the overhead storage in this area. Also, data on the concentration of uranium in the overhead storage indicates that it is currently less than 500 ppm. POTENTIAL CRITICALITY PATHWAYS INVOLVED [BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR]: The potential pathway for a criticality is a failure of the overhead storage system. This would allow uranium bearing solution to collect in the container. Since the container has a depth greater than the safe slab depth of 1.5 inches for 100% enriched material, a criticality could occur if the collected solution's depth exceeds 1.5 inches and the uranium concentration of the solution exceeds 11,600 ppm. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY. CONCENTRATION, ETC.): The parameters being controlled are geometry (container geometry and overhead storage piping) and concentration of solution in the overhead storage. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND PER CENT WORST CASE OF CRITICAL MASS): There was no uranium material involved with this event. If the overhead storage were to leak, the enrichment is considered to be 100% and the form would be U02F2 solution (worst case). NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The geometry control of container was lost. The NCSA requires that holes or slots be added to the container to limit the height of the solution that could collect to less than 1.5 inches. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEM AND WHEN EACH WAS IMPLEMENTED: Compliance was regained at 0130 on 02/11/00 when plastic has placed over the container to prevent the introduction of solution. There was no loss of hazardous or radioactive material nor radioactive or radiological contamination exposure as a result of this event. Portsmouth personnel notified the NRC Resident Inspector and the Site DOE Representative. PTS-2000-009 PR-PTS-00-00829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36682 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-02-11 13:46 | 2000-02-11 14:32 | 2000-02-11 | - MANUAL REACTOR TRIP FROM 96% POWER AFTER 2 CONTROL RODS DROPPED INTO THE CORE - During the performance of a tech spec surveillance test of control rod motion with Unit 2 at 100% power, one control rod dropped into the core for unknown reasons. Control room operators reduced power. With Unit 2 at 96% power, a second control rod dropped into the core for unknown reasons. Control room operators manually tripped Unit 2 from 96% power. All control rods inserted completely into the core. The auxiliary feedwater system actuated, as expected. Control room operators manually secured the auxiliary feedwater system. Steam generator water levels are being maintained in their normal range by the main feedwater system. Steam is being dumped to the main condenser. No safety or relief valves lifted. Unit 2 is stable in Mode 3 (Hot Standby). The licensee is investigating the cause of the control rods dropping into the core. The licensee notified state and local officials and the NRC Resident Inspector and plans to issue a press release. | 0 | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36681 | 0 | JASPER COUNTY HOSPITAL |  |  |  |  | 2000-02-11 08:45 | 2000-02-11 10:45 | 2000-02-11 | JASPER COUNTY HOSPITAL RECEIVED A SURFACE CONTAMINATED BOX WHICH CONTAINED NUCLEAR MEDICINE. A METAL AMMO BOX USED TO TRANSPORT NUCLEAR MEDICINE CONTAINED IN INDIVIDUAL PIGS WAS FOUND TO HAVE SURFACE TECHNICIUM CONTAMINATION ON THE LOCKING CLASP MEASURING 604 DPM/CM2 (LIMIT IS EQUAL TO OR LESS THAN 220 DPM/CM2). THERE WAS NO DAMAGE TO THE PIG CONTAINERS INSIDE THE AMMO BOX AND NO CONTAMINATION WAS MEASURED INSIDE THE BOX. THE SOURCE OF THE CONTAMINATION IS UNKNOWN, BUT IT COULD HAVE OCCURRED AT THE PHARMACEUTICAL COMPANY, THE TRANSPORTER OR IN THE HOSPITAL LABORATORY. HOSPITAL PERSONNEL HAVE ISOLATED THE AMMO BOX AND WILL ALLOW THE TECHNICIUM CONTAMINATION TO DECAY OFF. (CALL THE NRC OPERATIONS OFFICER FOR A LICENSEE CONTACT TELEPHONE NUMBER.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | [10 empty] | NON EMERGENCY | 3 | IN | HOS | [5 empty] | 0
36680 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2000-02-11 02:58 | 2000-02-11 07:13 | 2000-02-11 | HPCI DECLARED INOPERABLE, PLACING THE PLANT IN A LCO ACTION STATEMENT. On 2/11/2000 at 0258 hours, HPCI low pressure operability testing was in progress following a scheduled refueling outage. At that time, the HPCI turbine failed to roll when the motor speed changer was taken to its high speed stop. There was no change in steam flow as indicated by the main turbine bypass valve position. The operator in attendance visually verified HPCI was still on the turning gear. The surveillance was terminated and the system restored to standby lineup. At 0341 hours, reactor pressure was reduced below 150 psig to place the reactor in a condition where HPCI was not required to be operable, and they exited the LCO at that time. The cause of this failure is under investigation. The NRC Resident Inspector was notified. | 0 | 4 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36679 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-02-10 18:50 | 2000-02-11 00:59 | 2000-02-11 | THE LICENSEE SUBMITTED A 24 HOUR OPERATING LICENSE DEVIATION REPORT. While performing the Penetration Seal Firestop Configuration verification project, engineering determined that 37 firestop penetrations are not configured in accordance with existing approved details. Therefore, these 37 penetrations are not operable, putting the plant in a LCO action statement. Remedial action has been taken per Selected License Commitment 16.9-5 Fire Barrier Penetrations, this action establishes hourly fire watches on each affected penetration. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT | TECH SPEC LCO A/S |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0
36678 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2000-02-10 14:14 | 2000-02-10 16:11 | 2000-02-10 | DISCOVERY OF A 120-GALLON CONTAINMENT SPRAY ADDITIVE TANK LEVEL DEVIATION During review of calculations and calibration methods for the containment spray additive tank level indicator, it was determined that actual spray additive tank level was approximately 120 gallons below the technical specification required volume. Technical Specification Limiting Condition for Operation (LCO) 3.6.7 had been entered earlier in the day due to planned maintenance, and efforts to restore spray additive tank level minimum volume are underway. The impact of the 120-gallon level deviation is being further evaluated at this time to determine the impact on the plant design basis. The licensee expects to be able to resolve this issue prior to expiration of the 72-hour LCO. The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36677 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-02-09 15:46 | 2000-02-09 18:38 | 2000-02-09 | AUXILIARY FEEDWATER SYSTEM ACTUATION DUE TO UNEXPECTED AMSAC ACTUATION A main turbine trip and auxiliary feedwater system actuation occurred due to an unexpected ATWS mitigation system actuation circuitry (AMSAC) actuation. Because the reactor was operating below 50% power, the turbine trip did not cause an automatic reactor trip. The licensee is currently investigating the cause of the AMSAC actuation. The NRC resident inspector has been informed of this notification by the licensee. | 0 | 2 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Startup | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36676 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2000-02-08 12:09 | 2000-02-09 16:50 | 2000-03-07 | INFORMATION CALL REGARDING RIVER WATER PUMP PROBLEMS "This report is being made to provide preliminary notification of an event that is currently under investigation at Beaver Valley Power Station Unit No. 1 (BVPS Unit 1). "River Water Pump #WR-P-1B at BVPS Unit 1 tripped on overcurrent shortly after it was attempted to be started at 1209 on 02/08/00. The Action Statement for Technical Specification 3/4.7.4.1 was entered for less than two River Water subsystems being operable. River Water Pump #WR-P-1C (swing pump) was then aligned to the 'B' train header and it also tripped on overcurrent shortly after it was started at 1716 on 02/08/00. "Preliminary information identified that the #1B and #1C River Water Pumps would not operate due to the loss of gap between the pumps rotating assembly and the pump bowl. Investigation into the cause of the loss of the pumps' gap is ongoing. BVPS Unit 1 River Water Pump #1A on the 'A' train continues to operate satisfactorily and is operable. The 'A' train is being treated as protected equipment (i.e., no elective work is being done on or near 'A' train components). The BVPS Unit 1 operating crews have reviewed the procedures associated with operating the BVPS Unit 1 Auxiliary River Water System in the Alternate Intake Structure and the use of the cross tie connection with the diesel driven fire pump." The licensee stated that BVPS Unit 1 entered a 72 hour Technical Specification Limiting Condition for Operation at 1209 on 02/08/00. The NRC resident inspector has been informed of this notification by the licensee. * * * UPDATE AT 1827 ON 02/10/00 BY DAN MURRAY TO JOLLIFFE * * * The licensee has identified that the #1B and #1C River Water Pumps would not operate due to the loss of gap between the pump's rotating assembly and the pump bowl. This event is believed to have been initiated by a temporary operating procedure that started on 02/05/00 for maintenance on the non-safety related filtered water system. This procedure altered the filtered water system configuration which was the normal supply to the River Water Pumps' seal water system. One effect of this change was an increase in the seal water temperature at times as much as 30 degrees above its previous temperature which had been near the current river water temperature. This temperature increase adversely affects a pump in the standby configuration whereby thermal expansion of the pump's rotating assembly causes a loss of clearance. River Water Pump #WR-P-1A has remained operating satisfactorily throughout this event. The identified increased seal water temperature condition would not adversely affect an operating pump. Administrative controls have been implemented to require only the use of seal water supply sources with temperatures at or near the current river water temperature for the River Water Pumps. This condition is being reported to the NRC pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition that is outside the design basis of the plant because of the potential for one train of the two-train safety related River Water System (required to be operable per Technical Specification 3/4.7.4.1) to have been incapable of performing its design safety function for an extended period of time during operation. The licensee plans to revise the test procedure, perform the tech spec surveillance test using the safety related seal water supply source, and exit the tech spec action statement. The licensee notified the NRC Resident Inspector of this update. The NRC Operations Officer notified the R1DO Harold Gray of this update. * * * UPDATE AT 1816 ON 03/07/00 BY JOHN THOMAS TO JOLLIFFE * * * The following additional information is provided from a subsequent licensee evaluation of the safety related seal water design for the River Water System pumps at BVPS and the above event update: River Water Pump #WR-P-1C at BVPS Unit 1 was placed into service on 03/03/00 with bearing and motor cooling water supplied by its own discharge via the safety related "Y" strainer #RW-YS-42. Within 10-15 seconds of pump startup, the seal water pressure dropped to approximately 5 psig from its normal operating pressure of approximately 30 psig. The control room operator then blew down the strainer and normal seal water operation ensued. The normal non-safety related sources of seal water for the River Water System pumps have only recently been removed from service as a result of the above event update. A review of the adequacy of the current BVPS Unit 1 seal water design for the River Water System was initiated as part of the above event update. The partial plugging of the "Y" strainer on 03/03/00 identifies that starting a River Water Pump which has been idle for a period of time may initially ingest a slug of silt from the Intake Structure Bay large enough to restrict the flow of seal water through this strainer. Following an evaluation, the licensee has determined that a potential inadequacy may exist in the BVPS Unit 1 seal water design for the River Water System pumps that has been credited since initial operation of BVPS Unit 1. Given that the strainer anomaly was quickly corrected, this seal water design concern involves the operability of a non-operating pump during startup. Seal water strainer plugging during pump operation is more gradual and allows time for control room operator action. River Water System Pump #WR-P-1C remains in operation with seal water supplied from its self-supplied strainer. An Auxiliary River Water Pump in the Alternate Intake Structure is also available with its own separate seal water supply. BVPS Unit 1 is currently in a refueling outage with all fuel removed from the reactor vessel. The seal water design condition was previously reported pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition that was outside the design basis of the plant because of the potential for one train of the two-train safety related River Water System (required to be operable per Technical Specification 3/4.7.4.1) to have been incapable of performing its design safety function for an extended period of time during operation. This additional information provides further basis that the seal water design for the River Water System pumps was not sufficient to meet the design basis of the plant. The licensee is continuing to investigate this event and plans to resolve this issue prior to restarting Unit 1. The licensee plans to notify the NRC Resident Inspector of this update. The NRC Operations Officer notified the R1DO Greg Cranston of this update. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY | OUTSIDE DESIGN BASIS |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  |  | 50.72(b)(1)(ii)(B) |  |  | 0
36675 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2000-02-09 12:12 | 2000-02-09 16:36 | 2000-02-09 | EMERGENCY DIESEL GENERATOR TRIPPED FOLLOWING TESTING "While performing LOS-DG-M3, Monthly Operability Run of 2B Diesel Generator, Division three, the Diesel Generator tripped on reverse power before the output breaker was opened while preparing to take the Diesel Generator off line following this surveillance. Concurrently, a local alarm was received indicating a DC power failure, The reverse power trip is a function that is bypassed under accident conditions. Upon investigation, two fuses supplying engine control power were discovered blown. It is not known whether the fuses would have blown with the reverse power bypassed. The fuses which were installed were verified to be the correct type. The fuses were replaced with like for like and the power failure alarm cleared and the installed fuses did not blow. A plan is being developed to investigate the cause of the fuses blowing. The Diesel Generator is not available and is inoperable per LaSalle Technical Specifications, pending troubleshooting and potential corrective actions. The cause of the blown fuses is unknown at this time." The NRC resident inspector has been informed of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36674 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-02-09 12:45 | 2000-02-09 13:49 | 2000-02-09 | OFFSITE NOTIFICATION TO THE FLORIDA DEP INVOLVING THE REMOVAL OF A LOGGERHEAD SEA TURTLE IN THE PLANT INTAKE CANAL BARRIER NET. NOTIFICATION MADE TO FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION (DEP) REGARDING REMOVAL OF LOGGERHEAD TURTLE FROM PLANT INTAKE CANAL BARRIER NET. THE TURTLE WILL BE SENT OFFSITE FOR REHABILITATION. THERE WERE NO INJURIES TO THE TURTLE. THE LICENSEE INFORMED THE FLORIDA DEP AND THE NRC RESIDENT INSPECTOR. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36673 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-02-09 11:33 | 2000-02-09 12:35 | 2000-02-09 | THE SERVER TO THE EMERGENCY OFFSITE FACILITY FAILED CAUSING THE SAFETY PARAMETER DISPLAY SYSTEM (SPDS) AND EMERGENCY RESPONSE DATA SYSTEM (ERDS) TO BECOME INOPERABLE At 1645 CT on February 8, 2000 the server which transfers Plant Computer data to the two SDSs in the EOF and the ERDS modems failed. This caused the Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) to become unavailable in the EOF as specified in the FSAR section III.A.1.2. The server was replaced by Telecommunications and SPDS and ERDS restored to the EOF at 0834 CT on February 9, 2000. The total time that SPDS and ERDS were unavailable to the EOF is 15 hours and 49 minutes. The failure of the server occurred at the same time as a report of a fire at the Nuclear Operations Support Facility (the EOF is located inside) building. The server was replaced by Telecommunication. The SPDS and ERDS are available at the EOF. The NRC Resident Inspector was notified of this event by the Licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36672 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2000-02-09 09:15 | 2000-02-09 11:16 | 2000-02-09 | THE LICENSEE NOTIFIED THE NEW YORK DEPARTMENT OF ENVIRONMENTAL CONSERVATION THEY EXCEEDED THEIR DELTA T DISCHARGE LIMIT. On 2/9/00 @ 0915, the following information was reported as a State Pollutant Discharge Elimination System(SPDES) exception to the New York State DEC per the 24 hour notification requirement. On 2/8/00 from ~0630 - 0715 hours, the delta t for the main condenser at the site was above the limit of 28°F, with a maximum of 30.4°F, and estimated that the maximum discharge temperature would have been ~ 63°F. For the period ~ 0800 - 1100 hours, delta t was again above the 28°F limit, attaining a maximum delta t of 62°F, with an estimated discharge temperature of ~ 95°F. Observations indicate that no significant fish kill occurred. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36671 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2000-02-09 04:21 | 2000-02-09 06:45 | 2000-02-09 | INVALID ESF ACTUATION CAUSED BY BACKFILLING OF REACTOR LEVEL INSTRUMENTATION On 02/09/2000 @ 0421 hours, Unit Two received a full reactor SCRAM and a full Group II and Group lll isolation, including a Shutdown Cooling isolation. This event occurred as a result of scheduled backfilling of reactor level instrumentation, and is being reported as an invalid ESF actuation. At the time of the event, all control rods were fully inserted, so no rod motion occurred. All systems responded as designed. Shutdown Cooling was restored at 0432 hours with minimal temperature increase(5°F). The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36670 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-02-08 03:33 | 2000-02-08 07:14 | 2000-02-08 | ESF ACTUATION - OUTBOARD RECIRC SAMPLE VALVE CLOSED During performance of Main Steam Isolation Valve Functional Test 0255-07-IA-2, the outboard recirc sample valve CV-2791 closed due to activation of a Group I isolation signal. The procedure step de-energized the DC power to verify that the outboard main steam isolation valves would remain open with AC power. However, the procedure did not recognize that the other Group I outboard valves would close when DC power was interrupted. The licensee will notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36669 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-02-07 14:30 | 2000-02-07 18:56 | 2000-02-07 | POTENTIAL ENTRY INTO TECHNICAL SPECIFICATION 3.0.5 While the 'A' emergency diesel generator (EDG) was out of service for maintenance, the licensee determined that the 'B' service water booster pump had previously been removed from service due to its breaker repeatedly tripping on overcurrent. The 'B' service water booster pump may be attendant equipment for the 'B' service water train. The licensee is currently performing an attendant equipment evaluation of the 'B' service water booster pump. This condition may have required that the unit enter Technical Specification 3.0.5. The NRC resident inspector has been informed of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iii)(A) |  |  |  | 0
36668 | 0 | ST. ANTHONY MEDICAL CENTER |  |  |  |  | 2000-02-07 09:00 | 2000-02-07 17:14 | 2000-02-07 | MEDICAL MISADMINISTRATION A patient, who was prescribed a dose of 100 µCi I-131 for a thyroid scan, was administered a dose of 500 µCi I-131. The patient was released before the error was discovered. The patient has since been contacted and is returning to the hospital to be administered KI (potassium iodide) to limit the uptake of radioiodine in the thyroid. The licensee radiation safety officer did not provide an estimate of the thyroid dose, but stated that whole body dose would be approximately 31 rads without administration of KI. The patient's attending physician will be informed of this misadministration. The licensee has already contacted NRC Region III (T. Go). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.33 |  |  |  | 0
36667 | -1 | DRESDEN | 1 | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2000-02-07 02:40 | 2000-02-07 04:28 | 2000-02-11 | Minimum security personnel staffing requirements not met. Immediate compensatory actions taken upon discovery. The licensee will notify the NRC resident inspector. Additional details of this event may be obtained by contacting the NRC operations officer. * * * UPDATE AT 2057 ON 02/11/00 BY CHRIS KENT TO JOLLIFFE * * * The licensee desires to retract this event since the commitments in the approved Plant Physical Security Plan had been complied with during this event. The licensee plans to notify the NRC Resident Inspector. The NRC Operations Officer notified the R3DO Mike Parker. Additional details of this event retraction may be obtained by contacting the NRC Operations Officer. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 0
36666 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-02-07 00:55 | 2000-02-07 03:11 | 2000-02-07 | ESF ACTUATION - RECIRC SAMPLE ISOLATION VALVES During the performance of standby liquid control refueling tests, a signal is sent to the reactor water cleanup isolation valves and the recirc sample valves. The procedure addresses the RWCU valves, but not the recirc sample valves. Since the outboard sample valve was secured (tagged) open, it unexpectedly closed upon initiation of the standby liquid control system. The valves were returned to their pre-test positions. The licensee will notify the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36665 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-02-06 17:55 | 2000-02-06 18:37 | 2000-02-11 | PUBLIC PROMPT NOTIFICATION SYSTEM INOPERABLE FOR 2 MINUTES Due to technical difficulties in Jacksonville, Florida, the Public Prompt Notification System (NOAA weather radio) was lost at 1755 ET and was restored to service at 1757 ET. Primary and backup system were inoperable during this period of time. The NRC Resident will be notified of this event notification by the licensee. * * * UPDATE AT 1420 ON 02/11/00 BY TIM BEINKE TO JOLLIFFE * * * The licensee desires to retract this event in accordance with the guidance contained in NRC NUREG-1022 since the Public Prompt Notification System was inoperable for less than 15 minutes. The licensee plans to notify the NRC Resident Inspector. The NRC Operations Officer notified the R2DO Mark Lesser. | 93 | 98 | 0 | 93 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36664 | -1 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2000-02-05 13:06 | 2000-02-05 15:06 | 2000-02-06 | TECHNICAL SPECIFICATION 3.0.3 ENTERED AT 1306 CST DUE TO BOTH TRAINS OF LOW PRESSURE INJECTION/RESIDUAL HEAT REMOVAL (LPI/RHR) DECLARED INOPERABLE. "At 1306 on 02/05/00, both Low Pressure Injection/Decay Heat Removal Pumps (P-34A and B) were declared inoperable and Technical Specification 3.0.3 was entered. The pumps were declared inoperable after the inboard pump bearing temperatures exceeded their alarm setpoint after being placed in service for decay heat removal for normal cooldown. "Unit 1 was taken offline at 0010 on 02/05/00 for scheduled maintenance. The unit was in the process of cooling down at the time Tech Spec 3.0.3 was entered. Decay heat removal is being maintained with the use of the operable "B" Reactor Coolant System Loop." Low Pressure Injection pump "A" was placed in service at 1206 CST and a high temperature alarm for the inboard pump bearing was received. Later Low Pressure Injection pump "B" was placed in service and a high temperature alarm for the pump inboard bearing was also received at which time Tech Spec 3.0.3 was entered. The outboard bearing temperatures for both Low Pressure Injection pumps were below their high temperature alarm setpoint. The Low Pressure Injection pumps inboard and outboard bearing are cooled by the Service Water system. Reactor Coolant System pressure is currently 262 psig and plant temperature is 263 degrees F. The licensee said that as far as he knew the Service Water system was properly aligned for cooling both the inboard and outboard bearings of the Low Pressure Injection pumps. Reactor Coolant System Loop "A" is also fully operable if needed. All other Emergency Core Cooling Systems are operable. The licensee is investigating the cause of the high inboard bearing temperatures. The NRC Resident Inspector will notified of this event by the licensee. * * * UPDATE AT 1730 HOURS ON 02/05/00 BY MOSBY TAKEN BY MACKINNON * * * LICENSEE UPDATED EVENT AS A 4 HOUR CALL UNDER 10 CFR 50.72 (b)(2)(I) - DEGRADED WHILE SHUTDOWN. "When P-34A was initially placed in service, the inboard bearing temperature reached the alarm setpoint of 160 degrees F at which time the pump was secured. Currently, P-34A is aligned to recirculate the Borated Water Storage Tank (BWST) and is in operation with the temperature of the pump inboard bearing steady at 84.5 degrees F. Engineering, Operation and Predictive Maintenance are currently involved with the continued testing of the pump. The testing and subsequent operability assessment will be concluded prior to placing the pump in service for decay heat removal." R4DO (C. Johnson) notified. The NRC Resident Inspector was notified of this event update by the licensee. * * * UPDATE AT 1040 ON 02/06/00 BY SCHEIDE TAKEN BY WEAVER * * * The licensee has retracted this event notification based on the following discussion. Technical Specifications require LPI to be operable when three conditions are exist. 1. Fuel in the reactor vessel. 2. Reactor coolant temperature above 200 degrees F and 3. Primary system pressure > 300 psig. A subsequent review of the event verified that RCS pressure was at 240 psig at the time of the event. Therefore, LPI was not required to be operable and 3.0.3 was not applicable. Conditions for decay heat removal were satisfied since both reactor coolant loops and associated OTSGs remained operable. The licensee will notify the NRC resident inspector. The operations center notified the RDO (Johnson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEG/UNANALYZED COND |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(1)(i)(A) | 50.72(b)(2)(i) |  |  | 0
36663 | -1 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-02-04 20:59 | 2000-02-05 13:54 | 2000-02-17 | 2 TRAINS OF ESSENTIAL CHILLED WATER INOPERABLE On 02/04/00 at 2059 CST, Essential Chiller 12C was declared inoperable due to tripping after being started at 2056 CST on 02/04/00. This resulted in an entry into Technical Specification 3.7.14. Investigation revealed that Essential Chiller 12C tripped on high condenser pressure which was caused by not having cooling water flow properly aligned. Found Essential Cooling Water valve EVV-3025 to be closed, when it's required position is throttled to maintain Essential Cooling Water flow. The valve alignment was restored to normal and Essential Chiller 12C was declared operable at 2358 CST on 02/04/00. The investigation revealed that EVV-3025 was closed at approximately 1121 CST on 02/02/00 as indicated on integrated computer system trends. At that time Essential Chilled Water Train "B" was inoperable for planned maintenance and remained inoperable until 1527 CST on 02/02/00. This resulted in 2 trains of Essential Chilled Water being inoperable for 4 hours and 6 minutes which placed the plant in Technical Specification 3.0.3 (did not require plant shutdown). A Licensee Event Report will be submitted within 30 days. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1708 ON 2/17/00, BY MORRIS RECEIVED BY WEAVER * * * Upon further evaluation, it has been determined that Train 'B' of Essential Chilled Water was operable prior to the point in time when Train 'C' of Essential Chilled Water was rendered inoperable, and thus the event is not reportable and therefore should be retracted. Following maintenance, at 0814 CST hours on February 2, 2000, the 12B Essential Chiller was placed in service, and at 1100 CST hours post-maintenance testing was completed. Also by this time, the 'B' Train of Essential Cooling Water and the #12 ESF Diesel Generator had already been declared operable. Additionally, although post-maintenance testing was not signed-off as complete until 1237 CST hours for the 'B' Train Essential Chilled Water air handling unit, the unit was in service and the post-maintenance testing (completed at approximately 1014 CST hours) verified that the air handling unit had been capable of performing its function since the completion of its associated maintenance work. In summary, although the 12B Essential Chiller was not administratively considered operable until 1527 CST hours on February 2, 2000, following final paperwork close-out, it was fully capable of performing its intended design function at 1100 CST hours. Thus, when the 12C Essential Chiller was rendered inoperable at 1121 CST hours, the 'B' train of Essential Chilled Water (including necessary support equipment) was fully capable of performing its design function (i.e.. operable). Since the 'B' train of Essential Chilled Water was therefore operable when the 'C' train was made inoperable, only one train of Essential Chilled Water was inoperable at a time, and Technical Specification 3.0.3 was not entered. The licensee informed the NRC resident inspector of this event retraction. The Operations Center notified the R4DO(Tapia). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LICENSEE 24 HR REPORT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW | [5 empty] | 0
36662 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-02-04 20:00 | 2000-02-05 08:42 | 2000-03-03 | CRITICALITY ACCIDENT ALARM SYSTEM HORN FAILED SURVEILLANCE At 1600 on 02-04-2000 the PSS was informed of the failure of a criticality accident alarm system (CAAS) air horn to sound during the performance of surveillance testing. The cause of the failure was determined to be debris in the air line fouling the flow path for the horn. Subsequently, after this horn was repaired and the air horn line blown out, another air horn on the same branch line became clogged and would not sound sufficiently. This horn was also repaired and its line blown out. The system was retested satisfactorily and declared operable at 2245 on 02-04-00. It is possible that the system would not have performed its intended safety function if it had been required to before it was declared inoperable. This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. The NRC Senior Resident Inspector has been notified of this event. * * * UPDATE ON 3/3/00 @ 1732 BY WALKER TO GOULD * * * RETRACTION THIS EVENT HAS BEEN RETRACTED. Subsequent testing of the C-337A CAAS horn system with the subject horn valved out, has shown that the CAAS meets the requirements for audibility in this area without this horn. Engineering Evaluation EV-C-812-00-003 Rev. 0 was completed to document the conclusions of this testing. The NRC Resident inspector was informed. The Reg 3 RDO(Jordan) and NMSS EO(Sherr) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
36661 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-02-04 18:00 | 2000-02-04 19:36 | 2000-02-04 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) DECLARED INOPERABLE AT 1042 CST SPDS WAS DECLARED INOPERABLE BECAUSE OF A HARDWARE PROBLEM WITH THEIR PLANT PROCESS COMPUTER WHICH FEEDS DATA INTO THE SPDS. THE LICENSEE HAS INCREASED MONITORING PLANT PARAMETERS. CARDS ARE BEING REPLACED IN THE PROCESS PLANT COMPUTER AT THIS TIME. THE NRC RESIDENT INSPECTOR WAS INFORMED OF THIS EVENT BY THE LICENSEE. * * * UPDATE AT 2143ET ON 02/04/00 BY HALVERSON TAKEN BY MACKINNON * * * SPDS RETURNED TO SERVICE AT 1847CST. R3DO (VEGEL) NOTIFIED. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED BY THE LICENSEE. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36660 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-02-04 16:39 | 2000-02-04 17:14 | 2000-03-03 | VALIDITY OF ASSUMPTIONS FOR THE 30 MINUTE NITROGEN BACKUP SUPPLY IN QUESTION During the review of Consolidated Edison calculation FIX-0030-02, Nitrogen Backup Supply for control of Auxiliary Feedwater Flow Control Valves, Turbine Driven Auxiliary Feedwater Pump, and Atmospheric Steam Dump Controls, questions arose as to the validity of the assumption statements that resulted in the design basis for 30 minutes of nitrogen could not be sustained. The assumptions are in the process of being validated. A third nitrogen bottle has been placed in backup alignment to maintain the 30 minute requirement. 3 of the 6 Nitrogen Backup Bottles are now valved in instead of 2. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 0936 ON 03/03/00 BY PHIL SANTINI TO JOLLIFFE * * * Additional licensee engineering review has determined that the Nitrogen Backup Supply for control of Auxiliary Feedwater Flow Control Valves, Turbine Driven Auxiliary Feedwater Pump, and Atmospheric Steam Dump Controls does meet the design basis as documented in licensee calculation FIX-0030-02. Thus, the licensee desires to retract this event. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R1DO Jim Trapp. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36659 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-02-04 12:00 | 2000-02-04 12:18 | 2000-02-04 | LOW HEAD SAFETY INJECTION PUMPS SUCTION MAY SWAP FROM FWST CONTAINMENT SUMP BEFORE LOW FWST LEVEL IS REACHED. "On February 4. 2000 during a review of engineering staff comments on a proposed technical specification change, a condition was discovered that may have resulted in operation outside the design basis of the plant. The specific condition is a deficiency in the current ACTION statement for McGuire Technical Specifications when invoked for one inoperable level channel of the refueling water storage tank (FWST). Currently this Technical Specification allows for the option of placing the affected channel in the trip condition, operation is permitted in this condition for an indefinite period of time. "Because Technical Specifications allow operation in this condition for an indefinite period of time, this condition can not be considered a design basis single failure during a design basis accident. A single failure of an FWST level channel coincident with a design basis LOCA, with another channel in trip as allowed by technical specifications would result in premature swapover of the low head safety injection pumps to the containment sump. As a result of this premature swapover both trains of low head safety injection pumps could fail, which could result in a complete loss in recirculation phase post accident cooling. "Currently all 3 channels of FWST level instrumentation of both McGuire Units are operable. Therefore, the plant is not operating with this single failure vulnerability. Administrative controls have been put into place to limit the time which the plant could operate in this condition until such time as Technical Specifications can be revised to limit this single failure vulnerability" The NRC Resident Inspector was notified of this event by the licensee.. | 100 | 65 | 0 | 100 | 65 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36658 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-02-03 15:45 | 2000-02-03 17:18 | 2000-02-03 | ALL ALERT AND NOTIFICATION SYSTEM SIRENS INOPERABLE AFTER INSTALLING A SIREN STATUS FEEDBACK SYSTEM. Loss of all 14 offsite Alert and Notification System after installation of a siren status feedback system. A common failure has resulted in the inability to activate any sirens. The vendor and plant staff are actively troubleshooting. The licensee will notify state and local officials of this event. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 02/03/00 AT 1923 HOURS BY HARRSCH TAKEN BY MACKINNON * * * All Alert and Notification System sirens were returned to service at 1745 CT. A software problem caused the loss of the Alert and Notification system. State and Local officials were notified by the licensee of this update. R3DO (Tony Vegel) notified. The NRC Resident Inspector was notified of this update by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36657 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-02-03 11:14 | 2000-02-03 16:08 | 2000-03-01 | BOTH TRAINS OF POST ACCIDENT H2 ANALYZERS DECLARED ADMINISTRATIVELY INOPERABLE. During an ongoing review of calculations for "Normal and Accident Gamma and Beta Doses for Mechanical Equipment Qualifications" it was discovered that an inaccurate assumption was made concerning the operation of the Containment and Drywell post accident hydrogen monitoring system. This inaccurate assumption could lead to the sample isolation valves receiving more radiation exposure than assumed in the calculations curing a design bases accident. This extra radiation exposure could cause deterioration of the valve seats and prevent them from sealing properly. With the valves leaking the indicated hydrogen concentrations could be non-conservatively low leading to improper actions during an accident. This condition affects both safety trains of the post accident hydrogen analyzers. The actual affect is still indeterminate however both trains have been conservatively declared administratively inoperable. The system is still in a standby lineup and is expected to continue to perform its function during the early stages of an accident. Engineering is continuing to evaluate the actual affect of the increased radiation exposure on the equipment. The NRC Resident Inspector will be informed of this event by the licensee. * * * UPDATE AT 1713 ON 3/1/2000, BY FELTNER RECEIVED BY WEAVER * * * On 2/3/2000, (event notification 36657), River Bend Station reported that the Containment and Drywell hydrogen monitor system had been conservatively declared inoperable. The inoperability was based on the impact of an inadequate assumption in a post accident dose calculation for the system sample valves. This could have lead to more post accident radiation exposure than determined in the original calculation, which may have lead to failure of the sample valves to properly seat. At the time of the original report. the actual affect of the condition on the valves was indeterminate and the system was declared inoperable. Engineering re-evaluated the condition as documented in a revision to calculation PR(c) 547. This calculation found that the original assumption in the calculation did not impact system operability. The calculation states that the potential doses due to plateout in the system would be negligible when compared to the airborne beta doses, and therefore the doses presented in the original calculation conservatively represent dose expected following a design basis accident. Based on this the system it was determined to be operable, and the condition not reportable. The licensee notified the NRC resident inspector. The NRC Operations Center notified the RDO (Cain). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36656 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2000-02-03 10:21 | 2000-02-03 15:12 | 2000-02-03 | INADVERTENT START OF EMERGENCY DIESEL GENERATOR (EDG) DURING SURVEILLANCE TESTING On 02/03/00 at 1021 CST while performing surveillance test QCOS 0203-06 (ADS Logic Test) the Unit-1/2 EDG received an inadvertent autostart signal from Unit 2 Core Spray Logic system. The Unit 1/2 EDG autostart occurred during the installation of relay finger block being placed as part of the surveillance test. The finger block was being placed on the correct relay finger. However, during the installation, and due to the small contact clearances, a momentary relay actuation occurred and caused the EDG start. A Heightened Level of Awareness Briefing was conducted prior to the logic test, and discussed the potential for equipment actuations to occur during performance of the test. In addition, Limitations and Actions step F.7 of QCOS 0203-06 states that inadvertent actuations may occur during the performance of this test, including the EDG autostart, and requires immediate work stoppage and notification of the Unit Supervisor and a Shift Manager review for reportability. The EDG and associated plant systems responded as expected. This report is being made pending further review of the UFSAR and the stated design ESF systems contained in the UFSAR. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36655 | -1 | ALLEGHENY VALLEY HOSPITAL |  |  |  |  | 2000-02-02 15:30 | 2000-02-03 14:55 | 2000-02-03 | INCORRECT PATIENT GIVEN TECHNETIUM-99M FOR HDP BONE SCAN A medical technician went to room 113 on 1A level and read the patient name plate on the wall outside the room before entering the room. The medical technician entered the room and addressed the elderly patient by the name that was labeled outside her room. The patient responded by saying yes that was her name. The medical technician injected the patient with 22 millicuries of technetium-99m HDP bone scanning agent. When the medical technician reviewed the patient label chart she discovered that she had given the technetium-99m HDP bone scanning agent to the incorrect patient. The correct patient had been taken downstairs for the technetium-99m injection. The patient and her physician were notified of the error. No harm will come to the patient because of the error. * * * RETRACTION ON 02/03/00 AT 1635 HOURS BY FRANK OTTINON TAKEN BY MACKINNON * * * This event is being retracted because the patient did not receive 5 rems effective dose equivalent or 50 rems dose equivalent to any individual organ as a result of receiving the accidental dose of 22 millicuries of technetium-99m as specified in 10 CFR 35.2 item (6) (ii). NRC R1DO (Tony Dimitriadis) and NMSS EO (Joe Holonich) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.33 |  |  |  | 0
36654 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-02-02 23:00 | 2000-02-02 23:50 | 2000-02-02 | - LONG TERM ADS BACKUP NITROGEN SUPPLY HEADER MANUAL BLOCK VALVES FOUND CLOSED - At 2105 on 02/02/00, a plant operator found one manual block valve to each Long Term Automatic Depressurization System (ADS) backup nitrogen supply header isolated. This would have prevented Unit 2's ability to establish long term alternate decay heat removal capability in accordance with the plant design basis. Tech Spec 3.5.1.d requires Unit 2 to be placed in hot shutdown condition within 12 hours with these valves closed. At 2125 on 02/02/00, plant operators opened both ADS manual block valves reestablishing long term backup nitrogen supply to the ADS valves and exited Tech Spec 3.5.1.d. Normal ADS nitrogen supply header pressure was present with these valves in the closed position. The licensee is investigating the cause of these valves being in the closed position. At 2300 on 02/02/00, the licensee determined that this event was reportable to the NRC. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36653 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-02-02 11:34 | 2000-02-02 14:51 | 2000-02-02 | LICENSEE DISCOVERED A CONDITION THAT IS OUTSIDE THE PLANT DESIGN BASIS At 1134 PST on 02/02/00, after discussions with General Electric Company representatives, the licensee determined that the condition described below was not known to be previously analyzed and was outside the design basis of the plant and was reportable to the NRC. The plant remains in Condition 1 at 100% power with the condition yielding primary containment and reactor coolant pressure boundary OPERABLE but nonconforming in accordance with NRC Generic Letter 91-18, Revision 1. The WNP-2 UFSAR Section 7.4.1.1.2 and TMI response ll.K.1.22 state that the Reactor Core Isolation Cooling (RCIC) System is designed to automatically start if reactor water level decreases to the low level signal setpoint (level 2), automatically stop at the high water level signal setpoint (level 8), and restart if water level decreases again to low level signal setpoint (level 2). The RCIC System is equipped with a "Keep-Fill" pump designed to maintain the RCIC System full. However, the RCIC Keep-Fill pump is not single failure proof. Therefore, during accident or transient scenarios which include a sufficient decrease in reactor vessel water level, restart of the RCIC System in conjunction with a failure of the Keep-Fill pump, could create a water hammer in the RCIC System piping and potentially jeopardize the integrity of the reactor coolant pressure boundary (RCPB) or primary containment (PC) isolation barriers associated with the RCIC System. An operability assessment has determined that the RCPB and PC are OPERABLE but nonconforming to single failure criteria, crediting existing proceduralized operator actions. The RCIC System is equipped with low pressure alarm annunciation in the main control room. To prevent water hammer, plant procedures require operator action to inhibit RCIC pump starts (except as directed by emergency operating procedures) upon receipt of this low pressure alarm. WNP-2 is continuing to evaluate the significance of this postulated scenario through engineering analysis. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36652 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2000-02-01 22:24 | 2000-02-01 23:26 | 2000-02-01 | INFORMATION CALL INVOLVING A NON-CREDIBLE PLANT THREAT. CONTACT THE NRC OPERATIONS CENTER FOR ADDITIONAL DETAILS. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0
36651 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-02-01 12:25 | 2000-02-01 18:49 | 2000-02-01 | A condition that alone could have caused the loss of initiation capability of an engineered safety feature. At 1038 PST on 01/31/00, the division 2 low condenser vacuum main steam isolation initiation channel B was found to trip at approximately 2.4 inches Hg vacuum during the performance of plant technical specification surveillance test. This was less than the plant technical specification allowable value of greater than or equal to 7.2 inches Hg vacuum. The channel was declared inoperable and entry into plant technical specification limiting condition of operation (LCO) 3.3.6.1.A was made for the channel. Channel B was then adjusted to plant technical specification tolerance per approved plant procedures and returned to service. LCO 3.3.6.1.A was then exited at 1135 PST on 01/31/00. At 1310 PST on 01/31/00, the division 2 low condenser vacuum main steam isolation initiation channel D was found to trip at approximately 2.8 inches Hg vacuum during the performance of a plant technical specification surveillance test. This was less than the plant technical specification allowable value of greater than or equal to 7.2 inches Hg vacuum. The channel was declared inoperable and entry into plant technical specification LCO 3.3.6.1.A was made for the channel. Channel D was then adjusted to plant technical specification tolerance per approved plant procedures and returned to service. LCO 3.3.6.1.A was then exited at 1335 PST on 01/31/00. A problem evaluation request was initiated on 01/31/00 to investigate the cause of the setpoint problem. Preliminary investigation determined that on 11/10/99 the pressure switches had been miscalibrated during the previous surveillance due to a calibration equipment problem. The division 1 low condenser vacuum main steam isolation initiation pressure switch setpoints were verified to be in compliance with plant technical specifications. At 1225 PST on 02/01/00, plant system engineering determined, based on engineering judgement, that a loss of engineered safety feature initiation capability had occurred since the time that the pressure switches were miscalibrated and informed the control room staff. The control room staff performed an independent review and concurred with the assessment. Investigation into the cause of this condition will continue. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
36650 | 0 | IL DEPARTMENT OF NUCLEAR SAFETY |  |  |  |  | 2000-01-28 | 2000-02-01 18:00 | 2000-02-01 | MISSING THICKNESS GAUGE CONTAINING RADIOACTIVE SOURCE The individual responsible for a Generally Licensed device reported on 01/28/00 that he noticed the device containing a radioactive source was missing from the facility. The device was removed by some unauthorized person or persons. He noticed it missing when he attempted to perform a test for leakage. The Illinois company changed ownership within the last two weeks. The facility location and most personnel remain the same. The radioactive source was registered with the Illinois Department of Nuclear Safety on 09/05/96 (GL #9223308). The source is 150 mCi of Am-241 in a NDC Model 103 thickness gauge with serial number 11300. This device was used to measure thickness of plastic film. The device is stainless steel approximately eight inches long and 1-1/4 to 1-1/2 inches in diameter. The SS&D sheet (CA0471D102B) indicates a maximum radiation level of 5 mR/hour at one foot with the shutter open and 185 mR/hour near contact with the shutter open. With the shutter closed, the maximum radiation level is 0.1 mR/hour at one inch and less than 0.75 mR/hour near contact. The individual had searched the entire plant on 01/28/00, including the roof, in an attempt to locate the device. A police report has been filed. On 02/01/00, IL Department of Nuclear Safety staff personnel performed surveys in an attempt to locate the device and its source but did not find them. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0
36649 | 0 | TEXAS BUREAU OF RAD CONTROL |  |  |  |  | 2000-01-18 | 2000-02-01 17:42 | 2000-02-01 | TEXAS INCIDENT #7568 - RADIOGRAPHER RECEIVED A 1999 ANNUAL EXPOSURE OF 5.01 REM On 01/18/00 the licensee received its film badge report from Atomic Energy Industrial Laboratory showing that an employee had exceeded the allowable occupational dose limit of 5 rems for the year ending 12/31/99. In following the Technical Welding Laboratory (TWL) radiation safety program and their operating and emergency procedures, the employee was notified of his exposure. In addition, he was brought into the office and reviewed TWL's ALARA program to ensure that he understands his responsibilities according to Texas State regulations and TWL's operating and emergency procedures. After interviewing the employee and listening to his explanation of possible causes for the amount of radiation he received, it was determined that the employee needs to pay more attention to ALARA concerns in the future. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | PERS OVEREXPOSURE/TEDE >= 5 REM | [8 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  | 20.2202(b)(1) |  |  | 0
36648 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2000-02-01 07:40 | 2000-02-01 09:27 | 2000-02-01 | NOTIFICATION TO THE FLORIDA DEPARTMENT OF THE ENVIRONMENT INVOLVING A GREEN SEA TURTLE FOUND IN THE INTAKE CANAL "AT APPROXIMATELY 0740 EST ON 2/1/00, A JUVENILE GREEN SEA TURTLE WAS RESCUED FROM THE PLANT'S INTAKE CANAL. THE TURTLE WAS ALIVE BUT IN NEED OF REHABILITATION. AS REQUIRED BY THE PLANT'S SEA TURTLE PERMIT, THE FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION WAS NOTIFIED OF THE EVENT." THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36647 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-01-31 17:00 | 2000-01-31 17:12 | 2000-01-31 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE, THEREBY ENTERING THE PLANT INTO A 7-DAY LCO ACTION STATEMENT DURING A HPCI SURVEILLANCE TEST, HPCI WAS DECLARED INOPERABLE DUE TO FLOW AND SPEED ANOMALIES. THIS CONDITION ENTERS THE PLANT INTO A 7-DAY LCO TO RETURN HPCI TO AN OPERABLE CONDITION OR BE IN COLD SHUTDOWN WITHIN 24 HOURS. THESE ANOMALIES HAVE OCCURRED IN THE PAST SEVERAL MONTHS, WHICH IS THE REASON FOR THE INCREASED SURVEILLANCE TESTING. DURING TODAY'S SURVEILLANCE, THE PUMP SPEED JUMPED FOR NO APPARENT REASON FOR <1 MIN BEFORE RETURNING TO NORMAL SPEED. THIS IS THE FIRST TIME THEY HAVE SEEN THIS ANOMALY FOR 2 MONTHS. THEY HAVE NOT DETERMINED THE CAUSE FOR THE INCREASE IN PRESSURE AND SPEED, BUT THEY WILL BE TROUBLESHOOTING THE PUMP. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED BY THE LICENSEE. | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36646 | 0 | PENNSYLVANIA STATE UNIVERSITY |  |  |  |  | 2000-01-31 16:00 | 2000-01-31 16:52 | 2000-01-31 | REPORT OF A STOLEN TRITIUM EXIT SIGN THE PENNSYLVANIA STATE UNIVERSITY REPORTED THAT A TRITIUM EXIT SIGN WAS STOLEN FROM A BUILDING ON THEIR NEW KENSINGTON CAMPUS NEAR PITTSBURGH, PA, SOME TIME BETWEEN 01/28/00 AND 01/31/00. THE SIGN CONTAINS APPROXIMATELY 19 CURIES OF TRITIUM. THEY ARE CONTINUING THE SEARCH AND PLAN TO NOTIFY THE LOCAL AUTHORITIES. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
36645 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2000-01-31 10:05 | 2000-01-31 14:18 | 2000-01-31 | VOLUNTARY REPORT OF A MEDIA RESPONSE RELATED TO CALL-OUT OF LOCAL FIRE DEPARTMENT At 1005 hours (CST) on January 31, 2000, the control room received a report of a small explosion in the Unit 2 pipeway between the main steam isolation valve (MSIV) room and the low-pressure heater bay. Control room personnel, in accordance with station procedures, notified the local (Cordova, IL) fire department of an explosion and possible fire. There were no personnel injuries, no equipment damage, and no fire. As a result of the call to the fire department, local law enforcement agencies and two television stations responded to the site. The two television stations were KWQC (TV-6) (NBC) and WQAD (TV-8) (ABC). For a period of time, the state road in the vicinity of the plant was closed by law enforcement agencies. The cause of the report to the control room was a very loud, sudden noise that resulted when a nylon bag containing small oxygen and acetylene bottles and hoses was opened. The sound was most likely the result of the ignition of a small amount of oxygen and acetylene trapped in the bag. Although no notification was made or planned for local media or law enforcement support, personnel from both of these areas were dispatched to the site. There were no injuries or fire. No equipment was affected. This notification is being made voluntarily. The NRC Resident Inspector was notified, and there will be no media releases. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0
36644 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2000-01-31 11:45 | 2000-01-31 13:22 | 2000-01-31 | NOTIFICATION OF AN OIL SPILL TO THE STATE OF CONNECTICUT DEPARTMENT OF ENVIRONMENTAL PROTECTION, NATIONAL RESPONSE CENTER, AND THE U.S. COAST GUARD. THE LICENSEE HAD A MOTOR OIL SPILL OF ~1/2 CUP TO A STORM DRAIN SYSTEM WHICH CONNECTS TO THE CONNECTICUT RIVER. THE SPILL IS BEING CLEANED UP, AND OFFSITE NOTIFICATIONS WERE MADE. THE LICENSEE HAS NO NRC RESIDENT INSPECTOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36643 | 0 | DEPARTMENT OF THE NAVY |  |  |  |  | 2000-01-20 | 2000-01-31 12:34 | 2000-02-02 | U.S. NAVY REPORTED MISSING DROGUE LIGHTS AT THE MARINE CORP AIR STATION IN CHERRY POINT, N.C. A DROGUE LIGHT (USED DURING NIGHT AIRCRAFT REFUELING) IS A BASKET ASSEMBLY CONTAINING 6 ISOLITES WHICH CONTAIN 1 CURIE OF TRITIUM EACH FOR A TOTAL OF 6 CURIES. THERE WAS A SECOND BASKET ASSEMBLY CONTAINING 5 ISOLITES WHICH ALSO CONTAINED 1 CURIE EACH OF TRITIUM AND A 6th ISOLITE WHICH CONTAINED 25 MILLICURIES OF KRYPTON-85. THEREFORE, THERE IS A TOTAL ACTIVITY OF 11 CURIES OF TRITIUM AND 25 MILLICURIES OF KRYPTON-85 MISSING. THEY HAVE BEEN SEARCHING FOR THESE SOURCES SINCE 01/20/00 WITH NO SUCCESS. ON 01/28/00, IT WAS DETERMINED THAT THIS WAS A REPORTABLE EVENT. THEY BELIEVE, HOWEVER, THAT THESE SOURCES WERE NOT STOLEN OR LOST BUT WERE RETURNED TO THE NAVY SUPPLY SYSTEM AFTER THEY HAD BEEN REMOVED ON 12/14/99. THEY ARE HAVING A NAVY JAG INVESTIGATION ON THIS INCIDENT. CALL THE NRC OPERATIONS OFFICER FOR A LICENSEE CONTACT TELEPHONE NUMBER. * * * UPDATE AT 1033 ON 02/02/00 FROM HIGGINS TAKEN BY STRANSKY * * * The licensee has recovered the sources. The lights had been mistaken for surplus material, and had been installed on another aircraft. The licensee has already contacted NRC Region 2 regarding this update. The NRC Operations Officer notified the R2DO (Kerry Landis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | NC | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
36642 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-01-31 08:15 | 2000-01-31 10:10 | 2000-01-31 | SECURITY EVENT Unescorted access granted improperly to former plant employee. The licensee notified the NRC resident inspector. Contact the NRC Operations Center for additional details. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) |  |  |  | 0
36641 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-01-29 15:40 | 2000-01-29 17:20 | 2000-01-29 | BLOWN FUSE CAUSES VALVES TO REPOSITION. A short circuit in a relay coil caused a blown fuse and resulted in the following actuations: the main condenser mechanical vacuum pump tripped, turbine steam packing exhausters received a trip signal (they were not running at the time), partial primary containment isolation system (PCIS) Group 2 isolation (outboard valves), and a partial PCIS Group 1 isolation (outboard main steam line drain and reactor water sample valves). The licensee reported that all actuations were expected for this condition. The faulty relay has been electrically isolated for repair, and the blown fuse was replaced. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36640 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2000-01-28 22:00 | 2000-01-29 00:45 | 2000-01-31 | ECCS VENT SYSTEM FAILED SURVEILLANCE DUE TO PROBLEMS WITH THE CHARCOAL FILTERS. UPON THE COMPLETION OF MAINTENANCE PERFORMED ON THE 11 AND 12 ECCS PUMP ROOM VENT FANS, IT WAS DETERMINED THAT THE CHARCOAL FILTERS DID NOT SEAT PROPERLY DURING A CHARCOAL TEST (STPM-547-1) RESULTING IN THE TEST CRITERIA NOT BEING MET. SEVERAL LOOSE NUTS WERE DISCOVERED ON THE CHARCOAL TRAY HOLD-DOWN FASTENERS. THE NUTS WERE TIGHTENED, AND THE SURVEILLANCE WAS PERFORMED SATISFACTORILY. THE LICENSEE IS INVESTIGATING WHY THE NUTS WERE LOOSE SINCE THE FILTERS WERE NOT INVOLVED IN MAINTENANCE PERFORMED. THE NRC RESIDENT INSPECTOR WAS NOTIFIED BY THE LICENSEE. *************** UPDATE AT 0335 ON 01/31/00 FROM LEO GREGORY GETZ TO LEIGH TROCINE *************** The licensee called to change its internal event report number and to provide the following updated information. In an effort to check for a common mode problem, the licensee checked the Unit 2 charcoal filters on 01/29/00. They all tested satisfactorily. The licensee notified the NRC resident inspector. The NRC operations officer notified the R1DO (Rogge). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iii)(C) | 50.72(b)(2)(iii)(D) |  |  | 0
36639 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2000-01-28 13:31 | 2000-01-28 16:25 | 2000-01-28 | OFFSITE NOTIFICATION DUE TO WILDLIFE KILL The licensee notified the New York Department of Environmental Conservation and the U.S. Fish and Wildlife Service regarding the death of 101 blue billed ducks. The ducks were discovered after the circulating water system was realigned from reverse flow to normal flow. The NRC resident inspector will be informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36638 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2000-01-28 02:40 | 2000-01-28 05:14 | 2000-02-02 | BOTH EMERGENCY DIESEL GENERATORS INOPERABLE DURING CORE ALTERATIONS. "On 1/28/00 at 0005 hrs, the U-2 Emergency Diesel Generator was found to be inoperable due to the diesel generator room vent fan selector switch being selected to the alternate feed. The 1/2 Emergency Diesel Generator was inoperable due to Division I electrical system refuel outage work. Core alterations were in progress. "Per Tech Spec 3.9.B, one diesel generator must be operable in Mode 5 and when handling irradiated fuel in the secondary containment. "The switch was aligned to the normal position, and vent fan operation was verified within approximately 15 minutes to restore the U-2 diesel generator to an operable status. An internal investigation is commencing. Although both the 1/2 and U-2 EDGs were inoperable, both diesels remained available for operation. "This event is being reported as required by 10CFR50.72(b)(2)(iii)(D), an event which alone could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident." The licensee informed the NRC Resident Inspector. * * * UPDATE ON 02/02/00 AT 1841 FROM HILL TO GOULD * * * RETRACTION The licensee has completed its evaluation and determined that the Unit 2 Emergency Diesel Generator was able to meet its intended safety function considering reasonable operator actions. Therefore, this event is not reportable with respect to 10CFR 50.72(b)(2)(iii)(D) and is hereby retracted. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified R3DO (Tony Vegel). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36637 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-01-27 15:30 | 2000-01-27 19:13 | 2000-01-27 | UNITS OUTSIDE OF DESIGN BASIS DUE TO WORDING OF UFSAR "This notification is for San Onofre Units 2 and 3 and is being made in accordance with 10CFR50.72(b)(1)(ii)(B). "Southern California Edison was performing a review of plant drawings and noticed a potential discrepancy between some circuit designs and the specific wording used in the Updated Final Safety Analysis Report (UFSAR) to describe the design for those circuits. Further investigation of the affected components revealed that certain functions appear to not fully meet the separation criteria of Regulatory Guide 1.75, 'Physical Independence of Electrical Systems.' These circuits include relays for portions of some Engineered Safety Features (e.g., boric acid makeup pumps and input voltage to one of the four loss-of-voltage-signal circuits). The UFSAR for Units 2 and 3 indicates these systems comply with IEEE-279, 1971, 'Criteria for Protection Systems for Nuclear Power Generation Stations' which is referenced by Regulatory Guide 1.75. Consequently, at 1530 PDT, SCE concluded this condition was reportable in accordance with 10CFR50.72(b)(1)(ii)(B) as a condition 'outside the design basis of the plant.' "SCE has confirmed that the affected components remain capable of performing their intended safety functions and, therefore, concludes there is no safety significance to this occurrence. "At the time of this report. Unit 1 remains permanently shutdown, and Units 2 and 3 are operating at about 100% power. SCE will notify the NRC resident inspectors of this condition and provide them with a copy of this report." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36636 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-27 12:50 | 2000-01-27 17:12 | 2000-01-27 | OFFSITE NOTIFICATION DUE TO OIL SHEEN The licensee notified the Texas Natural Resource Conservation Commission and the US DOT National Response Center regarding the appearance of an oil sheen near the circulating water discharge. The licensee believes that the oil is residue from recent paving activities that has been washed out due to heavy rains. The licensee has deployed absorbent materials to control the spill. The NRC resident inspector has been informed of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36635 | 0 | USAF RADIOISOTOPE COMMITTEE |  |  |  |  | 2000-01-27 15:00 | 2000-01-27 16:51 | 2000-01-27 | MISSING CALIBRATION SOURCE On 1/26/00, the Keesler AFB Radiation Safety Officer (RSO) was unable to locate a 1.37 µCi Pu-239 calibration source during a routine inventory of Wolfe Hall. During the subsequent investigation, the Wolfe Hall RSO reported that the source was to have been transferred to Kelly AFB in Texas, but it had inadvertently been shipped to McLellan AFB in California. However, the McLellan AFB transportation office has no record of receiving the source. The Keesler AFB RSO will continue to attempt to locate the source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36634 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-01-27 12:01 | 2000-01-27 15:38 | 2000-01-27 | EXCESSIVE LEAKAGE THROUGH CONTAINMENT ISOLATION VALVE "On 1/27/00 at 1201 hours, as-found 10CFR50 Appendix J Type C leakage testing of the outside containment trip valve 2-DA-TV-200B was determined to be greater than 0.6 La. Leakage was determined to be approximately 182 scfh versus total minimum pathway leakage acceptance criteria of 180 scfh. "On 1/25/00 the inside containment trip valve 2-DA-TV-200A for the same penetration was replaced due to an unsatisfactory 1ST stroke time. Removal and installation of the valve was less than one hour in duration. Following replacement of the valve, Type C leakage was determined to be satisfactory for 2-DA-TV-200A, however, excessive leakage was suspected for the outside trip valve 2-DA-TV-200B. "By testing conducted on 1/27/00, it was confirmed that during the timeframe of 2-DA-TV-200A replacement, a condition which alone could have prevented the fulfillment of the safety function needed to control the release of radioactive material existed. "Currently containment integrity is being maintained by closure and deactivation of 2-DA-TV-200A in accordance with the station Technical Specification. Following replacement of 2-DA-TV-200A on 1/25/00, Type C testing was performed with satisfactory results (less than 1 scfh). Currently total minimum pathway leakage is approximately 3 scfh. This report is being made pursuant 10CFR50.72(b)(2)(iii)." The licensee has informed the NRC resident inspector of this event. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iii)(C) |  |  |  | 0
36633 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2000-01-27 14:57 | 2000-01-27 15:10 | 2000-01-27 | MANUAL REACTOR TRIP DUE TO SECONDARY SYSTEM TRANSIENT Operators manually tripped the unit from 100% power due to decreasing steam generator water levels caused by a decrease in feedwater flow. Feedwater flow decreased due to a transient in a feedwater heater string. All control rods inserted following the trip. Operators also manually initiated the auxiliary feedwater system to restore steam generator water levels (a confirmatory automatic initiation signal was received). The unit is currently stable in Hot Standby. All systems functioned as expected. The NRC resident inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36632 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-01-27 11:22 | 2000-01-27 15:06 | 2000-01-27 | REACTOR WATER CLEANUP ISOLATION WHILE PLACING SYSTEM IN SERVICE "During initial repressurization of the reactor water cleanup system (RWCU) after the maintenance outage, the control room received channel 'A' and 'B' RWCU high flow alarm (<=191% of rated flow) and subsequent Group 3 isolation (closure of RWCU-MOV-M015 and RWCU-MOV-M018 inboard / outboard primary containment isolation valves). This actuation occurred while the operator was throttling open RWCU-M018. The Group 3 was verified per G.O.P. 2.1.22 (Recovery From Group Isolations) and following recovery, system flow was restored." The NRC resident inspector has been informed of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36631 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-01-26 14:45 | 2000-01-27 14:12 | 2000-01-27 | 24 HOUR 91-01 BULLETIN RESPONSE AT APPROXIMATELY 1445 HRS @ 1/26/00, ELEVEN (11) BAGS WITH MISCELLANEOUS CONTENTS WERE DISCOVERED IN THE X-103 HEALTH PHYSICS SOURCE VAULT. THREE (3) OF THE ELEVEN ITEMS CONTAINED GREATER THAN 1% U-235 WITH THE HIGHEST ASSAY BEING 52.1 %. THE TOTAL GRAM CONTENT OF ALL THREE ITEMS INCLUDING ERROR IS 158.5 g U-235 FOR 52% ASSAY (MOST LIMITING). ALL ELEVEN ITEMS WERE PLACED INTO TWO (2) APPROVED CONTAINERS WHICH WERE MOVED TO AN APPROVED STORAGE FACILITY. THERE WAS NO LOSS OF HAZARDOUS/RADIOACTIVE MATERIAL OR RADIOACTIVE/RADIOLOGICAL CONTAMINATION EXPOSURE AS A RESULT OF THIS EVENT. THE NRC RESIDENT INSPECTOR WAS NOTIFIED AND THE DOE REPRESENTATIVE WILL BE NOTIFIED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36630 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-01-26 22:38 | 2000-01-27 12:09 | 2000-01-27 | FAILURE OF PRIMARY CONTAINMENT ISOLATION VALVE TO CLOSE ON A LOW REACTOR PRESSURE SIGNAL. PRIMARY CONTAINMENT ISOLATION VALVE "1E51-F008" DID NOT CLOSE ON A LOW REACTOR PRESSURE SIGNAL DUE TO INSTRUMENT "1E51-N685C" BEING INOPERABLE. THE OTHER VALVE IN THIS LINE, VALVE "1E51-F007", DID CLOSE TO ISOLATE THE PENETRATION. THE "1E51-F008" VALVE WAS CLOSED AS DIRECTED BY THE SHUTDOWN PROCEDURE "34G0-OPS-013-1S". THIS EVENT IS BEING INVESTIGATED TO DETERMINE THE ROOT CAUSE. THE REPORTABILITY OF THE EVENT WAS NOT DETERMINED AT THE TIME OF THE OCCURRENCE. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. [HOO NOTE: SEE RELATED EN 36625.] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36629 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2000-01-27 09:00 | 2000-01-27 11:35 | 2000-01-27 | OFFSITE NOTIFICATION TO FLORIDA FISH AND WILDLIFE CONSERVATION COMMISSION A GREEN SEA TURTLE(AN ENDANGERED SPECIES) WAS FOUND IN THE INTAKE. THE TURTLE WILL BE HELD FOR A DAY TO ENSURE ITS HEALTH AND THEN RELEASED IN ACCORDANCE WITH THE FISH AND WILDLIFE CONSERVATION COMMISSION DIRECTIONS. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36628 | 0 | METROPOLITAN DISTRICT |  |  |  |  | 2000-01-26 | 2000-01-26 18:23 | 2000-01-26 | REQUIRED REPORT - EXPLOSION IN SHREDDER, NO DAMAGE TO SOURCE IN LEVEL DETECTOR The operating procedures require notification of the NRC of any explosion in the trash shredders, even if no damage occurs to the source in the level measuring device. It has been determined that small gas welding bottle that contained acetylene caused an explosion in the shredder at Metropolitan District. The source was not damaged. Local authorities were informed and the fire department made the determination of the probable cause. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | NON CFR REPORT REQMNT | [9 empty] | NON EMERGENCY | 1 | CT | OTH | GEN |  |  |  |  | 0
36627 | 0 | SOLIDSTATE CONTROLS, INC. |  |  |  |  | 2000-01-21 | 2000-01-26 16:11 | 2000-01-26 | 10 CFR 21 - POTENTIAL DEFECT INVOLVING STATIC SWITCH CONTROL ASSEMBLY AND REGULATED RECTIFIER CONTROL ASSEMBLY USED IN AN UNINTERRUPTIBLE POWER SYSTEM This reports a potential for a defect in Static Switch Control assemblies and Regulated Rectifier Control assemblies used in Uninterruptible Power Systems manufactured under the Solidstate Controls, Inc., 10CFR50 Appendix B Program. Each of the plants has been notified of this report and requested to return the affected assemblies for replacement. The following plants have affected components: Indian Point 2, Catawba, Oconee, Arkansas Nuclear One, Waterford 3, Crystal River, Diablo Canyon, Sequoyah, and Surry. The problem is associated with a component part - Unijunction Transistor, part number 03-650007-00, that has been found to sometimes cause random, sporadic transfers of the static switch due to a higher level of sensitivity to noise spikes on the input line or cause the regulated rectifier to output a higher DC voltage. This increase in sensitivity will not cause the system to drop power to the load, if the alternate source is not available the static switch will not transfer, continuing to protect the load. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0
36626 | 0 | MILLSTONE | 1 | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2000-01-26 09:47 | 2000-01-26 11:06 | 2000-01-26 | OFFSITE NOTIFICATION TO STATE/LOCAL AGENCIES INVOLVING ERRONEOUS EMERGENCY "At 0947 on January 26, 2000 a notification to offsite emergency response agencies was made in error. The notification indicated that a General Emergency had been declared at Millstone. No emergency conditions currently exists at the site. The notification occurred during testing of the primary notification system. The cause of the condition is being investigated at this time. Backup means of notification is available in the event that a bonafide emergency condition arises prior to the restoration of the primary notification system. "Retractions of the event notification were issued to appropriate State and local agencies. Millstone emergency management personnel have also been in contact with representatives of these agencies." The licensee informed the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36625 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2000-01-26 06:48 | 2000-01-26 07:42 | 2000-01-30 | UNIT 1 EXPERIENCED AN AUTOMATIC REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL DUE TO A FEEDWATER (FW) CONTROL FAILURE. AT APPROXIMATELY 0648 EST ON 1/26/2000, CONTROL ROOM OPERATORS RESPONDED TO A FEEDWATER CONTROL FAILURE ALARM. WHILE INVESTIGATING, FEEDWATER PUMP SPEED DECREASED CAUSING REACTOR VESSEL WATER LEVEL (RVWL) TO DROP FROM ITS NORMAL OPERATING LEVEL OF 37.5" TO APPROXIMATELY -45". AT 0", AN AUTOMATIC REACTOR SCRAM AND GROUP 2 ENGINEERED SAFEGUARDS FEATURES (ESF) ACTUATION OCCURRED, AS EXPECTED. ALL CONTROL RODS FULLY INSERTED. AT -38", BOTH THE HIGH PRESSURE COOLANT INJECTION (HPCI) AND REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM RECEIVED A START SIGNAL. HPCI INJECTED UNTIL THE HPCI PUMP TRIPPED AT ITS RVWL SETPOINT OF 51.5". THE FW PUMPS TRIPPED AT 58" WITH RVWL SWELL CAUSING LEVEL TO REACH 100". FOLLOWING THE LEVEL TRANSIENT, OPERATORS HAD DIFFICULTY IN ESTABLISHING THE LOW-LOW SET RANGE FOR PRESSURE CONTROL. NORMALLY, ONE OF THE FOUR SAFETY RELIEF VALVES (SRV) USED FOR PRESSURE CONTROL (i.e., THE "H," "A," "G," OR "C" SRV) IS OPENED ELECTRICALLY FROM THE CONTROL ROOM WHICH THEN ESTABLISHES THE LOWER PRESSURE CONTROL. TEN OF THE ELEVEN SRVs FAILED TO OPEN IN RESPONSE TO CONTROL ROOM SWITCH POSITIONING. THE LAST SRV ATTEMPTED (THE "B" SRV) OPENED. UNIT 1 IS CURRENTLY STABLE IN HOT SHUTDOWN REJECTING DECAY HEAT TO THE TORUS WITH BOTH TRAINS OF SUPPRESSION POOL COOLING IN SERVICE. EFFORTS ARE UNDERWAY TO RESTORE THE MAIN CONDENSER AS A HEAT SINK. THE LICENSEE INTENDS TO COOL DOWN UNIT 1 TO INVESTIGATE AND RESOLVE THE PROBLEM WITH THE SRVs. THERE IS NO INDICATION THAT THE SRV MECHANICAL SAFETY OR AUTOMATIC DEPRESSURIZATION SYSTEM FUNCTION IS IMPAIRED AT THIS TIME. DURING THE TRANSIENT, REACTOR COOLANT SYSTEM (RCS) TEMPERATURE AND PRESSURE DECREASED FROM THEIR NORMAL AT POWER VALUES OF 532°F AND 1035 PSIG TO AN OBSERVED MINIMUM OF 480°F AND 871 PSIG. BOTH ARE CURRENTLY AT 510°F AND 977 PSIG. THERE IS NO INDICATION THAT THE 100°F/HOUR COOLDOWN RATE WAS EXCEEDED. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. ******************* UPDATE AT 0138 ON 01/30/00 FROM BRUCE BUTLER TO LEIGH TROCINE ******************* The following text is a portion of a facsimile received from the licensee: "Upon subsequent investigation, the event review team determined that the cause of the low level condition that resulted in the Unit 1 reactor scram was the inadvertent closure of feedwater valve 1N21-F005B. This valve is the inlet valve to the 5th-stage feedwater heater. Closure of the valve caused a feedwater flow reduction such that the low level scram setpoint was reached. The valve closure was apparently caused by the spurious contact closure within the control switch for the valve." "The plant systems initially appeared to respond automatically as expected to this transient condition. Even though the [HPCI] system appeared initially to trip at its high level setpoint, subsequent review of its operation revealed that it operated longer than expected, and reactor water reached a higher level than desired. Operators isolated the main steam isolation valves [(MSIV)] in accordance with plant procedures. The HPCI system eventually tripped, and reactor water level appeared to stop increasing before reaching the main steam lines. A more detailed review of the event using the plant's safety parameter display system (SPDS) revealed that reactor water level increased to the point that water apparently reached the bottom of the main steam lines with some water entering the lines." "Operators proceeded to control reactor pressure using the main [SRV] system manually and in the low-low set mode of operation. Normally one (1) of the four (4) SRVs used for pressure control is opened manually from the main control room, which then initiates automatic pressure control using the SRVs in the low-low set mode. An operator attempted to manually open nine (9) of the eleven (11) SRVs but did not receive direct indication that any of these SRVs opened. When a tenth SRV was opened, the operator received direct indication that the SRV opened." "During subsequent investigation, the event review team has preliminarily determined that apparently enough water entered the main steam lines to flood the SRVs. With the MSIVs closed, engineers calculated that a total of approximately 4,100 gallons of water would be necessary to flood the SRVs. The amount of water necessary to flood the SRVs differs with each steam line, but it would only require an entry of approximately 860 to 1,060 gallons to flood the affected SRVs. A review of the data indicated that the flooded SRVs, although flooded, apparently opened upon demand by the operator. This is based upon a significant and rapid increase in the tailpipe temperature for the SRVs that were given an 'open' signal. Since the medium passing through the SRV was two-phase, the tailpipe pressure switches that provide positive direct indication that the SRV opened, and initiate the low-low set logic, did not actuate on nine of the SRVs. This led the operator to believe that those SRVs had not opened. When the operator gave the 'B' SRV an 'open' signal, enough of the water had been displaced to allow the tailpipe pressure switch to react normally. This resulted in the operator seeing direct indication that the 'B' SRV opened and actuation of low-low set logic. The operation of the SRVs with a two-phase medium was confirmed by an engineer from General Electric with extensive experience in SRV design and operation." "The plant is currently in Cold Shutdown. As a conservative measure all eleven SRV topworks and solenoids were removed and replaced. Initially, five (5) topworks and four (4) solenoids were sent to Wyle labs. Preliminary results of testing performed at Wyle labs indicated [that] these five topworks and four solenoids functioned normally. The remainder of the solenoids is being checked by Target Rock technicians at the plant. Appropriate walkdowns of plant systems are being conducted, and followup is occurring for equipment items that require resolution prior to startup." "Plant management [plans to] review and evaluate the event in its entirety and the response of plant systems before granting permission for restart of the unit." The licensee notified the NRC resident inspector. The NRC operation officer notified the R2DO (Julian), NRR EO (Matthews), and IRO (Congel.) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION | ESF ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(1)(iv) | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  | 0
36624 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-26 00:39 | 2000-01-26 04:29 | 2000-01-26 | UNIT 2 ENTERED TECH SPEC 3.0.3 DUE TO BOTH TRAINS SAFETY INJECTION INOPERABLE "AT 0039 EST ON 1/26/2000 BOTH TRAINS OF THE SAFETY INJECTION PUMPS (SIPs) OF SEQUOYAH UNIT 2 WERE RENDERED INOPERABLE. THE '2A' SAFETY INJECTION PUMP AND ITS ROOM COOLER WERE TAGGED OUT UNDER THE SITES TAGOUT PROCEDURE FOR MAINTENANCE. EITHER OF THESE COMPONENTS [SI PUMP OR ITS ASSOCIATED ROOM COOLER] BEING TAGGED MADE THE PUMP INOPERABLE. WHILE THE '2A' SI PUMP WAS INOPERABLE, MAINTENANCE WORKERS MISTAKENLY DRAINED THE OIL FROM THE '2B' SAFETY INJECTION PUMP MOTOR BEARING FOR A PERIOD OF TIME WHICH MADE IT INOPERABLE AND UNAVAILABLE. THIS OIL CHANGING EVOLUTION REQUIRED APPROXIMATELY 30 MINUTES TO ACCOMPLISH. THE SIMULANTEOUS INOPERABILITY OF BOTH UNIT 2 SI PUMPS REQUIRED ENTRY INTO TECHNICAL SPECIFICATION LCO 3.0.3 ACTION. IMMEDIATE STEPS WERE INITIATED TO RESTORE OPERABILITY TO '2B' SI PUMP. AT 0316 EST ON 1/26/2000 THE '2B' SI PUMP WAS DECLARED OPERABLE WHEN THE PUMP WAS SUCCESSFULLY RUN. LCO 3.0.3 ACTION WAS THEN EXITED. AN INVESTIGATION INTO THE CAUSE OF THIS EVENT WILL BE CONDUCTED." MAINTENANCE WORKERS WERE TAKING A SAMPLE OF THE BEARING OIL FOR ANALYSIS WHICH IS USUALLY ACCOMPLISHED THROUGH DRAINING. THE NRC RESIDENT INSPECTOR WILL BE INFORMED. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36623 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2000-01-25 07:50 | 2000-01-25 08:45 | 2000-01-26 | LOSS OF AC POWER TO 23 OF 45 EMERGENCY SIRENS DUE TO SNOW AND ICE. Due to recent accumulation of snow and ice, sporadic power outages have occurred in the area. This has resulted in "loss of AC power" indications for 23/45 Public Warning Sirens per their remote siren monitoring system. This is considered a loss of off-site response capability . Actions are being initiated to restore operability. Local surrounding counties will be notified of this condition. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1509 EST ON 1/25/00 BY PETER YANDOW TO FANGIE JONES * * * Power outages continue to be a problem in the Darlington, Lee, and Chesterfield counties affecting the public warning sirens. A total of 31 of 45 have been out-of-service, but restorations have brought the number down to 26 of 45 out-of-service. The NRC Resident Inspector has been notified. The R2DO (Caudle Julian) has been informed. * * * UPDATE AT 1533 EST ON 1/26/00 BY PETER YANDOW TO FANGIE JONES * * * Greater than 75 % of the emergency sirens (only 9 of 45 remain out-of-service) have been restored to service, this is the last update as the minimum number operable is met. The NRC Resident Inspector has been notified. The R2DO (Caudle Julian) has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36622 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2000-01-25 07:07 | 2000-01-25 07:32 | 2000-01-25 | EMERGENCY RESPONSE ORGANIZATION (ERO) ABILITY REDUCED BY HEAVY SNOW STORM The plant is operating at 95% power. Unusually heavy snow has reduced the ability of the ERO organization to respond to the site in a timely manner. Plant equipment is operating normally. The licensee is trying to get vehicles that can be used to transport essential personnel to their EOF and the TSC if they are needed. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1725 EST ON 1/25/00 BY MIKE WEBER TO FANGIE JONES * * * Weather conditions have improved and the roads are cleared such that ERO manning can be accomplished in required time. The licensee notified the NRC Resident Inspector. The R2DO (Caudle Julian) has been informed. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36621 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2000-01-25 06:10 | 2000-01-25 06:44 | 2000-01-27 | BROKEN WINDOW IN A HIGH ENERGY LINE BREAK DOOR PLACES THE PLANT IN AN UNANALYZED CONDITION A broken window in a High Energy Line Break Door which is located between the Main Feed Regulating Valve Room and the Auxiliary Boiler Feed Pump Room places the plant in an unanalyzed condition. Maintenance is fabricating a metal replacement part to cover the opening. The door is supposed to remain closed at all times when the plant is above 350 degrees F. The NRC Resident Inspector will be notified of this event by the licensee. * * * RETRACTION 1259 1/27/2000 TAKEN BY STRANSKY * * * "Indian Point has performed an engineering evaluation of the broken window in the High Energy Line Break door located between the Main Feed Regulating Valve room and the Auxiliary Boiler Feed Pump room and determined that the equipment in the Auxiliary Boiler Feed Pump room would have maintained its environmental qualification and the plant would have remained in an analyzed condition even if the window was entirely missing. Therefore, this event has been retracted." The licensee will inform the NRC resident inspector of this retraction. Notified R1DO (Rogge). | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED COND OP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(A) |  |  |  | 0
36620 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2000-01-24 22:15 | 2000-01-24 22:37 | 2000-01-26 | MORE THAN 25% OF THE OFFSITE WARNING SIRENS LOST DUE TO ICE STORMS The licensee reported the loss of more than 25% of the offsite warning sirens due to ice storms passing through the local area. The licensee will be contacting the power suppliers of the sirens to take action to recover them. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1315 EST ON 1/26/00 BY BLAIR WILSON TO FANGIE JONES * * * Greater than 75 % of the emergency sirens (86 %) have been restored to service, this is the last update as the minimum number operable is met. The NRC Resident Inspector has been notified. The R2DO (Caudle Julian) has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ENS INOPERABLE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36619 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2000-01-24 15:30 | 2000-01-24 17:59 | 2000-01-24 | COURTESY NOTIFICATION OF LOCAL AND STATE LAW ENFORCEMENT AGENCIES The licensee notified local and state law enforcement agencies as a courtesy concerning an investigation. This prompted notification of the NRC under 10CFR50.72(b)(2)(vi), "Offsite Notification." The licensee notified the NRC Resident Inspector. Refer to the HOO log for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36618 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2000-01-24 11:42 | 2000-01-24 12:50 | 2000-01-24 | MANUAL REACTOR TRIP DUE TO FEEDWATER OSCILLATIONS The licensee had reduced power to 95% to examine the '4A' steam generator feedwater regulating valve due to feedwater oscillations. A preliminary determination of valve internal problems versus control problems was made. The licensee was ready to continue the down power to shutdown to repair the feedwater regulating valve, when a manual trip became necessary due to the feedwater oscillations on '4A' steam generator. All systems functioned as designed, all rods fully inserted, no secondary safety valves lifted, and the plant is stable in Mode 3. Heat removal is via the atmospheric steam dumps, normal procedure with no tube leaks, and feedwater is via the standby feedwater system. The plant will remain shut down until repairs to the feedwater regulating valve are complete. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36617 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-01-22 13:00 | 2000-01-22 16:58 | 2000-01-22 | FOUR HOUR 91-01 BULLETIN - NO NCS CONTROLS IN PLACE FOR A FISSILE MATERIAL OPERATION THE SHIFT SUPERINTENDENT'S OFFICE WAS NOTIFIED BY THE NUCLEAR CRITICALITY SAFETY STAFF THAT THEY HAD A FISSILE MATERIAL OPERATION FOR WHICH THERE WAS NO NUCLEAR CRITICALITY SAFETY APPROVAL IN PLACE. THEY HAD A UF6 CYLINDER STORAGE AREA IN THE X-344A THAT HAD PREVIOUSLY BEEN MARKED AS A DOE MATERIALS STORAGE AREA (DMSA). IN REVIEW OF THE DMSA, THEY DISCOVERED THAT IT WAS NOT LISTED IN THE USEC/DOE LEASE AGREEMENT AS A DMSA. SINCE NO DMSA WAS IDENTIFIED, USEC HAS THE RESPONSIBILITY FOR THE AREA INCLUDING RESPONSIBILITY FOR NUCLEAR CRITICALITY SAFETY COVERAGE. THE AREA CONTAINED MULTIPLE SMALL UF6 CYLINDERS GROUPED TOGETHER WHICH CONTAINED GREATER THAN 15 GRAMS OF U-235 AT MORE THAN 1% ENRICHMENT. THEREFORE, THE STORAGE AREA IS CONSIDERED TO BE A FISSILE MATERIAL OPERATION WITH NO NCSA IN PLACE TO ANALYZE THE CONDITIONS REQUIRED TO MAINTAIN NCS SAFETY. THIS AREA WAS THOUGHT TO BE REGULATED BY DOE, BUT IT WAS LATER DETERMINED TO BE USEC'S RESPONSIBILITY AND USEC SHOULD HAVE HAD THE NCS INPLACE. THEY ARE NOT MOVING THE CYLINDERS, BUT THEY WILL BOUNDARY THE AREA OFF AND DEVELOP THEIR NCS CONTROLS. THE NRC RESIDENT INSPECTOR WAS NOTIFIED AND THE DOE REPRESENTATIVE WILL BE NOTIFIED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0
36616 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-01-22 03:20 | 2000-01-22 05:55 | 2000-01-22 | ESF ACTUATION OCCURRED WHEN REACTOR CORE ISOLATION COOLING (RCIC) INBOARD STEAM SUPPLY VALVE CLOSED DURING TESTING. During the performance of routine surveillance testing of RCIC (STP-207-4538, "RCIC Isolation -RCIC Steam Supply Pressure Low Channel Functional Test"), an isolation of the inboard steam supply valve (E51-MOVF064) and the RCIC trip throttle valve (E51-C002) occurred. The Instrument and Controls Technician performing the test apparently misread step 7.1.3 and "N/A'd" the next step (7.1.4). During the performance of subsequent steps, the isolation occurred because the isolation signal input from E31-N685A was not disabled. The isolation signal was reset, RCIC was restored to standby in accordance with plant procedures. All Emergency Core Cooling Systems remained operable during the time period RCIC was isolated. The NRC Resident Inspector was notified of this event by the licensee. | 31 | 0 | 0 | 31 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36615 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2000-01-21 23:13 | 2000-01-21 23:33 | 2000-01-21 | ULTIMATE HEAT SINK (UHS) BELOW MINIMUM DESIGN TEMPERATURE LIMIT OF 33 DEGREES F (CONCERN IS SERVICE WATER TEMPERATURE). Below is the Basis for Initial Reasonable Expectation of Continued Operability performed by Engineering: CCI is Closed Cooling for Safety Injection, CCE is Closed Cooling for Charging, SW is Service Water, and Hx is Heat Exchanger "The concerns with low UHS temperature are pipe stress calculations and possible freezing of stagnant loops such as CCI and CCE. Other portions of the SW system are not vulnerable to small changes in UHS temp due to constant flows and large heat sinks. Additionally, the 33 degree F limit is the design basis of the plant per the FSAR and therefore is reportable if exceeded. "CCL and CCE freezing: "A review of the thermodynamic characteristics of the CCI and CCE heat exchangers, assuming UHS of 31 degrees F, shows that the temperature gradient of the process fluid, due to the high conductivity of the copper nickel pipe and room temperatures, results in CCI and CCE bulk fluid temperatures remaining above freezing for an extended period of time, although the bulk temperature of the shell side of the CCI heat exchangers is only 32.5 degrees F. To assure operability of the SI pumps, the CCI system should be started at a SWP temperature of 33 degrees F decreasing to move the water through the system. The historical UHS temperature dips below 33 degrees F have been for a short duration of hours followed by longer warming periods. Design calculations show that CCI/SIH operate properly with the entire bulk temperature at 32 degrees F. This is conservative as the majority of the CCI system will remain at ambient room temperature in the standby mode. Once operating, there is additional heat input from the SIH pump. Therefore, there is no limit to UHS temperature which would render CCI/SIH inoperable even over several hours. "A similar argument applies for the CCE/CHS system. The temperature gradient and bulk temperature characteristics are identical. Additionally, the CCE system utilizes a temperature control valve to maintain proper temperatures. The failed position of this valve (LOP) is to maximum flow through the SW Hx and has a position limiter designed for proper Charging lube oil temperature with a 33 degrees F UHS. The supporting calculation demonstrates that a 41.9 degrees F CCE inlet temperature at the lube oil cooler results in a 55 degrees F lube oil temperature (minimum required temperature for charging pump operability). If a service water temperature of 30 degrees F is used in the LMTD equation for the CCE HX, and the delta-T on both the SW & CCE sides are assumed to remain unchanged, the calculated CCE inlet temperature at the lube oil cooler is 42.2 degrees F, which is > 41.9 degrees F needed for the 55 degrees F lube oil temperature. "To prevent potential freezing of the shell side fluid in the CCI heal exchangers and assure the Operability of the Safety Injection pumps, the CCL pumps should be started at a SWP temperature of 33 degrees F decreasing. "Piping Stress: "The Service Water System piping, supports and equipment have been analyzed to meet Code stress limits at a minimum temperature of 33 degrees F as described in OD MP3-213-96. Lower temperatures will have no affect on the qualification status of the piping analysis since thermal expansion induced pipe stress is secondary, and is not evaluated under GL 91-18 Operability rules. "Increases in loads for pipe supports, equipment nozzles and equipment anchorage for temperatures below 33 degrees F are judged to be negligible and also have no affect on the operability of these components. ERC MP3-DE-96-059 revision 1 transmitted Technical Report TR-89014-1, revision 2, which evaluated low temperature piping at Millstone Unit 3. This report concludes that systems where the maximum operating temperature does not exceed 200 degrees F, and the temperature range does not exceed 200 degrees F, satisfy ASME Code requirements for thermal expansion loads. The Service Water maximum temperature range is well below 200 degrees F. "Therefore, Service Water temperatures below 33 degrees F (to the freezing point of sea water 27.5 degrees F) will have no effect on the operability of Service Water piping, supports, equipment nozzles, and equipment anchorage, from a stress standpoint. No compensatory action are required. "An OD has been prepared to support continued operation of MP3 with a Service Water temperature of 31 degrees F. This OD is stored on the MP3 server at K:\DeptData\MacDeb\UHSOD. Scoping calculations to support this OD have been completed and reviewed. This OD must be reviewed and PORC approved as required by the SM, if SWP temperatures lower than 33 degrees F are recorded." When the tide goes out the water temperature of the Ultimate Heat Sink temperature decreases and when the tide comes back in the temperature of the Ultimate Heat Sink increases. At the present time the tide is going out and the water temperature is 32.7 degrees F. In a couple of hours the tide will start coming back in and the water temperature of the Ultimate Heat sink should increase to above 33 degrees F (37 to 38 degrees F). The licensee notified State and Local Counties of this event. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36614 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-01-21 19:45 | 2000-01-21 20:05 | 2000-01-21 | INSUFFICIENT GUIDANCE FOR ENSURING THAT A SAFETY RELATED SYSTEM WAS OPERATING DURING A LOCA During the evaluation of a separate Condition Report concerning a Technical Specification 3.0.3 entry involving the Beaver Valley Power Station (BVPS) Unit 1 Supplemental Leak Collection & Release System (SLCRS), it was discovered that the operators did not have sufficient guidance for ensuring that this safety related system was operating following an accident. BVPS Units 1 and 2 Technical Specifications 3/4.7.8 Bases states "System operation was assumed in that portion of the design basis accident LOCA analysis which addressed ESF leakage following the LOCA Based on the results of the analyses, the SLCRS must be OPERABLE to ensure that ESF leakage following the postulated DBA LOCA will not exceed 10CFR 100 limits." ESF leakage is a concern during a LOCA following a Safety Injection Transfer to Recirculation. The BVPS Unit 1 and 2 operators did not have sufficient guidance to ensure that a SLCRS fan is operating during a LOCA after Transfer to Recirculation occurs. Thus, the SLCRS may not operate as assumed and credited in LOCA safety analyses. SLCRS also provides cooling air flow to the emergency core cooling pumps motors. The need for SLCRS for maintaining the qualification of emergency core cooling pumps motors is proportional to the ambient outdoor air temperatures. Current guidance does not ensure SLCRS would be available in all conditions where SLCRS flow is required to maintain the qualification of the emergency core cooling pump motors. This condition is an unanalyzed condition and is reportable pursuant to 10CFR50.72(b)(1)(ii). Verbal guidance has been provided to the BVPS Unit 1 and 2 operating crews to ensure a SLCRS fan is running in the event of a reactor trip or safety injection. This guidance is currently being formalized. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED COND OP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(A) |  |  |  | 0
36613 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-01-21 12:00 | 2000-01-21 14:26 | 2000-01-21 | THE LICENSEE NOTIFIED THE NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION OF A FISH KILL. THERE WAS A FISH KILL IN THE DISCHARGE CANAL OF MORE THAN 100 FISH (SEVERAL SPECIES) DUE TO COLD STRESS. THIS OCCURRED FOLLOWING THE REACTOR SCRAM WHEN COOLER WATER WAS DISCHARGED TO THE CANAL DECREASING ITS TEMPERATURE. THE RESIDENT INSPECTOR WILL BE NOTIFIED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36612 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2000-01-21 10:48 | 2000-01-21 11:17 | 2000-01-24 | MANUAL REACTOR SCRAM PER PROCEDURE FOLLOWING TRIP OF ALL RECIRCULATION PUMPS During the performance of a surveillance test, with a half scram signal inserted, a spurious trip signal from the other system initiated a trip of all the reactor coolant system recirculation pumps. The operators manually scrammed the reactor per procedure, all rods fully inserted. Heat removal is via the main condenser with main feedwater feeding the reactor. All systems functioned as designed and the plant is proceeding to cold shutdown. A trip review will be performed by the licensee. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1943 EST ON 01/24/00 BY FRANK CIGANIK TO FANGIE JONES * * * On 01/21/00, the licensee inserted a manual scram in accordance with station procedures in response to a trip of all the reactor recirculation pumps. The trip of all the pumps was due to an error in the performance of the ongoing surveillance test. "During the performance of an instrument logic surveillance test on the isolation condenser actuation logic which also inserts trip signals into the recirculation pump trip logic, the reactor recirculation pumps tripped. After testing the first instrument, the trip signal associated with the isolation condensers were reset; however, the recirc pump trip logic was not properly reset before proceeding to the second instrument. When a test signal was introduced on this instrument, the reactor recirculation pumps tripped as designed. In response to the pump trip, the operators manually scrammed the reactor. The plant is currently in cold shutdown. A trip review has been performed. Oyster Creek plans to take advantage of this shutdown to perform some other maintenance activities." The original report should have read "half trip" rather than "half scram" referring to the trip logic of the reactor recirculation pumps; this was entered wrong the first time. The licensee notified the NRC Resident Inspector. The R1DO (John Rogge) has been notified. | 0 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36611 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-01-14 | 2000-01-21 07:17 | 2000-01-21 | AGREEMENT STATE REPORT This is notification of an event in Washington state as investigated by the WA Department of Health, Division of Radiation Protection. STATUS: new Reported By: Federal Express City and state: Seattle, WA License number: Not Applicable Type of license: General license for Commercial Carrier Date of event: January 14, 2000 Location of Event: Seattle-Tacoma International Airport ABSTRACT: During off-loading a plane early in the morning of January 14, 2000, a two pound package containing 52 microcuries of I-125 labeled human insulin fell off the ramp loader and came to rest un-noticed under the extended ramp. The ramp was lowered after the unloading of the plane, crushing the package. The crushed package was discovered later that day and Federal Express procedures were followed. The package was noted to fall apart as it was lowered into the barrel overpack. The state Division of Radiation Protection was notified promptly via 206-NUCLEAR (the state's radiation emergency line). Staff from the Division responded and determined that neither the individual who had overpacked the package nor the ramp loader were contaminated. The barrel overpack was opened long enough to confirm the presence of removable contamination (approximately 2000 cpm per 100 sq. cm. using low energy gamma scintillation probe). Direct survey reading inside of the barrel showed 30,000 to 50,000 cpm. No contamination was found on the outside of the barrel or the barrel's storage location. The package was a Type A container labeled Yellow II with a transport index of 0.1 (UN2982, radioactive material, n.o.s.) shipped from Amersham Pharmacia Biotech to a Seattle research lab licensed by the state. What is the notification or reporting criteria involved? Damaged package. Activity and isotope(s) involved: 52 microcuries of I-125. Overexposures? No individuals were exposed or contaminated as a result of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
36610 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2000-01-21 02:39 | 2000-01-21 04:21 | 2000-01-24 | UNIT 1 MANUALLY TRIPPED FROM 40% POWER DUE TO A DECREASING FOREBAY LEVEL "UNIT 1 WAS MANUALLY TRIPPED FROM 40% POWER AFTER AN ANTICIPATORY POWER REDUCTION AT 0239 CST DUE TO DECREASING LEVEL IN THE CIRC. WATER INLET FOREBAY. DECREASING LEVEL WAS APPARENTLY DUE TO ICING OF THE INTAKE STRUCTURE. UNIT 1 CIRC. WATER SYSTEM HAS BEEN SECURED AND FOREBAY LEVEL HAS INCREASED. THE UNIT 1 CIRC. WATER SYSTEM WAS SECURED TO MAINTAIN OPERABILITY OF THE SERVICE WATER SYSTEM. UNIT 2 REMAINS AT 100% POWER AND IS STABLE." FOREBAY LEVEL HAD DECREASED TO -11 FT FROM THE NORMAL OPERATING -8 FT. THE -11 FT CORRESPONDS TO THE MINIMUM DESIGN LIMIT FOR THE SERVICE WATER SYSTEM. CURRENTLY, LEVEL IS -6 FT 4 INCHES. STEAM GENERATORS USING THE ATMOSPHERIC DUMPS ARE PROVIDING THE HEAT SINK FOR DECAY HEAT REMOVAL SINCE THE CONDENSER IS NOT IN SERVICE. ALL CONTROL RODS FULLY INSERTED FOLLOWING THE MANUAL TRIP. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. * * * UPDATE ON 01/21/00 @ 1339 EST BY KRAUSE TO GOULD * * * THE LICENSEE UPDATED THIS EVENT BY ALSO CLASSIFYING IT AS A RPS ACTUATION DUE TO THE MANUAL REACTOR TRIP. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED. THE R3DO (HILLS) WAS NOTIFIED. * * * UPDATE ON 01/24/00 @ 1201 EST BY KRAUSE TO JONES * * * The licensee performed an engineering evaluation that demonstrated that at no time was the design basis water level for service water exceeded. The report of the Tech Spec required shutdown is retracted, but the report of the RPS activation stands as previously updated. The licensee notified the NRC Resident Inspector. The R3DO (Monte Phillips) has been notified. | 0 | 0 | 0 | 40 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(i)(A) | 50.72(b)(2)(ii) |  |  | 0
36609 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2000-01-20 18:17 | 2000-01-20 19:05 | 2000-02-19 | INADEQUATE SHORT CIRCUIT PROTECTION ON CONTROL WIRING ASSOCIATED WITH THE LINE STARTER FOR MAIN TURBINE DRAIN VALVES While performing a design analysis on Beaver Valley Unit 2 (BV-2) to confirm adequate electrical fault protection, as follow-up to an Engineering fire protection self-assessment completed in May 1999, it was determined that the control wiring associated with the line starter for the nine main turbine drain valves is not adequately protected from short circuits. This protection inadequacy results from a lack of required fuse protection and/or current limiting features described in Section 9.5.A.1.2.1.5(4) of the Updated Final Safety Analysis Report. Due to this lack of adequate current limiting protection, an electrical fault on this circuit could result in a fire in multiple fire areas including the common Unit 1/2 Control Room, BV-2 Service Building, BV-2 Cable Vault, BV-2 Cable Tunnel, and BV-2 Turbine Building. The lack of current limiting protection for this circuitry introduces the possibility of a potential fire in these multiple areas, which is a violation of fire protection licensing basis commitments regarding safe shutdown capability. The subject main turbine drain valves are non-safety related and not required for safe shutdown. As an interim measure, the circuit has been de-energized and will remain de-energized until adequate electrical protection can be provided. The NRC Resident Inspector was notified. * * * UPDATE ON 2/19/00 @ 1105 BY MARACEK TO GOULD * * * RETRACTION Upon further review, it was determined that lack of adequate electrical fault protection for cable 2SDSNNC001 did not constitute a condition outside the design basis of the plant. The postulated fire event would be limited to non-safety related cable trays in which cable 2SDSNNC001 is routed and non-safety cables in the Control Room benchboard area. This determination is based upon use of flame test qualified cables, adherence to Regulatory Guide 1.75 separation criteria, and guidance provided by Generic Letter 81-12, regarding associated circuits for common enclosures. This cable is not routed in safety related Class 1E raceways. Review of cables in the Fire Protection Safe Shutdown Report indicates that the only safe shutdown related cables in the non-Class 1E raceways are for the station air compressors, which would already be assumed lost in the event of a fire in the Unit 2 Turbine Building (TB-1). For a fire in TB-1, safe shutdown is addressed in existing plant procedures to compensate for loss of equipment due to a fire in this area. Therefore, a fire resulting from a fault of cable 2SDSNNC001 would not have affected safety related circuits or the ability to achieve safe shutdown. Therefore the licensee is retracting this event. The NRC Resident Inspector will be notified. Reg 1 RDO (Kinneman) was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36608 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2000-01-20 14:00 | 2000-01-20 17:31 | 2000-01-20 | CABLES AND CONDUITS IN THE SALT WATER COOLING PIPE TUNNEL FOUND WITHOUT A PORTION OF THEIR FIRE WRAPS. ON 1/19/00, FOLLOWING A PLANT WALKDOWN, IT WAS DISCOVERED THAT SOME CABLES AND CONDUITS IN THE SALT WATER COOLING PIPE TUNNEL WERE MISSING PORTIONS OF THEIR FIRE WRAPS. AFTER REVIEW OF PLANT DOCUMENTATION, IT WAS DETERMINED THAT THIS CONDITION AFFECTED BOTH TRAIN "A" AND "B" SALT WATER COOLING PUMPS FOR UNIT 3. CONSEQUENTLY ON 1/20/00 @ 1400 PST IT WAS CONCLUDED THIS CONDITION DID NOT MEET THE REQUIREMENTS OF APPENDIX "R" TO ASSURE ONE TRAIN OF SAFE SHUTDOWN EQUIPMENT FREE OF FIRE DAMAGE IN THE EVENT OF A DESIGN BASIS FIRE. THE LICENSEE IMMEDIATELY ENSURED THAT A ROVING FIRE WATCH HAD BEEN POSTED(AND WAS ALREADY IN PLACE FOR OTHER UNRELATED REASONS). THIS ACTION SATISFIED THEIR LCO ACTION STATEMENT REQUIREMENT. IN THE EVENT OF A FIRE, PLANT OPERATORS WOULD HAVE BEEN ABLE TO RESTORE POWER TO THE SALT WATER COOLING SYSTEM(BY ISOLATING THE AFFECTED CABLES AND STARTING A PUMP FROM ITS SECOND POINT OF CONTROL). ADDITIONALLY, THE COMBUSTIBLE LOADING IN THE AFFECTED AREA IS EXTREMELY LOW(2 MINUTE FIRE DURATION), AND THAT AREA IS PROTECTED BY FIRE SPRINKLERS AND FIRE DETECTORS. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS | TECH SPEC LCO A/S |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36607 | -1 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-18 18:02 | 2000-01-18 19:15 | 2000-01-27 | SECURITY REPORT UNSUBSTANTIATED BOMB THREAT. COMPENSATORY MEASURES TAKEN. LICENSEE INFORMED THE LOCAL POLICE DEPARTMENT. * * * RETRACTION 1533 1/27/2000 FROM NOLDEN TAKEN BY STRANSKY * * * After review of NRC Regulatory Guide 5.62, the licensee has determined that this event was not reportable. Notified R3DO (Phillips). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 0
36606 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2000-01-19 14:55 | 2000-01-19 21:59 | 2000-01-19 | DISCOVERY OF A LOOSE STEM NUT AND THE INABILITY TO MANUALLY OPERATE A SAFE SHUTDOWN MAKEUP PUMP (SSMP) INJECTION VALVE FOLLOWED BY DISCOVERY THAT THE VALVE WAS NOT FULLY CLOSED The following text is a portion of a facsimile received from the licensee: "On January 19, 2000, at 1357 [CST], the MO 2-2901-8 [valve] (SSMP injection to Unit 2) was taken [out of service] for planned maintenance on the valve position limit switches. At 1455 [CST], the Maintenance Supervisor notified the control room that the stem nut was found loose and [that] the valve could not be manually operated. For Unit 2, a 14-day technical specification [(TS) limiting condition for operation (LCO)] was entered per TS 3.8.J, and a 14-day LCO for administrative technical requirements (ATR) was entered. At 1605 [CST,] it was determined that the valve was not fully closed, and the SSMP system [was] declared inoperable to Unit 1. [As a result, a] 14-day LCO for [TSs] and a 14-day ATR [were] entered for Unit 1. A plan is being developed to repair/correct the MO 2-2901-8 [valve]." "It was determined at 2040 [CST] that this event is reportable ... ." The licensee stated that both the pump and the valve have quarterly surveillances and that the surveillances were up to date. The licensee plans to notify the NRC resident inspector. | 100 | 85 | 0 | 100 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | TECH SPEC LCO A/S |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iii)(A) |  |  |  | 0
36605 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2000-01-19 09:00 | 2000-01-19 17:59 | 2000-02-03 | FAILURE OF HIGH PRESSURE FIRE WATER SPRINKLER SYSTEMS TO MEET SYSTEM OPERABILITY REQUIREMENTS (24-Hour Report) - (Refer the event #36018 for a similar event at Portsmouth and refer to event #35790 and event #36552 for related events at Paducah.) The following text is a portion of a facsimile received from Portsmouth: "On 01/19/00 at approximately 0900 hours during the scheduled semi-annual walkdown of the X-330 Process Building high pressure fire water (HPFW) systems, the Plant Shift Superintendent (PSS) was notified that sprinkler systems #284 and #365 were not capable of meeting system operability requirements due to corrosion problems identified on adjacent sprinkler heads." "Two adjacent heads on system #284 and three adjacent heads on system #365 were identified with corrosion around the valve seat. This condition prevents the heads from being able to actuate at normal water pressure. When two adjacent heads are inoperable, the system is considered unable to perform its design function. The PSS declared the affected sprinkler systems inoperable, and [technical safety requirement (TSR)] required actions were initiated and completed." "Further inspections of the Process Building sprinkler systems are planned. This report will be updated if additional sprinkler systems are determined to be inoperable." "There was no loss of hazardous/radioactive material or radioactive/radiological contamination exposure as a result of this event." At the time of this event notification, Portsmouth personnel had completed repairs and were in the process of closing out the paperwork to be able to declare the systems operable again. Portsmouth personnel notified the NRC resident inspector and a Department of Energy site representative. (Call the NRC operations officer for a site contact telephone number.) * * * RETRACTION AT 1800 HOURS ON 02/03/00 BY ERIC SPAETH TAKEN BY MACKINNON * * * The above listed sprinkler heads were replaced and taken to the USEC Laboratory for testing. Of the seven sprinkler heads tested, all operated at the proper temperature, 5 operated at < 7 psi pressure, one operated at 12 psi pressure and one operated at 16 psi pressure. An Engineering Evaluation (EVAL-SS-2000-0038) completed on 01/25/00, calculated that at roof level with 20 or more heads flowing, system pressure would remain at 18.4 psi. The corroded sprinkler heads were found at lower levels which have smaller pressure losses and less friction losses due to shorter piping runs. Since the available system pressure would have been greater than 18.4 psi and the sprinkler heads all operated at 16 psi or less, it was determined that the sprinkler heads would have operated when needed and performed their intended safety function. Since the sprinkler heads were operable, this condition is not reportable in accordance with 10 CFR 76.120[c][2]. Accordingly, this event is being retracted. R3DO (Vegel) & NMSS EO (Holonich) notified. The NRC Resident Inspector was notified of this retraction by the certificate holder. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EQUIP DISABLED/FAILS | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2)(ii) |  |  |  | 0
36604 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-19 14:24 | 2000-01-19 15:46 | 2000-02-17 | DISCOVERY THAT UNIT SPECIFIC LOADS WERE ON COMMON BUSES The following text is a portion of a facsimile received from the licensee: "FSAR section 1A(B) for compliance to [Regulatory] Guide 1.81 states that [the Comanche Peak] design complies with the provisions of Revision 1 of this [regulatory] guide. Contrary to the above, unit specific [118-volt AC] loads fed from common buses XEC1-1 and XEC2-1 were shared between two units." The licensee stated that affected loads involve a lot of different equipment and systems but did not specify which equipment or systems. The licensee also stated that the units are not currently in any technical specification limiting conditions for operation as a result of this issue because the loads are now aligned to an alternate power supply. Corrective actions have not yet been determined. The licensee notified the NRC resident inspector. *************** UPDATE AT 1412 ON 02/17/00 FROM SCOTTY HARVEY TO LEIGH TROCINE *************** The licensee is retracting this event notification based upon the following text, which is a portion of a facsimile received from the licensee: "After a further review of the condition (event #36604) reported on January 19, 2000, [the licensee] did not identify any deviation from the design basis requirements of the plant as defined in 10CFR50.2." "The basic premise of the conservative reporting of this condition was that some unit specific DC [See note 1] and AC (118-volt AC) loads fed from common buses were shared between two units and that this condition may not be in compliance with the design basis of the plant. Although, it was deemed that the statements in the FSAR may not be clear and that CPSES may not be in verbatim compliance with every aspect of Regulatory Guide 1.81. The plant's as-built configurations maintained their ability to perform their specified safety functions and were not in a condition outside of the design basis as defined in 10CFR50.2. Therefore, this condition is not reportable under the auspices of 10CFR50.72/73. Accordingly, this report described in event [#36604] is hereby retracted." "[NOTE 1: The licensee] believe[s] that the DC unit specific loads do not meet the specific requirements of the [regulatory guide (RG)]. However, [the licensee] believe[s] that this is technically [okay] and ... would justify this as an exception to the RG. The AC loads do not meet the RG as well, but [the licensee is] proposing changing some of the power sources and installation of an Automatic Bus Transfer as well." The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Marschall). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36603 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2000-01-18 10:00 | 2000-01-18 17:41 | 2000-03-07 | AGREEMENT STATE REPORT INVOLVING TROXLER DENSITY GAUGE MISSING FROM NUCLEAR TESTING SERVICES LOCATED IN SALT LAKE CITY, UTAH At 1000 MST on 01/18/00, Nuclear Testing Services located in Salt Lake City notified the Utah Division of Radiation Control of a lost, missing, or stolen gauge (Utah Incident Report UT-00-0002). The missing gauge was a Troxler Electronic Laboratories, Inc. gauge (model number 3430, gauge serial number 20882). The gauge contained two sealed sources: cesium-137 ( source serial number 7-2293) and americium-241/beryllium (source serial number 47-16381). Apparently, the licensee last had possession of the gauge during April of 1999. This was also when the last leak test was performed. The licensee believes that the gauge may have been leased out to another company during August of 1999. However, there may have been problems with the paperwork or accountability, and there were also changes in personnel. The Utah Division of Radiation Control instructed the licensee to contact local Police Department because there is the possibility of theft. It was also reported that the licensee had been in touch with Troxler. The Utah Division of Radiation Control stated that this event seemed to fit the Abnormal Occurrence Criteria under any substantial breakdown of physical security or material control. It was stated that one of those deals with accountability systems. (Call the NRC operations center for a state contact telephone number.) * * * UPDATE AT 1608 ON 03/07/00 BY JULIE FELICE TO JOLLIFFE * * * Representatives from Geomatrix Consultants, Inc,, Costa Mesa, CA, notified representatives of Nuclear Testing Services, Salt Lake City, UT that the missing Troxler Moisture Density Gauge, Model #3430, Serial #20882, is in Geomatrix's possession and had been all along. Geomatrix representatives plan to return the undamaged gauge to Nuclear Testing Services. The NRC Operations Officer notified the R4DO Dave Loveless and NMSS EO Scott Moore. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36602 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-18 10:51 | 2000-01-18 11:40 | 2000-01-18 | INADVERTENT SAFETY INJECTION DUE TO ELECTRICAL FAULT AND REACTOR TRIP Technicians were performing a modification to the vital inverter 2-IV when a safety injection signal was generated due to an electrical problem on vital instrument bus 2-IV. When the technicians were lifting a lead on the sync signal input to the inverter 2-IV in accordance with the modification, an inadvertent safety injection signal was generated. When the safety injection actuated, only Train 'A' safety injection occurred. The cause of the reactor trip is unknown at this time though it is expected with a safety injection. The operators followed the emergency procedures and started the Train 'B' safety injection and residual heat removal pumps; the train 'B' centrifugal charging pump started automatically (reason unknown and being investigated). The 2A-A motor-driven auxiliary feedwater pump tripped for unknown reasons. The #2 steam generator atmospheric relief valve controller appears to have failed, which required operators to take manual control and close the relief valve. An event investigation has been initiated, and all problems will be answered before the unit is restarted. The plant is currently stable in Mode 3 with heat removal via the atmospheric reliefs and feedwater via the 2B-B motor-driven and turbine-driven auxiliary feedwater pumps. All rods fully inserted. The safety injection signal was from the 'Low Steam Generator Pressure' section, and the main steam isolation valves closed automatically. The plant has no steam generator tube leaks. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION | ESF ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(1)(iv) | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  | 0
36601 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2000-01-18 09:25 | 2000-01-18 11:41 | 2000-01-19 | LOSS OF COMMERCIAL TELEPHONE SERVICE The licensee reported that all U.S. West commercial telephone service to the site (including the ENS) has been lost due to a problem offsite. The licensee is attempting to contact U.S. West to determine the cause of the problem and estimate time to restore. The NRC resident inspector will be informed of this event by the licensee. ******************** UPDATE AT 1916 ON 01/18/00 FROM DAN MARKS TO LEIGH TROCINE ******************** The following text is a portion of a facsimile received from the licensee: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a followup notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73." "NOTE: THIS ENS WORKSHEET IS A FOLLOW-UP TO ENS ID 36601, PERFORMED AT 09:41 MST. SINCE U.S. WEST LINES WERE AFFECTED, THE INITIAL CALL WAS MADE VIA A CELLULAR TELEPHONE." "On January 18, 2000, at approximately 0925 MST, Palo Verde Units 1, 2, and 3 determined that the ENS telephones were inoperable. This was related to the offsite damage to a 200-pair telecommunications cable affecting Palo Verde. The initial call was placed from the Nuclear Regulatory Affairs Director's cellular telephone, and that phone number was also provided to the [headquarters operations officer] if followup was necessary prior to restoration of the ENS." "The current prognosis for full restoration of the ENS is approximately 2400 MST. If the Palo Verde Units 1, 2, or 3 cannot be reached via the ENS, [commercial] ... phone numbers are available. [Call the NRC operations officer for site contact numbers.] ..." "Emergency Plan notification system backups for communication with State and County agencies were confirmed to remain operable; therefore, this notification was only for the loss of ENS and did not reflect a loss of emergency assessment or notification capability." "There is no corresponding 10 CFR 50.73 reporting requirement. Palo Verde does not expect to followup this report with a Licensee Event Report (LER)." "Palo Verde [plans to] complete a followup notification when full capability is restored." The licensee notified the NRC resident inspector. The NRC operations officer notified the R4DO (Smith). * * * UPDATE 0006EST ON 1/19/2000 FROM BRAD ROBINSON TO S.SANDIN * * * The ENS phones have been restored to complete functionality at 2206MST. The licensee notified the NRC resident inspector. Notified R4DO(Smith). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | ENS INOPERABLE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36600 | 0 | UNIVERSITY OF MINNESOTA |  |  |  |  | 1999-11-23 | 2000-01-18 11:24 | 2000-01-18 | MISSING TRITIUM FILLED EXIT SIGNS The licensee contacted the NRC Operations Center to report the loss of three tritium-filled exit signs, each containing 11.5 Ci, from a dormitory. The signs had initially been found to have been removed late in 1999, and the licensee had contacted the Region III office (G. Wright) at that time. During the semester break, housing personnel searched all student rooms but were unable to locate the signs. All other tritium filled signs have been removed from the dormitory and returned to the vendor. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36599 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-17 14:30 | 2000-01-17 16:49 | 2000-01-17 | DISCOVERY OF A POTENTIAL CONTAINMENT LEAKAGE PATH AND DEGRADED SAFETY BARRIER The following text is a portion of a facsimile received from the licensee: "This is ... American Electrical Power, D.C. Cook Plant Units 1 and 2 calling with a [4]-hour notification in accordance 10 CFR 50.72(b)(2)(i) of a condition which was found while the reactor is shutdown, which, had it been found while the reactor was in operation, would have resulted in the nuclear power plant, including its principal safety barriers, being seriously degraded or being in an unanalyzed condition that significantly compromises plant safety. "During the ongoing In-Service Program inspection of the Unit 2 containment liner, an indication was found that appeared to be a weld repair. After surface preparation to allow for further inspection, it was determined that the indication was actually a previously repaired area on the liner plate, probably dating from construction. The mechanism used for surface preparation was a needle gun, and the force exerted by the needle gun dislodged the weld metal that had been deposited in the damaged area. The result was a through-liner hole approximately 3/16 of an inch in size that is roughly circular. "Although the Unit 2 containment successfully passed its 10 CFR [Part] 50, Appendix-J, Integrated Leak Rate Testing in 1992, concern exists that under thermal stress of a postulated accident condition, the weld material could have become dislodged. This would potentially represent a containment leakage path and a degraded safety barrier. "This hole will be repaired in accordance with ASME Section XI, Repair or Replacement Program, prior to startup." The licensee stated that both unit are currently defueled. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEG/UNANALYZED COND |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0
36598 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2000-01-17 11:45 | 2000-01-17 12:42 | 2000-01-17 | CONFIGURATION ERROR RESULTING IN AN ALTERNATE LOW-TO-HIGH HEAD SAFETY INJECTION (SI) RECIRCULATION FLOW PATH OUTSIDE DESIGN BASIS ISSUE The following text is a portion of a facsimile received from the licensee: "On 10/10/1999, prior to plant startup from the last refueling outage, [SI] manual butterfly valve SI-1863 was closed as directed by refueling procedure SOP-RP-20, 'Draining the Refueling Cavity.' This valve is required to be open as directed by check off list COL-RHR-1, but the [check off list] was performed prior to the refueling procedure. As a result, it appears that the valve SI-1863 had been closed since startup from the refueling outage in October 1999. [Valve] SI-1863 is located in an alternate low-to-high head flow path. [Final Safety Analysis Report (FSAR)] Table 6.2-8 describes the use of this flow path should the normal low-to-high head recirculation flow path be unavailable (i.e., isolated in response to a passive failure). Hence, the inappropriate closure of [valve] SI-1863 could [have prevented] the ability of the [SI] system to accommodate a certain passive failure described in the FSAR during recirculation following a postulated event. This configuration error potentially placed the SI system outside its design basis. This mispositioning was discovered on 01/14/2000 during an extent of condition review for a suspected [chemical and volume control system] valve mispositioning in the excess letdown flow path. Valve SI-1863 was opened shortly after discovery. The extent of this condition for this event is still ongoing. Review of this deviation event report on Monday, 01/17/2000, determined that this event [was] potentially outside the system's design basis." The licensee notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36597 | 0 | EXXON BIOMEDICAL SCIENCES, INC. |  |  |  |  | 1999-12-08 | 2000-01-17 11:27 | 2000-01-17 | MISSING Ni-63 SEALED SOURCES The licensee reported that two gas chromatography detectors, each containing 15 mCi of Ni-63 foil, were discovered to be missing during a recent inventory. The detectors were last seen on 12/8/1999. The licensee is currently in the process of moving to a new facility but was unable to find the detectors after searching both facilities. The licensee will continue to search for the sources. (Call the NRC operations officer for a licensee contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0
36596 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2000-01-17 05:38 | 2000-01-17 06:32 | 2000-01-19 | SECURITY REPORT. FITNESS-FOR-DUTY QUESTIONED DUE TO INATTENTIVENESS. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. CONTACT THE NRC OPERATIONS CENTER FOR ADDITIONAL DETAILS. * * * UPDATE 1140EST ON 1/19/00 FROM MATTHEW ARSENAULT TO S.SANDIN * * * THIS REPORT IS BEING RETRACTED BASED ON THE FOLLOWING: "On January 17, 2000, at 6:32 EST, North Atlantic Energy Service Corporation (North Atlantic) submitted a 1-hour report to the Nuclear Regulatory Commission pursuant to 10 CFR 73.71 regarding a Security Officer that was discovered to be inattentive to duty (NRC Event Report 36596). "Subsequent to the report and after a thorough review, it was determined that this incident was loggable and did not meet the criteria for a 1-hour report. Specifically, this condition did not constitute an uncompensated loss as defined in Regulatory Guide 5.62 because the original capability was restored within 10 minutes of discovery of the event. Additionally, consistent with the guidance provided in Generic Letter 91-03, events involving inattentive security personnel can be logged if they are properly compensated for in accordance with Regulatory Guide 5.62 and NUREG-1304. Therefore, North Atlantic retracts the 1-hour report. This event has been captured in the event log." The licensee will inform the NRC resident inspector. Notified R1DO (Hinson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 0
36595 | -1 | VA COMMONWEALTH UNIV. HOSPITAL |  |  |  |  | 2000-01-15 15:30 | 2000-01-16 10:15 | 2000-01-20 | MEDICAL MISADMINISTRATION A patient received a 30% underdose after one of four strands of Ir-192 seeds became dislodged immediately following implantation. The activity of the strands was 7.5 mCi, 8.7 mCi, 6.0 mCi, and 7.6 mCi. (The licensee did not specify which strand became dislodged.) The strand was removed from the patient's bed shortly thereafter when the linen was changed. The licensee is currently reconstructing this event but does not believe that any employee received a significant dose. (Call the NRC operations office for a contact telephone number.) * * * UPDATE 0838 EST ON 1/20/00 FROM MARY BETH TAORMINA TO S. SANDIN * * * The licensee is retracting this report based on a re-evaluation of the patient treatment plan which concluded that the underdose was 15% and, as such, did not meet the 20% criteria for a misadministration. This finding was discussed with Region 2. Notified R2DO (Fredrickson) and NMSS (Moore). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | MED MISADMINISTRATION | [9 empty] | NON EMERGENCY | 2 | VA | HOS |  | 35.33 |  |  |  | 0
36594 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2000-01-11 14:01 | 2000-01-14 17:10 | 2000-01-14 | POSSIBLE COMPUTER PROBLEM WITH HIGH DOSE REMOTE APPLICATOR (Utah Report #00-0001) This is a preliminary report of a possible problem existing with the computer for a Nucletron Corporation, Model 105.999, MicroSelectron-HDR, version 2, remote afterloader brachytherapy device, serial #31062, that could lead to a medical misadministration. This device is located at the University of Utah Medical Center. The problem is being investigated by the vendor, and the problem is thought to be a CPU communication fault. The CPU has been sent to the manufacturer for further testing. Utah has contacted the State of Maryland as well as Nucletron Corporation. (Call the NRC operations officer for a contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | AGREEMENT STATE | [8 empty] | NON EMERGENCY | 4 | UT | OTH | PAR | 21.21 |  |  |  | 0
36593 | 0 | MERCK CO, INC |  |  |  |  | 2000-01-14 10:00 | 2000-01-14 16:08 | 2000-01-14 | FAILURE OF INTERLOCK DISCOVERED DURING NORMAL MAINTENANCE CHECKS During the performance of annual preventative maintenance checks, a technician discovered that one of the interlocks was not functioning. The interlock prevents the source from being raised or exposed with the shield doors open to protect the operator. The device is a J. L. Shepherd Mark-1 Model 30-1 irradiator. The irradiator has been tagged out of service until serviced by the vendor. The room contained audible and visible alarms that were functional, thus any operator would have been alerted if the source had become exposed. The vendor, J. L. Shepherd, has been contacted and expects to have a technician on site next week. (Call the NRC operations officer for a contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0
36592 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2000-01-14 06:00 | 2000-01-14 13:20 | 2000-01-14 | AGREEMENT STATE/TRANSPORTATION EVENT INVOLVING A SPILL OF MALLINCRODT RADIOPHARMACEUTICALS ON A FREEWAY IN THE LOS ANGELES VICINITY At 0600 PST on 01/14/99, the State Highway Patrol informed the California Radiation Control Program of a radiation spill and requested assistance. Apparently, a Mallincrodt radiopharmaceutical delivery vehicle was involved in an accident on the Route-2 Freeway (Glendale Freeway) in the vicinity of Los Angeles (believed to be in the town of Glendale). Prior to the accident, the total radioactive material onboard the delivery vehicle was 1.2 Ci of technetium-99m and 30 mCi of thallium-204. Some of the vehicle's contents were spilled, and some of the containers were broken creating contamination on the freeway. In response to the State Highway Patrol's request for assistance, a California Radiation Control Program Los Angeles staff representative was on the scene by approximately 0630 PST. At the time of this event notification, two of the four lanes had been opened, and traffic was passing through. California Radiation Control Program staff responders were still working to clean the hot spots in the other two lanes. NRC assistance was not requested. The California Radiation Control Program reported that this event was being broadcast by CNN. (Call the NRC operations officer for a California Radiation Control Program contact telephone number.) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | TRANSPORTATION EVENT | [8 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0
36591 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2000-01-14 09:50 | 2000-01-14 11:02 | 2000-01-14 | ELECTRICAL FAULT OF CONTROL ELEMENT DRIVE MECHANISM MOTOR GENERATOR SET (CEDM MG SET) CAUSES A REACTOR TRIP. The reactor automatically tripped, and all rods fully inserted into the core. Preliminary indication is that CEDM MG set #11 had an electrical fault which caused a reactor trip bus undervoltage condition which picked up the undervoltage relays which tripped the main turbine which caused the reactor trip. One of the second stage steam supply valves to the moisture separator reheater failed to close automatically (because the electrical breaker for the valve opened) which required the licensee to close the main steam isolation valves (MSIV). The licensee is maintaining no load T(ave) temperature by dumping steam to the atmosphere via the steam generator atmospheric valves and feeding the steam generators with one of the motor-driven auxiliary feedwater pumps. Neither of the steam generators have any leaking steam generator tubes. The licensee is making preparation to open the MSIVs. All emergency core cooling systems and the emergency diesel generators are fully operable if they are needed. The licensee stated that the electrical grid is stable. The licensee is investigating the event. The NRC resident inspectors were notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36590 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2000-01-14 08:00 | 2000-01-14 09:25 | 2000-01-14 | OFFSITE NOTIFICATION REGARDING HIGH SUSPENDED SOLIDS IN A SEWAGE TREATMENT EFFLUENT SAMPLE A sewage treatment effluent sample taken on 01/03/00 was reported today to have exceeded the suspended solids limit for the maximum daily value allowed by the NPDES Discharge Permit. The licensee plans to inform the Maryland Department of Environment that they exceeded the maximum limit of their NPDES Discharge Permit. The NRC resident inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36589 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-01-13 10:15 | 2000-01-13 17:41 | 2000-01-13 | FITNESS-FOR-DUTY REPORT - A NON-LICENSED EMPLOYEE SUPERVISOR (PLANT EMPLOYEE) WAS DETERMINED TO BE UNDER THE INFLUENCE OF ALCOHOL DURING A FOR-CAUSE TEST. THE SUPERVISOR'S PLANT ACCESS AUTHORIZATION HAS BEEN REVOKED. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. CALL TO THE NRC OPERATIONS OFFICER FOR ADDITIONAL DETAILS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0
36588 | 0 | PERRY | 1 |  |  | [1] GE-6 | 1999-03-25 03:30 | 2000-01-13 17:04 | 2000-02-03 | DISCOVERY THAT A SINGLE PASSIVE FAILURE OF THE INCLINED FUEL TRANSFER SYSTEM FLAP VALVE MAY HAVE RESULTED IN A LOSS OF ECCS DURING A DESIGN BASIS LOCA (HISTORICAL EVENT) The following text is a portion of a facsimile received from the licensee: "With the Inclined Fuel Transfer System (IFTS) flange removed at power, a single passive failure of the IFTS flap valve may have resulted in a loss of Emergency Core Cooling System (ECCS) during a design basis Loss of Coolant Accident (LOCA). This was determined during an engineering review examining the effects on containment structural capability with the IFTS Blind Flange removed." "An assumed single passive failure of the IFTS flap valve would have resulted in inventory loss from the upper containment pools with the IFTS gate removed. The postulated water inventory loss would reduce the inventory to less than required for the makeup to the suppression pool during a LOCA. Therefore, ECCS may not have met single failure criteria during the period when the IFTS Flange was removed at power." "The IFTS flange was removed for approximately 3 days prior to the commencement of the seventh refueling outage. Administrative controls are in place to preclude removal of the IFTS flange at power until this issue is fully evaluated." The licensee stated that this event was determined to be reportable approximately 10 minutes prior to the event notification. The licensee notified the NRC resident inspector. * * * UPDATE ON 02/03/00 AT 1312 BY STERLING SANFORD TAKEN BY STEVE SANDIN * * * The licensee made an editorial correction to the event time to show 0330 hours instead of 1530 hours. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R3DO Tony Vegel. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36587 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2000-01-12 17:49 | 2000-01-13 09:39 | 2000-01-13 | FITNESS-FOR-DUTY REPORT INVOLVING A LICENSED EMPLOYEE A licensed employee was arrested offsite by the Security force for possession of a controlled substance. The licensed employee was released on his own recognizance. The licensed employee notified his supervisor of his arrest, and his access to the protected area was suspended. The licensed employee took a drug test, and the results of the test have not been completed. (Refer to the HOO Log for further details.) | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0
36586 | -1 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-13 03:26 | 2000-01-13 04:21 | 2000-02-02 | ENTERED TECHNICAL SPECIFICATION 3.0.3 FOR 17 MINUTES DUE TO LOW DIFFERENTIAL PRESSURE BETWEEN THE CONTROL ROOM AND THE AUXILIARY BUILDING. A LOW CONTROL ROOM VENTILATION SYSTEM DIFFERENTIAL PRESSURE WAS DISCOVERED WHILE A CONTROL ROOM VENTILATION SYSTEM AND AUXILIARY BUILDING VENTILATION SYSTEM COMPENSATORY ACTION WAS IN EFFECT DUE TO AUXILIARY BUILDING VENTILATION SYSTEM WORK. THE LICENSEE ENTERED TECHNICAL SPECIFICATION 3.0.3 AT 0326 ET. AT 0333 ET, THE LICENSEE SECURED THE '2A' AUXILIARY BUILDING VENTILATION FILTER EXHAUST FAN. TECHNICAL SPECIFICATION 3.0.3 WAS EXITED AT 0343 ET AFTER CONTROL ROOM DIFFERENTIAL PRESSURE WAS VERIFIED ABOVE THE MINIMUM LIMIT. THE NRC RESIDENT INSPECTOR WILL BE NOTIFIED OF THIS EVENT BY THE LICENSEE. * * * UPDATE ON 02/02/00 AT 1644 BY TRUESDALE TO GOULD * * * RETRACTION The determination to declare both trains of the control room area ventilation system (CRAVS) inoperable on 01/13/00 was based on the data from only one of the two CRAVS intakes. At the time this decision was made, the 'A' train of the CRAVS was in operation. When the control room pressure was checked, the only intake alignment that was tested was the Unit 2 intake alignment. No test was performed using the Unit 1 intake for CRAVS. This was done because of how the procedure was written for the control pressure check. A licensee engineering evaluation was performed to review CRAVS test data and alignment before, during and after the event. This evaluation determined that the inability to pressurize the control room to technical specification (TS) surveillance requirement required value of 0.125 inches water gage using the Unit 2 intake caused one CRAVS train (but not both) to be inoperable. The cause of the event was a failed auxiliary building ventilation system supply damper. This supply damper prevented the auxiliary building system from supplying adequate air into the auxiliary building to compensate for the amount of air being exhausted by the auxiliary building system unfiltered and filtered exhaust fans. TS 3.7.10, Action A (restore CRAVS train to OPERABLE status within 7 days), not action E (enter TS 3.0.3 for two CRAVS trains inoperable), should have been followed. The inoperable train was restored to operable status by realigning auxiliary building exhaust and supply fans which restored auxiliary building pressure to normal. Thus, since only one train of CRAVS was inoperable, neither unit was ever in TS LCO 3.0.3 for this event. Therefore, this event is not reportable per 10CFR50.72(b)(l)(ii)(B) and the previous notification is being retracted. In addition, as a result of this event notification retraction, licensee event reporting regarding this issue is not required nor is planned. The licensee notified the NRC Resident Inspector. The NRC Operations Officer notified the R2DO (Kerry Landis). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36585 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-13 00:59 | 2000-01-13 02:55 | 2000-01-13 | SWITCHYARD FAULT RESULTED IN MAIN GENERATOR TRIP/TURBINE TRIP/REACTOR TRIP. At 0059CT, a Reactor Trip occurred on Unit 2. A fault in the switchyard resulted in a Main Generator Trip which caused a Turbine Trip/Reactor Trip. All rods fully inserted into the core. All other systems responded per design with the following exceptions: 1). A Unit 1/Unit 2 Containment Ventilation Actuation occurred (caused by electrical spike in the switchyard). This is not an Engineered Safety feature (ESF) Actuation because all the Containment Ventilation Isolation valves were already closed. 2). A Fuel Handling Building Ventilation ESF Actuation occurred (caused by the electrical spike in the switchyard). 3). An 'A'-Train Main Control Room Makeup Air Filter Unit ESF Actuation occurred (caused by the electrical spike in the switchyard). All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. At this time, the Motor-Driven Auxiliary Feedwater Pump is maintaining proper Steam Generator Water Levels with T(ave) being maintained at a no load temperature of 557°F. The switchyard fault is being investigated. The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36584 | 0 | STATE OF CALIFORNIA |  |  |  |  | 2000-01-10 | 2000-01-12 19:14 | 2000-01-12 | STOLEN CAMPBELL PACIFIC NUCLEAR MOISTURE DENSITY GAUGE ON 1/10, A CAMPBELL PACIFIC NUCLEAR (CPN) MOISTURE DENSITY GAUGE MODEL M, SERIAL NUMBER 36076956, WAS STOLEN FROM A VEHICLE IN IRVINE, CA. THE GAUGE CONTAINS TWO (2) SOURCES (9 mCi Cs-137 AND 40 mCi Am-241: Be). THE LICENSEE, GOFFMAN, McCORMICK AND URBAN, INC. LOCATED IN RANCHO SANTA MARGARITA, CA, REPORTED THE LOSS TO THE STATE OF CALIFORNIA RADIOLOGIC HEALTH BRANCH (INCIDENT #011100) AND THE IRVINE POLICE DEPARTMENT. A REWARD HAS BEEN OFFERED IN THE LOCAL NEWSPAPER. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36583 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-01-12 15:15 | 2000-01-12 17:26 | 2000-01-12 | TRANSPORT OFFSITE OF POTENTIALLY CONTAMINATED INJURED EMPLOYEE "At 1515 on 1/12/2000, an injured contract employee at River Bend Station was transported offsite to the West Feliciana Hospital for medical treatment. The individual was erecting scaffolding in the Turbine Building, fell approximately 20 feet and sustained injuries. The individual was working inside the Controlled Access Area, but not inside a Contaminated Area, and a thorough survey for radioactive contamination could not be performed prior to transport. Therefore, the individual is considered to be potentially contaminated. "In accordance with plant administrative procedures. a radiation protection technician is accompanying the ambulance to the hospital and a second radiation protection technician has been dispatched to the hospital as well." The NRC Resident Inspector was informed. * * * UPDATE 2057EST ON 1/12/2000 FROM ROHM TO S. SANDIN * * * "The injured contract employee has been verified not contaminated. Preliminary medical evaluation revealed no life threatening injuries." The licensee informed the NRC Resident Inspector. Notified R4DO(Shackelford). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(v) |  |  |  | 0
36582 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2000-01-12 14:19 | 2000-01-12 14:52 | 2000-01-12 | UNPLANNED INOPERABILITY OF HIGH PRESSURE CORE SPRAY DUE TO REQUIRED SURVEILLANCE TESTING NOT PERFORMED (TECH. SPEC. 4.3.3.3) "THE REQUIRED RESPONSE TIME TESTING OF HIGH PRESSURE CORE SPRAY SYSTEM ACTUATION INSTRUMENTATION WAS NOT PERFORMED WITH THE TECH SPEC SURVEILLANCE FREQUENCY. THE INSTRUMENTATION HAS BEEN DECLARED INOPERABLE. THE HIGH PRESSURE CORE SPRAY HAS BEEN DECLARED INOPERABLE PER TECH SPEC 3.3.3 ACTION 36b. "WITH HIGH PRESSURE CORE SPRAY INOPERABLE, ENTERED TECH SPEC 3.5.1.c.1 (14 DAY LCO)." THIS IS AN 18-MONTH SURVEILLANCE WHICH WAS LAST PERFORMED MARCH 1997. THE LICENSEE IDENTIFIED THAT AN INCORRECT SURVEILLANCE INTERVAL WAS USED IN THE TRACKING SYSTEM. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | TECH SPEC LCO A/S |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(A) |  |  |  | 0
36581 | 0 | TEST-CON |  |  |  |  | 2000-01-12 08:00 | 2000-01-12 12:19 | 2000-01-12 | STOLEN HUMBOLT MOISTURE DENSITY GAUGE THE RADIATION SAFETY OFFICER (RSO) FOR TEST-CON , LOCATED AT 16 E. FRANKLIN IN DANBURY, CT 06810, REPORTED THAT A HUMBOLT MODEL 5001 MOISTURE DENSITY GAUGE, SERIAL NUMBER 1967, CONTAINING TWO (2) RADIOACTIVE SOURCES [8 mCi Cs-137 AND 40 mCi Am-241:Be) WAS STOLEN FROM A VEHICLE PARKED ON MORRIS AVE IN BRONX, NY. THE DEVICE WAS REMOVED BETWEEN 0500 AND 0700 HOURS ON 1/12 FROM THE TRUNK OF A HYUNDAI AUTO WITH NO VISIBLE SIGN OF FORCED ENTRY. THE LICENSEE INFORMED NRC REGION I AND WILL FILE A POLICE REPORT WITH THE NY CITY PD. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0
36580 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2000-01-11 17:52 | 2000-01-11 22:26 | 2000-01-12 | POSTULATED CONDUCTOR-TO-CONDUCTOR SHORT IN FIRE PUMP CONTROL CIRCUITRY COULD INHIBIT THE ABILITY OF THE PLANT TO SAFELY SHUT DOWN FOLLOWING A FIRE. "During preparation of the permanent plant modification to replace a Temporary Modification associated with LER 96-009-03, another configuration was found that could inhibit the ability of the plant to safely shutdown following a fire. For an Alternate Shutdown Fire (10 CFR 50 Appendix R Section III.L) in the Cable Spreading Room fire area, the Diesel Fire pump is relied upon to provide emergency backup gland seal water to the essential service water pumps. A fire scenario in the cable spreading room assumes of a loss of offsite power (which disables the normal gland water supply) as well as concurrent hot shorts which disable the emergency gland seal water supply MOV's (because their control cables are routed through the Cable Spreading Room). A multi-conductor cable located in the Cable Spreading Room carries 24 VDC start control circuits and 120 VAC annunciator power circuits. The postulated fire scenario requires the assumption that the fire could cause a conductor to conductor short within this cable such that the 24 VDC circuits would be energized by the 120 VAC power. This would disable the automatic starting capability of the diesel fire pump (the currently credited emergency backup gland seat water). A fire watch has been posted in the Cable Spreading Room as a compensatory measure. The Cable Spreading Room fire area is the only fire area affected by this configuration. The operator's ability to recognize and correct a loss of gland water to the Service Water pumps would not be impaired. Sufficient procedural guidance is provided for the post-fire restoration of the essential service water pumps such that loss of gland seal water would have been detected prior to service water pump damage. Fire fighting activities would have immediately indicated loss of the fire pump. A modification to separate the starting circuits from the power circuits is being pursued. CNS has conservatively concluded that this postulated scenario is reportable under 10CFR50. 72(b)(2)(iii)(A). "The NRC Resident Inspector has been notified." * * * UPDATE 1833EST ON 1/12/00 FROM STEVEN JOBE TO S. SANDIN * * * "Per the requirements of 10 CFR 50.72 (c) (2), the licensee is providing the following additional information. "The 120 VAC annunciator power circuits referred to in the initial report are more appropriately described as indicating lamp power circuits. "As additional clarification, the diesel fire pump running capability would be disabled along with the automatic starting capability. "Based on further investigation, the licensee has determined that insufficient time exists to recognize and correct the loss of gland seal water prior to the onset of service water pump damage. "The compensatory measures described in the initial report (posting of fire watch) are still in place. These measures, in conjunction with the defense in depth fire protection program, are adequate to ensure the ability of the plant to safely shutdown following a fire, and are consistent with the facility license and the guidance of Information Notice 97-78 'Inadequate or Inappropriate Interim Fire Protection Compensatory Measures." "Evaluation of this postulated scenario is ongoing and additional action will be taken as appropriate. "The Senior Resident lnspector has been notified." Notified R4DO(Shackelford). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iii)(A) |  |  |  | 0
36579 | 0 | WNP-2 | 2 |  |  | [2] GE-5 | 2000-01-11 09:50 | 2000-01-11 13:47 | 2000-01-11 | 1-HOUR REPORT INVOLVING THE LOSS OF THE DEDICATED LAND LINES TO STATE/LOCAL AGENCIES FOR REASONS UNKNOWN. "THE DEDICATED TELEPHONE COMMUNICATION LINK TO STATE AND LOCAL AGENCIES IS LOST. NO PROJECTED TIME OF REPAIR." THE LICENSEE INFORMED STATE/LOCAL AGENCIES AND WILL INFORM THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36578 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2000-01-10 | 2000-01-10 17:10 | 2000-08-11 | AGREEMENT STATE REPORT INVOLVING STOLEN TROXLER 3430 MOISTURE DENSITY GAUGE "Troxler Model 3430, Serial # 27239, stolen January 9/10, 2000, from 605 East Safari Parkway, D-2, Mesquite, Texas. The gauge contained two radioactive sources: 8 millicurie (nominal activity) Cs-137 source, Serial # 750-976 and 40 millicurie (nominal activity) Am-241:Be source, Serial # 47-23865. Stolen from a parked Ford Ranger pickup truck belonging to the machines operator during the hours of darkness January 9/10, 2000. Gauge had been locked in the pickup's cab and covered by a jacket or blanket. Listed as Texas Incident 7561 Texas Licensee L05233 is based in Houston and had been performing work at a jobsite in East Fort Worth. Reported as missing to the Mesquite Fire Department January 10, 2000. Further details pending contact with company R.S.O." * * * UPDATE 1632 8/9/2000 FROM OGDEN (VIA FAX) INPUT BY STRANSKY * * * "Troxler Model 3430 was discovered in a garbage truck that set off radiation monitors at a local Dallas-Fort Worth landfill. The gauge was discovered in the back of the garbage truck operated by Duncan Disposal, 1220 Dowdy Ferry Road, Hutchins, Texas. It is believed that the gauge was picked up from apartment dumpsters located in the City of Seagoville. "The gauge is Serial Number: 27239 which was stolen in Mesquite, Texas on the evening of January 9/10, 2000. The gauge appears to be undamaged but is not in its transportation case which was taken during the theft. The Texas Licensee from whom the gauge was stolen is Petra Technologies Incorporated, Texas License # L05233. This licensee is currently in the process of revocation for failure to pay fees. All known phone numbers for the firm have been disconnected, therefore, and no one has yet been contacted within the firm. "Troxler both in North Carolina and in Arlington have been notified. "Texas Department of Health, Region 3 (Arlington) Bureau of Radiation Control personnel have picked-up the gauge from the disposal firm and have it secured at regional headquarters. The gauge appears to be intact. The gauge will be leak tested by Troxler's Arlington location." * * * UPDATED ON 08/11/00 AT 1035 EDT BY JAMES H. OGDEN (VIA FAX) INPUT BY MACKINNON * * * "The gauge has been placed in storage at the Texas Department of Health, Region 3 (Arlington) by Bureau of Radiation Control personnel until picked up by the licensee (Petra Engineering). "The licensee was contacted on August 10, 2000, and informed of the recovery of the gauge. Revocation of the licensee's current Radioactive Materials License has been placed on hold due to the supposed mailing of payment of overdue fees. The licensee has also reorganized operations during the period January - April 2000 which involved changing the licensee's names. An amendment to the firm's license is necessary before the gauge will be returned." NRC R4DO (Kriss Kennedy) & NMSS EO (Brian Smith) notified by the NRC Operations Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36577 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2000-01-10 06:45 | 2000-01-10 15:30 | 2000-01-10 | 24-HOUR NRC 91-01 BULLETIN REPORT INVOLVING THE LOSS OF GEOMETRY CONTROL DURING FEED PRESS OPERATION "At approximately 0645 on January 10, 2000, during routine operations surveillance, operators discovered a mechanical failure inside an enclosed press feed station. The Silletta feeder assembly rubber boot de-coupled from the lower metal pipe and allowed UO2 powder to spill inside the dump hood. The spill resulted in a loss of geometry. Moderation control remained intact, thus no unsafe condition existed. "Controls were reestablished within 4 hours, by cleanup of the spilled material and placement into favorable geometry 3-gallon containers. This event is reported pursuant to NRC Bulletin 91-01 (within 24 hours) due to loss of geometry control. The gad press feed station has been shutdown pending investigation and implementation of corrective actions. "SAFETY SIGNIFICANCE OF EVENTS: Low safety significance - actual powder spill occurred inside hood containment - moderation control remained intact. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): Multiple failure modes required before a criticality accident could occur. "CONTROLLED PARAMETER(S) (MASS, MODERATION, GEOMETRY. CONCENTRATION. ETC.): Geometry - analyzed safe geometry equipment; Moderation - limited to dry UO2 powder (not more than 50,000 ppm H2O equivalent moderation) "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Net UO2 spilled material removed was 75.13 kg (2.97% enrichment) with 5,211 ppm H2O actual moderator content. Moderation control remained intact - safe hemisphere mass at 50,000 ppm H2O is ~600 kgs UO2 (at 5.00% U235 enrichment). "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Geometry control on the rubber boot clamp and cable lanyards failed, allowing rubber boot to de-couple from feed pipe. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Gad press feed station shutdown. 2. NSE direction of spilled material removal. 3. Investigation and implementation of corrective actions pending." The licensee will inform both local/state representatives and the Region II based Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0
36576 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2000-01-10 11:45 | 2000-01-10 14:02 | 2000-01-10 | AUTOSTART OF THE "1B" EMERGENCY DIESEL GENERATOR DUE TO THE UNEXPECTED LOSS OF THE "A" AUXILIARY TRANSFORMER THE "1B" EMERGENCY DIESEL GENERATOR AUTOSTARTED AND LOADED FOLLOWING THE LOSS OF THE "A" AUXILIARY TRANSFORMER. A PRELIMINARY INVESTIGATION ATTRIBUTES THE CAUSE TO AN INVALID SIGNAL FROM THE TRANSFORMER FAULT PRESSURE RELAY. TROUBLESHOOTING IS CURRENTLY IN PROGRESS INCLUDING ANALYSIS OF THE TRANSFORMER OIL. BASED ON THE RESULTS OF THE ONGOING INVESTIGATION, THE LICENSEE TENTATIVELY PLANS TO RETURN THE TRANSFORMER TO SERVICE AND SECURE THE EDG LATER TODAY. THE LICENSEE INFORMED THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36575 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2000-01-10 13:20 | 2000-01-10 13:30 | 2000-01-10 | LICENSEE NOTIFIED THE STATE OF MAINE OF AN UNSCHEDULED LIQUID RAD RELEASE BETWEEN 1600 HOURS ON 1/7/2000 AND 0700 HOURS ON 1/8/2000 A DECOMMISSIONING CONTRACTOR WAS FILLING THE CONTAINMENT EQUIPMENT HATCH PIT WITH TOWN WATER. THE PIT LEAKED APPROXIMATELY 5500 GALLONS OF WATER WHICH CONTAINED AN ESTIMATED 0.01 CURIES TOTAL ACTIVITY (Co-60 AND Cs-137). THE LICENSEE NOTIFIED THE STATE OF MAINE AND WILL INFORM THE NRC REGION I OFFICE. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(vi) |  |  |  | 0
36574 | 0 | WASHINGTON DEPT OF HEALTH |  |  |  |  | 2000-01-07 | 2000-01-10 09:15 | 2000-01-10 | STOLEN TROXLER GAUGE. A MODEL 3440 TROXLER GAUGE, SERIAL # 19036 CONTAINING 8 MILLICURIES OF Cs-137 AND 40 MILLICURIES OF Am-241/Be, WAS STOLEN FROM A GAUGE OPERATOR'S TRUCK AFTER HE HAD TAKEN IT HOME FOR THE NIGHT. THE GAUGE WAS LEFT CHAINED TO THE PICKUP ALL NIGHT AND THE OPERATOR DID NOT DISCOVER IT WAS MISSING UNTIL HE WAS HALF WAY TO THE JOB SITE THE NEXT MORNING. THE POLICE WERE NOTIFIED AND BY MID-AFTERNOON, TWO INDIVIDUALS HAD BEEN ARRESTED AND THE GAUGE WAS RETURNED TO THE LICENSEE. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0
36573 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2000-01-08 16:31 | 2000-01-08 19:58 | 2000-01-08 | TURBINE TRIP FOR UNKNOWN REASONS RESULTING IN AN AUTOMATIC REACTOR SCRAM The following text is a portion of a facsimile received from the licensee: "At 1631, Unit 2 received a main turbine trip signal and [an automatic] reactor scram [from 100% power.] All systems operated as designed. The investigation into the turbine trip is ongoing. There was no release of radiation to the environment." The licensee stated that all rods fully inserted upon receipt of the reactor scram. There was no pressure transient. Reactor vessel level decreased to approximately +10" and recovered to approximately +30". (The reactor scram setpoint is at +12.5", and the emergency core cooling system actuation setpoint is at -38".) There were no engineered safety feature (ESF) actuations (other than the reactor scram), and none were required. The licensee also stated that there were no turbine-related maintenance or surveillance activities ongoing at the time of the event. An AC bus outage was commenced the previous night. The unit is currently stable in Mode 3 (Hot Shutdown). Normal condensate and feedwater is being supplied to the reactor vessel, and steam is being dumped to the main condenser. There was no adverse effect on containment parameters. The licensee notified the NRC resident inspector as well as applicable state and local agencies. ******************** UPDATE AT 2338 ON 01/08/00 FROM PHIL CHASE TO LEIGH TROCINE ******************** The licensee updated this event notification to clarify that there was an ESF actuation. The end of cycle recirculation pump trip breakers opened as designed on the turbine trip. The NRC operations officer notified the R1DO (Meyer). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36572 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2000-01-07 18:07 | 2000-01-07 21:24 | 2000-01-07 | LOSS OF TRANSFORMER XST1 (ONE OF TWO OFFSITE POWER SOURCES TO THE CLASS-1E BUSES) The following text is a portion of a facsimile received from the licensee: "At 1807 CST, Comanche Peak experienced a loss of power to transformer XST1 (one of two offsite power sources to class 1E buses). Unit 2 momentarily [lost] power to [the] train 'A' and 'B' safeguards buses due to the [automatic] transfer to alternate offsite power. [The] train 'A' and 'B' blackout sequencers operated to realign [engineered safety feature (ESF)] equipment. [The] train 'A,' [train] 'B,' and turbine-driven auxiliary feedwater pumps started due to the blackout signal. All safeguards equipment responded as designed." "Currently, ESF equipment has been restored to a normal lineup[, and transformer] XST2 is supplying offsite [Class-1E] power to [both Units] 1 and 2. An investigation into the cause of the event is in progress." "The NRC resident inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ESF ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36571 | 0 | HOWARD UNIVERSITY |  |  |  |  | 2000-01-07 16:00 | 2000-01-07 16:45 | 2000-01-07 | INFORMATION REPORT REGARDING A FAILURE TO FOLLOW PROCEDURES FOR RECEIPT OF RADIOACTIVE MATERIAL (3 mCi OF TRITIUM) AT HOWARD UNIVERSITY IN WASHINGTON D.C. On 07/02/99, 3 mCi of tritium was transferred from George Washington University to Howard University using a private vehicle, and the Radiation Safety Office at Howard University was not notified until today (01/07/00) at 1630. An individual brought the material with him when he transferred from George Washington University to Howard University and locked the material in a laboratory. Apparently, this individual had the mistaken understanding that the material could remain in his laboratory until he became an authorized user. After completing his training and becoming an authorized user, the individual informed the Radiation Safety Officer at Howard University (on 01/02/00) that he had brought 3 mCi of tritium with him from George Washington University (on 07/02/99). The licensee stated that all of the paperwork for the transfer of the material was in order and that the Radiation Safety Office at George Washington University was informed of the transfer of radioactive material at the time of the transfer. Between 07/02/99 and 01/02/00, the tritium was locked in a laboratory at Howard University. It was still in its original container. Call the NRC operations officer for a licensee contact telephone number. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | DC | MAT | [5 empty] | 0
36570 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2000-01-07 12:00 | 2000-01-07 15:51 | 2000-01-13 | OBSERVATION OF UNUSUAL CAVITATION NOISE AND VIBRATION OF THE HIGH PRESSURE CORE SPRAY (HPCS) PUMP DURING QUARTERLY INSERVICE TESTING (IST) The following text is a portion of a facsimile received from the licensee: "During the quarterly IST surveillance on the high pressure core spray pump, unusual cavitation noise and vibration was observed. Abnormal low suction pressure alarms were also noted. These conditions could not be explained, and therefore, the high pressure core spray pump was declared inoperable, and plant engineering was contacted to investigate. The data collected on the surveillance test was satisfactory including vibration readings. The abnormal conditions were noted during system realignment for continuation of the testing." The cause of the unusual cavitation noise and vibration of the high pressure core spray pump is currently under investigation. In accordance with Technical Specification 3.5.1, the reactor core isolation cooling system was verified to be operable within one hour. Technical Specification 3.5.1 also requires the licensee to restore the high pressure core spray system to an operable status within 14 days or place the unit in Cold Shutdown. The licensee stated that all other emergency core cooling systems are currently operable. The licensee notified the NRC resident inspector. * * * UPDATE AT 1826 ON 01/13/00 FROM MARK FELTNER TO JOLLIFFE * * * Following the identification of the above condition, licensee actions were taken to investigate the reported deficiency. A loop calibration was performed on the HPCS pump suction transmitter with no abnormal conditions identified. The HPCS pump was run in a variety of configurations including the configuration that produced the original event, and all the data obtained was satisfactory. During each of these runs no abnormal noise, vibrations or pump characteristics were noted. Based on the observed condition and the additional data obtained, a determination was made that the pump did not experience cavitation conditions for more than a short period of time (5 to 8 seconds) if at all. This, coupled with information obtained from the pump vendor, the subsequent successful performance of multiple pump runs, successful calibration of the suction pressure transmitter, and the lack of any abnormal noise or vibration; provides assurance that the HPCS pump is capable of performing its intended safety function. Based on this information, the licensee determined that this condition is not reportable to the NRC and desires to retract this report. The licensee plans to notify the NRC resident inspector. The NRC Operations Officer notified the R4DO Jeff Shackelford. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36569 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2000-01-07 08:29 | 2000-01-07 10:58 | 2000-01-07 | UNIT ENTERED TECH SPEC 3.0.3 AFTER BOTH SUBSYSTEMS OF THE LOW PRESSURE COOLANT INJECTION (LPCI) SYSTEM WERE RENDERED INOPERABLE DURING MAINTENANCE ACTIVITIES. "At 0829 on 1/7/2000, the E1150-F015A Division I Low Pressure Core Injection (LPCI) Inboard Isolation Valve lost power. The Fermi 2 Accident Analysis takes credit for the operation of the E1150-F015A with the initiation of 'LPCI Loop Select Logic,' to inject with both divisions of LPCI during a [loss of coolant accident (LOCA)]. With the E1150-F015A inoperable, both Division 1 and Division 2 LPCI subsystems were declared Inoperable. T.S. 3.5.1 and T.S. 3.0.3 were immediately entered. Operators were dispatched to the [motor control center (MCC)] area and reported that MCC 72CF position 2C was in the open position. [An] operator noted maintenance activities in the area and no damage to the MCC. "At 0837, the MCC was re-energized, restoring power to the E1150-F015A, and T.S. 3.5.1 and 3.0.3 were exited. Currently, all maintenance activities in the vicinity of the MCC area have been put on hold pending investigation. "During the time of this event, [the] Division I Core Spray System was in a scheduled maintenance outage. "This event is being reported under 10CFR50.72(b)(2)(iii)(D), 'Any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems needed to: D) Mitigate the consequences of an accident'." The licensee informed the NRC resident inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iii)(D) |  |  |  | 0
36568 | 0 | WATERFORD | 3 |  |  | [3] CE | 2000-01-07 07:30 | 2000-01-07 09:29 | 2000-01-07 | DISCOVERY THAT FIRE SYSTEM FPM-18 HAD BEEN OPERATING OUTSIDE THE PLANT DESIGN BASIS "[At 0730 CST on 01/07/00], with the plant operating at 100% power, the licensee determined that Fire System FPM-18 had been operating outside the plant design basis due to having a sprinkler system pressure and flow demand that could exceed the water supply capability (fire pumps). [Fire] System FPM-18 was found to be deficient by over 170 psi. The fire area (RAB-6) is an electrical penetration area located at the +35[-foot elevation] of the Reactor Auxiliary [Building]. This area has cables from both trains located therein. The 'B' Train is the protected train, with [1-hour] fire wrap. This area is also provided with [fire] detection and suppression. Ongoing determinations found the fire loading in the fire area to exceed the [1-hour] fire rating of the cable fire wrap. At that point, it was determined that a fire in that area could result in not being able to achieve safe shutdown. The system had been declared inoperable on [01/05/00,] and compensatory measures [including the posting of a continuous fire watch] were established. There was no actual fire event involved, so there had been no actual impact on health and safety as a result of this condition." The licensee notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0
36567 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2000-01-06 16:11 | 2000-01-06 19:16 | 2000-01-06 | MANUAL REACTOR TRIP DUE TO LOSS OF A FEEDWATER PUMP AND DEGRADED FEEDWATER PUMP SUCTION WHICH RESULTED FROM THE ISOLATION OF THE LOW PRESSURE FEEDWATER HEATER STRINGS The following text is a portion of a facsimile received from the licensee: "At 1611, a manual reactor trip was performed due to loss of [the #]12 steam generator [feedwater] pump (SGFP) and degraded SGFP suction pressure. At approximately the same time, [the #]11 SGFP also tripped. The secondary transient was due to isolation of the low pressure feedwater heater strings. An [auxiliary] feedwater (AFW) [automatic] start signal was received due to low [steam generator] level due to normal shrink. All safety systems performed as designed except for [the #]12 AFW [pump] and source range N-31. No flow was observed from [the #]12 AFW [pump,] and operators manually initiated flow from the control room by depressing [the] low pressure override defeat. [The #]13 AFW pump started and fed all four [steam generators] as designed, and [the #]11 AFW [pump] started and delivered flow to [two] steam generators as designed. Source range N-31 was erratic when it automatically energized. At this time, the unit is stable in Mode 3." The licensee stated that all control rod fully inserted as a result of the manual reactor trip, and none of the primary or secondary safety relief valves lifted. There were no related maintenance or surveillance activities ongoing at the time of the event. The causes of the issues mentioned above are currently under investigation. The licensee stated that (with the exception of the items previously mentioned) all systems functioned as required and that there was nothing unusual or misunderstood. The unit is currently stable in Mode 3 (Hot Standby). Normal charging and letdown, pressurizer heaters and sprays, and the reactor coolant pumps are currently being utilized to maintain primary system inventory, pressure, and transport control. Secondary steam is being dumped to the condenser, and AFW is being supplied to the steam generators. The licensee notified the NRC resident inspector, and the Lower Alloways Creek Township. The licensee plans to notify the State of New Jersey and also plans to issue a media/press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36566 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2000-01-06 09:23 | 2000-01-06 11:16 | 2000-01-06 | LICENSEE UNABLE TO ESTABLISH AN ERDS CONNECTION FOR > 1 HOUR DURING SURVEILLANCE TESTING. "ON JANUARY 6, 2000, [HOPE CREEK PERSONNEL] MADE [A] PROCEDURAL NOTIFICATION TO [THE] NRC OF THE COMMENCEMENT OF THE QUARTERLY EMERGENCY RESPONSE DATA SYSTEM (ERDS) TEST AT 0855 [HOURS]. THE TEST IS PERFORMED IN ACCORDANCE WITH [THE] EMERGENCY PLAN IMPLEMENTING PROCEDURE - EPIP 1008. DURING THE PERFORMANCE OF THE TESTING, THE PREVIOUSLY NOTIFIED NRC CONTACT CALLED THE HOPE CREEK CONTROL ROOM AT 0923 HOURS AND STATED THAT THEY WERE NOT RECEIVING ANY DATA, BUT [THEY] DID VERIFY [THAT THE] SYSTEM WAS ATTEMPTING TO CONNECT. "[THE] HOPE CREEK EMERGENCY CLASSIFICATION GUIDE DETAILS [THAT THE] LOSS OF THE NRC PHONE LINE OR MODEM USED FOR ERDS DATA TRANSMISSION FOR GREATER THAN 1 HOUR AS A 1-HOUR REPORT. TROUBLESHOOTING IS IN PROGRESS. "NO OTHER SIGNIFICANT ISSUES EXIST AT STATION HOPE CREEK." * * * UPDATE AT 1138 EST ON 01/06/2000 FROM BOYLE TO S. SANDIN * * * THE ERDS LINK WAS ESTABLISHED AT 1130 EST. TESTING IS CURRENTLY IN PROGRESS. THE LICENSEE WILL INFORM THE NRC RESIDENT INSPECTOR. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36565 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2000-01-05 12:09 | 2000-01-05 15:30 | 2000-01-05 | REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL DURING RESTORATION OF REACTOR VESSEL WIDE RANGE LEVEL INSTRUMENTATION "During the performance of Surveillance Test Procedure 3.3.3.2-01, Remote Shutdown System Instrument Calibration, an instrument technician was restoring the wide range (flood-up) reactor vessel level instrument which resulted in a level transient for the 'A' and 'B' reactor vessel narrow range level instruments which share a common reference leg. The level transient resulted in a Reactor SCRAM on reactor vessel low level and a Turbine trip on reactor vessel high level. All rods fully inserted into the core. Upon receipt of the low level (170 inches), Group 2 (RHR sump & Drywell drains, etc.), Group 3 (Reactor Building Isolation), and Group 4 (Primary Containment Isolation Signal for Shutdown Cooling) isolations were completed. However, a Reactor Water Cleanup partial isolation was initiated as well. The Reactor Operator as directed by the Shift Supervisor took the isolation to completion. The cause of this partial isolation is still under investigation at this time." "Subsequent to the reactor SCRAM, a Reactor Feed Pump and High Pressure Coolant Injection (HPCI) turbine high level trip occurred (HPCI was not running at this time) and the "A" Reactor Recirculation Pump failed to run back to minimum speed. It was further recognized that a Fuel Pool Cooling pump had tripped but the cause of that trip is still under investigation. Reactor Vessel Level as indicated on the GEMAC Level Indicators was downscale. The plant is at a normal level band with pressure and temperature stable." The high level turbine trip was caused by the Reactor Feed Regulating Valve not going fully closed. No Safety Relief Valves opened and the offsite electrical grid is stable. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION | ESF ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(ii) | 50.72(b)(2)(ii) |  |  | 0
36564 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2000-01-05 11:50 | 2000-01-05 13:48 | 2000-01-05 | EMERGENCY SIRENS INOPERABLE. DURING THE MONTHLY TEST OF THE EMERGENCY SIREN NOTIFICATION SYSTEM, THE LICENSEE EXPERIENCED A 59% LOSS OF CAPACITY. THE PROBLEM APPEARS TO BE ASSOCIATED WITH THE INITIATION EQUIPMENT NOT THE REMOTE RECEIVER OR EQUIPMENT. A CALL FOR EQUIPMENT REPAIR HAS BEEN PLACED AND REPAIRS SHOULD BE COMPLETED BY THE END OF THE WORKDAY. A FULL FUNCTION TEST OF A SECONDARY REMOTE LOCATION WAS SATISFACTORY. THE NRC RESIDENT INSPECTOR WAS NOTIFIED. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36563 | 0 | ADVANCED INPUT DEVICES |  |  |  |  | 2000-01-05 | 2000-01-05 13:47 | 2000-01-05 | MISSING 10 MILLICURIE POLONIUM-210 STATIC IONIZER ELIMINATOR CARTRIDGE On 03/14/99, Advanced Input Devices Company moved to a new location. A box containing one polonium-210 static ionizer eliminator cartridge was shipped to the new office and the box apparently got lost during the move. The caller discovered that the ionizer eliminator was missing since last week and that the box ended up in a land fill. The model P-2021 series static ionizer eliminator cartridge, made by NDR, Grand Island, NY, contained 10 millicuries of polonium-210. The static ionizer eliminator is used to remove static from the air at their printing company. The caller has already relayed the above information to NRC Region 4 Jeffrey Cruz. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0
36562 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2000-01-05 11:30 | 2000-01-05 12:34 | 2000-01-05 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) INOPERABLE (NOT Y2K RELATED) Clinton Power Station's SPDS was determined to be inoperable at 0400 CST on 01/05/00 due to the loss of computer points utilized in the SPDS for determining Emergency Operating Procedure entry conditions. At 1130 CST on 01/05/00, the licensee determined that the extent of repairs to restore the SPDS function would take longer than 8 hours. Thus, based on the potential unavailability of the SPDS function for longer than 8 hours, this condition is being reported pursuant to 10CFR50.72(b)(1)(v). This problem has no apparent link to transition to Y2K issues. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1743 ON 01/05/00 FROM HALVERSON TAKEN BY MACKINNON * * * SPDS returned to service at 1605 CST on 01/05/00. R3DO (Madera) notified. The NRC Resident Inspector was notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER ASMT/COMM INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36561 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2000-01-04 12:50 | 2000-01-04 14:34 | 2000-01-04 | EMERGENCY OFFSITE SIRENS INOPERABLE On 01/03/00 at 0557 ET twelve emergency notification sirens were inoperable due to a loss of power to the sirens. Power was restored to all of the sirens by 0714 ET on 01/03/00. This item was not identified until 01/04/00 at 1250 ET when the licensee performed a printout of their emergency offsite sirens status at the EOF. The power loss was due to an insulator breakdown on a transformer on the CP&L system. Other means of warning the public were available. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY SIREN INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(1)(v) |  |  |  | 0
36560 | 0 | WASHINGTON DEPARTMENT OF HEALTH |  |  |  |  | 1999-12-19 | 2000-01-04 10:40 | 2000-01-04 | AGREEMENT STATE REPORT - INDUSTRIAL RADIOGRAPHY CAMERA AUTO-LOCKING MECHANISM FAILED THIS EVENT WAS E-MAILED TO THE HEADQUARTERS OPERATION CENTER "This is notification of an event in Washington state as reported to the WA Department of Health, Division of Radiation Protection. STATUS: new Licensee: Inspection Service Inc. City and state: Kennewick, WA License number: WN-IR064-1 Type of license: Industrial Radiography Date of event: December 19, 1999 Location of Event: Pasco, WA ABSTRACT: The auto-locking mechanism malfunctioned on an INC model IR 100 industrial radiography camera containing approximately 25 Curies of Ir-192. The malfunction was detected during the radiographer's survey of the circumference of the camera following the completion of a shot when approximately 500 mRem per hour was noted at the exit port of the camera. Upon cranking in the source, the radiographer had observed the "plunger" drop into position indicating the source had been fully retracted and the auto-locking mechanism engaged. Upon reaching the camera the radiographer key-locked the camera while initiating the required circumference survey. Once locked, the key could not be moved to unlock the camera. The radiographer discovered that the source was not fully shielded and was not locked in place. The camera could not be unlocked to crank the source the extra one eighth turn needed to fully shield the source although it could be cranked out. The manufacturer was contacted and a procedure obtained for by-passing the locking mechanism. The licensee was told by the manufacturer that this type of event is 'extremely rare but it does happen'. Using the procedure supplied by the manufacturer, the licensee was able to remove the locking assembly, free the key lock, re-set the auto-lock, re-assemble the mechanism and retract the source into its fully shielded position. No unusual exposures were received by any personnel involved during this event or the successful completion of this operation. What is the notification or reporting criteria involved? Equipment malfunction: inability to retract source to fully shielded position and secure it in this position. Activity and isotope(s) involved: 25 curies of Ir-192 Overexposures? NONE Device (HDR, etc.) Mfg., Model; computer code: I.N.C. model IR 100, serial number 4495" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | EQUIP DISABLED/FAILS | [8 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  | 30.50(b)(2)(ii) |  |  | 0
36559 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 1999-12-30 04:00 | 2000-01-04 09:10 | 2000-01-04 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following text is a portion of a facsimile received from the Texas Department of Health: "Troxler Model 3411-B, Serial # 10518, stolen December 30, 1999, between 4 and 4:30 p.m. along with a company pickup truck (1995, White Isuzu Pup with markings Terra-Mar, Inc. on both doors, License Plate # SL9314). Reported by Texas Licensee: Terra-Mar, Inc., 2402 Gravel Drive, Fort Worth, Texas 76118-6935. Gauge includes two radioactive sources: 1) Am-241:Be, 40 millicuries, Serial # 46-1940; and 2) C-137, 8.4 millicuries, Serial # 40-7844. Completed work Thursday and departed worksite at Carlswell Naval Reserve Base, Texas Army National Guard, Fuel Hanger site and departed. Truck and operator have not been seen since. Suspected by firm that the primary theft was for the vehicle for the holiday weekend. A new operator /technician is the primary suspect in the theft of both the gauge and vehicle. Neither truck nor gauge have been located. The theft has been reported to Fort Worth Police Department (Report # 00006249) and the Texas Department of Public Safety. A copy of the report is not yet available." (Call the NRC Operations Center for a contact telephone number and address.) *** UPDATE ON 01/04/00 AT 1705 ET FROM JAMES OGDEN TAKEN BY MACKINNON *** The Troxler Model 3411-B, Serial # 10518, stolen December 30, 1999, from Fort Worth, Texas , has been recovered today (January 4, 2000) and appears to be intact. The gauge is currently being leak tested by the licensee. NRC R4DO (Chuck Cain) and NMSS EO ( John Hickey) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  | 20.2201(a)(1)(i) |  |  | 0
36558 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2000-01-03 14:45 | 2000-01-03 16:14 | 2000-01-25 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE. During Technical Specification required surveillance testing an oil leak was detected on a fitting in the HPCI hydraulic governor control system (EGR actuator). It was determined that had this leak developed during accident conditions, the HPCI system may not have been able to perform it's intended function for the duration of time required. The licensee entered the appropriate Technical Specification for declaring HPCI inoperable (7 day Limiting Condition of Operation). All other Emergency Core Cooling Systems and the Reactor Core Isolation Cooling system are fully operable if needed. The licensee is preparing to repair the HPCI hydraulic governor control system oil leak. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED AT 1412 EST ON 1/25/00 BY JAMES COSTEDIO TO FANGIE JONES * * * The licensee has performed an engineering evaluation of the reported oil leak and determined that the amount of oil expected to be lost as a result would not have resulted in inadequate oil level. HPCI would have been able to perform its intended function for the duration of time required. Therefore, this event notification has been retracted. The licensee notified the NRC Resident Inspector. The R1DO (John Rogge) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION | TECH SPEC LCO A/S |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iii)(B) | 50.72(b)(2)(iii)(D) |  |  | 0
36557 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2000-01-03 12:57 | 2000-01-03 14:13 | 2000-01-03 | MANUAL TURBINE TRIP FROM 28% CAUSED AN AUTOMATIC REACTOR TRIP Unit 3 was initially at 100% power level when a Stator Coolant Runback initiated due to High Stator Coolant Temperature. Turbine Runback to 0 MWe with Reactor power at approximately 28% power. The Turbine was manually tripped and the Reactor automatically tripped on Turbine to Reactor anticipatory Trip. All rods fully inserted into the core. A couple of Once Through Steam Generator Safety Relief Valves opened/closed. Main Feedwater Water remained inservice and steam is being dumped to the condenser to maintain a Tave no load condition. All Emergency Core Cooling systems, Diesel generator, and their Keowee system are fully operable if needed. The licensee believes that the Stator Water Cooling Temperature Control Valve (TCV) failed closed which caused the Stator water to bypass its coolers. The licensee also stated that it took approximately 3 to 4 minutes to reduce reactor power from 100% to 28% at which point the Turbine was manually tripped. The operators believed they were below the Turbine trip/Reactor Trip setpoint when the Main Turbine was manually tripped. One of the three Turbine Trip/Reactor Trip setpoint bypasses was bypassed but the other two were right on their bypass setpoint when the Turbine was manually tripped. The NRC Resident Inspector was notified of this event by the licensee. *** UPDATE ON 01/03/00 AT 1640 HOURS FROM DUNTON TAKEN BY MACKINNON *** The licensee revised the above event report to state that the Turbine was manually tripped at 55% reactor power by orders of the SRO because of potential electrical damage to the generator. Therefore the licensee was expecting the reactor to automatically trip when the Turbine was manually tripped. R2DO (Chris Christensen) notified. NRC Resident Inspector was notified of this update by the licensee. | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(ii) |  |  |  | 0
36556 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2000-01-03 11:20 | 2000-01-03 12:33 | 2000-01-03 | "C" CHARGING PUMP APPENDIX "R" CONCERN During the Appendix "R" rebaselining project it was discovered that the Unit 2 "C" charging pump (Positive Displacement Pump) may require replacement of a control power fuse for the equipment to be available following certain postulated fires. 10CFR 50 Appendix "R" does not allow repair of hot shutdown equipment. The replacement of fuses is considered a repair. The "C" charging pump is relied on for Unit 2 charging following certain postulated fires. This situation could potentially leave Unit 2 without any charging pumps following certain postulated fires which would be outside the plants Appendix "R" design basis. Fire rounds will be instituted in affected fire zones until this issue is resolved. The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OUTSIDE DESIGN BASIS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(1)(ii)(B) |  |  |  | 0