52746 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2017-04-26 | 2017-05-11 12:16 | 2017-05-11 | AGREEMENT STATE REPORT - IMPROPER SHIPPING PACKAGE LABELS The following information was received from the State of New Jersey via facsimile: "Notifications: Phone call was made to the State of New Jersey Department of Environmental Protection [NJDEP] Bureau of Environmental Radiation on 5/10/17. The event occurred on 4/26/17. "Event Description: PADEP [Pennsylvania Department of Environmental Protection] staff notified NJDEP staff of a package that was transported by a [New Jersey] pharmacy from a [Pennsylvania] nuclear medicine office. It appears that the package was accompanied by an inaccurate bill of lading and package label/[Transport Index]. and brought to the licensee's [Somerset, New Jersey] facility. Investigation is ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2017-05-19
52745 | 0 | TIOGA PIPE, INC. |  |  |  |  | 2017-04-28 | 2017-05-11 09:40 | 2017-09-22 | INTERIM REPORT CONCERNING SUPPLY OF STAINLESS STEEL TUBING The following is a summary of a report received via fax: "This [interim report is being provided] in accordance with 10 CFR Part 21.21 concerning the supply of 0.5 inch Stainless Steel Tubing to the Duke/Progress Energy Brunswick Nuclear Generating Station. Mackson Nuclear subcontracted Tioga Pipe to supply the tubing. Tioga Pipe in-turn subcontracted Summerill Tube; in which Summerill Tube procured the tubing commercially utilizing the provisions of ASME Section III, NCA 3855.5. However, Summerill failed to properly implement the requirements of NCA-3855.5(a)(2) in that a product analysis of each piece of unqualified source material was not performed. "Tioga Pipe does not have the capabilities to conduct an evaluation of the defect to determine if a substantial safety hazard exists in the tubing supplied to Duke/Progress Energy. As such, Tioga cannot provide a timeframe as to an expected completion date, and is relying on the licensee, Duke/Progress Entergy, to make the final determination. "If you have any questions, please feel free to contact William Kotcher at (713) 512-3569 or our Quality Director, Russell Lion, at (484) 546-5612." * * * UPDATE AT 1400 EDT ON 09/22/17 FROM RUSSELL LION TO JEFF HERRERA * * * The following is an excerpt from a report submitted via facsimile: "Closure of Interim Report Notification Pursuant To 10 CFR Part 21.21, Regarding Supply Of 0.5 inch OD X 0.065 inch MW SA213 TP 316/316L Tubing. "This letter is being provided to update the status of a recent interim report submitted by Tioga Pipe Co in accordance with 10 CFR 21.21. The interim report was provided on Tioga letter (TP-LTR-NRC-17-01) dated May 10, 2017 (NRC Log No. 2017-31-00, Accession No. ML17142A323). In a joint effort with Duke Energy, Brunswick Nuclear Plant, the evaluation of the condition identified in the interim report has been completed. The condition reported has been determined to be not reportable in accordance with 10 CFR 21. If you have any questions, please feel free to contact our Quality Director, Russell Lion, at (484) 546-5612 or myself at (713) 512-3569." See EN 52734. Notified R2DO(Musser) and Part 21 Reactors group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-05-11
52744 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2017-05-10 14:11 | 2017-05-10 21:40 | 2017-05-10 | APPENDIX J LOCAL LEAKAGE EXCEEDED ACCEPTANCE CRITERIA "On Wednesday May 10, 2017, at 1411 EDT, with the reactor at 0 percent core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) was in a Refueling Outage, performing a review of Local Leak Rate Testing results, when it was concluded that PNPS had exceeded its Title 10 Code of Federal Regulations Part 50, Appendix J, Option B, Type B and C Local Leak Rate Test (LLRT) leakage criteria. "Previously, on April 22, 2017, when PNPS was performing LLRT of the High Pressure Coolant Injection (HPCI) steam exhaust line check valves, both valves failed to meet their LLRT acceptance criteria specified in plant procedures. Neither of the check valves seated acceptably. Based on the ongoing evaluation of these test exceedances, it was concluded that these test results cause the plant to exceed the overall as-found minimum path Appendix J acceptance criteria of 0.6 La (126.3 SLM [Standard Liters per Minute]). "Further investigation is ongoing. "This event has no impact on the health and safety of the public. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A), any event or condition that resulted in the condition of the nuclear power plant, including its principle safety barriers, being seriously degraded. "The licensee will notify the Commonwealth of Massachusetts Emergency Management Agency." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-05-10
52743 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-05-10 | 2017-05-10 17:05 | 2017-05-10 | AGREEMENT STATE REPORT - INOPERABLE SHUTTERS ON TWO STORED GAUGES The following information was received from the state of Texas via email: "On May 10, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that during routine testing it found the shutters on two Berthold model LB8010 nuclear gauges that were in storage were inoperable. The shutters were in the closed position. Each gauge contains a 20 milliCurie cesium - 137 source. One source handle was reported as missing and the other handle rotates around the shutter's operating shaft, but does not turn the shaft. The licensee has contacted the manufacture to inspect and repair or replace the gauges. The gauges are not an exposure risk to members of the general public or the licensee's work force. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-05-18
52742 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-05-10 07:55 | 2017-05-10 11:46 | 2017-05-10 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTUATION "At approximately 0755 CDT, on May 10, 2017, Pierce County inadvertently actuated their sirens while performing a scheduled weekly cancel test. All fifty two (52) Pierce County sirens actuated county wide for approximately 11 seconds before Pierce County Dispatch canceled the activation. This 4-hour non-emergency report is being made per 10 CFR 50.72(b)(2)(xi), Offsite Notification. Capability to notify the public was never degraded during this time. All Emergency Notification sirens remain in service. No press release is planned at this time. The license has notified the NRC Senior Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-05-10
52741 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2017-03-10 | 2017-05-09 14:36 | 2017-06-09 | PART 21 REPORT - POTENTIAL MINIMUM WALL THICKNESS ISSUE ON CERTAIN POSI-SEAL VALVES The following report was received via email: "Pursuant to 10 CFR 21.21 (a)(2), Fisher Controls International LLC ('Fisher') is providing required written interim notification of a potential failure to comply concerning minimum wall requirements in the packing box region of certain Posi-Seal valves [A11]. "On March 10, 2017, Fisher discovered a minimum wall issue while processing an order. While the order at issue was corrected prior to shipment, Fisher is currently engaged in an extent of condition investigation to determine whether the noncompliance extends beyond the specific order. Fisher anticipates completing this investigation and disseminating additional information on or before June 9, 2017. Appropriate corrective action will be initiated to prevent reoccurrence. "Should there be any further questions concerning this matter, please contact Benjamin Ahrens, Manager, Quality by email at Benjamin.Ahrens@Emerson.com or via phone at 641-754-2249." * * * UPDATE ON 6/9/17 AT 1708 EDT FROM DEBBIE SCHAEFER TO BETHANY CECERE * * * The following report was received via email: "Fisher Information Notice: FIN 2017-03 9 June 2017 "Subject: Potential Minimum Wall Thickness Issue on Certain Posi-Seal A11 Packing Boxes "Purpose: The purpose of this Fisher Information Notice (FIN) is to alert affected customers that, as of 10 March 2017, Fisher Controls International LLC (Fisher) became aware of a situation which may affect the minimum wall thickness of certain Posi-Seal designed valve bodies. Fisher is informing affected customers of this circumstance in accordance with Section 21.21 (b) of 10 CFR 21. "Discussion: Fisher engineering identified a potential minimum wall thickness issue on a 14 [inch] Posi-Seal Type A11 body drawing in the process of fulfilling an order. The valve body drawing was such that it was possible to machine the packing box region of the valve body neck within drawing-specified tolerances but fail to meet minimum wall thickness as required by ASME B16.34. As a result of this discovery, the affected order was halted and an investigation was initiated. "Extent of Condition: POSI-SEAL manufactured and supplied Type A11 valve bodies from their location in N. Stonington, CT to the nuclear industry prior to being acquired by Fisher in 1985. An extent of condition investigation was conducted to identify all potentially affected body drawing numbers and instances of orders shipped by Posi-Seal and subsequently by Fisher that could have had minimum wall issues. The scope of this investigation included all sizes and appropriate pressure classes of potentially affected valves shipped from either Posi-Seal or Fisher. The investigation concluded that only the 14 [inch] size for certain body drawing numbers are affected. Other sizes or types of valves are not affected by this FIN. "Equipment Affected by this Fisher Information Notice: Items subject to this FIN are confined to the 14 [inch] Type A11 valve bodies having original Posi-Seal drawing/serial numbers referred to in the attached Appendix A. All affected equipment was shipped from N. Stonington. No affected equipment was shipped from the Fisher Marshalltown, IA location. "Action Required: Fisher has revised the affected drawings to ensure the minimum wall requirements of ASME B16.34 are met. Fisher will also work directly with the affected customers to evaluate and resolve the potential minimum wall thickness issues. "The in-process order was stopped and will be verified to meet minimum wall thickness requirements prior to shipment. "10 CFR 21 Implications: Fisher requests that the recipient of this FIN review it and take appropriate action in accordance with 10 CFR 21. If there are any technical questions or concerns, please contact: "Ben Ahrens Quality Manager Emerson Automation Solutions Fisher Controls International LLC 301 South First Avenue Marshalltown, IA 50158 Phone: (641) 754-2249 Benjamin.ahrens@emerson.com "List of Affected Equipment "Customer/Site Niagara Mohawk Power Corp., Nine Mile Point, Unit 2, Shipped in 1983 Purchase Order NMP2-P304D/12177 Customer Tag Numbers 2CPS*AOV104, 2CPS*AOV106, 2CPS*AOV108, 2CPS*AOV110 Posi Serial Number 19157-3 Qty 4 "Customer/Site Niagara Mohawk Power Corp., Nine Mile Point, Unit 2, Shipped in 1983 Purchase Order NMP2-P304D/12177 Customer Tag Numbers 2GTS*V51, 2GTS*V52, Posi Serial Number 19157-35 Qty 2 "Customer/Site Union Electric Company, Callaway Plant Unit 1, Shipped in 1985 Purchase Order 14894-M-236-2 Customer Tag Numbers EF-V343, -V344, -V345, -346, GN-V057, -V058, -V059, -V060 Posi Serial Number 35287-01 Qty 8" Notified R1DO (Welling), R4DO (Rollins), and Part 21/50.55 Reactors Group by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-05-09
52740 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-05-08 | 2017-05-09 11:10 | 2017-05-09 | AGREEMENT STATE REPORT - FAILED SHUTTER PISTON The following information was obtained from the Commonwealth of Pennsylvania via fax: "Event Description: The licensee reported that on May 8, 2017 the indicator light on an AccuRay Model U-3 gauge, serial number 6631901, containing 1 Curie of americium-241 would not change from red (open) to green (closed). The area around the shutter was surveyed and the shutter was determined to be in a closed position. A service provider was contacted and the piston was replaced. All regulatory precautions were taken and no exposures occurred. "Cause of the Event: Equipment failure. "Actions: The Department [PA Department of Environmental Protection] will perform a reactive inspection. A service provider has already corrected the problem. More information will be provided upon receipt." PA Event Report ID No.: PA170010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-05-17
52739 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2017-04-19 | 2017-05-09 09:42 | 2017-05-09 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER MECHANISM FAILED TO FUNCTION AS DESIGNED The following information was received from the Commonwealth of Virginia via email: "On May 8, 2017, the licensee notified the Virginia Office of Radiological Health (ORH) that on April 19, 2017, the shutter mechanism of the fixed gauge device (Thermo EGS Gauging Inc. Model TFC-185, Serial Number QC00323; 1250 millicuries of Krypton-85) was not opened all the way to the end as it should function by design. The gauge is used to scan the thickness of plastic sheeting. The licensee has contacted the gauge manufacturer (Thermo EGC Gauging, Inc.) and found that the cause of the problem was due to failure of the Solenoid Rotary Coil found in the device. "The licensee's report indicated that Thermo EGS Technician replaced the Solenoid Rotary Coil and fixed the problem. The case is closed. "There was no public health and safety concern. "Event Report ID No.: VA-17-006" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2017-05-17
52738 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-05-08 09:25 | 2017-05-08 13:55 | 2017-05-08 | THROUGH-WALL LEAKAGE IDENTIFIED ON REACTOR COOLANT SYSTEM PRESSURE BOUNDARY DURING TESTING "On May 8th, 2017 at 0925 [EDT], during the performance of LGS [Limerick Generating Station] leakage testing of the reactor pressure vessel and associated piping, a through-wall leak was identified on an instrument line connected to the N16D nozzle. "The reactor will be maintained shutdown until pipe repairs and testing are complete." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-05-08
52737 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2017-05-08 06:45 | 2017-05-08 10:48 | 2017-05-08 | AGREEMENT STATE REPORT - CO-60 IRRADIATOR SOURCE DOWN SWITCH FAILURE "According to 180 NAC 3-026.02 (NRC 10 CFR 30.50) this is the twenty four hour report to the HOO [NRC Headquarters Operations Officer] due to an event in which equipment is disabled or fails to function as designed and is required to regulation or license condition and no redundant equipment was available and operable to perform the required safety function. "The RSO [Radiation Safety Officer], called to report that on May 6th, [2017] at approximately 0645 [CDT] in the morning, Becton Dickinson had a source rack time-out alarm. The Source Rack down switched failed to indicate the rack reached the down position. Upon initial investigations they determined the source was in the down and shielded position. With the help of their service company, Nordion, they bypassed the door interlock and with survey instruments, they ensured the sources were down in the shielded position. No exposure to personnel occurred. Upon initial visual inspection, it appears there may have been a broken [electrical] cable that caused the alarm. Nordion is expected to be on-site today, Monday, May 8, to fix the problem. Will update when we receive the written report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2017-05-16
52736 | 0 | AMETEK SOLID STATE CONTROLS |  |  |  |  | 2017-05-08 | 2017-05-08 09:52 | 2017-06-01 | PART 21 - INTERIM NOTIFICATION OF A POTENTIAL DEFECT ON A PRINTED CIRCUIT BOARD "Ametek Solidstate Controls began a 10 CFR Part 21 evaluation after receiving notification from NextEra Energy Seabrook Station that a 7.5kVA Inverter would prematurely transfer to alternate source at 27A load during commissioning. The X202 Crest factor board (80-9213516-90) was replaced and the unit operated normally. "Analysis of the failed X202 Crest Factor board identified an SCR on the printed circuit board was turning on prematurely and resulted in a transfer to alternate source or with the absence of the alternate source, to a dead bus. A capacitor was placed across the SCR on the X202 board to protect the SCR from dv/dt turn on. Subsequent testing determined the added capacitor corrected the anomaly. "In addition to Seabrook, Ametek has recently experienced similar anomalies on two separate occasions. However, these occurrences were discovered during manufacturing and in-house testing phase for new product and were attributed to a SCR failure, excessive noise, and long leads. "ACTION RECOMMENDED: Ametek Solidstate Controls recommends installing a 0.22 microfarad capacitor p/n 80-134734-90 across X202 terminals J1-11 to J1-12. This capacitor will have no effect on EMI or seismic qualifications. "If you wish to acquire the 80-134734-90 capacitor, Ametek Solidstate Controls will work with you to provide spare parts. Please contact Mr. Mark Shreve of our Client Services group at 1-800-222-9079 or 1-614-846-7500 ext. 6332. mark.shreve@ametek.com" * * *UPDATE FROM ETHAN SALSBURY TO VINCE KLCO ON 6/1/2017 AT 0750 EDT * * * The following information was excerpted from an Ametek Solidstate Control email: "Ametek Solidstate Controls began a 10 CFR Part 21 evaluation after receiving notification from NextEra Energy Seabrook Station that a 7.5kVA Inverter would prematurely transfer to alternate source at 27A load during commissioning. The X202 Crest factor board (80-9213516-90) was replaced and the unit operated normally. "Analysis of the failed X202 Crest Factor board identified an SCR on the printed circuit board was turning on prematurely and resulted in a transfer to alternate source, or with the absence of the alternate source, to a dead bus. A capacitor was placed across the SCR on the X202 board to protect the SCR from dv/dt turn on. Subsequent testing determined the added capacitor corrected the anomaly. "In addition to Seabrook, Ametek has recently experienced similar anomalies on two separate occasions. However, these occurrences were discovered during manufacturing and in-house testing phase for new product and were attributed to an SCR failure, excessive noise, and long leads. "Ametek Solidstate Controls recommends installing a 0.22 microfarad capacitor, p/n 80-134734-90 across X202 terminals J1-11 to J1-12. This capacitor will have no effect on EMI, seismic, or aging qualifications. "If you wish to acquire the 80-134734-90 capacitor, Ametek Solidstate Controls will work with you to provide spare parts. Please contact Mr. Mark Shreve of our Client Services group at 1-800-222-9079 or 1-614-846-7500 ext. 6332. mark.shreve@ametek.com" Notified R1DO (Bower), R3DO (Daley) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-05-08
52735 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-05-01 | 2017-05-05 16:02 | 2017-05-05 | AGREEMENT STATE REPORT - THEFT OF TROXLER MOISTURE DENSITY GAUGE The following information was provided by the State of California: "S-2 Engineering reported the loss of a Troxler 3411-B # [S/N] 12398 moisture density gauge that had been in storage at a job site in Barstow, CA. This device contains 0.296 GBq (8 mCi) of Cs-137 and 1.48 GBq (40 mCi) of Am-241. "The licensee was conducting a physical inventory of their devices containing radioactive material and found this one to be missing from the locked storage box. "The licensee checked with all of their authorized gauge users to determine if the device was in use but not checked out properly before reporting it as lost. The last documented use of the density gauge was Sept. 22, 2016. "This investigation is ongoing." The licensee notified their Local Law Enforcement Agency (LLEA) of the theft. CA 5010 Number: 050417 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-05-15
52734 | 0 | SUMMERILL TUBE CORPORATION |  |  |  |  | 2017-03-08 | 2017-05-05 14:38 | 2017-05-05 | INTERIM PART 21 - UNQUALIFIED SOURCE MATERIAL FOR NUCLEAR APPLICATIONS During a Vendor Audit by Consolidated Power Supply located in Birmingham, AL, it was discovered that three (3) orders had been received from Summerill Tube Corporation that did not meet the ASME BPVC, Section III, NCA-3800 criteria. Management Systems Analysis, Inc. completed a Supplier Quality Audit Report for Consolidated Power Supply which is described, in part, below: "SUPPLIER QUALITY AUDIT REPORT "SUPPLIER NAME/LOCATION: Summerill Tube Corp., Franklin Street, P.O. Box 302, Scottdale, Pa 15683, Phone: 724-887-9700 "PRODUCT: Ferrous & Nonferrous Tubing "SPECIFICATIONS: ASME SECT III Div 1NCA3800 15 Ed, 10CFR50 APP 'B', ANSIN45.2, NQA-1 94 Ed thru & including 08 Ed/09 Ad Basic Requirements, 10CFR21, SNT-TC-1a ASME Nx 5500 "AUDIT SCOPE "Summerill Tube is a Material Organization manufacturing Ferrous and Nonferrous Tubing in accordance with their Quality Assurance Manual Rev 04 dated 10/22/12 and Nuclear Code Manual Rev 03 dated 12/19/12 that supplements the program in accordance with the ASME Code. "QUALITY ASSURANCE SUMMARY: On March 2, 2017 an audit was conducted of Summerill Tube in Scottdale, Pennsylvania. The primary contact during the investigation was Scott Salvatore Quality Assurance Manager. "Summerill was procuring qualified materials from approved sources, typically ASME QSC holders for extrusion into its final form. Once material is accepted at their facility it is entered into inventory and stored in a lay down area outside. Upon acceptance of an order materials are allocated the job, a work order is issued detailing the sequence of operations to be performed and the customer's requirements. Testing is performed on each heat of material issued for code work using qualified materials. During the past year this has changed as documented in Audit Finding No 1. "The material is annealed to remove work hardening, passivated to remove any scale or contamination and tested. Testing typically consists of eddy current testing, hydrostatic testing and ultrasonic examination as required. The completed materials are then line marked packaged and shipped. "The following orders were reviewed as the primary basis of the investigation including certification of the material by Summerill material certifications, associated Shop Orders, testing performed to qualify the material, hydro testing, flare testing, heat treatment and final inspection of the parts prior shipment. "Reviewed the following orders: "Order 32422 Lot 32422 SA213 316L 5/17/16 ASME III NC 15 Ed Ht 541455 from Sandvik dated 7/7/15 Penn State Metals 5/12/16 Chem Analysis by LTI dated 5/13/16 Solution Anneal 5/3/16. Dim Inspection dated 5/16/16 Certification dated 5/17/16 "Order 32675 Lot 32675 SA213 to ASME III Cl 2 15Ed Ht 541366 from Sandvik dated 11/4/15 Tensile by Penn State dated 9/26/16 & Chem by Lab Testing dated 9/26/16 Solution Anneal dated 9/21/16. Dim Inspection dated 10/3/16 Certification dated 10/6/16 "Order 32676 Lot 32676 SA213 316L ASME III NC 15 Ed Ht 541028 from Sandvik dated 5/19/15 Tensile by Penn State dated 9/30/16 Chem by LTI 9/26/16 Solution Anneal dated 9/21/16. Dim Inspection dated 10/11/16 Certification dated 10/12/16 "Order 32120 Lot 32120 SA213 304L to ASME III Cl 1 15 Ed Ht 531223 from Sandvik dated 4/18/12 Tensile by Penn dated 9/1116 Chem by Lab Testing dated 8/31/16 UT by LTI 9/21/16 Solution Anneal dated 8/22/16. Dim Inspection dated 10/1/16 Certification dated 11/22/16 "As a part of the investigation corrective action to previous audit deficiencies was reviewed with the following results. "Audit Finding No. 1 (V16-7) Contrary to NCA 1140.g STC does not have a copy of the 2015 Edition of the ASME Code and consequently has not reviewed the edition for changes that would impact their program. A copy of the 2015 Ed of Section III was obtained and reviewed. Actions taken found to be satisfactory. "Based on the investigation the supplier program was found to be adequate and effective. "RESULTS "As a result of the investigation performed at Summerill revealed the following deficiency was noted. "Audit Finding No. 1 "Two suppliers appear on the Approved Suppliers List, Walsin Specialty dated 4/15/16 and Shanghai Maxmount dated 4/13/16, as ASME III NCA 3800 suppliers. Audits of each of these suppliers performed by AccuInspection. The checklist sections covering NCA 3800 indicate 'Minor NC' and 'N/A' as a result without further explanation. Materials from these supplier were purchased from Krupala in Canada and unaudited source. "Audit Finding No. 2 "Contrary to NCA 3855.5 and Section 7.3 of the manual only one chemistry was performed by Lab Testing on Ht E110462 Sa213 316L unqualified source material from Outokumpu via Krupalu and Walsin to represent 18 pieces used on order 32132. This material was certified as ASME Section III NC 2015 Ed." Summerill identified three (3) additional unqualified orders that were shipped to Tioga who was notified on 04/28/2017. For additional information, you may contact: Scott Salvatore Quality Manager Summerill Tube Corp. P. O. Box 302 220 Franklin Street Scottdale, PA 15683 Work: 724.887.1412 / Cell: 412.901.9643 / Fax: 724.887.1450/Email: scotts@summerilltube.com http://www.summerilltube.com/ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-05-05
52733 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-05-04 21:03 | 2017-05-05 00:45 | 2017-05-05 | OFFSITE NOTIFICATION DUE TO MISCOMMUNICATION DURING ON-THE-JOB TRAINING "On 5/4/17 at 2103 CDT, the South Texas Project [STP] Security Department was conducting on-the-job training for Bomb Threat response. While simulating the Bomb Threat Checklist via phone call, the trainer mistakenly contacted the Brazoria County, TX Child Protective Services (CPS) and reported a bomb threat. In response, the Child Protective Services notified the City of Brazoria, TX Police Department of the threat. The Brazoria Police Dept. then contacted both the Bay City, TX Police Department and the STP Security Department. By approximately 2130 CDT, all agencies had been notified by the STP Security Department of the mistaken phone call and that no actual bomb threat existed. "The NRC Senior Resident Inspector was notified of the issue." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-05-05
52732 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-05-04 17:09 | 2017-05-04 19:53 | 2017-05-04 | MANUAL REACTOR TRIP DUE TO FAILED REACTOR COOLANT PUMP POWER TRANSFER "On May 4th, 2017, at 1709 EDT, Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to a failure of the #3 Reactor Coolant Pump normal feeder breaker to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and Steam Generator Atmospheric Dump Valves. Unit 1 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72(b)(2)(iv)(B). "There was no effect on WBN Unit 2. "The NRC Senior Resident [Inspector] has been notified." | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-05-04
52731 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2017-05-02 | 2017-05-04 13:14 | 2017-05-04 | PART 21 - C8, M8 AND H8 SWITCHES EXHIBITED CONTINUITY FROM INTERNAL CIRCUITRY TO CASE GROUND DURING INSPECTION AND TEST The following report was received via email: "TopWorx Information Notice: TIN 2017-01 "04 May 2017 "Subject: C8, M8 and H8 Switches "From: James McDill Director of Operations TopWorx 3300 Fern Valley Road Louisville, KY 40213 Fax: (502) 969-7315 "Equipment Affected by this Information Notice: C8, M8 & H8 Series Products released prior to April 01, 2017. "Purpose: The purpose on this TopWorx Information Notice (TIN) is to alert that as of 02 May 2017 TopWorx was made aware of a situation which may affect the performance of the equipment listed above. TopWorx is informing its customers of this circumstance in accordance with Section 21.21 (b) and 50.55 (e) of 10CFR21. "Applicability: This notice applies only to the C8, M8, and H8 series of switches. "Discussion: A potential nonconformance was discovered during product review when X-Ray analysis revealed a small piece of loose solder inside a completed C8 switch. Investigations revealed that the cause of this defect was the amount of solder used to hermetically seal the switch and enclosure together. Under the right conditions and circumstances, excessive solder on this specific switch model could potentially bridge between a circuit connection and the internal surface of the switch enclosure causing a high potential (Hipot) failure. "Extent of Condition: No other series of switches are affected by this information notice. "Actions Required: The recommended corrective action for installed switches is to continue monitoring for ground fault indications. If you do not currently monitor for ground fault indications, then a resistance check using an ohmmeter from each contact to the case to ensure no continuity to ground exists. Any switches exhibiting continuity to ground should be returned to TopWorx for replacement. "10CFR21 Implications: TopWorx requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR21. Customer notifications [Quantity purchased and Customer Purchase Order numbers]: Nuclear Logistics Inc. [Qty 2 - PO #NLI57759, Qty 1 - PO #NLI-50192 REPL] Control Southern Inc. [Qty 10 - PO #X230280199, Qty 24 - PO #X230303436, Qty 1 - PO #X230315950, Qty 14 - PO #X230336922] Ralph A. Hiller Co. [Qty 10 - PO #NUC9868] Weir Valves & Controls USA Inc. [Qty 1 - PO #2022132/0, Qty 1 - PO #202321/0] Emerson Process Mgmt (Bettis) [Qty 4 - PO #4125106730, Qty 8 - PO #4125084349] Fisher Controls [Qty 4 - PO #G133492, Qty 4 - PO #4123340399, Qty 0 - PO #G132951 (ordered but not shipped), Qty 18 - PO #G132951, Qty 1 - PO #G133421] "If there are any technical questions or concerns, please contact: Mark Brozak Manger, Quality TopWorx 3300 Fern Valley Road Louisville, KY 40213 Fax: (502) 969-8000 Phone: (502) 873-4689 Mark.Brozak@emerson.com" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-05-04
52730 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-05-02 14:00 | 2017-05-03 15:57 | 2017-05-03 | AGREEMENT STATE REPORT - LEVEL DENSITY GAUGE SHUTTER STUCK OPEN The following information was obtained from the state of Louisiana via email: "On 05/03/2017, the Assistant Radiation Safety Officer (RSO) for ExxonMobil Chemical received notice that a level density gauge was having difficulty with the operation of the shutters on a gauge installed on a process. During follow-up checks, the one level gauge was found with shutters that were stuck in the open position and the manual operation handle had broken. The report was received by the RSO at approximately 1400 [CDT] on May 02, 2017. "The gauge was an Ohmart Corporation Gauge, devices involved, Model Number SHF-2-45. The gauge/device S/N unknown is loaded with approximately 200 mCi of Cs-137 and the S/N 5828GK. The source and source holder usually have one S/N for the whole device. BBP Sales/Service Company was contacted to fix the problem by repairing the gauge or replacing the device. The gauge is installed on processes and does not pose a health and safety threat to the general public or the employees. The source survey revealed the readings were less than 2 mR/hr and proper safety precautions will be taken when personnel enters the area. This is considered an equipment failure with the manual shutter handle device breakage." LA Event Report ID No.: LA-170007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-05-11
52729 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-05-03 02:04 | 2017-05-03 15:04 | 2017-05-03 | FITNESS FOR DUTY - PROHIBITED ITEM FOUND IN PROTECTED AREA "At 0204 [CDT] on 5/3/2017, a facilities person was removing the trash bags from the garbage can in the restroom of the Administrative Building inside the Protected Area. While emptying the trash, they discovered a 100ml alcoholic beverage container in the trash. The container was empty, however, there was an odor of alcohol coming from the bottle. The item was turned over to the security department. The investigation identified the last time this trash bag had been changed out was on 5/2/2017 at 1530 [CDT]. This event is being reported per 10CFR26.719(b)." The licensee has notified the NRC Resident Inspector. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2017-05-03
52728 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2015-12-03 | 2017-05-03 12:58 | 2017-05-03 | ADMINISTERED DOSAGE DIFFERENT FROM PRESCRIBED DOSAGE The following was received from the Veterans Affairs National Health Physics Program via email: "As requested via a telephone conversation with the NRC Operation Center, this is a written notification, pursuant to 10 CFR 35.3045(a)(1), regarding a series of medical events that occurred at the VA New Jersey Health Care System in East Orange, New Jersey. A brief description of the events, cause of the events, and other required information are contained in the enclosure. The East Orange VA facility holds VHA Permit Number 29-04481-01 under our master material license, NRC License No. 03-23853-01VA. "There are six apparent medical events with four resulting from the use of a pre-printed form with the incorrect unit selected; the first occurring on December 3, 2015 involving a dosage of 155 microCuries of radium-223 dichloride; the second on March 7, 2016 involving a dosage of 128 microCuries of radium-223 dichloride; the third on June 3, 2016 involving a dosage of 131 microCuries and the fourth on August 14, 2016 involving a dosage of 155 microCuries of radium-223 dichloride that was administered to patients for treatment of osseous metastases from prostate cancer. The written directives incorrectly stated the intended dosages as 155 milliCuries; 128 milliCuries; 131 milliCuries and 155 milliCuries, respectively. The fifth medical event occurred on February 20, 2016 involving a dosage of radium-223 dichloride 121 microCuries when the written directive stated 211 microCuries. The prescribed dose was 211 microCuries. The dose administered was 121 microCuries, which is a 43% variance. The whole body dose calculation is 85.50 rad/mCi x 0.09 mCi = 7.7 rem, which exceeds the 5 rem dose limit. However, the physician intended to administer 121 microCuries and had transposed the numbers on the written directive. The sixth occurred on March 28, 2017 with 25 milliCuries of sodium iodide iodine-131 where the written directive stated 25 milliCuries of radium-223 dichloride with the intended dose of 25 milliCuries of sodium iodide iodine-131 ordered and administered. No harm to the patients is expected since these treatments were successfully performed by administration of a dosage that was in accordance with the intentions of the authorized user physician. The details of corrective actions are being ascertained at the facility due to the absence of the Radiation Safety Officer at the time of discovery. NHPP [National Health Physics Program] staff was on site and discovered the events on May 2, 2017, during a routine inspection. We notified the NRC Operations Center by telephone on May 3, 2017. "As part of our routine, we evaluated circumstances of the medical events, reviewed actions to prevent a recurrence, and assessed regulatory compliance." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2017-05-11
52727 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2017-04-30 18:18 | 2017-05-03 12:59 | 2017-05-03 | OPEN BYPASS VALVE CAUSES LOSS OF SAFETY FUNCTION "On April 30, 2017, at 1818 [EDT], the main turbine steam bypass valve #1 partially opened. Power was incrementally lowered. While lowering power the bypass valve would shut and then reopen and power would again be lowered. When power was lowered to approximately 74 percent the bypass valve remained closed. During the transient the reactor protection system (RPS) Turbine Stop Valve Closure and Control Valve Fast Closure trip functions were declared inoperable due to the opening of the bypass valve which affects the bypass setpoint for those RPS trip functions. With the loss of these RPS trip functions a loss of safety function existed intermittently for approximately 37 minutes. The manual reactor trip function and other RPS functions remained operable. "Both channels of the rod withdrawal limiter (RWL) and the end of cycle reactor recirculation pump trip (EOC-RPT) function were also declared inoperable. These functions are credited in accident analysis, this also resulted in a loss of safety function. "Currently the bypass valve is closed and the RWL, EOC-RPT and RPS function are operable. Troubleshooting continues to determine the issue with the main turbine that caused the bypass valve to open." NRC Resident Inspector has been notified. | 74 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-05-03
52726 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2015-06-04 | 2017-05-03 12:28 | 2017-05-03 | AGREEMENT STATE REPORT - LOST SOURCE The following was received from the State of New Jersey via email: "An inspection of Evoqua Water Technologies was conducted on 4/30/15. During the inspection, a device listed on Generally Licensed Device Registration Form #664 could not be found. The device was a model 4000 [SN 732], manufactured by Metorex Inc, and contained 10 mCi of Am-241. The device was listed as being at the facility since 1989. However, no current employee remembered the device being in use for several years. On 5/15/15, the original unit was discovered, but without the attached probe which contained the source. On 6/4/15, after repeated search attempts, the probe was declared lost." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2017-05-11
52725 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-05-02 19:45 | 2017-05-02 22:33 | 2017-05-02 | MANUAL REACTOR TRIP DUE TO FAILED REACTOR COOLANT PUMP POWER TRANSFER "On May 2nd, 2017, at 1945 EDT, Watts Bar Nuclear [WBN] Plant Unit 1 reactor was manually tripped due to a failure of the #3 Reactor Coolant Pump normal feeder breaker to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All control and shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via auxiliary feedwater and main steam dump systems. Unit 1 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "There was no effect on WBN Unit 2. "The NRC Senior Resident [Inspector] has been notified." | 0 | 0 | 0 | 26 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-05-02
52724 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2017-05-02 17:00 | 2017-05-02 18:34 | 2017-05-19 | UNANALYZED CONDITION FOR COMBUSTION TURBINE GENERATOR CONFIGURATION "On May 2, 2017, while performing a past operability review associated with Combustion Turbine Generator (CTG) 11-1, it was determined that a past configuration of CTG 11-1 could not have assured all of the applicable Appendix R success criteria under all of the postulated scenarios described in the Updated Final Safety Analysis Report [UFSAR]. From November 21, 2016 until March 18, 2017 when Mode 4 was entered, CTG 11-1 was in a configuration where it could not be started from the dedicated shutdown panel, although it could be started locally. One of the specific scenarios for Appendix R in the UFSAR credits CTG 11-1 to support a safe shutdown based on an assumed time required to start CTG 11-1 and then provide flow to the reactor pressure vessel using the Standby Feedwater System. During the time period where CTG 11-1 could only be started locally, this assumed time would have been exceeded. Therefore, this event is being reported as an 'unanalyzed condition that significantly affects plant safety' under 50.72(b)(3)(ii)(B). At the time of discovery, CTG 11-1 was fully operable and the described condition had already been corrected. "The NRC Resident Inspector has been notified." * * * RETRACTION PROVIDED BY GREG MILLER TO JEFF ROTTON AT 1532 EDT ON 05/19/2017 * * * "The purpose of this notification is to retract a previous report made on May 2, 2017 (EN 52724) under 10 CFR 50.72(b)(3)(ii)(B). The notification to the NRC involved an event where Combustion Turbine Generator (CTG) 11-1 could only be started locally such that required operator actions during an Appendix R safe shutdown scenario could be delayed. Subsequent to the initial notification, the event, additional site documentation, and the NRC guidance in NUREG-1022 pertaining to 10 CFR 50.72(b)(3)(ii)(B) were reviewed further. lt was verified that Fermi 2 procedures contained actions to ensure Appendix R safe shutdown capability under the plant conditions during the relevant time period. A time validation study was performed [May 9, 2017] which verified that the operator actions could have been completed within the time described in the Updated Final Safety Analysis Report (UFSAR) for initiating Standby Feedwater flow to the reactor pressure vessel. In addition, a review of the supporting design calculation identified margin in the required time described in the UFSAR. Based on this information, the condition of CTG 11-1 during the time period from November 21, 2016 until March 18, 2017 would not have prevented compliance with the Appendix R safe shutdown requirements. Under these circumstances, the event does not represent an 'unanalyzed condition that significantly affects plant safety' under 10 CFR 50.72(b)(3)(ii)(B) per the guidance in NUREG-1022. Therefore, EN 52724 can be retracted and no Licensee Event Report (LER) under 10 CFR 50.73(a)(2)(ii)(B) is required to be submitted." The licensee has notified the NRC Resident Inspector. Notified R3DO (Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-05-02
52723 | 0 | NC DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2017-05-01 | 2017-05-02 16:29 | 2017-05-02 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL SHIPMENT EXCEEDING RADIATION LIMITS The following was received by the state of North Carolina by email: "On 5/1/2017, licensee received a 5 gallon shielded drum containing 8 Cf-252 sources with a total activity of 148 MBq (4.0 mCi). Shipment of the sources originated from E&Z Isotope Products, License Number: 1509-19. Shipment was made through [a common carrier]. The drum was labeled Yellow-III and had a TI [Transport Index] of 9.4. The licensee followed procedures for receiving and securing radioactive materials shipments. Once the drum was secured, the licensee noted surveys of the drum were higher than expected: Side survey of the drum was 18 mrem/hr (gamma) on contact and 90 mrem/hr (neutron) for a total of 108 mrem/hr. Top survey of the drum was 40 mrem/hr (gamma) on contact and 400 mrem/hr (neutron) for a total of 440 mrem/hr. Bottom survey of the drum was 3 mrem/hr (gamma) on contact and 20 mrem/hr (neutron) for a total of 23 mrem/hr. "The drum was then shielded with polyethylene and cadmium. Upon resurveying the drum to confirm readings the following differences were noted: With the drum upright and the neutron detector on top of the drum, the reading was 400 mrem/hr. With the drum on its side and the neutron detector in contact with the drum, the reading was 440 mrem. Wipes of the drum were then taken and the results were [less than] MDL (Minimum Detectable Levels). "The drum was then opened for further inspection by the licensee. It was noticed that a polyethylene bag containing sources was sitting on top of the shield plug and was only about 2 inches from the top of the drum and not covered by any shielding indicating that the sources were not shielded correctly prior to shipment. "The sources were in-processed by the licensee and are still in the licensee's possession (quantity and activity as approved per their NC License). "North Carolina Radiation Protection, [the common carrier] and E&Z Isotope Products were notified of the event on 5/1/2017. "NC Radiation Protection is actively investigating this event at this time. "Report ID Number (NC): NC170020 "At this time the cause and corrective action is to be determined. NC Radiation Protection will be reaching out to E&Z Isotope Products and [the common carrier] for more information. The licensee was authorized to receive the materials in the quantity and activity they received." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-05-10
52722 | -1 | PALISADES | 1 |  |  | [1] CE | 2017-05-02 09:28 | 2017-05-02 15:26 | 2017-05-09 | FAILED ULTRASONIC TESTING OF WELD "On May 2, 2017, during planned inspections, an ultrasonic examination performed on weld PCS-4-PRS-1P1-1, revealed an axial indication in the pressurizer nozzle to safe end area of the weld. This indication does not meet applicable acceptance criteria under ASME, Section XI. "The plant was in cold shutdown at 0% power for a planned refueling outage at the time of discovery. The condition will be resolved prior to plant startup. "This condition has no impact to the health and safety of the public. "The licensee notified the NRC Senior Resident Inspector. "This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A), since an indication was found that did not meet acceptance criteria referenced in ASME Code, Section XI. * * * RETRACTION ON 5/9/17 AT 1303 EDT FROM BARBARA DOTSON TO BETHANY CECERE * * * "Additional evaluations of the recorded indication concluded that the indication was attributed to an erroneous ultrasonic response. This was the result of a combined effect of compromised surface contact at the area of the recorded indication and associated examination scan speed. The contact issue is attributed to the specific tooling configuration required for this exam. The combination of these factors resulted in the introduction of an erroneous reflector in the area of interest that had characteristics of a relevant indication. "The vendor repeated the entire examination for axial flaws and there were no service induced indications recorded. A review of the newly acquired data by site, vendor and EPRI personnel confirmed that no service induced flaws are present." The licensee has notified the NRC Resident Inspector. Notified the R3DO (Hills). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-05-02
52721 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2017-04-29 18:30 | 2017-05-02 14:16 | 2017-06-21 | AGREEMENT STATE REPORT - FIXED GAUGE WITH STUCK SHUTTER The following report was received from the State of Arkansas via e-mail: "The Arkansas Department of Health was notified via telephone and e-mail on Monday, May 1, 2017, at approximately 1337 [CDT] of the licensee's general licensed device stuck shutter and the failure of the shutter mechanism. The equipment failure appears to have occurred from strong thunderstorms. The lockout procedure was verbally verified with the licensee. "The licensee's fixed gauge is a ThermoFisher Scientific, Model Number E-SFL10-XX, Serial Number SP9810, which contains approximately 1,178.42 mCi Kr-85 (approximately 43.60 GBq Kr-85). "The original activity: 1,250 mCi Kr-85 (approximately 46.25 GBq Kr-85) as of June 1, 2016. The source's Model Number is TFC-185 and the Serial Number is QC00256. "Licensee operations with the gauge are twenty-four hours a day. The gauge has a fail-safe closing shutter mechanism and the gauge immediately went into the safe mode electronically during the thunderstorm. The closed shutter position was verified by the visual colored indicators in place. "There have been no known radiation exposures to personnel and/or members of the public. There have been no known radiological health and safety concerns. "The shutter will be repaired by the manufacturer today, May 2, 2017, whom will perform a root cause analysis. The State of Arkansas is awaiting information from today's evaluation, repairs, and surveys. "The State is awaiting a 30 day written report from the licensee." State Event Number: ARK-2017-002 * * * UPDATE ON 6/9/17 AT 1507 EDT FROM ANGIE HALL TO BETHANY CECERE * * * The following follow-up report was received from the State of Arkansas via e-mail: "The [Arkansas] Department [of Health] has received the required thirty (30) day report from the licensee, along with the related exposure survey and service reports from the manufacturer. "The licensee states, 'We have several of these gauges that have been operating normally for several years. Due to the nature of this repair and the fact that this is the only time we have ever had to do this repair, it is my belief that a component in the device failed to operate as intended. The technician scraped paint off the surface of the shutter/flag mechanism that would help the mechanism stick to the magnet. The technician also tightened and applied thread lock to the securing hardware for the magnet. Both items should have been done at the factory.' "The manufacturer's Field Engineer (also known as Technician) stated, 'I believe the issue started with the holding magnet being loose. This may have caused the solenoid to work harder and fail, and that could have caused the board to fail.' "The manufacturer's Radiation Safety Officer stated, 'Thermo EGS Gauging LLC. is aware of the shutter mechanism failing in the closed or failing to the closed position on the TFC-185 and the TFC-190 sensors. The R&D manufacturing team has been working on a engineering project to correct this issue. We are currently in the testing phase and will manufacture all future sensors with the updated materials and parts. There is also an upgrade retrofit kit in the works for existing sensors that are demonstrating/developing this shutter issue. Currently we are sending out Field Service engineers to the customer's site to offer temporary repairs on an as needed basis.' "The Department is waiting on a response from the manufacturer concerning the above statement. "There have been no known radiological health issues, radiological exposures, safety hazards, or concerns to personnel or members of the public during this event. "Event Cause: Equipment failure/design, manufacturing, or installation error. "Corrective Action by licensee: New equipment obtained and repairs made with engineering change to system. "Reporting Requirement Information: "Arkansas State Board of Health 'Rules and Regulations for Control of Sources of Ionizing Radiation' RH-1502.f.2 and RH-402.c. "U.S. Nuclear Regulatory Commission (NRC) Regulations Title 10 CFR Section 30.50 (b) (2) - Equipment is disabled or fails to function as designed, and Title 10 CFR Section 21.21 - A failure to comply or a defect affecting a basic component that is supplied for a facility or an activity that is subject to licensing requirements. "The licensee and manufacturer reports and surveys have been sent to Randy Erickson, Regional State Agreement Officer, U.S. NRC, Region IV Office, and the NRC Headquarters Operations Center. "Note: Leak tests are not required for this type of gauge." NMED Item Number 170231. Notified R4DO (Rollins) and NMSS Events Notification by email. * * * UPDATE ON 6/21/17 AT 1407 EDT FROM ANGIE HALL TO BETHANY CECERE * * * The following follow-up report was received from the State of Arkansas via e-mail: "The Department has received clarification from the manufacturer's Radiation Safety Officer, stating in part, 'Due to a manufacturing defect of some source housing parts, about 10% of our sensors sold in the past could be affect' (affected). "He also stated, 'Our customer Baxter Healthcare is aware of this issue and unfortunately cannot provide a solution to them until their sensors develop this issue on a case by case basis.' "The Department considers this event to be closed." Notified R4DO (Gaddy) and NMSS Events Notification by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2017-05-10
52720 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2017-04-27 15:00 | 2017-05-01 11:30 | 2017-05-01 | AGREEMENT STATE REPORT - MISSING SOURCE The following information was received from the Commonwealth of Kentucky via facsimile: "KY RHB [Kentucky Radiation Health Branch] Inspector, Christopher Keffer, was performing a routine health and safety inspection of the licensee when the RSO [Radiation Safety Officer] discovered that a stored device was missing. According to the RSO, the laboratory where the device was stored was cleaned out the week before; it is currently believed that the device has been thrown away and is now in a landfill." The sealed source identification number is NR-536-D-808-B associated with a Perkins Elmer Clarus Model 500. The source is a Ni-63, 15 microCurie source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2017-05-09
52719 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-04-29 | 2017-04-30 22:05 | 2017-04-30 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILED TO RETRACT The following information was received from the state of Texas via email: "On April 30, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's Radiation Safety Officer (RSO) that a radiography crew working at a temporary field site was unable to retract a 101 Curie iridium-192 source into a SPEC 150 exposure device (camera). The failure occurred after the radiography crew had moved the camera from one location to another at the same job site. The radiography crew notified the licensee of the event. The licensee sent an individual to the site to retrieve the source. The individual found that the guide tube had disconnected from the front of the camera and the flex in the cable was causing the connector to hang up on the camera inlet port. The recovery individual straightened the cable by pulling on the crank out cables and was able to fully retract the source. The RSO stated no over exposures occurred from this event. The RSO stated he believes sand had gotten into the guide tube to camera connection preventing the guide tube from fully latching on the camera outlet connection. The licensee possesses a license issued by the Nuclear Regulatory Commission and is operating under reciprocity in the State of Texas. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-05-08
52718 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2017-04-29 18:44 | 2017-04-29 21:19 | 2017-04-29 | MANUAL REACTOR TRIP DUE TO STEAM GENERATOR HI-HI LEVEL SIGNAL AND FEEDWATER ISOLATION "At 1844 [EDT] on 04/29/2017, while the unit was in a low power condition exiting from a refueling outage, the reactor was manually tripped following a P-14 signal (Steam Generator Hi-Hi Level) and a resulting feedwater isolation signal. All control rods were verified to be fully inserted. The cause of the ['B'] steam generator high level is currently being investigated. "Emergency feedwater actuated at 1845 due to a low-low water level in steam generator 'D'. Plant equipment response is being evaluated and the plant is stabilized in Mode 3 with decay heat removal through the steam dump system to the condensers. There was no release and the emergency feedwater system has been restored to standby. "The event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-04-29
52717 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-04-28 | 2017-04-29 19:27 | 2017-06-16 | AGREEMENT STATE REPORT - RADIOGRAPHER TRAINEE BADGE READ GREATER THAN 5 REM "On April 29, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that on April 28, 2017, one of its radiographer trainees had reported their self-reading dosimeter had gone off-scale. The licensee stopped all work and sent the trainee's OSL [Optically Stimulated Luminescence] dosimeter to be processed. The licensee received a verbal report from the processer on April 29, 2017, and the dose was reported as 5.392 REM. The licensee did not know if the dose was static or dynamic. The licensee stated that the trainee had not operated the exposure device and did not know how the trainee could have received the exposure. The licensee stated there was a chance that the dose was to the badge only. The licensee is conducting a formal investigation into the event. No other individual reported an unusual exposure. The exposure device was a QSA 880D camera containing a 51 Ci Ir-192 source. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-9482 * * * UPDATE AT 1121 EDT ON 06/08/17 FROM IRENE CASARES TO STEVE SANDIN VIA EMAIL * * * The following information was received from the State of Texas via email: "On May 30, 2017 a detailed report was received by the corporate RSO [Radiation Safety Officer] stating the details of this event. The amount of information was limited and an on-site investigation was conducted on June 7, 2017. By interviewing employees who were at the event, it was determined that the individual did receive the dose of 5.392 REM (whole body) on April 28, 2017 as indicated on his badge reading. He was wearing monitoring devices and an alarming rate meter. There was extreme noise in the area. The exposed employee was a trainee and did not operate the radiography device, although the trainee was experienced in rope repelling in this specific situation and positioned the camera 30 feet above the floor in a pipe rack and collected the film. He did not crank the source in or out. He mounted the camera in the pipes, repelled down the ropes out of the area while the weld was imaged. He returned to the area after the trainer cranked in the source, checked a survey meter on the floor level, 30 feet below the camera, and shielded (there were pipes containing fluids and concrete columns shielding the area), while the trainee climbed the distance to collect the film. The trainee did not take the survey meter with him to do a post exposure survey near the camera or film (the meter is routinely snapped on the harness or cow-tail lanyard, but not this time). He collected the film and lowered it by rope to the trainer. The trainee decided on his own to stay in the rope harness near the camera, unknown to him that the source was slightly exposed. His alarming rate meter may have alarmed although he wouldn't have heard it, nor did he check it. The trainer took the film to the developer in another trailer onsite. When he returned (about 20 minutes) to say, film good, the trainee tried to unhook the cable. When it failed to unhook, another trainer in the crew had seen him and turned the crank handle to fully retract the source (uncertain, about half a turn). The trainee immediately lowered himself to the ground and both went to the vehicle. It was found that his pocket dosimeter was off scale, alarming rate meter was not alarming at this point and trainer phoned the RSO to get advice. Work stopped and the employees stayed on site. The RSO collected badge and sent it for immediate processing and gathered as much information as possible. It is believed the trainee's dose, according to the trainers, was to his whole body and possibly a few seconds to his right hand while trying to disconnect the cable. Within days, the trainee was released from employment from the company and disciplinary action taken against the other trainers. In an attempt to contact the trainee, the trainee responded to a phone text message stating he has not had any redness or tingling in his hand. He also stated he did not touch the collimator. The hand dose is estimated to be less than 2.5 millirem for three seconds or less." Notified R4DO (Rollins), NSIR (Milligan), NMSS (Rivera-Capella), and NMSS Events Notification via email. * * * UPDATE FROM IRENE CASARES TO HOWIE CROUCH VIA EMAIL AT 1410 EDT ON 6/16/17 * * * "The RSO has finally completed and provided a rough calculation of the extremity dose on June 16, 2017. The hand dose was difficult to calculate due to deficiencies in rationale of where the source was in position to the exit port on the camera. The company dose was initially rejected due to rationale that if the whole body dose was 5 rem; how could the extremity dose be smaller. The deficiency in knowing the time, distance and actual source shielding was resulting in varied numbers for the extremity dose. After discussing the situation and calculations with the RSO, it was agreed that the dose be assigned 10 rem to the right hand which is below the 50 rem reportable limit." Notified R4DO (Campbell) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-05-08
52716 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-04-29 16:23 | 2017-04-29 17:59 | 2017-04-29 | OFFSITE NOTIFICATION DUE TO SMALL GRASS FIRE IN OWNER CONTROLLED AREA "A grass fire was reported to the Unit 1 control room at 1102 CDT. The grass fire was reported to be in the owner controlled area 1/2 mile west of the protected area and switchyard. The local fire department was dispatched to fight the grass fire. The fire was reported to be out at 1155 CDT. No plant equipment was damaged and the operation of the plant was not affected. Region 12 (Houston) of the Texas Commission of Environmental Quality (TCEQ) was notified of the event at 1623 CDT for visible emissions resulting from the grass fire. No further actions are required by the TCEQ at this time and no press release is planned." An insulator on a 345 kV line failed and the attached line separated and hit the ground. A spark was created when the 345 kV line hit the ground and started a fire that eventually grew to a 20 feet x 20 feet area. The licensee notified the NRC Resident Inspector. | 15 | 90 | 0 | 15 | 90 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-04-29
52715 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2017-04-28 16:43 | 2017-04-28 21:21 | 2017-04-28 | OFFSITE NOTIFICATION FOR RELEASE OF WASTEWATER "This report is being made pursuant to 10 CFR 50.72(b)(2)(xi), as an event where notification to other government agencies has been made. On April 28, 2017, notification to the Minnesota State Duty Office was made due to a non-compliance with release of wastewater requirements in the Monticello Nuclear Generating Plant's National Pollutant Discharge Elimination System permit. There were no consequences to the health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-04-28
52714 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2017-04-28 | 2017-04-28 17:30 | 2017-04-28 | AGREEMENT STATE REPORT - HIGH DOSERATE AFTERLOADER CHECK SOURCE CABLE FAILURE The following is an excerpt of a report received from the Oregon Department of Health via email: Yesterday, April 27, 2017, while treating a patient with a 2 channel plan the licensee received the fault that the 'dummy' cable could not extend to the end of the applicator on the second channel. The licensee's procedure is to go into the HDR vault, check connections and position of the transfer tubes and then retry. The retry failed as well. Because this was a 2 channel treatment, the patient had received only half of the treatment. The licensee explained what was going on to the patient and gave them the option of ending the treatment that day or waiting while the licensee did some testing and, if all went well, would finish the treatment. The patient opted to wait. The licensee changed some of the applicators and transfer tubes, tested without failure, then brought the patient back into the vault to finish the treatment without any issues. After the patient completed treatment and left, the licensee was able to extend the check source cable out of the afterloader and could see right away that the dummy source/end of cable had a bend in it. The licensee inspected the applicator that was used during the fault and thought there was a slight 'burr' in it. Between the bent cable and burr, there might have been snagging, leading to a fault. The licensee called service (ELEKTA, Inc.) to come change the check source cable, which was done today, April 28, 2017. After the check source cable change was completed, the licensee ran all combinations of transfer tubes and applicators without any failures. The licensee believed their theory about the burr and snag may have been wrong as that particular combination ran multiple times without any issues. Therefore, the bent cable caused the fault. There were no adverse or unintended results for the patient, other than waiting 15 minutes while the licensee did some equipment testing. The patient received the prescribed dose. The system is designed so that if the check source/dummy cable cannot extend all the way to the end of the applicator you cannot proceed with the treatment so no possible way in this event to deliver an unintended dose to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2017-05-08
52713 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2017-04-27 18:50 | 2017-04-27 19:59 | 2017-06-13 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. Compensatory measures taken upon discovery. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/13/17 AT 1513 EDT FROM MARCY BLOW TO DONG PARK * * * "Security evaluations indicate the compensatory measure was always in place per the Physical Security Plan. The discrepancy was the vehicle had not been properly secured in accordance with written instruction. Therefore, this event does not meet the reporting criteria in 10CFR73.71, and Event Notification Number 52713 is being retracted." The licensee notified the NRC Resident Inspector. Notified R4DO (Campbell) and 73.71 Safeguards group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-04-27
52712 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-04-27 | 2017-04-27 12:58 | 2017-04-27 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED NUCLEAR GAUGE The following information was received from the state of Texas via email: "On April 27, 2017, the Agency [Texas Department of State Health Services] was notified by the radiation safety officer of a licensee that a fixed gauge was discovered with a stuck shutter. The gauge is a line level indicator on a hydrogen fluoride tank and was stuck in the normal operating position. The gauge is a Vega SHLG containing cesium-137, 300 milliCuries, serial number 321300. The gauge is scheduled for repair and an amendment to the license is in process to operate the gauge in the open position until repaired. There is no risk of exposure to an individual. Updates will be provided as acquired." Texas Incident No.: I-9481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-05-05
52711 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-04-20 | 2017-04-26 16:36 | 2017-06-08 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO INCORRECT NUCLEAR MEDICAL SCAN PERFORMED The following information was obtained from the state of Louisiana via email: "[On] April 21, 2017, [the licensee's RSO] called [Louisiana Department of Environmental Quality (LDEQ)] to inquire if one of his facilities had a 'Recordable Event' or if the facility had a 'Reportable Medical Event'. The event occurred under the Ochsner Clinic Foundation Broad Scope Medical License (OCFBS), LA-0002-L01. The event involved 2 mCi of I-131 being administered as an error when the PA [Physician Assistant] was ordering a medical test/scan. The test should have been one for the parathyroid, but a thyroid scan was ordered in error in the EPIC System [health informatics software]. "[The] RSO for this licensee called in to see if the OMCBR [Ochsner Medical Center, Baton Rouge], Baton Rouge Medical Center error in administration had to be reported or just recorded for the OCFBS medical records. He was instructed it was a reportable event and he should investigate and make the appropriate corrective actions. The 2 mCi [of] I-131 was ordered and administered on [April] 18, 2017 and the error was discovered on April 20, 2017. The Nuclear Medicine Tech placed the patient on the table and the thyroid gland 'lit up' due to the I-131 uptake. "According to [the RSO's] verbal report, the written orders were incomplete or did not exist; the parathyroid was the tissue to be scanned; and discovered on [April 20, 2017]. [The RSO] did a preliminary report on the phone April 21, 2017. His report gave an estimated target organ dose [of approximately] 600 rads to the thyroid. At that time, he stated there were additional aspects to be investigated, corrected, and reported. "Corrective Action: The order capture procedure was changed recently and all of the Technologists, ordering Physicians, and Physician's Assistants will be re-trained in the current/new procedures. The wrong procedure was performed and the results will be sent to the referring physician. The patient was notified of the error. "LDEQ considers this incident still open and subject to investigation and corrective action implementation." LA Event Report ID No.: LA-170006 * * * UPDATE ON 6/8/17 AT 1515 EDT FROM JOSEPH NOBLE TO BETHANY CECERE * * * The following information was obtained from the state of Louisiana via email: "Investigated by LA: Preliminary: Phone Investigation Event was discovered by the wrong organ uptake for the patient scan to be performed. Facility findings wrong study ordered and wrong unit dose ordered and administered. Facility request a site visit when fact can be delivered and management can be present. Facility Investigation Visit, on 05/01/2017 "Findings: PA ordered the unit dose without a written directive. PA ordered the scan through the OMCBR electronic order/records system. Patient was administered the I-131 and counselled when to return for the scan. [Patient] returned after numerous attempts to contact [patient]. The desired scan was different from the wrong scan ordered. At the scan time was when the ERROR was discovered. The wrong activity was ordered and administered due to electronic ordering and records system without confirmations of orders. "Facility Calculations: from 2.0 mCi NaI-131 unit absorbed dose. 10% to 30% uptake from 2 mCi NaI-131. Absorbed Radiation Dose range to thyroid 1100 to 3200 rads with the thyroid gland dose approximately 1630 rads at 15.7 percent uptake from 1.65 NaI-131. State Confirmation From FDA Prescribing Dosage for NaI-131, Table 1, Absorbed Radiation Doses. "Corrective Actions: 'PROOF' of EPIC electronic patients records system and for ordering studies Suspension of I-131 usage until system is corrected and staff training is complete Training for Written Physician's orders and ordering scans Confirming orders before administering drugs/isotopes" NMED #170217 Notified R4DO (Rollins) and NMSS Events Notification by email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-05-04
52710 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2017-04-26 10:04 | 2017-04-26 14:49 | 2017-04-26 | UNIT 1 AUTOMATIC REACTOR SCRAM DUE TO PARTIAL LOSS OF OFFSITE POWER "At 1004 CDT, Arkansas Nuclear One, Unit 1 (ANO-1) reactor automatically tripped due to the partial loss of offsite power. At the time of the trip, the site was in a Tornado Warning and a Severe Thunderstorm Warning. The Emergency Feedwater (EFW) system auto-actuated due to the loss of main feedwater pumps and the loss of the Reactor Coolant pumps. Both Emergency Diesel Generators started as expected with only one loading as expected. All control rods fully inserted. Currently, ANO-1 has stabilized in Hot Standby via natural circulation. "ANO-1 also lost Spent Fuel Pool cooling for approximately 69 minutes. The temperature of the spent fuel pool at the beginning of the event was approximately 102 [degrees] F. The spent fuel pool saw a heatup of 1 [degree] F during the loss of spent fuel pool cooling. The Spent Fuel Pool cooling has been restored. "ANO-2 is currently in a refueling outage with all fuel in the spent fuel pool. ANO-2 completed a full core off load to the spent fuel pool and this was completed on April 12, 2017. Spent Fuel Pool cooling was lost for approximately 10 minutes. The Spent Fuel Pool temperature was 91 [degrees] F prior to the event. No heat up of the pool was identified during the event. Cooling has subsequently been restored. The #1 Emergency Diesel Generator auto-started as designed but did not supply the safety bus due to availability of offsite power. "No radiological releases have occurred from either unit due to this event." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Defueled |  | Hot Standby | Defueled |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-04-26
52709 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-04-25 | 2017-04-26 13:44 | 2017-04-26 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO UNDERDOSE OF YITTRIUM-90 THERASPHERES The following information was obtained from the Commonwealth of Pennsylvania via fax: "Event Description: The event involved a patient who was scheduled to be treated with 11.87 mCi of Y-90 microspheres (TheraSphere), but only received an estimated 5.07 mCi, or 43% of the prescribed dose. The licensee reported the event to the Department [Pennsylvania Department of Environmental Protection] on April 25, 2017. Initial indication is that there was a faulty connection on the catheter line that allowed a leak to occur. The patient and referring physician were notified the day of the procedure. No Jefferson personnel skin contamination occurred. However, gloves, drapes and the patient's skin were contaminated. The patient was quickly decontaminated with alcohol wipes. All remaining areas were also decontaminated. A skin calculation is currently being completed by the licensee to determine the patient's exposure, if any. No overexposure is believed to have occurred. "Cause of the Event: Unknown at this time. Suspected human error. "Actions: The Department will perform a reactive inspection. The licensee will update their procedure to include additional checks of the Y-90 administration kit. More information will be provided upon receipt." PA Event Report ID No.: PA170009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-05-04
52708 | 0 | CB&I AREVA MOX SERVICES |  |  |  |  | 2016-09-29 | 2017-04-26 13:34 | 2017-04-26 | PART 21 REPORT - WELDS ON MODULAR FRAME ASSEMBLIES DETERMINED TO BE DEFECTIVE The following is the summary of information received from CB&I AREVA MOX Services, Savannah River Site, via fax: MOX Services has determined that some welds on modular frame assemblies supplied by Shaw SSS Fabricators in Addis, LA do not comply with procurement documents and require repair. It is unknown by MOX Services if Shaw SSS Fabricators supplied any assemblies to other facilities. Individual informing the Commission was David Del Vecchio, President and Project Manager, CB&I AREVA MOX Services, Savannah River Site, P.O. Box 7097, Aiken, SC 29804-7097. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-04-26
52707 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-04-25 16:30 | 2017-04-25 17:53 | 2017-04-25 | ENGINEERING RE-EVALUATION OF TORNADO IMPACTS "Following engineering evaluation of tornado missile protection, the Emergency Diesel Generator (EDG) 7 day tank vent piping is subject to potential damage for EDGs D, 3A, 3B, 3C, and 3D. In the event that a tornado missile impact occurs on the aforementioned ventilation piping, there is a possibility that the vent lines could crimp. This could prevent the tanks from venting and would inhibit the transfer of fuel oil from the 7 day tank to the associated EDG. As a result, EDGs D, 3A, 3B, 3C, and 3D are inoperable for tornado missile protection and the Tech Spec actions cannot be met. "These conditions are reportable IAW 10CFR50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "This issue is being addressed IAW EGM 15-002, Revision 1, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance. "The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-04-25
52706 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-04-25 | 2017-04-25 15:45 | 2017-04-25 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE STUCK SHUTTER The following report was submitted via e-mail: "On April 25, 2017, the Agency [Texas Department of State Health Services] was contacted by a licensee to report that a gauge would not close during a preventive maintenance check and the shutter is stuck. The gauge is an Ohmart SH-F1A, serial number 6228GK, containing a 50 mCi Cs-137 source. The shutter is stuck in the normal [open] operating position. The licensee is in contact with the manufacturer for a repair plan and with licensing for an exemption to operate the gauge temporarily with a stuck shutter. No exposures to the public are expected." Texas Incident: I-9480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-05-03
52705 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2017-04-25 09:00 | 2017-04-25 14:53 | 2017-04-25 | FUEL HANDLING BRIDGE RADIATION MONITOR OUT OF SERVICE "On April 25, 2017 at approximately 0900 [EDT], it was identified that power to RM-G8 Area Gamma Radiation Monitor for the Fuel Handling Building Bridge, had not been restored within 72 hours. RM-G8 was de-energized during the B train essential bus outage and was restored on April 25, 2017 at 1148. It was out of service for approximately 92 hours. Compensatory measures were in place per HPP-904 while RM-G8 was out of service. "RM-G8 is identified in the emergency plan as an equipment important to emergency response. NUREG-1022, Rev. 3 Supplement 1 Event Report Guidelines 10 CFR 50.72(b)(3)(xiii), allows a 72 hour planned outage time to restore equipment important to emergency response. "Since RM-G8 was not restored in 72 hours, it is reportable as an 8 hour ENS. "This event should have been reported when it was known that the 72 hour outage time was not going to be met. This issue has been entered in the station's corrective action program." Fuel inspections were occurring during this time with compensatory measures in place. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-04-25
52704 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-04-20 12:30 | 2017-04-21 17:05 | 2017-04-21 | AGREEMENT STATE REPORT - UNSECURED RADIOGRAPHY CAMERA The following report was received from the State of Louisiana via email: "Event type: The source/exposure device, a QSA Global 880D s/n # D11837 loaded with 86.7 Ci Ir-192 source s/n #53959G, was left in an unlocked transport buggy and left unattended while the crew took a work break and moved to another work location at the site. Three crew members were in the area, but could not maintain surveillance of the unsecured source. The Bechtel Safety Officer walked up to the transport vehicle and observed the exposure device not secured or locked in the transport vehicle and the Mistras personnel did not have direct surveillance of the transport vehicle. The source incident was reported to the Mistras Group's RSO. Human error, operator distracted. "Notifications: LDEQ [Louisiana Department of Environmental Control] was notified directly by [the Mistras Group's RSO] to an inspector during office hours approximately 1600 [CDT] on 04/20/2017. "Event description: On 04/20/2017, approximately 1230 [CDT], the Bechtel Safety Office, BSO, made a site visit to where a Mistras Group crew was working on a liquid natural gas pipeline in Cameron Parish. The BSO observed an exposure device in an unlocked and unattended Mistras vehicle. The Mistras crew was working at this temporary jobsite and moved to help another crew member working at the site. The crew became distracted and left the vehicle unattended and unlocked. The BSO contacted the Mistras RSO about the incident. [The Mistras RSO] investigated and reported the incident to LDEQ. The incident was under control with no possible radiation exposures to the crew members or the general public. "A LDEQ investigator was contacted to follow-up on the report." Event Report ID No.: LA-17005. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-05-01
52703 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-04-20 | 2017-04-21 14:37 | 2017-04-21 | AGREEMENT STATE REPORT - DELIVERED DOSE LESS THAN PRESCRIBED DOSE The following information was provided by the State of South Carolina via email: "On April 21, 2017, the licensee provided notification of a medical event that occurred on April 20, 2017. The licensee stated that a patient was administered a dose of Y-90 SIR-Spheres for treatment of a liver tumor. During the treatment process, the tubing used to administer the SIR-Spheres became clogged, and the full dose could not be administered. The prescribed dose for the patient was 120 Gy. The dose delivered to the patient was 90 Gy. The licensee indicated that the required written report detailing the event is being completed, and will be submitted to the Department [South Carolina Department of Health and Environmental Control] within the next few days. Updates to this event will be made through the NMED system." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-05-01
52702 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2017-04-20 14:49 | 2017-04-21 11:28 | 2017-04-21 | TECHNICAL SPECIFICATION REQUIRED REPORT FOR AN ABNORMAL OCCURRENCE "On 4/20/17 at 1449 CDT, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to a failure of the regulating blade drive mechanism to move the regulating blade during reactor operation. This email is a required notification per MURR Technical Specification (TS) 6.6.c. (1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by MURR TS 1.1, had occurred. Specifically, MURR was not in compliance with all Limiting Conditions for Operations (LCOs). MURR was not in compliance with two (2) LCOs: 1. TS 3.2.a states, 'All control blades, including the regulating blade, shall be operable during reactor operation' and 2. TS 3.2.f states, 'The reactor shall not be operated unless the following rod run-in functions are operable.' Specifically, the rod run-in function that occurs when the regulating blade position is less than or equal to 10% withdrawn was not operable as TS 3.2.f.8 requires. "The regulating blade drive mechanism was repaired, the required compliance procedure was conducted on the regulating blade, and permission from the Acting Facility Director was obtained prior to the reactor returning to operation later on 4/20/17. Currently, MURR is at 10 MW. A detailed event report will follow within 14 days as required by MURR TS 6.6.c.(3). "The cause of this event is not related to the cause of the earlier regulating blade drive mechanism failure on 1/17/17." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2017-04-21
52701 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2017-04-21 02:02 | 2017-04-21 07:33 | 2017-06-13 | HIGH SWITCHYARD VOLTAGE RENDERS BOTH OFFSITE CIRCUITS INOPERABLE "On 4/21/17, high grid voltage conditions were experienced, resulting in voltages higher than those established for operability of the offsite circuits. Grid voltages have been observed at approximately 355.8 kV on the nominal 345 kV system. As a result, both qualified circuits between the offsite transmission network and the onsite Class 1E AC Electrical Power Distribution System were declared inoperable at 0202 hours [EDT]. Main generator voltage control has been lowered to the minimum possible excitation with the unit operating at 100 percent power. "The inoperability of both offsite circuits results in a loss of safety function in accordance with NRC reporting guidance. The voltage of the onsite Essential busses remains within acceptable values, and both Emergency Diesel Generators are operable. At 0715 [EDT] on 4/21/17, grid voltage has returned to an acceptable value and the equipment was declared operable. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM ANDREW MILLER TO VINCENT KLCO ON 6/13/17 AT 1128 EDT * * * "Following the reporting of high switchyard voltage on 4/21/17, the licensee-established voltage limits were re-evaluated. The new high voltage limit has been established at 362.94 kV on the nominal 345 kV system, or 105.2 percent of nominal voltage, as compared to the previous maximum grid voltage of 103.3 percent. This new limit is above the 355.8 kV experienced on 4/21/17. Therefore, the equipment remained operable and no loss of safety function existed for the qualified circuits between the offsite transmission network and the onsite Class 1E AC electrical power distribution system, and the notification made per 10 CFR 50.72(b)(3)(v)(A-D) is being retracted. "An evaluation of the past three years of switchyard voltage data was also performed, and it was concluded the AC power system and its connected safety-related equipment remained capable of performing its required safety functions during the three-year evaluation period. "The NRC Resident Inspector has been briefed on the evaluation results and informed of this retraction." Notified the R3DO (Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2017-04-21
52700 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2017-04-20 23:45 | 2017-04-21 05:41 | 2017-04-21 | VALID REACTOR PROTECTION SYSTEM ACTUATION WHILE SHUTDOWN "At 2345 [EDT] on 04/20/2017, the Unit 1 Reactor Mode Switch was taken to the Shutdown position to comply with Technical Specification 3.10.4 due to having no operable IRM's [Intermediate Range Monitors] in one quadrant of the reactor vessel as a result of maintenance activities. Placing the mode switch to Shutdown inserts a valid scram signal into the Reactor Protection System (RPS). All control rods had been previously inserted and no rod movement occurred when the mode switch was positioned to Shutdown. "Due to this valid RPS scram, and not being a part of a preplanned evolution, this condition is reportable under criteria 50.72(b)(3)(iv)(A) as an event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-04-21
52699 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-04-20 21:10 | 2017-04-20 21:36 | 2017-04-21 | UNUSUAL EVENT DECLARED DUE TO HYDRAZINE IN CONTAINMENT "At 2110 EDT, Salem control room received data that supported unacceptable levels of hydrazine concentration in the U2 Containment atmosphere based on Site Protection atmospheric sampling. The high hydrazine levels were caused due to Steam Generator [S/G] venting into the Containment atmosphere in support of maintenance for the current Salem Unit 2 Refueling Outage (2R22). The NIOSH habitability limit for hydrazine is 0.03 ppm (2 hour limit). Area samples indicated concentrations as high as 0.25 ppm. Salem Unit 2 Containment has been evacuated while a mitigation plan is being developed. There were no personnel injuries as a result of this occurrence. Salem Unit 2 defueling activities were in progress during this event. All fuel assemblies have been placed in a safe condition. All Salem Unit 2 Containment activities are currently on hold. There has been no impact to the equipment in the Unit 2 Containment, no adverse impact to any equipment located in the vicinity of the high hydrazine concentration, and no operational impact to the plant including Shutdown Cooling which is currently on RHR." The Unusual Event was declared under EAL HU3.1, Toxic/Flammable Gas Release Affecting Plant Operations. The licensee plans to issue a press release. The licensee notified the NRC Resident Inspector, Lower Alloways Creek Township, State of New Jersey and State of Delaware. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATED FROM JOHN COOK TO DONALD NORWOOD AT 1305 EDT ON 4/21/2017 * * * "Salem Unit 2 terminated the Unusual Event at 1258 EDT on 4/21/17. The basis for termination was no longer restricting access to the containment after getting two sets of satisfactory air sample results. With the access restored, normal plant operations can resume and EAL HU3.1 is no longer applicable. "The details of the sample results are: Fire Protection performed satisfactory results of no detectable Hydrazine (0.01 ppm with a NIOSH limit of 0.03 ppm) completed both at 1001 EDT and 1247 EDT at the following locations: - (3) at 130 ft. elevation - at 78 ft. in the bioshield - at 78 ft. outside the bioshield. "Additional mitigating actions taken following U2 Containment evacuation were as follows: - FME screen installed on open manways for 21/23 S/G with additional plastic covering and tape to prevent further gas release into containment. - Modified Containment Purge in service to maximize ventilation in Containment. - 21/24 S/G draining to support filling and draining evolutions to reduce Hydrazine concentrations in the S/G's. - Releasing tags on the AFWST to commence filling and further support filling and draining evolutions on the U2 S/G's." The licensee notified the NRC Resident Inspector. Notified R1DO (Arner), NRR EO (King), and IRD (Stapleton). Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Refueling; FMode2: Refueling | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-04-20
52698 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2017-04-20 13:06 | 2017-04-20 19:13 | 2017-04-20 | SEISMIC MONITOR PANEL NON-FUNCTIONAL "At 1306 [EDT] on April 20, 2017, Control Room Overhead Alarm C6-C4, Seismic Monitor Panel, was received. This alarm normally indicates an actuation of the Hope Creek OBE [Operational Basis Earthquake] Seismic Switch at 0.1g, however, this alarm was accompanied by no other indications of seismic activity. The indicator for a 0.01g earthquake was not actuated, no earthquake was felt on site, and the National Earthquake Information Center recorded no seismic activity in the area. "The Seismic Monitor Panel was considered non-functional. With the Seismic Monitor Panel non-functional, the ability to classify EAL HA1.1, Operating Basis Earthquake Detected Onsite, was lost. Testing of the Seismic Monitor Panel is in progress to determine system functionality." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-04-20
52697 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2017-04-12 | 2017-04-20 15:38 | 2017-04-20 | AGREEMENT STATE REPORT - LESS THAN INTENDED DOSE ADMINISTERED TO THE PATIENT The following information was provided by the State of New York via facsimile: "On 04/12/2017, a patient with widespread neoplasm of liver, intrahepatic bile duct, received treatment with Y90 SIRTEX microspheres to 2 separate segments in the right lobe. The intended activities were 0.946 GBq (25.6 mCi) to a small segment and 2.38 GBq (64.3 mCi) to the large segment. "On 4/18/17, during a review of the patient's medical record, the AU [authorized user] physician discovered that the activity ordered for the large lesion was 0.38 GBq, not 2.38 GBq, as the written directive had stated. NYS DOH [New York State Department of Health] was informed on 4/19/17. Both the patient and the referring physician have been informed. AU physician stated that there is no harm to the patient, because they plan to administer the deficit dose to this segment in the right lobe during the procedure scheduled to treat the left lobe next month. "The licensee stated that documentation/communication appears to be the primary cause. Facility is investigating. Will update when more information becomes available." NY Event Report ID No. NYDOH-NY-17-07 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-04-28
52696 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2017-04-20 03:02 | 2017-04-20 05:57 | 2017-04-20 | AUTOMATIC REACTOR SCRAM DURING STARTUP "On 04/20/2017 at 0302 EST during a reactor startup, a reactor scram resulted from upscale spike on two Intermediate Range Monitors (IRMs), 1C51K601A and 1C51K601B. IRM A, 1C51K601A is in Reactor Protection System Channel A and IRM B, 1C51K601B is in Reactor Protection System Channel B. All control rods fully inserted. No PCIS [Primary Containment Isolation System] actuations occurred and none were expected to occur based upon plant condition following the reactor scram. "Investigation is in progress. Condition was not due to a true flux event. "This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) as an event or condition that resulted in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. "CR 10356172 "The NRC Resident has been notified." The reactor was at 0.5% (percent) power at the time of the event and will remain in Hot Shutdown pending the results of the root cause investigation. | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-04-20
52695 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2017-04-19 | 2017-04-19 17:30 | 2017-04-19 | AGREEMENT STATE REPORT - CONTAMINATED PACKAGE The following was received from the State of New Jersey via email: "The RSO [Radiation Safety Officer] for this radiopharmacy called to report the receipt of a contaminated package. The package arrived from another Zevacor facility located in Virginia (Virginia license # 107113-1). The package as shipped contained 21 mCi of liquid Zr-89. While performing their routine wipe test during the opening of the package, the wipe test of the inner package found removable contamination of 240,000 counts per minute. The outer package was not found to be contaminated. The RSO of the New Jersey facility contacted their counterpart at the Virginia facility. The Virginia facility maintained that the package was free of contamination when it was shipped. Zevacor believes the primary container was not sealed properly. This may have caused some of the material to evaporate during shipment and contaminate the exterior of the primary container. A written report will be supplied within 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2017-04-27
52694 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2017-04-18 12:10 | 2017-04-19 11:31 | 2017-04-21 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was provided by the State of Arkansas via email: "On April 18, 2017, at 1210 [CDT], the licensee contacted the Department [Arkansas Department of Health] reporting that a moisture density gauge was missing from the permanent storage facility in Hot Springs, Arkansas and presumed stolen. In addition to the Department, the licensee had notified local law enforcement offices. "The licensee believes that the gauge was taken between Friday, April 14, 2017 and Tuesday morning, April 18, 2017. The licensee believes that the gauge may be in possession of a former employee. "The gauge is a Troxler, Model 3440, Serial Number 15160, containing 40 milliCuries of Americium-241 and 8 milliCuries of Cesium-137. "In accordance with RH-1501.c.1.A. (10 CFR 20.2201(a)(1)(i)) the stolen gauge is immediately reportable. "Law Enforcement is investigating. "The State of Arkansas is awaiting the outcome of the law enforcement investigation and a written report from the licensee. The State's event number is AR-2017-001." * * * UPDATE FROM DAVID STEPHENS TO DONALD NORWOOD AT 1338 EDT ON 4/20/2017 * * * The following information was received via E-mail: "The Arkansas Department of Health Radiation Control Section received notification that the Troxler Electronic Laboratories Gauge (Model 3440, Serial Number 15160) reported stolen on April 19, 2017, was recovered in Hot Springs Village by the Garland County Sheriff's office. The gauge does not appear to be damaged, and has been transported to the licensee's permanent storage location. A leak test has been performed by the licensee. The Department considers the matter closed pending receipt of the licensee's report and leak test results." Notified R4DO (Azua), ILTAB (Salisbury), and NMSS Events Notification Group. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2017-04-27
52693 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-12-31 | 2017-04-19 10:59 | 2017-04-19 | AGREEMENT STATE REPORT - RADIOGRAPHER OVEREXPOSURE The following report was received via e-mail: "On April 14, 2017 we [Oklahoma Department of Environmental Quality] learned that a certified radiographer employed by Tulsa Gamma Ray (OK-17178-02) received a TEDE of 5.808 REM for calendar year 2016. The licensee was unaware of this until it was pointed out by the inspectors during their routine inspection." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2017-04-27
52692 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2017-02-27 | 2017-04-19 10:29 | 2017-07-12 | PART 21 REPORT - CONTROL ROD DRIVE MECHANISMS CONTAMINATED WITH CHLORIDES Dale E. Porter GE-Hitachi Nuclear Energy Safety Evaluation Program Manager 3901 Castle Hayne Rd., Wilmington, NC 28401 (910) 819-4491 Dale.Porter@GE.Com "The inappropriate addition of chlorinated water from container box desiccants into the CRDMs [Control Rod Drive Mechanisms] during leak testing after rebuild could potentially initiate Intergranular Stress Corrosion Cracking (IGSCC) or Transgranular Stress Corrosion Cracking (TGSCC). These two types of SCC could cause a separation of the stop piston or separation of the index tube contained within the CRDM. The stop piston separation could cause a slower scram speed and damage the drive so it could not be withdrawn. An index tube separation could result in a similar type of rod uncoupling event that would have the potential to result in a rod drop accident (RDA). The piston tube located within the CRDM is a reactor coolant pressure boundary (RCPB) and is an ASME component. There is a possibility of cracking causing a RCPB leak. SCC initiation on the Cylinder Tube and Flange (CTF) area of the CRDM could result in a separation that could prevent a scram or normal insertion of a CRDM. "Reports have been issued to River Bend, LaSalle Unit 2, and Hatch Unit 2 providing the results of an evaluation that concludes that the condition will not create a substantial safety hazard or potentially cause a Technical Specification Safety Limit violation for a minimum of one operating cycle. The Browns Ferry Unit 2 drives were shipped but were not installed prior to recall, thus a short-term evaluation for Browns Ferry has not been completed. "River Bend, Entergy, Shipped Date: 2017, Quantity Shipped: 15, Customer PO Number: 10478763 LaSalle Unit 2, Exelon, Shipped Date: 2017, Quantity Shipped: 24, Customer PO Number: 00414787-66 Hatch Unit 2, Southern Nuclear, Shipped Date: 2017, Quantity Shipped: 15, Customer PO Numbers: SNG50295-0001 & SNG50295-0002 Browns Ferry Unit 2, TVA, Shipped Date: 2017, Quantity Shipped: 32, Customer PO Number: 2424171" * * * UPDATE ON 7/12/17 AT 1035 EDT FROM LISA SCHICHLEIN TO BETHANY CECERE * * * "Pursuant to 10 CFR 21.21(d)(4), GEH is providing the final report with the conclusion that, in limited cases, the chloride contamination could create a substantial safety hazard. Attachment 1 identifies the potentially impacted plants and Attachment 2 contains the final report information. The enclosure provides additional details of the evaluation. Updated Attachment 1 notes: "A portion of the CRDMs at the Hatch Plant are Reportable while the remainder are not. Summary of updates to Attachment 2: "The inappropriate addition of chlorinated water from container box desiccants into the CRDMs during leak testing after rebuild could potentially initiate Intergranular Stress Corrosion Cracking (IGSCC) or Transgranular Stress Corrosion Cracking (TGSCC). These two types of SCC were initially considered for the potential to cause a separation of the stop piston or separation of the index tube contained within the CRDMs that are constructed of 304 Stainless steel. The completed evaluation indicates that a stop piston separation could cause a slower scram speed and damage the drive so it could not be withdrawn. The potential exists for the control rod to drift out. The piston tube located within the CRDM is a reactor coolant pressure boundary (RCPB) and is an ASME component. The possibility of cracking causing RCPB leakage was eliminated by the evaluation. An index tube separation was eliminated as a potential failure mode. Likewise, the potential for SCC initiation on the Cylinder Tube and Flange (CTF) area of the CRDM resulting in a separation that could prevent a scram or normal insertion/withdrawal of a CRD was eliminated. "The long-term evaluation concluded there is no concern for TGSCC. This evaluation also determined the stop piston to piston tube separation is the only failure mechanism that could occur, and only if those components were manufactured from 304 SS. "GEH initiated a Root Cause Evaluation (RCA) to determine why this event occurred and has implemented process changes to ensure that the condition does not reoccur. Actions to prevent recurrence, such as eliminating the desiccant material and flushing the closed loop water system, have been completed. "For Hatch Unit 2, the 12 CRDMs that have the 304 SS piston tubes should be replaced prior to those CRDMs exceeding 10 years in service. See table below: CRDM S/N, Piston Tube SE0474, 304 SS A8737, 304 SS A9423, 304 SS A6791, 304 SS 3095, 304 SS A8729, 304 SS 7253, 304 SS A6786, 304 SS SE0368, 304 SS A5409, 304 SS 7080, 304 SS A9484, 304 SS "Interim Reports were issued to River Bend, LaSalle Unit 2, and Hatch Unit 2 providing the results of an evaluation that concluded the condition would not create a substantial safety hazard or potentially cause a Technical Specification Safety Limit violation for a minimum of one operating cycle. The Browns Ferry Unit 2 drives were shipped but were not installed prior to recall, thus a short-term evaluation for Browns Ferry was not provided. "GEH has completed the long-term CRDM evaluation with the following results: "A Safety Information Communication is being issued to River Bend, LaSalle Unit 2, and Browns Ferry Unit 2 stating that the CRDMs exposed to the chloride intrusion will not cause a substantial safety hazard, or cause a Technical Specification Safety Limit violation and is therefore not reportable (see enclosure 1 for details). "For Hatch Unit 2, the introduction of chlorides could cause a substantial safety hazard for the 12 CRDMs that were manufactured from 304 SS material, and is therefore a reportable condition per 10CFR 21.21(d); however, the 3 CRDMs manufactured from XM-19 material would be considered not reportable. "The results of the short-term evaluations for all three plants where CRDMs were installed remains valid." Notified the R2DO (Bonser), R3DO (Peterson), R4DO (Proulx), and Part 21/50.55 Reactors Group by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-04-19
52691 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2017-04-18 02:30 | 2017-04-18 19:25 | 2017-04-18 | FAILURE OF THE RADIOGRAPHY CAMERA LOCKING MECHANISM After performing a routine exposure with a QSA model 880D (serial number D8127) camera containing a 133 curie Iridium-192 source, the source was cranked back into the camera. The radiographer noted that the outer locking mechanism did not lock. The source was let out again then retracted. The camera locking mechanism worked the second time. The locking mechanism did not work because of the icing condition. The radiography camera was placed in a warmer environment, and the locking mechanism was retested. No overexposure occurred during the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-04-26
52690 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-04-17 | 2017-04-18 16:58 | 2017-04-18 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following information was provided by the State of California via email: "On 04/17/17, Ninyo & Moore RSO [Radiation Safety Officer] contacted RHB [California Radiologic Health Branch] to report a moisture density gauge incident happened at a construction site in the City of Hayward, CA. The gauge involved was a Troxler 3430, S/N T343 32379 containing 8 mCi of Cs-137 and 40 mCi of Am-241. The gauge was backed into by a Bobcat. Technician was performing a density test and happened to be about 12 feet away from the gauge at the time of the incident. After the incident, the technician requested the personnel to clear the area. The gauge source rod was bent and could not be retracted into the shielded position. The area was isolated and the gauge was placed next to a concrete slab until help arrived. The RSO immediately contacted a gauge vendor, PNT [Pacific Nuclear Technology], and the RSO from PNT arrived on site within a short period of time. He placed a lead pig around the exposed source rod, loaded up the gauge in his truck and took it away for repair. PNT performed a survey around the incident site and no contamination was detected. RHB will be following up on this incident." CA 5010 Number: 041717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-04-26
52689 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-04-18 11:00 | 2017-04-18 15:55 | 2017-04-18 | FITNESS FOR DUTY REPORT - FALSE NEGATIVE OCCURRED ON QUALITY ASSURANCE TEST The testing laboratory returned results for a blind specimen that was inconsistent with what was expected. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2017-04-18
52688 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2017-04-18 11:30 | 2017-04-18 14:57 | 2017-04-18 | FITNESS-FOR-DUTY TEST POSITIVE FOR A NON-LICENSED SUPERVISOR "A non-licensed employee supervisor had a confirmed positive for a prohibited substance during a random fitness-for-duty test. The individual's unescorted access to the plant has been suspended. "The licensee has notified the NRC Resident [Inspector]." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2017-04-18
52687 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-04-18 09:31 | 2017-04-18 11:14 | 2017-04-20 | SAFEGUARDS REPORT An contractor individual failed to disclose derogatory information which would have precluded unescorted access. The information was provided after the individual's access was terminated. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 4/20/17 AT 1533 EDT FROM LANCE STERLING TO DONG PARK * * * "The purpose of this report is to retract the ENS 52687 report made 04/18/2017 at 1014 CDT under 10 CFR 73.71. Specifically, 10 CFR 73.71, Appendix (G)(I)(b) for actual entry of an unauthorized person into a protected/vital areas." The licensee has notified the NRC Resident Inspector. Notified R4DO (Azua) and 73.71 Safeguards group via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-04-18
52686 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2017-04-18 | 2017-04-18 10:17 | 2017-04-18 | AGREEMENT STATE REPORT - LOST SOURCE The following information was received from the State of New Jersey via facsimile: "The RSO [Radiation Safety Officer] for this cardiology office called to report a lost/missing Cs-137 dose calibrator vial source. Control of this facility was recently transferred to a medical center. When the new RSO visited the cardiology office to become familiar with it, it was discovered that the Cs-137 source was missing. The source, as listed on the cardiology office's inventory, contained 199.04 uCi [microCuries] of activity as of its calibration date of 9/1/2005. The decayed source would contain approximately 152.2 uCi [microCuries] of activity as of the date of this notification. The manufacturer and model # of the source were not immediately available. The RSO will follow-up with a written report within 30 days." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2017-04-26
52685 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-02-17 10:21 | 2017-04-17 13:35 | 2017-04-17 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "On February 17, 2017 at 1021 EST, secondary containment isolated and Standby Gas Treatment (SBGT) systems started on Unit 1 and Unit 2 during a maintenance activity to replace a relay in the Unit 2 primary containment isolation system. The work was being conducted as part of planned maintenance during the Unit 2 refueling outage. Poor work instruction led to a jumper not being installed as required, thus causing relays to de-energize, resulting in an invalid actuation of the Unit 1 and Unit 2 outboard primary and secondary containment isolation valves and auto-start of the Unit 1 and Unit 2 SBGT system. "This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) since the containment isolation and auto-start of SBGT on both units was not part of a pre-planned sequence and the event resulted in the invalid actuation of general containment isolation valves in more than one system. "All primary and secondary containment isolation valves and SBGT systems functioned successfully. The associated wires were re-landed and secondary containment was returned to normal service. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-04-17
52684 | 0 | US COAST GUARD |  |  |  |  | 2017-04-17 | 2017-04-17 13:00 | 2017-04-17 | UNACCOUNTED STRONTIUM-90 SOURCES The U.S. Coast Guard did not properly dispose of Inflight Blade Inspection Systems (IBIS) containing 100 microCurie, Sr-90 sources during the retirement of 72 HH-52 aircrafts from 1987 to 1989 and 50 HH-3 aircrafts from 1990 to 1994. The HH-52 contain 3 canisters and HH-3 contain 5 canisters, each canister contain a 100 microCurie, Sr-90 source. Most canisters were retrieved and returned to the manufacture, General Nucleonics, Inc. The licensee has notified R1 (Jackson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-04-25
52683 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-04-17 00:04 | 2017-04-17 07:40 | 2017-04-17 | AUTOMATIC ACTUATION OF EMERGENCY DIESEL GENERATORS "On April 17, 2017, at 0004 Eastern Daylight Time (EDT), an automatic actuation of the four Emergency Diesel Generators (EDGs) was received. At the time of the event, Unit 2 was in the process of starting the main turbine following a refueling outage. Operations personnel tripped the main turbine due to elevated bearing vibrations. When the main turbine was tripped, Power Circuit Breakers (PCBs) 29A and 29B failed to open. This caused a main generator primary lockout due to generator reverse power and the subsequent automatic actuation of all four EDGs. All emergency buses remained energized from offsite power and therefore, the EDGs did not tie to their respective buses. The protective relaying and EDGs responded per design to this event. This event is being reported in accordance with 10 CFR 50.73(b)(3)(iv)(A) as an event that results in a valid actuation of the EDGs. Due to the shared configuration of the Brunswick electrical system, both Unit 1 and Unit 2 are affected. "This event did not impact public health and safety. The NRC Resident lnspector has been notified." | 100 | 22 | 0 | 100 | 22 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-04-17
52682 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2017-04-15 04:41 | 2017-04-15 13:03 | 2017-04-15 | VALID REACTOR PROTECTION SYSTEM AND PARTIAL PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATIONS ON LOW WATER LEVEL "During shutdown activities with the reactor subcritical, actions were being taken to remove 11 Reactor Feed Pump from service in support of a scheduled refueling outage. Reactor Water Level on Safeguards level instrumentation dropped below +9 inches, which resulted in a valid Reactor Protection System (RPS) Scram signal and Partial Group 2 Primary Containment Isolation System (PCIS) signal. All systems functioned as required. Reactor Water Level on Safeguards instrumentation was restored to greater than +9 inches immediately. RPS and PCIS logic was reset. There was no impact to the health and safety of the public as a result of this event. "This actuation of these systems is being reported per 10 CFR 50.72(b)(3)(iv)(A) as an event that resulted in a valid actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-04-15
52681 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-04-14 13:57 | 2017-04-14 16:45 | 2017-04-14 | UNPLANNED EMERGENCY DIESEL GENERATOR START DUE TO LOSS OF A 4160 V BUS "At 1357 [EDT] on April 14, 2017, an unplanned automatic start signal was generated for the 2C Emergency Diesel Generator (EDG). The station was in the process of transferring the 2C 4160 volt vital bus from the 24 Station Power Transformer (SPT) to the 23 SPT, which are the offsite power in-feeds for the 2C 4160 volt vital bus. The 24 SPT infeed breaker opened as expected; however, the 23 SPT infeed breaker failed to close. The failure to swap from the 24 SPT to 23 SPT resulted in a momentary loss of power to the 2C 4160 volt vital bus generating the automatic start signal for the 2C EDG. The 2C 4160 volt vital bus was automatically re-energized by the 2C EDG as expected. "Abnormal operating procedures were entered for loss of the 2C 4160 volt vital bus. Salem Unit 2 was in Mode 1 operating at 100% power. All equipment operated as expected. "At 1555 [EDT], 2C 4160 volt vital bus was reenergized from 24 SPT, and the 2C EDG was secured in accordance with station implementing procedures. "There was no impact to the health and safety of the public. The Resident Inspector has been notified." The Lower Alloways Creek Township, State of New Jersey, and State of Delaware will be notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-04-14
52680 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2017-04-11 | 2017-04-14 14:38 | 2017-04-14 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was obtained from the Commonwealth of Massachusetts via email: "Licensee reported one leaking sealed source (Model A3901-2, S/N P4-892, 6 mCi, Co-57) and one contaminated sealed source (Model A3901-2, S/N P4-898, 6 mCi, Co-57). These were among ten sources received from manufacturer individually wrapped in plastic ziplock bags. Leak test results for the other eight sources indicated that they were free of contamination. Leak test result for SN P4-892 was reported as 5.04 times the 0.005 microCurie wipe test limit and the leak test result for SN P4-898 was reported as 23 percent of the 0.005 microCurie limit. Leak test wipes were taken on 4/10/17 and analyzed on 4/11/17. "Licensee reported the subject sources were not taken out of their respective bags and did not come into contact with anything other than the leak test swab. Initial survey of the outside of the transport package, and subsequent surveys of gloves worn during the leak testing, work area surfaces, inside the lead pig that contained the plastic bags, and outside the ten individual plastic bags indicated no other contamination present other than the interiors of the two plastic bags containing the two suspect sources and the sources themselves. P4-892 was returned to Eckert and Ziegler for analysis. P4-898 was re-wiped for analysis by licensee's leak testing consultant service. "Agency [Massachusetts Radiation Control Program] considers this event docket to currently be OPEN." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2017-04-24
52679 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-04-14 00:15 | 2017-04-14 07:37 | 2017-04-14 | DRYWELL AND SUPPRESSION CHAMBER SIMULTANEOUSLY ALIGNED FOR VENTING "On April 14, 2017, at approximately 0015 Eastern Daylight Time (EDT), during a control board walk-down, it was discovered that the drywell and the suppression chamber were simultaneously aligned for venting. This alignment created a flow path from the drywell to the suppression chamber, which would have bypassed the pressure suppression function of the suppression chamber water volume during a Loss of Coolant Accident (LOCA). This condition existed tor approximately 43 minutes, from 2347 EDT on April 13, 2017, when Unit 2 transitioned from Mode 4 to Mode 2, until 0030 on April 14, 2017, when the proper alignment was restored. This condition is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Additionally, the change from Mode 4 to Mode 2 with primary containment inoperable constitutes operation prohibited by Technical Specifications (i.e., reportable in accordance with 10 CFR 50.73(a)(2)(i)(B)). "The condition did not impact public health and safety. The NRC Resident Inspector has been notified." Unit 2 entered Technical Specification 3.6.1.1, Primary Containment, Condition A, which requires Primary Containment to be restored to operable within 2 hours. Unit 2 exited Condition A within 43 minutes when the proper alignment was restored. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-04-14
52678 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2016-08-30 | 2017-04-13 15:53 | 2017-04-13 | PART 21 NOTIFICATION - IDENTIFIED FISHER 546S ELECTRO-PNEUMATIC TRANSDUCERS STANDARD MOUNTING BRACKETS FAILED SEISMIC TESTING STANDARDS Fisher Controls International LLC issued Fisher Information Notice FIN 2017-02 to inform users that certain identified Model 546NS electro-pneumatic transducers, when mounted on the supplied standard mounting brackets, were determined to be not adequately robust at seismic test levels. Affected customers have been notified. Fisher requests that the recipient of this FIN review it and take appropriate action in accordance with 10 CFR 21. If there are any technical questions or concerns, please contact: Ben Ahrens Quality Manager Emerson Automation Solutions Fisher Controls International LLC 301 South First Avenue Marshalltown, IA 50158 Phone: (641) 754-2249 Benjamin. ahrens@emerson.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-04-13
52677 | 0 | ABB INC |  |  |  |  | 2017-02-15 | 2017-04-13 14:04 | 2017-04-13 | PART 21 REPORT - VENDOR SUPPLIED INCORRECT RELAYS FOR CLASS 1E APPLICATION In 1993, ABB Switchgear Division supplied 12 ABB Ground-Shield ground fault relays to the Point Beach Nuclear Plant that did not meet the seismic qualifications required of Class 1E rated relays. This deviation is for GKT relay model 202L. If you have any questions regarding this notice, please contact ABB Technical Support at 954-752-6700 or 1-800-222-1946. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-04-13
52676 | 0 | QAL-TEK ASSOCIATES, LLC |  |  |  |  | 2017-04-13 09:40 | 2017-04-13 13:51 | 2017-04-13 | SHIPMENT EXCEEDING PACKAGE DOSE RATE LIMITS The following was received via email from the Licensee: "At 0940 [MDT] on April 13th, 2017 [the common carrier] dropped off a 20 gallon drum (37.8 Kg) at Qal-Tek Associates (QTA) Idaho [ID] facility with an on-contact reading of 1.45 R/hr and a TI [Transport Index] of 15, both in excess of 10CFR20.1906(d)(2). No contamination existed on the inside or outside of the package. Upon further investigation, all three sources (Cs-137, 19.4 mCi; Cs-137, 23 mCi; and Co-60, 2.5 mCi) shipped in a gray lead pig were outside their gray lead pig and in the Type 7A drum. The gray lead pig was found packaged upright in the drum with a slight tilt. The pig lid was intact and properly seated on the pig base. Apparently, the lid was displaced enough during shipment that all three sources came out of the pig by the time they arrive[d] at QTA ID. The root cause appears to be from improper sealing of the gray pig. The pig wasn't taped or strapped shut to prevent displacement of the pig and lid resulting in the release of the sources. "The shipper confirmed the sources where originally placed in the gray pig around 1100 [MDT]. "The [common] carrier was contact[ed] at 1140 [MDT]. Assuming the maximally exposed member of the public was [the common carrier] transport employee, and they were on-contact with the drum at the highest reading, they could have potentially received 100 mrem in a little over 4 minutes. Likewise, they could have received 2 mrem in 5 seconds. Considering the TI of 15 mrem/hour, the MEI [maximally exposed individual] could potentially receive 100 mrem in 6.67 hours and 2 mrem in 0.13 hours." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2017-04-21
52675 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-04-11 | 2017-04-13 12:23 | 2017-04-13 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the state of North Carolina via email: "1. Essential Details "a. Narrative event description (e.g., Event circumstances and details including source radionuclide and activity). RSO [Radiation Safety Officer] discovered gauge missing while doing inventory check on Tuesday, April 11, 2017. It was last checked in the log book on March 8, 2017 when it came back from calibration and leak testing from the manufacturer. "b. Report identification number. NC Local NMED 170014 "c. Event date and notification date. Event discovered 4/11/2017 and notified on 4/12/2017. "d. Licensee/reporting party information (i.e., name license number, and address). NC License #: 092-0104-1 Licensee: NC Department of Transportation Address: 1801 Blue Ridge Rd. Raleigh NC 27607 "e. Location (site) of event. "f. Whether the event is NRC reportable and the applicable reporting requirement. 10 CFR 20.2201(a)(1)(i) "g. Cause and corrective actions (States and licensees' actions). Failure to properly log or check out gauge at time of use. RSO believes that it was checked out to a DOT field office and not properly recorded. They are currently contacting all trainers of gauge users, DOT engineers, and any District Engineers that may have access in order to locate gauge. They are in the process of developing a barcode scan in/out electronic use log to maintain better accountability and knowledge of gauge locations. Final causes/corrective actions are still to be determined. "h. Notifications: local police, FBI, and other States; as needed. Upper State DHSR/DHHS [North Carolina Department of Health Service Regulation/Department of Health and Human Services] management notified; working on press release with public information office. "i. Indicate if there are any generic implications (i.e., generic issues or concerns). None. "2. Source/Radioactive Material Isotope and activity; manufacturer, model and serial number, and leak test results, if applicable. Nuclear Gauge Make: Troxler Model: 4640-B (thin-lift asphalt) Serial Number: 1628 Type of Source: Cs-137 (8.0 mCi) Source Serial Number: 75-7134 Leak Test Results: Pass (Performed by manufacturer at last calibration)." * * * UPDATE FROM DAVID CROWLEY TO HOWIE CROUCH (VIA EMAIL) ON 4/13/17 AT 1535 EDT * * * "Gauge was discovered back at the manufacturer's facility. It apparently was checked back into the licensee, but something didn't work appropriately (not regarding RAM sources) and went immediately back to the manufacturer. Gauge was not logged appropriately for being shipped right back out and it was forgotten by the licensee sometime in the last month." Notified R1DO (Jackson) and NMSS Events Resource and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-04-21
52674 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2017-04-12 15:30 | 2017-04-12 21:06 | 2017-04-20 | LOSS OF THE TECHNICAL SUPPORT CENTER VENTILATION SYSTEM "Oyster Creek Generating Station has experienced a loss of the Technical Support Center (TSC) ventilation system due to charcoal filter test failure. A charcoal filter replacement is planned. "If an emergency is declared requiring TSC activation during the time TSC ventilation is non-functional, the TSC will be staffed and activated using existing emergency planning procedure unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to a loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector will be notified." * * * RETRACTION ON 4/20/17 AT 1447 EDT FROM JIM RITCHIE TO DONG PARK * * * "This is a retraction of ENS notification 52674. After further testing and evaluation, the station concluded that the TSC Ventilation Charcoal filter met the acceptance criteria, and the TSC Ventilation was not inoperable at the moment the original ENS notification was performed." The licensee will notify the NRC Resident Inspector. Notified R1DO (Arner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-04-12
52673 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2017-04-10 | 2017-04-11 14:28 | 2017-04-11 | AGREEMENT STATE REPORT - LEAKING TRITIUM EXIT SIGN The following information was received from the State of Utah via email: "[University] Radiological Health personnel responded to an incident involving a damaged tritium exit sign at the University Guest House. It was determined the damaged exit sign was leaking tritium and the licensee notified the [Utah] Division of Waste Management and Radiation Control. This incident report is the initial notification of the NRC Operations Center." Utah Event Report: UT170003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2017-04-19
52672 | -1 | HARRISON STEEL |  |  |  |  | 2017-04-11 12:00 | 2017-04-11 14:23 | 2017-04-17 | RADIOGRAPHER LOST FILM BADGE IN VAULT "On April 11, 2017 our Radiographic Supervisor dropped his film badge within the exposure vault after the clip had broken. [The individual] was not in the exposure vault during any exposure but his badge will reflect an exposure. His badge has been sent for processing this afternoon. [The individual] was working with another radiographer and their exposure amounts for this day should be comparable as to estimating his true daily exposure amount." * * * RETRACTION ON 4/17/17 AT 1700 EDT FROM AMANDA DILL TO DONG PARK * * * The event was initially reported by the licensee out of caution. Since the event does not meet reporting criteria, this notification is being retracted. The licensee notified R3 (Craffey). Notified R3DO (Kunowski) and NMSS Events Notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2017-04-19
52671 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-04-08 | 2017-04-09 13:46 | 2017-04-09 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILS TO RETRACT PROPERLY The following information was provided by the State of Texas via email: "On April 9, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's Radiation Safety Officer (RSO) that on April 8, 2017, one of his crew was unable to retract a 95 curie iridium-192 source into a Spec 150 exposure device [at a work site 2 miles inside the Texas border near Jal, NM]. The RSO stated that after the first exposure for the day, the radiographers noted they could not lock the source inside the exposure device. The radiographers established a two millirem per hour boundary and evacuated two trailers that were inside the two millirem per hour barrier. The RSO stated the people were in the trailer for five minutes before the radiographers had them leave the area. The radiographers contacted the site RSO who responded to the scene. The site RSO found the guide tube had separated from the front of the exposure device. The site RSO was able to retract the source into the fully shielded position. The RSO stated they believe that sand had built up in the guide tube to camera connection which prevented the guide tube connector to fully seat in the connection. The RSO stated his initial calculations indicated no member of the general public exceeded any exposure limits. No licensee personnel exceeded any exposure limit from this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-04-17
52670 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2017-04-05 | 2017-04-07 14:49 | 2017-04-07 | PART 21 - CIRCUIT BREAKER DEFECT DISCOVERED DURING CURRENT INJECTION TESTING "On April 5, 2017, Arizona Public Service Company (APS) completed an evaluation of a deviation, and concluded the condition represented a defect under 10 CFR 21. APS previously submitted an interim report (ADAMS Accession Number ML 16344A118) for this condition pursuant to 10 CFR 21.21(a)(2). "A GE-Hitachi Type AKR-2BE-50, 2000 Amp circuit breaker (used to connect Class 1E batteries to the related Class 1E 125 VDC busses) exhibited arcing and smoking during current injection testing performed to test the overcurrent trip setpoint prior to installation. Arcing occurred at one of two hex bolts anchoring the protective trip device to the line side bus. The electrical arcing resulted from inadequate tightening of both hex bolts which caused a loose electrical connection on the bus within the breaker. "APS concluded this condition could result in the breaker failing to perform its safety function and thus could create a substantial safety hazard. The breaker had been refurbished by GE-Hitachi and was received by APS and tested on October 13, 2016. Following the test failure, the damaged bolt was replaced, both bolts were tightened, and the breaker was retested and installed. "Pre-installation inspection and testing that includes current injection testing, recommended in GEH document GEK-64459, should, and did, detect faults such as the condition identified in this notification. GE-Hitachi entered this failure into their corrective action program. "Vendor: GE HITACHI NUCLEAR ENERGY, 3901 CASTLE HAYNE RD., WILMINGTON, NC 28402-2819 "Device: Breaker Model AKR-2BE-50, 2000 Amp, Serial No. N8682600001 "The NRC Resident Inspector has been informed." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2017-04-07
52669 | -1 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-04-06 16:20 | 2017-04-06 22:40 | 2017-05-18 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 1620 EDT on April 6, 2017, a Main Control Room (MCR) door was found ajar. At that time, both control room ventilation filtrations trains (CREVS) were declared inoperable in accordance with Technical Specification 3.7.10, condition B, due to the inoperability of the Control Room Envelope (CRE). At 1623 EDT, the door was closed, CREVS was declared operable and LCO 3.7.10, Condition B was exited. "The safety function of the CRE boundary is to ensure the in-leakage of unfiltered air into the CRE will not exceed the in-leakage assumed in the licensing basis analysis of Design Basis Accident (DBA) consequences to CRE occupants. Additionally, it ensures that the occupants are protected from hazardous chemicals and smoke. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D). "NRC Resident Inspector has been notified." * * * RETRACTION FROM DAVID ALLEN TO S. SANDIN ON 5/18/17 AT 1459 EDT * * * "Event Notification EN 52669, made on 4/06/2017, is being retracted because additional reviews have been performed supporting that a loss of safety function did not occur. "Watts Bar Unit 2 has concluded that there was no loss of safety function, because when the door was found open it was capable of being closed and able to support the control room envelope function. A simulation performed on 04/07/17 also showed that with the door in question opened 1-2 inches that the control room pressure would have remained above the TS required positive pressure of 0.125 inches of water. "The control room envelope is designed such that the door is expected to be opened to allow personnel entry and exit, and thus positive pressures in the control room will fluctuate. The event that occurred is similar to a number of individuals entering and exiting the control room in series. Since the control room envelope function was not lost, this event is not reportable and NRC Event Number 52669 is being retracted. The basis for this conclusion will be provided to the NRC Resident Inspector." The licensee informed the NRC Resident Inspector. Notified R2DO (Blamey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-04-06
52668 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2017-04-06 09:48 | 2017-04-06 15:58 | 2017-04-06 | FITNESS FOR DUTY VIOLATION A contractor manager had a confirmed positive for alcohol during a pre-access test. The employee's access to the construction site has been revoked. The licensee notified the NRC Unit 2 & 3 Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2017-04-06
52667 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2017-04-05 | 2017-04-06 12:11 | 2017-04-06 | AGREEMENT STATE REPORT - LESS THAN PRESCRIBED DOSE ADMINISTERED TO PATIENT The following information was provided by the State of New York via facsimile: "On 04/05/2017, a patient with metastatic esophageal cancer received right hepatic lobar treatment [to the liver] with Y90 from SIRTEX microspheres. "The intended activity was 32.9 mCi. Drawn activity was 32.7 mCi. The administered activity measured at the end of the procedure was 8.2 mCi [25 percent of intended activity]. "Probable cause stated by the licensee: 'clumping' of microspheres resulting in occlusion of vial 'delivery C' needle provided by the vendor. The licensee plans to (1) request review from the manufacturer of the preparation and handling of the microspheres prior to arrival to the IR suite, (2) Since the patient is already planned for a left lobar treatment, a whole liver treatment will be planned to deliver the deficit dose to the right lobe." NY Event Report ID No. NYDOH-NY-17-06 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-04-14
52666 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2017-04-05 14:00 | 2017-04-05 16:32 | 2017-04-06 | UNANALYZED CONDITION FOR BOTH EDG TRANSFER LINE CONNECTIONS "Both Emergency Diesel Generators [EDGs] have truck connections connected to transfer lines that are potentially not compliant with general design criteria. A potentially unanalyzed condition exists due to threat of tornado generated missiles. "While in Mode 1 at 100% power, the Control Room was notified that the outdoor portion of the line upstream of JEV0001, EMERG FUEL OIL STORAGE TK A TRUCK CONN ISO, and the outdoor portion of the line upstream of JEV0002, EMERG FUEL OIL STORAGE TK B TRUCK CONN ISO, potentially have not been reviewed to meet general design criteria. "No major equipment was out of service. No systems were required to respond to this event. The unit remains in Mode 1 at 100% power. "The NRC Senior Resident Inspector has been notified. "Compensatory measures have been established IAW [in accordance with] EGM 15-002." The Unit entered Tech Spec 3.8.1 Condition B and D for approximately 45 minutes until compensatory measures were put into effect. The licensee identified this condition during a design review and is currently identifying long-term corrective actions. * * * UPDATE ON 4/6/17 AT 0938 EDT FROM DAVID GHOLSON TO DONG PARK * * * The Unit entered Tech Spec 3.8.1 Condition B and F, not Tech Spec 3.8.1 Condition B and D mentioned earlier. Notified R4DO (Vasquez). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2017-04-05
52665 | -1 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2017-04-05 09:23 | 2017-04-05 10:23 | 2017-04-05 | SAFEGUARDS REPORT - DEGRADED SAFEGUARDS SYSTEM Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. * * * RETRACTON AT 1842 EDT ON 04/05/17 FROM RICH BOWEN TO S. SANDIN * * * The licensee is retracting this report following a review that concluded it did not meet the reporting criteria. The licensee informed the NRC Resident Inspector. Notified R2DO (Nease) and 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-04-05
52664 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2017-04-04 07:35 | 2017-04-04 11:32 | 2017-04-04 | HIGH PRESSURE COOLANT INJECTION INADVERTENTLY ISOLATED DURING CONDUCT OF MAINTENANCE SURVEILLANCE "On April 4, 2017, at 0735 [EDT], the HPCI System was inadvertently isolated during the performance of l&C [Instrument and Control] testing. "Technicians were in the process of performing instrument surveillance tests for the HPCI [high pressure coolant injection] System (using Allowed Out of Service Times) when a trip signal was applied to the incorrect instrument. This caused a HPCI System isolation signal on High Area Temperature, resulting in the closure of the HPCI steam isolation valves and rendering the system inoperable and unavailable. RCIC was immediately verified to be operable. "The surveillance testing was aborted and system restoration is in progress. "This condition is being reported as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident per 10CFR50.72(b)(3)(v)(D)." This placed the plant in a 14-day LCO action statement under Technical Specification 3.5.1. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-04-04
52663 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-04-04 00:10 | 2017-04-04 06:57 | 2017-04-04 | MANUAL REACTOR SCRAM DUE TO CONDENSATE LEAK "At 0010 [CDT], 04/04/2017, the reactor was manually scrammed from approximately 75 [percent] core thermal power due Condensate Storage tank level lowering to 24 feet. All control rods fully inserted and all systems actuated and operated as designed. No safety relief valves actuated. Reactor level and pressure are currently being controlled within normal bands. RCIC [reactor core isolation cooling] was manually initiated for level control. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) for the reactor trip and 50.72(b)(3)(iv)(A) for the manual start of the reactor core isolation cooling system." The cause of lowering level was a condensate pipe leak. Decay heat is being removed via steam dumps to the condenser. The electrical grid is stable and supplying plant loads. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-04-04
52662 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2017-04-03 21:55 | 2017-04-04 02:33 | 2017-04-04 | AUTOMATIC ACTUATION OF AUXILIARY FEEDWATER SYSTEM DURING SURVEILLANCE TESTING "At 2155 hours EDT on 04/03/2017, with the unit in Mode 3 at 0 [percent] power, an automatic actuation of the Auxiliary Feedwater (AFW) System occurred during surveillance testing. The cause of the AFW system auto-start was an improperly performed procedure step to bypass the auto-start logic of the AFW pumps during performance of the surveillance test. The 'A' and 'B' AFW pumps automatically started as designed when the feedwater isolation signal was received. "Due to the valid actuation of the AFW system, this event requires an 8-hour non-emergency notification under 10 CFR 50.72(b)(3)(iv)(A)(B)(6). At no time did this occurrence pose undue risk to the health and safety of the public. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-04-04
52661 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2017-04-03 13:48 | 2017-04-03 16:37 | 2017-04-03 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED BY HEAVY EQUIPMENT AT CONSTRUCTION SITE An in-use Troxler gauge was damaged at a construction site on US 83 near Garden City, KS. The gauge, a Troxler model 3430, S/N 28271, contains a 0.3 GBq [8 mCi] Cs-137 source and a 1.48 GBq [40 mCi] Am-241/Be source. The Cs-137 source rod was extended at the time of the incident and could not be withdrawn into the shielded volume. Rad surveys on-site confirmed that both sources were intact [No contamination at the jobsite]. The gauge was returned to its case and temporary shielding used to prevent personnel exposure during transport back to the licensee's Ellsworth Office. The licensee will return the gauge to the manufacturer for disposition. Item Number: KS170004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2017-04-11
52660 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2017-03-22 | 2017-04-03 16:07 | 2017-04-03 | AGREEMENT STATE REPORT - WRITTEN DIRECTIVE INCORRECTLY IDENTIFIED THE TARGET ORGAN The following information was received from the Commonwealth of Virginia via fax: "On March 31, 2017 the licensee notified the Virginia Office of Radiological Health (ORH) that an eye plaque therapy procedure was not performed in accordance with the procedure's written directive. "The plaque was installed on the patient's right eye on March 22 and removed on March 31. The source, 38.8 mCi of l-125, delivered a dose of 85 Gy to the right eye. The right eye was the intended treatment location but the written directive incorrectly identified the target organ as the left eye. The disagreement between the written directive and the treatment location meets the definition of a medical event even though the correct target organ was treated. "ORH will review the licensee's written report and determine additional actions to be taken. "Event Report ID No.: VA-17-004" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2017-04-11
52659 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-03-22 | 2017-04-03 14:33 | 2017-04-11 | AGREEMENT STATE REPORT - PACKAGE LOST DURING SHIPMENT The following information was provided by the State of Ohio via email: "On 3/31/17 the licensee (Cardinal Health) notified ODH [Ohio Department of Health] that a package containing a Ge [Germanium] Generator was being returned to the manufacturer (IRE Elit) in Belgium. "The package was sent on 3/7/17 and on 3/22/17 Cardinal was notified by IRE that the package had not arrived. Cardinal immediately contacted the shipper [common carrier] concerning the package and at that time they had indication that it was stuck in customs in Paris, France. "On 3/31/17 Cardinal was told by [common carrier] that the package has not been located in customs and they are continually searching for the package. "On 4/3/17 licensee told by [common carrier] that there was no record that the package had ever left the [common carrier] hub in . . . and still have not located the package. "Package is labeled as a Yellow II DOT Type A container with 1371 MBq (37 mCi) of Germanium 68. Solid/self-shielded container with a TI at shipment of 0.3. "Item No.: OH170002 "Reference Number: OH 2017-017" * * *UPDATE FROM STEPHEN JAMES TO VINCE KLCO ON 4/11/17 AT 1618 EDT * * * The following information was received from the State of Ohio via email: "Package was located by common carrier and returned to the licensee (Cardinal Health) in Dublin, Ohio. Package had one of two security seals still intact; however, licensee stated that there was no indication that package had been opened during time in transit. Package will be wipe tested and repacked for return to manufacturer." Notified the R1DO (Jackson), R3DO (Jeffers) and NMSS Events via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-04-11
52658 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-04-03 10:45 | 2017-04-03 11:37 | 2017-04-03 | EXCLUSIVE USE TRANSPORT VEHICLE EXCEEDED CONTACT DOSE RATES "This is being reported under 10CFR20.1906(d)(1,2). At 1045 hours [EDT], the SSES [Susquehanna Steam Electric Station] Radwaste shipper was notified by the RP [Radiation Protection] shipping technician performing a receipt survey of an open transport vehicle shipped exclusive use carrying an empty radwaste liner exceeded the 10CFR71.47(b)(1) vehicle contact dose rates of 200 mR/hr. Per NDAP-QA-0720 [Nuclear Department Administrative Procedure] Attachment E, contaminated /radioactive shipments this is a 1 hour notification for exceeding the radiological receipt survey requirements of 200 mR/hr at any point on the outer surface of the vehicle." The vehicle was from Energy Solutions. The licensee will be using the vehicle to transport radwaste from the facility. The licensee has notified the Pennsylvania Emergency Management Agency and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS | SURFACE CONTAM LEVELS > LIMITS |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | PA | POW |  | 20.1906(d)(2) | 20.1906(d)(1) |  |  | 0 | 2017-04-03
52657 | 0 | AMETEK |  |  |  |  | 2016-06-01 | 2017-04-03 09:28 | 2017-04-06 | PART 21 NOTIFICATION - FAILURE OF VISHAY DIODES The following information is the summary letter was received from Ametek via email: "Product: Vishay/ International Rectifier Clamp, Diodes 600 V, 250A, forward and reverse bias. Ametek part numbers 07-600254-00 and 07-600255-00. "Ametek Solidstate Controls is submitting the following Report of a Potential Defect in accordance with the requirements of 10CFR21. This notification is applicable to equipment model number 85-VC0250-29 provided to Dominion Nuclear at Millstone Power Station. Serial numbers affected by this potential defect are: C901880111 C901880211 C901880221 C901880231 C901880244 "AMETEK SOLIDSTATE CONTROLS CORRECTIVE ACTION: If you wish to replace the diodes, Ametek Solidstate Controls will work with you to arrange replacements. Please contact Mr. Mark Shreve of our Client Services group at 1-800-222-9079 or 1-614-846-7500 ext. 6332. mark.shreve@ametek.com" "Please contact us at telephone: 614-846-7500; 1-800-635-7300 or e-mail: ethan.salsbury@ametek.com, if there are any questions. * * * UPDATE ON 4/6/17 AT 0839 EDT FROM ETHAN SALSBURY TO BETHANY CECERE * * * "The original notification for this report contained a typo on the last serial number of the equipment affected." Instead of serial number C901880244, the correct serial number is C901880241. Notified R1DO (Cahill), R2DO (Nease), R3DO (Skokowski), R4DO (Vasquez), and Part 21 Reactors group by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-04-03
52656 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2017-04-02 | 2017-04-02 10:36 | 2017-04-02 | OREGON AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE An Oregon state licensee reported that a Campbell Pacific moisture density gauge model CPN-MC3 (serial number MC380304170) was stolen from a jobsite in Merlin, OR sometime late last night or early this morning. The licensee reported that the gauge was properly secured in a temporary storage building when the building was burglarized. The gauge and other equipment were stolen during the burglary. The licensee has contacted the local police department. The gauge contains 10 mCi of Cs-137 and 10 mCi of Am-241/Be. The state of Oregon will be contacting state and county officials to request public notification about the stolen gauge. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2017-04-10
52655 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2017-03-31 11:55 | 2017-03-31 19:14 | 2017-03-31 | PRESSURE SUPPRESSION POOL DECLARED INOPERABLE DUE TO TORUS HIGH WATER LEVEL "On March 31, 2017 at 1155 hours [EDT], with the reactor at 97% core thermal power and steady state conditions, operators inadvertently caused water level to rise in the Pressure Suppression Pool (TORUS). Pilgrim Nuclear Power Station (PNPS) was restoring normal system valve line-ups after performing flushing of the suction piping of the Core Spray system in accordance with station procedures. During the process of restoring the appropriate valve line-ups, water was inadvertently transferred to the TORUS from the Condensate Storage Tank. The cause of the event is understood. "The Technical Specification (TS) Limiting Condition for Operation (LCO) Action Statement (AS) 3.7.A.5 was entered. The LCO AS was exited at 1540 when TORUS water level was restored to the limits specified in LCO's 3.7.A.1.b and 3.7.A.1.m. Because the TORUS was declared inoperable, PNPS is providing an 8-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(v)(D), an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. "This was a case of the water level in the TORUS being above the TS limit. The TORUS was potentially available to provide cooling to the reactor if required. "The NRC Resident Inspector has been notified." The licensee notified the Commonwealth of Massachusetts and Plymouth County. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-03-31
52654 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2017-03-28 | 2017-03-31 16:15 | 2017-03-31 | AGREEMENT STATE REPORT - LOSS OF CONTROL OF A SEALED SOURCE The following information was received from the Commonwealth of Kentucky via facsimile: "On 3/28/2017 the licensee left a Cs-137 brachytherapy sealed source at [address provided]. On 3/30/2017 the licensee discovered the source was not in its shielded container and immediately determined the location of the source and took steps to retrieve and secure it. This event is actively being investigated by the licensee." Kentucky Event: KY170003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2017-04-10
52653 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-03-22 | 2017-03-31 11:21 | 2017-03-31 | AGREEMENT STATE REPORT - STUCK GAUGE SHUTTER The following report was received from the South Carolina Department of Health and Environmental Control via email: "The licensee provided notification of a stuck shutter on a Berthold Model LB7440 fixed gauging device. The shutter was stuck in the open position. The gauging device contains 100 mCi of Cs-137. A licensed contractor found the shutter stuck in the open position on March 22, 2017, and the licensee notified the State [of South Carolina] on March 30, 2017. The contractor proceeded with corrective maintenance on the shutter mechanism. The licensee stated that a written report will be sent within 30 days of the event. Updates to this event will be made through the NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-04-10
52652 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-03-30 16:30 | 2017-03-30 21:58 | 2017-03-30 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY "At 1630 PDT on March 30, 2017, a non-work related fatality occurred on the Diablo Canyon Power Plant property. The individual's work location was outside of the Protected Area. The fatality was not related to the health and safety of the public. Specifically, a contractor for Pacific Gas and Electric (PG&E) was found in the Security Training Building unresponsive. The individual was promptly attended to by Diablo Canyon personnel. The individual was subsequently pronounced dead by the San Luis Obispo County Paramedics. "PG&E has not observed any heightened public, media, or government concerns as a result of the fatality. Because the fatality is unrelated to Diablo Canyon Power Plant industrial or radiological health and safety, no news release is planned. "Because the fatality was not work related, nor the result of an accident, no notification to other government agencies was made at the time. However, PG&E will make a notification to the California Occupational Safety and Health Administration. Thus this ENS notification is in response to a notification to another government agency in accordance with 10 CFR 50.72(b)(2)(xi). "The NRC Senior Resident Inspector and Resident Inspector have been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-03-30
52651 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2017-03-30 17:10 | 2017-03-30 20:05 | 2017-05-15 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On March 30, 2017 at 1710 EDT, with Reactor Building HVAC in service maintaining normal building pressure, Reactor Building pressure began to rise for an unknown reason. The Technical Specification (TS) for secondary containment pressure boundary was not met for approximately 50 seconds. Division 1 Standby Gas Treatment System was started and returned Secondary Containment pressure to the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1). The highest pressure observed on the Main Control Room indications was 0.105 inches of vacuum water gauge. During the event, Operations with the Potential to Drain the Reactor Vessel (OPDRV) were in progress. Actions to immediately suspend OPDRVs were taken. "Investigation of the cause of the event is in progress. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION AT 1652 EST ON 5/15/17 FROM JEFF YEAGER TO JEFF HERRERA * * * "The purpose of this notification is to retract a previous report made on March 30, 2017 (EN 52651). The notification to the NRC involved an event where secondary containment momentarily exceeded the Technical Specification (TS) requirements during refueling activities which had been designated as operations with the potential to drain the reactor vessel (OPDRVs). The notification was made under 10 CFR 50.72(b)(3)(v)(C) as an 'event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to ... control the release of radioactive material.' Subsequent to the initial notification, the event and the NRC guidance in NUREG-1022 pertaining to 10 CFR 50.72(b)(3)(v) were reviewed further. At the time of the event, Fermi 2 was shutdown (Mode 5. Refueling). In Mode 5, the pressures and temperatures that could cause a loss of coolant accident (LOCA) are not present. No movement of fuel was in progress such that the fuel handling accident (FHA) was also not applicable. Thus secondary containment was only required per TS 3.6.4.1 due to the ongoing OPDRVs. The Fermi 2 UFSAR does not describe OPDRVs as an accident that secondary containment is required to mitigate. Based on this information, secondary containment was not required to mitigate the consequences of an accident as described in the UFSAR during the event on March 30, 2017. Under these circumstances, the momentary exceedance of TS requirements for secondary containment is not considered a loss of safety function under 10 CFR 50.72(b)(3)(v) per the guidance in NUREG-1022. Therefore, EN 52651 is retracted and no Licensee Event Report (LER) under 10 CFR 50.73(a)(2)(v) is required to be submitted." The NRC Resident Inspector has been notified. Notified the R3DO (Cameron). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-03-30
52650 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-03-30 09:22 | 2017-03-30 12:58 | 2017-03-30 | UNANALYZED CONDITION DUE TO POTENTIAL TORNADO GENERATED MISSILES "During the evaluation of tornado missile vulnerabilities and the potential impacts to safety-related plant equipment, it was concluded that the following structures are vulnerable to tornado generated missiles: "All five of the Unit 1 and Unit 2 Emergency Diesel Generator (EDG) fuel oil storage tanks have ventilation pipe extending approximately 5 feet above grade. In the event that a tornado missile impact occurs on the aforementioned ventilation piping, there is a possibility that the vent lines could crimp. This could prevent the tanks from venting and inhibit the transfer of fuel oil from the main fuel oil storage tanks to the day tank. Ultimately, this causes the emergency diesels to be inoperable. "These conditions are reportable per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(D) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety and also an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequence of an accident. This issue is being addressed in accordance with EGM-15-002, Revision 1, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance. "The NRC Resident Inspector has also been notified." | 97 | 100 | 0 | 97 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-03-30
52649 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-03-30 03:10 | 2017-03-30 03:19 | 2017-03-30 | LOSS OF ALL CONTROL ROOM ANNUNCIATORS "The Unit 1 DC Cook Nuclear Plant (CNP) Annunciator System failed on Thursday, March 30, 2017 at 0255 [EDT]. The failure resulted in a complete loss of all alarm function of the Annunciator System in the Unit 1 Control Room. Unit 2 was unaffected by this failure. At 0310 [EDT], an Unusual Event (UE) was declared due to System Malfunction S-6, Loss of Alarms or Indication, due to an unplanned loss of safety system annunciators and/or indications in the Control Room for greater than 15 minutes. "The Unit 1 PPC [Plant Process Computer] and ERDS [Emergency Response Data System] remain functional and available. "This notification is being made in accordance with 10 CFR 50.72(a)(1)(i) due to the declaration of an Emergency Classification specified in the licensee's approved Emergency Plan." The licensee has notified the NRC Resident Inspector, the State and local agencies. Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. * * * UPDATE FROM MAX MILLER TO DONG PARK AT 0821 EDT ON 3/30/2017 * * * "Unit 1 DC Cook Nuclear Plant Annunciator System has been returned to functional. Unusual Event Classification was terminated at 0817 EDT on 3/30/17." The NRC Resident Inspector will be notified. Notified R3DO (Cameron), NRR EO (Miller), and IRD (Grant). Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-03-30
52648 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-03-29 18:44 | 2017-03-29 23:36 | 2017-03-29 | MANUAL SCRAM INITIATED DURING STARTUP "At 1844 CDT on 3/29/2017, Unit 2 initiated a manual scram due to multiple rods inserting. "At 1842 during Unit 2 start-up, Intermediate Range Monitor (IRM) 'G' drifted low. The operator adjusted the range down one position with no immediate reaction. At 1844, a spike on IRM 'G' caused a half scram on Reactor Protection System (RPS) 'A' trip system. The half scram was being reset after evaluating no trip condition was present. As the operator reset groups 2 and 3, a trip signal from IRM 'F' was received on the RPS 'B' trip system, resulting in rod insertion for groups 1 and 4. When the operator identified multiple rods inserting, the actions of procedure 2-AOI-100-1 were followed and a manual scram was inserted. Investigation is ongoing. "All safety systems remained in standby readiness configuration. No Emergency Core Cooling System (ECCS) or Reactor Core Isolation Cooling (RCIC) reactor water level initiation set points were reached. Primary Containment Isolations Systems did not receive an actuation signal and performed as designed. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the RPS when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of systems listed in paragraph (b)(3)(iv)(B) Reactor Protection System(RPS) including reactor scram and reactor trip'. This event requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-03-29
52647 | 0 | PALISADES | 1 |  |  | [1] CE | 2017-03-29 15:08 | 2017-03-29 18:10 | 2017-03-29 | DISCOVERY OF NON-CONFORMING CONDITIONS DURING TORNADO HAZARDS ANALYSIS "During an evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Palisades Nuclear Plant personnel identified conditions in the plant design such that specific TS equipment is considered not adequately protected from tornado missiles. "Specifically, vulnerabilities were identified in the following systems and components: Service Water System - Service water pump discharge header and service water pump cable trays. Fuel Oil Transfer System - Fuel oil transfer piping and transfer pump cable trays. Emergency Diesel Generators - Vent lines on the fuel oil day tanks. Control Room Heating, Ventilation, and Cooling System - Both the normal and emergency intake ducts. Steam Driven Auxiliary Feedwater Pump - Feedwater pump relief valves. Component Cooling Water System - Component cooling water surge tank. "The identified vulnerabilities are being addressed in accordance with Enforcement Guidance Memorandum (EGM), 15-002, and Interim Staff Guidance, DSS-ISG-2016-01. Initial compensatory measures are in place." The licensee notified the NRC Resident Inspector. | 70 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2017-03-29
52646 | -1 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-03-28 19:57 | 2017-03-29 03:28 | 2017-05-23 | UNANALYZED CONDITION FOR A POSTULATED MODERATE ENERGY LINE BREAK "On March 28, 2017 at approximately 1957 CDT, a condition was discovered whereby a postulated moderate-energy line break (MELB) involving three fire protection (FP) pipe segments in the Safeguards Building did not contain MELB shielding. It was subsequently determined a postulated crack in one of the affected FP piping sections could adversely affect circuitry associated with the cooling support system for the train A RHR [Residual Heat Removal] pump room, potentially causing the ventilation system to be unavailable to support operation of the train A RHR pump. This condition is not consistent with the CPNPP licensing basis for the protection of essential safe shutdown RHR equipment. "At approximately 1957 CDT train A RHR was declared inoperable but available and the unit entered a seventy-two hour LCO [Limiting Condition for Operation] Action Statement per Technical Specification 3.5.2 B pending completion of mitigative actions. "Since Unit 1 train B RHR system components and related supporting equipment have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, given the MELB condition, both trains of RHR and or support equipment could have been inoperable and this represents an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B). At the time of discovery, train B RHR and support equipment were operable. Therefore, the identified condition is not reportable as a loss of safety function per 10 CFR 50.72(b)(3)(v). "The Senior NRC Resident Inspector has been notified." Compensatory actions will include installing a spray shield on the affected cable trays. * * * RETRACTION FROM JOHN ALEXANDER TO VINCE KLCO ON 5/23/17 AT 1720 EDT * * * "On 03/29/2017 Comanche Peak reported an ENS Report (no. 52646) related to the identification of potential moderate-energy line break (MELB) considerations in the Safeguards Building and the potential for adverse interaction with specified Unit 1 electrical equipment. The specific interactions of concern were related to ventilation equipment which would support operation of the Unit 1 A RHR train and several segments of fire protection piping. "Subsequent investigations by Engineering have determined: (1) all but one of the suspected potential interactions were determined to not be credible, i.e., the potential MELB would not result in an adverse interaction with the 'target' equipment, and (2) for the remaining potential interaction, an assessment of piping stresses determined there was not a credible MELB source in the affected piping segment and therefore there was not a potential for adverse interaction with the ventilation support equipment. "Based on the above, the condition described in ENS report no. 52646 is not considered to be an un-analyzed condition as described in 10 CFR 50.72(b)(3)(ii)(B)." The licensee informed the NRC Resident Inspector. Notified the R4DO (Groom). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-03-29
52645 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2017-01-31 14:25 | 2017-03-28 14:47 | 2017-03-30 | 60-DAY REPORT DUE TO INVALID ECCS ACTUATION SIGNAL "The following report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to an unintended initiation signal that occurred on January 31, 2017 with James A. FitzPatrick Nuclear Power Plant (JAF) in Mode 5 at zero (0) percent power. "On January 31, 2017 at 1425 [EST] the control room received multiple annunciations associated with the following Systems / Trains: Primary Containment Isolation System (PCIS) / Trains A and B Residual Heat Removal System (RHR) / Trains A and B Core Spray (CS) / Trains A and B Reactor Core Isolation Cooling (RCIC) "All four (4) Emergency Diesel Generators (EDG) auto-started with their associated Emergency Service Water pumps operating. RHR and CS both received initiation signals but were defeated per procedure. The HPCI [High Pressure Coolant Injection] auxiliary oil pump was taken to Pull-to-Lock per procedure, and the RCIC steam isolation valve cycled until the breaker was opened to close the valve. "An evaluation concluded that the [Emergency Core Cooling System - ECCS] initiation signals were caused by the opening of a portable job box that was stored near sensitive equipment. Upon opening the job box, the lid bumped a reference leg resulting in the initiation signals. All initiation signals were reset and systems restored to normal shutdown lineups." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 3/30/17 AT 0840 EDT FROM DUSTIN SCURLOCK TO DONG PARK * * * To the original report, the licensee added, "This condition recurred at 1624 [EDT on 1/31/17]." The licensee notified the NRC Resident Inspector. Notified R1DO (Cook). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-03-28
52644 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-03-28 07:00 | 2017-03-28 08:57 | 2017-03-28 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENISTY GAUGE The following information was provided by the State of Texas via email: "On March 28, 2017, the Agency [Department of State Health Services] was notified by the licensee that a Troxler Model 3411 moisture/density gauge was stolen from one of its trucks. The gauge contains a 40 milliCurie americium-241 source and an eight milliCurie cesium-137 source. The gauge had been used at a job site the day before by a technician and taken to their home [located in Fort Worth] for the night, stored (locked) in the bed of the truck. Since the operating rod for the cesium source was locked in the shielded position and the case was also locked, the licensee does not believe a member of the general public would receive any significant exposure. The radiation safety officer stated he would provide additional information to the Agency as soon as he completed his interview with the technician. Additional information will be provided as it is received in accordance with SA-300." TX Incident #: I-9475 * * * UPDATE PROVIDED BY ART TUCKER TO JEFF ROTTON AT 1029 EDT ON 03/28/2017 * * * The following information was provided by the State of Texas via email: The stolen moisture density gauge was actually a Troxler 3430 versus a Troxler 3411 as described in the above paragraph. Notified R4DO (Hipschman), NMSS Events Notification group, ILTAB, and Mexico via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-04-05
52643 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2017-03-27 18:25 | 2017-03-27 21:54 | 2017-03-27 | HPCI DECLARED INOPERABLE DUE TO INADVERTENT ISOLATION "On March 27, 2017, at 1825 hours EDT, with the reactor at 100 percent core thermal power and steady state conditions, technicians inadvertently caused a High Pressure Coolant Injection (HPCI) System isolation, by testing the incorrect temperature switches in the TIP [Traversing In-core Probe] room. Pilgrim Nuclear Power Station (PNPS) was performing testing on the temperature switches for Reactor Core Isolation Cooling (RCIC), but the HPCI temperature switches were inadvertently actuated causing HPCI to isolate. "The Limiting Condition for Operation (LCO) Action Statement 3.5.c.2 has been entered and the planned testing has been secured pending further investigation. PNPS is providing an 8-hour non-emergency notification that the HPCI System was declared inoperable in accordance with 10 CFR 50.72(b)(3)(v)(D), an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. HPCI was returned to Operable within 40 minutes." The licensee notified the NRC Resident Inspector and the Commonwealth of Massachusetts. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-03-27
52642 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2017-03-27 | 2017-03-27 16:51 | 2017-03-27 | PART 21 - IDENTIFICATION OF FAILED DIODE SURGE SUPPRESSOR WITH INTERNAL MANUFACTURING DEFECT The following information is excerpted from an Engine Systems, Inc. (ESI) report received via fax: "COMPONENT: "Diode Surge Suppressor "Allen-Bradley P/N: 199-FSMZ-1 "SUMMARY: "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on February 10, 2017 after receiving notification from FirstEnergy Corp - Perry Nuclear Power Plant (PNPP) of a manufacturing defect in a diode supplied by ESI. The evaluation was concluded on March 27, 2017 and it was determined that this issue is a reportable defect as defined by 10CFR21. The manufacturing defect identified was in a diode of the same date code as two diodes that failed while installed at PNPP. The failed diodes resulted In loss of class 1E control power which could have prevented the emergency diesel generator set from performing its safety related function. "Discussion: In January 2007, ESI supplied a governor system upgrade to PNPP. The upgrade replaced the existing Woodward EGB-35C governor/actuator, EGA control (w/ resistor box), and MOP with an EGB-35P governor/actuator, 2301A control, and DRU. The electrical components were housed in a control panel assembly. To support the slow start feature of the new system, 4 relays were used, each of which used a surge suppressor (flyback) diode. "PNPP experienced two failures in 2016 of the aforementioned diodes supplied by ESI. The diodes are Allen Bradley part number 199-FSMZ-1 and they were installed across the coils of Allen-Bradley 700DC series relays. The Allen-Bradley date code stamped on the side of the diodes is BX9. The failure in both cases resulted in a short circuit condition that resulted in a loss of class 1E control power to the EDG. "Root cause evaluation: "The root cause of the failure is determined to be a manufacturing defect internal to the diode. Though an analysis of the diodes that failed at PNPP was unable to be performed due to their condition, the analysis performed on a degraded diode of the same date code, BX9, detected an internal manufacturing defect. Affected Users: A listing of users with suspect diodes includes FirstEnergy - Perry, Entergy - Grand Gulf, Progress - Shearon Harris, and Duke - Shearon Harris. A total quantity of 34 diodes are suspect. "Corrective Action: "All affected users . . . [identified above] . . . should perform the following: "1. Review their inventory for suspect diodes listed in Table 1. Any suspect diodes should be removed from inventory and discarded. "2. Determine if suspect diodes listed in Table 1 have been installed. Thus far, ESI has identified degraded diodes from date codes BX9 and ZX9 and it is possible that diodes from the other date codes are degraded as well. ESI has been unable to determine an expected service life. Therefore, the recommendation is to remove or replace any installed suspect diodes as soon as possible. Note that the applications for which this diode has been supplied (Enterprise engine control panels) used the same style Allen-Bradley relays as original equipment but without diode surge suppressors. It is therefore acceptable to remove the diodes and expect no change or impact to the existing equipment. "To prevent recurrence of this issue, the following has been Implemented by ESI: "1. The test procedure for the diode has been enhanced to increase the test voltage and decrease the allowable leakage current. Although this was not the cause of the failure, it may have prevented identification of a degraded condition. This corrective action has already been implemented. "2. A review has been performed of other diodes supplied by ESI and at this time only this one part number is affected. A typical diode would be procured and/or sold under the diode manufacturer part number; whereas in this case it was procured from the relay manufacturer. Testing was performed using typical relay values in lieu of the diode manufacturer's acceptance criteria." If you have any questions, you may call: Tom Horner Quality Assurance Manager Tel: (252) 977-2720 ESI Report ID: 10CFR21-0116, dated 03/27/17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-03-27
52641 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2017-03-27 09:40 | 2017-03-27 16:02 | 2017-03-27 | FITNESS-FOR- DUTY TEST POSITIVE FOR NON-LICENSED CONTRACTOR A non-licensed contractor employee had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employee's access to the site has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2017-03-27
52640 | -1 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2017-03-25 01:42 | 2017-03-25 09:28 | 2017-03-30 | REFUELING WATER TANK LEVEL INADVERTENTLY LOWERED BELOW TS "While performing a purification subsystem alignment on the Unit-2 Refueling Water Tank, an inadvertent transfer of Refueling Water Tank level to the common Spent Fuel Pool occurred. This transfer resulted in lowering Unit-2 Refueling Water Tank level below the Technical Specification [TS] required limit for the current mode of operation at 0142 [EDT] on 3/25/17. Upon recognition of the inadvertent transfer, Operations secured the lineup and restored Unit-2 Refueling Water Tank level to its normal operating band at 0225 on 3/25/17. "This event is reportable under 10 CFR 50.72(b)(3)(v)(D) '...any event or condition that at the time of discovery could have prevented the fulfillment of the safety function structures or systems that are needed to mitigate the consequences of an accident.' With less than the required Technical Specification volume in the Refueling Water Tank, insufficient volume existed in the Refueling Water Tank to maintain 30 minutes of full flow Safety Injection, and subsequent continued pump operation after transition to recirculation mode of operation." This level is required by Technical Specification 3.5.4.B and has a one hour action statement to restore level. The NRC Resident Inspector has been notified. * * * RETRACTION FROM KENT MILLS TO DONALD NORWOOD AT 1637 EDT ON 3/30/2017 * * * "The purpose of this notification is to retract ENS notification 52640 made on March 25, 2017 for Calvert Cliffs. After further evaluation, it has been determined that the volume of water in the Unit 2 Refueling Water Tank was never below the TS required volume of 400,000 gallons. The evaluation considered the as-found condition of the level transmitter and the existing environmental conditions of the tank in determining the actual RWT water volume on the day of the event. Therefore, this event does not meet the criteria of 10 CFR 50.72(b)(3)(v)(D) and the ENS report is being retracted." The licensee will notify the NRC Resident Inspector. Notified R1DO (Cook). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-03-25
52639 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2017-03-24 20:00 | 2017-03-24 20:25 | 2017-03-24 | VIRGINIA DEQ NOTIFIED OF SMALL GLYCOL RELEASE TO JAMES RIVER "On 03/24/2017 at approximately 1500 hours [EDT], a hydraulic line on vendor supplied cleaning equipment failed and leaked approximately 8 gallons of 65% glycol solution into the Surry Power Station Unit 2 D intake bay. Since the intake bay communicates with the James River, the State of Virginia Department of Environmental Quality (DEQ) was notified of the discharge at 2000 hours. "The glycol solution is water soluble and dispersed quickly. All work stopped while the issue is being investigated and corrective actions implemented. No sheen was observed and no impact to state waters is expected to result from this issue. "This non-emergency notification is being made in accordance with 10 CFR 50.72(b)(2)(xi), any event or situation related to the protection of the environment for which notification to other government agencies has been made." The NRC Senior Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-03-24
52638 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-03-20 16:39 | 2017-03-24 17:15 | 2017-04-10 | HISTORICAL EVENT RELATED TO PAST OPERABILITY "On February 3, 2017, Prairie Island staff performed maintenance on the transom above Battery Room Door 225. This activity resulted in the transom being unlatched for approximately five minutes. On February 6, 2017, a question from the NRC Resident Inspector resulted in an evaluation of this condition for past operability. On March 20, 2017, the past operability evaluation of Door 225 concluded that, in the event of a postulated HELB [High Energy Line Break], the transom being unlatched during the five minute maintenance period resulted in the inoperability of multiple systems in the Unit 1 and Unit 2 battery, auxiliary feedwater, and Unit 1 safeguards bus rooms that would be required to mitigate the postulated HELB. "The loss of safety functions required to mitigate the postulated HELB make the condition reportable under 50.72(b)(3)(ii) for an unanalyzed condition that significantly degrades plant safety. "Unlatching the transom above the Battery Room Door creates an opening not accounted for in design bases documents. This occurred due to an improperly prepared work permit. Corrective actions are in place to preclude recurrence." The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM MARK LOOSBROCK TO JEFF ROTTON AT 1559 EDT ON 04/10/2017 * * * "Further analysis determined that an unlatched transom would result in a relative humidity of 100 percent in 11 Battery Room for about 10 minutes following a postulated HELB. Since the equipment in the Battery Rooms is not qualified for a harsh environment, the components in 11 Battery Room would have been inoperable. Temperature and relative humidity in the other Battery Rooms, Auxiliary Feedwater Rooms, and the Unit 1 Safeguards Bus Rooms would have remained within the allowable limits. "Therefore, for the five minutes the strike was removed from the transom, only equipment in 11 Battery Room and supported A Train components would have been inoperable. This event was not an Unanalyzed Condition that significantly degraded plant safety, under 10 CFR 50.72(b)(3)(ii), as no safety function would have been lost." The licensee notified the NRC Resident Inspector. Notified R3DO (Skokowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-03-24
52637 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-03-23 11:00 | 2017-03-24 11:48 | 2017-03-24 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER MALFUNCTION The following information was received from the State of Louisiana via fax: "On March 24, 2017, LDEQ [Louisiana Department of Environmental Quality] was notified by Blue Cube Operations LLC, that during an annual equipment inspection, it was determined that a level density gauge shutter was malfunctioning. "The density gauge was a TN Technologies Inc. Model: 5202, and equipped with a TN Technologies Inc. Model 57157C sealed source - serial number: GK-9492. Initial source activity was 500 mCi [Cs-137], after decay correction, it is 341.78 mCi. "No release or exposure to personnel. Blue Cube Operations plans to repair the shutter to the level density gauge. "Event Report ID No.: LA170004" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-04-03
52636 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-03-23 03:25 | 2017-03-23 21:06 | 2017-03-23 | SIGNIFICANT FFD POLICY VIOLATIONS OR PROGRAMMATIC FAILURES "On 3/23/17, at 0325 hours CDT, it was discovered that a prohibited item was present in the protected area from 0508-1718 hours on 3/22/17, which resulted in a reportable condition pursuant to 10 CFR 26.719(b)(1). "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2017-03-23
52635 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-03-23 | 2017-03-23 18:13 | 2017-03-24 | AGREEMENT STATE REPORT - PACKAGE RECEIVED WITH REMOVABLE CONTAMINATION The following report was received from the Texas Department of State Health Services via email: "On March 23, 2017 the radiation safety officer [RSO] from a hospital called stating a package was received from BTX Global Logistics (31x2130417) containing a Germania-Gallium generator. The device was intact and not leaking although the outside of the package had removable contamination at 21,866 dpm over a 300 cm squared area. The RSO stated she contacted the delivery service. She [the RSO] explained that the device she received wasn't leaking and the contamination may be inside their vehicle. She [the RSO] stated that the package was received at 1221 [CDT] at the hospital. Her staff confirmed the device was not leaking and the contamination was on the outside of the package. Investigation ongoing. Updates to be provided as received." * * * UPDATE AT 1211 EDT ON 3/24/17 FROM CHRIS MOORE TO JEFF HERRERA * * * The following update was received from the Texas Department of Health Services via email: "On March 23, 2017 the Radiation Safety Officer (RSO) from The University of Texas MD Anderson Cancer Center called stating a package was received from BTX Global Logistics (31x2130417) at 1221 containing a Germania-Gallium generator. The device was intact in a package although the bottom of the package was contaminated. The highest level of contamination was 466 dpm per square cm based on 777,425 dpm over a 16 inch by 16 inch area of the box. The inside of the box was not contaminated and the generator was not leaking. The only spread of contamination from the box was onto a cart used to transport the generator from the loading dock to the lab. The cart was decontaminated. The contamination appears to be a low energy beta emitter with a short life in the 2-3 hour range. The contamination cannot be detected by a GM or scintillator probe only by the use of liquid scintillation counter. The hospital is attempting to identify the radionuclide. The Agency [Texas Department of Health Services] surveyed the transport vehicle, contents and driver for the delivery vehicle with a pancake probe for contamination on March 23, 2017. This was completed prior to understanding that it would not be detectable with available probes so today the vehicle will be surveyed with wipes. The package was picked up from Houston Intercontinental Airport on the evening of March 22, 2017 after clearing customs from a [common carrier] Aircraft flying from Germany. BTX Global Logistics picked up the package on March 22, 2017, placed it in their warehouse until it was delivered on March 23, 2017. Both times while the package was being transported in the vehicle, there were no other packages in the vehicle. There were no other deliveries of radioactive material in this vehicle over the last 2 days. The investigation is ongoing." Texas Incident #: I 9474. Notified the R4DO (Drake) and NMSS Events (Email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-03-31
52634 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-03-22 | 2017-03-23 17:30 | 2017-04-21 | AGREEMENT STATE REPORT - FOUR STUCK SHUTTERS IDENTIFIED DURING A SIX MONTH INSPECTION The following report was received from the Texas Department of State Health Services via email: "On March 23, 2017, [at 1545 CDT] a consulting company called the Agency [Texas Department of State Health Services] to report that on March 22, 2017, during [a] six month inspection of devices, four devices were found with stuck shutters. Two Ohmart Vega devices contained cesium-137, models SHLG with source serial numbers SM-6918 (120 milliCuries) and 5811GK (5000 milliCuries). The other two were [the] same manufacturer, same isotope, but model SHF2 with source serial numbers M-0076 and M-0077 at 200 milliCuries each. The consulting service is in contact with the licensee's radiation safety officer who is submitting a request to amend the license maintaining the devices in the open position until repaired. No exposures are anticipated and the repairs should be performed within the next 90 days. Updates will be provided as received." Texas Incident #: I 9473 * * * UPDATE ON 4/12/17 AT 1416 EDT FROM ART TUCKER TO DONG PARK * * * The following information was provided by the State of Texas via email: "On April 12, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that part of its corrective actions in response to this event was to inspect all the gauge shutters again to insure proper operation. The inspection was done on April 11, 2017. During this inspection, two additional gauge shutters were found stuck in the open position. "Both gauges are Ohmart model SH-F2 gauges one with a 30 millicurie cesium-137 source, and the second one contains a 100 millicurie [cesium-137] source. No member of the general public or employees at the facility will receive any additional exposure from this event. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Kramer) and NMSS Events Notification via email. * * * UPDATE ON 4/21/17 AT 1628 EDT FROM ART TUCKER TO DONG PARK * * * The following information was provided by the State of Texas via email: "The Agency [Texas Department of State Health Services] received inspection reports from the licensee and has identified two additional gauges, one SHGL-1 and one SHGL-2, that were found to have shutters that would not close. This inspection occurred in October, 2015. The gauges were reported as functional on the next inspection in April of 2016. The Agency has requested additional information on the gauges. The Agency will be performing an on-site inspection on May 4, 2017. The licensee has replaced the radiation safety officer. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Azua) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-03-31
52633 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2017-03-23 13:50 | 2017-03-23 14:48 | 2017-03-23 | SAFEGUARDS REPORT An individual failed to disclose derogatory information which would have precluded unescorted access. Compensatory measures taken upon discovery. The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-03-23
52632 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-03-23 06:00 | 2017-03-23 13:55 | 2017-03-23 | FITNESS-FOR-DUTY REPORT INVOLVING DISCOVERY OF KOMBUCHA TEA INSIDE THE PROTECTED AREA An employee reported finding a container of herbal tea (Kombucha) in the Administrative Building refrigerator which is inside the Protected Area. Kombucha tea is a fermented tea containing trace amounts of alcohol. A similar incident occurred on 6/16/2016. The licensee issued a communication to all employees at that time identifying that Kombucha tea is not permitted on-site. The licensee will re-issue their communication to all employees and continue their investigation to identify who may have brought the tea on-site. The licensee informed the NRC Resident Inspector and R4 (Haire). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2017-03-23
52631 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-03-23 02:56 | 2017-03-23 07:24 | 2017-03-23 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "River Bend Station personnel declared the High Pressure Core Spray (HPCS) system inoperable at 0256 on 3/23/2017. "During performance of the HPCS Pump and Valve Operability Test, the operators observed an unusual system response after E22-MOVF023 (HPCS Test Return to the Suppression Pool) was stroked closed. A field check showed that the key that connects the E22-MOVF023 valve stem to the anti-rotation device had become dislodged. "E22-MOVF023 is a Primary Containment Isolation Valve (PCIV) and is designed to close automatically on an ECCS [Emergency Core Cooling System] initiation signal to ensure that injection flow is directed to the reactor vessel. Technical Specification (TS) 3.6.1.3 requires that containment penetrations associated with an inoperable PCIV be isolated. E22-MOVF023 was declared inoperable at 0028. Operators were unable to close or demonstrate that E22-MOVF023 was fully closed as required by TS 3.6.1.3 and proceeded to isolate the associated containment penetration by closing other system valves. This action was completed at 0320. "The net effect of the actions taken to isolate the containment penetration is that HPCS is inoperable as of 0256. This results in 14 day LCO." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM DAN JAMES TO KARL DIEDERICH ON 3/23/17 AT 10:01 EDT * * * The Event Time was 0028 CDT rather than 0256 CDT. "The scheduled surveillance test of the high pressure core spray system was initiated at 2355 CDT on March 22, and the pump was secured at 0028 CDT on March 23. The inspection of the HPCS test return valve to the suppression pool occurred at 0050 CDT, and it was at that point that an apparent malfunction of the valve had occurred to the extent that it did not appear to be able to perform its safety function to close upon receipt of a design basis system initiation signal. Thus, the event time for this condition would be more accurately defined as 0028 CDT." Notified R4DO (James Drake) via e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-03-23
52630 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-03-23 00:14 | 2017-03-23 02:48 | 2017-03-23 | AUTOMATIC START OF AUXILIARY FEED WATER "On March 23, 2017, at 0014 EDT, Watts Bar Nuclear Plant Unit 2 (WBN2) experienced an unplanned trip of both Turbine Driven Main Feed Pumps (TDMFP) following a loss of Main Condenser Vacuum. The trip of both TDMFPs caused an automatic start of both Motor Driven Auxiliary Feed Water Pumps and the Turbine Driven Auxiliary Feed Water Pump. [The] cause of the loss of Main Condenser Vacuum is currently under investigation." The plant was performing a normal startup, and had just synced the main generator to the grid. Subsequent to the event, the plant was transitioned to Mode 3. All rods are fully inserted. Decay heat is being removed via the atmospheric relief valves. Unit 1 remains in Mode 5 for a refueling outage. The licensee has notified the NRC Resident Inspector. | 0 | 3 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Startup | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-03-23
52629 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2016-12-09 | 2017-03-22 17:18 | 2017-03-22 | AGREEMENT STATE REPORT - TOTAL DOSE LESS THAN 80 PERCENT OF PRESCRIBED DOSE The following report was received from the Wisconsin Department of Health Services via email: "On March 22, 2017, the [Wisconsin Department of Health Services] received a telephone call and email from the licensee's medical physicist that a medical event occurred on December 9, 2016, involving a permanent implant of I-125 seeds for a prostate manual brachytherapy procedure where the total dose delivered differs from the prescribed dose by 20% or more. This is a medical event as described in DHS 157.72(1)(a)1.a. The prescribed dose was 145 Gy; the dose delivered was 114 Gy. The licensee uses D90 (dose delivered to 90% of the clinical target volume) less than 80% for determining medical events. Using the licensee's dose based criteria; the dose received by the prostate was 78% of the intended dose. The underdose was identified during the post-implant computed tomography scan on January 9, 2017 and subsequent dosimetric analysis on January 27, 2017. The licensee's radiation oncologist informed the physicist that supplemental radiation will not be administered and that it is a reportable event on March 22, 2017. Corrective actions are being reviewed by the licensee's staff. DHS [Department of Health Services] inspectors will investigate this medical event." Wisconsin Event ID No.: WI-170005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-03-30
52628 | -1 | MICHIGAN STATE UNIVERSITY |  |  |  |  | 2017-03-17 10:00 | 2017-03-22 08:10 | 2017-03-22 | WRONG MODE OF TREATMENT: PET SCAN ADMINSTERED WHEN CT SCAN WAS ORDERED A PET scan was administered to a patient even though a CT scan was ordered by the prescribing physician. Initially the prescribing physician ordered a PET scan, but changed the order to a CT scan. An administrative error resulted in the order change not being implemented to reflect the change to a CT scan. The patient was provided all release forms for the PET scan and was aware that a PET scan was being administered. The patient received 1R of exposure. There was no harm to the patient. * * * RETRACTION AT 1429 EDT ON 3/22/17 FROM BRYAN HARRIS TO DONG PARK * * * The licensee has determined that this event did not meet reporting requirements. The licensee notified Region 3 (Craffey). Notified R3DO (Orlikowski) and NMSS Events Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(2) |  |  |  | 0 | 2017-03-30
52627 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2017-03-20 16:20 | 2017-03-20 17:53 | 2017-03-20 | UNUSUAL EVENT DECLARED FOR FIRE ALARM IN CONTAINMENT "At 1620 [CDT], an unusual event was declared due to a smoke detector alarm in Unit 1 containment. [There were] no indications of any other detector alarms, no abnormal equipment indications, and containment parameters are normal (temperature, humidity). "At 1631 [CDT], visual inspection [of the] 66 ft. hatch indicated no smoke or abnormal smell. "At 1640 [CDT], local inspection of Unit 1 containment verified no fire or hot spots." The licensee has notified the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. * * * UPDATE FROM RYAN RODE TO DONG PARK AT 2208 EDT ON 3/20/2017 * * * "Event transmitted under ENS # 52627 is terminated at 2022 [CDT on] 3/20/17." The NRC Resident Inspector has been notified. Notified R3DO (Orlikowski), NRR EO (Miller), and IRD (Stapleton). Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-03-20
52626 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-03-20 | 2017-03-20 11:37 | 2017-03-20 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following report was received from the State of Florida Bureau of Radiation Control via email: "[The licensee] called to inform the BRC [Bureau of Radiation Control] that a Troxler gauge, Model 3430, in use at a construction site on Midway Rd. in Ft. Pierce had been run over by a pick up truck. The gauge was not in the transport case. The source rod was retracted. The outer plastic case and the screen are damaged. Reading of unit taken with a TroxAlert, Model 3105B indicated source / shielding is intact. All reading around the meter were normal background. Gauge will be taken to Atlantic Drill Supply, Rivera Beach, FL for repairs. "Florida Incident Number: FL17-089" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-03-28
52625 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-03-20 08:13 | 2017-03-20 10:17 | 2017-03-20 | MANUAL REACTOR TRIP AS A RESULT OF SECONDARY PLANT TRANSIENT "On March 20, 2017 at 0813 EDT, Watts Bar Nuclear Plant (WBN) Unit 2 operations personnel manually tripped the plant from approximately 91 percent power based on lowering steam generator levels. Prior to the plant trip, the 2A Hotwell pump tripped at 0758 EDT and the 2C Condensate Booster Pump subsequently tripped at 0802 EDT. Operations personnel commenced to lower plant power after the 2A Hotwell pump trip in an attempt to maintain steam generator levels, but were unable to recover level and manually tripped the unit. "All control rods fully inserted and all automatically actuated safety related equipment operated as designed. At 0905 EDT, operations personnel exited the emergency operating instructions after the plant was stabilized. The cause of the event is under investigation. "This event is reportable to the NRC within four hours under 10 CFR 50.72(b)(2)(iv)(B) as a result of the actuation of the Reactor Protection System and in eight hours under 10 CFR 50.72(b)(3)(iv)(A) as a result of actuation of the Auxiliary Feedwater system. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-03-20
52624 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2017-03-20 02:27 | 2017-03-20 04:40 | 2017-03-20 | MANUAL SCRAM DUE TO PRESSURE OSCILLATIONS "On March 20, 2017 at 0227, Nine Mile Point Unit1 was manually scrammed due to pressure oscillations. The Unit was offline and reactor shutdown was in-progress at the time of the scram. The scram was inserted at approximately 4% reactor power when pressure oscillations occurred exceeding the procedurally required limit for pressure oscillations. The cause of the scram was due to Operators manually inserting the scram. The cause of the pressure oscillations is being investigated." The licensee notified the NRC Resident Inspector. Notified the R1DO (Gray). | 0 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-03-20
52623 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2017-03-18 11:07 | 2017-03-18 15:07 | 2017-03-18 | REACTOR TRIP AND LOSS OF ABILITY FOR UNIT 4 TO SUPPLY POWER TO UNIT 3 "On 3/18/17 at 1107 [EDT], the Unit 3 reactor tripped as a result of the loss of the 3A 4kV bus. All three reactor coolant pumps (RCP) tripped and the 3B RCP was restarted for forced recirculation. The reactor is stable in Mode 3. The 3A 4kV bus remains deenergized until troubleshooting and repairs are complete. In addition, Technical Specification 3.8.1.1, Action C requires a four hour report for the concurrent inoperability of the Unit 4 startup transformer to Unit 3 via the 3A 4kV bus and the Unit 3 3A diesel generator. "The NRC Senior Resident Inspector will be notified." * * * UPDATE ON 3/18/2017 AT 1854 EDT FROM JAMES SPICHER TO BETHANY CECERE * * * "Update to previous report (EN 52623) to include additional reporting criteria. "On 3/18/17 at 1107 [EDT] the Unit 3 reactor tripped as a result of the loss of the 3A 4kV bus. The 3A Emergency Diesel Generator (EDG) started on the loss of power signal but did not load, as designed, due to the bus fault. The 3A EDG was manually stopped at 1332. The Auxiliary Feedwater (AFW) System also initiated as expected. AFW was stopped at 1135. The actuations of the 3A EDG and AFW are reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A). "A loss of safety function affecting Units 3 and 4 occurred due to the loss of the 3A high head safety injection (HHSI) pump because it could not be powered from the faulted 3A 4kV bus with both Unit 4 HHSI pumps earlier (0624) removed from service due to planned maintenance. This caused three of the four HHSI pumps to be inoperable. The four HHSI pumps are shared by both Units 3 and 4. The safety function is achieved by two of the four HHSI pumps. Both Unit 4 HHSI pumps were restored to operable status at 1336. The loss of safety function is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D). "The Unit 3 reactor is stable in Mode 3. The 3A 4kV bus remains deenergized until troubleshooting and repairs are complete. Unit 4 remains operating at 100% power." The licensee will notify the NRC Resident Inspector. Notified R2DO (Ehrhardt) and NRR EO (Miller). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) | 0 | 2017-03-18
52622 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-03-18 06:15 | 2017-03-18 13:54 | 2017-03-18 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the state of Texas via email: "On March 18, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that a Troxler model 3440 moisture density gauge, serial #64732, containing a 1.48 GBq (40 mCi) Am-Be source and a 0.3 GBq (8 mCi) Cs-137 source was stolen. The licensee stated a technician improperly took the gauge home and left it in the back of his pickup truck. The sources were locked and inside their case. The case was secured by two locking mechanisms, both were cut sometime during the night before 0615 [CDT]. Local law enforcement was notified. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9472 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-03-27
52621 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2017-03-18 11:19 | 2017-03-18 12:09 | 2017-03-18 | ALERT DECLARED FOR INDICATIONS OF FIRE IN SAFETY RELATED SWITCHGEAR "Alert declared at 1119 EDT 3/18/17 based on EAL H.A.2 - Fire or Explosion affecting plant safety systems. Fire alarms in the Unit 3 4kV switchgear rooms resulting in a loss of the 3A 4kV bus and trip of all three Reactor Coolant Pumps. The reactor tripped and was stabilized in Mode 3. No actual fire was observed. The 3A 4kV is deenergized. The 3B Reactor Coolant Pump was restarted for forced circulation. All other safety systems functioned as required. A refueling outage was scheduled to begin on 3/20/17." All control rods fully inserted on the reactor trip. Decay heat is being removed using feedwater and steam generator atmospheric steam dumps. One person was injured with a minor burn and possible sprained ankle and was taken to a local hospital. The licensee notified the NRC Resident Inspector. Notified DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, FDA (e-mail), NWC (e-mail), NNSA (e-mail), and NRCC SASC (e-mail). * * * UPDATE AT 1426 EDT ON 3/18/2017 FROM DAN HAGARDY TO BETHANY CECERE * * * "Unit 3 was determined by the Emergency Coordinator to be in a safe and stable condition, the Emergency Plan personnel at the Technical Support Center and Emergency Operations Facility were no longer required for support, the Operations Support Center was staffed for recovery efforts, and plant personnel were sufficient and capable for continuing mitigation efforts. "Investigation of the fault on the 3A 4kV bus is ongoing. "Based on the above conditions, the Alert was exited at 1420 hours [on 3/18/2017]." The injured electrician was taken to an offsite hospital to treat minor burns and possible sprained ankle. The licensee notified the NRC Resident Inspector. Notified the R2DO (Ehrhardt), NRR EO (Miller and King), IRD MOC (Stapleton), DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, FDA (e-mail), NWC (e-mail), NNSA (e-mail), and NRCC SASC (e-mail). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | ALERT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-03-18
52620 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-03-16 16:04 | 2017-03-17 16:45 | 2017-03-17 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "RHB-North [Radiologic Health Branch - North] received an email from CDPH [California Department of Public Health], Emergency Preparedness Office, Disaster Information Coordinator that they received a message from CAL OES [California Office of Emergency Services] stating that a nuclear density gauge was run over and damaged by earth moving equipment. "Incident location: 308 Love Lane, Danville, CA 94526 - Contra Costa County, time 16:04 [PDT]. "RHB North contacted the Manager, Pacific Nuclear Technology (PNT), to survey the area and collect the damaged gauge. [He] went to the incident location, evaluated the moisture density gauge, and confirmed that the sealed sources Cs-137 and Am-241:Be were intact and were in the shielded position. In addition [he] surveyed the gauge and the surrounding area with a Ludlum Model 3, PR 44-9 and found no contamination, [he] further verified that exposure at 1 meter was 0.4 mRem/hr. "Because the source was not damaged and the TI [Transportation Index] was within the limit, the licensee owner/operator insisted in taking the damaged gauge to the storage location . . . . [The owner/operator] said that the following day he will take the damaged gauge to CPN InstroTek Inc. for exchange or disposal. "On March 17, 2017 RHB-North verified that CPN InstroTek Inc. has received the damaged gauge and the leak test result was negative. "PNT equipment: Ludlum Model 3, PR 44-9, Calibration date 04/28/2016." 5010 Number: 031617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-03-27
52619 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-03-17 15:17 | 2017-03-17 17:12 | 2017-03-17 | AUTOMATIC ACTUATION OF EMERGENCY DIESEL GENERATOR "At approximately 1517 [EDT], while restoring protective relay power to the 1B Reserve Auxiliary Transformer, a valid undervoltage actuation signal was sent to the 1B Emergency Diesel Generator (EDG). The 1B EDG automatically started and tied to the safety bus (1BA03). The 1BA03 bus was loaded by the automatic load sequencer. This actuation was identified by the Control Room Operators and the 1B EDG was locally monitored while in service. "This actuation is reportable due to the automatic actuation of a system listed in 10 CFR 50.72(b)(3)(iv)(B). "The reactor was not critical at the time of the event and not challenged throughout the event. "Containment Cooler Number 8 did not automatically start in 'Fast Speed' as expected. Containment Cooler Number 8 was successfully started in 'Fast Speed' manually by the Control Room Operators. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-03-17
52618 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-03-09 01:20 | 2017-03-17 17:08 | 2017-03-17 | CONTAINMENT AIRLOCK FUNCTION LOST DUE TO EQUALIZING VALVE NOT CLOSING "On March 9, 2017 at 0120 EST, the equalizing valve for the Watts Bar Nuclear Plant (WBN) Unit 2 upper containment airlock inboard door was found not closed while the outboard airlock door was open. This created a containment bypass with leakage potentially greater than allowed by the design. The operator immediately identified, after opening the outer door of the elevation 757 Air Lock, the pressure equalizing valve for the inner door was not fully closed. The outer door was promptly shut to isolate the airlock. The inner door was then cycled which closed the equalizing valve. The total time that a containment bypass was present is estimated at five minutes. "This condition was initially recognized as being potentially reportable. However, the assessment performed at the time, based on operator control of the outer airlock door, concluded there was a reasonable assurance of meeting the safety function. A subsequent independent review of this condition identified that this should have been reported under 10 CFR 50.72(b)(3)(v)(C) within eight hours of the event. "The NRC Resident Inspector has been informed of this event." The licensee is planning on replacing the equalizing valve in the near future. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-03-17
52617 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-03-17 07:00 | 2017-03-17 13:14 | 2017-03-17 | AGREEMENT STATE REPORT - TRANSPORTATION ACCIDENT DAMAGING LICENSED MATERIAL The following report was received via email: "At about 0700 [EDT] on March 17, 2017, the Department [Pennsylvania Bureau of Radiation Protection] received notification through the Pennsylvania Emergency Management Agency of a vehicle fire near mile marker 286 on I-76 (PA Turnpike) [near Reading, PA]. The vehicle was carrying approximately 0.6 Ci (22 GBq) Tc-99m and 1 Ci (37 GBq) of F-18 for Cardinal Health (PA licensee PA-0415). Department emergency response and radiological health physics staff responded to the scene. The vehicle was entirely engulfed in flames and allowed to burn itself out. There are no reports of injuries. A representative from the licensee was on scene and collected contaminated debris and ash which was returned to their facility for decay. "The vehicle will be removed from the scene and isolated to allow any remaining material to decay. Departmental health physics inspector will oversee operations." PA Event Report ID No: PA 170006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-03-27
52616 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-03-16 | 2017-03-17 12:52 | 2017-03-17 | AGREEMENT STATE REPORT - PATIENT DOSAGE LOWER THAN PRESCRIBED The following report was received via email: "On March 16, 2017, a patient was prescribed a 12.16 milliCurie treatment dosage of Y-90 Sirspheres. As the AU [Authorized User] was pushing on the syringe he noticed a strong resistance, as did the interventional radiologist. Therefore, the administration was stopped to prevent any further safety issues. The micro catheter was pulled from the patient and the vial with the micro catheter and other radioactive waste was put in the jar for measuring. As the micro catheter was pulled, a very small defect was observed. The activity administered was 53% less than the prescribed dosage (5.64 milliCuries). The outer wrapping of the catheter was kept. The patient will be notified once recovered from the anesthesia. The licensee is investigating. "The cause of the event may be a potential manufacturing defect. "A reactive inspection is planned by the Department [Pennsylvania Bureau of Radiation Protection]. More information will be provided upon receipt." PA Event Report ID No: PA 170005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-03-27
52615 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-03-14 16:00 | 2017-03-16 15:07 | 2017-03-16 | PART 21 NOTIFICATION - EVALUATION OF A DEVIATION - STARTER CONTACTOR FAILURE "Pursuant to 10 CFR Part 21, this is a non-emergency notification by Energy Northwest concerning a defect in Size 1 Freedom Series Starters with nominal 120 VAC coils manufactured by AZZ/NLI [Nuclear Logistics Inc.] used at Columbia Generating Station. "On February 8, 2017 Energy Northwest was notified by NLI of a deviation associated with starter contactors used at Columbia that failed to close due to overheating of the starter coil. The coils that were provided were determined to not meet specified voltage ratings. "The evaluation completed by Energy Northwest on March 14, 2017 concluded that the deviation did create a Substantial Safety Hazard, and is reportable under 10 CFR 21.21(d)(1) as a defect. "A 30 day report will be issued by April 13, 2017 per 10 CFR 21.21(d)(4)." The licensee performed a prompt operability assessment for the two starters currently installed. The licensee will notify the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2017-03-16
52614 | 0 | SIOUXLAND UROLOGY CENTER |  |  |  |  | 2017-03-16 08:00 | 2017-03-16 14:28 | 2017-03-17 | MEDICAL EVENT - PATIENT DOSAGE HIGHER THAN PRESCRIBED At approximately 0800 CDT today, a patient was treated with 110 Palladium-103 seeds (1.68 milliCuries each) to the prostrate. The quantity was determined by calculation for a prescribed dose of 125 Gy, however the calculation was incorrect. The mistake was discovered after the patient's treatment. Only 80 seeds should have been implanted. The activity injected is 38 percent higher than prescribed. The referring physician has been notified. The physician is notifying the patient. It is believed that this event will not result in any harm to the patient. The licensee is in the process of determining corrective action to prevent reoccurrence. * * * UPDATE FROM GREG HAAR TO BETHANY CECERE VIA EMAIL 1241 EDT ON 3/17/17 * * * "This email is to confirm our notification to the NRC of a possible medical event that occurred during an LDR [Low Dose Rate] brachytherapy prostate seed implant at our clinic on (3/16/2017) at approximately 0800 [CDT]. The associated license number is #40-34223-01. "The procedure was a Palladium-103 implant, with a prescribed dose of 125 Gy. The implant was using Pd-103 seeds with an average activity of 1.68 milliCuries per seed. During this implant, 110 seeds were implanted into the patient instead of 80 seeds. This resulted in a total implanted activity of 184.8 milliCuries, which we estimate to exceed the prescribed dose to the patient by 20 percent. "The patient and the referring physician have been notified." Notified R4DO (O'Keefe) and NMSS Events Notification (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2017-03-24
52613 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2017-03-15 | 2017-03-16 09:44 | 2017-03-16 | AGREEMENT STATE REPORT - IRRADIATOR ROD STUCK IN UP POSITION The following report was received from the Maryland Radioactive Materials Division via email: "This afternoon [3/15/17], our [Johns Hopkins University (JHU)] JL Shepherd Mark I irradiator malfunctioned. This is a manual model. The source is lifted up into position by a knob that lifts a rod attached to the source. When lifting the knob up, the rod became jammed. The rod is stuck in an up position, slightly past halfway. It will not move up or down. "JL Shepherd was called for help. One suggestion was to move the knob slightly from side to side while lifting or lowering. This had no effect. Because this is a manual model not much can be done besides a repair by manufacturer. The technician [at JL Shepherd] said the most likely cause was due to some part (bearing, spring, etc.) falling down into transfer tube causing it to jam. "The irradiator's power supply is controlled by computer and is off now. The door latch on the irradiator is locked. The alarming area radiation monitor on the irradiator door is on and functioning. The key to both the irradiator controller and the door latch have been removed from the irradiator room. The irradiator room is locked and monitored by corporate security and a Remote Monitoring System. The irradiator room is only accessible to approved individuals. Because this unit is a self-shielded irradiator, radiation levels outside the unit are minimal, <0.2 mR/hr) even with the source being partially exposed inside. There is no sample inside the chamber. There is no way to physically open the irradiator door due to an electric interlock. The interlock will not function without power and will not function without the rod in the fully down position. A sign has been put on the irradiator, 'Do Not Use'. "JL Shepherd was scheduled to visit [the JHU] site to calibrate another irradiator in March. On Thursday we [JHU] will find out when we [JHU] can have a technician here to fix the problem. "Source Make: J.L. Shepherd and Associates Source Model: 6810-G Source Serial #: 81Cs-S14 NSTS Source ID Number: 6729 Isotope: Cs-137 Activity: 5329 Ci Activity Date: 02/25/2017" MD Event Report ID No.: 52613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2017-03-24
52612 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-03-15 09:00 | 2017-03-15 16:22 | 2017-03-15 | COLORADO AGREEMENT STATE REPORT - MISSING CO-57 ANALYZER SOURCE The following information was obtained from the state of Colorado via email: "The general license section of the Radioactive Materials Program [at the Colorado Department of Public Health and Environment (CDPHE)] sent out annual notifications requesting response regarding a Cobalt 57, 0.165 mCi, FA4C Analyzer Source serial #C9285 distributed under Edax Portable Products Division back in July 22, 1996. After 10 years of sending a report requesting information to the [business] address with no response, our [CDPHE] general license section is closing out this record." Colorado Event Report ID No.: CO17-0007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-03-23
52611 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2017-02-16 | 2017-03-14 17:35 | 2017-03-14 | AGREEMENT STATE REPORT - ADMINISTERED DOSE LOWER THAN PRESCRIBED DOSE The following information was received from the Commonwealth of Kentucky via email: "Hardin Memorial Hospital (HMH) reported that a patient only received 106 mCi of I-131, instead of the prescribed 150 mCi post-thyroidectomy on 2/16/17. Two capsules of I-131 were received from the radiopharmacy in a single vial. When the technologist gave the patient the vial, the patient shook the contents of the vial into her mouth only swallowing one capsule. The tech did not see one capsule remained in the vial. Surveys on the package (containing the vial) that was to be sent back to the radiopharmacy were higher than background so [it] was held for decay. Another survey on 2/28/17 was taken and was still higher than background so the tech opened the package and discovered the remaining pill." Kentucky Event Report ID No.: KY170002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2017-03-22
52610 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-03-12 | 2017-03-13 18:09 | 2017-03-13 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the state of California via email: "A Troxler model 3440, serial number 69286 moisture density gauge was stolen from a gauge user's locked vehicle during the night of March 11, 2017. The vehicle was parked at his residence overnight (in Northridge, CA and with permission from the RSO) due to an early morning job on March 12, 2017. This Troxler model contains an 8 mCi Cs-137 sealed source and a 40 mCi Am-241:Be sealed source. "The Troxler's Cs-137 source rod was locked into SAFE mode with a padlock and the transport case had two locked padlocks. One chain with two locks secured the transport case to the crew cab seat, within the locked truck. Los Angeles Police Dept. [LAPD] responded and found the truck's window had been broken. The police took fingerprints from the vehicle and filed a report. In addition, LAPD advised AESCO to place a Craigs List ad under Lost and Found offering a reward for the return of the stolen gauge." California report number: 5010-031217 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-03-21
52609 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2017-03-13 15:45 | 2017-03-13 17:45 | 2017-03-14 | SAFEGUARDS REPORT - DEGRADED VITAL AREA BARRIER Safeguards system degradation related to vital area barrier. Compensatory actions taken. The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 3/14/17 AT 1728 EDT FROM JUSTIN WIEMER TO DONG PARK * * * Safeguards system degradation related to vital area barrier potentially occurred earlier than originally reported. Compensatory actions remain in place. The licensee has notified the NRC Resident Inspector. Notified R4DO (O'Keefe). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-03-13
52608 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2017-03-09 | 2017-03-13 17:11 | 2017-03-13 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK IN OPEN POSITION The following information was obtained from the state of Minnesota via email: "Minnesota Dept. of Health [MDH] was notified by phone message March 10, 2017. The message was retrieved March 13, 2017 by the RAM [Radioactive Material] unit Supervisor. MDH visited the site March 13, 2017 and gathered the following information regarding the source holder. "Category: External EMS Housings Source Model: P-2608-100 (Co-60) Gauge Model: LB 300 ML Manufacture Date: 10/2013 Manufacturer: Berthold Systems, Inc. Source Number: 1816-10-13 (mold housing 12) Original Activity: 1.5 mCi Current Activity: 1.4050 mCi "The licensee is a steel processor and the incident involved molten steel encasing the source holder, locking the shutter in an open position. This is not a typical occurrence. The licensee is working with a consultant (Applied Health Physics) to develop a plan for removing the source holder from the mold and determining whether the source holder is repairable or if it needs to be disposed of." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2017-03-21
52607 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2017-03-13 13:58 | 2017-03-13 16:47 | 2017-04-18 | DISCOVERY OF NON-CONFORMING CONDITIONS DURING TORNADO HAZARDS ANALYSIS "On March 13, 2017, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Callaway Plant identified non-conforming conditions in the plant design such that specific Technical Specification equipment is considered to not be adequately protected from tornado missiles. "The Emergency Fuel Oil Truck Connection Lines for both redundant Emergency Fuel Oil trains extend through the Plant South wall of the Diesel Generator Building structure where they may be exposed to design bases tornado missile impact. The direct impact by the design basis missile could result in damage to the fuel oil transfer lines, thereby preventing delivery of the fuel supply from the Emergency Fuel Oil buried storage tank to the Fuel Oil Day Tank. This condition affects the fuel supply to both supported Emergency Diesel Generator trains. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) Shut down the reactor and maintain it in a safe shutdown condition, (B) Remove residual heat, or (D) Mitigate the consequences of an accident. "These conditions are being addressed in accordance with EGM 15-002 and DSS-ISG-2016-01 [enforcement discretion and interim guidance documents]. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 4/18/17 AT 1547 EDT FROM BRANDON LONG TO DONG PARK * * * "Event Notification EN # 52607, made on 03/13/2017, is being retracted because new information has been obtained that negates the originally reported condition. Specifically, subsequent to the Event Notification, an engineering analysis was performed which confirmed that a design basis missile strike on either of the unprotected truck connection lines would not result in damage to the extent that the affected fuel oil transfer lines would be prevented from delivering the fuel supply from the Emergency Fuel Oil buried storage tank to the Fuel Oil Day Tank. (The analysis showed that although bending / deformation of the lines would occur in response to the postulated missile strike, integrity of the lines would remain.) "Based on the above, the unanalyzed condition did not prevent the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition, remove residual heat, or mitigate the consequences of an accident, nor did it significantly degrade plant safety. Consequently, the condition does not meet the criteria for 8-hour notification that are provided in 10 CFR 50.72(b)(3)(ii)(B) or 10 CFR 50.72(b)(3)(v)(A), (B), or (D). "As the condition does not require enforcement discretion, the provisions of EGM 15-002 and DSS-ISG-2016-01 [enforcement discretion and interim guidance documents] need not be invoked. However, the immediate and long-term compensatory actions that have been taken following discovery of the condition will remain in place until the condition is fully resolved. "The NRC Resident Inspector has been informed of this Event Notification retraction." Notified R4DO (Azua). | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2017-03-13
52606 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-03-13 09:50 | 2017-03-13 11:48 | 2017-03-21 | AGREEMENT STATE REPORT - IR-192 SOURCE SHIPPED TO THE WRONG LOCATION The following information was obtained from the state of Louisiana via email: "On Friday, March 10, 2017, TEAM Industrial Services, Inc., in Borger, TX expected to receive two Ir-192 radiography camera sources from Source Production & Equipment Co., Inc., in St. Rose, LA. Only one source arrived at TEAM Industrial. The transportation company began a search for the missing source and discovered that the source had been shipped to Portland, OR. The source, 105 Ci of Ir-192 (as of 3/13/17), is enroute to TEAM Industrial in Texas and expected to be there by Thursday 3/16/17. The source was a G-60 source, serial number YC0801, in a SPEC-150, serial number 137." Louisiana Event Report ID No.: LA170003 *** UPDATE ON 3/21/17 FROM JAMES PATE TO NESTOR MAKRIS *** The following update was received via email: "The transportation misplaced source was located and was received by TEAM Industrial on Friday 03/17/2017. "The source was received at the designated receiving location on Friday 03/17/2017." Notified R4DO (Drake), ILTAB DO (Davis), and NMSS Events Notification. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-03-21
52605 | 0 | ZION |  |  |  | ISFSI | 2017-03-10 15:00 | 2017-03-10 19:13 | 2017-03-10 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED TO A MEDICAL FACILITY "At 1500 CST on 3/10/17, the Safety Department notified the Zion ISFSI Shift Supervisor that a contracted employee was injured while working inside of Unit 2 containment. The individual was struck in the back by a cable. This individual required off-site medical treatment, and an ambulance responded to site at 1508 CST. At 1520 CST, It was decided that this event was to be treated as a potentially contaminated injured individual being transported to an off-site medical facility. Vista East Medical Center was notified at 1523 CST to prepare for the receipt of the potentially contaminated individual. A Radiation Protection Technician and a Radiation Protection Supervisor accompanied the injured person to the hospital in an ambulance which departed the site at 1525 CST. A preliminary radiation survey was performed inside the ambulance at 1536 CST which detected no contamination on the individual. Due to the nature of the injury, a complete body survey was unachievable at that time. The ambulance arrived at the hospital at 1552 CST. At 1554 CST, Radiation Protection Technician performed a more comprehensive contamination survey in which no contamination was detected on the individual. Again, due to the nature of the injury, a whole body survey was still unable to be completed. At 1609 CST, a survey encompassing the individual's entire body was performed by the Radiation Protection Technician and no contamination was found." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OFFSITE MEDICAL | [9 empty] | NON EMERGENCY | 3 | IL | ISF |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2017-03-10
52604 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-03-10 | 2017-03-10 13:52 | 2017-03-10 | AGREEMENT STATE REPORT - LOST TROXLER GAUGE The following report was received from the State of Florida Bureau of Radiation Control via email: "[The licensee] left the gauge on the tailgate of his truck and drove away from the jobsite. Realizing that he had forgotten to secure the gauge properly he retraced his travel back to the last known location, but could not find the missing gauge. "Device Type: Moisture Density Manufacture: Troxler Model Number: 3430 Serial Number: 70824 Isotope and Activity: Cs-137, 8 mCi and AmBe 40 mCi. "Florida Incident Number: FL17-074" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-03-20
52603 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2017-03-09 | 2017-03-10 13:08 | 2017-03-10 | AGREEMENT STATE REPORT - FIRE DURING RADIOGRAPHY OPERATIONS The following information was provided by the State of Minnesota via email: "A Team Industrial Services radiography crew was working at Flint Hills Refinery on March 9, 2017. Approximately 7 minutes after starting a 13 minute exposure, one of the radiographers (Radiographer 1) noticed a fire had started near the exposure device. Radiographer 1 instructed the other radiographer (Radiographer 2) to call the plant's fire department and notify the Team's lead radiographer at their Rosemount location. Radiographer 1 then attempted to retract the source and was unsuccessful. Radiographer 1 then successfully extinguished the fire however the fire started again shortly after. At this point Radiographer 1 exited the unit. [The Team's lead radiographer] instructed the crew to extend their boundaries and wait for assistance. [The Team's lead radiographer] contacted the Team's Radiation Safety Officer. "The fire department arrived and was able to extinguish the fire from a ladder truck located outside the radiographer's boundaries. The Team's lead radiographer and [another individual] arrived on-site and assessed the situation. Other available radiographers were dispatched to the site to assist in monitoring the site boundaries. [The Team's lead radiographer] sent pictures of the site to [the Team's Radiation Safety Officer] who contacted QSA for assistance in planning the source retrieval. The retrieval team was able to identify that the drive cables conduit was melted, exposing the drive cable and separating the connection from the camera causing the crank to malfunction. They manually attempted to retract the drive cable and were able to confirm with survey meters that the source was still connected to the drive cable. The drive cable was manually retracted and the source was pulled into the shielded position. Surveys were taken to confirm the source was shielded, and the source was locked in position. "The source has been leak tested and the sample was overnighted to QSA for analysis. The plant is assessing the situation and will issue a report regarding the cause of the fire. The pocket dosimeter readings for the crew were as follows: Radiographer 1: 54 mR Radiographer 2: 15 mR Another individual: 13 mR Team's lead radiographer: 5 mR "The licensee is in the process of assessing the dose received by the fire fighters, however it is assumed that their doses were minimal based on the doses received by the radiography crew and their distance from the source. The licensee is preparing and will issue a written report within the required 30 day time frame. "Exposure device: QSA 880 D. Source: A-424-9, Ir-192, 64 curies" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2017-03-20
52602 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-03-10 07:14 | 2017-03-10 11:41 | 2017-03-10 | MANUAL REACTOR SCRAM DUE TO CLOSURE OF THE MAIN TURBINE CONTROL VALVES "At 0714 CST on March 10, 2017, with the unit in Mode 1 at approximately 17% power, a manual actuation of the reactor protection system (RPS) was initiated due to rising reactor pressure caused by the closure of the Main Turbine Control Valves (MTCV's). The cause of the closure of the MTCV's is under investigation. "The unit is currently stable in Mode 3. "All control rods inserted as expected; water level control is stable in the normal control band and reactor pressure is being maintained with steam line drains [aligned to the main condenser]. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-03-10
52601 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-03-09 03:19 | 2017-03-09 10:57 | 2017-03-09 | UNANALYZED CONDITION DUE TO RELAY FAILURE "On March 7, 2017, Division 2 Residual Heat Removal (RHR) system was inoperable due to a scheduled maintenance system outage window. At 2258 [CST], Operations identified a Division 1 Unit Substation Switchgear relay was cycling, which is part of the Division 1 AC Power system. The specific relay could not be identified at the time. Division 1 AC Power systems were protected. "On March 8, 2017 at 1830 hours, Division 2 RHR was restored to operable status. "On March 9, 2017 at 0319 hours, Operations declared Division 1 Emergency Diesel Generator (EDG) inoperable due to the [identification of the] Division 1 relay as related to properly tripping non-essential loads on a bus under-voltage condition. The relay would not have actuated to trip non-essential loads. The proper tripping of non-essential loads is a requirement for Division 1 EDG. "The Updated Safety Analysis Report (USAR) Emergency Core Cooling Systems (ECCS) analysis specifies with the Division 1 DG failure, the remaining systems available are: Automatic Depressurization System (ADS), High Pressure Core Spray (HPCS), and 2 Low Pressure Core Injection (LPCI) systems. "As a result of Division 2 RHR [being] inoperable at the same time Division 1 EDG was inoperable, an unanalyzed condition existed. While Division 2 RHR was inoperable, Division 1 EDG was inoperable. Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.1, AC Sources - Operating, was not met. Condition B, One Required DG Inoperable, Required Action B.2 declares required features, [normally] supported by the inoperable DG, inoperable when the redundant required features are inoperable, with a completion time of 4 hours. The action would have required declaring Division 1 ECCS inoperable, which includes Division 1 RHR and Low Pressure Core Spray (LPCS). "With Division 1 EDG, Division 1 RHR, and Division 2 RHR inoperable, the station did not satisfy the USAR ECCS analysis and was in an unanalyzed condition. This condition is reportable under 10 CFR 50.72(b)(3)(ii)(B), Unanalyzed Condition, since the condition occurred within three years of the date of discovery. "The NRC Resident Inspector has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-03-09
52600 | 0 | WATERFORD | 3 |  |  | [3] CE | 2017-03-08 16:27 | 2017-03-08 20:13 | 2017-03-08 | BOTH TRAINS OF LOW PRESSURE SAFETY INJECTION INOPERABLE DUE TO MAINTENANCE ERROR "This is a non-emergency notification from Waterford 3. "On March 8, 2017 at 1627 [CST] Technical Specification (TS) 3.5.2 action 'c' was entered due to both trains of Low Pressure Safety Injection (LPSI) being inoperable. This TS action requires one train of LPSI be restored within 1 hour or be in at least Hot Standby within the next 6 hours. "It was identified that LPSI train B was inoperable due to SI-135B, Reactor Coolant Loop 1 Shutdown Cooling Warmup Valve, being found open. At the time of discovery, LPSI train A was inoperable for pre planned maintenance, but available and awaiting operability retest. The station was in compliance with TS 3.5.2 action 'a'. Maintenance workers were scheduled to work Sl-135A Reactor Coolant Loop 2 Shutdown Cooling Warmup Valve, and inadvertently began work on Sl-135B and manually opened the valve which resulted in the LPSI Train B being inoperable. "Once identified by Operations Control Room staff, the valve [SI-135B] was placed in the closed position and stroke tested to ensure operability. TS 3.5.2 action 'c' was exited at time 1705. The station remained in compliance with TS 3.5.2 action 'a'. " The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-03-08
52599 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-03-08 02:39 | 2017-03-08 08:49 | 2017-03-08 | LOSS OF SECONDARY CONTAINMENT DUE TO CONTAINMENT FAN TRIP "On March 08, 2017 at 0239 hours [EST], Secondary Containment Zone 3 (Unit 1 and 2 Reactor Building) differential pressure lowered to 0 [inches] WG due to a trip of the running Zone 3 Secondary Containment fans. The fan trip was caused by a human performance error during a Unit 2 outage related activity. Required differential pressure per SR 3.6.4.1.1 could not be maintained. Zone 3 differential pressure recovered to [greater than] 0.25 [inches] WG at 0255 hours after restart of Zone 3 Secondary Containment fans. All other Zones of Secondary Containment were unaffected by this event. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022 Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-03-08
52598 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-02-23 | 2017-03-07 20:00 | 2017-03-07 | AGREEMENT STATE REPORT - LOST I-125 SEED The following information was provided by the State of California via email: "On 02/23/17, the RSO [Radiation Safety Officer] contacted RHB [California Radiologic Health Branch] to report a lost I-125 seed with an activity of 0.388 mCi. Licensee stated that three lead pigs each with an I-125 seed (0.303 mCi and 0.388 mCi from February 22nd and a 0.388 mCi I-125 seed from February 8th) believed to be accidentally thrown in Mission Bay Hospital general waste. When this was discovered, licensee contacted Recology, requested an urgent pickup of their waste compactor container at Recology site on 02/23/17. Digging through the waste, licensee was able to locate two of the three lead pigs (both from February 22nd). The pig containing 0.388 mCi I-125 from February 8th was not recovered and believed to be buried in the landfill. UCSF [University of California, San Francisco] was getting seeds from Oncura, [which] was recently bought out by Theragenics. UCSF medical physicists were accustomed to receiving just the patient seeds. Theragenics, the new vendor, had included an additional calibration seed in a separate led pig in the same package and physicist were not looking for this additional seed. "RHB will be following up on the corrective actions." CA 5010 Number: 022317 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-03-15
52597 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-03-07 08:30 | 2017-03-07 14:39 | 2017-03-07 | BREACH IN AUXILIARY BUILDING SECONDARY CONTAINMENT "At 0830 [EST] on March 7, 2017, operators discovered that on March 3, 2017 at 2046 a door was blocked open creating a breach of the auxiliary building secondary containment enclosure (ABSCE) boundary that exceeded the allowed ABSCE breach margin. As a result, both Unit 1 and Unit 2 entered Technical Specification Limiting Condition of Operation (LCO) 3.7.12 Condition B for two trains of Auxiliary Building Gas Treatment System (ABGTS) inoperable due to an inoperable ABSCE boundary in MODE 1, 2, 3, or 4. The condition has been corrected and ABGTS was restored to operable as of 0949 March 7, 2017. "In MODES 1, 2, 3, and 4, the analysis of the loss of coolant accident (LOCA) assumes that radioactive materials leaked from the Emergency Core Cooling System are filtered and adsorbed by the ABGTS. For the fuel handling accident, the analysis assumes that the ABSCE boundary is capable of being established to ensure releases from the auxiliary and containment buildings are consistent with the dose consequence analysis. "The event is reportable in accordance with 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to: (C) control the release of radioactive material and (D) mitigate the consequences of an accident. "No actual LOCA or fuel handling accident occurred while both trains of ABGTS were inoperable. The condition had no impact on the health and safety of the public. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-03-07
52596 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2017-03-06 20:00 | 2017-03-07 13:44 | 2017-03-13 | RADIOGRAPHY CAMERA SOURCE DID NOT LOCK IN THE SHIELDED POSITION WHEN RETRACTED While performing radiography in arctic conditions at the Alpine oil field between ice roads CD1 and CD5, the radiographer retracted the source after an exposure and failed to recognize that the source was not in the locked position. Prior to moving the radiography camera to the next area for an exposure, the survey indicated the source was in the shielded position. The radiographer picked up the camera to take it to the next weld location for an exposure. When the radiographer placed the radiography camera down, his dosimeter rate alarm sounded, his survey meter (on the 10 scale setting) was off scale and his pocket dosimeter was off scale. It is believed that during the moving of the camera to the next shot location the source came out of the fully shielded position. The exact time and distance of the exposure is not known. Calculations show that the radiographer may have received between 3.5R - 39R of exposure. The radiographer's dosimeter has been sent for processing and results are expected in approximately 2 days. The assistant radiographer was not in the direct vicinity and received no exposure due to this event. The radiography camera involved was a QSA Global Model 880D with a 84.6 Ci Ir-192 source. * * * UPDATE FROM PATTON PETTIJOHN TO HOWIE CROUCH AT 1148 EDT ON 3/13/17 * * * The badge reading of the radiographer indicated that he received 452 mR exposure for the month therefore no overexposures occurred due to this event. Notified R4DO (O'Keefe), NMSS (McIntosh) and NMSS Events Notification email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-03-15
52595 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-03-06 18:30 | 2017-03-07 11:32 | 2017-03-07 | AGREEMENT STATE REPORT - STUCK SHUTTER DEVICE The following was received by email from the Texas Department of State Health Services: "On March 7, 2017, the Agency [Texas Department of State Health Services] was contacted by a representative of the licensee to report that on the previous day a gauge was found to have a stuck shutter. The gauge is a Berthold LB 7442D with a 30 mCi Cs-137 source. The shutter is stuck in the normal operating position. The licensee is in contact with the manufacturer for a repair plan and with licensing for an exemption to operate the gauge temporarily with a stuck shutter. No exposures to the public are expected. Additional information will be shared as it becomes available in accordance with SA-300. "Texas Incident #: I-9470" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-03-15
52594 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2017-03-06 11:45 | 2017-03-06 13:07 | 2017-03-06 | UNAUTHORIZED SITE ACCESS Licensee discovered an individual had provided false information to gain site access to the Protected Area. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-03-06
52593 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2017-03-04 | 2017-03-06 11:40 | 2017-03-06 | AGREEMENT STATE REPORT - MISSING IODINE 125 CALIBRATION SOURCES The following information was provided by the State of New York via Facsimile: "A New York Licensee's RSO [Radiation Safety Officer] left voice mail on March 5, Sunday afternoon, stating that he was informed on the evening of the previous day (March 4, 2017) that 2 vials containing 15 seeds of I-125 that were to be used for calibration purposes were missing from their inventory. The total activity of the 15 seeds was reported to be less than 7 mCi. The surface exposure rates at the exterior of the lead shielded vials was stated to be at background radiation levels. The AU [Authorizing User] physician and the RSO conducted a thorough search on March 5, 2017, but and were unable to locate the seeds. "DOH will staff became aware of the event earlier this morning [March 6, 2017] on arrival at work. Will update after following up with the licensee." NY State Event Report ID NO. NYDOH-NY-17-05 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-03-14
52592 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-03-05 08:00 | 2017-03-05 16:05 | 2017-03-06 | PLANNED ULTRASONIC TEST ON PREVIOUSLY REPAIRED REACTOR VESSEL PENETRATION DID NOT MEET ACCEPTANCE CRITERIA "On 3/5/2017 at 0800 [CST], during the Byron Station Unit 1 refueling outage, it was determined that the results of a planned Ultrasonic (UT) examination performed on a previous repaired penetration of the reactor vessel head did not meet applicable acceptance criteria. These indications are not in the reactor coolant pressure boundary; however they are very near the previously repaired J-groove weld. The indication will be addressed prior to returning the vessel head to service. The examination was being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1 to ensure the structural integrity of the reactor vessel head pressure boundary. "This event is being reported under 10 CFR 50.72(b)(3)(ii)(A) for 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' "The licensee has notified the NRC Resident Inspector. "Exelon Generation Company, LLC is also notifying the NRC Division of Component Integrity or its successor, by use of this ENS Report, of changes in indication(s) or findings of new indications(s) in the penetration nozzle or J-groove weld beneath a seal weld repair, or new linear indications in the seal weld repair, prior to commencing repair activities." See also EN #52591 * * * UPDATE PROVIDED BY CHARLES BERGER TO JEFF ROTTON AT 1750 EST ON 03/06/2017 * * * "Byron Event Notification 52952, made on March 05, 2017, reported two indications on one reactor head penetration. "On March 06, 2017, ultrasonic examination identified two additional indications on the same penetration nozzle, (P-76). Additionally, two indications were identified on a second penetration nozzle (P-74), and one indication was identified on a third penetration nozzle (P-77). The indications on these three penetrations are all of the same type and none are within the reactor vessel head pressure boundary. "This event is being reported under 10 CFR 50.72(b)(3)(ii)(A) for 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' "The NRC Resident Inspector has been notified. "Exelon Generation Company, LLC is also notifying the NRC Division of Component Integrity or its successor, by use of this ENS Report, of changes in indication(s) or findings of new indications(s) in the penetration nozzle or J-groove weld beneath a seal weld repair, or new linear indications in the seal weld repair, prior to commencing repair activities." Notified R3DO (Jeffers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-03-05
52591 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-03-03 17:05 | 2017-03-03 20:52 | 2017-03-03 | PREVIOUS OVERLAY REPAIR DID NOT MEET ACCEPTANCE CRITERIA "On 3/3/2017 at 1705 [CST], during the Byron Station Unit 1 refueling outage, it was determined that the results of a planned Liquid Penetrant (PT) examination performed on a previous overlay repair of the reactor vessel head did not meet applicable acceptance criteria. The penetration overlay weld indication will be addressed prior to returning the vessel head to service. The examination was being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1 to ensure the structural integrity of the reactor vessel head pressure boundary. Ultrasonic examinations have been performed and no ultrasonic indications were identified. "This event is being reported under 10 CFR 50.72(b)(3)(ii)(A) for 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-03-03
52590 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-03-02 | 2017-03-03 16:29 | 2017-03-03 | AGREEMENT STATE REPORT - TOTAL DOSE DELIVERED TO PATIENT DIFFERED FROM PRESCRIBED DOSE BY MORE THAN 20 PERCENT The following report was received from the Ohio Department of Health via email: "On March 3, 2017, The Urology Center, LLC, Ohio Radioactive Material licensee no. 02200310002, reported an incident pursuant to which the total dose delivered differed from the prescribed dose by more than 20 [percent]. The radiant source was brachytherapy seeds surgically inserted to the prostate. The incident occurred on March 2, 2017 and was confirmed on March 3, 2017 by a review of the post procedure CT [computed tomography] scan. The prescribed dose was 110 cGy using I-125 (model AgX100) seeds. The post CT plan shows that the actual dose delivered to the prostate was 27.6 cGy. The physicians do not believe that there are side effects to the rectum, urethra or neurovascular bundle as a result. "The patient has been informed." OH NMED Item Number: OH170001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-03-13
52589 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2017-03-03 15:32 | 2017-03-03 15:40 | 2017-03-03 | LOSS OF A SMALL QUANTITY OF SPECIAL NUCLEAR MATERIAL "This is a non-emergency notification regarding an extremely small amount of unaccounted Special Nuclear Material (SNM). At 1532 [EST] on 03/03/2017, the location of one ex-vessel dosimeter could not be determined. Ex-vessel dosimetry is used to measure radiation outside the reactor vessel over time. According to the station SNM inventory, the normally installed location for this dosimeter is the annulus between the shield wall and the pressure vessel, however the dosimeter was not in the expected location. "A thorough review of records was performed to locate the dosimeter. The dosimeter was installed in 1991. In 1993, the chain associated with the dosimeter broke and per a Westinghouse report the dosimeter was located in the under vessel sump area and was irretrievable at the time. The document states that this dosimeter will be removed in a future outage. A review of radiological waste transfer records could not specifically identify the disposition of the dosimeter. However, considering the last known location of the dosimeter, the most likely location is at Barnwell via a low level radioactive waste shipment. "This detector consisted of a small amount of SNM (approximately 2.67E-13g Pu 239). There is no evidence of theft or diversion of this dosimeter. "This is being reported under 10 CFR 74.11(a) for loss of SNM. This event had no effect on plant operations and no impact on public health and safety has been identified. "The station NRC Resident Inspector has been notified." Notified DHS, FEMA, DOE, EPA (NRC), USDA, and HHS. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 74.11(a) |  |  |  | 1 | 2017-03-13
52588 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-03-02 | 2017-03-03 14:40 | 2017-03-03 | TEXAS AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON A NUCLEAR GAUGE The following information was obtained from the state of Texas via email: "On March 3, 2017, SunTrac Services called about licensee Marathon Petroleum. They reported a stuck shutter found yesterday afternoon on a vessel. The line level indicator device was found with the shutter stuck open (normal operating position) during preparations to empty the vessel for entry to complete maintenance on the vessel. The measuring device was a Vega model SHF2 containing a Cs-137, 500 milliCurie source, serial number 0174CO. The device was removed from the fluid catalytic cracking unit and placed in storage by Suntrac Services, per authorization on their license. A lead plate will be affixed to the gauge to cover the source. The device will be serviced by either the manufacture or TexStar servicing company within the next two weeks while the vessel undergoes maintenance. There is no risk of exposure to any employees or member of the public. A written report will be provided in the next 30 days as per the consultant. "Updates will be in accordance with SA-300." Texas Incident #: I-9469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-03-13
52587 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-03-02 12:30 | 2017-03-02 13:53 | 2017-03-02 | NOTIFICATION OF UNUSUAL EVENT DECLARED At 1230 CST, the licensee declared a notification of unusual event based on Emergency Action Level 6.7-U, a non-hostile security event, due to introduction of contraband into the protected area. All required actions have been completed. There was no impact to the operation of any of the units at the Browns Ferry site. The licensee has notified the NRC Resident Inspector. See EN #52586. Notified DHS SWO, FEMA Ops, DHS NICC, FEMA NWC (email) and NuclearSSA (email). * * * UPDATE FROM THOMAS BRADFORD TO JEFF HERRERA AT 1611 EST ON 3/2/17 * * * At 1500 CST, the licensee terminated the notification of unusual event. The licensee has notified the NRC Resident Inspector. Notified R2DO (McCoy), NRR EO (King), and IRD (Grant). Notified DHS SWO, FEMA Ops, DHS NICC, FEMA NWC (email) and NuclearSSA (email). | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-03-02
52586 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-03-02 12:30 | 2017-03-02 13:53 | 2017-03-03 | SAFEGUARDS REPORT - ACTUAL INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA The licensee declared a notification of unusual event based on Emergency Action Level 6.7-U, a non-hostile security event, due to introduction of contraband into the protected area. All required actions have been completed. The licensee has notified the NRC Resident Inspector. See EN #52587. * * * UPDATE AT 1723 EST ON 3/3/17 FROM DAVID RENN TO JEFF HERRERA * * * The licensee provided additional information regarding the timeline of events. The Licensee has notified the NRC Resident Inspector. Notified the R2DO (McCoy), 73.71 (Group). | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED | SAFEGUARDS REPORTS |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) | 73.71(b)(1) |  |  | 1 | 2017-03-02
52585 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-03-01 13:03 | 2017-03-01 15:18 | 2017-03-01 | NOTIFICATION OF OFFSITE AGENCIES DUE TO SULFURIC ACID LEAK WITHIN THE D.C. COOK PROTECTED AREA "At 1303 EDT on March 1, 2017, DC Cook notified the State of Michigan of a sulfuric acid tank leaking over 1,000 gallons of acid into the tank's berm. The leak was identified at approximately 1000 EDT coming from a drain line flange. The berm is designed to contain over 15,000 gallons which is sufficient to collect the known capacity of the tank. Cleanup of the sulfuric acid from the berm is ongoing, with no release to the environment or nearby drains." "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of offsite agencies." "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-03-01
52584 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2017-02-28 14:30 | 2017-03-01 12:57 | 2017-03-01 | AGREEMENT STATE REPORT - TWO SEALED SOURCES TESTED POSITIVE FOR LEAKAGE The following information was received via email from the Commonwealth of Massachusetts: "The licensee reported on February 28, 2017 that licensee learned from its licensed leak test service provider that two 6 milliCurie, Cobalt-57, sealed sources, of 20 sources received in a package from the source manufacturer, Isotope Products Laboratories, tested positive for leakage. "The leak test result for one of the sealed sources was reported to be at least 0.4 microCuries which is the maximum activity that the instrument used can measure. The leak test result for the other sealed source was reported to be below the reporting requirement of 0.005 microCuries. "The sealed sources are each Isotope Products Laboratories Model 3901-2 sources. The serial number attributed to the source having leak test result of at least 0.4 microCuries was reported to be P3-682. The serial number attributed to the source having leak test result of below 0.005 microCuries was reported to be P3-689. "The licensee reported that each of the sources is contained and secured in a separate plastic bags; that there is no facility contamination based on area surveys performed; that the external surfaces of the package received, that had contained the sources, had been wipe tested and that the package was not contaminated; and that the sources were not used pending leak test results. "The licensee reports that it will notify the source manufacturer, to inquire about proper return of the sources back to the source manufacturer. "The Agency [Massachusetts Radiation Control Program] considers this event to be open." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2017-03-09
52583 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-02-28 10:30 | 2017-02-28 21:48 | 2017-02-28 | FITNESS FOR DUTY - PROHIBITED ITEM FOUND INSIDE PROTECTED AREA "Event Report per 10 CFR 26.719(b)(1). "On February 28, 2017, a violation of the site Fitness For Duty policy was committed. A prohibited item was found inside the Protected Area. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2017-02-28
52582 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2017-02-28 18:25 | 2017-02-28 21:34 | 2017-04-14 | SHORT DURATION LOSS OF SECONDARY CONTAINMENT DUE TO SEVERE WEATHER "At 1825 [CST] on 02/28/2017, Dresden Station received unexpected alarm 923-5 C-1, RX BLDG DP LO [Reactor Building Differential Pressure Low]. Reactor Building differential pressure was observed to briefly lose vacuum and return to a normal reading of 0.6 inches vacuum water gauge. At the time of the transient, Grundy County was under a Severe Weather Warning and gusts of wind were being monitored from the Main Control Room up to approximately 57 mph. The Reactor Building differential pressure returned to [greater than or equal to] 0.25 inches vacuum water gauge at 18:25 after 18 seconds with no operator action. Operators observed differential pressure reading to lose vacuum, below 0 inches vacuum water gauge, for approximately 3 seconds. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.1. As a result, entry into Technical Specifications 3.6.4.1 condition A was made due to Secondary Containment being inoperable. This event is being reported in accordance with 10CFR50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "An issue report has been initiated and a 60-day Licensee Event Report will be submitted in accordance with 10CFR50.73(a)(2)(v)(C). "The NRC Resident Inspector has been notified." * * * RETRACTION ON 4/14/17 AT 1429 EDT FROM BOBBY SHORT TO DONG PARK * * * "The purpose of this notification is to retract ENS notification 52582 made on 2/28/17 for Dresden Nuclear Power Station. The previous notification reported a potential loss of Reactor Building differential pressure due to high wind conditions and associated entry into Technical Specification 3.6.4.1 Condition A for failure to meet Surveillance Requirement 3.6.4.1.1 to maintain differential pressure above 0.25 inches vacuum water gauge. "After further evaluation, it has been determined that the high winds caused a momentary low pressure pocket on the leeward side of the Reactor Building causing the differential pressure reading seen in the Main Control Room, but it did not challenge Reactor Building differential pressure or Secondary Containment. Reactor Building differential pressure indication utilizes four transmitters, one on each wall of the Reactor Building, and the most conservative reading is transmitted to the indicator in the Main Control Room. Wind conditions impacting a single transmitter would result in indication of low Reactor Building differential pressure in the Main Control Room. Procedures direct action to obtain local readings from all four Reactor Building differential pressure transmitters. After the low indication in the Main Control Room, Equipment Operators were dispatched to obtain local indication and all four transmitters were found to be indicating 0.6 inches vacuum water gauge. "This was a short duration transient with no indications of an equipment failure that could impact Secondary Containment. The entire transient occurred within an 18 second window where differential pressure indication began at 0.6 inches vacuum water gauge, dropped to below 0 inches vacuum water gauge, and subsequently restored to 0.6 inches vacuum water gauge with no operator intervention. Furthermore, a significant change in Reactor Building differential pressure would impact readings on Drywell pressure because the Reactor Building pressure is used as a reference leg. Trends of Drywell pressure during the event indicated no adverse conditions implying that Reactor Building differential pressure was stable. Thus, it has been concluded that this was an indication issue and at no point during the transient would Secondary Containment have been unable to perform its safety function. "Therefore, this event does not meet the criteria of 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function, and the ENS notification is being retracted. There is no longer a requirement for an associated 60-day Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(v)(C). "The NRC Resident Inspector has been notified." Notified R3DO (Jeffers). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-02-28
52581 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-02-28 10:00 | 2017-02-28 16:24 | 2017-04-14 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE "On February 28, 2017 at 0930 [EST], a containment visual inspection was performed to identify the source of elevated RCS [Reactor Coolant System] leakage. A leak was identified between 13RC6 and 13SS661, 13 RCS hot leg sample isolation valves at 1000 [EST]. These valves are manual isolation valves in the reactor coolant hot leg sample line. Leak isolation could not be initially verified and is considered RCS pressure boundary leakage. Salem Unit 1 entered Technical Specification 3.4.6.2a, RCS operational leakage, for the existence of pressure boundary leakage. "This event is being reported under the requirements of 10 CFR 50.72(b)(2)(i) for 'The initiation of a plant shutdown required by Technical Specifications' and 10 CFR 50.72(b)(3)(ii)(A) or 'Any event of condition that results in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded.' "The unit was placed in mode 3 at 1554 [EST] on 02/28/2017. "This condition has no impact on public health and safety." Per Technical Specifications, the unit is proceeding to mode 5. The leak rate at the time of shutdown was 0.33 gpm. This event has no effect on Unit 2. The licensee has notified the NRC Resident Inspector. The licensee will be notifying the Lower Alloways Creek Township, the State of New Jersey and the State of Delaware. * * * RETRACTION FROM MATT MOG TO HOWIE CROUCH AT 1144 EDT ON 4/14/17 * * * "The purpose of this notification is to retract event report number 52581 made on 2/28/2017 at 1624 (EST). Previously, PSEG notified the NRC that Salem Unit 1 initiated a shutdown required by Technical Specifications (TS) for Reactor Coolant System (RCS) Pressure Boundary Leakage. "Subsequent to the initial report, PSEG has determined that the leak occurred in tubing downstream of the design specification break between Safety Related, Nuclear Class 1, Seismic Class1 and Non-Safety-Related, Nuclear Class 2, Seismic Class 2. Therefore, the observed leakage is not RCS pressure boundary leakage as defined in the Salem Unit 1 Technical Specifications and in the tubing design classification specification. "At the time of the event, during initial entry into the containment, the volume of steam present and the height of the break above the floor made it difficult to ascertain the location of the steam source with certainty. The initial judgment of RCS Pressure Boundary Leakage was conservative under these circumstances. The plant was taken offline to minimize radiation exposure when personnel operated the isolation valves. Following the shutdown, the leak was isolated. Based on an observed reduction in RCS leak rate and visual verification of leakage isolation, the TS Limiting Condition for Operation (LCO) was exited and the unit remained in Mode 3, Hot Standby, to affect repairs. The condition did not meet the Technical Specification Pressure Boundary Leakage definition of leakage through a non-isolable fault in a RCS component body, pipe wall or vessel wall. "The leakage did not impact the ability to shut down the unit and no TS limits were exceeded during this event. Therefore, the plant shutdown to investigate and correct leakage from flawed sample system tubing does not meet the reporting requirements of 10 CFR 50.72 and PSEG is retracting the notifications made under 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(3)(ii)(A). "The NRC Resident Inspector was notified of this retraction by the licensee." Notified R1DO (Jackson). | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2017-02-28
52580 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-02-24 | 2017-02-28 14:37 | 2017-02-28 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO HIGH DOSE The following information was supplied via email from the State of North Carolina: "On 2/27/2017 the North Carolina Radiation Protection Section (RPS) received the following notification from Duke University Medical Center, License number 0247-4. "A possible Medical Event occurred at Duke University Medical Center on February 24, 2017 involving Y-90 microspheres during a liver embolization procedure. Duke personnel reported to North Carolina Radiation Protection Section (RPS) on February 27, 2017 of the event meeting the reporting requirements for a Medical Event as dictated in NRC Licensing Guidance, Rev. 9 under: "Medical Event [ME] Reporting: The licensee shall commit to report any event, except for an event that results from intervention of a patient or human research subject, in which: the total dose or activity administered differs from the prescribed dose or activity, as documented in the written directive, by 20 percent or more, except when stasis or emergent patient conditions are documented and resulted in a total dose or activity administered that was less than that prescribed; "At this time, the details provided by Duke University Medical Center for this ME are as follows: Delivered dose was 94 percent higher than the prescribed dose in the Written Directive to the treatment site. The apparent cause appears to be an error in reading the prescribed radioactivity (in GBq) before converting to the administered activity (in mCi), indicating operator error that occurred in the radio pharmacy at Duke University Medical Center. "RPS has dispatched an investigator to perform a reactive inspection at Duke University Medical Center. This investigation is ongoing and RPS will have additional information to complete this report." The State on North Carolina does not know if the patient has been notified of the received dose being higher than the prescribed dose. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-03-08
52579 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2017-02-24 | 2017-02-27 16:27 | 2017-02-27 | UCI TERMINAL BOXES P/N 005650-01 DISCOLORATION AND CORROSION The following information is excerpted from an email submitted by the reporting organization: "In July of 2016, UCI [United Controls International] identified extensive discoloration and corrosion on P/N: 005650-01, terminal box enclosures, that were fabricated under UCI's Quality Assurance Program in April of 2015. The identified discoloration and corrosion was not present at the completion of fabrication and became evident when pulled from stock in July of 2016. It was determined that the fabrication process was changed during fabrication of the April of 2015 items to utilize a different vendor for fabrication activities. Evaluation of the fabrication process performed on the subject items identified that this new vendor utilized a polishing process that was not performed on previously fabricated items. Particles/crystals from the discolored areas of the affect items were analyzed by Fourier Transform Infra-Red (FTIR) method and it was identified that ammonium phosphate crystals had formed on the items. It is the determination of UCI that the affected items were cleaned/polished with unknown chemicals during the polishing process of fabrication that resulted in the formation of these crystals and degradation of the enclosure material overtime. The items manufactured utilizing this new process were supplied to Clyde Union Limited under purchase orders 4500109863/4 (Qty. 1) and 4500113688/4 (Qty. 1). Clyde Union Limited was notified of the subject issue on January 13, 2017 and UCI is awaiting concurrence from Clyde Union Limited that the affected items are to be returned for replacement items manufactured per the original manufacturing process. "If you have any questions or wish to discuss this matter or this report, please contact: Wesley Hackle Engineering Manager whickle@unitedcontrols.com 770-496-1406 x 165" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-02-27
52578 | 0 | BAYER CROP SCIENCES |  |  |  |  | 2017-02-27 14:05 | 2017-02-27 16:04 | 2017-02-27 | SOURCE HOLDER STUCK OPEN Licensee reported that they were in the process of removing a Kay-Ray Model # 7062B source holder from an installed position. The device serial number is #24093 with a Cs-137 10 mCi source. They believed the source holder to be closed during the removal operation. While in the process of removing the source holder from its installed location, they received unexpected radiation levels on their survey meter and laid the source holder on the room floor with the source pointing in the down direction. They then used some lead shielding to cover the source device and moved it to a storage location. The current radiation levels in the vicinity of the source holder are normal background. The licensee plans on reviewing the radiation dose information when personal dosimetry is processed at the end of the quarter (March 15, 2017). The licensee also plans on contacting Berthold Technologies for disposal of the device. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-03-07
52577 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-02-25 08:30 | 2017-02-26 13:00 | 2017-02-27 | AGREEMENT STATE REPORT - POTENTIAL CONTAMINATION EVENT The State of Texas provided information on a potential contamination event at the Halliburton Energy Services facility in Houston, TX. An employee was working on a well logging tool that contained a 1.3 microCurie Cs-137 source. While removing the Cs-137 sealed source from the tool, an employee noticed a small hole in the Cs-137 capsule. The employee stopped working on the tool, cleared the area, and restricted access to the room where the work was being performed. Contamination swipes were taken in the area and sent to a third party laboratory for analysis. No over exposures were indicated. The initial survey of the worker identified a small area of one of his boots that had some contamination. * * * RETRACTION FROM KAREN BLANCHARD TO DONG PARK AT 1030 EST ON 2/27/17 * * * The following event retraction was received from the State of Texas via email: "Initial information concerning this event was provided via telephone on 2/26/2017. However, after further evaluation of the information provided by the licensee, it has been determined that this event does not meet any reporting requirement." Texas Incident #: 9467 Notified the R4DO (Deese), NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-03-06
52576 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-02-24 22:39 | 2017-02-25 04:23 | 2017-02-25 | SECONDARY CONTAINMENT DIFFERENTAIL PRESSURE EXCEEDED TECHNICAL SPECIFICATIONS "At approximately 2239 [CST] on 2/24/17, the Main Control Room received numerous annunciators that indicated a loss of the 138 kV off-site feed to the Emergency Reserve Auxiliary Transformer (ERAT). As a result of the voltage transient, the Division 1 Fuel Building ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no running VF fans, secondary containment differential pressure rose to slightly greater than 0 inches water gauge which exceeded the Technical Specification requirement of greater than 0.25 inches vacuum water gauge. The Control Room entered EOP-8, Secondary Containment Control. This event is being reported as a Condition that Could Have Prevented Fulfillment of a Safety Function under 10CFR50.72(b)(3)(v)(C). Secondary Containment differential pressure was restored within Technical Specification requirements at 2242 [CST] by starting the Standby Gas Treatment HVAC (VG) system. "The NRC Resident [Inspector] has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-02-25
52575 | 0 | LACROSSE | 1 |  |  | [1] AC (ALLIS CHAMBERS) | 2017-02-24 12:45 | 2017-02-24 14:40 | 2017-02-24 | OFFSITE NOTIFICATION TO STATE OF WISCONSIN DUE TO INADVERTENT RELEASE OF CONTAMINATED WATER "The Wisconsin Department of Natural Resources (WDNR) was notified today at 1245 [CST] of an inadvertent release of radioactively contaminated water [as required by the licensee's site permit to report any release of contaminated water into the Mississippi River]. "At approximately 0715 on February 23, 2017, Solutions Management was notified by a Radiation Protection Technician (RPT) that the containment berm of the East (immediately north of Turbine Building) Baker Tank (20,000 gallon storage tank) was full and spilling out of the containment berm. The water that spilled out of the containment berm had pooled to the north of the tank and eventually began draining into the Radiological Controlled Area (RCA) storm sewer drain. "Upon discovery and initial investigation the RPT ascertained that a sump pump hose which was left in the tank overnight was siphoning into the containment berm. The RPT immediately removed the hose from the water in the Baker Tank to stop the water from siphoning. Once the water was secured actions were taken [to minimize the contamination]. "Approximately 400 gallons had been lost from the tank. The 400 gallons was siphoned from the tank through a garden hose attached to a sump pump which was sitting in the containment berm. Over the course of approximately 16 hours the water siphoning from the tank filled the containment berm which holds a little over 3,100 gallons and spilled on to an asphalt surface. The water then traveled approximately 30 feet over the asphalt surface to the storm sewer which contained inlet protection in accordance with the Storm Water Pollution Prevention Plan. After filtering through the inlet protection the water remained in the storm water drain until the volume was sufficient enough to reach the 10 inch discharge piping (approximately 12 inches). The water traveled approximately 100 feet to the next storm water drain where it remained until the volume was sufficient enough to reach the 10 inch discharge piping (approximately 8 inches). When the manhole was opened, the level of the water was just above the bottom of the 10 inch discharge piping and was flowing slowly. The water leaving the 10 inch discharge piping flowed to a 60 inch discharge pipe that discharges to the Mississippi River. "Water samples and smear surveys were analyzed, documented and reviewed by the Lacrosse Solutions (Solutions) Radiation Protection Manager (RPM) and NRC Region 3 Inspector Dr. Peter Lee, who was on site performing a routine inspection. Analytical results of the released water showed that it contained only Cs-137 in concentrations ranging from 1.1E-06 uCi/ml to 2.86 E-06 uCi/ml. The concentration levels exceed the 10CFR20 Table 2 limits for effluents (water) for Cs-137 which is 1 E-06 uCi/ml. The concentration levels exceed the 10CFR20 Table 2 limits for effluents(water) for Cs-137 which is 1 E-06 uCi/ml. Although the concentration levels exceed the 10CFR20 Table 2 limits for effluents (water) for Cs-137 they did not exceed the criteria for reportability which is 20 times the Table 2 effluent limit for Cs-137. The smear surveys of the storm sewer piping, manhole vaults taken during entries into the RCA yard drain & Administration Building drain manholes were all considerably less than CA posting criteria. The Standard Dose Calculations used for planned water releases were utilized for the water release assuming no dilution. Using the Standard Dose Calculations it was calculated that 1.05 E-02 mRem was the worst case for organs and 5.72E-03 mRem for total body dose. "Following the RPM's review, it was determined that the asphalt area of the RCA could be down posted as a CA and the storm drain vault to the north of the Administration Building could be unplugged to allow regular flow of storm water. "Solution's has issued a Conditions Report (CR) and initiated an investigation to prevent this occurrence from happening again. "Regulatory reportability limits for liquid effluent releases were not exceed as result of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-02-24
52574 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-02-16 13:08 | 2017-02-24 09:28 | 2017-02-24 | COLORADO AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was obtained from the State of Colorado via email: "The general license section of the Radioactive Materials Program [at the Colorado Department of Public Health and Environment] sent out annual notifications requesting response regarding tritium exit signs reported in use at locations given by the manufacturer. Upon an audit of the annual mailing for non-responders, Elkco Properties & Olson's Greenhouse were contacted. After a complete inspection of the greenhouse and several confirmations, only 3 tritium exit signs remain in the facility. It is unknown as to the disposition of the lost 3 exit signs as further information is unavailable due to time of reporting loss. Elkco has plans to remove the existing signs and replace them with non-tritium signs. They will inspect each building they lease and should any tritium exit signs be found, follow the regulations in the Colorado Rules and Regulations Pertaining to Radiation Control. "Event Description: Manufacturer; SRB Technologies, 3 exit signs are reported as lost, Model#; BX10WH, Serial number's; C12805, C12806, C12810; Isotope H-3 Tritium; Activity; 9.21 Ci, they were shipped from SRB Technologies on 10/23/2004. "Event is completed/closed." Colorado Event Report ID No.: CO17-0006. See similar EN#s 52494, 52538, and 52553 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-03-06
52573 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-02-23 19:22 | 2017-02-23 22:01 | 2017-02-23 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO RCS PRESSURE BOUNDARY LEAKAGE "On February 23, 2017, a containment visual inspection was performed to identify the source of elevated RCS [Reactor Coolant System] leakage. A leak was identified at the nozzle connection of the boron injection line to 2D RCS cold leg at 1922 [EST]. It was determined that the leak cannot be isolated and is considered RCS pressure boundary leakage. Unit 2 entered TS LCO 3.4.13, RCS Operational Leakage, Condition B, for the existence of pressure boundary leakage. "This event is reportable in accordance with 10CFR50.72(b)(2)(i) (4 hours) for 'initiation of plant shutdown required by Technical Specifications' and 10CFR50.72(b)(3)(ii)(A) (8 hours) for 'any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' "The unit will shutdown and repairs will be performed in Mode 5. "This condition has no impact on public health and safety. "The licensee has informed the NRC Resident Inspector." At the time of the event notification, Unit 2 was at 33 percent power. Unidentified RCS leakage is estimated at 0.28 gpm. Unit 2 is expected to be in Mode 3 by 0122 EST on 02/24/2017. Unit 1 is not affected by this event. | 0 | 33 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2017-02-23
52572 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2017-02-22 | 2017-02-23 14:44 | 2017-02-23 | AGREEMENT STATE REPORT - MISADMINISTRATION OF RADIOISOTOPE TO PATIENT The following information was received via email from the State of Oklahoma: "[State of Oklahoma] has been informed that MUSKOGEE REGIONAL MEDICAL CENTER, LLC dba EASTAR HEALTH SYSTEM (OK-13157-01) administered 10 mCi of Tc-99m to a patient without an order from an Authorized User. This was done on the basis of a phone call from a nurse on the ward who indicated the patient was to have a stress test. After the initial dose had been administered, the physician [patients attending physician] called the Nuclear Medicine department and informed them that no study had been ordered for this patient. The second dose was not administered. The highest dose resulting from the administration is 1.25 REM to the gallbladder and 340 mR whole body. This does not appear to be a medical event." The State of Oklahoma did not know if the patient has been informed of the misadministration. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2017-03-03
52571 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2017-02-23 10:40 | 2017-02-23 13:02 | 2017-02-23 | POTENTIAL TORNADO MISSILE VULNERABILITIES "In order to address the concerns outlined in RIS [Regulatory Information Summary] 2015-06 'TORNADO MISSILE PROTECTION', an evaluation of tornado missile vulnerabilities and their potential impact on Technical Specification (TS) plant equipment was conducted. This evaluation concluded that the following Structures, Systems, and Components (SSCs) are potentially vulnerable to tornado generated missiles: "The BVPS Unit 1 (BV-1) and BVPS Unit 2 (BV-2) Main Steam Safety Valve (MSSVs) discharge flow paths to atmosphere (reference TS 3.7.1) are potentially vulnerable to tornado generated missiles. A tornado could generate missiles capable of striking the exhaust piping of the MSSVs potentially crimping the piping and resulting in reduced flow capacity. In the worst case, all MSSV's could be rendered inoperable. This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B), and 10 CFR 50.72(b)(3)(v)(A). "The BV-1 and BV-2 Atmospheric Steam Dumps (ADVs) discharge flow paths to atmosphere (reference TS 3.7.4) are potentially vulnerable to tornado generated missiles. A tornado could generate missiles capable of striking the exhaust piping of the ADVs potentially crimping the piping and resulting in reduced flow capacity. In the worst case, all ADVs could be rendered inoperable. This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B), and 10 CFR 50.72(b)(3)(v)(A). "The BV-2 Auxiliary Building tornado missile shield door (A-35-5A), credited for tornado missile protection of the Primary Component Cooling Water (PCCW) system, was found to not be fully closed and latched. A tornado could generate missiles capable of striking the PCCW system with the missile door open rendering both trains of the PCCW system inoperable. This door is now maintained closed and latched except when opened under administrative controls. This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B). "The BV-2 Spent Fuel Building tornado missile shield door (F-66-3), credited for tornado missile protection of the irradiated fuel assemblies in the Spent Fuel Pool including the Cask Pit, was found to not be fully closed and latched. This door is now maintained closed and latched except when opened under administrative controls. This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B). "The potential tornado missile vulnerabilities for the MSSVs and ADVs (discussed above) are being addressed in accordance with EGM-15-002 Rev 1 and DSS-ISG-2016-01 (NRC enforcement discretion and interim guidance documents). Immediate compensatory measures were taken to reduce the likelihood and mitigate the potential consequences of an onsite tornado generated missiles. "The NRC Resident inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2017-02-23
52570 | 0 | DBI, INC. |  |  |  |  | 2017-02-21 13:23 | 2017-02-22 10:59 | 2017-02-22 | RADIOGRAPHY SOURCE CABLE DISCONNECTED FROM SOURCE "On February 21, 2017, DBI Inc. had an industrial radiography source disconnect incident occur while at a pipeline customer's field site in Rutledge, MO (approx. 4hrs. from Overland Park, KS office). At approximately 1323 CST during the crew's first source retraction it was determined that the source had become disconnected from the drive cable. The crew immediately recognized the situation through the use of their dosimetry equipment and established the emergency 2 mR/hr boundaries. "The Corporate Radiation Safety Officer (CRSO) was immediately notified of the issue. The CRSO informed the crew to maintain surveillance of the restricted area barricades and to wait until he arrived before any further actions were taken. The CRSO arrived at the job site at approximately 1705 CST to retrieve the source. The source was secured back into the exposure device by 1730 CST. The CRSO received less than 1 mR during the retrieval procedure. "Listed below are the manufacturer and model number of equipment involved in the incident: - QSA Global 880 Delta Exposure Device - QSA Global lr-192 Source (45 Curies) Model A424-9 - QSA Global 35 foot Extreme Weather Control Cables - QSA Global 7 foot Extreme Weather Source Tube with a 4hvl Collimator "The level II radiographer involved holds a current Iowa Industrial Radiographer Trainer Card and the assistant is a trainee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | KS | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-02-22
52569 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-02-20 | 2017-02-21 16:44 | 2017-02-21 | AGREEMENT STATE REPORT - LOST THEN RECOVERED RADIOGRAPHY CAMERA The following information was received via E-mail: "On February 20, 2017, the licensee's radiation safety officer (RSO) notified the Agency [Texas Department of State Health Services] that one of its New Mexico radiography crews was performing radiographic operations on a pipeline that was being built in Reeves County, Texas. The crew finished work at one section and put the Spec 150 radiography device on the tailgate of their truck while they drove down the pipeline right-of-way to their next location. Unbeknownst to the radiographers, the device fell off the tailgate. The licensee and crew learned of the loss after a contractor found the device, picked it up, put it in the back of his pickup, and took it to another of the licensee's radiography crews who was also working on the pipeline. That crew called their site RSO who then called the crew who lost the camera. "The camera was surveyed and readings were as expected. The source was in the fully shielded position and the safety plug was in the front of the camera. Based on calculations by the RSO on February 21, 2017, the contractor's exposure does not appear to have exceeded any regulatory limit. "An investigation into this event is ongoing and further information will be provided as it is obtained in accordance with SA-300. "The device was a Spec model 150, serial No.: 1778 containing a 60 Curie (current activity) Iridium-192 source, serial No.: YA0302." Texas Incident No.: I-9466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-03-01
52568 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-02-20 12:40 | 2017-02-20 17:24 | 2017-02-22 | UNANALYZED CONDITION DUE TO POTENTIAL FAILURE OF CONTROL ROOM AND CONTROL BUILDING AIR HANDLING UNITS "During the investigation associated with Event Notification 52566 that was reported on 2/18/17, it has been determined that an unanalyzed condition (new potential single failure concerns) exists. This condition exists only during periods of manually alternating divisions of Control Building Chilled Water systems; in that potential failures of Control Room Air Handling Units (HVC-ACU1A or B) or Control Building Air Handling Units (HVC-ACU2A or B) could fail in a manner that challenges the operability of the alternate division. "As reported in Event Notification 52566, the impact of this event was a loss of safety function cooling to both Division 1 and 2 AC/DC power distribution systems and Divisions 1 and 2 Control Room Fresh Air systems. "Contingency actions are in development to address the impact of the potential failure mode. The plant remains in a planned refueling outage, Mode 5 with water level greater than 23' above the vessel flange. Shutdown cooling remains in service and is not affected by this issue. Investigation is ongoing. "The NRC Resident Inspector has been briefed on this issue." * * * UPDATE FROM ROB MELTON TO DONALD NORWOOD AT 2129 EST ON 2/20/2017 * * * The licensee updated information in the first paragraph of the original above with the following: "During the investigation associated with Event Notification 52566 that was reported on 2/18/17, it has been determined that an unanalyzed condition (new potential single failure concerns) exists. During periods of alternating divisions of Control Building Chilled Water systems, the potential exists for failures of Control Room Air Handling Units (HVC-ACU1A or B) or Control Building Air Handling Units (HVC-ACU2A or B) that could challenge the operability of the alternate division." The licensee notified the NRC Resident Inspector of this update. Notified R4DO (Gepford) * * * UPDATE FROM STEVEN CARTER TO MARK ABRAMOVITZ AT 1513 EDT ON 2/22/17 * * * "After further investigation it has been determined that an unanalyzed condition (new single failure concerns) exists with the dampers associated with the Control Room Fresh Air system. The potential exists for damper failures for HVC-FN1A Control Room Booster Fan 1A motor and HVC-FN1B Control Room Booster Fan 1B motor that could challenge the operability of the alternate division. "Contingency actions are in development to address the impact of the potential failure mode. The plant remains in a planned refueling outage, Mode 5, with water level greater than 23 feet above the vessel flange. Shutdown cooling remains in service and is not affected by this issue. Investigation is ongoing. "The NRC Resident Inspector has been briefed on this issue." Notified R4DO (Pick). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-02-20
52567 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-02-19 23:23 | 2017-02-20 01:14 | 2017-02-20 | CONTAINMENT PENETRATION EXCEEDED ALLOWABLE LEAKAGE "On 2/19/2017 at 2323 EST, during LLRT [local leak rate test] testing per 42SV-TET-001-2, 2T48F320 exceeded the maximum allowable leakage limit. The companion isolation valve in the same line (2T48F319) had previously failed LLRT. The failure of the 2T48F320 represents a failure of the 2T23X26 penetration to maintain primary containment integrity. "This event is reportable per 10CFR50.72(b)(3)(ii)(A) since the failure of the 2T23X26 penetration caused primary containment leakage to exceed La [allowable leakage] and thus represents a degraded principle safety barrier. "CR [condition report] 10333178. "NRC Resident Inspector has been notified." 2T48F319 and 2T48F320 are 18 inch dampers. This event places the licensee in a Technical Specification limit that requires the dampers to be repaired and pass LLRT prior to the plant entering Mode 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-02-20
52566 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-02-18 15:37 | 2017-02-19 00:21 | 2017-02-19 | LOSS OF CONTROL BUILDING CHILLED WATER "At 1537 CST on February 18th, 2017, while the plant was in MODE 5 for a scheduled refueling outage, the main control room experienced a loss of Control Building chilled water and the associated ventilation systems while attempting to alternate divisions for testing. An equipment malfunction in a breaker supplying a Main Control Room air handling unit caused a loss of both divisions of Control Room and Control Building chilled water systems and associated ventilation systems until 1737 CST. During the period between 1537 and 1737, neither division of Control Building chilled water was able to perform the support function for cooling Division 1 and 2 AC and DC power distribution systems or the support function for the Division 1 and 2 Control Room Fresh Air systems. "Shutdown Cooling remained in service throughout this event. There were no apparent effects on any plant equipment from the loss of chill water and ventilation. "The Division 1 Control Building chill water and ventilation system was returned to service at 1737 on February 18, 2017. "Actions were initiated to terminate the OPDRV [operations with potential to drain the reactor vessel] that was in progress at the time of the event by installing the reactor recirculation pump seal. As a conservative measure, actions were initiated to set containment and containment was set at 2145. "Troubleshooting and analysis is ongoing to confirm and correct the problem which caused the loss of the Control Building chill water and ventilation system. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v)(B). "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2017-02-19
52565 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-02-17 17:30 | 2017-02-18 13:04 | 2017-02-23 | AGREEMENT STATE REPORT - MISSING TRITIUM SOURCE AND DEPLETED URANIUM DISKS "The Wisconsin Department of Health was notified by phone at 5:30 PM on February 17, 2017 that the licensee has lost components of a radio-synthesis device containing approximately 70 Ci of Hydrogen-3 and 20 grams of Depleted Uranium in the form of uranium tritide (UT3) discs. More than three years ago, the licensee had packaged the material and placed it into a metal drum while a disposal option was to be determined. The drum was stored in a restricted area near the licensee's incineration facility. A week ago the licensee was preparing to repackage the material in order to transfer it for final disposal. The drum was found to be empty when opened. The licensee has search all facilities used for radioactive material storage and reviewed disposal records; but has been unable to account for the material. At this time the licensee suspects that the material was incorrectly disposed of in either a non-hazardous waste stream or incinerated within the last three years. The department has started an investigation to determine the most likely disposal pathway and the exposure impact. Site visits and updates will [be] perform[ed]. "Event Report ID No.: WI170003" * * * UPDATE PROVIDED BY KYLE WALTON TO JEFF ROTTON VIA EMAIL AT 1331 EST ON 02/23/2017 * * * "The licensee has performed a preliminary investigation and concluded that it is unlikely the loss of material was malicious. The licensee has already begun an impact assessment for the potential incineration of material, and Wisconsin DHS has coordinated with the licensee on what actions need to take place going forward. Inspectors will be performing an on-site inspection to further gather information." Notified R3DO (Jeffers) and NMSS Events Notification group via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-02-27
52564 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2017-02-17 23:53 | 2017-02-18 02:58 | 2017-04-14 | AUTOMATIC REACTOR SCRAM RESULTING FROM FEEDWATER REGULATING VALVE FAILURE "This notification is being provided in accordance with 10CFR 50.72(b)(2)(iv)(B). "On February 17, 2017 at 2353 CST, Unit 1 Reactor Automatic Scram signal was received due to Turbine Control Valves Fast Closure. The turbine trip was due to receipt of Level 8 Trip due to a failure of the Feedwater Regulating Valve to Full open. Plant is in a stable condition with reactor pressure being maintained by the Turbine Bypass valves. Reactor water level is being controlled with Feedwater thru the Low Flow Feedwater Regulating Valve. Further investigation into the cause of the event is in progress." All control rods fully inserted, and decay heat is being removed via steam to the main condenser using bypass valves. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM BROCK POLLMANN TO HOWIE CROUCH AT 1721 EDT ON 4/14/17 * * * "Upon further review of the event data, it was determined that the Nuclear Station Operator (NSO) had initiated a manual scram, which was followed by a Turbine Control Valve (TCV) fast closure automatic scram when the turbine tripped." The licensee has notified the NRC Resident Inspector. Notified R3DO (Jeffers). | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-02-18
52563 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-02-17 14:14 | 2017-02-17 17:46 | 2017-02-17 | SECONDARY CONTAINMENT INOPERABLE "On 2/17/2017 at 1414 EST, secondary containment was declared inoperable due to the discovery of an 18-inch open pipe penetration in the secondary containment boundary. During walkdown activities, it was discovered that a blind flange installed to support removal of a Unit 2 secondary containment isolation valve had been installed on the wrong flange to provide isolation for secondary containment. At 1503 EST, the blind flange was moved to the correct side of the flange and secondary containment was declared operable. "This event is reportable per 10 CFR 50.72(b)(3)(v)(C) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material. In conjunction with operation of the Standby Gas Treatment (SGT) subsystems, secondary containment is designed to reduce the activity level of the fission products prior to release to the environment and to isolate and contain fission products that are released during certain operations. Therefore, the lack of a qualified isolation device to limit the release of radioactive material constitutes a loss of safety function due to a loss of secondary containment integrity. "CR 10332592 "The NRC Resident has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-02-17
52562 | 0 | CINER WYOMING LLC |  |  |  |  | 2017-02-16 15:00 | 2017-02-17 15:09 | 2017-02-17 | SHUTTERS STUCK OPEN ON TWO FIXED BERTHOLD GAUGES "Company Name: Ciner Wyoming LLC Address: 254 County Road 4-6, Green River, WY 82935 RSO Name: Hilary Huckfeldt License #: 49-11578-01 Issue: Shutters on two fixed gauges did not operate during the semi-annual inventory shutter operation check. Date of Discovery: February 16, 2017 at 3:00 PM MST "Gauge 1 Manufacturer: Berthold Serial #: FN-782-14-11-97 Activity: 20 milliCuries Isotope: Cs-137 Model: LB7440D Issue: Shutter stuck in open position. Currently in use on pipe. "Gauge 2 Manufacturer: Berthold Serial #: FR411-22-01-98 Activity: 50 milliCuries Isotope: Cs-137 Model: LB7440D Issue: Shutter locked in open position. Currently in use on pipe. "Corrective Action: Contacted manufacturer to repair/replace the failed components. Working with manufacturer to get this corrected as soon as possible." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-02-27
52561 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2017-02-13 | 2017-02-17 14:40 | 2017-02-17 | AGREEMENT STATE REPORT - LEAKING NICKEL-63 SOURCES The following information was provided from the State of NY via email: "License No.: G5498 "Licensee: Global Foundries "Event date and time: 2/13/2017 "Event location: 400 Stone Break Road Extension, Malta, NY 12020 "Event type: Leaking Nickel-63 sources "Event description: Global Foundries reported that leak testing of three (3) Eckert & Ziegler Isotope Products Inc., model NER-004R, 10-millicurie Nickel-63 sources indicated removable contamination in excess of 0.005 microCuries. Test results of serial no. 89051 vacuum measured 0.406 microCuries contamination, serial no. 87622 vacuum measured 3.12 microCuries contamination, and serial no.88706 vacuum measured 4.32 microCuries contamination. Initial testing was performed on February 8, 2017, by Jay R. Dockendorff of RSA laboratories, Connecticut License No. 06-300007-01. The report to the NYS Department of Health stated that the sources were isolated and the licensee has contacted the manufacturer for return instructions. Retesting has been arranged with the samples collected February 15, 2017. They were requested to provide the retesting results to the NYS DOH along with the receipt when the sources are returned to the vendor/manufacturer. "Event Report ID No.: NYDOH - NY-17-03" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-02-27
52560 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-02-11 | 2017-02-17 12:20 | 2017-03-03 | AGREEMENT STATE REPORT - LEAKING URANIUM-235 SOURCE WITH CONTAMINATION IN PUBLIC AREAS The following report was received from the State of North Carolina via email: "On 2/15/2017 Duke University reported to the NC Radiation Protection Section (NCRPS) a leaking source: U-235 3 microCuries 1.5 grams S/N: D16156 "This source was loaned to Duke University through Los Alamos National Laboratory (LANL) for experimentation, research, education and calibration purposes. NCRPS personnel were dispatched to conduct a reactive inspection on 2/15/2017. Through interviews with Duke personnel it was determined that during an experiment the source integrity was compromised and assumed to be leaking. No direct wipe of the source was taken. The source was packaged to prevent contamination and then isolated for pending disposal. It was also determined that the actual breach of the source occurred on 2/11/2017. Given the lapse of when the source was compromised and when Duke Radiation Safety Office was notified it is apparent that established Duke SOPs were not followed. Duke personnel and researchers believed to have been exposed to the leaking source had lung scans performed on 2/15/2017, in which all came back indicating no exposure. Duke personnel accompanied by NCRPS staff began testing for contamination of the affected area and surrounding areas due to the compromised source. "On 2/16/2017, Duke personnel again notified NCRPS that contamination was discovered outside of the anticipated areas where contamination was suspected. On 2/16/2017, NCRPS personnel continued the reactive inspection. The scope to the surveys was expanded to now cover high traffic areas, vehicles of the individuals involved, bathrooms and other areas where potential contamination from the leaking source may have been in. Testing of these areas for contamination is ongoing at the time of this report. For the identified personnel directly associated with the leaking source, surveys and wipes were expanded to their residences. One residence, that of a Duke Physicist Researcher, presented contamination on a toilet seat which was decontaminated and re-surveyed and re-wiped and the results confirmed the decontamination. Other areas of the residence were surveyed and at the time of this report all results indicate no further contamination. Additional researchers identified on 2/16/17 to have been involved with the leaking source, were also scheduled to have lung scans on 2/17/2017. Additionally, Duke University decided to compound testing to include urinalysis and possibly bloodwork at the advice of REACTS. At this time, it is believed that contamination due to the leaking source has been contained and no members of the public have received radiation exposures. To date, the highest reading in proximity to the source on Duke University's property was 7000 CPM and 4280 DPM. "On 2/17/2017, NCRPS in conjunction with Duke personnel reconvened to continue to complete the expanded surveys and wipes of all possible suspected areas and to conduct additional interviews with Duke personnel to rule out any chances of additional affected persons. Currently, this is an ongoing investigation and this event will be updated as additional details are received." North Carolina Event Report 2/17/2017. * * * UPDATE FROM TRAVIS CARTOSKI TO HOWIE CROUCH VIA EMAIL 1436 EST ON 3/3/17 * * * "The state of North Carolina submitted their final report for the Duke incident via email: "Radiation Protection Section - Duke Incident Report March 3, 2017 "Friday 2/10/2017: U-235 Source was removed by RES [researcher] D from storage located at Triangle Universities Nuclear Laboratory (TUNL) and taken to the Upstream Target Room (UTR) at the High Intensity Gamma-ray Source (HIGS) facility. "Saturday 2/11/2017: RES A utilizing the U-235 sealed source for research compromised the integrity of the source by bending the corners of the source to fit in a target holder resulting in the contamination of a researcher's hand (RES A) and work surface. The sealed source of a water insoluble form of U-235 with an activity of 3 micro curies containing a total of 1.5 grams of powdered U-235 with the majority still inside. This took place in the UTR located in HIGS and at no time was the source exposed to the accelerator beam. RES A informed RES D of the compromised source where it was confiscated by RES D. Both the RES A & RES D decontaminated their hands and work surfaces suspected to be contaminated. "RES A expressed their concern over the leaking source to RES D, this concern was dismissed by RES D who did not report the status of the source or the possibility of contamination as dictated in Duke University established procedures. "No contamination surveys were reported as performed for the compromised source or work surface areas at the location of UTR in HIGS. The compromised source was contained (bagged), sealed and moved back to storage located at TUNL by RES D following transport to Physics where an attempt was made to repair the source also by RES D. Surveys at Physics on the contained source indicated no contamination by RES D after resealing the source. "At no time were gloves or any Personal Protective Equipment (PPE) reported to be utilized by either RES A or RES D before and after the source was compromised. "Researchers and Duke personnel failed to follow established procedures which dictate that any damage to a radioactive source or suspected contamination be immediately reported to Duke Radiation Safety, RSO [Radiation Safety Officer] or RSM [Radiation Safety Manager] 1 or RSM 2. "Monday 2/13/2017: RES D notified RSM 1 of the possibility of leaking compromised source and requested the source be detected for possible leakage. Again, the possible incident was not immediately reported. "Tuesday 2/14/2017: RSO was notified by RSM 2 (who overheard the discussion between RES D & RSM 1 on 2/13/2017) about the possible incident that occurred on Saturday 2/11/2017. This notification should have come from any of the researchers involved (RES A, B, C & D or RSM 1). "Wednesday 2/15/2017: Radiation Protection Section (RPS) was called by RSO Wednesday morning and informed of a possible incident at Duke University. SC [North Carolina Radiation Protection Section Chief] and HP [North Carolina Radiation Protection Section Health Physicist] 1 were dispatched to conduct a reactive inspection. RPS led a fact finding discussion with Duke personnel (Res D, RSO, RSM 1, RSM 2, LW [Laboratory Worker] 2 & LW 3) and international researchers (RES A, RES B & RES C) to establish the chain of events from 2/10/2017 to present. "Following these discussions, RPS determined: 1. The investigation will remain open pending a follow up report from Duke University regarding the compromised source and; 2. That any contamination had been contained at UTR in HIGS by Duke personnel the verification of which; to be included in the follow up report. "Duke Environmental Safety Office then began surveys of the affected areas of UTR at HIGS due to the compromised source and also to verify no further contamination. RES A, RES D & RSM1 were identified as being in contact with the source and were evaluated for contamination exposures by lung scans at TE [Technical Experts] 1. Results indicated no inhalation occurred. Because of the insoluble nature of the isotope, it was advised by TE 1 that no further bioassays (urine or fecal) were necessary. "SC notified the Division of Public Health (DPH) of the Duke University incident. Roles and collaboration efforts were discussed during this time. The incident was also discussed with Division of Emergency Management (DEM). "Thursday 2/16/2017: RPS was notified at Thursday morning that Duke personnel were discovering contamination found outside of UTR at HIGS. RPS (SC, HP1, HP 2, HP 3 & HP 4) was dispatched again to Duke. "Additional areas at Duke were found to be contaminated at Free-Electron Laser Laboratory (FELL). RPS requested that Duke personnel immediately expand surveys for possible contamination well beyond original surveyed areas to include: bathrooms, stairwells, hallways and other high traffic areas at FELL. This was necessary to establish a high confidence that contamination was contained to Duke property/facilities. HP 1, HP 2, HP 3 & HP 4 observed all surveys conducted by Duke for his incident investigation. "It was during these observations that many common radiation safety practices were not adhered to including: a. Several chances for cross contamination of the samples could take place due to the technique employed (crossing of one hand for samples taken and the other hand for sample collections), witnessed by HP 1. b. While licensee personnel were taking surveys of personal items and surveys of hands and shoes, it was observed that the detector surface was held at an angle which could allow contaminant particles to contaminate the survey window of the detector, potentially compromising the detector to make accurate survey determinations, witnessed by HP 1 & HP 2. c. Through observations, it was discovered that researchers consumed beverages in a radiation use area which lead RPS to the possibility that ingestion was now a possible exposure pathway, witnessed by HP 2. "An additional 2 researchers (RES B & C) and a laboratory worker (LW 1) were identified as possibly having contact with the source on the 2/11/2017 (total of 6 people). RES B & C were also scheduled for lung scans on Friday 2/17/2017 at TE 1. "All individuals that may have come into contact with the source (RES A, RES B, RES C, RES D, & RSM 1) were interviewed to map their routes from Saturday 2/11/2017 to present, with the exception of LW 1 who was not available for interview due to being unreachable via phone, email or page. LW 1 was finally contacted on Friday 2/17/2017. "Based on those interviews, high risk areas were surveyed utilizing an alpha detector to include: initial laboratory areas, immediately surrounding areas, personal items (cell phones, wallets & shoes of RES A, B, C, D & RSM 1) and the vehicle of 1 RES D were completed and indicated no contamination. Duke personnel performed wipe surveys of these items and at the time indicated no contamination. "RPS requested that Duke extend surveys to include the residences of those identified to have come into contact with the source to include: hotel rooms of 3 researchers (RES A, B, & C) who are visiting international researchers, and the residences of RES D & RSM 1 (LW 1 still unavailable at this time). All surveys indicated no contamination with the exception of the residence of RES D. That contamination was found on a toilet seat of the residence, remediated by Duke personnel and resurveyed and indicated no contamination. All other areas of RES D residence surveyed indicated no further contamination. "Public Health Preparedness and Response (PHP&R) supported RPS on site for the investigation. Occupational and Environmental Epidemiology Branch (OEEB) was consulted for additional recommendations for bioassays and Duke personnel was made aware. Durham County Health Director and DPH leadership were informed and through conference call, determined a plan of action for public health. Conference call with Duke VP of Communications, Department of Health and Human Services (DHHS) Communications Office, RPS and PHP&R was held to draft public and employee messaging. United States Nuclear Regulatory Commission (USNRC) was consulted by RPS on the details of this incident to this point. "Friday 2/17/2017: RPS continued its investigation with Duke Friday morning. "Lung scans for RES B & C were conducted at the location of TE 1 and indicated negative results. LW 1 was interviewed and was eliminated from the list of possible contaminated personnel, as they did not have any contact with the source from when the incident took place (final total of 5 potentially exposed people). "Surveys were expanded to areas known to be frequented by the researcher (RES D) whose residence was found to be contaminated on Thursday 2/16/2017. A keyboard in the researcher's office was found to be contaminated, contained by Duke personnel and removed for isolation. All other areas frequented by this researcher were surveyed and indicated no further contamination. "An additional 10 personnel (ancillary, housekeeping, students, faculty, engineers) were identified as having frequented the affected areas involved with this incident. These individuals were interviewed and were found to not have had contact with any of the contaminated areas or any involvement with the compromised source. "At this time, RPS generated a report to the USNRC under the assumption that a 24-hour report was to be required. This was necessary in assuming a reporting requirement for unplanned contamination and assuming a worst case scenario as the investigation was still ongoing. Additional consultation was provided to RPS from TE 3 & TE 4 with regards to the compromised source to add perspective, that, should one individual were to consume the entire U-235 source, that person would receive 2 years of natural background radiation upon ingestion. Additionally, given that the source contained an activity of 3 microCuries, it would not have exceeded the threshold for Allowable Limits for Intake (ALI). "Training for those involved with this incident was also reviewed. During this review, it was confirmed that all individuals involved in this incident received Radiation Safety Training. This training specifically indicates that any damage to radioactive sources, suspected contamination and unexpected radiation exposures be reported immediately. The fact that this was not reported on 2/11/2017 appears to be in violation of Duke University Procedures. "Other Procedures were reviewed with regards to the compromised source. Specifically, Duke's own customized procedures tailored for this source, indicated that the source was to be tested for leakage every six months. Duke could not provide documentation that these leak tests took place and freely admitted that they were not conducting these tests for this source. "As surveys were continued to be expanded it was discovered that equipment used to reseal the compromised source on 2/11/2017 was found to be contaminated at the location in Physics. This equipment was remediated and removed. Additional surveys expanded out of Physics (door leading to Physics & hallways leading to Physics room) were conducted to confirm containment of any contamination and the area cordoned off pending results. Additional surveys and observations made where the source was stored at TUNL and no further contamination was detected at this location. "Through interviews by HP 1 & HP 2 with Duke personnel conducting the wipe surveys for areas suspected to contain contamination, it was discovered that techniques utilized were suspected as inadequate (samples exposed to ESD [electrostatic discharge], improper lighting, temperature control) to provide reliable results and further put into question the capabilities of the detector equipment via Liquid Scintillation Counter (LSC) to provide reliable results. RPS requested that Duke personnel utilize another reliable LSC and re-run all samples up to this point for this incident and any future samples taken in this investigation. The results of which are pending. "Duke personnel decided to conduct Whole Body [WB] scans for RES A, B & C to compound the Lung Scans previously performed for these individuals. The results for the WB scans were negative. This was necessary as these individuals were scheduled to depart to their home countries on Saturday 2/17/2017 and this was the most reliable additional testing that could be conducted in the time available. Urine samples were also taken for bioassays from RES A, B & C. RSO has reached out to the Japanese Atomic Energy Agency Radiation Safety Officer to inform him of events and discussed testing and results of the researchers from Japan. Additionally, Duke personnel committed to conducting 24-hour urine bioassays and possible blood analysis for Duke personnel involved in this incident. The results of which are pending. The decisions to conduct further tests were made in consultation with TE 1 & TE 2. "An exit meeting was conducted by Radiation Protection Program with Duke University personnel in which preliminary items of Non-Compliance were discussed. A corrective action plan was presented which was acceptable to Radiation Protection Program as next steps: "1. Shut down the High Intensity Gamma Source (HIGS) operations within the Free Electron Laser Laboratory (FELL) until March 27, 2017. During this time DU [Duke University] will be modifying procedures and working toward needed improvements. On 2-18-17 this commitment had been upgraded by the new Director of FELL and Triangle Universities Nuclear Laboratories (TUNL), to an indefinite suspension of operations in HIGS using radioactive targets. HIGS is where the incident occurred using radioactive targets. 2. [A Duke Radiation Safety Program (DRSP) Health Physicist will temporarily manage the laboratory] until a permanent replacement may be found. DRSP will maintain a larger footprint and role in operations within the facility while improvements are being made. 3. DRSP is considering hiring a consultant to help with procedural improvements and restore safety culture beyond implementing their own resources. 4. Duke University has committed to begin leak testing all sealed sources prioritizing custom radioactive sources. 5. Duke University leadership has committed to providing DRSP with funding and resources needed to upgrade radiological analysis equipment and facilities. 6. DRSP has suspended online training practices and have committed to face-to-face training with all new researchers emphasizing safety practices and procedures. "NOTE: This report was submitted March 3, 2017. RPS is continuing its investigation until all deficiencies identified in this report have been corrected to the satisfaction of RPS that Duke University is in compliance." Notified R1DO (DeFrancisco), NMSS EO (Collins), and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-02-27
52559 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-02-16 13:00 | 2017-02-16 21:43 | 2017-02-22 | AGREEMENT STATE REPORT - CPN INSTROTEK NOTIFIED CALIFORNIA OF MISSING CPN NUCLEAR GAUGE LOCATION The following information was received from the State of CA via email: "[The] President of CPN InstroTek in North Carolina called Thomas G. Miko of Los Angeles County Radiation Management, the LEA for Radiologic Health Branch [RHB], on February 16, 2017, from his office in North Carolina. [The CPN President] received a phone call from an anonymous caller in California who found a nuclear gauge from CPN InstroTek. The anonymous caller told [the CPN President] that the gauge is in a shed on a ranch in Southern California. [The CPN President] provided the anonymous caller's cell phone number. Thomas G. Miko spoke with the anonymous caller at 4:30 p.m. on February 16, 2017. The anonymous caller stated that he is in Palm Springs, and that the gauge is in a storage shed of items removed from a pawn shop in Temecula, California, after it went out of business. He said that this shed is in Desert Hot Springs, California, outside of Los Angeles County's jurisdiction. "Arrangements were made with the anonymous caller for him to drop off the gauge in its original case at the Riverside County Fire Station, where he would contact [a designated] Firefighter. "[The CPN President] requested that Radiologic Health Branch provide him with the serial number of the gauge for his own reference, once Radiologic Health Branch employees take possession of the gauge from Riverside County Fire Department. "Arrangements were made for [a] Radiologic Health Branch employee to drive from the Brea, Orange County, California office to take possession of the device from Riverside County Fire Department on Friday, February 17, 2017. "RHB Brea will follow up to see if they can match the gauge's serial number with that of any previously reported lost or stolen gauges." CA 5010 Number: 021617 * * * UPDATE AT 1229 EST ON 2/17/17 VIA EMAIL * * * The missing gauge was not in the case. Law Enforcement is conducting an investigation. Notified R4DO (Gepford), NMSS (McIntosh) and ILTAB (Pearson). * * * RETRACTION AT 1603 EST ON 2/17/17 FROM THOMAS MIKO TO S. SANDIN * * * The State of California is retracting this report since no gauge was identified or recovered. Notified R4DO (Gepford), NMSS (McIntosh) and ILTAB (Pearson). * * * UPDATE AT 0116 EST ON 2/22/17 VIA EMAIL * * * The missing radiological source was returned tonight (2/21/17) and is currently at a fire station in Riverside County. The gauge will remain at the station overnight and will be picked up by California Department of Public Health, Radiologic Health Branch tomorrow (2/22/17). Notified R4DO (Pick), ILTAB (Whitney) and NMSS (McIntosh). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-02-21
52558 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-02-16 13:20 | 2017-02-16 17:28 | 2017-02-16 | UNEXPECTED AUTOSTART OF AN EMERGENCY DIESEL GENERATOR "On February 16, 2017 at 1320 EST, the 2A Emergency Diesel Generator (EDG) started in response to a valid actuation signal due to the momentary loss of the 2C Startup Transformer (SAT). While performing maintenance activities on the 2D SAT, the alternate supply breaker tripped and reclosed, allowing the 4160 2E Emergency Bus to be momentarily de-energized. When the 4160 2E Emergency Bus de-energized, the 2A EDG received a valid autostart signal due to emergency bus low voltage. Although, the 2A EDG did autostart, it did not tie to the 4160 2E Emergency Bus as the 4160 2E Emergency Bus was re-energized from the 2C SAT. "This event is reportable per 10 CFR 50.72(b)(3)(iv)(A) since the autostart of the 2A EDG was not part of a pre-planned sequence and the event resulted in the valid actuation of an emergency ac electrical power system. "CR 10332134 "The NRC Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-02-16
52557 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-02-16 10:52 | 2017-02-16 15:57 | 2017-02-16 | HPCI SYSTEM INOPERABLE DUE TO BLOWN FUSE "On February 16, 2017 at 1052 CST, Unit 2 received a High Pressure Coolant Injection (HPCI) System 120V Power Failure alarm. Troubleshooting identified a cleared fuse for the HPCI System Flow Controller, 2-FIC-73-33, which would have prevented automatic or manual HPCI System initiation and rendered the HPCI System inoperable. At 1145 CST, the cleared fuse was replaced and the HPCI system was declared available. The HPCI System remains inoperable for additional troubleshooting. "This constitutes an unplanned HPCI System inoperability and requires an 8 hour ENS notification in accordance with 10 CFR 50.72(b)(3)(v)(D), due to the failure of a single train system affecting accident mitigation and a 60 day written report in accordance with 10 CFR 50.73(a)(2)(v)(D). "The Senior NRC Resident Inspector has been notified." | 0 | 77 | 0 | 0 | 77 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-02-16
52556 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2017-02-16 08:35 | 2017-02-16 13:54 | 2017-02-16 | SECONDARY CONTAINMENT INOPERABLE DUE TO INTERLOCK FAILURE "This report is being made in accordance with 10 CFR 50.72(b)(3)(v)(C), for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. An employee entered a secondary containment airlock and identified that both doors of the airlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the airlock and notified the Main Control Room Supervisor. Both doors in the airlock were open for approximately 5 seconds. "With both doors open, Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.2 was not met. This rendered secondary containment inoperable in accordance with TS 3.6.4.1. Reactor Building differential pressure, as observed in the Main Control Room, has remained more negative than -0.25 inches of vacuum water gauge at all times. Initial investigation determined that the interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the interlock." The licensee informed the NRC Resident Inspector. | 5 | 0 | 0 | 5 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Startup | Defueled |  | Startup | Defueled |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-02-16
52555 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-02-15 15:15 | 2017-02-16 13:03 | 2017-02-16 | FAILURE OF SECURITY DATABASE TO INCLUDE ALL PERSONNEL IN THE FFD POOL FOR RANDOM TESTING "On February 15, 2017 at 1515, it was discovered by corporate Fitness for Duty (FFD) personnel that an unescorted access reactivation feature in the security database (Illuminate) does not reset the flag to include an individual in the random FFD pool due to a database coding error. The Illuminate database was implemented fleet-wide 1/3/17. "Review by corporate FFD personnel found one individual currently badged at Clinton Power Station was affected by the coding error. The individual was not in the FFD random pool from 1/3/17 until 2/15/17. Corporate security personnel found no other individuals to be affected by this issue. "Affected individual was added to the FFD random pool. Corporate security personnel notified all Exelon sites of the issue. Sites were notified that the ability to use the re-activation feature in Illuminate would be removed from use by site personnel. Pending removal, a daily query would be run in the database to assure the re-activation feature had not been used by site personnel." The licensee informed the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2017-02-16
52554 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-02-15 22:28 | 2017-02-16 01:55 | 2017-02-23 | SAFEGUARDS REPORT Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. Compensatory measures taken upon discovery. The licensee will notify the NRC Senior Resident Inspector. * * * RETRACTION PROVIDED BY PATRICK EGAN TO JEFF ROTTON AT 1223 EST ON 02/23/2017 * * * A review by the licensee determined there was no degradation in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. This event does not meet the requirements of Part 73 Appendix G for reporting safeguards events, therefore Diablo Canyon is retracting the one hour report. The licensee will notify the NRC Resident Inspector. Notified R4DO (Pick) and Part 73 Safeguards group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-02-16
52553 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-02-15 10:09 | 2017-02-15 19:08 | 2017-02-15 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was received via e-mail from the Colorado Department of Public Health and Environment: "The general license section of the Radioactive Materials Program sent out annual notifications requesting response regarding tritium exit signs reported in use at locations given by the manufacturer. Upon an audit of the annual mailing for non-responders, Envision Inc. was contacted. After a complete inspection of the base store they are reporting the store was remodeled approximately 8 years ago; at that time the 4 tritium exit signs were removed. It is unknown if the exit signs were lost, destroyed or placed into the dumpster with the debris from the demolition. No further information is available due to time of reporting loss and lack of response by Envision Inc. "Number of Tritium exit signs were 4, Model #2040. Since Isolite Corporation did not report serial numbers on quarterly reports in 2001, no serial numbers are available. Each tritium exit sign contained 7500 mCi [milliCuries] of H-3, they were shipped from Isolite on 9/28/2001." CO Event Report ID No.: CO17-0005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-02-23
52552 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-02-15 13:37 | 2017-02-15 18:10 | 2017-04-12 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "On February 15, 2017 at 1337 [EST], Secondary Containment Zone 1 (Unit 1 Reactor Building) differential pressure lowered to 0 inches WG [Water Gauge] due to a trip of the running Unit 1 B Filtered Exhaust Fan. Required differential pressure per SR [Surveillance Requirement] 3.6.4.1.1 could not be maintained. Zone 1 differential pressure recovered to greater than 0.25 inches WG less than one minute later after start of the standby Zone 1 Filtered Exhaust Fan. Zone 2 (Unit 2 Reactor Building) and Zone 3 (Common Areas of Unit 1&2 Reactor Buildings) ventilation remained in service and stable. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG-1022, Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." Post-maintenance testing was underway when the fan tripped. While the investigation is on-going to determine the cause, the licensee does not believe the maintenance or testing caused the fan to trip The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM RONALD FRY TO DONALD NORWOOD AT 0833 EDT ON 4/12/2017 * * * "The Unit 1 B Filtered Exhaust Fan trip that resulted in loss of secondary containment differential pressure occurred during post maintenance testing (PMT). The PMT was being performed following replacement of a flow controller associated with the Unit 1 B Filtered Exhaust Fan. In support of the PMT, Technical Specification (TS) 3.6.4.1 Condition A had been entered and was in effect at the time of the fan trip. The maintenance and the associated PMT were performed in accordance with approved work instructions/procedure. Subsequent to the initial report, Susquehanna troubleshooting determined that the fan trip was the result of an internal leak in the newly installed controller that prevented the new controller from functioning properly. The condition was therefore determined to have been the result of the completed maintenance. "NUREG-1022, Section 3.2.7, includes the following guidance: '...reports are not required when systems are declared inoperable as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that would have resulted in the system being declared inoperable).' "Following completion of the troubleshooting, Susquehanna determined that, per NUREG-1022, Section 3.2.7, the event was not reportable. Secondary Containment was declared inoperable as a part of a planned evolution for maintenance which was done in accordance with an approved procedure and the Susquehanna TS. The discovered condition was not a pre-existing condition that would have resulted in the system being declared inoperable prior to the planned maintenance activity." The licensee notified the NRC Resident Inspector. Notified R1DO (Jackson). | 100 | 94 | 0 | 100 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-02-15
52551 | 0 | WEST VIRGINIA UNIVERSITY HOSPITAL |  |  |  |  | 2017-01-18 | 2017-02-15 14:05 | 2017-02-15 | LOST IODINE-125 IMPLANT SEED "In compliance with 10 CFR 20.2201(a), this report serves as notification of the loss of licensed material under West Virginia University Hospital Broad Scope License 47-23066-02. "On January 18, 2017, the Radiation Safety Department discovered that one Iodine-125 seed used in a Radioactive Seed Localization (RSL) procedure was missing. The seed in question had been implanted on November 8, 2016 and contained 241 microCuries of I-125. The patient had surgery to excise the specimen with the seed on the same day as implantation. "The specimen went to the Breast Care Center for imaging and then to the Pathology gross room where the seeds are removed and placed into plastic vials to await pick up by Radiation Safety staff. Radiation Safety staff documented that the seed in question plus 3 others were picked up from the gross room on November 9, 2016 and taken to the radioactive waste storage area. "The seed was discovered missing on January 18, 2017 during preparation of a return shipment of seeds to the manufacturer. WVU Radiation Safety promptly investigated the cause of the incident and performed thorough radiation surveys in the Pathology gross room, radioactive waste storage area, and specimen blocks in Pathology, however all surveys were indistinguishable from background. WVU Hospital feels it is likely that the seed was extracted from the specimen in the gross room but was never placed into the plastic vial and subsequently ended up discarded in the gross room waste. "During pick up by Radiation Safety, the seed was falsely identified by a visual verification as being present in the plastic vial. A blue plastic spacer, which comes preloaded in the syringe with the seed, may have been mistakenly identified as the seed due to its similar size and shape. WVU Hospital has instituted corrective actions to include more intense radiation surveys and better documentation of those surveys to prevent a future occurrence. In compliance with 10 CFR 20.2201(b), please expect a written report within the next 30 days for more details regarding this incident." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2017-02-23
52550 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2017-02-14 | 2017-02-15 10:30 | 2017-02-15 | AGREEMENT STATE REPORT - DAMAGED DENSITY GAUGE The following report was received via e-mail: "On February 14, 2017, we [Oklahoma Department of Environmental Quality] were informed by Producers Service Corp. that a routine inspection of a generally-licensed Berthold Technologies Model LB 8010 (S/N 10456) fixed density gauge revealed a crack in the rod which operated the shutter. The shutter operated normally despite this. A leak test was performed and was negative. The device contains 20 mCi of Cs-137. The rod and source shield have been replaced, and the damaged parts will be returned to Berthold." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2017-02-23
52549 | 0 | U.S. NAVY |  |  |  |  | 2017-01-18 05:45 | 2017-02-15 10:06 | 2017-02-15 | LOST RADIOACTIVE MATERIAL The following report was received via email: "1. The lost radioactive material consisted of one in flight blade inspection system (IBIS) pressure indicator which was installed on one CH-53E aircraft. The IBIS pressure indicator (P/N: 12210-1, S/N: 293) contained one 500 microCurie Strontium-90 source. "2. The IBIS pressure indicator was last visually accounted for prior to an aircraft flight on January 18, 2017. Much of the flight was over water and maneuvers were conducted over unpopulated woodland adjacent to Marine Corps Air Station (MCAS) New River, North Carolina. During the flight, nothing out of the ordinary was noted. After the flight, a post flight inspection was conducted and it was then discovered that an IBIS pressure indicator was missing. "3. The IBIS pressure indicator was discovered missing at 0545 [EST] on January 18, 2017 during a post flight inspection when the crew chief went to reinstall the IBIS pressure indicator covers. The likely location of the IBIS pressure indicator is in the water or unpopulated wooded area beneath the aircraft flight path in the New River, North Carolina region. "4. Exposure to individuals from radiation from the IBIS pressure indicator is unlikely due to its likely location in an uninhabited area. "5. Upon discovery of the missing IBIS pressure indicator, the aircraft maintenance crew at MCAS New River immediately performed an inspection of the flight line in the vicinity of the aircraft. On January 18, 2017 at approximately 1500 [EST] an extensive foreign object detection walk was conducted on the aircraft parking line. No debris associated with the missing IBIS pressure indicator was found. "6. An inspection was completed on all IBIS pressure indicators installed on aircraft associated with the MCAS New River in order to verify that the IBIS pressure indicators did not exhibit excessive wear indicating the potential for the displacement of an IBIS pressure indicator from the aircraft. MCAS New River aircraft operational and maintenance crew were re-briefed on the importance of vigilant pre-flight and post-flight aircraft inspections in order to identify potential material defects of aircraft components." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-02-23
52548 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-02-06 | 2017-02-14 14:17 | 2017-02-14 | AGREEMENT STATE REPORT - DENSITY GAUGE SHUTTER MALFUNCTION The following information was received via facsimile: "On February 13, 2017, the Department [PA DEP Bureau of Radiation Protection] was notified by Universal Well Services that a malfunction of a roll pin on a shutter handle occurred at a temporary job site in Zelienople, Pennsylvania. It is initially reportable per 10 CFR 30.50(b)(2). "A roll pin, which holds the shutter handle to the shutter shaft, on one of the in-line density gauges became sheared off during an attempt to move the shutter to the open position, rendering the gauge unusable. The shutter is in the closed position and out-of-service awaiting repair from a service provider. No exposures occurred. "The shutter is in the closed position and the gauge is out-of-service and secure. There was no other damage to the gauge. A reactive inspection is planned by the Department. "The gauge was a Berthold, Model LB 8010, Serial Number 10055, containing 20 mCi of Cs-137." Pennsylvania Event Report ID No.: PA170002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-02-22
52547 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2017-02-13 23:09 | 2017-02-14 02:40 | 2017-02-14 | UNIT 1 AUTOMATIC REACTOR SCRAM DUE TO MAIN GENERATOR TRIP ON DIFFERENTIAL CURRENT "This notification is being provided in accordance with 10 CFR 50.72(b)(2)(iv)(B). "On February 13, 2017 at 2309 CST, a Unit 1 Reactor Automatic Scram signal was received due to Turbine Control Valve Fast Closure. The turbine trip was due to the main generator trip on Differential Current. The 'U' safety relief valve actuated in the relief mode on the turbine trip, and has subsequently reset with tailpipe temperature returning to normal. The plant is in a stable condition with reactor pressure being maintained by the Turbine Bypass valves. Reactor water level is being controlled with feedwater. Investigation into the cause of the event is in progress." All control rods fully inserted on the scram. Unit 1 is in a normal shutdown electric plant alignment. Unit 2 was not affected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-02-14
52546 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-02-08 | 2017-02-09 13:12 | 2017-02-09 | AGREEMENT STATE REPORT - FIXED PROCESS GAUGE STUCK SHUTTER The following information was received via E-mail: "On February 9, 2017, the licensee notified the Agency [Texas Department of State Health Services] that on February 8, 2017, it was attempting to close the shutter on a Vega SHLG-1 fixed nuclear gauge to shut down the unit it was mounted on for maintenance and the shutter would not close. The gauge contains a 2,000 millicurie cesium-137 source, serial number 6380GG. The licensee reported there was no risk of exposure to employees or members of the public. A licensed service company is onsite and will secure a lead plate onto the device then remove the device and return it to the manufacturer for repairs. "More information will be provided as it is obtained in accordance with SA-300." Texas Incident No.: I-9463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-02-17
52545 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-02-08 16:31 | 2017-02-09 11:57 | 2017-02-09 | AGREEMENT STATE - RADIOACTIVE DEVICE FOUND IN SCRAP YARD The following report was received from the Wisconsin Department of Health Services Radiation Protection Section via email: "We [Wisconsin Department of Health] have an immediately reportable event under DHS 157.32(1)(a)1 regarding stolen, lost or missing material that is equal to or greater than 1,000 times the quantity specified in Appendix F. A phone message was left with the Wisconsin Department of Health Services at 1631 [CST] on February 8, 2017 [concerning] found radioactive material. The message was returned this morning, February 9, 2017 and the following information has been gathered. An NDC System 101 thickness gauge (SSD CA0471D102B), containing 150 mCi of Am-241 was recovered at a scrap yard in Wisconsin. The device was received in a load of scrap originating from Bemis Corporation in Neenah Wisconsin. The device, with serial number 11125, with 150 mCi of Am-241 assayed on 12/28/2009 is generally licensed to Bemis Corporation. The device was separated out of a load at Alter Trading in Green Bay Wisconsin. The State is currently in contact with both Alter Trading and Bemis Corporation to coordinate a response. An individual at Alter measured up to 3000 microR/h with their survey meter. The department will verify this measurement and determine if there is any contamination or personnel exposure. The department has dispatched staff to the site for response and to help facilitate transfer of the device to the owner." Wisconsin Event ID No.: WI-170001 * * * UPDATE AT 1701 EST ON 02/09/07 FROM KYLE WALTON TO JEFF HERRERA * * * The following update was received via email: "Inspectors investigated on February 9 at Alter Trading in Green Bay, where the device was being stored. It was determined that the device had unintentionally been removed from a machine during maintenance work at Bemis Company, Inc. and that it was then grouped with scrap metal before being transported to Alter Trading. While the shutter was open, the time spent around the device by any employees or members of the public, or employees of either Bemis or Alter, is believed to be minimal. The shutter has been closed, and wipe tests confirm that there is no removable contamination. There are no known or suspected overexposures resulting from this incident. Bemis is working with a service provider to arrange for packaging and transportation of the gauge back to their facility. Inspectors will perform an inspection of Bemis on February 10 to gather more information." Notified the R3DO (Kunowski) and NMSS Events (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-02-17
52544 | -1 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-02-03 20:24 | 2017-02-08 22:19 | 2017-04-04 | UNANALYZED CONDITION DUE TO UNACCOUNTED LOADS IN SAFE SHUTDOWN ANALYSIS "On February 3rd, 2017, during engineering modification reviews of electrical busses for a station switchyard transformer, electrical loads were identified on 4kV breakers that are not accounted for in the current safe shutdown analysis. Further reviews revealed the unanalyzed loads are associated with 26 cables that are routed through multiple fire zones in the Turbine Building and both Unit 1 and Unit 2 4kV rooms that have the potential to be affected from a fire event. Per NFPA 805 requirements, the cables need to be analyzed for overcurrent trip capability to demonstrate that the breakers will isolate a fault for a fire. "Hourly Fire Watch tours have been established in the identified fire zones. The public health and safety is not impacted. This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. "The NRC Resident Inspector was notified. This is a late notification for the 8 hour report." * * * RETRACTION PROVIDED BY ERIK LANKHEET TO JEFF ROTTON AT 1522 ON 04/04/2017 * * * "The condition reported in EN# 52544 pursuant to 10 CFR 50.72(b)(3)(ii)(B) has been evaluated, and determined not to be an unanalyzed condition that significantly degraded plant safety and is being retracted. "Fire Protection Engineering performed circuit analysis of the discovered loads and determined that the Fire Safety Analysis credited power supply for an established recovery action was lost due to a Turbine Building fire. This was determined to not be a significant impact to plant safety due to the availability of an alternate offsite 4kV power supply that was not impacted by this fire. Emergency Operating Procedures already contain guidance that directs operators to align the 4kV busses to this offsite power circuit and that can be accomplished within the time necessary to perform the recovery action. During periods when this offsite power circuit was removed from service over the past three years, risk was managed using the online risk management process and no additional actions would have been required for its use as the credited power source in the Fire Safety Analysis. "The NRC Resident Inspector was notified of this retraction." Notified the R3DO (Skokowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-02-08
52543 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2017-02-08 11:51 | 2017-02-08 17:31 | 2017-02-08 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE DUE TO DEGRADED DC TO AC INVERTER "During a control room panel walk down by an on-shift Reactor Operator at approximately 1151 [EST] on 2/8/2017, Unit 1 High Pressure Coolant Injection (HPCI) suction and discharge pressure indicators were noted to be downscale. I & C investigated and found the output of 1E41K603, DC to AC inverter, degraded. This inverter also powers the HPCI flow controller. Without the flow controller HPCI would not auto-start to mitigate the consequences of an accident, thus HPCI was declared inoperable. All other emergency core cooling systems and the Reactor Core Isolation Cooling (RCIC) system remain operable. "HPCI is a single train system with no redundant equipment in the same system, thus this failure is reportable as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident, 10CFR50.72(b)(3)(v)(D). "Inverter 1E41K603 was replaced and functionally tested satisfactorily at 1630 on 2/8/2017, restoring HPCI to operable status." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-02-08
52542 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2017-02-08 08:51 | 2017-02-08 17:06 | 2017-02-10 | TECHNICAL SUPPORT CENTER EMERGENCY VENTILATION SYSTEM INOPERABLE "At 0851 CST on Wednesday, February 8th, 2017, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) Emergency Ventilation System was emergently declared inoperable due to a failure of the outside air damper to reposition. This resulted in the inability for the TSC ventilation to maintain the required air flow to support habitability during emergency conditions. Actions are being taken to repair damper to restore functionality of the TSC ventilation system. In the interim, station procedures provide guidance to relocate the TSC to an alternate facility. This event is being reported under 10 CFR 72(b)(3)(xiii), Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system). "The NRC Resident Inspector has been notified." * * * UPDATE PROVIDED BY RYAN CHAMBERLAIN TO JEFF ROTTON AT 0418 EST ON 02/10/2017 * * * "At 0108 CST on February 10, 2017, Dresden TSC ventilation has been restored and is now functional. "The NRC Resident Inspector has been notified." Notified R3DO (Kunowski). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-02-08
52541 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2017-02-08 | 2017-02-08 14:37 | 2017-02-08 | AGREEMENT STATE REPORT - FAILURE OF FIXED GAUGE MOUNTING SYSTEM The following report was received from the Kentucky Department of Public Health and Safety, Radiation Health Branch via email: "Licensee discovered fixed gauge had become dismounted from associated equipment due to failed mounting system. RSO supervised placing gauge in safe condition which included closing the shutter mechanism and placing the gauge in secure storage. The licensee does not suspect any radiation related injuries or exposures; however, they are still investigating." KY Event Report ID No.: KY170001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2017-02-16
52540 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-02-08 | 2017-02-08 13:28 | 2017-02-08 | AGREEMENT STATE REPORT - CONTAMINATED PACKAGES The following report was received via e-mail: "On February 8, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee (a nuclear pharmacy) that three packages received were contaminated with radioactive material. The contamination does not seem to have come from the contents of the packages themselves, the receiving facility, or the origin facility. Additional information will be shared as it is received in accordance with SA-300." * * * UPDATE ON 2/8/17 AT 1655 EST FROM GENTRY HEARN TO DONG PARK * * * The following report was received via e-mail: "On February 8, 2016, the Agency [Texas Department of State Health Services] dispatched an inspector to the licensee's facility to investigate. No additional contamination was found in the licensee's facility. No likely sources of contamination for the packages were identified. The truck and driver that had delivered the packages was intercepted by the shipper and redirected back to the licensee's facility. The truck and driver were surveyed for fixed and removable contamination. No contamination was found on the truck, driver, or associated equipment. Additional information will be shared as is received in accordance with SA-300. "Texas Incident #: I - 9462" Notified R4DO (Warnick) and NMSS Events Notifications via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-02-16
52539 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-12-15 13:32 | 2017-02-08 13:04 | 2017-02-08 | 60 DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID CONTAINMENT VENTILATION ISOLATION ACTUATION "This 60 day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report an Invalid Containment Ventilation Isolation (CVI) actuation at Watts Bar Nuclear Plant (WBN) Unit 2. "On December 15, 2016 at 1332 Eastern Standard Time (EST), Unit 2 maintenance personnel were preparing to perform a breaker swap for the normal feed to the 2B1B C and A vent board. When the power was removed from Radiation Monitor 2-RM-90-131, the B Train master isolation signal status panel was unexpectedly lit for CVI. The only automatic action observed from the containment isolation status panel was that 2-FCV-30-037, Lower Compartment Purge Control valve, went closed. The loss of power to 2-RM-90-131 de-energized the relay associated with the high radiation setpoint, resulting in an invalid Train B CVI actuation. "During this event, the train B CVI actuation was complete and equipment functioned as designed. Upon identification of the Train B CVI, maintenance activities were halted and a prompt investigation was initiated. WBN found that the work order to perform the breaker swap was planned to lift leads to disable actuation of CVI. The work order lifted the lead for the K622 relay, which was insufficient to prevent the actuation. Two other leads on relays should have been lifted to prevent the actuation in Mode 1. A contributor to this error was that this work had been rescheduled several times prior to actual performance. From the time it was planned to the actual performance, mode changes had been performed on the Unit and no further reviews were performed. "The licensee notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-02-08
52538 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-02-07 12:00 | 2017-02-08 12:21 | 2017-02-10 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was received via e-mail: "Detail: The general license section of the Radioactive Materials Program sent out the annual notification requesting response regarding tritium exit signs reported in use at the location given by the manufacturer. Upon an audit of the annual mailing for non-responders, Colorado Dept of Corrections - Sterling Correctional was contacted. The contact at Sterling Correctional explained they conducted an inspection of the property and were not able to find any of the exit signs ordered from SRB Technologies still in use. It is unknown what occurred with the Tritium exit signs since 16 years have passed. The contact was not able to confirm if the tritium exit signs were ever installed in the building. "SRB Technologies was contacted to obtain information from a purchase order number provided on the manufacturer report. No response has been received. The information on the manufactures report shows the ship to address as Holcomb & Hoke MFG CO. Inc. In trying to contact them it was discovered the business had closed several years ago. When the tritium signs were shipped to them the company was manufacturing movable walls/panels for large spaces. Note: companies who make movable walls will install tritium exit signs in the wall prior to shipping to end user. "The lost tritium exit signs are model # BX-10-WH, Serial Numbers 243257 thru 243261, 5 signs, Isotope H-3, Activity 10 Curies, Shipped 07/06/2001. No further information is obtainable. "The Colorado Dept of Corrections is being asked to supply a corrective action with policy and procedure should any additional signs are ordered. "Event Report ID No.: CO17-0004" * * * UPDATE FROM LINDA BARTISH TO DONALD NORWOOD AT 1553 EST ON 2/10/2017 * * * The following information was received via E-mail: "After contacting the Colorado Sterling Correctional Facility and explaining we [Colorado Department of Health] needed a corrective action regarding how they will track additional remaining tritium exit signs and asking for a safety policy and procedure guide, I guess the plant manager decided to go and see if they actually had any of the movable wall in the facility. As it turns out he did find the area with the walls and the 5 Tritium Exit Signs. "They are now in the process of taking the signs out to return to the manufacturer. "Case Closed." Notified R4DO (Warnick) and NMSS Events Notification. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-02-16
52537 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2017-01-02 | 2017-02-08 11:17 | 2017-02-08 | PART 21 - VALVE ASSEMBLY NONCONFORMANCE "Subject: 3" Style HPNS Valve Body/Cage/Plug Retainer Binding "Equipment Affected by this Fisher Information Notice: Items subject to this Fisher Information Notice (FIN) are confined to the equipment and orders referred to in Appendix A attached. Specifically, affected equipment refers to the 3" style HPNS valve body for next-generation nuclear plants and its associated cage and plug retainer. "Purpose: The purpose of this FIN is to alert affected customers that, as of 2 January 2017, Fisher Controls International LLC (Fisher) became aware of a situation which may affect the performance of the aforementioned equipment, including its safety-related function. Fisher is informing affected customers of this circumstance in accordance with Section 21.21(b) of 10 CFR 21. "Applicability: This FIN applies only to the equipment identified in Appendix A, which lists serial numbers and order numbers that were delivered to customers. Specifically, it applies to the Fisher 3 style HPNS valve body assembly, sold to AP1000 next generation plant sites, Commodity Package PV14, Datasheet 111. "Discussion: During plant hot functional testing, certain valve assemblies did not achieve full travel. Upon disassembly, site inspection found wear between the cage and plug retainer in some valves. Vertical scratches in the cage internal diameter and plug retainer outside diameter was confirmation of galling which prohibited full travel. In one valve, the cage could not be removed from the body as it was friction-welded due to galling. "The valve body-to-cage interference is attributed to body-to-bonnet gasket compression which caused the valve body gasket groove to distort/yield, particularly the cage guide internal diameter bore. Regarding the cage-to-plug retainer binding, thermal expansion calculations between cage internal diameter and plug retainer outside diameter indicate an undersized diametrical clearance at temperature. "Extent of Condition: In addition to the equipment listed in Appendix A, all other style HPNS designs (NPS 1/2, 1, 2, 3, 4, 6, and 8) were examined for extent of condition. Results indicate that DS111 was a lone outlier and this issue is not expected to occur for the other sizes, material combinations and datasheets sold into their respective applications and temperatures. Arrangements have been made with the customers to replace or maintenance the trim for the equipment listed in Appendix A. In addition, a Corrective Action Request (CAR 1817) has been initiated by Fisher to prevent reoccurrence of this issue. "10 CFR 21 Implications: Fisher requests that the recipient of this FIN review it and take appropriate action in accordance with 10 CFR 21. If there are any technical questions or concerns, please contact: Ben Ahrens, Quality Manager, Emerson Automation Solutions, Fisher Controls International LLC, 301 South First Avenue, Marshalltown, IA 50158, Phone: (641) 754-2249, F (641) 754-2830." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | CONSTRUCT DEFICIENCY | [8 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) | 50.55(e) |  |  | 0 | 2017-02-08
52536 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2017-02-03 | 2017-02-06 17:30 | 2017-02-06 | AIR EFFLUENT CONCENTRATION EXCEEDED TECHNICAL SPECIFICATIONS "[The following] is a required notification per MURR [University of Missouri Research Reactor] Technical Specification (TS) 6.6.c.(1) to report to the NRC Operations Center that an Abnormal Occurrence as defined by MURR TS 1.1.b occurred on February 3, 2017. Specifically, MURR was not in compliance with the Limiting Condition for Operations TS 3.7.b. "On February 3, 2017, MURR released the radioisotope Iodine-131 from the ventilation exhaust stack at a concentration equal to 1.07 times AEC [Air Effluent Concentration] which exceeds the one (1) AEC Maximum Controlled Instantaneous Release Concentration for 'Particulates and halogens with half-lives greater than 8 days'. The Iodine-131 originated from the MURR Iodine-131 Processing Hot Cells, not from the reactor. By February 4, 2017, the ventilation exhaust stack radioisotope concentration was within TS limits. "Currently, all Iodine-131 processing activities have ceased and will not resume until corrective actions are implemented and permission from the Facility Director is obtained. MURR has convened an Event Review per MURR procedure AP-RR-026 to identify the causes and corrective actions for this departure from specification. "A detailed event report will follow within 14 days as required by MURR TS 6.6.c.(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2017-02-06
52535 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-02-06 | 2017-02-06 12:40 | 2017-02-06 | AGREEMENT STATE REPORT - TRANSPORTATION POSTING INACCURACY The following report was received from the State of Louisiana via email: "Event description: On February 6, 2017, LDEQ [Louisiana Department of Environmental Quality] was notified by Alpha-Omega, Inc., that the facility had received three 'EMPTY' Nucletron V2 containers from a Mexico site then transported to the United States, Alpha-Omega Services, Inc., Vinton, Louisiana, 70668. "When inspected, two of the containers had Ir-192 sources in them, Model 105.002. Container 2785C6 had source D36F3728, 25 mCi of Ir-192, a QSA Global source. Container 2053C6 had source D36P3481, 351 mCi of Ir-192, an Alpha-Omega, Inc. source. "Event Report ID No.: LA-170002." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-02-14
52534 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-02-03 15:45 | 2017-02-03 18:56 | 2017-02-03 | UNIT 1 MANUAL REACTOR TRIP DUE TO LOOP 1 MSIV STARTING TO FAIL CLOSED "At 1545 EST on 2/3/17, Vogtle Unit 1 was manually tripped from 100% power when loop 1 Main Steam Isolation Valve (MSIV) started to fail closed. Non-Safety Related 4160V bus 1NA01 failed to transfer to alternate incoming power supply automatically and was successfully manually energized. "All control rods fully inserted and AFW [Auxiliary Feedwater] and FWI [Feedwater Isolation] actuated as expected. "Unit 1 is in Mode 3 and stable with decay heat being removed by AFW." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-02-03
52533 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-02-03 | 2017-02-03 18:45 | 2017-02-03 | AGREEMENT STATE REPORT - MOISTURE DENISTY GAUGE SHIPMENT LOST IN TRANSIT The following report was received via e-mail: "Texas licensee, Amarillo Testing and Engineering, reported that two moisture density gauges being shipped to them from Qal Tek in Idaho Falls had gone missing during shipment. The trucking company, has been unable to locate the packages and last identified them in Pocatello, Idaho. The gauges are Troxler model 3411 and 3440 and each contain an 8 mCi Cs-137 and a 40 mCi Americium- 241 source. The packages were delivered to the carrier on 01/18/2017." Texas Incident: I-9460 See also Event Notification 52532 for this event reported from Qual-Tek in Idaho. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-02-13
52532 | 0 | QAL-TEK ASSOCIATES, LLC |  |  |  |  | 2017-01-31 | 2017-02-03 18:02 | 2017-02-08 | MOISTURE DENSITY GAUGE SHIPMENT LOST IN TRANSIT "On January 18th, 2017, two Troxler nuclear density gauges (NDG's) were shipped via [the common carrier] from our Idaho calibration facility to the client in Amarillo, Texas. The two gauges (Make: Troxler, Models: 3411 and 3440 Plus, sn: 12605 and 39690) each container 8mCi of Cs-137 and 40 mCi of Am-241/Be were checked in at the Pocatello [the common carrier] hub on January 18th. The gauges owner notified the Idaho calibration facility on January 31, 2017 inquiring why the gauges have not arrived. The Idaho calibration facility immediately called [the common carrier] to check the status. [The common carrier] after tracking and looking for the gauges notified the calibration facility that they were not at the Pocatello hub. According to [the common carrier's] tracking system as of 1/24/2017, they were still in Pocatello with no further movement toward the Amarillo, Texas destination. On February 1st, the calibration facility then called on the [common carrier] account manager to apprise him of the priority situation. The account manager said he would call each hub from Pocatello to Amarillo, Texas where the gauges should pass through. The account manager returned the call the same day stating they did not find the gauges in the hub along the anticipated shipping route. The calibration facility continued to pressure [the common carrier] to search their system. On February 3rd, [the common carrier] initiated a 'corporate flag' for every dock to search for the gauges. The calibration facility also dispatched an employee with a meter to survey the Pocatello distribution hub floor and storage locations. The gauges were not found at the Pocatello hub during the survey conducted by the calibration facility representative. On February 3rd, the calibration facility RSO contacted the gauges owner to discuss the status and immediate reporting requirement. Both parties agreed to notify their respective regulators. On February 6th, the [common carrier] account manager notified the calibration facility stating that they have not made any progress finding the missing gauges in their distribution system." See also Event Notification 52533 for this event reported by Texas. * * * UPDATE AT 1043 EST ON 02/08/17 FROM MICHAEL ALBANESE TO S. SANDIN * * * The missing gauges were located by [the common carrier] in their Salt Lake City hub and are enroute to the customer in Amarillo, TX. Notified R4DO (Warnick) and NMSS Events Notifications via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-02-13
52531 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-02-03 14:58 | 2017-02-03 16:33 | 2017-02-03 | UNANALYZED CONDITION - APPENDIX R FIRE ANALYSIS "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10CFR50.48(b) (Appendix R) to 10CFR50.48(c) (NFPA 805), a weak-link and operator manual action (OMA) analysis for Information Notice (IN) 92-18 type hot shorts on motor-operated valves (MOVs) was performed to support the Plant Hatch Appendix R Safe Shutdown Analysis. As a result of the analysis, it was identified that cable impacts can bypass valve limit and torque switches, resulting in physical damage to valves required for Safe Shutdown. This would prevent the valves from being operated locally or being operated from the remote shutdown panel. These cable failures could also cause the valve motors to fail. This updated analysis has identified circuit configuration deficiencies in Fire Areas 0024 A & C (Main Control Room & Cable Spread Room), 1203F (U1 Reactor Building SE), 1205F (U1 Reactor Building NE), and 2203F (U2 Reactor Building NE). Therefore, due to the identified deficient conditions, it was determined that in the event of a postulated fire in the affected fire areas, the paths of safe shutdown on the affected unit(s) could be compromised and impact the ability to achieve safe shutdown conditions. "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions in these same fire areas. The presence of the compensatory measures in addition to automatic fire detection in these fire areas ensure that the safe shutdown paths are preserved until the degraded conditions can be repaired. "CRs 10326399, 10326401, 10326402, 10326404 and 10326405" The licensee notified the NRC Resident Inspector. The unanalyzed condition is applicable to 10CFR50.48(b) Appendix R and not to 10CFR50.48(c) (NFPA 805). | 100 | 88 | 0 | 100 | 88 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-02-03
52530 | 0 | US COAST GUARD |  |  |  |  | 2017-02-03 08:00 | 2017-02-03 13:50 | 2017-02-03 | LOST TRITIUM EXIT SIGN An inventory of the tritium exit signs at US Coast Guard Air Station Barbers Point, Kapolei, HI determined that one sign was missing. Last test date: January 2001 Quantity of tritium: 7.5 Ci Manufacturer: Isolite Model: 2040 Serial Number: A071367 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-02-13
52529 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-01-29 | 2017-02-03 11:51 | 2017-02-03 | AGREEMENT STATE REPORT - STOLEN X-RAY FLUORESCENT ANALYZER "On Sunday evening January 29, 2017 an instrument case containing a portable lead in paint analyzer belonging to an Environmental Design International, Inc. employee was stolen from a vehicle. The general licensee reported the event the following day to the Agency but had already been in contact with the Chicago Police Department who were investigating. The theft took place in the Near West Side neighborhood of Chicago while the locked case was in the trunk of a vehicle. This device can only be operated with a password. The maximum surface radiation level from the device as reported by the manufacturer does not exceed 0.1 milliR/h. It contains an IAEA Category 5 level source, the lowest risk category assigned by the IAEA in that no one could be permanently injured by this source and if the radioactive material could be dispersed, would not permanently injure anyone." Manufacturer: Niton Model: XLp-300 Serial Number: 84640 Source Manufacturer: Eckert & Ziegler Source Activity: 25 mCi Cd-109 Source Model: XFB-3 Source Serial Number: TR3631 Illinois Event: IL17003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-02-13
52528 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2017-02-02 13:30 | 2017-02-02 20:44 | 2017-02-02 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER FAILED TO CLOSE DURING PREVENTATIVE MAINTENANCE The following information was provided by the State of Utah via email: "DWMRC [Utah Department of Environmental Quality, Division of Waste Management and Radiation Control] was notified of the event at 4:26 PM MST, on February 2, 2017. "The licensee indicated that an employee had been assigned to conduct some preventative maintenance checks on an Ohmart Vega Gauge, Model SH-1, Serial Number 2199CG. At about 1:30 PM MST, the employee attempted to shut the gauge's shutter and one of the two screws attaching the handle to the shutter sheared off. The shutter could not be closed after that because the handle would just spin around. The gauge contained 50 mCi (as assayed 11/01) of Cs-137. The gauge is located about 10 feet above the walkway in the smelter/slag mill. The beam is running parallel to the ground and poses no danger to individuals in the building." The licensee will remove the gauge and send it to an authorized repair facility. UT Event Report ID No.: UT170002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2017-02-10
52527 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2017-02-01 19:38 | 2017-02-01 21:22 | 2017-02-02 | ALERT - FIRE IN SAFETY RELATED SYSTEM "On February 1, 2017, at 1929 hours [CST], a fire was discovered on the Unit 2 Main Control Room panel 902-3 in the 3E ERV/ADS valve switch. A reactor SCRAM was not required. No automatic isolations/actuations occurred. The fire was extinguished at 1932 and the reactor remained at 100% power. "An Alert was declared at 1938 [CST]. "The initiation of the event was attempting to change a light bulb. The cause of the event is under investigation. "The Senior Resident Inspector has been notified of the event." The licensee entered a 14 day Technical Specification Action statement as a result of the damage to the switch. Notified DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, FDA, NNSA (e-mail), and NRCC SASC (e-mail). * * * UPDATE AT 0040 EST ON 2/2/17 FROM DAVID KNEPPER TO JEFF HERRERA * * * Notified that the Alert was terminated at 2336 CST on 2/1/17. The licensee stated that the fire was extinguished and an extent of condition walkdown did not identify any additional equipment damage as a result of the fire. The licensee will be issuing a press release. The licensee will be notifying the NRC Resident Inspector. Notified the R3DO (Duncan), IRD MOC (Gott), NRR EO (Miller), DHS SWO, DOE, FEMA, HHS, NICC, USDA, EPA, FDA, NNSA (e-mail), and NRCC SASC (e-mail). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-02-01
52526 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-02-01 16:05 | 2017-02-01 16:46 | 2017-02-01 | UNUSUAL EVENT - POTENTIAL SECURITY EVENT Plant Hatch declared a notification of unusual event. Subsequent investigation determined the paraphernalia was related to plant drills. The Unusual Event was terminated at 1727 EST. The licensee notified the NRC Resident Inspector. Notified the DHS SWO, FEMA, NICC, and NNSA (via e-mail). * * * RETRACTION FROM KENNETH HUNTER TO MARK ABRAMOVITZ AT 1829 EST ON 2/1/2017 * * * The event was retracted. The licensee notified the NRC Resident Inspector. Notified the R2DO (Shakur), NSIR (Holian), IRD MOC (Gott), DHS SWO, FEMA, NICC, and NNSA (via e-mail). | 100 | 90 | 0 | 100 | 90 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-02-01
52525 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2017-02-01 11:00 | 2017-02-01 15:41 | 2017-02-01 | AGREEMENT STATE REPORT - LOST/FOUND MOISTURE DENSITY GAUGE The following report was received via e-mail: "Nebraska Department of Health and Human Services, Office of Radiological Health was notified on February 1, 2017, by a representative from Olsson Associates, of a loss and subsequent return of licensed material from the back of a pickup truck on Wednesday, February 1, 2017, in Omaha, Nebraska. The licensed material is a Troxler 3400 series moisture density gauge, serial number 19309, containing 9 mCi of Cs-137 and 44 mCi of Am:Be. The licensee reported to the State that an employee placed the licensed material on the back of the pickup truck and not in the yellow shipping case, and drove away from a temporary jobsite. While the employee made a right hand turn, the Troxler gauge fell out of the truck. A vehicle that was passing nearby found the Troxler gauge and returned it to the licensee about 10 minutes after the employee notified the Radiation Safety Officer. The gauge was visually inspected and no physical damage was found. The gauge was also surveyed to confirm the presence of the source. No elevated readings were found. The licensee has locked the gauge in the yellow shipping container and removed it from service. A follow-up site visit is scheduled and a 30 day written report is to follow." Nebraska Event: NE-17-0001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2017-02-09
52524 | 0 | HENRY FORD HOSPITAL |  |  |  |  | 2017-01-31 10:51 | 2017-02-01 15:13 | 2017-02-01 | POTENTIAL MEDICAL EVENT A patient at the Henry Ford Hospital Interventional Radiology Department was prescribed a Y-90 Theraspheres treatment of 60 Gray to the left lobe of the liver. The Interventional Radiologist administered 46 Gray total to both the right and the left lobe of the liver. The referring physician has been notified and the licensee has notified the patient. It is believed that this event will not result in any harm to the patient. The licensee is in the process of determining corrective action to prevent reoccurrence. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | DOSE TO OTHER SITE > SPECIFIED LIMITS | [8 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) | 35.3045(a)(3) |  |  | 0 | 2017-02-09
52523 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2017-01-31 12:00 | 2017-01-31 15:39 | 2017-01-31 | REACTOR COOLANT PRESSURE BOUNDARY PIPING DEFECT "At 1200 [EST] on January 31, 2017, during investigation of potential 1B2 Reactor Coolant Pump seal degradation, a through wall defect was identified on Class 1 piping servicing the Lower Seal Heat Exchanger, which is part of the Reactor Coolant Pressure Boundary (RCPB). The reactor is presently in Mode 3 with decay heat being removed by the atmospheric steam dump valves. The plant is being maneuvered to Mode 5 to affect appropriate repairs." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-01-31
52522 | 0 | WECTEC LLC |  |  |  |  | 2017-01-31 | 2017-01-31 15:36 | 2017-01-31 | PART 21 - PIPING SPOOL WELD NONCONFORMANCE The following is an excerpt from WECTEC LLC received via email: "Based on information contained in nonconformance and disposition (N&D) report, a piping spool that was supplied to Aecon Industrial for use in a portion of the Chemical and Volume Control System (CVS) for the V. C. Summer Unit 2 AP1000r project was found to have a weld with an underfill condition. The piping spool was fabricated by CB&I Laurens based on a purchase order from WECTEC LLC. The identified weld defect is associated with a Safety Class B piping spool as part of the containment penetration boundary for the CVS makeup line. Evaluation of the nonconforming weld condition was inconclusive, and therefore, this condition is conservatively assumed to result in the potential failure of the associated containment penetration if it had been left uncorrected." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-01-31
52521 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2017-01-30 | 2017-01-31 15:05 | 2017-01-31 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The following report was received via e-mail: "We [Oklahoma Department of Environmental Quality] have just been informed of an incident which occurred yesterday (1/30/2017) involving the failure of an industrial radiography source to retract. The licensee was NDE Solutions, LLC (TX license L05879) operating out of Bryan, TX. The incident occurred at a temporary job site near Checotah, OK. The licensee was working in Oklahoma under reciprocity. According to the report the drive cable failed, it isn't clear whether the source just wouldn't retract or became disconnected. The source was retrieved yesterday. The drive cable has been removed from service and is being returned to Texas." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-02-08
52520 | 0 | WASHINGTON UNIVERSITY IN ST. LOUIS |  |  |  |  | 2016-04-08 | 2017-01-31 10:15 | 2017-02-20 | PATIENT DELIVERED RADIATION DOSE TO RIGHT LOBE OF LIVER VERSUS LEFT LOBE The following was received via email: "On 4/8/2016 a patient was being treated with Y-90 TheraSpheres. Written directive prescribed 4.15 GBq (117 mCi) Y-90 TheraSpheres to the left liver lobe. The catheter placement was confirmed by the Interventional Radiologist with an angiogram to administer the microspheres to the left liver lobe. The dose of 4.07 GBq of Y-90 TheraSpheres was administered. This patient was part of a study to image the location of the Y-90 TheraSpheres using a PET/MRI unit. The PET/MRI images were taken on 4/15/2016 and were read by a Radiation Oncology Authorized User on 4/16/2016. The PET/MRI images indicated that the majority of the microspheres were deposited in the right liver lobe. The Radiation Safety Officer (RSO) was immediately notified. Evaluation of the incident in accordance with the 'Yttrium-90 Microsphere Brachytherapy Sources and Devices TheraSphere and SIR-Spheres Licensing Guidance' (February 12, 2016, Revision 9) event reporting criteria was done by the RSO, Radiation Safety Committee (RSC) Chairman, Management and Radiation Oncology and the incident was judged not to be a medical event due to unintentional patient intervention. The patient and the physician were notified of the incident. "The RSO has been discussing this incident with the University's NRC Region III Lead Inspector [Gattone] over the past few weeks. The Inspector let the RSO know that NRC Headquarters and Region III had determined that the incident is a medical event. The Inspector requested on 1/30/2017 that the RSO report the medical event to the NRC Operations Center." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM SUSAN LANGHORST (RSO) TO HOWIE CROUCH ON 2/20/17 AT 0923 EST * * * The RSO provided some minor corrections to the organization name as well as correcting one date in the original report. The original report stated that PET/MRI images were taken on 4/15/16 when they were actually taken on 4/8/16. Notified the R3DO (Pelke) and NMSS (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PATIENT INTERVENTION DAMAGE | [10 empty] | 3 | MO | MAT |  | 35.3045(b) |  |  |  | 0 | 2017-02-08
52519 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2017-01-30 19:08 | 2017-01-30 23:34 | 2017-01-30 | ONE DIVISION EMERGENCY DIESEL GENERATOR COOLING WATER SYSTEM DECLARED INOPERABLE "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D), event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. During routine surveillance testing of the Unit 2 Division 3 Emergency Diesel Generator (LOS-DG-M3), the Cooling Water Strainer Backwash Valve, 2E22-F319, was identified to have stem/disk separation and could not be opened. "This condition has been evaluated and the Division 3 Diesel Generator Cooling Water system has been declared inoperable. The Division 3 Diesel Generator Cooling Water system is a support system for the Division 3 Emergency Diesel Generator and the High Pressure Core Spray System (HPCS). The required actions of Technical Specification (TS) 3.5.1 were entered on 1/30/17 at 1908 CST when the HPCS system was determined to be inoperable. "This condition could have prevented the HPCS, a single train safety system, from performing its design function." The licensee has notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-01-30
52518 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-01-30 11:43 | 2017-01-30 14:38 | 2017-01-30 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY "At approximately 1049 EST, an individual was discovered to be unresponsive at a site training facility outside of the Protected Area. The individual was transported via ambulance to the Burke County Hospital and was declared deceased at 1143 EST. "The licensee has notified the NRC Resident Inspector. The licensee notified the State of Georgia Department of Labor - OSHA at 1414 EST." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-01-30
52517 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-01-29 02:09 | 2017-01-29 16:30 | 2017-02-08 | LOSS OF BOTH DIVISIONS OF CONTROL BUILDING CHILL WATER AND VENTILATION SYSTEM "At 0209 CST, on January 29, 2017, while the plant was in MODE 4 for a refueling outage, the main control room crew removed the AC/DC inverter in the Division 1, 120 VAC electrical distribution system from service due to an equipment malfunction. Removing the inverter from service caused a loss of the associated 120 VAC instrument buss. This instrument buss loss caused a trip of the Division 1 Control Building Chill Water and Ventilation system. The Division 2 Control Building Chill Water and Ventilation System was locked out for surveillance testing at the time of the equipment failure. This condition rendered both divisions of Control Building Chill Water and Ventilation Systems unable to perform the support function for cooling Division 1 and 2 AC and DC power distribution systems. These systems are required to support the operability of two required divisions of shutdown cooling. Division 2 Shutdown Cooling System was in service and remained in service through out the event. "The Division 2 Control Building Chill Water and Ventilation System was returned to service at 0220 CST on January 29, 2017. "Division 1 Control Building Chill Water remains inoperable pending restoration with the installed backup Division 1 DC/AC inverter. Actions are ongoing to place this component in service and restore the associated 120 VAC instrument buss. "The equipment malfunction was limited to the Division 1 inverter. The investigation of the inverter failure is ongoing. This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v)(B). "The NRC Senior Resident Inspector has been notified." * * * RETRACTION ON 2/8/17 AT 1617 EST FROM STEVEN CARTER TO DONG PARK * * * "Engineering has previously performed an evaluation for a loss of Control Building Chill Water and Ventilation, reference Engineering Change-58699. Based on the evaluation, it can be determined that in the event of a Loss of Coolant Accident with a loss of Offsite Power, a loss of all Control Building cooling the Inverter, Battery, and Switchgear Rooms will not exceed 122 deg. F for 2.80 hours or greater with no operator actions required. The 2.8 hours is based on the switchgear room inverters operating which is bounding for the case where the DC equipment room inverters are operating. The 122 deg. F criterion is significant because that is the manufacturer ambient maximum temperature for the Division 3 DC Equipment Room. This is the limiting temperature for the Battery, Inverter, and Switchgear Rooms. "During the event, operators performed the dedicated actions of AOP-0060 Loss of Control Building Ventilation and restored Division II Chill Water and Ventilation in 11 minutes. All required actions are in the Control Building, either in the Main Control Room or on the 98 foot Elevation. There are no radiological concerns in the Control Building, such as high radiation areas or contaminated areas. Per Engineering Change-58699, assuming a single operator error, the total time to recover from a single operator error and to complete the standby chiller realignment and start is 76 minutes ([approximately] 1.3 hours) which is less than half of the 2.8 hours established in Engineering Change-58699. Therefore, there was no loss of safety function for Control Building Chill Water and Ventilation." The licensee has notified the NRC Resident Inspector. Notified R4DO (Warnick). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2017-01-29
52516 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-01-27 18:08 | 2017-01-27 23:05 | 2017-01-27 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "This notification is to report a loss of safety function in accordance with 10 CFR 50.72(b)(3)(v)(D). At approximately 1808 CST hours on Friday, January 27, 2017, the Grand Gulf Nuclear Station Unit 1 High Pressure Core Spray (HPCS) system was declared inoperable due to the trip of the HPCS Jockey Pump. "At the time of discovery, Unit 1 was in Mode 2 and raising power in the source range to return to power operations. No other safety systems were inoperable at the time of this event. "Investigation into the cause of the event is ongoing and the system will be returned to operational status prior to proceeding to Mode 1." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-01-27
52515 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-11-01 10:00 | 2017-01-27 13:49 | 2017-01-27 | AGREEMENT STATE REPORT - FAILED SEALED SOURCE LEAK TEST The following information was received via E-mail: "On November 1, 2016, Eastman Kodak Company informed the Department [New York State Department of Health] that an NRD Model A-2003 static eliminator sealed source leak test result indicated a measurable contamination of 0.00661 microCuries. The device was taken out of service and another leak test was performed on the unit. The second leak test results showed only 0.0003 microCuries." New York Event Report ID No: NYDOH - NY-16-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-02-06
52514 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-01-24 | 2017-01-27 12:10 | 2017-01-27 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION AT HOSPITAL The following was received from the State of Illinois via email: "On January 25, the licensee's Radiation Safety Officer (RSO) contacted the Agency [Illinois Emergency Management Agency] to report an issue with an administration of a capsule containing I-131 which had occurred the previous afternoon. A nominal dose of 30 milliCi in capsule form was given to a child within the nuclear medicine department of the licensee's facility. Although the patient was being treated on an outpatient basis, the licensee was keeping the patient for a short time to ensure there would be no complications before being sent home. During this period, staff checked in on the patient several times and during one of the visits, discovered that rather than swallowing the capsule as instructed, the patient had spit the capsule out into their hand and was hiding the capsule. This resulted in extensive contamination of the patient's hand, clothing and the chair they were sitting in as well as the immediate surrounding area. During the process to evaluate and decontaminate the patient, additional contamination was discovered in adjacent camera rooms and corridors where the staff had traversed. Staff moved to close the department and restrict passage into/out of the nearby areas to prevent additional spread of contamination. Initial estimates suggest that the patient ingested little if any of the activity and that excessive levels were throughout the area of the nuclear medicine department. Based on this finding, barriers were erected and the department was closed for over 48 hours while assessment and decontamination efforts were ongoing. "Agency inspectors were at the site on January 26 to perform assessments of exposure, contamination levels, potential uptake by staff and corrective action being taken by the licensee. This matter will remain open while those assessments are on going. Initial bioassay results suggest only negligible uptakes have occurred with staff. Potential exposures/uptakes continue to be evaluated by the licensee throughout the decontamination process. The licensee is exploring the potential for having additional outside resources complete the necessary decontamination and remediation steps so that the department can reopen and provide at least limited services." Illinois Item Number: IL17002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-02-06
52513 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2017-01-27 06:41 | 2017-01-27 07:25 | 2017-01-27 | UNUSUAL EVENT DECLARED DUE TO UNVERIFIED FIRE ALARM IN CONTAINMENT "An Unusual Event [HU.4] was declared at BVPS [Beaver Valley Power Station] Unit 1 at 0641 EST due to a fire alarm in Containment which was unable to be verified extinguished within 15 minutes. Current Containment parameters do not indicate an actual fire. The Fire Alarm has subsequently been reset [at 0648 EST]. "The Licensee notified the NRC Resident Inspector." The Licensee has notified State and local government agencies. A containment entry is planned for 1000 EST to verify that there is no fire. Unit 1 continues at 100 percent power. Unit 2 was unaffected. Notified DHS SWO, FEMA Ops Center, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA. * * * UPDATE FROM MICHAEL SMITH TO STEVEN VITTO ON 1/27/2017 AT 0952 EST * * * "The time of the fire alarm reset was at 0648 EST on 1/27/2017. "The Unusual Event has been terminated at 0934 EST on 1/27/2017 after a containment entry and visual inspection determined no fire or indications of a fire exist. "The following notifications were made: Commonwealth of Pennsylvania Emergency Management Agency, Beaver County in Pennsylvania, The State of Ohio Emergency Management Agency, Columbia County in Ohio, The State of West Virginia Emergency Management Agency and Hancock County in West Virginia." The Licensee notified the NRC Resident Inspector. Notified R1DO (Welling), NRR EO (Miller), and IRD MOC (Gott). Notified DHS SWO, FEMA Ops Center, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-01-27
52512 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2017-01-25 17:45 | 2017-01-26 15:54 | 2017-01-26 | FITNESS FOR DUTY POLICY VIOLATION A contract employee had a prohibited item in the Protected Area. The employee's access to the site has been restricted. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.719 |  |  |  | 0 | 2017-02-03
52511 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2017-01-26 03:00 | 2017-01-26 11:26 | 2017-01-26 | CONTAINMENT VALVES FAILED SURVEILLANCE TESTING "On January 25, 2017, at 1800 CST, during planned surveillance testing, the Drywell Vent Line Inboard Isolation valve, CV-4302, was found to exceed its valve leakage limits and was declared inoperable. After completion of repairs to CV-4302, post maintenance testing showed that the Drywell Vent Line Outboard Isolation valve, CV-4303, was exceeding its valve leakage limits, and therefore, was declared inoperable at 0300 CST on January 26, 2017. This resulted in a containment penetration flow path not within purge valve leakage limits and is reportable in accordance with 10 CFR 50.72(b)(3)(v)(C). "Repairs were completed on CV-4303 and both containment valves were declared operable at 1007 CST on January 26, 2017. Secondary Containment was operable at all times. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-01-26
52510 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-01-25 18:36 | 2017-01-26 03:11 | 2017-02-03 | HIGH PRESSURE CORE SPRAY SYSTEM DIESEL ROOM FAN MOTOR FAILURE "On January 25, 2017, at 1836 PST, smoke was detected in the High Pressure Core Spray System (HPCS) diesel room with no indication of a fire. Investigation found the motor starter coil for DMA-FN-32 (Diesel Mixed Air Fan 32), HPCS diesel generator room normal cooling fan, failed. This fan is required for operability of the switchgear that powers the HPCS pump. The HPCS pump is currently inoperable due to maintenance being performed on other support systems. "This condition is being reported under 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. "The licensee has notified the NRC Resident Inspector." * * * RETRACTED ON 0036 EST ON 2/3/17 FROM QUOC VO TO JEFF HERRERA * * * "At the time of discovery HPCS was out of service in accordance with plant technical specifications, therefore the failure of the supporting equipment, DMA-FN-32, is not reportable under 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." Notified the R4DO (Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-01-26
52509 | 0 | KINROSS |  |  |  |  | 2017-01-24 14:30 | 2017-01-24 19:40 | 2017-01-24 | STUCK OPEN SHUTTER During the semi-annual inspection, the licensee discovered that the shutter on a fixed density gauge would not close. The gauge is used to monitor slurry flow at a gold mining operation and the shutter is normally open. The gauge remains in operation and does not present a safety concern to personnel. There are no exposures involved with this event. The licensee has notified the manufacturer of the gauge to request that an authorized technician repair the shutter. The gauge is Ronan SA-1 Density Gauge containing a Cs-137 1000 mCi source, Serial # M4884. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-02-01
52508 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2017-01-24 10:00 | 2017-01-24 14:00 | 2017-01-24 | SECONDARY CONTAINMENT INTERLOCK DOORS OPEN SIMULTANEOUSLY "On January 24, 2017, at 1000 hours [CST], Operations was notified that two Secondary Containment interlock doors (between the Unit 2 Reactor Building and Unit 2 Turbine Building) were open simultaneously. The doors were immediately closed and Secondary Containment pressure remained negative. Unit 1 and Unit 2 share secondary containment. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2 given two doors in a single access opening were open. As a result, entry into Technical Specification 3.6.4.1, Condition A. was made momentarily due to Secondary Containment being inoperable. "This event is reportable under 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Senior Resident Inspector has been notified." The cause of this event was due to an equipment interlock (solenoid) failure and the doors are currently blocked closed. | 98 | 100 | 0 | 98 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-01-24
52507 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2017-01-12 | 2017-01-23 15:11 | 2017-01-23 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the State of Nebraska via email: "[The licensee] contacted [the Nebraska Office of Radiological Health] on January 12, 2017. The licensee indicated that they purchased the theater from Perkins Delaware, LLC but were not informed of the Tritium exit signs or the related license. The licensee became aware of the signs and the related license when they received the annual renewal and related inventory. The licensee opted to dispose of the signs with SRB technologies. During the packing process, the licensee discovered two signs missing from the inventory and is unable to ascertain when they were lost." Lost Source Number: 1, Source/Radioactive Material: SEALED SOURCE LUMINOUS, Manufacturer: Isolite, Model Number: 2040, Serial Number: A4N1925, Radionuclide: H-3, 7.5 Ci 277.5 GBq. Lost Source Number: 2, Source/Radioactive Material: SEALED SOURCE LUMINOUS, Manufacturer: NRD, INC., Model Number: T4001, Serial Number: 61821, H-3, 25 Ci 925 GBq. Cause: Human Error. Corrective Action: None. The State of Nebraska considers this event to be closed. Nebraska Item Number: NE170001. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2017-01-31
52506 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-01-22 | 2017-01-23 12:27 | 2017-01-23 | AGREEMENT STATE REPORT - FIRE AT A URANIUM RECOVERY FACILITY The following report was received from the State of Texas via email: "On Sunday, January 22, 2017, at 1041 [CST], [the Texas Commission on Environmental Quality] CID [Critical Infrastructure Division] received a call from URI's Radiation Safety Officer [RSO], for the Kingsville Dome facility, that a fire occurred on the west side of well field 17 in Production Area 3, on Sunday morning, January 22, 2017. [The RSO] stated the cause of the fire appeared to be a cigarette butt. A URI operator working at the site noticed the fire. When the operator arrived at the fire location, he noticed that the fire department (FD) was already putting out the fire. At the time of the call, according to [the RSO], the fire was under control and the FD was making sure to put out the hot spots. At the time of the fire, the well field was on a shutdown status and there were no other activities at the well field. The preliminary findings were damage to some of the well field fences and wells in the well field." The extent of damage is still being evaluated and there are no reports of contamination or exposures, outside of the facility, at this time. The URI, Inc., Kingsville Dome is an In-Situ Uranium Recovery facility in Texas. Texas Report Number: None assigned at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-01-31
52505 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2017-01-23 08:06 | 2017-01-23 10:34 | 2017-01-23 | MANUAL REACTOR SCRAM DUE TO STATOR WATER COOLING RUNBACK SIGNAL AND TURBINE BYPASS VALVE OPENING "This notification is being provided pursuant with 10 CFR 50.72 (b)(2)(iv)(B). "[On January 23, 2017] at 0806 [CST], Unit 2 Manual Scram was inserted due to a Stator Water Cooling runback signal and a Turbine Bypass Valve opening. The Plant is stable, reactor pressure is being maintained with Bypass valves. Reactor water level is being controlled with feedwater. Investigation into the cause of the event is in progress." All control rods fully inserted. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-01-23
52504 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-01-19 | 2017-01-23 08:53 | 2017-01-23 | AGREEMENT STATE REPORT - RECEIVED DOSE LESS THAN PRESCRIBED DOSE The following is excerpted from an email: "On January 20, 2017 the licensee informed the Department [Pennsylvania Department of Environmental Protection Bureau of Radiation Protection] of an under dose incident involving yttrium-90 (Y-90) TheraSpheres. It is reportable as per 10 CFR 35.3045(a)(1)(i). "On January 19, 2017 a patient underwent a Y-90 TheraSphere treatment. The staff reported the procedure went as planned; however, upon surveying the waste and performing a dose calculation it was found that the patient received approximately 29% of the prescribed dose. The patient was notified of this under dose on January 20, 2017. The physician utilized contrast medium to view the flow prior to the procedure and no issues were seen. No increased resistance was noted and the physician was able to flush the line post administration. The manufacturer was notified and will be conducting a joint investigation with the hospital staff. No harm is expected to the patient. "A reactive inspection is planned by the Department. More information will be provided upon receipt. "PA Event Report ID No: PA 170001" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-01-31
52503 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2017-01-22 14:00 | 2017-01-22 16:19 | 2017-01-22 | WELD DEFECT FOUND DURING A SHUTDOWN INSPECTION "Information from a Manual Phased Array UT (Ultrasonic Testing) examination of the 'A' RHR LPCI [Residual Heat Removal Low Pressure Coolant Injection] Injection Loop indicates an axially oriented indication 0.95 inch in length and 0.81 inch through wall. This is on weld number 24-10-130 (T to Valve dissimilar metal weld). "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii)(A) based on the fact that the indications result in a defect in the primary coolant system which cannot be found acceptable under ASME Section XI. "The licensee informed the NRC Resident Inspector." The weld is located where the RHR piping taps into the reactor vessel. The wall thickness at this location is 1.15 inches. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-01-22
52502 | -1 | C&D TECHNOLOGIES, INC. |  |  |  |  | 2016-11-23 | 2017-01-20 16:01 | 2017-03-20 | PART 21 - PLASTIC JAR DEDICATION SAMPLING The following is an excerpt of a part 21 received via email: "The purpose of this letter is to provide the NRC an interim report in general conformity to the requirements of 10CFR Part 21.21 (a)(2). During an internal audit in November 2016, the sampling plan for dedication of plastic jars used in 1E battery cells was reviewed. Two lot numbers are associated with each plastic jar, a material lot number and a molding number. A material lot may encompass several molding lots. The dedication sampling plan was based on the material lot, and may not have properly sampled variations in critical characteristics generated by molding lots. An analysis of historical data is underway to determine whether any deviations to specifications for critical characteristics may have occurred, and whether these possible deviations could represent a defect as defined by Part 21. C&D expects that this analysis will be completed by March 20, 2017. The facilities where the components have been supplied are: Arkansas Nuclear One, Limerick, Beaver Valley, Millstone, Braidwood, Monticello, Browns Ferry, Nine Mile Point, Byron, Oconee, Clinton, Palisades, Columbia, Perry, Cook, Point Beach, Cooper, Prairie Island, Crystal River, River Bend, Diablo Canyon, Robinson, Duane Arnold, Salem, Farley, Sequoyah, Fermi, St. Lucie, Fitzpatrick, Summer, Ft. Calhoun, Susquehanna, Grand Gulf, Three Mile Island, Harris, US Navy, Hatch, Vogtle, Hope Creek, Vermont Yankee, Indian Point, Waterford, Watts Bar, LaSalle "If you have any questions or wish to discuss this matter or this report, please contact "Robert Malley VP Quality and Process Engineering bmalley@cdtechno.com (215) 619-7830" * * * RETRACTION ON 3/20/17 AT 1602 EDT FROM ROBERT MALLEY TO DONG PARK * * * The following is an excerpt of a part 21 received via email: "Based on this review the Interim Report (NRC Log No. 2016-00-06) dated January 20, 2017 is retracted. If you have any questions or wish to discuss this matter, please contact "Robert Malley VP Quality and Process Engineering bmalley@cdtechno.com (215) 619-7830" Notified R1DO (Bickett), R2DO (Ernstes), R3DO (Orlikowski), R4DO (Drake), Part 21/50.55 Reactors group, and Part 21 Materials group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-01-20
52501 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2017-01-20 08:35 | 2017-01-20 16:02 | 2017-01-20 | FAILURE OF A SECONDARY CONTAINMENT DOOR TO CLOSE "At 0835 [EST] on January 20, 2017, at Millstone Power Station Unit 3, subsequent to personnel passage through a door in the auxiliary building, the door failed rendering it unable to completely close. At this time, in accordance with Technical Specification 3.6.6.2 "Secondary Containment," the Shift Manager declared the secondary containment inoperable. The door was repaired and the door completely closed at 1256 [EST] on January 20, 2017, and secondary containment was declared operable. "Since Secondary Containment was rendered inoperable, Dominion is reporting that this condition could have prevented the fulfillment of the safety function to control the release of radioactive material and mitigate the consequences of an accident. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D). "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-01-20
52500 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-01-19 13:00 | 2017-01-20 15:04 | 2017-01-20 | AGREEMENT STATE REPORT - INCORRECT DRUG DELIVERED TO PATIENT The following was received via E-mail: "The North Carolina Radioactive Materials Branch (RMB) is submitting a report of a possible Medical Event reportable under 10 CFR 35.3045(a)(2)(i). Specifically, a dose was delivered to a patient with an effective dose equivalent (50 rem) to an organ through the administration of a wrong radioactive drug containing byproduct material. The RMB received the report of the possible Medical Event on 1/19/2017. "NC Licensee Duke University, License 0247-4, reported to the RMB that around 1300 EST on 1/19/2017 a patient scheduled for a thyroid uptake scan in the Diagnostic Nuclear Medicine Department was incorrectly identified and received an oral dose of 2.0 mCi of Iodine-123 instead of the intended dose of 5-12 microCi of Iodine-131. "An investigation was held on 1/20/2017 with members of Duke University to include the individual that delivered the incorrect dose to the patient. Following a review of the licensee's current procedures, it was noted that there is a minimum of two methods of patient verification prior to the administration of any diagnostic radioactive drug to any patient. An interview was conducted with the CNMT [Certified Nuclear Medicine Technologist] that delivered the incorrect dose and they freely admitted to not following the proper protocol which consists of confirming the Name and Date of Birth of the patient. Other factors may have attributed to this misadministration to include the volume of patients being treated that day and that there were two patients present that day with very similar first and last names. The patient with the similar name received the proper dose for their procedure. "Following interviews with Duke personnel, it was determined that the CNMT received the proper training to adhere to this two factor authentication as dictated by internal procedures and was authorized under an approved AU for such uses. At this time, it appears the cause for this misadministration is due to human error. "This investigation is ongoing and more details are to follow to update this report. Several records were requested of the licensee to include a dose assessment to verify the EDE of 50 rem or any excess of 50 rem delivered to the organ. The licensee is compiling it's 15 Day Report and will be providing it to the RMB as required by the Rule. Following receipt of that report, this event will be updated." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-01-30
52499 | 0 | GEO ENGINEERING & TESTING INC |  |  |  |  | 1988-01-01 | 2017-01-20 03:52 | 2017-01-20 | LOST/MISPLACED MOISTURE DENSITY GAUGE A Troxler moisture density gauge was last leak checked in 1988. The gauge handle was damaged by construction equipment and put aside sometime between 1988 and 1990. The current location of the gauge is unknown. Troxler Model 3411B Serial Number 8117 Sources: Cs-137 10 mCi and Am-241 60 mCi THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | GU | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-02-03
52498 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-01-19 | 2017-01-19 11:50 | 2017-01-19 | AGREEMENT STATE REPORT - SHUTTER STUCK CLOSED ON FIXED NUCLEAR GAUGE The following information was provided by the State of Texas via email: "On January 19, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that the shutter on a Ronan model SA1-F37 gauge, S/N 5432GK containing a 50 millicurie cesium - 137 source would not open during an inspection. The RSO stated the gauge does not create an exposure risk to their employees or any member of the general public. The RSO stated a service provider has been contacted to repair the gauge. Additional information will be provided in accordance with SA-300. "Texas Incident #: I-9459" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-01-27
52497 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2017-01-18 11:34 | 2017-01-19 10:12 | 2017-01-19 | VIOLATION OF TECHNICAL SPECIFICATIONS During startup of the reactor with reactor power less than one kilowatt, one of the two required reactor period channels was deenergized. Technical Specification 3.2.3 requires that the reactor shall not be made critical unless there are two such operable channels. For a period of approximately 10 seconds one of the operators inadvertently lifted the wrong cable. The operator identified the error and realized Technical Specifications had been violated. The reactor was shutdown at 1134 EST. An evaluation was performed to identify corrective actions. A labeling issue was identified which contributed to the incident. The licensee notified the NRC RTR Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MA | NPR | [5 empty] | 0 | 2017-01-19
52496 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2017-01-18 20:56 | 2017-01-19 00:39 | 2017-01-19 | BOTH SECONDARY CONTAINMENT AIRLOCK DOORS OPEN SIMULTANEOUSLY "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(C), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and 10 CFR 50.72(b)(3)(v)(D), event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. An employee entered a secondary containment interlock [airlock] and identified that both doors of the interlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the interlock and notified the Main Control Room Supervisor. Both doors in the interlock were open for approximately five seconds. With both doors open, TS SR 3.6.4.1.2 was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor Building differential pressure, as observed in the Main Control Room has remained less than -0.25 in. H2O at all times. Initial investigation determined that the interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the interlock." The licensee notified the NRC Resident Inspector. Notified R3DO (McCraw). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-01-19
52495 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2017-01-17 21:30 | 2017-01-18 10:04 | 2017-01-18 | FAILURE OF THE REGULATING BLADE TO MOVE "On 1/17/17 at 2130 CST, the MURR [University of Missouri Research Reactor] was shut down due to the failure of the regulating blade to move. This email is a required notification per MURR TS 6.6.c.(1) to report to the NRC Operations Center that an Abnormal Occurrence as defined by MURR TS 1.1 happened. Specifically, MURR was not in compliance with all Limiting Conditions for Operations (LCOs). MURR was not in compliance with the LCO TS 3.2.a. which states, 'All control blades, including the regulating blade, shall be operable during reactor operation.' The regulating blade was repaired, and the required compliance procedure was conducted on the regulating blade prior to the reactor being started up on 1/18/17. Currently, MURR is again at 10 MW. A detailed event report will follow within 14 days as required by MURR TS 6.6.c.(3)." The reactor was at 10 MW power when this event occurred. The cause of this event is under investigation. The licensee notified the NRC RTR Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2017-01-18
52494 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-01-17 08:00 | 2017-01-17 14:04 | 2017-01-17 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received via E-mail: "The general license section of the [Colorado Department of Public Health and Environment] Radioactive Materials Program sent out annual notifications requesting response regarding tritium exit signs reported in use at locations given by the manufacturer. Upon an audit of the annual mailing for non-responders, Cintas First Aid & Safety was contacted. The contact at Cintas Fire & Safety explained they had moved from the event location and provided a new address. According to the contact since 6 years have passed and due to the move to a new location records from 2010 are no longer available. The contact was not able to confirm if the tritium exit sign was installed in the building or sold to one of their companies they provide service to. "Isolite was contacted to obtain information from a purchase order number provided on the manufacturer report. According to Isolite, the tritium exit sign was ordered through Grainger (PO# 4604805115). No information was provided showing any other address other than the event location. The lost tritium exit sign is model #SLX60, Serial Number 10-225-10, Isotope H-3, Activity 8.1 Curies, It was shipped 8/5/2010 from Isolite's Pennsylvania location. "Cintas First Aid & Safety has been requested to provide a corrective action regarding the lost/abandoned tritium exit sign." Colorado Event Report ID No.: CO17-0003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-01-25
52493 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-01-16 | 2017-01-17 10:36 | 2017-01-17 | AGREEMENT STATE REPORT - RADIOGRAPHY DEVICE DAMAGED The following information was received via E-mail: "On January 17, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that on January 16, 2017 at 0200 CST a source retrieval had been completed. The source was Ir-192, 94 curies, serial number YA0408, used in a Spec 150 radiography device. The licensee reported that piping being imaged fell from the holding stand onto the guide tube crushing it and causing the source to become stuck and non-retractable. The radiographers called the radiation safety officer (RSO) who after several unsuccessful attempts to open the guide tube had to cut the source from the cable and placed it into the device with long reach tongs. No member of the public was exposed and the RSO maintained his exposure to not exceed regulatory limits. The licensee stated the device was taken out of service and will supply a detailed report of the incident. Additional information will be provided as it is received in accordance with SA300." Texas Incident #: I-9457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-01-25
52492 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2017-01-16 11:55 | 2017-01-16 16:39 | 2017-01-16 | FAILURE OF REACTOR BUILDING ISOLATION DAMPERS TO ISOLATE "On January 16, 2017, with the reactor at 100 percent and the mode switch in RUN, Pilgrim Station was performing preventative maintenance of secondary containment isolation dampers when dampers AO-N-82 and AO-N-83, refueling floor supply isolation dampers, failed to fully close when the control switches were taken to close. "This 8-hour non-emergency notification is being made in accordance with 10 CFR 50.72(b)(3)(v), Any event or condition that at the time discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. "The reactor building isolation dampers were cleaned and lubricated and post-work tested and timed in accordance with station procedures to verify that they had satisfactory closing times. Pilgrim Nuclear Power Station has returned the dampers to Operable status. "The licensee will notify the Commonwealth of Massachusetts." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-01-16
52491 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2017-01-16 09:15 | 2017-01-16 15:55 | 2017-01-16 | FITNESS-FOR- DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the site has been terminated. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2017-01-16
52490 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2017-01-14 06:13 | 2017-01-14 13:09 | 2017-01-14 | DEGRADED CONDITION DUE TO THROUGH-WALL LEAK "At 0613 EST on 1/14/2017, with the unit in Mode 2 at 0 percent power at the start of Refueling Outage 22, Drywell inspection identified a through-wall leak on the 3/4-inch vent line off the bonnet of valve 02MOV-43A, Reactor Water Recirc Pump A Suction Isolation Valve, in the Reactor Coolant System (RCS) loop inside the Primary Containment. This condition constitutes a defect in the primary coolant system. "This event notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A) as a condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-01-14
52489 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-01-10 | 2017-01-13 16:46 | 2017-01-13 | AGREEMENT STATE REPORT - DENSITY GAUGE WITH STUCK OPEN SHUTTER The following report was received from the State of Louisiana via email: "Event type: Level density gauge on a process had a shutter malfunction. Eagle was performing their annual operational checks when the malfunction was discovered. The malfunction is the gauge shutter is stuck in the open position on an active process. The gauge Service Company, BBP Sales will make the repair or replacement after the assessment of the device. They discovered the shutters would not close. The Gauge is a RONAN SA1-C-10 device/source holder, S/N 9527GG, loaded with a 200 mCi Cs-137 source. "Notifications: LDEQ [Louisiana Department of Environmental Control] was notified by Eagle US 2 in a message on the voice mail system on 1/10/2017. The notice was sent to the Compliance Radiation Assessment Section of LDEQ. The notification was readdressed when Eagle was contacted on 1/12/2017, to get the preliminary information report. Eagle US 2 will send LDEQ a corrective action and a final report no later than 30 days of the corrective action. The Eagle US 2 preliminary written report was received 1/12/2017 at 1457 CST. "Event description: On 1/10/2017, Eagle US 2 was performing their annual inventory and operational checks of their licensed devices. During their routine annual maintenance checks, the shutter malfunction was discovered. The gauge shutter would not close. "Eagle US 2 called a service contractor, BBP Sales, to evaluate the situation and determine the best course of action to correct the problem. [The contractor] was unable to close the shutter and will determine the course of corrective action. The cause appears to be the corrosive environment where it [the gauge] is installed and used. "The source and device with shutter stuck open will remain installed and utilized on the process until the repairs are made. This is not a radiation exposure hazard and does not pose a health and safety situation for the Eagle US 2 employees or the general public. "This event is considered closed by LDEQ. This event is being reported to the NRC as required by Regulatory Requirement 10 CFR 30.50(b)(2)." Event Report ID No.: LA-17001. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-01-23
52488 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2017-01-12 13:00 | 2017-01-13 15:32 | 2017-01-13 | AGREEMENT STATE REPORT - LEAKING BARRELS CONTAINING RADIOACTIVE MATERIAL The following report was received from the State of Utah via email: "DWMRC [Division of Waste Management and Radiation Control] was notified of the event at about 1500 MST, on January 12, 2017. The licensee indicated that the shipper, Honeywell (Converdyne) had notified the NRC and the US DOT. This incident report is the initial notification of the NRC Operations Center from the DWMRC. "The following description is the initial information received by DWMRC. The information will be updated as the Division obtains more information. "A van carrying [three] barrels of [solid and wet] radioactive materials was received at the White Mesa Mill. When the employees were unloading the van they realized that a barrel, maybe two, had rusted bottoms and was leaking. Although the bottom of the barrels were not rusted through, they were characterized as 'being soft'. The barrels were on plastic sheeting that should have restricted the leaking materials to the plastic; however, when the barrels were unloaded, the employees noted that there was a hole in the sheeting. When the RSO was informed of the incident and arrived at the van, he noted that there was visible leakage on the girders and the siding of the van. Unfortunately, he was unable to take measurements of the area where the leak occurred to determine the radiation levels. The RSO [Radiation Safety Officer] stated that the van had been pulled in and cleaned prior to any measurements being taken, so the only measurements were taken after the van was cleaned." * * * UPDATE FROM GWYN GALLOWAY TO JOHN SHOEMAKER, VIA EMAIL, AT 1830 EST ON 1/13/17 * * * "On January 12, 2017, at approximately 1142 MST, a TAM International van carrying barrels of KOH alternate feed materials from Honeywell International arrived at the White Mesa Mill Scale house. According to Honeywell the materials are basically uranium ore concentrates. The White Mesa employees began unloading the van, but as they began offloading some of the last barrels, they noticed that some of the barrels were leaking. From what they could tell, three barrels were potentially leaking . The barrels were not rusted through, but were 'soft' and allowed liquid contained in the solid materials to leak from the barrel. The material leaked from the barrel onto a plastic sheet; however, the plastic sheet had an opening (rip, tear) through which the material was able to pass. The RSO [Radiation Safety Officer] was notified of the event at about 1300 MST. "When the RSO reached the van, the employees had completed emptying the van and had 'cleaned' the van. The RSO indicated he was able to see visible evidence that the material had been able to leak from the van, but the area had been cleaned and no valid measurements or samples of the materials leaked from the van were able to be taken. Pictures were taken and from the pictures provided to the Division [Utah Division of Waste Management and Radiation Control], it appears that only a small quantity of liquid material was leaking from the barrels. Because the contents of the barrels are primarily solid and only contain small amounts of liquid and the liquid contents in the barrels were leaking through the bottom of the barrel, through a plastic sheet, across the van floor and out of the van along a girder and the siding, it is likely that only small quantities of materials were leaking from the van. The weather across the nation has been fairly stormy this past week and has included both rain and snow. Because of the rain and snow that has been occurring while the vehicle was traveling to the Mill site, it is likely that any small amounts of materials that leaked from the van were subsequently washed away and diluted. The Mill analyzes each alternate feed stream annually to verify the isotopic content of the alternate feed. At the last verification, the Honeywell KOH material contained, approximately 633,000 mg/kg uranium (about 61% uranium), 39 pCi/g Pb-210, 44.6 pCi/g Ra-226, 358 pCi/g Th-230, and 27 pCi/g Th-232." This event was also reported by National Response Center to the Nuclear Regulatory Commission , Report # 1168447, on 01/12/17 at 1720 EST. Utah Event Number: UT170001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2017-01-23
52487 | 0 | CURTISS WRIGHT ELECTRO MECHANICAL C |  |  |  |  | 2017-01-12 | 2017-01-13 13:56 | 2017-06-29 | PART 21 INTERIM REPORT - EXCESS MATERIAL CONDITION ON THE CASING FOR THE AP1000 REACTOR COOLANT PUMP The following summary was excerpted from report #EMD-GM-17-02, provided by the Curtis-Wright Electro-Mechanical Corporation: "Curtiss-Wright Electro-Mechanical Corporation (CW-EMD) has identified a condition which is currently being evaluated to determine if a significant safety hazard exists in the casing for the AP1000 Reactor Coolant Pump (RCP). The investigation is underway, but will not be completed within the required 60 days from discovery as required by paragraph 21.21(a)(1) of the regulation. This submission constitutes CW-EMD's interim report on the condition in accordance with paragraph 21.21(a)(2) of the regulation. "Casings for the AP1000 Reactor Coolant Pump. The casings have an excess material condition in the transition region between the cast bowl and the suction nozzle. The condition is a discontinuous (non-tangential) axisymmetric feature between the cast bowl region and machined suction nozzle OD. The as-built transition feature on the casings has not been analyzed and is not included in CW-EMD Engineering Memorandum 7242, Revision 1, Volume 1, which is the applicable generic design report for the AP1000 RCP casing and main closure. "At present, the following domestic deliveries have been made: - 8 casings have been provided to V.C. Summer Units 2 and 3. - 8 casings have been provided to Vogtle Units 3 and 4. "Name and address of the individual or individuals informing the Commission: Brian W. Eckels, General Manager Curtiss-Wright Electro-Mechanical Corporation 1000 Wright Way Cheswick, Pa 15024" * * * UPDATE AT 1238 EDT ON 06/29/17 FROM JAY GARDINER TO JEFF HERRERA * * * The following update was received via email: "Curtiss-Wright Electro-Mechanical Corporation (CW-EMD) submitted an interim report concerning a deviation in the AP1000 Reactor Coolant Pump casing via letter EMD-GM-17-02, dated January 12, 2017. This letter updates the status of the investigation. "1. Extent of condition evaluation has been completed. CW-EMD has confirmed that the discontinuous (non-tangential) axisymmetric feature between the cast bowl region and machined suction nozzle OD is limited (domestically) to the 8 AP1000 RCP casings delivered to V.C. Summer units 2 & 3. "2. AP1000 RCP casing stress and fatigue supplemental analyses have been performed to assess the excess material condition discovered on the suction nozzle OD. The deviation has been determined to still satisfactorily meet the pressure boundary stress requirements of the ASME Code and can therefore be accepted as-is. "3. The analysis included generation of a 2D axisymmetric FEA [Finite Element Analysis] of the casing with a bounding representation of the as-built geometry, based on extraction of cross-sectional profiles from the V.C. Summer laser scan data of 2 casings. The 2D FEA was used to determine the stress concentration factor(s) associated with the as-built deviated feature, enabling a fatigue strength reduction factor to be estimated and applied to the existing 3D FEA casing fatigue (nominal design) analysis. "4. The maximum fatigue usage at the location of the deviation on the casing suction nozzle was conservatively estimated to increase from 0.287 to 0.633. This condition still satisfies the 1.0 usage limit specified in the ASME Code. "5. Therefore, this deviation does not constitute a substantial safety hazard, and the condition has been determined to be not reportable under the provisions of Title 10 Code of Federal Regulations, Part 21." Notified the R2DO(Bartley) and Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-01-13
52486 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2017-01-12 14:00 | 2017-01-12 18:25 | 2017-01-12 | FITNESS-FOR-DUTY TEST POSITIVE FOR NON-LICENSED SUPERVISOR "A non-licensed supervisor has been found in violation of the Duke Energy Fitness for Duty Policy during a random fitness for duty test. The individual's access to the plant has been suspended. "The licensee has notified the NRC Senior Resident Inspector." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2017-01-12
52485 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-01-12 13:00 | 2017-01-12 16:35 | 2017-01-12 | AGREEMENT STATE REPORT - LOST GAS CHROMATOGRAPH The following report was received from the State of Colorado via email: "Detail: Wibby Environmental sold the business to Phenova in 2010. Through a long process of trying to reach the company contact at Wibby, contact with Phenova was made in February of 2016. After several attempts to discover what occurred with the assets of Wibby Environmental, one device is being reported as lost/abandoned. According to Phenova they do not see the gas chromatograph as being on the asset sheet at the time of purchase. "It is unknown as to what Wibby Environmental did with the device or if the device was returned for disposal. Our office has received no records from manufactures including CJ Bruyn & Company, showing the Gas Chromatograph was returned. "Device information: Model # N610-0133 Source SN# 0767, NI-63, 15 mCi, Date shipped from CJ Bruyn 02-27-2004. "Event Description: Due to the length of time for discovery this case is closed." Colorado Event Report ID No.: CO 17-0002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-01-20
52484 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-01-11 15:00 | 2017-01-11 16:56 | 2017-01-11 | TEFLON FOUND IN CONTAINMENT SPRAY PUMP COMPONENTS "On September 16, 2016, Comanche Peak reported an unanalyzed condition and potential loss of safety function per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v) related to Teflon (PTFE) installed in the pressure gauge diaphragm seal assemblies for all four of the Centrifugal Charging Pumps and both of the Positive Displacement Charging Pumps on Units 1 and 2 (EN#52244). On November 14, 2016, this event was subsequently retracted. "On December 12, 2016, during the ongoing extent of condition review, Teflon was also found to be installed in the suction and discharge pressure gauge diaphragm seal assemblies for the Unit 1 and 2 Containment Spray Pumps. On January 11, 2017 at approximately 1500 CDT, the reportability evaluation determined that reasonable assurance did not exist that the Containment Spray system would have been able to fulfill its design function of removing heat from the containment environment without impacting the applicable dose limits. "Teflon (PTFE) is a restricted material normally prohibited from use in contact with reactor coolant or in radiation environments. Teflon (PTFE) is not radiation tolerant and degrades in a radiation environment. The Teflon (PTFE) used in these diaphragm seal assemblies could fail during a postulated Loss of Coolant Accident (LOCA) which could cause the Containment Spray Pumps on Units 1 and 2 to be inoperable, and exceed system leakage limits. This could challenge dose limits and in plant post-accident accessibility. This represents an unanalyzed condition. The pressure gauges and diaphragm seals for all of the Unit 1 and 2 Containment Spray Pumps have been isolated and the Unit 1 and 2 Containment Spray Pumps are operable. The Teflon (PTFE) has likely existed in these diaphragm seals since initial plant licensing. Luminant Power is continuing to investigate the extent of this condition and potential repair techniques. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-01-11
52483 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-11-23 10:30 | 2017-01-11 16:06 | 2017-01-11 | AGREEMENT STATE REPORT - STOLEN THEN RECOVERED LICENSED MATERIAL The following information was received via facsimile: "Licensee notified the Department on 11/23/16, of the theft of an RMD LPA-1 Lead-Paint Analyzer containing 12 milliCuries of Cobalt-57 (Device S/N 3447R). The theft occurred at approximately 1030 EST on 11/23/2016 at a temporary jobsite located at 40-01 Vernon Boulevard, Queens, New York 11101. "According to the licensee, the authorized user realized the device was missing shortly after departing the jobsite. He recalled putting the protective case containing the XRF [X-Ray Fluorescence Lead Paint Spectrum Analyzer] on the ground next to his vehicle to access his vehicle keys. Soon after, he was distracted by a pedestrian asking for directions and stepped into his vehicle to travel to the next jobsite without the device. He immediately returned to the previous site to search for the device. He was unsuccessful in his search. "After filing a report at the local police department, the authorized user returned to the jobsite. He was informed by the maintenance department that there was video surveillance at that location and was provided a copy of the tape. This video showed two men walking away with the XRF protective case from the location where the authorized user's vehicle was originally parked. The licensee indicated that fliers were put up in the neighborhood where the device was originally stolen with a reward for the safe return of the XRF. "On December 8, 2016, the Radiation Safety Officer (RSO) notified the Department [New York State Department of Health] that someone had contacted their office claiming to have the stolen XRF in their possession. The RSO verified it was the correct device by the S/N and arranged to retrieve the device the next day. Two of the Licensee's authorized users met the individual at the previously agreed upon location, paid the negotiated reward, and retrieved the device. The XRF and XRF accessories appeared to be in perfect condition." New York Event Report ID No: NY-17-02 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-01-19
52482 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2017-01-11 10:58 | 2017-01-11 13:52 | 2017-01-11 | FITNESS-FOR-DUTY TEST POSITIVE FOR NON-LICENSED SUPERVISOR A non-licensed supervisor tested positive for alcohol during a for-cause test. The individual's access to the site has been terminated pending the results of an investigation. The licensee notified RII (Patterson) and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2017-01-11
52481 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2017-01-10 20:40 | 2017-01-10 22:50 | 2017-01-10 | OFFSITE NOTIFICATION "On January 10, 2017, at approximately 2040 EST, a spill to the environment was determined to be reportable to state environmental and local health agencies. A press release is planned. "The spill occurred when a portable chemical toilet tipped over and was identified at approximately 2040 EST. The quantity of the spill is estimated to be five gallons. The spill contacted the ground but did not reach any waterways or storm drains. Cleanup efforts are in progress. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-01-10
52480 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-11-10 16:04 | 2017-01-10 22:45 | 2017-03-23 | PART 21 - FAILURE OF POWER SUPPLIES TO MEET VOLTAGE STABILITY SPECIFICATIONS "This notification is a 10 CFR 21.21(a)(2) interim report for power supply model N-2ARPS-A6. Two instrument power supplies for the 'B' Residual Heat Removal (RHR) system were being bench tested prior to installation when it was discovered that they failed to meet Vendor Technical Manual specifications for voltage stability for varying loads. The deviation was a voltage drop of approximately 300mV. This did not meet the specification of less than 150mV when varying current from 5 amps (full load) to 2.5 amps. A second replacement power supply exhibited a similar 300 mV drop. "James A. FitzPatrick (JAF) reviewed the work order instructions to determine if there was a deviation from the recommendations in the Foxboro technical manual F180-0309 Spec 200 Multinest Power Supply 2ARPS Series calibration. Since as-found voltage readings were within the required tolerance of the RHR instrument loops, the power supplies appear to have been capable to perform their intended function. However, this evaluation did not troubleshoot why the power supplies failed to meet the calibration requirements. "The power supplies were sent to a repair vendor. The input from this vendor is expected to allow JAF to complete the evaluation per 10 CFR 21.21(a)(1) by March 21, 2017, and a notification for failure to comply or defect per 10 CFR 21.21(d)(3)(i) is expected by March 24, 2017, if necessary. This notification is being submitted as an interim report per 10 CFR 21.21(a)(2)." The licensee notified the NRC Resident Inspector. * * * RETRACTED AT 1705 EDT ON 03/23/17 FROM MARK HAWES TO S. SANDIN * * * The licensee is retracting this report based on the following: "The testing vendor Argo Turboserve Corp provided input to this condition in Non Conformance Report NC161. Engineering reviewed NC161 and discussed this condition with the vendor. The power supplies showed an initial drift following a 100 hour burn-in but continued operation was stable. Therefore, even though the initial voltage drift did not meet the power supply's calibration requirement in F180-0309, it would not be expected to drift significantly further. Engineering concluded that this condition will have a negligible impact on system components. Readings were steady and within the tolerance of the RHR instrument specification. Based on all current information, the component will function over its mission time of 100 days. "Based on these results, a notification for failure to comply or defect per 10 CFR 21.21(d)(3)(i) is not required and the interim report per 10 CFR 21.21(a)(2) may be retracted." The licensee informed the NRC Resident Inspector. Notified R1DO (Bickett) and Part 21 Group via email. | 67 | 0 | 0 | 67 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INTERIM EVAL OF DEVIATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 21.21(a)(2) |  |  |  | 0 | 2017-01-10
52479 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2017-01-09 | 2017-01-10 09:56 | 2017-01-10 | ABNORMAL OCCURRENCE DURING MOVEMENT OF A REGULATING BLADE On Jan 09, 2017, during movement of a reactor regulating blade, an expected annunciator did not occur. This required entry into Technical Specification 3.2.F.8. The rod run in relay and contact block were replaced and the system tested satisfactorily. Technical Specification 3.2.F.8 was subsequently exited. The licensee will be notifying the Research and Test Reactor Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2017-01-10
52478 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2017-01-09 15:30 | 2017-01-09 16:56 | 2017-01-09 | EMERGENCY DIESEL GENERATORS NON-CONFORMING WITH LICENSING BASIS FOR TORNADO GENERATED MISSILES "On January 9, 2017, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornado generated missiles, Peach Bottom Atomic Power Station identified a non-conforming condition in the plant design such that specific TS equipment is considered to not be adequately protected from tornado generated missiles. A tornado could generate multiple missiles that could strike one or more of the four emergency diesel generator (EDG) exhaust stacks. This could result in crimping of the stack, which could affect the ability of the EDG to perform its design function if such a tornado would occur. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with NRC enforcement guidance provided in EGM 15-002 and DSS-ISG-2016-01. Compensatory measures have been implemented in accordance with these documents. "The NRC Resident Inspector has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-01-09
52477 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2016-11-12 | 2017-01-06 16:02 | 2017-01-06 | PART 21 - SEIZURE OF FUEL INJECTOR ON EMERGENCY DIESEL GENERATOR The follow is a summary of the Part 21 report that was received via fax: "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on November 12, 2016, following the seizure of a fuel injector at Entergy Operations Inc. - Arkansas Nuclear One (ANO). ANO had completed installation of new fuel injectors on both of their EMD emergency diesel generator sets. During post-maintenance surveillance testing the fuel injector installed in the #7 cylinder of unit K4A seized (injector S/N 16C2 3186). During an attempt to shut down the unit, operators were unable to reduce the engine's load because of the seized injector/fuel rack. "The seized fuel injector was then returned to ESI for failure analysis where it was received on November 16. The failure investigation determined that foreign material within the injector was the cause of the seizure. The report (8002768-FA) was completed on December 8, 2016, and submitted to the customer for review. "The root cause of the failure was determined to be foreign material which likely entered the fuel injector during manufacture/assembly. Once the injector was installed on the engine, it was during engine surveillance (run) testing that this foreign material migrated into the plunger and bushing assembly. This decreased the running clearance between the components which ultimately lead to seizure. "Component: EMD Fuel Injector, Part Number 40084720. "Entergy Operations Inc.- Arkansas Nuclear One is the only customer to whom ESI has supplied suspect fuel Injectors." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-01-06
52476 | 0 | BELLEFONTE |  | 2 |  | [1] B&W-R-LP (205),[2] B&W-R-LP (205) | 2016-12-06 | 2017-01-06 12:20 | 2017-01-06 | CONTAINMENT VERTICAL TENDON FAILED "During a routine inspection on December 6, 2016, Tennessee Valley Authority (TVA) found the Unit 2 Reactor Building Containment Vertical Tendon V281 rock anchor/tendon anchor coupling had failed. The anchor coupling appears to have sheared in the threaded portion allowing the anchor head for the vertical tendon and the anchor head for the rock anchor tendon to separate. TVA had inspected the failed tendon coupling on October 19, 2016, and identified no signs of component specific damage or improper installation creating the potential for an unknown common mode failure. "Cause of Deficiency: At this time, the cause for the failure of the V281 rock anchor/tendon anchor coupling is unknown. "Safety Significance: As noted previously, the cause for the failure of the V281 rock anchor/tendon anchor coupling is unknown. As a result, the extent of condition can not be determined at this time. If multiple containment tendons are found to be losing the capability to carry tendon design force, and this condition was left uncorrected, it could reduce the capability of the containment structure to perform its design function. TVA had previously completed an analysis of containment structure integrity considering a single tendon coupler failure as a result of a similar failure of a Unit 1 Reactor Building Containment Vertical Tendon V9 in 2009 and determined that the containment structure is maintaining its design capability. "Interim Action: Upon discovery on December 6, 2016, the following actions were taken by BLN [Bellefonte] personnel: Access to the Unit 2 tendon gallery was restricted. The area of the V281 tendon failure was subsequently cleaned. Grease samples were obtained and sent to TVA Central Labs for analysis. The couplings from both the rock anchor and tendon anchor locations were removed and sent to TVA Central Labs for metallurgical analysis. Grease samples were also collected from adjacent tendons (V272 through V290) to evaluate if conditions are similar to tendon V281 samples. The failure was entered into the BLN Corrective Action Program (Condition Report 1239343). "Update Schedule: TVA plans to provide an update to this report by May 25, 2017 following the completion of the metallurgical and grease analysis." The Licensee has notified the NRC Construction Inspector (Baptist). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY | [9 empty] | NON EMERGENCY | 2 | AL | POW |  | 50.55(e) |  |  |  | 0 | 2017-01-06
52475 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-01-04 11:30 | 2017-01-05 09:26 | 2017-01-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received via e-mail: "Detail: Chateau Residence Club had a fire inspection that required the removal of two expired tritium exit signs. Encore Electric was contracted to remove the signs approximately around 10-13-16. According to Encore, the staff person performing the work tossed the exit signs in the trash. Encore Electric was informed by CDPHE [Colorado, Department of Public Health and Environment]/General License Coordinator to complete a corrective action to include tracking to disposal of all tritium exit signs, writing a report explaining their safety, handling and disposal of radioactive tritium signs. Colorado Rules and Regulations Pertaining to Radiation Control were provided to Encore Electric as guidance to complete the corrective action. "Manufacturer: Best Lighting Products aka Forever Light., Model Number: SLXYU1BB10, Serial Numbers: 215656 & 215657, Isotope: H-3, Activity: 7.09 Ci "Event Description: Due to the continuous lack of information from manufacturing companies reaching the responsible parties at the destination where exit signs are to be installed; companies have no understanding of the regulations for products containing tritium. The General License Coordinator at CDPHE provided the Chateau Residence Club management a copy of the Colorado Rules and Regulations Pertaining to Radiation Control and the NRC guidelines K & L. The Chateau Residence Club uses sub contractors for services like fire safety and lighting. Encore Electric was unaware of the regulations for Tritium Exit Signs." Event Report ID No.: CO17-0001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-01-13
52474 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-01-04 13:47 | 2017-01-04 20:07 | 2017-01-04 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for a prohibited substance during a random fitness-for-duty test. The individual's unescorted access to the plant has been denied. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2017-01-04
52473 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-12-29 | 2017-01-04 16:03 | 2017-01-04 | AGREEMENT STATE REPORT - MEDICAL EVENT The following report was received via fax: "We [New York State Department of Health] were informed on January 3, 2017 that on December 29, 2016, a 61 year old female patient was to receive SIR spheres Y90 infusion to 2 lesions in her liver at a hospital. The small lesion was to receive 10% and the large lesion was to receive 90% of 24.53 mCi Y90. "Staff prepared 2 vials according to the Written Directive, and labeled each vial shield. When the first infusion, for the smaller lesion, was called for, a technologist took one vial to the IR room. She believed she had the correct 10% marked vial. She removed the top of the shielded container holding the vial, then she left the IR suite. The patient was injected. When the second infusion, for the large lesion, was called for, the same technologist took the second shielded vial from the hot lab and noticed that it was the one marked with the 10% label. It appears that the vials themselves were not labeled, only the lids of the containers holding the vials were labeled. Once they realized what had happened, they decided to infuse the second larger lesion with what was left over in the first vial as well as what was in the second vial. The licensee has not yet provided the values for the actual administered dose to each lesion. However, it appears clear that the discrepancy in the prescribed activity and administered activity for each lesion meets the reportable medical event criteria. "[The licensee's] initial report stated there is no harm to the patient. A full report, including the actual activity delivered and a root cause analysis is required/pending." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-01-12
52472 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2017-01-02 12:52 | 2017-01-02 17:49 | 2017-01-02 | OFFSITE NOTIFICATION OF A MALFUNCTION OF TWO LASALLE COUNTY WARNING SIRENS "At approximately 1403 (CST) on January 2, 2017, LaSalle County Station was informed by the LaSalle County Sheriff that two warning sirens had malfunctioned at approximately 1252 earlier this afternoon. The warning sirens had inadvertently operated for nearly 3 minutes during maintenance at the LaSalle County 911 Communications Center. The warning sirens have been restored to standby and are fully functional. No other emergency notification systems or sirens were affected. "The licensee has notified the NRC Resident Inspector of the issue." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-01-02
52471 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-01-01 19:55 | 2017-01-02 15:21 | 2017-01-02 | FITNESS-FOR-DUTY A non-licensed employee had a confirmed positive for alcohol during a "for cause" fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2017-01-02
52470 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-12-23 | 2016-12-30 18:48 | 2017-01-17 | AGREEMENT STATE REPORT - MISADMINISTRATION DURING HIGH DOSE RATE PROCEDURE The following information was received via facsimile: "At approximately 1355 PST on Friday, 12/30/2016, Seattle Cancer Care Alliance called the Washington State Radioactive Materials Section to report a medical event. The event had occurred on Friday, 12/23/2016 but the date that the event was discovered was not provided. The summary of the event is as follows: An Ir-192 source was incorrectly positioned during an HDR procedure, resulting in a reduced dose to the treatment volume and an unintended dose to the surrounding healthy tissue. Limited information was provided by the licensee because they are still investigating the misadministration, but additional information will be provided in a follow-up conversation on Tuesday, 1/3/2017." Washington Incident Number: WA-16-049 * * * UPDATE ON 01/17/2017 AT 1714 EST FROM ANDREW HALLORAN TO STEVEN VITTO * * * The following was received via email from the State of Washington: "Patient was referred to SCCA [Seattle Cancer Care Alliance] for high dose rate (HDR) brachytherapy for treatment to a cervical lesion extending primarily on the left lateral side with upper to mid-vaginal involvement. Procedures were initially being developed to treat the patient with an interstitial Syed applicator. However, due to a medical condition that arose, the patient was no longer a candidate for this procedure. Therefore, the plan was to treat the patient with intracavitary brachytherapy, consisting of two fractions (1 & 2) with a tandem and ovoid (T&O) applicator set (because of a more favorable paracervical dose distribution provided by the T&O applicator configuration), and an additional two fractions (3 & 4) using the Miami cylinder applicator with tandem (to enable dose delivery to the vaginal target using the cylinder configuration). "The first two tandem and ovoid (T&O) HDR treatments (fx 1 & 2) were delivered as intended on 12/19/16 and 12/21/16. During the first fraction of the Tandem/Miami cylinder applicator (fx 3) delivered on 12/23/16, an incorrect tandem applicator length (119.8 cm) was entered into the treatment planning system instead of the 131.9 cm distance for the Miami tandem. This error was not caught prior to treatment delivery and the treatment dose in the tandem was offset by 12 cm inferiorly. The error was discovered prior to the 4th fraction being delivered on 12/29/16. The patient was notified of the error and the treatment was corrected and postponed to 12/30/16. "The intended dose to the cervical tumor volume for the 3rd fraction was 660 cGy, and the actual dose delivered for the fraction was 65 cGy to 90 percent of the target volume." Notified R4DO (Werner) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2017-01-09
52469 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-12-30 13:05 | 2016-12-30 16:37 | 2016-12-30 | MANUAL REACTOR TRIP DUE TO CONTROL ROD NOT WITHDRAWING AS EXPECTED "On 12/30/16 at 1302 EST, Unit 1 began withdrawing control bank rods for an approach to criticality following a refueling outage. At 1305 EST, operators observed that control rod H-6 did not withdraw. Operators entered the applicable Abnormal Operating Procedure. Operators tripped the reactor as required by plant procedures and entered applicable Emergency Operating Procedures. The act of manually tripping the reactor generated a valid trip signal in the plant Reactor Protection System. "Following the reactor trip, all safety related equipment operated as designed. Auxiliary feedwater was already supplying the Steam Generators; a Feedwater Isolation occurred due to plant conditions. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators, and decay heat removal via the steam dumps. "Method of decay heat removal is Steam Generators via the steam dumps. Current reactor coolant system conditions: Temperature at 548 degrees F and stable, pressure 2235 psig and stable. All control and shutdown banks are inserted. Electrical alignment is normal, supplied by offsite power. No impact to Unit 2, Unit 2 is in Mode 1 at 100 percent power." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-12-30
52468 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2016-12-28 22:29 | 2016-12-30 14:40 | 2016-12-30 | LOSS OF SAFETY FUNCTION DUE TO TWO INOPERABLE STANDBY LIQUID CONTROL SUBSYSTEMS "On December 28, 2016 at 2119 EST, the Standby Liquid Control system (SLC) subsystem A was declared inoperable in accordance with the surveillance instruction for performance of a routine surveillance test. At 2229 EST, control room operators received an out-of-service alarm for the explosive-actuated injection valve for SLC subsystem B and declared subsystem B inoperable, thereby rendering both subsystems inoperable. With both subsystems inoperable, the SLC system was unable to fulfill its safety function. At 2335, the surveillance was completed and subsystem A was restored to operable status, which restored the ability for the system to fulfill its safety function. "Troubleshooting determined that the cause for subsystem B inoperability was an intermittent electrical connection for the explosive-actuated injection valve. Repairs were conducted and the subsystem was restored to operable status on December 29, 2016 at 1708 EST. "This issue was entered into the Corrective Action Program and during post reportability review, it was determined that this was a reportable event under 10 CFR 50.72(b)(3)(v)(A) for an event or condition that could have prevented the fulfillment of a safety function of a system that is needed to shut down the reactor and maintain it in a safe shutdown condition and under 10 CFR 50.72(b)(3)(v)(D) for a system that was unavailable for accident mitigation. "The NRC Resident Inspector has been notified." | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-12-30
52467 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-12-29 | 2016-12-29 15:40 | 2016-12-30 | AGREEMENT STATE REPORT - APPARENT UNCONTAINED RADIATION SOURCE DETECTED The following information was received via facsimile: "On December 29, 2016, the Office of Radiological Health (ORH) was notified that radiation had been detected on a local law enforcement officer's personal radiation detector at the intersection of Route 123 and the I-95 southbound exit ramp in Woodbridge, Virginia. The Prince William County HazMat unit responded and identified the source as cesium-137 using a radioisotope identifier. The source was present in the grassy knoll in the median of the interchange. ORH and other agencies, including the Virginia State Police, Virginia Department of Emergency Management and FBI, participated in the initial investigation. The Virginia Department of Transportation, which had representatives at the location, has responsibility for this area and has been requested to arrange for mitigation of the source through the services of a radiation consulting company. Radiation levels were measured at about 10 mR/hr at 1.5 feet above the apparent location of the source and between 30 mR/hr and 50 mR/hr at ground level. Based on the radiation levels and the source location, no radiation exposure occurred to members of the public. The source is apparently below ground and will remain isolated and undisturbed until the Virginia Department of Transportation can arrange for the consultant to remove the item, analyze it, and arrange for its disposal. The consultant is enroute and expected to begin mitigation and disposal efforts late this afternoon. ORH is continuing its investigation and will update this notification when additional information is obtained." Virginia Event Report ID No.: VA-16-015 * * * UPDATE AT 1451 EST ON 12/30/16 FROM CHARLES COLEMAN TO JEFF HERRERA * * * The following update was received from the Virginia Radioactive Materials Program via facsimile: "On December 29, 2016, the Office of Radiological Health (ORR) was notified that radiation had been detected at the intersection of Route 123 and the I-95 southbound exit ramp near Woodbridge, Virginia. The Virginia Department of Transportation (VDOT) took mitigation action. VDOT contacted a radiation safety consulting firm which arrived at the scene that evening. A metallic pellet was found after removal of about one inch of soil. The pellet was confirmed to be a cesium-137 source with an activity of about 8 millicuries and a contact exposure rate of 900 milliRoentgen per hour. It was approximately 7 millimeters in diameter and approximately 15 millimeters long. A field leak test of the source and surveys of the area after removal of the source indicated no contamination. The source was placed in a lead shield inside a DOT 7A Type A steel drum overpack. It was sent to the consulting firm's facility for temporary storage pending disposition. This notification will be updated if additional information becomes available." Notified the R1DO (Lilliendahl), NMSS (Henderson), ILTAB (Tucker) and NMSS Events (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2017-01-06
52466 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2016-12-21 | 2016-12-29 16:54 | 2016-12-29 | PART 21 - ISSUES IDENTIFIED WITH THE ENTERPRISE DIESEL ENGINE SUBCOVER The following information is excerpted from a facsimile report submitted: "Engine Systems Inc. (ESI) began a 10 CFR 21 evaluation on November 18, 2016 upon notification of an issue with a subcover assembly at Perry Nuclear Plant. Attempts to install the subcover on their Enterprise diesel engine revealed two issues that prevented successful installation. First, one of the bolt holes was not fully machined through the entire depth of the subcover. Though the bolt could be inserted into the top of its corresponding hole, it would not pass completely through. The second issue was an interference between the rocker arm shaft and its mating pedestal. It was found that incomplete machining of the pedestal prevented the shaft from sitting flat on the pedestal. "The evaluation was concluded on 12/21/16 and it was determined that this issue is a reportable defect as defined by 10 CFR 21." The affected facilities are: First Energy - Perry Georgia Power - Vogtle Also listed was the following affected facility: Korea - Yonggwang Component: Subcover Assembly, P/N 1A-7846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-12-29
52465 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-12-29 02:50 | 2016-12-29 09:25 | 2016-12-30 | LOSS OF TECHNICAL SUPPPORT CENTER VENTILATION SYSTEM "Oyster Creek Generating Station has experienced a loss of the TSC [Technical Support Center] ventilation system. "If an emergency is declared requiring TSC activation during the time TSC ventilation is non-functional, the TSC will be staffed and activated using existing emergency planning procedure unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to a potential loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector has been notified." * * * UPDATED FROM JOSH MCGUIRE TO DONALD NORWOOD AT 1521 EST ON 12/30/16 * * * "At 1410 EST on 12/30/16, maintenance is complete and the TSC ventilation system has been restored to normal operation." The licensee notified the NRC Resident Inspector. Notified R1DO (Lilliendahl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-12-29
52464 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-11-16 | 2016-12-29 07:55 | 2016-12-29 | AGREEMENT STATE - LEAKING GENERAL LICENSED KR-85 SOURCE The following information was received from the State of Georgia via email: "Valmet was recently notified by one of their customers [WestRock MWV, LLC, Evadale, TX] regarding a leaking Kr-85 source in one of their general licensed [GL] devices that Valmet had supplied them a year or so ago. [Valmet personnel] retrieved the source and found that it was a slow leaker, and that it needed to be returned to the manufacturer. Valmet exchanged the source in the device and brought the faulty source back to Valmet's office to be returned to the manufacturer. The mill began to suspect a leaking source because of the operating parameters of the equipment. Valmet believes there were no exposures or ingestions of radioactive material, and will have the source returned to the manufacturer soon after the holidays when people are back to work. We expect them to let [the Georgia Radioactive Materials Program] know what the cause of the leak might be." Facility where event occurred: WestRock MWV, LLC, 1913 FM 105, Evadale, TX 77615 - PM4 reel Service Company: Valmet, Inc. 242225 Commerce Ave., Suite 100, Duluth, GA 30096 Source manufacturer: QSA Global, GL Device SS&D NR-0596-D-113-G Serial # 50048138, current activity 380 mCi of Kr-85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2017-01-06
52463 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-12-28 | 2016-12-28 19:11 | 2017-01-25 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received via email: "On December 28, 2016, the Hazardous Materials [Manager] at NBC Universal i.e. Universal Studios in Universal City, California called Los Angeles County Radiation Management on the telephone to report the loss of two Tritium exit signs. As of December 28, 2016, the Los Angeles County does not have information regarding the make, model, or serial numbers of the missing exit signs, or the quantity of H-3 (Tritium) in them." CA 5010 Number: 122816 * * * UPDATE FROM GEZA MIKO TO JOHN SHOEMAKER AT 1552 EST ON 1/25/2017 * * * The following report update was received via email: "On January 10, 2017, [the licensee's] Manager of Hazardous Materials at NBC Universal (i.e. Universal Studios in Universal City, California) reported to Los Angeles County Radiation Management by email that they have found the two Tritium exit signs that our agency reported to [the NRC] on December 28, 2016 (California 5010 # 122816). As of January 25, 2016, Los Angeles County does not have information regarding the make, model, or serial numbers of the missing exit signs, or the quantity of H-3 (Tritium) in them. [The State of California Los Angeles County Radiation Management] has requested this information from [the licensee], again, today. When [the Licensee] provides this information, it will be included in the California 5010 close-out. "The NMED number for this event is 170010." Notified the R4DO (Rollins) and NMSS_Events_Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-01-05
52462 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2016-12-27 | 2016-12-27 16:15 | 2016-12-27 | AGREEMENT STATE REPORT - FAILURE OF ON/OFF MECHANISM ON A FIXED GAUGE The following report was received via e-mail: "Failure of the on/off mechanisms on one fixed gauge to function as designed. The failure was discovered while clearing danger tags following routine maintenance on associated systems. The licensee is contacting a service provider to schedule removal/repair." Event Report ID No: KY160009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2017-01-04
52461 | 0 | ARMED FORCES RADIOBIOLOGY RSCH INST |  |  |  | 1100 KW TRIGA MARK-F | 2016-12-27 09:45 | 2016-12-27 10:44 | 2016-12-27 | SAFEGUARDS REPORTS Actual discovery of contraband in an office not in the controlled access area. The Licensee notified the RTR PM (Montgomery). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 0 | MD | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2016-12-27
52460 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-12-22 | 2016-12-23 16:30 | 2016-12-23 | AGREEMENT STATE REPORT - MEDICAL UNDERSOSE The following report was received via e-mail: "On December 22, 2016, UCLA's alternate RSO for UCLA sent an e-mail to an RHB ICE inspector for the Radiologic Health Branch [RHB] to report a medical event, per 10 CFR 35.3045. "A patient with metastatic sarcoma of the liver was treated by an authorized user at the medical center with Sirtex SIR-spheres containing yttrium-90 (Y-90) on December 22, 2016. A post treatment dose assessment was completed by radiation safety personnel. The authorized user prescribed 0.2 GBq (5.49 mCi) of Y-90 SIR-spheres to the left lobe of the patient's liver, but only 4.07 mCi or 74.1% was delivered. This underdose of 25.9 % caused a medical event to be reported. The patient was also treated with Y-90 SIR-spheres to the right lobe of the liver in compliance with the physician's written directive. The patient was notified by the physician and UCLA's radiation safety office is investigating the cause of the event." California event: 122216 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-01-02
52459 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-12-23 | 2016-12-23 15:00 | 2016-12-23 | AGREEMENT STATE REPORT - LEAKING KRYPTON-85 SOURCE The following report was received via e-mail: "On November 17, 2016 the Agency [Texas Department of State Health Services] received notice from a service company that it had a gauge which appeared to have leaked the radioactive material. The gauge potentially leaked Krypton-85 gas because the device failed to operate normally. The device activity did not produce acceptable measurements and was removed from service/operation. The device was removed from service by the service company and set into a storage area and labeled to prevent movement. The licensee made arrangements for the manufacturer to service the gauge stating to the Agency [Texas Department of State Health Services] that it would take the manufacturer three weeks before it could schedule a visit to the plant site. The manufacturer must confirm that Kr-85 indeed did leak from the gauge. "Device information provided included by the licensee: Manufacturer - Valmet/Metso, Gauge model - BMW2, Gauge S/N - 50048138, Isotope - Kr-85, Activity - 400mCi, Source S/N - QA00168. "On December 23, 2016, the licensee verbally confirmed the device had leaked the Kr-85 gas. The manufacturer will be providing a service description and details of how the device was checked and or repaired. Awaiting the service report from the manufacture." The seam on the source capsule had ruptured. Texas incident: I-9442 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-01-02
52458 | 0 | ITT ENIDINE INC. |  |  |  |  | 2016-11-02 | 2016-12-22 17:35 | 2017-02-28 | PART 21 - POTENTIAL TRANSDUCER COMPONENT DEFECT The following information was received via fax: "The ITT Conoflow models GT25CA1826 and GT25CD1826 current to pressure (l/P) transducers produce a calibrated 3.0 to 15.0 psi output pressure from a 4.0 to 20.0 mA DC (input) signal. On November 2, 2016, a discovery was made of unqualified electrical component substitutions on the internal circuit board. Supplier and internal record reviews indicate these unqualified components were used as early as May 10, 2013, as the previously qualified PCB components are no longer available. Environmental qualification of the suspect circuit boards is planned for early 2017. If any component falls to meet requirements, nuclear facilities which use this product will be advised to examine their product for unqualified printed circuit boards via notification and visual references. Qualified replacement components will be provided to all affected customers. "Customer Name / Item Number / No.: Units Calvert Cliffs Nuclear / GT25CD1826 / 30 Control Components Inc. / GT2SCD 1826 / 3 Duke Energy Carolinas LLC / GT25CA1826 / 8 Duke Energy Carolinas LLC / GTI:SCD1826 / 4 Enertech Curtiss-Wright / GT25CA1816 / 19 Enertech Curtiss-Wright / GT25CD1826 / 4 Ergytech Inc. / GT25CA1826 / 3 Ergytech Inc. / GT25CD1826 / 3 Gefran Benelux NV / GT25CD1826 / 2 Ontario Power Generation / GT25CD1826 / 31 SPX Flow Technology / GT25CA1826 / 2 Weir Valves & Controls UK / GT25CA1826 / 78" * * * UPDATE ON 2/28/17 AT 0918 EST FROM RAY SMITH TO DONG PARK VIA FAX* * * "On November 2, 2016 a discovery was made of unqualified electrical component substitutions on the internal circuit board. Supplier and internal record reviews indicate these unqualified components were used as early as May 10, 2013, as the previously qualified PCB components are no longer available. Environmental qualification of test samples containing the suspect circuit boards has been completed. The subject parts continued to operate and perform their intended safety function throughout all EQ [Equipment Qualification] tests." Notified R1DO (DeFrancisco), R2DO (Bartley), R3DO (Jeffers), R4DO(Deese), NMSS Events Resource, and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-12-22
52457 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-12-20 | 2016-12-22 12:46 | 2016-12-22 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following report was received via fax: "On December 20, 2016, a leak occurred during an administration of Yttrium-90 (Y-90) TheraSpheres to a patient, resulting in less than 80% of the prescribed dosage being administered. A total of about 8.99 millicurie of Y-90 activity was administered; or 34.6% of the prescribed 25.95 mCi activity. The prescribed dose was 17,470 rad (174.7 gray), with the leak resulting in a dose to the patient's liver of about 6,040 rad (60.4 Gy). The leak also caused contamination of the administration area, which was immediately and successfully decontaminated. As an under-dose, no immediate harmful effect to the patient resulted from the event. The referring physician and patient were made aware of the event during the procedure." Pennsylvania event: PA-160040 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-12-30
52456 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-12-21 23:00 | 2016-12-22 05:45 | 2017-05-22 | EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE "With D.C. Cook Unit 1 in Mode 1 and 100 percent power and Unit 2 in Mode 4 during a refueling outage, the following emergency diesel generators (EDGs) were declared inoperable due to a discovered design and manufacturing issue involving some of the diesel fuel pumps/injectors in each of the following EDGs: "Unit 1 CD (Train A) EDG, Unit 2 AB (Train B) EDG, and Unit 2 CD (Train A) EDG "Due to both Unit 2 EDGs being inoperable, Unit 2 is required to be in Mode 5 by 1300 [EST] on 12/23/16. Unit 1 is required to restore its emergency diesel generator within 14 days (by 2300 [EST] on 1/04/17). "In connection with both trains of Unit 2 EDGs being inoperable, this is being reported as an 8-hour report pursuant to 10CFR50.72(b)(3)(v)(D) as loss of safety function in connection with mitigating the consequences of an accident. "The NRC Resident Inspector has been informed." Unit 1 maintenance will be prioritized over Unit 2 and Unit 2 will most likely proceed to Mode 5. * * * RETRACTION AT 1406 EDT ON 5/22/17 FROM RODNEY PICKARD TO JEFF HERRERA * * * "The condition reported in ENS 52456 pursuant to 10 CFR 50.72(b)(3)(v)(D) has been evaluated, and determined not to be a loss of safety function in connection with mitigating the consequences of an accident, and is being retracted. "With D.C. Cook Unit 1 in Mode 1 and 100% power and Unit 2 in Mode 4 during a refueling outage, the following Emergency Diesel Generators (EDGs) were declared inoperable due to a discovered design and manufacturing issue involving some of the diesel fuel pumps/injectors in each of the following EDGs: Unit 1 CD (Train A) EDG, Unit 2 AB (Train B) EDG, and Unit 2 CD (Train A) EDG. "Subsequent endurance testing was performed on selected Delivery Valve Holders (DVH), which were the affected components of the diesel fuel pumps/injectors, to evaluate the expected degradation of the DVHs during the EDG mission. This testing determined that the identified design and manufacturing issue would not have prevented the EDGs from performing their intended safety functions. Therefore, all EDGs were OPERABLE and did not result in a loss of safety function in connection with mitigating the consequences of an accident. "The NRC Resident Inspector was notified of this retraction." Notified the R3DO (Kunowski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-12-22
52455 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-12-21 13:50 | 2016-12-21 19:45 | 2016-12-21 | UNANALYZED CONDITION DUE TO VALVE FAILURE "During review of the Limerick future modification list, a concern was raised with a proposed modification for HV-011-015A, ESW [Emergency Service Water] 'A' Discharge to 'B' RHR Service Water Return, which failed to fully close during routine testing. "As a result of the failure to close, a clearance was applied and a 10CFR50.59 screening was performed to close and de-energize HV-011-015A and open and de-energize valve HV-011-011A, ESW 'A' Discharge to 'A' RHR [Residual Heat Removal] Service Water Return. This clearance isolated one of the two ESW return flow paths so that only one flow path is available to return cooling water flow to the spray pond. "The 10CFR50.59 screening did not address that fire areas 12 (Unit 1 4kV D13 switch gear room) and 18 (Unit 2 4kV D23 switch gear room) are not in compliance with the existing fire safe shutdown (FSSD) analysis. The FSSD analysis credits both flow paths so that Emergency Service Water can be returned to the spray pond. With only one of the two return flow paths available, a single spurious fire induced valve operation can result in deadheading an ESW pump and starving an operating emergency diesel generator of cooling water. Running the emergency diesel generator with a loss of cooling water will initiate a diesel protective trip on high temperature. "Compensatory measures are in place for the specific fire areas listed above." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-12-21
52454 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-12-21 09:35 | 2016-12-21 18:00 | 2017-01-18 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "At 0935 [CST] on 12/21/2016, while performing the High Pressure Coolant Injection (HPCI) Comprehensive Pump and Valve Tests for post-maintenance testing following scheduled maintenance, the HPCI turbine did not start as expected due to the HPCI turbine stop valve failing to open. This issue is being reported under 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function at the time of discovery. Investigation into the failure of the HPCI system to start is in progress. The plant remains at 100% power with no challenges to the health and safety of the public. "The NRC Resident Inspector has been notified." The plant is in a 14-day action statement under LCO 3.5.1, 'ECCS - Operating' due to the HPCI turbine stop valve failure. The licensee notified the Minnesota State Duty Officer. * * * RETRACTION FROM KIM HOFFMAN TO JOHN SHOEMAKER AT 1303 EST ON 1/17/18/17 * * * "On December 21, 2016, the NRC Operations Center was notified of Event Number 52454 that described a failure of the High Pressure Coolant Injection (HPCI) turbine stop valve to open during post maintenance testing prior to being declared operable. The condition was reported in accordance with 10 CFR 50.72 (b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function at the time of discovery. At the time, it was not readily apparent that the failure was due to the maintenance activities. Subsequent return-to-service testing showed the oil system vent and fill had been inadequate following the maintenance. This event occurred as a result of the maintenance process and would not have occurred during normal operation of the system. ''NUREG-1022, Revision 3 states, 'reports are not required when systems are declared inoperable as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that would have resulted in the system being declared inoperable).' "There was no discovered condition that would have resulted in the safety function of the system being declared inoperable under normal, non-maintenance conditions. "Based on the above additional information, Monticello Nuclear Generating Plant is retracting this report. The plant was in a planned evolution and did not discover a condition that could have prevented performing a safety function. "The licensee has notified the NRC Resident Inspector." Notified R3DO (McCraw). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-12-21
52453 | 0 | TERRACON CONSULTANTS, INC. |  |  |  |  | 2016-12-21 10:47 | 2016-12-21 16:55 | 2016-12-21 | TROXLER MOISTURE DENSITY GAUGE DAMAGED A Troxler moisture density gauge (Model 3440) was damaged when it was struck by an asphalt roller. The source rod was out at the time of the incident but the source was able to be retracted into the shielded position. The licensee's radiation safety officer surveyed the meter and found no abnormal radiation readings. The gauge was transported back to the licensee's facility for storage awaiting results of the swipe test. Once the swipe test results are returned, the licensee intends to ship the gauge to the vendor for repair or replacement. The gauge contains Am-241/Be and Cs-137 sources. No personnel overexposures occurred during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-12-29
52452 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-12-21 11:20 | 2016-12-21 16:55 | 2016-12-21 | UNANALYZED CONDITION - 480V BUS VOLTAGE LOWER THAN ANALYZED "On October 8, 2016, it was initially discovered that the voltage tap changer settings for the 480V Shutdown Board Transformers 1-XFA-231-TS1A (TS1A) and 1-XFA-231-TS1B (TS1B) were incorrect (4160/480V instead of 3952/480V). This could potentially result in lower than minimum required voltages at the electrically downstream buses and equipment during a postulated loss of coolant accident coincident with design minimum voltage conditions. An initial Licensee Event Report (LER 50-259/2016-004-00) was submitted on December 7, 2016 following the initial review. This LER identified that a supplement would be required pending additional technical evaluation. While comprehensive analysis is not complete, the initial aggregate dynamic loading evaluation does not provide assurance that sufficient voltage would be available for various loading scenarios during postulated accident conditions. This condition was determined to have existed since a Unit 1 Design Change was implemented in 2004. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(ii), as any event or condition that resulted in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety. "On October 9, 2016, and October 12, 2016. the transformer taps for TS1B and TS1A, respectively, were set in accordance with the applicable drawing, which specify the correct tap settings. "The NRC Resident Inspector has been notified." In October 2016, the licensee validated that this problem did not exist on units two and three. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-12-21
52451 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-10-24 17:45 | 2016-12-21 16:38 | 2016-12-21 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being submitted in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to report an invalid actuation of the 12 Emergency Diesel Generator Emergency Service Water pump (12 ESW pump). "At 1745 [CST] on October 24, 2016, an unexpected auto-start of the 12 ESW pump occurred. The 12 Emergency Diesel Generator (12 EDG), was previously properly removed from service and isolated for scheduled maintenance. Upon investigation, is was determined that no valid start signal was present and actuation occurred during relay replacement activities on the 12 EDG in C-92 (12 EDG (G-38) electrical control panel) cabinet when electricians inadvertently bumped a 12 EDG start relay. During this period, the Control Room received annunciators indicating the 12 EDG engine was running/cranking and the 12 ESW pump started. Due to being isolated, the 12 EDG did not actually start. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-12-21
52450 | 0 | INDIANA MICHIGAN POWER |  |  |  |  | 2016-12-20 15:10 | 2016-12-21 14:09 | 2016-12-21 | SHUTTER AND SHUTTER MECHANISM SEPARATED FROM SOURCE HOLDER "On December 20, 2016 [at approximately] 1510 CST, a [level detector] nuclear source holder was found fallen off of its mounting on the unit 2 economizer hopper #49. The shutter mechanism and the shutter appear to have separated from the source holder. This occurred at the Indiana Michigan Power Rockport plant in Rockport, Indiana. The source holder is a Vega Americas Model SHLD-1-45, serial number: 7185CP. It is a 20 millicurie Cesium 137 source. The plant's general license number is GL704402-21. The radiation around the fallen source holder was tested and found to be a maximum of 35 millirem/hr at 1 foot in the source beam path. The radiation was tested at the 20 foot boundary where danger tape has been placed around the source holder and readings of 0.08 to 0.12 millirem/hr were noted. A nuclear technician from Vega Americas is currently on his way to the plant and we are planning to attempt to repair the source holder this evening [December 21]. "If we are unable to repair the source holder it will be prepared for shipping and will be sent back to Vega Americas' office in Cincinnati, Ohio for repair." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-12-29
52449 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-12-20 18:30 | 2016-12-20 19:45 | 2016-12-20 | OFFSITE NOTIFICATION - RELEASE OF HYDROGEN GAS IN EXCESS OF THE REPORTABLE QUANTITY OF TEN POUNDS "At 1830 EST on 20 December, 2016 the Massachusetts Department of Environmental Protection and the Plymouth Massachusetts Fire Department were notified of a Hydrogen release in accordance with plant procedures and 310CMR40.300, Massachusetts Contingency Plan Notification for Oil and Hazardous Material; Identification and Listing of Oil and Hazardous Material, due to a release of hydrogen gas to the environment exceeding the reportable quantity of ten pounds. The release, which is an expected part of a routine plant start-up was from the generator hydrogen cooling system. "This event posed no danger to the health and safety of plant personnel or members of the general public. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-12-20
52448 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2016-12-20 13:00 | 2016-12-20 16:36 | 2017-01-03 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING WRONG TREATMENT SITE The following information was obtained from the state of Maine via facsimile: "On 12/19/2016, patient was scheduled for initial verification and treatment with electrons of a right sided metastatic rib lesion of 5 fractions at 400cGy per fraction. Patient was also to be treated with photons to a spinal lesion. Patient had previously been treated to a right sided rib lesion approximately 11 cm superior to the intended treatment site. Treatment location tattoos were present for each of these sites. Failure to identify the correct treatment tattoo and confusion over the treatment note led to the patient being setup to the previous rib tattoo location and treated. A single fraction of 400 cGy was delivered to the previous treatment site. Following treatment, the physician suspected a setup error. Further review of treatment plan confirmed the error. The licensee has notified the patient. "A review of causes of the event and corrective actions was initiated." Maine Event Report ID No.: ME 16-002 * * * UPDATE AT 1704 EST ON 1/3/2017 FROM THOMAS HILLMAN TO MARK ABRAMOVITZ * * * The following information was received via fax: "On 12/19/2016, a patient initiated treatment to a right sided metastatic rib lesion with 12 MEV electrons. The patient was also treated with photons to a T9 spinal lesion. The patient had previously been treated to a right sided rib lesion approximately 11 cm superior to the intended treatment site and a T2 spinal lesion. Each treatment site was marked with a small tattoo as is common in Radiation Oncology. "The treating therapists incorrectly identified and set up the radiation treatment to the wrong rib tattoo. This was the patient's first radiation treatment of this course. Therefore, consistent with Radiation Oncology practice, a documented verification step in which the prescribing physician is present and verifies field setup prior to initiating treatment occurred. The physician also failed to identify that the radiation treatment was setup to the wrong tattoo. A single fraction of the intended 5 fractions of 400cGy was then delivered. "Referencing SOM rules, PART X, THERAPEUTIC RADIATION MACHINES, a 'Medical Event' means 'the administration of an external beam radiation therapy dose: (1) Involving the wrong patient, wrong treatment modality, or wrong treatment site; or, .. 'The event is considered to meet the intent of 'wrong treatment site' under the rule and is being reported. An initial notification of the State occurred with 24 hours, as prescribed by the rule. This was followed up the same day with an email containing initial details of the event. This report constitutes the written report requirement under that rule required within 15 days of identification. "Why the event occurred: The patient had previously been treated to two sites. The new treatment included two additional sites. Each treatment site is marked with a small tattoo. The appropriate treatment tattoo was misidentified. Patient was set up to the tattoo of the previously treated right sided rib lesion approximately 11 cm superior to the intended treatment site. Treatment setup information was available in the form of simulation photos and graphical treatment plan to adequately identify the appropriate treatment site. Available information was not accessed in the treatment room during set up of the patient. "When the plan is brought up on the treatment machine, information is presented on the overhead monitors in the treatment room. This is limited to 3 photos (1 being patient race photo) and 256 characters of text. Prior to treatment, dosimetrists load all available simulation images into the electronic chart only assuring that the face photo is the first for each field. During initial therapist chart review the most informative photos are selected by the therapist to be presented in the room that they will find useful to setup the patient. This did not occur in this case. Two face photos and an ambiguous photo was present. This 1 photo when coupled with the note did not provide clear field setup direction. "When a right rib tattoo was readily identified by the therapist they assumed that they were on the correct tattoo and chose to rely on the limited information that was presented on the overhead monitor. Comprehensive setup information was available in the simulation documentation, EMR and the graphical treatment plan available in the electronic medical record (EMR). This information was available on the in room EMR computer. It is understood by the therapist that the overhead monitor may not be able to convey all necessary setup information and routinely refer to the EMR. This physician routinely requests a hard copy print out of the setup of electron treatments so that the image can be compared to surface landmarks. The image print out is not requested by all physicians. A print out was not provided by the dosimetrist. When requested, the therapist did bring up the plan information on the in room EMR computer monitor for reference by the physician. "The setup error was also not detected by the physician. Immediately following treatment the physician requested a print out of the patient setup from dosimetry and noted the error. A review of causes of the event and development or corrective actions was initiated. "The effect on the patient: Due to the superficial nature of electrons the dose delivered to the wrong site will result in no appreciable impact on skin or underlying healthy tissues. The treatment dose can be made up in the remaining days of scheduled treatment safely providing full therapeutic dose to the target lesion. "What improvements are needed to prevent recurrence; actions taken to prevent recurrence? "The need to select the most informative images to be presented in the treatment room was added to a newly created comprehensive pre-treatment chart checklist. This step is required to be initialed by both the dosimetrist and therapist performing pre-treatment chart check. "The need to select those photos as photo 1 and photo 2 in the EMR was reviewed with the dosimetrists, who were previously unaware of the functionality added approximately 1 year ago. The need to no longer add the face photo to the plan, which is now presented in the room automatically, was also shared. "The need to review and configure the in-room field notes and photos, the need to utilize additional information in the EMR if the in-room note is unclear, and the need to reach out to the planning dosimetrist if treatment remains ambiguous was reemphasized with the therapist. "The newly installed TrueBeam treatment machines allow electronic reference field images to be easily generated and taken through the field aperture even for clinical patient setups. A comparison of proximal bony anatomy at the treatment site to the reference derived from the planned treatment can performed at the treatment console to assure treatment of the correct location. Initial verification image guidance, common on most photon treatments, will now also be required for electron treatments. "The prescription was titled Right 8th rib. The treatment plan was titled Right Inferior Rib. The dosimetrist considered inferior rib to be more descriptive and one more generally understood by staff than 8th rib. Consistency of prescription and plan name is weak potential barrier in this case, but in general consistency will serve to minimize potential for gross errors such as wrong body part and laterality issues. The verification of consistency of prescription and plan names was added to newly created comprehensive pre-treatment chart checklist. "As of this date, Maine General has classified this as a Sentinel Event. As such, an independent Root Cause Analysis is planned by our Risk Management Department. That assessment is in progress and as yet no additional corrective actions have been identified. "Event and corrective actions will be reviewed in the department Quality Committee. "Notification of the patient: Event was reviewed with the patient by the physician on 12/20/16 prior to delivery of the next scheduled treatment. Patient was informed that an error had been made, that impact was negligible to the re-treated site, and that full therapeutic dose could be delivered safely to the intended site. A physician's note is available in the patients chart documenting that conversation. "Conclusion: The root cause of the event is determined to be human error. The incorrect one of two right rib tattoos was identified and referenced for treatment setup. Contributing factors included limited in-room information to initially setup patient and failing to access readily available information if setup information was ambiguous. Corrective actions have been put in place to assure than in-room data presented on the overhead monitors ls present and as comprehensive as possible. The need to access additional information using the EMR or other resources when the setup is ambiguous was reemphasized with the staff. "An additional barrier created to prevent repetition of the event is the addition of image guidance for all electron treatments during initial treatment verification. A comparison of proximal bony anatomy at the treatment site to the reference derived from the planned treatment can performed at the treatment console to assure treatment of the correct location." Notified the R1DO (Dentel) and NMSS (via e-mail). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2016-12-28
52447 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2016-11-23 | 2016-12-20 16:01 | 2016-12-20 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING HIGH DOSE RATE THERAPY DOSE TO AN UNINTENDED LOCATION The following information was obtained from the state of New Hampshire via facsimile: "NH Radiological Health Section 'Agency' was notified on November 23 by Chief Physicist followed by an e-mail from the Radiation Safety Officer (RSO) at Mary Hitchcock Memorial Hospital on November 24, 2016, of the HDR [high dose rate therapy] dose to an unintended location. The patient and the Authorized User were notified of the error and the correct fraction was administered. "The licensee's RSO conducted an investigation and interviewed persons involved with the administration. A written explanation of the event was obtained. Cause of incident was identified as equipment malfunction (a deformed transfer tube)." New Hampshire Event Report ID No.: NH-16-001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2016-12-28
52446 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-12-20 | 2016-12-20 12:49 | 2017-01-24 | TEXAS AGREEMENT STATE REPORT - RADIOGRAPHY CAMERAS DAMAGED IN BUILDING FIRE The following information was obtained from the State of Texas via email: "On December 20, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee's corporate radiation safety officer (CRSO) that a fire had occurred at their Poth, Texas location causing extensive damage to the building. The licensee reported that inside the building was its storage location for its radiography exposure devices. The storage location had ten QSA 880D cameras containing between 32.2 and 90.2 curies Ir-192. Dose rates five feet from the storage location after the fire was out were near normal. "Once the licensee gained access to the storage location they discovered that at least two of the handles on the devices had been melted to some degree. The licensee removed all the cameras from the storage location and a radiation survey on each was completed. The licensee stated the measured dose rates were normal. It appears the integrity of the shielding was maintained, but could have been affected. The CRSO stated all cameras were being returned to the manufacturer for leak test and inspection. "No licensee personnel or member of the general public were exposed to any significant levels of radiation due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-9452 * * * UPDATE FROM ART TUCKER TO JOHN SHOEMAKER AT 1049 EST ON 12/23/16 * * * The following report update was received from the State of Texas via email: "On December 23, 2016, the Agency contacted the licensee to get an update on the status of the radiography exposure devices. The licensee stated ten exposure devices were involved in the event and all have been delivered to the manufacturers Houston, Texas location for leak test and inspection. The licensee stated the exposure device storage area has been surveyed and no contamination was found. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO(Hay) and NMSS_Events_Notification via email. * * * UPDATE FROM TUCKER TO KLCO AT 1056 EST ON 12/28/16 * * * The following information was received from the State of Texas via email: "On December 28, 2016, the Agency was notified by the licensee that the state Fire Marshal determined the fire was an electrical short at a plug. Additional information will be provided as it is received IAW SA-300." Notified R4DO (Drake) and NMSS_Events_Notification via email. * * * UPDATE FROM ART TUCKER TO JOHN SHOEMAKER AT 1151 EST ON 1/24/17 * * * The following update information was received from the State of Texas via email: "On January 19, 2017, the Agency received the written report from the licensee. Due to the nature of this event, the information is being provided directly to the HOO [NRC Headquarters Operations Officer]. The report included the report from the device manufacturer. The manufacturer's report states that due to the heat the devices were exposed to, none of the QSA 880 devices should be used to perform radiography work. In addition, the type 'B' containers could not be used as transportation containers for radioactive materials. The report also stated 12 cameras were involved in the fire, but only 10 had sources in them. All of the devices will be disposed of. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Rollins) and NMSS_Events_Notification (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-12-28
52445 | -1 | U.S. ARMY |  |  |  |  | 2016-12-15 13:00 | 2016-12-19 16:30 | 2017-01-04 | REMOVABLE CONTAMINATION IDENTIFIED IN VAULT At 1300 CST on December 15, 2016, during a survey, removable contamination above 1000 dpm was identified in a normally controlled and restricted area. Access was restricted to the area, the area was roped off and a decontamination team was assigned to decontaminate the area. Additional surveys were conducted outside the area identified and no additional areas were found to be contaminated. The licensee reported that the initial investigation indicates that none of the individuals who had access were contaminated or accessed the area. The cause of the contamination is still under investigation. * * * RETRACTION AT 1755 EST ON 1/4/2017 FROM MICHAEL GRAY TO MARK ABRAMOVITZ * * * The following retraction was received via e-mail: "Since the notification, we have confirmed the source of contamination as cracked vial containing cobalt-60. Calculations of the current activity of the source and associated exposure levels were sent to NRC Region III. We also determined that total amount of cobalt-60 involved was less than the annual limit on intake (ALI) for ingestion. "Mr. Zahid M. Sulaiman, Health Physicist, NRC Region III, called today to confirm: (a) they verified our calculations on activity and exposure levels (b) the amount of radioactive material involved does not exceed the ALI for ingestion (c) this is not a reportable event and to notify NRC Operations Center of their decision." Notified the R3DO (Daley) and NMSS (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2016-12-19
52444 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-12-19 07:15 | 2016-12-19 08:14 | 2016-12-19 | SAFEGUARDS REPORT Attempted introduction of contraband into a protected area. The licensee will notify NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2016-12-19
52443 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2016-12-18 23:20 | 2016-12-19 07:39 | 2017-05-24 | UNISOLABLE LEAK ON HIGH PRESSURE CORE SPRAY "On December 18, 2016 at 2320 [PST], a leak was discovered on the High Pressure Core Spray (HPCS) system minimum flow line. The leak is located at a bolted flange downstream of the manual isolation valve HPCS-V-53. The location of the leak is not isolable from the suppression pool. This provides a direct path from inside the Primary Containment to the Reactor Building. "High Pressure Core Spray system is a single train Emergency Core Cooling System (ECCS) system, therefore inoperability is reportable per 10 CFR 50.72(b)(3)(v)(D). "Based on the location of the leak, Primary Containment integrity is compromised. Primary Containment was declared inoperable and is reportable per 10 CFR 50.72(b)(3)(ii)(A). "The cause of the leak is under investigation. Actions are underway to cool down and enter MODE 4." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM MATT HUMMER TO HOWIE CROUCH AT 2245 EDT ON 5/24/17 * * * "Engineering evaluations indicate that there was neither a High Pressure Core Spray (HPCS) system inoperability nor a condition that resulted in a significantly degraded principal safety barrier (Primary Containment). Therefore, this event does not meet the reporting criteria in 10 CFR 50.72(b)(3)(v)(D) and 10 CFR 50.72(b)(3)(ii)(A), and Event Notification# 52443 is being retracted. "Bases for the retraction are: (1) Extent or accumulation of water flooding the HPCS room would not have prevented the system from fulfilling any of its designated safety functions, if the system had received a starting signal due to an emergency; and (2) the consequences of the HPCS Minimum Flow Line leak into the Reactor Building were within the dose limits and did not have a significant effect on Primary Containment integrity; therefore, the Primary Containment was degraded but operable. "The licensee has notified the NRC Resident Inspector." Notified R4DO (Groom). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | DEGRADED CONDITION |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2016-12-19
52442 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2016-12-18 11:24 | 2016-12-18 18:13 | 2016-12-18 | AUTOMATIC SCRAM DUE TO LOAD REJECT FROM SUBSTATION "On December 18, 2016 at time 1124 PST the plant experienced a full reactor scram. Preliminary investigations indicate that the scram was caused by a load reject from the Bonneville Power Administration (BPA) Ashe substation. Further investigations continue. The following conditions have occurred: "Turbine Governor valve closure Reactor high pressure trip +13 inches reactor water level activations E-TR-B (backup transformer) supplying E-SM-7/SM-8 (vital power electrical busses) Complete loss of Reactor Closed Cooling (RCC) E-TR-S (Startup transformer) supplying SM-1/2/3 (non-vital power electrical busses) E-DG-1/2/3 (emergency diesel generators) auto start Low Pressure Core Spray (LPCS) and Residual Heat Removal (RHR) A/B/C initiation signals Main Steam Isolation Valves (MSIV) are closed "Reactor Core Isolation Cooling (RCIC) RCIC and High Pressure Core Spray (HPCS) were manually activated and utilized to inject and maintain reactor water level. Pressure control is with Safety Relief Valves (SRV) in, manual. Level control is with RCIC and Control Rod Drive (CRD). RCIC has experienced an over speed trip that was reset so that level control could be maintained by RCIC. "This event is being reported under the following: 10 CFR 50.72(b)(2)(iv)(A) which requires a 4 hour notification for Emergency Core Cooling System (ECCS) discharge into the reactor coolant system. 10 CFR 50.72(b)(2)(iv)(B) which requires a 4 hour notification for any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical. 10 CFR 50.72(b)(3)(iv)(A) which requires an 8 hours notification for actuation of ECCS systems. "All control rods fully inserted. "The NRC Resident Inspector has been informed." The licensee indicated that no increase in radiation levels were detected. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-12-18
52441 | -1 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2016-12-16 14:00 | 2016-12-17 05:43 | 2017-02-07 | VENTILATION SYSTEM INOPERABLE "At approximately 1400 CST on 12/16/16, during the performance of VEF-38A Lead Penetration Room Ventilation System (PRVS) Exhaust Fan Monthly Test, flow was found to be at 2000 SCFM with an operability limit of 1620 to 1980 SCFM. VEF-38A was declared inoperable. Unit 1 entered Technical Specification Limiting Condition for Operation (LCO) 3.7.11 Condition C for both trains of PRVS inoperable. With VEF-38A aligned as the lead fan and capable of auto-start, the operable standby fan (VEF-38B) would not have started. "During the time that VEF-38A was inoperable and capable of auto-starting, the Unit 1 PRVS was in a condition that could have prevented the control of the release of radioactive material. "At 1546 CST on 12/16/16, Unit 1 rendered VEF-38A incapable of auto starting by placing its hand switch in PULL-TO-LOCK. Unit 1 Entered LCO 3.7.11 condition A for one PRVS train inoperable and Exited LCO 3.7.11 Condition C. "This is a notification per 10 CFR 50.72(b)(3)(v) for a condition that could have prevented the control of the release of radioactive material." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 2/7/17 AT 1528 EST FROM BUCHANON DICKSON TO DONG PARK * * * "EN 52441 was initiated on December 16, 2016, when the VEF-38A fan flow was found to be in excess of the procedurally defined operability limit during the monthly lead penetration room ventilation system test. "The revision of the procedure in use at the time had inadvertently included acceptance criterion for fan air flow in the monthly supplements. The monthly tests demonstrate the flow paths for the two trains are functional and open, but they are not performed in the designed Engineered Safeguards (ES) configuration. The monthly tests do not secure the normal supply and exhaust ventilation within the penetration room boundaries; therefore, flow may be outside limits required during the ES configuration. The 18 month surveillance, which measures the flowrate of the system while in the ES configuration, was completed in April 2016. The surveillance verified the system's operability. The systems have not been modified or altered since this surveillance; therefore the measured flowrate remains the same. "The procedure has been revised subsequent to this event to remove the flowrate as an 'acceptance criterion' for the monthly test. "Because the VEF-38A flow did not result in fan inoperability, both fan trains remained operable; therefore, ANO-1 did not lose a safety function to control a radioactive release. Based on that, conclusion EN 52441 is being retracted." The licensee will notify the NRC Resident Inspector. Notified R4DO (Warnick). | 33 | 0 | 0 | 33 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-12-17
52440 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2016-12-16 07:00 | 2016-12-16 09:27 | 2016-12-16 | OFFSITE NOTIFICATION OF AN INDUSTRIAL SAFETY INCIDENT "On December 15, 2016, a grid area employee was moving containers in the plating room, where his finger was pinched between two containers. He was taken to the emergency room where he was treated for an injury to the tip of his left ring finger. The event did not involve special nuclear material or contamination and is classified as an industrial safety incident. "This concurrent report is being made under Paragraph (c) of 10 CFR 70, Appendix A because a 24 hour report was made to the South Carolina Department of Labor [at 0700 EST on 12/16/16] per 29CFR1904.39." The employee was not admitted to a hospital and was sent home after treatment. The licensee has notified NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2016-12-16
52439 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-12-15 10:30 | 2016-12-15 15:38 | 2016-12-15 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following was received from the State of Texas via email: "On December 15, 2016, the Agency [Texas Department of State Health Services] received notice that the licensee had retrieved a source disconnected via a broken drive cable. The camera was an 880 Delta with a 135 curie iridium-192 source. The retrieval agent received an estimated 113 mRem to the whole body and 1 Rem to the hands for the procedure. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I - 9450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-12-23
52438 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2016-12-15 11:30 | 2016-12-15 13:50 | 2016-12-28 | OFFSITE NOTIFICATION MADE FOR POTENTIAL FUEL OIL LEAKAGE "On 12/14/16 at 1206 [EST], 0-PT-89.9K (underground fuel-oil piping pressure test), was performed UNSAT after a failed attempt to maintain pressure in the supply line to the Unit 2 'H' Emergency Diesel Generator (EDG) Day Tank. The exact source of the leakage is unknown at this time but is reasonable to believe some fuel oil was released underground. The associated Fuel Oil line is currently tagged out and isolated. This condition is reportable to the Virginia Department of Environmental Quality [VA DEQ] as part of the Underground Storage Tank Program. Pressure tasting of the other EDG fuel oil supply lines has been previously completed satisfactorily. The 2H EDG remains Operable as the redundant fuel oil transfer pump and its fuel oil piping are Operable and capable of maintaining adequate day tank level. The VA DEQ was notified of this condition at 1130 [EST] on 12/15/16. "This event is reportable in accordance with 10CFR50.72(b)(2)(xi) for 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.'" The licensee has notified the NRC Resident Inspector and will notify Louisa County. * * * UPDATE ON 12/28/16 AT 1659 EST FROM JAY LEBERSTIEN TO DONG PARK * * * "This is a follow-up report to Event Number 52438, made on 12/15/2016, regarding offsite notification to the Virginia Department of Environmental Quality for potential fuel oil leakage from the supply line to the Unit 2H Emergency Diesel Generator (EDG) Day Tank. "During investigation of the potential fuel oil leak from the 2HB EDG Day Tank supply line (as previously reported in EN 52438), the 2HA fuel oil line, which runs close to the 2HB line, was disturbed and began to leak a mist of fuel oil. The fuel oil was contained in the area and was being cleaned via vacuum truck as it was leaking. Personnel at the scene noted the soil was not contaminated with fuel oil initially and saw the leak start on 2HA line. It has been estimated that less than one gallon of fuel oil was released to the surrounding soil during troubleshooting of the leak. The fuel oil was immediately vacuumed. The 2HA line was isolated and the leakage was stopped. The 2HA line is to be repaired and tested. The 2H EDG remains available, however, it is considered inoperable at this time. Investigation of the 2HB fuel oil line continues. "The condition of the 2HA fuel oil line was reported to the Virginia Department of Environmental Quality [VA DEQ] as part of the Underground Storage Tank Program on 12/28/16. Therefore, this event is reportable in accordance with 10CFR50.72(b)(2)(xi) for 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.' "The licensee has notified the NRC Resident Inspector and will notify Louisa County." Notified R2DO (Rose). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-12-15
52437 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-12-15 10:10 | 2016-12-15 11:47 | 2017-03-17 | SECONDARY CONTAINMENT MOMENTARY LOW PRESSURE "On December 15, 2016, at 1010 EST, the startup of the Reactor Building HVAC [Heating Ventilation and Air Conditioning] system resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met for approximately 1 second. The maximum secondary containment pressure observed during that time was approximately 0.044 inches of vacuum water gauge. "Secondary containment pressure was returned to within the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4. 1.1) by Reactor Building HVAC and Standby Gas Treatment System already in operation. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-12-15
52436 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-10-28 01:39 | 2016-12-15 10:23 | 2016-12-15 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "This telephone notification is being made in lieu of a Licensee Event Report in accordance with 10CFR50.73(a)(1) to notify the NRC of on invalid actuation of a group isolation, reportable under 10CFR50.73(a)(2)(iv)(A). "On October 28, at 0139 Central Daylight Time, electricians were removing a test jack from a terminal on a primary containment isolation system relay due to the test jack being installed on the wrong relay. During removal of the test jack, a neutral wire came out of the terminal causing multiple relay actuations resulting in a half Group 2 isolation signal on the Division 2 side. Because of the plant being in Mode 5, refueling, the only isolation valves that closed because of the invalid isolation signal were the Division 2 isolation valves associated with the drywell ventilation monitor and the drywell floor and equipment sumps. "The specific train and system actuated was the Primary Containment Isolation System [PCIS] Division 2 portion of the Group 2 isolation circuit (i.e. half group isolation). This was a partial actuation affecting only half of the logic and causing isolation of two systems. Based on the inadvertent actuation of the affected PCIS relays, the system isolated and functioned as expected. The isolation signal was reset at 0230 and the affected systems restored to service." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-12-15
52435 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2016-12-15 04:10 | 2016-12-15 06:55 | 2016-12-15 | ALERT DECLARED - CATASTROPHIC FAILURE OF AN EMERGENCY DIESEL GENERATOR "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "During a scheduled surveillance test run of the PVNGS [Palo Verde Nuclear Generating Station] Unit 3 'B' Train Emergency Diesel Generator, there was a catastrophic failure of a piston to include crankcase damage and diesel trip. The Emergency Plan has been entered and an ALERT was declared at 0410 [MST] on 12/15/16 based on an explosion resulting in visible damage to a safety system required for safe shutdown. The cause of the failure is unknown at this time. PVNGS Fire Department responded and no fire was observed. Unit 3 remains on line at 100% power. No other safety functions are impacted." No personnel injuries occurred. The unit is in a ten day technical specification on an emergency diesel generator being inoperable. The licensee notified the NRC Resident Inspector. Notified DHS, DOE, EPA, FEMA, NICC, USDA, HHS, FDA, NSSA, Mexico, and OIP (Skeen). * * * UPDATE AT 0947 EST ON 12/15/2016 FROM MICHAEL GOODRICH TO MARK ABRAMOVITZ * * * "This serves as the notification of the termination of Alert HA2.1 declared at 0410 MST at Palo Verde Nuclear Generation Station. The event terminated at 0636 MST." The licensee will notify the NRC Resident Inspector. Notified R4DO (Keller), NRR EO (Miller), IRD (Stapleton), DHS, DOE, EPA, FEMA, NICC, USDA, HHS, FDA, NSSA, Mexico, and OIP (Skeen). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Power Operation; FMode3: Power Operation | ALERT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-12-15
52434 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-12-14 23:45 | 2016-12-15 03:40 | 2017-03-17 | SECONDARY CONTAINMENT MOMENTARY LOW PRESSURE DUE TO HIGH WINDS "On December 14, 2016, starting at 2345 EST, high wind conditions encountered on site resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met numerous times. The duration of time that the secondary containment Technical Specification was not met was approximately one second for each instance. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. At 0300 EST on December 15, 2016, high wind conditions had subsided and secondary containment vacuum was greater than the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) and steady, and the LCO was exited. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-12-15
52433 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2016-12-13 15:00 | 2016-12-14 16:12 | 2016-12-14 | NON-PERFORMANCE OF ADMINISTRATIVE ITEM RELIED ON FOR SAFETY "On 12/13/2016 at approximately 1500 [PST], the AREVA Nuclear Criticality Safety Staff was notified that an administrative IROFS [Item Relied On For Safety] control had not been performed in the ELO raffinate treatment process. The ELO raffinate treatment process requires the sampling of a favorable geometry process tank (IROFS 306) that is discharged to one of two sets of favorable geometry quarantine tanks. When one of the two sets of quarantine tanks is full, the input is diverted to the other set of tanks and the set that is full is recirculated and sampled for U [Uranium] concentration (IROFS 307). When both sample results have been confirmed to be acceptable the discharge valve on the transfer line may be unlocked and the raffinate solution transferred to a filter press. Sampling of the process tank was completed as required, however; the quarantine tank transfer line was unlocked and contents were pumped to the filter press without completing the required independent sampling of the quarantine tank. AREVA is conservatively reporting this plant condition under 10CFR70 Appendix A, because an accident sequence that could result in accidental nuclear criticality may not have remained highly unlikely in the absence of IROFS 307." The licensee will notify NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2016-12-14
52432 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-12-14 | 2016-12-14 15:10 | 2017-03-17 | SECONDARY CONTAINMENT PRESSURE BOUNDARY OUT OF SPECIFICATION "On December 14, 2016, at 1314 EST, the startup of the Reactor Building HVAC [Heating, Ventilation and Air Conditioning] system resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met for approximately 1 second. The maximum secondary containment pressure observed during that time was approximately 0.07 inches of vacuum water gauge. "Secondary containment pressure was returned to within the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) by Reactor Building HVAC and Standby Gas Treatment System already in operation. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-12-14
52431 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-12-13 | 2016-12-14 14:39 | 2016-12-14 | AGREEMENT STATE REPORT - DAMAGED DENSITY GAUGE The following report was received from the State of California via email: On December 13, 2016, the RSO [Radiation Safety Officer] of Cal Land Engineering, contacted the RHB [California Radiologic Health Branch] at the Brea, CA office about a gauge that had been run over. The gauge was a CPN MC-3, S/N M310706239 (10 mCi Cs-137, 50 mCi Am:Be-241). The gauge operator had removed the gauge from it's transport case, but had not set up or used the gauge at the site (the Cs-137 source was still in the shielded position). The operator then stepped away from the gauge to answer his cell phone. While the operator was on the phone, a pickup truck backed into the gauge. The gauge body remained intact, but the guide tube and source rod had been sheared off the body of the gauge. After the incident, the area was isolated and the operator contacted the RSO, who then contacted RHB. Pictures were provided by the gauge operator and forwarded to RHB for review. After the pictures confirmed that the gauge body was intact, the RHB inspector authorized the operator to place the gauge in the storage case, secure it for transport, and then return the gauge to their [licensee's] office. An RHB inspector met the operator at their office to inspect the gauge. A Canberra Inspector 1000 with the LaBr (IPROL-1) and neutron (IPRON-N) probes was used to verify the sources remained in the gauge. The Cs-137 source was identified by the Inspector 1000 and a neutron dose of 20 counts per second (with a background of 0 counts per second) confirmed the Am:Be-241 source was present. A Victoreen 450 CHP was used to survey the gauge. The contact dose rate was 20 mR/hr (background 0.01 mR/hr), which is consistent for an MC-3 gauge. The gauge will remain in storage until disposal can be arranged. Maurer Technical Services will be used to assist in the disposal. California 5010 number: 121316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-12-22
52430 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-12-14 09:45 | 2016-12-14 11:20 | 2016-12-14 | OFFSITE NOTIFICATION MADE FOR A SEWAGE LEAK "At 0945 EST on 12/14/16, Fermi 2 discovered a sanitary sewer system leaking through a covered manhole in the Owner Controlled Area. Approximately 100 gallons of the sewage has entered the storm drain system. The sewage leak was stopped at 1030. A local sanitary contractor is currently responding to the site to clean the affected areas. The cause and extent of the sewage teak is under investigation. "Reports to the Michigan Department of Environmental Quality (MDEQ), the local health department (Monroe County), and the local news media are in progress. Since these reports are in the process of being made, this is considered a News Release or Notification to Other Government Agencies, therefore this event is reportable under 10CFR50.72(b)(2)(xi). "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-12-14
52429 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2016-12-08 | 2016-12-14 10:14 | 2016-12-14 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following report was received via e-mail: "During an annual inventory review, the licensee discovered a tritium exit sign was missing/lost. The licensee notified our office [Nebraska Office of Radiological Health] via phone call on 12/8/16 and followed it up with an e-mail the same day. The licensee stated there has been new construction in the area and assumes the sign went missing during this time." Manufacturer: Safety Light Corp Model: 880-12-6R-20 Source Activity: 11.5 Ci Nebraska Event: NE160003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2016-12-22
52428 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2016-11-23 | 2016-12-14 09:23 | 2016-12-14 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received via e-mail: "Doan College contacted our office [Nebraska Office of Radiological Health] by phone on November 23, 2016 to notify our office of two lost exit signs. Licensee was notified they would need to send in written notification. In a letter dated November 29, 2016, the licensee indicated that multiple renovations were made to the building housing the exit signs between 2006 and 2016. The exit signs were likely removed during one of these renovations. They also estimate that the incident was not caught prior to this due to personnel changes." Manufacturer: Safety Light Corp. Model: 880-12-6-10 Source Activity: 7.5 Ci Nebraska Event: NE160002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2016-12-22
52427 | 0 | TE CONNECTIVITY |  |  |  |  | 2016-12-09 | 2016-12-13 16:08 | 2016-12-13 | PART 21 NOTIFICATION - DEFECTIVE SAFETY-RELATED RELAYS SUPPLIED BY TE CONNECTIVITY The following information is a summary of a letter of nonconformance submitted by TE Connectivity: Limerick Generating Station reported that four TE Connectivity supplied relays failed power labs analysis. The relays are TE part number 1-1431775, ETR14I3D004. The affected relays appear to be those in date code ranges 1604 and 1612. The preliminary evaluation revealed an incorrect orientation of one capacitor installed on the printed circuit board. The relays were purchased by Curtiss-Wright (8 relays), Limerick Generating Station (8 relays) and NextEra (2 relays). An investigation is ongoing. Point of Contact: Oswaldo R Vargas, Quality Manager, TE Connectivity Aerospace, Defense and Marine Division 1396 Charlotte Highway Fairview, NC 28730 E-mail: oswaldo.vargas@te.com Telephone: 828-338-1093 Fax: 828-338-1101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-12-13
52426 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-12-13 14:10 | 2016-12-13 14:40 | 2016-12-13 | OFFSITE NOTIFICATION - WATER CONTAINING TRITIUM SPILLED INTO STORM DRAIN "On 12/13/16 at 1410 [EST], the following voluntary communication was made to the State of Tennessee in accordance with Tennessee Valley Authority's (TVA) guidance for communicating inadvertent radiological spills/leaks that are below regulatory reporting requirements to outside agencies and in alignment with NEI 07-07, 'Industry Ground Water Protection Initiative'. "On 12/12/16, Sequoyah Nuclear Plant determined that a spill of greater than 100 gallons (approximately 3000 gallons) of condensate storage tank water with tritium levels of 1560 pCi/L [picocuries per liter] was spilled to a yard drain. The spill occurred on 12/5/16, during the filling of the Unit 1 #4 steam generator when a hose connection on a temporary fill skid failed. No elevated tritium levels have been detected at the Sequoyah Yard Drainage Pond before or after the event. "This is reported in accordance with 10CFR50.72(b)(2)(xi), the required reportable threshold for tritium is 20,000 pCi/L." The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-12-13
52425 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2016-12-10 08:48 | 2016-12-10 12:31 | 2016-12-10 | MANUAL REACTOR SCRAM DUE TO HIGH MAIN TURBINE VIBRATIONS "On December 10, 2016 at 0848 EST, [operators at] Nine Mile Point Unit 1 manually scrammed the reactor due to high vibrations on the Main Turbine. Cause of the high vibrations is being investigated. "Following the scram, the High Pressure Coolant Injection (HPCI) system automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI system actuation signal on low reactor pressure vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater system and is not an emergency core cooling system. At 0849, RPV level was restored above the HPCI system low level actuation set point and the HPCI system initiation signal was reset. Pressure control was established on the turbine bypass valves, the preferred system. No Electromatic relief valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. "The unit is currently implementing post scram recovery procedures." The licensee has notified the state of New York Public Service Commission and the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-12-10
52424 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-12-09 | 2016-12-10 11:12 | 2016-12-10 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE COULD NOT BE RETRACTED The following was received from the State of Texas via email: "On December 10, 2016, the Agency [Texas Department of State Health Services] was notified that on December 9, 2016, the licensee [while working at Exxon Mobil in Beaumont, Texas] was required to perform a source retrieval of a 74.9 curie iridium-192 source. The exposure device associated with the source is a QSA 880 exposure device. The licensee reported the exposure device fell on the guide tube and crimped it to a point where the source could not pass by. The radiographers verified their boundaries and contacted their radiation safety officer. The licensee sent a qualified recovery team to the location. The recovery team cut the guide tube and was able to retract the source. No individual received an exposure that exceeded any limits. No member of the general public was exposed as a result of this event. The licensee stated the camera would be sent to the manufacturer for inspection. The licensee stated they would provide additional information on December 13, 2016. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I - 9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-12-19
52423 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-12-09 20:42 | 2016-12-09 23:46 | 2016-12-10 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On December 09, 2016 at 1734 EST, U2 Train-A NSCW [Nuclear Service Cooling Water] Transfer Pump #8 tripped during Return To Service Surveillance testing for Train-B NSCW Transfer pump #7. Technical Spec 3.7.9 Condition E entered at 1734 with Required Actions to be in M3 [mode 3, Hot Standby] in 6 hours AND M4 [mode 4, Hot Shutdown] in 12 hours. A unit shutdown was commenced at 2042 EST [as a conservative measure] to comply with TS 3.7.9 Condition E. "At 1937, U2 B-train NSCW Transfer Pump #7 was declared operable and TS 3.7.9 Condition E was exited. The plant is currently raising power to 100%." The licensee notified the NRC Resident Inspector. | 0 | 82 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-12-10
52422 | 0 | JANX INTEGRITY GROUP |  |  |  |  | 2016-12-09 09:00 | 2016-12-09 17:21 | 2016-12-09 | RADIOGRAPHY SOURCE BECAME TEMPORARILY STUCK OUTSIDE OF SHIELD While preparing to perform his first exposure of the day, the radiographer determined that the source became stuck near the camera and guide tube connection. He notified the client, verified his boundaries, and contacted the Radiation Safety Officer (RSO). After discussion with the radiographer, the RSO believed the source was lodged due to freezing temperatures and a small amount of ice within the guide tube. The radiographer was able to obtain a heater and, after about an hour of warming the guide tube, was able to retrieve the source into the camera normally. No overexposures occurred due to this event. The camera is a SPEC-150 that contains 47 Ci of Ir-192. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-12-19
52421 | 0 | ANS CONSULTANTS |  |  |  |  | 2016-12-08 16:30 | 2016-12-09 17:02 | 2016-12-12 | TROXLER MOISTURE DENSITY GAUGE DAMAGED BY PAVING EQUIPMENT While preparing to conduct a measurement, the gauge operator placed the gauge on the asphalt. A paving roller operator did not see the gauge and ran it over. At the time of the accident, the source was in its shielded and locked position. While the case and controls of the gauge were damaged, there was no damage to the source or the shield. As a precaution, the Radiation Safety Officer contacted the local hazmat team to confirm the source was not damaged. A leak check swipe was performed by the gauge owner and it was sent to Troxler for evaluation. There were no overexposures to the workers or members of the public. The gauge is a Troxler model 3430 (serial number 37669). It contains a 9 mCi Cs-137 source (serial number 77-4904) and a 44 mCi AmBe source (serial number 78-2427). The gauge will be returned to Troxler for disposal. * * * UPDATE FROM THE STATE OF NEW JERSEY (DANIEL RICE) TO HOWIE CROUCH AT 1544 EST ON 12/12/16 * * * The licensee also reported the event to the New Jersey Department of Environmental Protection (NJDEP) at 1630 EST on 12/9/16. Additional information included: "The license reported the gauge user was nearby, but not in direct observation of the device, at the time of the incident. "NJDEP will be investigating further. The incident is reportable within 24-hours under N.J.A.C. 7:28-51.1 (10 CFR 30.50(b)2). NJDEP is tracking this incident internally as incident ID# C62454. NMED Report No. to be assigned." Notified R1DO (Schroeder) and NMSS_EVENTS_NOTIFICATION Resource, both via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-12-19
52420 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-12-07 | 2016-12-09 10:54 | 2016-12-09 | AGREEMENT STATE REPORT - CANCER TREATMENT DOSE LESS THAN PRESCRIBED The following was received from the state of Ohio via e-mail: "On 12/9/16, the licensee reported a medical event that occurred on 12/7/16 and was discovered on 12/8/16. During a prostate seed implant procedure, the patient received a dose that was 30.57% less than the prescribed dose. The patient was informed and the physician is evaluating if a boost will be administered. The patient is not expected to have any adverse affects." Ohio report: OH160010. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-12-19
52419 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2016-12-08 22:37 | 2016-12-09 05:29 | 2017-01-19 | HPCI SURVEILLANCE FAILURE "On 12/08/16 at approximately 2237 [EST], the Unit 2 HPCI [High Pressure Coolant Injection] system failed to meet surveillance testing requirements for achieving rated flow at greater than or equal to a minimum test pressure established per the surveillance. Operations declared the HPCI system inoperable and entered Technical Specification 3.5.1 Condition C for HPCI being inoperable. Other standby systems (Reactor Core Isolation Cooling and low pressure emergency core cooling systems) are operable. "HPCI is a single train system. Therefore, per NUREG-1022, this condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system required to mitigate the consequences of a design event. "This condition has been entered into the Corrective Action program (IR 3951006). Investigation of the exact failure condition is in progress so that repairs can be made." At the surveillance flow of 5,000 gpm, the system was approximately 80 psi below the required pressure of 1,278 psi. Technical Specification 3.5.1, Condition C, is a 14-day Limiting Condition of Operation. The NRC Resident Inspector will be notified. * * * RETRACTION AT 1440 EST ON 01/19/17 FROM ELMER KAUFFMAN TO S. SANDIN * * * The licensee provided the following information as the basis for retracting this report: "This is a retraction of an event notification made on 12/09/16 at 0529 EST (EN #52419). This event was initially reported pursuant to 10 CFR 50.72(b)(3)(v)(D) as a condition that, at the time of discovery, was believed to have prevented the fulfillment of the High Pressure Coolant Injection (HPCI) system safety function. "On 12/08/16 at 2237 EST, the Unit 2 HPCI system was declared inoperable due to failing to meet surveillance testing requirements for achieving rated flow at greater than or equal to a minimum test pressure established per the surveillance. Prompt troubleshooting was performed and it was determined that an adjustment to the HPCI turbine governor control system was required. This adjustment was performed and HPCI was returned to an operable status on 12/09/16. "Subsequent to this occurrence, Engineering has completed an evaluation that concluded that HPCI was capable of fulfilling its safety function and that the associated Technical Specification (TS) Surveillance Requirement (SR) 3.5.1.8 was met. The evaluation concluded that HPCI was degraded, but met the threshold for TS operability. "The NRC Senior Resident has been informed of this retraction." Notified R1DO (Kennedy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-12-09
52418 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-12-08 13:30 | 2016-12-08 21:05 | 2016-12-08 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO FAILED AIR INTAKE FAN "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality of the Technical Support Center (TSC) Ventilation System was discovered on December 8, 2016, at 1330 [EST]. The issue involved a loss of the ability to maintain habitability of the TSC due to a failed outside air intake fan. The repair of the equipment failure is currently being planned. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. The secondary TSC has been notified that relocation may be necessary upon facility activation. This condition does not affect the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-12-08
52417 | 0 | COMMUNITY MEDICAL CENTER |  |  |  |  | 2016-12-07 10:30 | 2016-12-08 10:51 | 2016-12-08 | SURFACE CONTAMINATION INSIDE HIGH DOSE RATE AFTERLOADER On 12/7/16 at approximately 1030 MST, surface contamination was discovered on the interior of a High Dose Rate (HDR) afterloader. The contamination is limited to the inside of the housing and the interior portions of the transfer cables. The contamination was discovered by the manufacturer when the manufacturer was replacing the Ir-192 seeds used by the afterloader. Direct radiation readings could not be taken due to the proximity to the sources. Wipes were observed at 200 to 4000 counts per minute. There was no observed damage to the sources. There was no contamination of personnel. The room has been secured. The resolution planned is for the manufacturer to replace the afterloader. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2016-12-16
52416 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-12-07 22:40 | 2016-12-08 02:29 | 2016-12-08 | CONTROL ROOM FAN SWITCH MIS-POSITIONED "At 2240 [CST], December 16, 2016, it was identified that HV-SW-(SF-C-1A)(CS), control switch for supply fan SF-C-1A for HV-FAN-(SF-C-1A), main control room A/C unit supply fan had been inadvertently been placed to OFF, leaving no supply fan running as required to maintain CREFS [Control Room Emergency Filtration System] operable. This was discovered following the performance of 6.1HV.302 Essential Control Building Ventilation Functional Test (DIV 1). "It is estimated that the control switch was placed in OFF at approximately 2220 during preparation of 6.1HV.302 per S.O.P. 2.2.38. Time of discovery was 2240. This resulted in an unplanned LCO entry for the CREFS. CREFS was subsequently declared inoperable and LCO 3.7.4 Condition A was entered, with required action A.1 to restore CREFS to operable status within 7 days. The switch was restored to its required position at 2247 and CREFS was subsequently declared operable and the referenced LCO was exited. "CR-CNS-2016-08744 was written to document the unplanned inoperability." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-12-08
52415 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2016-12-07 18:00 | 2016-12-07 23:39 | 2016-12-07 | UNISOLABLE REACTOR COOLANT SYSTEM BOUNDARY LEAKAGE "While TMI [Three Mile Island] Unit 1 was in a hot shutdown condition, leakage was identified coming from an RCS [reactor coolant system] pressure boundary on a welded connection on the 'A' Reactor Coolant Pump. The leakage is unisolable from the RCS and is less than 0.5 gpm. Planned actions are to cooldown Unit 1 to cold shutdown conditions in order to repair the leakage." The licensee will be notifying the Pennsylvania Emergency Management Agency and has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-12-07
52414 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-12-07 13:43 | 2016-12-07 17:24 | 2016-12-07 | DISCOVERY OF NON-CONFORMING CONDITIONS DURING TORNADO HAZARDS ANALYSIS "During the evaluation of tornado missile vulnerabilities and the potential impacts to Technical Specification (TS) plant equipment, it was concluded that the following SSCs [systems, structures, and components] were vulnerable to tornado generated missiles. "The Service Water Intake Structure (SWIS) intake and exhaust ventilation hoods, located on the roof of the SWIS, are not adequately protected from missiles generated by a tornado. Should a tornado-generated missile strike the SWIS intake and exhaust ventilation hoods, the hoods could crimp thus reducing air flow and challenging the performance of their heating and cooling safety functions. If the intake hoods were damaged or removed due to a missile strike, entry of rainwater could occur due to severe weather high wind velocity, and could affect safety related electrical equipment in the rooms directly below the hoods. These potential conditions could render Service Water trains inoperable on either or both units. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with EGM-15-002 and DSS-ISG-2016-01 (enforcement discretion and interim guidance documents). Required actions have been taken. Corrective actions will be documented in a follow up licensee event report. "The NRC Resident Inspector will be notified." The licensee is evaluating the operability of the service water system. Should one train be declared inoperable, the licensee would be in a 72 hr. LCO action statement. If both trains are inoperable, then the licensee would enter T.S. 3.0.3. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-12-07
52413 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2016-10-17 15:19 | 2016-12-07 16:59 | 2016-12-07 | INVALID ENGINEERED SAFETY FEATURES ACTUATION SYSTEM (ESFAS) SIGNAL "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This telephone notification is being made pursuant to the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) and 50.73(a)(1) to describe an invalid actuation of the Palo Verde Nuclear Generating Station (PVNGS) Unit 1 train A emergency diesel generator (EDG), train A high pressure safety injection (HPSI) pump, and train A essential spray pond (SP) pump. These components are portions of the emergency ac electrical power system, the emergency core cooling system, and the emergency service water system, respectively, as described in 10 CFR 50.73(a)(2)(iv)(B). "On October 17, 2016 at approximately 1519, Mountain Standard Time, a portion of the Unit 1 train A engineered safety features equipment was automatically started by the balance-of-plant (BOP) engineered safety features actuation system (ESFAS) while the plant was at steady state conditions. Initiation of the train A ESFAS actuation signal was momentary, and the ESFAS actuation signal cleared 0.2 seconds after being initiated. The invalid ESFAS signal initiated a test-mode start signal for the train A EDG and started the train A HPSI pump. The train A essential SP pump started in support of the train A EDG. "All actuated components started and functioned successfully. No systems started in response to actual plant conditions, and no actuation was required to mitigate the consequences of an event. The invalid HPSI actuation neither resulted in an emergency core cooling system discharge, nor should it have. The invalid actuation was the consequence of a spurious momentary signal into the BOP-ESFAS control panel due to an intermittent high resistance electrical connection. The event was entered into the PVNGS corrective action program. There were no adverse impacts to public health and safety nor to plant employees. "The NRC Resident Inspectors have been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-12-07
52412 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2016-11-30 16:00 | 2016-12-07 13:12 | 2016-12-07 | REACTOR COOLANT PUMP BREAKER CABINET MODIFICATION - ITAAC POSTCLOSURE NOTIFICATION "In accordance with 10 CFR 52.99(c)(2), Vogtle Units 3 and 4 Construction is making this notification to NRC for determining that Inspection, Test, Analysis, and Acceptance Criteria (ITAAC) 2.6.01.02.ii (ECS System Seismic Category I Equipment Design Basis Loads) for both units requires additional actions to restore its completed status. The Closure Notification for this ITAAC (NRC Index No. 580) was originally submitted on May 17, 2016 (reference ML 16138A080 and ML 16166A030). "On November 1, 2016, it was determined by the Vogtle 3&4 Contractor that modifications to the Reactor Coolant Pump (RCP) breaker (i.e., switchgear) cabinet design were required to ensure compliance with the applicable portions of IEEE 384, 'Standard Criteria for Independence of Class 1E Equipment and Circuits.' The modification involves an engineering change which adds different equipment to the RCP Breaker cabinet that function to trip the RCP. The new components were not previously qualified for use in the RCP breaker cabinet assembly. "Additional seismic qualification type testing and analysis of components are being performed for the added components in the RCP breaker. Update of the Equipment Qualification Data Package and Equipment Qualification Summary Report for the RCP breaker to confirm the breaker withstands seismic design basis loads and Licensee's acceptance is in progress. The revised ITAAC Completion Notice will be submitted to the NRC once all related ITAAC activities have been completed." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW | [5 empty] | 0 | 2016-12-07
52411 | 0 | ACRUEN USA INSPECTIONS |  |  |  |  | 2016-12-07 06:30 | 2016-12-07 11:27 | 2016-12-07 | RADIOGRAPHY CAMERA LOST WHEN BARGE SANK IN BERING SEA At approximately 1030 EST, a QSA 880 industrial radiography camera containing an Ir-192 source of approximately 26.3 Ci (source serial number - 32186G) was lost when the barge named Exito sank in the Bering Sea outside Dutch Harbor, Alaska. The ship was in transit and the camera was stored in a pelican case and not in use, with the source in the protected position. There were no unintended exposures to individuals. The licensee has notified the local area Coast Guard command. Notified the following Federal Agencies: DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, EPA EOC. Notified the following Federal Agencies via email only: FDA EOC, Nuclear SSA, FEMA National Watch Center, and DNDO-JAC. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-12-15
52410 | 0 | AGILENT TECHNOLOGIES |  |  |  |  | 2016-11-07 | 2016-12-07 09:15 | 2017-01-27 | LOST SOURCES Agilent Technologies is a manufacturer of a part containing an electron capture detector (ECD) that fits into a gas chromatograph. The ECD contains an embedded sealed source (Ni-63; 15 milliCuries) and is manufactured in Shanghai, China and is transferred into the United States through the JFK Airport Worldwide Flight Services Warehouse. When the licensee's Philadelphia truck shipping service attempted to retrieve the two ECD sources at the JFK warehouse, the sources were discovered missing. The warehouse was searched without success. The ECD source serial numbers are U30355 and U30356. The model number is 62397AECD. Agilent Technologies holds an NRC license and is located at 2850 Centerville Road, Wilmington, DE 19808. * * * UPDATE ON 1/27/17 AT 1457 EST FROM DAVID BENNETT TO DONG PARK * * * As a corrective action, the licensee has changed warehouse operations to a different warehouse used to receive devices manufactured in China. Notified R1DO (Welling) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-12-15
52409 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2016-12-05 06:38 | 2016-12-05 16:24 | 2016-12-05 | FITNESS FOR DUTY "A non-licensed supervisory employee had a confirmed positive for a prohibited substance during a random fitness-for-duty test. The individual's unescorted access to the plant has been denied. "The licensee has notified the NRC Resident Inspector." | 100 | 23 | 0 | 100 | 23 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 26.719 |  |  |  | 0 | 2016-12-05
52408 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-12-01 12:30 | 2016-12-05 15:11 | 2016-12-05 | AGREEMENT STATE REPORT - NON CONTAMINATED WATER LEAK INTO A CONTAMINATED BERMED AREA The following report was received from the State of Tennessee via email: "On December 3, 2016, M & EC [East Tennessee Materials & Energy Corporation] staff notified DRH [Tennessee Division or Radiological Health] regarding an event in which a [Fire Protection] water line outside an M & EC building began leaking [on 12/1/16]. The water entered the building flooding a non-contaminated area (radiologically clean) and a bermed contaminated area. After the leak was stopped, water removal was performed Friday and over the weekend. M & EC staff were able to segregate removal of water from the clean area from removal of water from the bermed contaminated area. A total of [approximately 136,000 to 242,000] gallons was removed, a large percentage of which was in the contaminated area. M & EC is in process of completing the clean up, and is also in the process of performing radio-analysis of both the clean and the contaminated water. The contaminated bermed area had an average contamination of [approximately] 15,000 dpm/100 cm2." No release to the public has occurred and a follow-up investigation by the Tennessee DRH is being conducted and additional information will be provided by DRH when available. Report #: TN-16-173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-12-13
52407 | 0 | VALCOR ENGINEERING CORPORATION |  |  |  |  | 2016-12-05 | 2016-12-05 14:09 | 2016-12-05 | PART 21 - NON-CONFORMING COVER MACHINING ON SOLENOID VALVE The following is a synopsis of the Part 21 report that was received via fax: "Cover Machining is installed on upper section of Solenoid Valve and it allows for the electrical connection to the valve solenoid and protects inside wiring of the solenoid from environmental condition. Cover machining part number V52636-567 has 0.190 radius (Drawing V52620-50 Zone D3) which was machined too deep removing material from surface needed for proper O-ring seal. The lack of material exposes part of the sealing O-ring which could diminish the O-ring sealing capability. With O-ring sealing capability diminished, Valcor cannot ensure that valves with Cover Machining Installed on Solenoid Assembly will perform its safety function during all postulated events. "This item has historically been manufactured by machining a casting. For the lot involved, castings were not available. Authorization was given to manufacture the Cover directly from suitable bar stock. To accomplish this, Valcor's vendor used the casting drawing and casting machining drawing to manufacture the finished machined part. The combination of these two drawings had insufficient control on the corner radius, resulting in this nonconformance. "All defective covers in stock have been quarantined and a nonconformance report has been generated. Lack of location controlling dimension on the Cover Machining drawing for 0.190 radius was discovered to be the root cause of the defect. Valcor has created and released a new engineering drawing that properly controls the location of 0.190 radius. This action has been completed as of 11/22/2016. Engineering Manager-Nuclear was responsible to this action. "Valcor is in a process of notifying all affected customers. "Customers: Ameren, Valve Part Number V526-6000-16 (Stock# 7731643), S/N 9, QTY 1, Location Ameren Missouri - Callaway Bruce Power (BPC), Valve Part Number V526-6000-20 (Cat ID 142129), S/N 28-36, QTY 9, Bruce NGS "Note: All 9 valves supplied to BPC have been returned to Valcor for nameplate correction and are accounted for. "If you have any questions or addition information is needed regarding this matter, please contact Fran Lucano at 973-467-8400." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-12-05
52406 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2016-12-03 22:24 | 2016-12-04 01:48 | 2016-12-04 | AUTOMATIC REACTOR TRIP CAUSED BY MAIN TURBINE TRIP "On 12/3/16 at 2224 EST, Calvert Cliffs Unit-2 experienced an automatic reactor trip from full power due to a leak in the Unit-2 Main Turbine Electro-Hydraulic Control (EHC) system. The EHC leak caused the Unit-2 Main Turbine governor valves to close, resulting in a turbine trip and automatic reactor trip. The site Outage Control Center is manned, and investigation into the cause of the leak is underway. Unit-2 remains stable in Mode 3 with normal heat removal. "Unit-1 remains at full power and was not affected by the trip." The plant is in a normal shutdown electrical lineup. All Control rods fully inserted and no primary or secondary safety relief valves lifted during the trip. The licensee has notified the NRC Resident Inspector. The licensee will be notifying Calvert County. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-12-04
52405 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-12-01 13:31 | 2016-12-02 13:23 | 2016-12-02 | FITNESS FOR DUTY - POLICY VIOLATION A Supervisor employee failed to report for completion of random testing following notification. The employee's access to the plant has been suspended. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.719 |  |  |  | 0 | 2016-12-12
52404 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-12-01 10:14 | 2016-12-01 15:05 | 2016-12-01 | OFFICE AREA ALARM AUDIBILITY DISABLED "On December 1, 2016, at 1014 hours (EST), the speakers for a portion of the bottom floor of Building 305, office and lunch room areas, were inadvertently disabled during construction activities to remove obsolete equipment. Special Nuclear Material (SNM) is not processed, handled, or stored within the areas where the speaker system was disabled; however, these areas require evacuation in the unlikely event of a nuclear criticality accident as described in the NFS [Nuclear Fuel Services] Emergency Plan. "There were no actual radiological or other nuclear safety consequences. The potential consequence was that in the event of a nuclear criticality accident, evacuation could have been delayed for those personnel within these areas with a resultant increase of postulated doses. Additionally, awareness of a fire event could have been delayed for these same personnel. A series of compensatory actions were taken including restricting access to the affected areas to essential personnel, and establishing radio communications between the personnel in these areas and the personnel continuously monitoring the alarm station panel. "On December 1, 2016, at approximately 1159 hours (EST), full compliance was restored by repairing a disabled cable in the speaker circuit and by successfully performing a speaker system test in the affected areas. "The licensee notified the NRC Resident Inspector on. December 1, 2016." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2016-12-09
52403 | 0 | ATC NUCLEAR |  |  |  |  | 2015-12-08 | 2016-12-01 13:18 | 2016-12-01 | PART 21 - PAWL FASTENERS FAILED TO PROVIDE SUFFICIENT STRUCTURAL SUPPORT The following is an excerpt of a Part 21 received via email: "On December 8, 2015, ATC Nuclear performed seismic qualification testing on an ATC Nuclear Assembly with a W-2 Electroswitch Switch, Part Number W2-45B640-84 and W2-45B640-85, for TVA Watts Bar 2. During the first Safe Shutdown Earthquake (SSE) test run, the pawl fasteners used to secure the assembly in a test fixture failed to provide sufficient structural support, rendering the switch assembly non-captive. "Based on the testing and analysis, ATC Nuclear concluded that the minimum force required to maintain structural integrity cannot be achieved with the existing pawl fasteners installed in the ATC Nuclear Assembly. This condition, if left uncorrected, could potentially cause a failure of the switch assembly to maintain its mounting configuration during a seismic event. This information provides the basis to establish a deviation in the pawl fasteners provided with the ATC Nuclear assembly that could be considered a potential defect as defined in 10 CFR Part 21. It is worth noting that there have been no failures identified by customers associated with this potential defect. "If you have any questions or need additional information regarding this matter, please contact Ray Chalifoux at (865) 384-0124." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-12-01
52402 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-11-29 13:00 | 2016-11-29 16:10 | 2016-11-29 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE The following was received from the State of Arizona via email: "During a routine and unannounced inspection, the Arizona Radiation Regulatory Agency found an incident while reviewing personnel dosimetry reports. In quarterly reports covering dates 4/1/14-6/30/14, 7/1/14-9/30/14, 10/1/14-12/31/14, a single worker received a dose of 3017 mrem, 3497 mrem, and 853 mrem respectively. This resulted in a yearly total of 7367 mrem, above the 5000 mrem yearly limit for radiation workers. The overexposure was not reported to the Arizona Radiation Regulatory Agency. "The [Arizona Radiation Regulatory] Agency is continuing to investigate the event. "First Notice: 16-027" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-12-07
52401 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-11-29 13:00 | 2016-11-29 16:08 | 2016-11-29 | AGREEMENT STATE REPORT - TROXLER DENSITY GAUGE STUCK SHUTTER The following was received from the State of Arizona via email: "During a routine and unannounced inspection, the Arizona Radiation Regulatory Agency discovered a Troxler 3400 series portable density gauge (Serial# 6666) was in storage with a shutter that was stuck open. The gauge contains approximately 8 milliCuries of Cesium-137 and 40 milliCuries of Americium-241. The licensee was informed of the malfunction and will have a service company come and repair the gauge. "The [Arizona Radiation Regulatory] Agency is continuing to investigate the event. "First Notice: 16-026" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-12-07
52400 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-11-29 07:32 | 2016-11-29 09:54 | 2016-11-29 | OFFSITE NOTIFICATION DUE TO CHEMICAL SPILL ONSITE "On 11/29/16 at 0654 EST, a chemical spill of approximately 525 gallons of Flo-guard was reported to the main control room from the raw water system chemical treatment control building (near the intake pumping station). No personnel injuries have resulted from this spill. The spill has stopped and is contained to the immediate area of the building. The spill has not reached the waters of the United States. The hazardous constituent of Flo-guard is Zinc Chloride. "Source of spill was a piping failure that allowed the contents of a storage tank to drain onto the ground in the immediate vicinity overnight. The area has been contained and does not impact any plant operations. "At 0728, TVA determined that due to the volume of spill (approximately 525 gal.) being greater than 306 gal. of Zinc Chloride, this event is reportable under the WBN [Watts Bar Nuclear] Integration Pollution Prevention Plan. The Shift Manager notified the National Spill Response Center at 0732 and the Tennessee Emergency Management Agency at 0738. Rhea County Emergency Response, Nuclear Duty Officer and NRC Resident have been informed. "This is being reported under 10 CFR 50.72(b)(2)(xi), 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made,' due to the notification of other government agencies of the spill." | 100 | 85 | 0 | 100 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-11-29
52399 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2016-11-29 01:45 | 2016-11-29 06:19 | 2016-11-29 | OFFSITE NOTIFICATION DUE TO 150 GALLON OIL SPILL IN THE SWITCHYARD "While operating in mode 1 at 100% rated thermal power an approximately 150 gallon oil spill occurred in the switchyard. Westar Energy personnel were performing corrective maintenance on the station's #6 transformer that required cleaning the oil. The #6 transformer was out of service at the time. The oil was being transferred to a group of hold up tanks. One of the tanks overflowed before the next tank could be placed in service. This resulted in the spill of approximately 150 gallons of UNIVOLT N 61 B, electrical insulating oil onto gravel and soil. The spill has been stopped. The oil had recently been sampled and there were no detectable polychlorinated biphenyls, PCBs. A clean up plan is being developed. Condition Report 00109759 has been generated. "The acting NRC Senior Resident has been informed." The reportable quantity for the oil is 5 gallons. The licensee has notified the State of Kansas Department of Health and Environment and the National Response Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-11-29
52398 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-11-28 21:05 | 2016-11-29 01:41 | 2017-03-17 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On November 28, 2016, starting at 2105 hrs. EST, high wind conditions encountered on site resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met numerous times. The duration of time that the secondary containment Technical Specification was not met was approximately 1 second for each instance. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. At 0055 EST on November 29, 2016, high wind conditions had subsided and secondary containment vacuum was greater than the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) and steady, and the LCO was exited. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM CHRIS MCALLISTER TO HOWIE CROUCH AT 1027 EST ON 11/29/16 * * * "On November 29, 2016, at 0242 EST, high wind conditions encountered on site resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met numerous times following the initial event notification. The duration of time that the secondary containment Technical Specification was not met was approximately 1 second for each instance. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure to within TS limits. High wind conditions are expected to decrease throughout the day. If additional instances are identified that require entry into the Technical Specifications (TS) for secondary containment pressure boundary not being met, another follow up notification will be performed. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Stoedter). * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-11-29
52397 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2016-11-28 10:50 | 2016-11-28 11:48 | 2016-11-28 | SAFEGUARDS REPORT An actual entry of an unauthorized person into a controlled access area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-11-28
52396 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-11-27 14:47 | 2016-11-27 21:22 | 2016-11-27 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "At 1447 [CST] on 11/27/2016 while troubleshooting a minor leak on the High Pressure Coolant Injection (HPCI) turbine, it was discovered that the HPCI turbine exhaust drain pot high level bypass switch was not functioning per design to support removal of condensate from the HPCI turbine casing. This resulted in some water accumulation within the HPCI turbine casing. Subsequently, HPCI was declared INOPERABLE and this issue is being reported under 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function at the time of discovery. The plant remains at 100 percent power with no challenges to the health and safety of the public. The NRC Resident Inspector has been notified." Technical Specification limiting condition for operation requires HPCI to be Operable within 14 days. The licensee will be notifying the State of Minnesota regarding the event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-11-27
52395 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2016-11-27 00:26 | 2016-11-27 03:08 | 2016-11-27 | MANUAL REACTOR TRIP WITH AUTOMATIC AUXILIARY FEEDWATER SYSTEM ACTUATION DUE TO VOLTAGE OSCILLATIONS "At 0026 [CST] on November 27, 2016, Farley Unit 1 was manually tripped from 100% reactor power due to voltage swings suspected to be caused by the Auto Voltage Regulator. All control rods fully inserted and Auxiliary Feedwater (AFW) auto-started as expected. "All systems responded as expected. The plant is currently stable in Mode 3 (Hot Standby). The cause of the main generator voltage oscillations is under investigation. "The NRC Resident Inspector has been notified." The trip was uncomplicated. Decay heat is being removed via the steam dumps to condenser. The plant is at normal operating pressure and temperature with auxiliary feedwater supplying the steam generators. The electrical grid is stable and supplying plant loads. All safety equipment is available, if needed. Unit 2 was unaffected by the event and remains at 100% power. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-11-27
52394 | 0 | ENERCON |  |  |  |  | 2016-09-28 | 2016-11-23 11:56 | 2017-02-09 | PART-21 NOTIFICATION - DESIGN BASIS ERRORS USING FLO-2D SOFTWARE The following report was received via e-mail: "This letter serves as an Interim Report in accordance with 10 CFR 21.21 pertaining to a potential defect associated with a design basis calculation delivered to First Energy Nuclear Operating Company's Perry Nuclear Power Plant. Subsequent to delivering this calculation, FLO-2D software errors were identified which resulted in erroneous outputs that affect the local intense precipitation calculation. These errors were discovered on September 28, 2016, at which time, ENERCON generated a Corrective Action Report (CAR) to address the issue. ENERCON has initiated a reevaluation of the calculation using the latest version of the software that will correct the errors in the calculation. "An evaluation of the reportability of this issue in accordance with 10 CFR Part 21 is not able to be completed within the 60-day evaluation period due the need to verify and validate the latest version of the software and then complete all the analysis required for updating the calculation. This evaluation is being tracked by CAR 2016-0335 and will be completed no later than February 10, 2017. "If you have any questions or need further clarifying information, please contact Nick Eggemeyer, Corporate Quality Assurance Manager, at (770) 590-2031." * * * UPDATE AT 0910 EST ON 12/13/2016 FROM TIMOTHY CLEARY TO MARK ABRAMOVITZ * * * The following update was received via e-mail: "This letter serves as an amendment to the 10 CFR 21.21 Interim Report filed on November 23, 2016, pertaining to a potential defect associated with a design basis calculation delivered to First Energy Nuclear Operating Company's Perry Nuclear Power Plant. Subsequent to delivery of the calculation, a standard, periodic review of the FLO-2D Pro software supplier website indicated that a new build of this software (version 16.06.16) had been issued. It replaced the software build (version 14.08.09) that was used for the above referenced design calculation. As a result of the model revision associated with FLO-2D, it was determined that the outputs were impacted which could affect this design basis calculation. These output changes were discovered on September 28, 2016, at which time ENERCON generated a Corrective Action Report (CAR) to address the issue. ENERCON has initiated a reevaluation of the calculation using this new build of the FLO-2D Pro software. "An evaluation of the reportability of this issue in accordance with 10 CFR Part 21 is not able to be completed within the 60-day evaluation period due the need to verify and validate the latest version of the software and then complete all the analysis required for updating the calculation. This evaluation is being tracked by CAR 2016-0335 and will be completed no later than February 10, 2017. "If you have any questions or need further clarifying information, please contact Nick Eggemeyer, Corporate Quality Assurance Manager, at (770) 590-2031." Notified the R1DO (Schroeder), R3DO (Cameron), and Part 21 Group (via e-mail). * * * UPDATE FROM TIMOTHY CLEARY TO DONALD NORWOOD AT 1602 EST ON 2/9/2017 * * * The following information was received via E-mail: "This letter serves as an evaluation summary in accordance with 10 CFR 21.21 pertaining to a potential defect associated with a design basis calculation delivered to FirstEnergy Nuclear Operating Company's Perry Nuclear Power Plant. The 10 CFR 21.21 Interim Report was filed on November 23, 2016. An Amendment to the 10 CFR 21.21 Interim Report was filed on December 12, 2016. "Subsequent to the filing of the Amendment to the Interim Report, the updated FLO-2D software, build 16.06.16, was verified and validated and a re-analysis performed. A comparison between the original analysis and the updated analysis using the updated software was then performed. This analysis indicates flood water level changes assumed in the Perry Nuclear Plant flooding analyses are small, -0.14 feet to +0.16 feet (-1.6 inches to +1.9 inches). "The comparative results between the two analyses were provided to First Energy Company's Perry Nuclear Power Plant on February 3, 2017. Perry Nuclear Plant staff are continuing to review these results in order to complete the determination of whether the change in flood water levels results in additional reporting requirements. "If you have any questions or need further clarifying information, please contact Nick Eggemeyer, Corporate Quality Assurance Manager, at (770) 590-2031." Notified the R2DO (Sandal), R3DO (Kunowski), and Part 21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-11-23
52393 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-10-28 11:56 | 2016-11-23 11:21 | 2016-11-23 | AGREEMENT STATE REPORT - PROCESS GAUGE SHUTTER FAILS TO CLOSE The following report was received via e-mail: "On 10/28/2016, GA-PAC [Georgia Pacific] was shutting down this process to perform routine annual maintenance. In the process of securing the radiation sources from becoming a radiation exposure hazard, it was discovered that the gauge shutter would not close. "GA-PAC called a service contractor, BBP Sales, to evaluate the situation and determine the best course of action to correct the problem. [BBP Sales] was unable to close the shutter and determined the source holder would have to be replaced. Further evaluation determined one of the pins holding the shutter had sheared off and would have to be replaced, not repaired. "The sources and device with shutter failure will remain installed until the replacement source and device are received. The failed device will be sent for disposal when replaced. This is not a radiation exposure hazard and does not pose a health and safety situation for the GA-PAC employees or the general public. "The gauge is a RONAN C-10 device/source holder, S/N 9830GG, loaded with a 2,000 mCi Cs-137 source. The manufacturing date was 1994. "This event is considered to be closed by LDEQ. This event is being reported to the NRC as required by Regulatory Requirement 10 CFR Part 30.50(b)(2)." Louisiana Event: LA-160016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-12-01
52392 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-11-17 | 2016-11-23 12:11 | 2016-11-23 | AGREEMENT STATE REPORT - MISPLACED AM-241 SOURCE The following report was received via e-mail: "The Tennessee Division of Radiological Health was notified on November 22, 2016, of the discovery by Bionomics staff of an Americium-241 source in a shipment to Bionomics of depleted uranium counterweights. The 2 mCi source is reported to be part of an aircraft fuel gauge." Tennessee Event: TN-16-166 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-12-01
52391 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-11-03 | 2016-11-23 10:21 | 2016-11-23 | AGREEMENT STATE REPORT - LEAKING KR-85 SOURCE DURING TRANSFER TO APPROVED SHIPPING CONTAINER The following report was received from the Louisiana Department of Environmental Quality via email: "On the 3rd of November, 2016, QSA Global, Inc. had an incident during the transfer of Kr-85 sources to approved shipping containers for transportation to Qual-X, Inc. for recycling. The work was being preformed at approximately 1530 to 1600 hrs. [CST]. After the completion of the work, there was no indication at that time of any possible leakage. "At approximately 1800 hrs., it was noticed that the scintillation counter background had a slightly higher than normal background reading. It was determined that the only possible cause was the Kr-85 sources, as that is all that QSA Global, Inc. had worked with that day. A visual inspection of the possible leaking Kr-85 sources was performed. There was no damage to any of the windows, but QSA Global, Inc. now knows that was the point of origin of the contamination due to the surveys of the lead container that they were stored in. The sources were sealed in a 10 gallon steel drum and then placed in a plastic bag to prevent any additional release of material. "The sources involved are LFE Model S-70A s/n 9234 at 168 mCi, 9332 at 184 mCi and 9333 at 184 mCi. The original activity of these sources was 1200 mCi. "The building was ventilated using fans to remove the Kr-85 that had accumulated in the building. The building was surveyed at 0230 hrs. [on November 4, 2016] with no contamination detected. Another survey of the building was performed again at 0530 again with no contamination found. "After QSA Global discussed the situation with Qual-X, Inc. and using their expertise in these types of situations, it was determined from survey readings and building size, that an estimated amount of less than 1-2 mCi may have been released. They also indicated that the sources were of the type that are known to leak due to the way they are manufactured and their age being 29 years. At this point QSA Global, Inc. believes that all three may be leaking." Event Report ID No.: LA160015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-12-01
52390 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-11-22 15:15 | 2016-11-22 18:44 | 2016-11-22 | OFFSITE NOTIFICATION OF A MINOR RELEASE OF NON-RADIOLOGICAL DILUTED CLEANING SOLUTION TO THE OHIO RIVER "During routine floor cleaning activities inside of the BVPS [Beaver Valley Power Station] Main River Water Intake Structure, approximately one and one half cups (approximately 12 oz.) of Simple Green cleaning solution diluted in three gallons of mop cleaning water was inadvertently released into the Ohio River. Subsequent to confirmation of the inadvertent release to the Ohio river, a notification was made to the Pennsylvania Department of Environmental Protection, (PADEP). "This offsite notification to PADEP requires a 4-hour report per 10 CFR 50.72(b)(2)(xi). Actions were taken to preclude any further liquid cleaning solution to be released, and no detectable impact to the Ohio River was observed. The amount of cleaning solution does not exceed any Reportable Quantity limit that would be hazardous to the environment or personal health. No press release is planned. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-11-22
52389 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-11-17 | 2016-11-22 12:17 | 2016-11-22 | AGREEMENT STATE REPORT - I-125 SEED LEFT INSIDE A PATIENT "Yesterday (November 21, 2016) we [Oklahoma Department of Environmental Quality] were notified by Integris Health (OK-11022-01) that a brachytherapy seed containing 0.1 mCi of I-125 had been lost. The seed was implanted in a patient on November 14 for localization of a non-palpable breast lesion. The tissue was removed on November 17 and sent to pathology. The patient had also had a sentinel node procedure on the same day and received a dose of Tc-99. The licensee believed that the seed had been removed with the specimen. The specimen was sent to the pathology lab on November 18 and showed no radiation when surveyed there. The licensee initiated a search of their facilities at that time. The patient returned to the hospital yesterday for their post-operative evaluation, was again surveyed, and the seed was detected. "Yesterday evening, the licensee emailed us that the seed had actually been left in the patient. We are making this notification as a possible medical event. The licensee is performing a dose calculation on the patient. Our investigation is ongoing and we will provide more information as it becomes available." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-11-30
52388 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-11-21 17:38 | 2016-11-21 21:22 | 2016-11-21 | SERVICE WATER LEAK INSIDE CONTAINMENT "At 1738 [EST] on November 21, 2016, a leak was identified inside the Vapor Containment building on a Service Water line associated with 24 Fan Cooler Unit. The leak was isolated at 1743 by shutting the Service Water Isolation valves to 24 Fan Cooler Unit. This isolation meets the Technical Specifications of 3.6.1 Condition A Required Action. The leaking defect could have resulted in post-LOCA air leakage out of containment in excess of that allowed by Technical Specification 3.6.1 (Containment) which requires leakage rates to comply with 10 CFR 50, Appendix J. This event had no effect on the health and safety of the public. "This event is being reported under 10 CFR 50.72(b)(3)(v) and the guidance of NUREG 1022, section 3.2.7 as a loss of safety function." The service water was quantified at approximately 15 gpm. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-11-21
52387 | 0 | US ARMY |  |  |  |  | 2016-10-12 14:24 | 2016-11-21 13:38 | 2016-11-21 | LOST SHIPMENT OF MATERIAL CONTAINING TRITIUM "USMC shipped the package [containing 45.06 Ci of tritium] via [common carrier] out of Hawthorne Army Depot, Hawthorne, NV on October 6, 2016 to MARCORLOGBASE, Director Fleet Support Dir Code 587, Radford Blvd, Suite 20320, Albany, GA. The package was signed for with initials and a signature showing delivery on October 12, 2016 at 1424 [EDT]. There were several attempts of delivery before the package was delivered. The initials of who signed for the shipment cannot be traced to anyone and the signature is unreadable. [The common carrier] indicates delivery to the address of a receptionist. The package had UN2911 markings on opposite sides of the package. "USMC RADCON conducted a physical search of USMC Albany locations to include the Post Office with no results. Defense Logistics Agency (DLA) Albany was contacted and DLA performed a physical search with no results. Also, another shipment from Hawthorne was sent out to a different location, which was received. This location was checked for receipt of the concerned package. On November 2, 2016, an Albany All Hands/Base wide official message was sent out regarding the package. "The conclusion at this time is that the package is considered missing and likely somewhere at MCLB, Albany. The US Navy indicates that physical searches and base wide notifications continue in the effort to locate the package." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-11-29
52386 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-11-19 18:00 | 2016-11-21 13:18 | 2016-11-21 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GUAGE The following information was received via E-mail: "On Saturday at 2300 CST, the licensee's radiation safety officer called the Agency [Illinois Emergency Management Agency] to report that a vehicle carrying a moisture density gauge had been stolen. The theft had occurred around 1800 [CST] that evening while the truck was in Chicago, IL. It was reported that, at the time of the theft, the gauge was secured in the truck in accordance with the 'two lock' rule within a toolbox. The operator indicated that after he started the truck, he realized he had left his cell phone in the house and gone in to retrieve it without turning off the truck. When he returned, the truck was already being driven off down the street. The Chicago Police Department has been contacted about the theft and are aware that the gauge was present in the vehicle as well as several other company issued tools. Given the manner of the theft, it is not believed the device with radioactive sources was targeted for the theft, but that it was a theft of opportunity." Troxler model: 3440 Serial number: 15107 Chicago Police report: HZ522208 Illinois event: IL16013 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-11-29
52385 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-11-19 | 2016-11-21 16:30 | 2016-11-21 | AGREEMENT STATE REPORT - FAILURE OF SOURCE TO RETRACT The following information was received via E-mail: "On November 21, 2016, the licensee notified the Agency [Texas Department of State Health Services] that on November 19, 2016, one of its radiography crews had been unable to retract an iridium-192 source back into a Spec 150 radiography exposure device (camera). "Following their third exposure on a pipeline inspection at a temporary job site [near Mentone, Texas], one of the radiographers retracted the source and went to the camera to disconnect the guide tube. The 6-foot guide tube was laying over the top of the pipe they had been inspecting and the collimator was on the opposite side from the radiographer. When he disconnected the guide tube, the collimator was pulled to the top of the pipe. The radiographer's alarming rate meter sounded and his survey meter went off-scale. He left the area, monitored the 2 mR/hr boundary and called the site radiation safety officer (SRSO). "The SRSO, on the license to perform retrievals, responded and retrieved the source. The control cable was found to be broken approximately one inch from the connector and the licensee suspects the automatic securing mechanism malfunctioned. The device and control assembly have been sent to the manufacturer for evaluation/repair. "The radiographer's pocket dosimeter had a reading of 80 mR. The other radiographer had a reading of 10 mR on his pocket dosimeter. The SRSO had the following readings on pocket dosimeters located on his chest and taped to the backs of his hands: chest 131 mR; right hand 163 mR; and, left hand 167 mR. Their dosimetry badges have been sent for emergency processing. More information will be provided as it is obtained in accordance with SA-300. "Device: SPEC 150 SN: 1845 "Source: Iridium-192, 66 curies, SPEC G-60, SN: XI-0909" Texas Incident #: I-9443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-11-29
52384 | 0 | AMETEK SOLID STATE CONTROLS |  |  |  |  | 2016-10-26 | 2016-11-21 12:13 | 2016-11-23 | PART-21 - INCORRECT CAPACITOR USED ON CIRCUIT BOARDS The following report was excerpted from an e-mail: "Product: Ametek Solidstate Controls Analog Oscillator, printed circuit board part number 80-9230404-90 "A single unit, Ametek part number 80-9230404-90, was shipped to Exelon Dresden Station on the reference purchase order has an incorrect capacitor installed. This error was identified during testing of a subsequent identical part. Ametek reviewed all printed circuit boards built under that run and verified all affected printed circuits boards less one, were still in house. This shipment was made on October 26, 2016. Ametek contacted Exelon Dresden immediately upon identification of the incorrect part installation and Exelon was able to have the board retrieved from their inventory. Ametek Solidstate Controls is submitting this notification as a precaution under the requirements of 10 CFR Part 21, but considers it a limited incident as the single defective part was isolated and the board is in the process of being returned. No further action is required and this notification does not affect any other installation, client, inventory, or equipment provided by Ametek." * * * UPDATE AT 0921 ON 11/23/16 EST FROM ETHAN SALSBURY TO JEFF HERRERA * * * The following report is an excerpt from an email received: "Dresden was incorrectly identified as the recipient of the printed circuit board in question. Byron warehouse was the correct recipient and was the facility notified upon identification of the issue. "Ametek reviewed all the printed circuit boards built under that run and verified all affected printed circuits boards less one, were still in house. The single affected board was shipped to Exelon Generation Company, Byron warehouse on purchase order # 00588294 and Ametek sales order #46001912. This shipment was made on October 26, 2016. "Ametek contacted Exelon Byron immediately upon identification of the incorrect part installation and Exelon was able to have the board retrieved from the inventory." Notified R3DO (McCraw) and Part 21/50.55 (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-11-21
52383 | 0 | SYSTEM ONE SOLUTIONS LLC |  |  |  |  | 2016-10-28 | 2016-11-21 11:43 | 2017-03-28 | PART-21 NOTIFICATION - WILLFUL MISCONDUCT AND FALSIFICATION OF RECORDS The following report was excerpted from an e-mail: "On September 28th, System One received an email from Curtis Wright that a 'forged' VT-1, 2, 3 Level II training record was being circulated by [an individual], who was seeking employment with Applied Technical Services. "On September 28th 2016, System One voided the certification of [the individual] and proceeded to address the condition under the nonconformance reporting process. "On October 11th, 2016, System One determined that [the individual], who was certified in VT-1, 2, 3 by the System One Quality Assurance Manager, did not fully meet the certification requirements of the System One Written Practice under CP-199 (in effect at the time) due to lack of acceptable VT [visual testing] Training (40 hours of required class room training) to support the VT-1, VT-2 and VT-3 certification issued by System One. A review of the original certification record found/confirmed there was indication of alteration on a training record used for the original certification. "On October 28th, 2016, System One notified stakeholders (AREVA NP). [The individual was deployed to Areva on two occasions] based upon holding VT-1, 2, 3 certification. AREVA NP - deployed in 10/7/2012 to Cooper with VT-1, 2, 3 Certification AREVA NP - deployed in 3/31/2013 to DC Cook with VT-1, 2, 3 Certification Carolina Energy Services - deployed in 8/23/2013 - certification conducted by CES not System One LLC. AREVA NP - deployed in 10/27/2013 to Palo Verde with PT Level II and QC Mechanical (not deployed for VT-1, 2, 3) "AREVA NP has informed System One that they have conducted/completed their extent of condition review regarding work performed by [the individual], and confirmed to System One, that [the individual] did not perform any safety related VT-1, 2, 3 work at either the D. C. Cook or Cooper facilities. "Our internal investigation has determined this matter does not represent a breakdown in the mechanics of the System One Quality Assurance Program or procedures in effect at the time. We have established the event represents willful misconduct and the falsification of a record by an individual, and use of such forged record, under 10 CFR references contained in US NRC Information Notice 2013-15." * * * UPDATE ON 3/28/17 BY BETHANY CECERE * * * System One determined that the individual who had been deployed to the various sites referenced, did not falsify the certification documents in question. Notified R1DO (Cook), R3DO (Cameron), R4DO (Hipschman), and Part 21/50.55 Reactors Group by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-11-21
52382 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2016-11-20 14:02 | 2016-11-20 18:53 | 2016-11-20 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE LESS THAN TECHNICAL SPECIFICATION REQUIREMENT "On November 20, 2016 at 1402 PST, Reactor Building Exhaust Air Fan 1B, REA-FN-1B, failed to start in manual which caused the Technical Specification (TS) for secondary containment pressure boundary to not be met. The duration of the time that the secondary containment TS was not met was approximately less than one minute. REA-FN-1B was being started in manual during a shift of Reactor Building Ventilation to support a post-maintenance support task on REA-FN-1B. "Secondary containment differential pressure was restored within the TS requirement of greater than or equal to 0.25 inch of vacuum water gauge by restarting Reactor Building HVAC Train A. "The cause of REA-FN-1B failing to start is currently under investigation. "This condition is being reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and accident mitigation. "The licensee has notified the NRC Resident Inspector." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-11-20
52381 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-11-20 03:42 | 2016-11-20 06:01 | 2016-11-20 | AUTOMATIC REACTOR SCRAM DURING MAIN TURBINE TESTING "At 0342 EST, an automatic reactor scram was processed during turbine valve testing. All rods inserted into the core as expected and all systems functioned as expected during the scram. "The event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a preplanned sequence during testing or reactor operation." The plant response to the reactor scram was uncomplicated. The main feedwater system is maintaining reactor water level and decay heat is being removed by the main turbine bypass valves to the main condenser. The unit is in a normal shutdown electrical lineup. No SRVs lifted during the scram. The licensee was testing the main turbine trip function just prior to the scram. The cause is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-11-20
52380 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-11-19 21:50 | 2016-11-20 04:56 | 2017-03-17 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On November 19, 2016, starting at 2150 EST, high wind conditions encountered on site resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met numerous times. The duration of time that the secondary containment Technical Specification was not met was approximately 1 second for each instance. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. At 0430 EST, high wind conditions have subsided and secondary containment vacuum was greater than the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) and steady, and the LCO was exited. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * UPDATE ON 11/20/16 AT 1416 EST FROM BRETT JEBBIA TO BETHANY CECERE * * * "On November 20, 2016, starting at 0654 EST, high wind conditions encountered on site resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met on multiple different occasions as of event notification update time. The duration of time that the secondary containment Technical Specification was not met was approximately 1 second for each instance. "Fermi 2 continues to remain in a gale force wind advisory for the local area of Lake Erie. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." The R3DO (Jeffers) has been notified. * * * UPDATE ON 11/20/16 AT 2104 FROM GREG MILLER TO BETHANY CECERE * * * "On November 20, 2016, at 1426 EST, high wind conditions encountered on site resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met. The duration of time that the secondary containment Technical Specification was not met was approximately 1 second. "The Fermi 2 local area of Lake Erie is no longer in a gale force wind advisory and the high wind conditions have subsided. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." The R3DO (Jeffers) has been notified. * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter) | 100 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-11-20
52379 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-11-18 12:00 | 2016-11-18 19:57 | 2016-11-18 | AGREEMENT STATE REPORT - AUTOMATIC LOCKING DEVICE FAILURE The following is a synopsis of information received via E-mail from the Louisiana Department of Environmental Quality (LDEQ): TUV Rheinland (TUVR) was working at the Sasol Mega Project in Westlake, Louisiana under reciprocity (RC-662). TUVR was utilizing four industrial radiography exposure devices but only had a problem with one device. TUVR made an exposure and then retracted the source into the shielded position. The source returned to the shielded position, but the automatic locking device did not lock/engage. The exposure device was manually locked with the plunger-lock and then key locked. It appears that the spring in the locking mechanism was either broken or blocked from working. The device is a Sentinel model 880D with S/N D13509. The device contains an INC model 7 source with 36.9 Curies of Ir-192 with S/N T0274. Safety surveys were made and there appears to be no radiation exposure hazard. The device was taken out of service, 'locked and tagged' out of service, and is being transported back to Woodstock, Alabama for a complete evaluation. LDEQ was notified of the event by a phone call and a follow-up written report. From the report, it appears there is not a Radiation Safety Officer named on the Texas license at this time. A copy of the complete evaluation report will be provided when available. Louisiana Event Report ID No.: LA-160014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2016-11-28
52378 | 0 | WESTINGHOUSE |  |  |  |  | 2016-11-18 | 2016-11-18 14:42 | 2016-11-18 | PART 21 NOTIFICATION - CONTROL ROD GUIDE CARD EXCESSIVE WEAR The following report is excerpted from Westinghouse fax LTR-NRC-16-74: "Westinghouse nuclear steam supply system (NSSS) plants that are using iron nitride rod cluster control assemblies (RCCAs) in conjunction with Westinghouse 17x17 A or 17x17 AS style guide tubes (GTs), the GT guide card wear inspection guidance provided in Westinghouse report WCAP-17451-P, Revision 1, is not conservative. "Based on the data, a determination was made as to whether an affected plant could exceed its permissible number of worn guide cards before completing its first guide card wear measurement (GCWM) inspection, the timing of which is based on recommendations documented in the WCAP. The concern associated with exceeding the permissible number of worn guide cards is that a rodlet might slip out of alignment with the GT guide card fingers and become stuck. For example, if an unsupported rodlet were to deflect as a result of applied lateral fluid forces during normal operation, it could get caught on the corner of a worn guide card finger and jam or buckle during rod motion (i.e., scram). Additionally,. if a GT with an excessive number of worn guide cards experiences a seismic event or loss-of-coolant accident (LOCA), an unsupported rodlet might become plastically deformed, which could prevent a RCCA from scramming properly. Should this affect multiple GT locations, it could prevent a plant from achieving reactor shutdown using only the RCCAs. "Left uncorrected, the wear inspection guidelines in WCAP-17451-P, Revision 1, underestimate the 17x17 A and 17x17 AS style GT guide card wear attributed to the use of iron nitride RCCAs to the extent that, for the four plants listed, the WCAP recommended number of effective full-power years (EFPYs) until the first GCWM is performed may no longer have margin to safety. The guidelines presented in this WCAP do not result in a defect for the other plants to which the WCAP applies." Affected reactors are: Catawba Units 1 and 2, McGuire Unit 2 , and Millstone Unit 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-11-18
52377 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-11-17 17:00 | 2016-11-18 13:40 | 2016-11-18 | INCORRECT METHOD USED FOR CALCULATION OF CONTROL ROOM HABITABILITY "During the NRC CDBI [Component Design Basis Inspection], it was identified that the calculation used to demonstrate Control Room Habitability following a Design Basis Accident (DBA) utilized an inappropriate methodology. Specifically, the calculation used dual air inlets for the emergency zones as the type of system used for Main Control [Room] Ventilation (VC) system. In order to use the dual inlet type system in the analysis, each of the VC subsystems is required to be single failure proof. The VC system is single failure proof, but the individual subsystems at the inlet, as designed, are not. "The dual inlet type system allows for certain calculated dose concentrations to be reduced by a factor of 4. Elimination of this reduction factor results in higher calculated control room dose following a DBA which exceeds the 5 Rem limit. "This event is reportable under 10 CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.'" A standing order has been issued for compensatory actions in the event of an emergency. The licensee notified the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-11-18
52376 | -1 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2016-11-16 09:00 | 2016-11-18 12:22 | 2017-01-12 | AGREEMENT STATE REPORT - MEDICAL RADIATION TREATMENT OVERDOSE The following information was received via E-mail: "The licensee reported on November 17, 2016 that the licensee administered on November 16, 2016 to a patient a first fraction dose of 1100 centigray to the vagina instead of the prescribed first fraction dose of 600 centigray to the vagina. "This dose was the first of three fractionated doses, the second and third fractionated doses have not yet been administered. Each fractionated dose was prescribed to be 600 centigray for a total dose of 18 gray (1,800 centigray). "The licensee used a Varian Medical Systems, Inc. GammaMed plus iX High Dose Rate (HDR) remote afterloader unit containing 7 curies of iridium-192 to deliver the dose. "This is a reportable medical event in accordance with 105 CMR 120.594(A)(1)(a)3. "The licensee reported that the patient and the referring physician have been notified and that no harmful effect to the patient has been reported. "The licensee reported that the event occurred because the physician's plan was not performed as prescribed in the written directive and that no other cause was known at time of report. "The Agency (Massachusetts Radiation Control Program) Director requested the licensee to cease HDR use until a corrective action to prevent recurrence has been implemented. "The Agency plans to perform a special inspection and considers this event to be open." * * * RETRACTION FROM JOSHUA DAEHLER TO JOHN SHOEMAKER AT 1506 EST ON 01/12/17 * * * "The Agency is retracting this medical event. This is not a reportable event. "Based upon inspection/review by the Agency with the licensee, it was determined that each of the three fractions was actually prescribed to be 700 centigray for a total dose of 2,100 centigray to the vagina. The first fraction dose of 700 centigray was successfully administered to the vagina. The two additional fraction doses of 700 centigray each were also successfully administered to the vagina. The licensee prematurely reported the issue without having all the facts and without review by the RSO. Subsequently to review of information available to the licensee it was determined no reportable event occurred." Notified R1DO (Dimitriadis) and NMSS_Events_Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2016-11-28
52375 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-09-01 | 2016-11-18 10:20 | 2016-11-18 | AGREEMENT STATE REPORT - POLONIUM-210 STATIC ELIMINATOR GAUGE MISSING The following information was obtained from the Commonwealth of Pennsylvania via email: "Event Description: During an inventory record check on September 1, 2016, the general licensee discovered that the static eliminator gauge was missing. Its last known use was during the first six months of the year 2011. The general licensee was unaware of its reporting responsibility. "Gauge info: Radionuclide: Polonium-210 Manufacturer: NRD, Inc. Model: P-2021-5000 Device SN#: A2HM769 Activity: 10.2 milliCuries "Cause of the Event: Unknown at this time, the general licensee believes that the equipment was lost when the company reconfigured its machinery at some point during 2012. "Actions: A reactive inspection is planned by the Department [PA Department of Environmental Protection]. More information will be provided upon receipt. Note: Given that over 13 half-lives have transpired since the gauge was lost, there is no current public health and safety hazard." PA Event Report ID: PA160035 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-11-28
52374 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2016-11-17 18:59 | 2016-11-17 20:51 | 2016-11-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN INITIATED "At 1859 CST on November 17, 2016, Farley Nuclear Plant Unit 1 initiated a shutdown from approximately 99 percent reactor power. The shutdown was initiated per Technical Specification LCO 3.0.3. This LCO entry was based on having no operable steam flow channels on the C loop for Farley Nuclear Plant Unit 1. "Unit 2 as not affected. "The NRC Resident Inspector has been notified." | 93 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-11-17
52373 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-11-16 14:00 | 2016-11-17 14:07 | 2016-11-17 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED NUCLEAR GAUGE The following was excerpted from information received from the Texas Department of State Health Services by email: "On November 17, 2016, the licensee notified the Agency [Texas Department of State Health Services] that on November 16, 2016 at approximately 1400 CST, during its semi-annual fixed nuclear gauge inspection [at Chocolate Bayou Works], it had discovered that the shutter mechanism on an Ohmart Model SHLM-BR-2, which contains a 1,000 millicurie cesium-137 source (SN: 2807CG), had become inoperable. The licensee's radiation safety officer reported the source could be moved up/down inside the source tube, but it could not be retracted into the housing. He suspects there is an issue with the positioning of the pin that holds the 2-piece source rod together. Repairs are scheduled to be completed during an operations shut-down in January/February 2017. The source is in its normal operating position and there is no risk of exposure to any individual due to its location." Texas Incident #: I-9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-11-25
52372 | 0 | U.S. NAVY |  |  |  |  | 2016-11-16 15:00 | 2016-11-17 10:56 | 2016-11-17 | PART 21 - NOTIFICATION OF DEFECT - IRRADIATOR MALFUNCTION The following is excerpted from an email/fax received from the U.S. Navy, Radiological Controls Office: An irradiator located as Naval Surface Warfare Center, Carderock on 16 November [2016] at approximately 1500 [EST] malfunctioned. During routine use of the JLS 81-20 self-shielded irradiator (Co-60 source with all attenuators 1000, 100, 10, 1, 2, in place) the device did not terminate the shot at the end of the exposure period. The end-user attempted to use the emergency stop at the control panel, which did not work as intended. The panel displayed the source was in "MOVEMENT" status for approximately 70 minutes. No injuries or overexposures occurred, there seems to be an operational issue with the irradiator source moving from an exposed position to the shielded position, which Carderock is taking steps to correct. They have verified the source returned to the shielded position and have placed the calibrator out of commission until maintenance can be performed. The licensee has notified the NRC Project Manager (Seeley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 21.21(d)(3)(i) |  |  |  | 0 | 2016-11-25
52371 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2016-11-16 21:09 | 2016-11-16 23:39 | 2016-11-17 | EMERGENCY DIESEL GENERATOR STARTED ON VALID UNDERVOLTAGE SIGNAL "While in Mode 5, power from the switchyard east bus was lost. AC Emergency Bus NB01 is fed from east or west buses through [breakers] 345-80 or 345-90. Both breakers tripped. The 'A' train emergency diesel generator started on the undervoltage signal and powered NB01. All other systems functioned normally including the Shutdown Sequencer. Shutdown cooling was being provided by train 'B' RHR [residual heat removal] and was uninterrupted. "Initial reports are that the #6 transformer brought in an air/gas trouble alarm. "The plant is still in Mode 5. The 'A' emergency diesel generator is supplying power to NB01. The switchyard west bus and NB02 remain stable. Transmission reports that the grid is stable. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-11-17
52370 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-11-16 11:05 | 2016-11-16 18:22 | 2016-11-17 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM INOPERABLE "At 1105 CST on Wednesday, November 16th, 2016, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) Emergency Ventilation System was emergently declared inoperable due to an unplanned loss of the pneumatic air supply compressor. The loss of the air compressor resulted in the emergency air filtration unit flow control damper failing to the full open position. In this condition, the emergency air filtration unit could exceed the max flow rate of 1100 SCFM and the max differential pressure of 6 inches H2O at rated flow rate resulting in degraded performance. This results in a potential loss of protective action function provided by the emergency ventilation filtration system and could impede the ability to perform Emergency Assessments should a radiological emergency event occur requiring the system to be in service. "Actions are being taken to repair the pneumatic air system to restore functionality of the TSC ventilation system. In the interim, contingency actions are being developed to manually control the emergency air filtration unit flow control damper in a degraded condition. In the event that ventilation cannot be restored, Station Procedures provide guidance to relocate the TSC to an alternate facility. This event is being reported under 10 CFR 50.72(b)(3)(xiii), 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system).'" The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM ADAM SCHUERMAN TO HOWIE CROUCH AT 0812 EST ON 11/17/16 * * * The pneumatic air supply compressor has been repaired and tested satisfactorily. The Technical Support Center is now considered operable. The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Peterson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Startup |  | Power Operation | Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-11-16
52369 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-11-16 10:45 | 2016-11-16 17:13 | 2016-11-16 | FAILURE OF UNIT 2 B ENGINEERED SAFEGUARDS SYSTEM BUS SYNC SELECTOR SWITCH "On November 16, 2016 at 1045 [EST], Unit 2 B ESS [Engineered Safeguards System] Bus Sync Selector switch failed and was unable to be switched out of the ON position. The failure rendered all other sync selector switches associated with Emergency Diesel Generators and Off-Site supplies to the ESS buses unable to fulfill their intended function of allowing manual transfer between power supplies to the ESS buses. This resulted in the inability of Unit 1 and Unit 2 to comply with SR [Surveillance Requirements] 3.8.1.8 and 3.8.1.16 thus requiring declaration of Operating AC Sources inoperable. This condition could have prevented the fulfillment of the safety function of systems required to maintain the reactor in a safe shutdown condition, remove residual heat, control the release of radioactive material, and mitigate the consequences of an accident. Subsequent actions were taken in accordance with station procedures to remove fuses for the affected sync circuit, restoring the manual transfer function to all but the Unit 2 B ESS bus. One Emergency Diesel and one offsite source remain inoperable with the fuses removed. "At no time were any ESS buses disconnected from offsite power. All ESS buses remained capable of being automatically energized from their respective emergency diesel in an emergency." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2016-11-16
52368 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2016-11-16 10:10 | 2016-11-16 14:32 | 2016-11-16 | INADVERTENT ACTIVATION OF EMERGENCY SIRENS AND NEWS RELEASE DURING EMERGENCY PLANNING EXERCISE "On November 16, 2016 at approximately 1010 CST, a local government agency (Whiteside County, Illinois) inadvertently activated emergency response sirens for less than one minute. The inadvertent actuation occurred during the scheduled Quad Cities Station emergency planning graded exercise while local government agencies were participating. "A related news release and radio message was subsequently issued by Whiteside County to report that Whiteside County was participating in a drill in coordination with the Quad Cities Exelon Generating Station that the emergency response sirens were inadvertently activated, and that there is no emergency at this time and no action is required. "There was no impact to the health and safety of the public as a result of this event as the offsite response capabilities remain functional. The site is operating normally with no emergency conditions present. "This event is being reported under 10 CFR 50.72(b)(2)(xi), as an inadvertent activation of emergency response sirens and news release. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-11-16
52367 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-11-15 15:59 | 2016-11-16 13:34 | 2016-11-18 | AGREEMENT STATE REPORT - LOST INDUSTRIAL RADIOGRAPHY CAMERA The following report was received from the New York State Department of Health via email: "On 11/15/2016, an employee of Applied Inspection reported that an Industrial Radiography camera is missing/lost in transport. There was no source in the camera. The camera was being shipped by [a common carrier] to Industrial Nuclear Company in La Porte, TX to be resourced. According to the tracking number the last known location is Memphis, TN. "The camera is a Sentinel (QSA Global), model Delta 880, serial number D11011. The camera contains 50 kilograms of depleted uranium. "According to the licensee, the package was picked up from their Tonawanda, NY location on November 1, 2016. Tracking showed it arriving in Memphis, TN, on November 2, 2016. [The common carrier] has not been able to locate the package. The Corporate RSO [Radiation Safety Officer] for [the common carrier] was notified about the missing package on November 15, 2016. "Although it was reported to the department that there was no source, the camera still contains depleted uranium, which is listed on the license. The Department [New York State Department of Health] will continue the investigation." NY Event ID No: NYDOH-NY-16-08 * * * UPDATE ON 11/18/16 AT 0921 EST FROM DESMOND C. GORDON TO DONG PARK * * * The following report was received from the New York State Department of Health via email: "On 11/17/2016, the Corporate Radiation Safety Officer (CRSO) of [the common carrier], reported (via email) that the camera was found and was delivered to its final destination. According to [CRSO] note, he was contacted by the [the common carrier] Spill Clean-up office about a shipment marked with a Radioactive Material Excepted Package UN2909 handling label. He had them open the package, verify it as a QSA Global Model 880 and they confirmed the D11011 serial number. The package was an orphan package without paperwork and had been there since the first of the month. He gave them the tracking number and instructed them to move the package that morning. Industrial Nuclear received the package in La Porte, Texas. Although the orphan package had been 'written-up' when it arrived, there had been no follow up." Notified R1DO (Bickett), NMSS Events Notification, and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-11-24
52366 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-11-15 14:00 | 2016-11-15 16:14 | 2017-05-15 | AGREEMENT STATE REPORT - MULTIPLE RADIUM PAINTED DIALS FOUND IN MUNICIPAL SOLID WASTE The following information was reported by the New Jersey Department of Environmental Protection via email: "On November 15, 2016 a specifically licensed waste broker company reported the discovery of multiple (estimated 85) radium-painted dials within two loads of municipal solid waste. The items appear to be dials from U.S. Navy and U.S. Coast Guard deck clocks. A few items appeared within clock housings, while most were loose. The waste broker indicated the items were all found contained within garbage bags and no further contamination was identified outside the bags. The items were placed inside two 5-gallon pails and will be secured on-site pending proper disposal. The estimated total activity was reported as 240 microCuries. This is a reportable incident under N.J.A.C. 7:28-6.1 (10 CFR 20.2201(a)(i)). NJDEP [New Jersey Department of Environmental Protection] is tracking this incident internally as incident ID# C621791 and C622346 (one for each waste load)." * * * UPDATE FROM JAMES MCCULLOUGH TO DONALD NORWOOD AT 1550 EST ON 11/18/2016 * * * "One truck which had been screened by the waste broker consultant was again rejected at a PA [Pennsylvania] landfill and returned to the facility. The consultant returned to the facility on 11/17/2016 and 11/18/2016 to more thoroughly scan the contents of both truck loads. NJDEP was present on 11/17/2016 to observe. Additional radium dials, movements and associated waste contents were isolated in three 30-gallon waste drums. The three drums and two pails will be secured at the waste facility in a sea van container with lock. An estimated total activity has not yet been provided by the consultant. "Paperwork, dated in 1980s and mixed into the load, identified a possible responsible party in New York, which appears may no longer be in business. New York State Department of Health Bureau of Environmental Radiation Protection was informed of this by telephone on 11/18/2016. "NJDEP has received responses from U.S. military contacts who are looking into the possibility of assisting with disposal of the materials." Notified R1DO (Bickett) and via E-mail NMSS Events Notification group. * * * UPDATE AT 1222 EST ON 5/15/17 FROM JAMES MCCULLOUGH TO JEFF HERRERA * * * The following update was received from the New Jersey Department of Environmental Protection via email: "On May 12, 2017 the US Army Joint Munitions Command, Safety/Risk Assessment Directorate - Risk Assessment Division reported that their contractor had picked up the waste shipment on May 11th. The shipment was received by a waste broker in Pennsylvania; the final waste disposal site was identified as US Ecology in Grand View, Idaho." Notified the R1DO (Burritt), ILTAB (email), NMSS Events group (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-11-23
52365 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-11-11 | 2016-11-14 16:26 | 2016-11-14 | AGREEMENT STATE REPORT - LOST AM-241 SOURCE The following report was received from the Illinois Emergency Management Agency via email: "On October 14, 2016, the licensee's RSO [Radiation Safety Officer] called to report a lost Am-241, 45 mCi source that was part of a wave generator manufactured on 12/2/1982. The manufacturer and model number of the wave generator and radioactive component are not known. It was noted as lost during a recent inventory. An exhaustive search of nearby laboratories and waste areas did not reveal any clues of its whereabouts. During a radioactive material inventory in March 2016, records show this source was identified and accounted for. Access to the storage room is strictly controlled. It is only speculation to how the source became missing. First, it is possible that the source was mistakenly shipped as part of the University's participation in the Source Collection and Threat Reduction (SCATR) program. A vendor for the SCATR program removed nearly 200 sealed sources in December 2015. It is possible that the Am-241 source was mistakenly included in this shipment and the March 2016 inventory was in error. Another possibility is that the source was misplaced by staff during the summer clean-up of 2016. Personnel were questioned about this likelihood but there was no recollection of moving or discarding of such a unit. Inquiries with staff and SCATR are ongoing." IL Item Number: IL 16012 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-11-22
52364 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-11-14 11:06 | 2016-11-14 14:01 | 2016-11-14 | OFFSITE NOTIFICATION DUE TO ON-SITE SEWAGE SPILL "At 1106 EST on 11/14/16, Fermi 2 discovered a sewage leak from a temporary restroom trailer that had reached a permeable gravel surface. The majority of the spill was confined to the impermeable surface below the restroom trailer. lt was estimated that the quantity of the spill which reached the permeable gravel surface was less than approximately 5 gallons. None of the sewage entered the storm drain system. The source of the sewage leak was eliminated by 1126 EST. A local sanitary contractor will be contacted to respond to the site to clean the affected areas. "Reports to the Michigan Department of Environment.al Quality, the local health department (Monroe County), and the local news media are in progress. Since these reports are in the process of being made, this is considered a News Release or Notification to Other Government Agencies, therefore this event is reportable under 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." | 63 | 0 | 0 | 63 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-11-14
52363 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-11-13 10:12 | 2016-11-13 17:39 | 2016-11-13 | ONE MAIN STEAM LINE RADIATION MONITOR FAILED "At 1012 [CST], Unit 1 Main Steam Line 1-01 Radiation Monitor (1-RE-2325) failed high. With this radiation monitor non-functional, all of the emergency action levels for a steam generator tube rupture in steam generator 1-01 could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant (CPNPP) has assurance of steam generator integrity and fuel cladding integrity and there is a negligible safety significance to the current condition from a public health and safety perspective. Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. "Until this radiation monitor can be restored, Operations has implemented compensatory measures to monitor the main steamline 1-01 N-16 [Nitrogen-16] radiation monitor for early signs of a steam generator tube leak/rupture and pre-brief radiation protection technicians on taking local readings with a Geiger-Muller tube on Main Steam Line 1-01 and reporting the reading to the Control Room. Corrective actions are being pursued to restore 1-RE-2325 to functional status. "The NRC Resident Inspector has been notified." Radiation monitor 1-RE-2325 is not in the plant technical specifications but is important to safety and the Emergency Plan. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-11-13
52362 | 0 | NORTHERN INDIANA PUBLIC SVC COMPANY |  |  |  |  | 2016-11-10 14:00 | 2016-11-11 12:57 | 2016-11-11 | SHUTTER FAILURE ON A FIXED GAUGE At 1400 CST on 11/10/16, technicians performed a routine shutter check on a fixed gauge located at their Wheatfield, IN facility. The gauge, a Kay-Ray Model 7062BP, S/N 30340 containing 50 mCi Cs-137 as of 8/81, failed to properly operate with the shutter returning to the mid-position. The shutter is currently in the locked closed position with no potential for personnel exposure. The gauge is 30 ft. above floor level with the beam directed upward. The licensee will contact the manufacturer for repairs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-11-21
52361 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-11-10 14:00 | 2016-11-10 15:30 | 2016-11-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "Building and Earth Sciences had a Troxler Model 3430 portable gauge run over by construction equipment at a temporary job site in Tulsa, OK. The source rod has been retracted and the sources are shielded. A leak test has been collected and will be counted as soon as possible. The gauge will be returned to Troxler for repair or disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-11-18
52360 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-10-12 | 2016-11-10 10:33 | 2016-11-10 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The following information was excerpted from a report received from the State of Georgia via email: "On Wednesday, November 9th, it was reported to the Department [Georgia Radioactive Materials Program] by Theragenics Corporation in Buford, GA that an employee's dosimetry report indicated that she had exceeded the annual whole body dose limit of 5000 mRem. An investigation has been conducted by the employer and no possible explanation has been found as of yet. Our office has an ongoing investigation and further details will be provided as we receive them. "[The licensee reports receiving] notification from their dosimetry processor, on October 12, an individual received a whole body dose of 5,215 mRem. [The licensee] spent the last month trying to recreate a situation that could have exposed this worker to a dose of this magnitude and can't make it happen. According to discussions, with the worker, she never left her dosimetry in a lab where it could have been exposed to an unshielded source of radiation. According to her supervisor, team leads in the lab in which she worked, and HP [Health Physics], she is a very good radiation worker and, there is never anything out of the normal at her work station. "[The worker] did take her whole body dosimeter and both finger rings home with her one evening. Even more baffling is her ring dose is less than 200 mRem. [The licensee has] tried to recreate that scenario of taking the dosimeters home as well and have not had a dosimeter come back from processing that is above its minimal level of detection. "It is [licensee's] interpretation of [the CFR,] Reportable Events, that this report of an overexposure is due to [the State of Georgia] 30 days after notification, or Friday, 11/11/16. [The licensee is] waiting on additional information [from the dosimetry processor] prior to report submittal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2016-11-18
52359 | 0 | SOR |  |  |  |  | 2016-11-03 | 2016-11-09 17:50 | 2016-12-02 | PART 21 - NOTIFICATION OF DEVIATION - SOR QUALIFICATION TEST REPORT 9058-102 The following information was excerpted from a facsimile received by SOR: Pursuant to the requirements of 10CFR Part 21, this letter notifies the NRC of a Part 21 condition. Irradiation testing performed since 1984 did not take into account all of the uncertainties associated with reported doses of gamma radiation to nuclear test specimens for qualification testing. SOR contracted services with lsomedix in 1992 for the radiation aging that was performed per SOR nuclear qualification report 9058-102 Revision 1. Although SOR imposed Part 21 reporting requirements, lsomedix did not include SOR as part of their Part 21 notification. The Part 21 was brought to SOR's attention through an inquiry by a nuclear power station. SOR requested a conference with Steris lsomedix which occurred on November 3, 2016. The teleconference confirmed that the subject radiation aging test results report would be affected by the Steris lsomedix Part 21. As a result, corrections are underway per qualification test report 9058-102 regarding the uncertainty calculations. SOR does not have the capability to perform further evaluations to determine if a safety hazard exists as the specific customer application is unknown. The end user must confirm for each application that the qualified life dose + accident dose + 10% of accident dose is less than or equal to the corrected values. SOR is currently identifying all customers potentially affected by this deviation. At the conclusion of this activity, SOR will notify the customers and the U.S. Nuclear Regulatory Commission in accordance with the requirements of 10 CFR Part 21. * * * UPDATE FROM MELANIE DIRKS TO JOHN SHOEMAKER AT 1455 EST ON 12/2/16 * * * The following is an excerpt of an updated Part 21 received via email: "Corrections are now complete to test report 9058-102 regarding the uncertainty calculations. The calculations changed from 8% uncertainty to 9.6% uncertainty for the minimum irradiation aging. "SOR does not have the capability to perform further evaluations to determine if a safety hazard exists as the specific customer application is unknown. The end user must confirm for each application that the qualified life dose + accident dose + 10% of accident dose is less than or equal to the above noted values." Should you have any additional questions regarding this matter, please contact: Linda Coutts Inside Sales Representative Email: lcoutts@sorinc.com Tel 91.3ú-956ú-3071 Charles Lautner Customer Service Manager Email: clautner@sorinc.com Tel 913-956-3070 Notified R1DO (Bower), R2DO (McCoy), R3DO (Stoedter), R4DO (Haire), NMSS_Events_Notification, and Part 21/50.55 Reactors via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-11-09
52358 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-11-09 11:15 | 2016-11-09 17:42 | 2016-11-09 | INSUFFICIENT ALARM AUDIBILITY "On November 9, 2016, at approximately 1115 hours (EST), the speaker system in Buildings 302, 303, and 306 West was identified as non-operational while performing a functional test of the system. This speaker system is designed to annunciate alarms generated from the Criticality Accident Alarm System (CAAS) required by 10CFR70.24, alarms generated from the Fire Alarm Control Panel and Public Address System announcements. Additional functional testing identified that no redundant speakers could adequately provide speaker coverage for all affected areas of these buildings. Special Nuclear Material (SNM) is processed, handled, or stored within the areas where the speaker system failed; these areas require evacuation in the unlikely event of a nuclear criticality accident as described in the NFS Emergency Plan. "There were no actual radiological or other nuclear safety consequences. The potential consequence was that in the event of a nuclear criticality accident, evacuation could have been delayed for those personnel within these areas with a resultant increase of postulated doses. Additionally, awareness of a fire event could have been delayed for these same personnel. A series of compensatory actions were taken including implementing a plant-wide stop-movement of SNM, limiting access to the affected areas to essential personnel, and establishing radio communications between the personnel in these areas and the personnel continuously monitoring the alarm station panel. "On November 9, 2016, at approximately 1725 hours (EST), full compliance was restored by repairing a damaged cable and by successfully performing a speaker system test in the affected areas. "The licensee notified the NRC Resident Inspector on November 9, 2016." NFS Event Number: 55579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2016-11-17
52357 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2016-11-09 13:39 | 2016-11-09 14:58 | 2016-11-09 | OFFSITE NOTIFICATION DUE TO SANITARY SYSTEM DISCHARGE "At approximately 1008 [EST] on 11/9/16, site personnel discovered a sanitary lift station overflowing in the protected area. The overflow entered a nearby storm drain that discharges into Outfall 13. The estimated release volume is approximately 10 gallons. The release has been stopped. At 1339 an initial notification was made to SCDHEC [South Carolina Department of Health and Environmental Control]. The cause of the overflow is still under investigation. Functionality of the lift pump has been restored and cleanup is complete. "The NRC Senior Resident has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-11-09
52356 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2016-11-08 | 2016-11-08 17:36 | 2016-11-08 | MANUAL REACTOR TRIP DUE TO STEAM GENERATOR REDUCED FEEDFLOW "At 1331 [CST] on November 8, 2016, Farley Nuclear Plant Unit 1 manually tripped from 32% reactor power. The plant was ramping down to remove the main generator from service due to an unrelated issue. 1A SGFP did not respond to control Steam Generator (SG) level as expected when the miniflow was opened per procedure. SG levels lowered due to lower feed flow and the reactor was manually tripped in accordance with plant procedures. All control rods fully inserted and Auxiliary feedwater (AFW) auto started as expected. The Main Steam Isolation Valves were closed to minimize the cool-down. Decay heat is being removed through the Atmospheric Relief Valves. "All other systems responded as expected. The plant is currently stable in Mode 3 (Hot Standby). The failure of the 1A SGFP control is under investigation. "Unit 2 was not affected. "The NRC Resident Inspector has been notified." There is no primary to secondary leakage. | 0 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-11-08
52355 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-11-08 05:10 | 2016-11-08 12:50 | 2016-11-08 | REACTOR BUILDING TO ATMOSPHERE DIFFERENTIAL PRESSURE OUT OF SPECIFICATIONS "On 11/8/16, Operators were performing Division I Undervoltage Testing Surveillance on Unit 3, when a 2 [psi] drywell signal was inserted, Reactor Building Ventilation tripped and SBGT initiated as expected. At 0510 [CST], reactor building to atmosphere differential pressure dropped below the [negative] 0.25 inches water. This condition represents a failure to meet Surveillance Requirement 3.6.4.1.1. As a result, entry into Technical Specification 3.6.4.1 condition A was made due to Secondary Containment becoming inoperable. This event is being reported in accordance with 10CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. At 0532, the 2/3 Reactor Building material interlock inner door was closed and Reactor Building [differential pressure] was restored to greater than [negative].25 inches of water column. An issue report has been initiated. An investigation will be conducted and a 60 day Licensee Event report will be submitted in accordance with 10 CFR 50.73(a)(2)(v)(C). "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-11-08
52354 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2016-11-02 | 2016-11-08 11:44 | 2016-11-08 | SWITCHGEAR CABINET DESIGN MODIFICATION REQUIRED "In accordance with 10CFR52.99(c)(2), V.C. Summer Units 2 and 3 Construction is making this notification to NRC for determining that Inspection, Test, Analysis, and Acceptance Criteria (ITAAC) 2.6.01.02.ii (Seismic Qualification of Reactor Coolant Pump Switchgear) for both units requires additional actions to restore its completed status. The Closure Notification for this ITAAC (NRC Index No. 580) was originally submitted on February 29, 2016 (reference ML16060A344 and ML16060A345). "On November 2, 2016, it was determined that modifications to the RCP switchgear cabinet design were required to ensure compliance with the applicable portions of IEEE 384, Standard Criteria for Independence of Class 1E Equipment and Circuits. The modification involved an engineering change which adds different equipment to the RCP Switchgear cabinet which function to trip the RCP. The new components were not previously seismically qualified for use in the RCP switchgear cabinet assembly. The additional components have now undergone seismic qualification testing for use in the RCP switchgear. The Equipment Qualification Data Package and Equipment Qualification Summary Report for the RCP switchgear will be revised based on the results of the testing to confirm the switchgear withstands seismic design basis loads. The revised testing report has been completed on November 8 2016." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0 | 2016-11-08
52353 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-11-08 08:51 | 2016-11-08 08:59 | 2016-11-08 | UNUSUAL EVENT DECLARED DUE TO EQUIPMENT FAILURE CAUSING AN EXPLOSION IN THE PROTECTED AREA "On November 8, 2016, at approximately 0840 EST, plant personnel reported an explosion within the Protected Area resulting in a fire with potential damage to plant structures or equipment. An Unusual Event was declared at 0851 EST. The onsite Fire Brigade was mobilized. The fire was extinguished at 0848 EST. The explosion was to the 138 kV power cross connect cable between the Unit 2 and 3 Station Auxiliary Transformers. Both Units are operating normally. There was no release of radioactive material. An investigation of the event is in progress." Offsite assistance was not required. Unit 2 was in a normal electrical line-up and Unit 3 was not affected. The licensee has notified the NRC Resident Inspector, State, Local, and Other Government Agencies. The licensee will issue a press release. Notified DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM R.T. THOMAS TO BETHANY CECERE AT 0955 EST on 11/8/16 * * * The Unusual Event was terminated at 0946 EST based on the fire being out. The licensee has notified the NRC Resident Inspector. Notified R1DO (McKinley), IRD (Gott), and NRR EO (Miller). Notified DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-11-08
52352 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-11-07 16:09 | 2016-11-07 20:44 | 2016-11-07 | HPCI DECLARED INOPERABLE DUE TO FAILURE OF IST SURVEILLANCE TEST "On November 7, 2016, at 1609 [EST], with the reactor at 100 percent core thermal power and steady state conditions, the High Pressure Coolant Injection (HPCI) system was declared inoperable. Pilgrim Nuclear Power Station (PNPS) was performing planned quarterly testing per Technical Specifications 4.13.A.1. During a review of the HPCI pump data taken during the test, it was determined that the recorded vibration reading on the Main Pump Outboard horizontal point (P4H) was 0.8335 in./sec which exceeds the IST required action range high limit of less than or equal to 0.830 in./sec. Accordingly, the HPCI pump was declared inoperable. "The Limiting Condition for Operation Action Statement 3.5.C.2 has been entered and planned troubleshooting Into the cause of the high vibration is in progress. In accordance with 10 CFR 50.72(b)(3)(v)(D), PNPS is providing an 8-hour non-emergency notification that the HPCI System is inoperable. "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector has been notified." The licensee will be notifying the State of Massachusetts regarding the event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-11-07
52351 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-11-07 13:45 | 2016-11-07 16:50 | 2016-12-01 | AGREEMENT STATE REPORT - SHUTTER FAILURE TO CLOSE The following was excerpted from information received from the State of New Jersey by email: "Event Narrative: On November 7, 2016, during the six-month shutter checks, the pneumatically operated shutter on the Vega source holder Phillips 66-Bayway Tag # PBL002 (source capsule S/N 0321CG) failed to close when tested. Several attempts were made wherein the shutter position indicator seemed to move slightly. It was concluded that the issue was not a failure of the air system controlling the pneumatic shutter actuator. The manufacturer was contacted to assess the problem. "Root cause(s) and contributing factors: The source remained in the holder attached to the vessel in its normal operating position. The integrity of the source holder remains intact so there should be no exposures. "Source/Radioactive Material/Devices: radioactive level gauge "Isotope and activity; manufacturer, model and serial number, leak test results as applicable: The source is a 50 mCi Cs-137 solid sealed source, S/N 0321CG. The last leak test was 10/19/15." The equipment is an Ohmart/Vega model SH-F1A source holder mounted to a vessel. New Jersey Case Number: 161107162023 * * * UPDATE FROM ED TRUSKOWSKI TO JOHN SHOEMAKER AT 1323 EST ON 12/1/2016 * * * The following update was received from the State of New Jersey via email: "Vega serviced the unit on November 11, 2016, with lubrication. It was considered to work properly after service. Phillips 66 notified NJDEP [New Jersey Department of Environmental Protection] on November 30, 2016, that a new unit will be purchased to replace the old unit. Event status is 'closed'." Notified R1DO (Bower) and NMSS_Events_Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-11-15
52350 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2016-10-19 | 2016-11-07 16:26 | 2016-11-07 | AGREEMENT STATE REPORT - NUCLEAR PHARMACIST RECEIVES GREATER THAN 50 REM EFFECTIVE DOSE EQUIVALENT The following report was received from the Oregon Department of Health via facsimile: "Oregon Health Authority, Radiation Protection Services (RPS) has confirmed on 11/07/16 that a cumulative effective dose equivalent of 50 rem [received by] a pharmacist working in several facilities. This information is being reported by PETNET Solution's corporate office in Knoxville, TN. "Oregon Health Authority, Radiation Protection Services (RPS) received a call on October 20, 2016 at 1348 [PDT] informing the office that a contract pharmacist may have received an exposure greater than 50 rem to [the] right ring dosimeter and is conducting an analysis to determine if the individual received a dose greater than 50 rem. [The] caller is [the], Corporate Radiation Safety Officer (CRSO), PETNET Solutions. "It's suspected that the individual received multiple doses while working at PetNet's Phoenix, Arizona and Portland, Oregon pharmacies. Dosimetry rings from both sites demonstrate a possible cumulative dose greater than 50 rem. The individual has now been restricted from working with radiopharmaceuticals at this time. "CRSO states that the incident was discovered on 10/19/2016 and as of 11/07/16, exposure levels of greater than 50 rem are confirmed. This notification involves two facilities in Arizona and Oregon and RPS is not sure if the HOO [NRC Headquarters Operations Officer] was contacted by other regulatory agencies. "CRSO has commenced a root cause analysis of the incident with an estimated date for completion within approximately two weeks." Oregon Incident Number: 16-0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2016-11-15
52349 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-11-03 | 2016-11-07 15:35 | 2016-11-07 | AGREEMENT STATE REPORT - FAILURE OF SOURCE TO RETRACT TO SAFE POSITION The following report was received from the Illinois Emergency Management Agency via email: "On Thursday, November 3, [2016] the licensee's Corporate RSO [Radiation Safety Officer] called to advised that one of their crews experienced a source retraction problem while at a temporary jobsite. Radiography shots were being taken with a nominal 60 Ci Ir-192 source at the Wood River Refinery, Wood River, IL. During a shot around 1230 [EDT] that afternoon it became obvious that the source would not retract using normal means. The crew contacted the local facility radiation safety officer to advise him of the event. The local radiation safety officer responded to the site within 30 minutes to discover that a portion of the drive cable assembly had been laid across a bare spot on a pipe that was otherwise insulated. The heat from the uninsulated section of pipe had caused the return side, cable housing coating to melt, forming an obstruction that the return cable could not pass. The RSO, having retrieved a source from a similar predicament in the past was able to quickly and efficiently cut the return side cable guide tube creating an open path for the cable and bypass the obstruction. The source was then able to be returned to the safe position without undue effort. The matter was resolved within an hour. The drive cable equipment has been removed from service. The camera was inspected and tested and put back into service. The direct ion storage dosimeter for the facility RSO was immediately analyzed at the end of the event and a dose of 3 mR was noted. Doses for the crew members were similarly analyzed and both found to be less than 30 mR since the last read which was performed at the end of the previous month. As the area being radiographed was on an overhead scaffold, no other personnel were in the work area at any time during the event other than the radiographers who maintained vigilance over the scene. A preliminary report with supporting photos was received the next day. Based on that report, an immediate investigation was not conducted at that time." Device: Radiography Exposure Device Manufacture: QSA Global Equipment Serial Number: D10972 Source Serial Number: 32867G Model Number: 880-D Radionuclide: IR-192 Activity: 2168.2 GBq Illinois Item Number: IL16011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IN | OTH | AGR |  |  |  |  | 0 | 2016-11-15
52348 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-10-06 | 2016-11-07 12:28 | 2016-11-07 | AGREEMENT STATE REPORT - SHUTTER FAILED TO OPERATE AS DESIGNED The following information was received by email: "On November 2, [2016], the registrant's representative reported [to the State of Illinois] that a generally licensed gauge under their control had failed to operate as designed. A Gamma Instruments model GR100 device exhibited signs of the shutter not closing properly. A contractor was notified and repairs affected. The gauge was subsequently returned to service with no additional engineering issues noted. Procedures at the plant were modified such that the area around the gauge is now cleaned following each shift." The fixed gauge serial number was 930706, and the sealed source was 37 GBq of Am-241. Illinois Event: IL 16010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-11-15
52347 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2016-11-05 04:04 | 2016-11-05 10:16 | 2016-11-05 | VALID ACTUATION OF RPS WHILE REACTOR SHUTDOWN "On November 5, 2016 an RPS [Reactor Protection System] actuation occurred from an actual high scram discharge volume level reaching the RPS actuation setpoint. This actuation was the result of a Redundant Reactivity Control System (RRCS) signal inadvertently generated during excess flow check valve testing with the reactor in cold shutdown. At the time of the actuation, all control rods were inserted. RCS pressure was approximately 830 psig to support excess flow check valve testing and shutdown cooling was removed from service. When RRCS initiated, the B Reactor Recirculation Pump tripped as expected and the scram air header depressurized as expected, which caused the high level in the scram discharge volume. The cause of the RRCS signal is being investigated. The A loop of RHR was placed back into the Shutdown Cooling mode of operation with reactor temperature being maintained at approximately 150 degrees F. There were no injuries as a result of this event." The licensee has notified Lower Alloways Creek Township and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-11-05
52346 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2016-11-01 | 2016-11-04 13:05 | 2016-11-04 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE ON NUCLETRON MICROSELECTRON The following is an excerpt of a report received from the Oregon Department of Health via email: [The Oregon Department of Health] had a teleconference with the Radiation Safety Officer (RSO). [The RSO] stated that during the morning QA check, the source would not retract. No patient was in the room and the QA check was performed with no one in the room. The RSO went inside the room just at the door and obtained an exposure [rate] reading of 2.6 mR/hr at approximately 15 feet from the HDR [high dose rate] unit, a Nucletron model microSelectron 106.990. The treatment room is secured at the current time until the Elekta FSE [Field Service Engineer] arrives. The RSO is working on treatment of another patient and will get more information as he gets time to do so. During a phone call with the Elekta RSO, the Elekta RSO stated that the FSE found that the HDR unit [obstruction alarm] was being tested during QA by locking the HDR exit port [in order to block the source] and [cause an] alarm condition. The port was only partially locked so that the source was able to get out but not able to retract. The FSE was able to retract the source by opening the port fully and didn't have to manually do it. Total dose received was estimated at 10 mR maximum. The Elekta RSO mentioned that there could be shavings from the sealed source capsule around the port and that leak tests have been negative but that the entire HDR head, including source is now to be replaced. Device: Nucletron Model: microSelectron 106.990 Activity: Ir-192, 10 Ci. Oregon Incident Number: OR160004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2016-11-14
52345 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-11-02 | 2016-11-03 12:36 | 2017-04-10 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DID NOT RETRACT CAUSING DOSIMETER ALARM The following report was received from the Texas Department of State Health Services via email: "On November 3, 2016, the Agency [Texas Department of State Health Services] was contacted by the licensee's radiation safety officer (RSO). The RSO was reporting that two radiographers had experienced a radiation dose causing pocket dosimeters to go off scale. The crew were working at a temp job site on a power plant. The camera had a 36 curie Ir-192 source. The crew could not hear the alarming rate meters due to excessive noise. The radiographers noticed the source had not retracted completely into the camera while trying to disconnect the guide tube to move the camera to another location. The radiographer reported to the RSO that the source was retracted immediately after finding the source extended. The time reported to the RSO with the source exposing the radiographer was less than 3 minutes. The pocket dosimeters were checked outside the area and found off scale. The RSO stopped all work, requested radiographers return to the shop and he checked the camera to find no defects. The RSO has sent the monitoring badges in for processing and is in the process of completing an investigation to determine exposure dose. A complete report will be provided by the RSO. Updates will be provided in accordance with SA 300 guidelines." Texas Incident #: I 9437 * * * UPDATE FROM IRENE CASARES TO JOHN SHOEMAKER AT 1613 EST ON 12/13/16 * * * "On November 3, 2016, the Agency received a call stating that a radiography crew had experienced an incident on November 2, 2016. The crew had been working at a Power Plant near Franklin, Texas when they experienced an incident involving a possible overexposure. The radiographers were working in a noisy area with all monitoring devices on their person. They had performed several exposure shots and were completing the last shot on a pipe before moving the camera to the next weld area. The radiographer had cranked in the source and both walked to the weld to discuss the next shot position. They were about five feet from the camera and behind the camera which was partially shielded by conduit and piping. Then one radiographer walked to the camera and using the quick disconnect, disconnected the guide tube. When he did this he noticed he source protruding from the camera about six inches and yelled at the other radiographer to get back away from the area. Both ran to the crank, one grabbed the survey meter and the other then cranked in the source, about a turn and half on the crank to secure the source in the camera. The source was in the camera. Both checked their alarming rate meters which were alarming and the pocket dosimeters were off scale. They called the RSO and then packed up their equipment for the day. An incident report was completed at the power plant before leaving the site. Once back at the radiography headquarters the badges were collected and mailed for processing. Both radiographers were interviewed by the RSO and then suspended until monitoring results were received. The RSO calculated the dose to be 1593 mrem for the one radiographer's hand dose. "Monitoring badge results were reported to the Agency on November 10, 2016, with a whole body dose of 309 mrem and a whole body dose of 317 mrem. The annual dose for both radiographers was provided with results of 2053 mrem and 2761 mrem. The November badges had been worn for two days when the incident occurred. "A re-enactment investigation was conducted on November 29, 2016, due to limited details on the report provided by the RSO and the calculations appeared to be short in dose. The investigation and interviews with the radiographers on November 29, 2016, revealed the dose to the hand, foot, gonads, knee, and whole body were slightly higher dose but still under the limits for an overexposure. We had calculated the dose to the hand to be approximately 29 rem instead of 15.9 rem reported by the RSO. The distance of the hand dose was provide by the RSO at 4 inches, during the re- enactment, a smaller distance of one half inch during the time the radiographer removed the guide tube was more accurate. His hand passed directly over the source when he pulled the guide tube over the source when it was extended from the camera. The shorter distance increased the dose, however was still under the 50 rem limit for an overexposure. The radiographer has not experienced any redness, blisters or soreness to his hand. He has been viewing his hands daily and has not notice any radiation burn or injury. During the investigation his hands were viewed and no noticeable damage was seen (26 days after the incident). "The cause of the incident was not retracting the source completely into the shielded position and not using a survey meter to ensure the source was shielded. The two radiographers had changed positions during this job. One usually worked the crank and the other collected the film. Neither radiographer heard the alarms on the rate meters due to the noise. Both radiographers commented during the investigation, that they weren't using the meter like they should and it was their fault for not doing the required survey. Violations were cited to company and radiographers." Notified R4DO (Kellar) and NMSS Events Notification via email. * * * RETRACTION FROM IRENE CASARES TO VINCE KLCO ON 4/10/17 AT 1253 EDT * * * The following information was received from the State of Texas via email: "[The Texas Department of State Health Services] would like to retract NRC event number 52345. At the initial reporting from the regulated entity, it was believed two radiographers had received an overexposure from a non-retractable source. After further investigation, it was not a non-retractable source, such as equipment failure. It was human error and the source was retracted by the radiographer. There was no equipment failure. It was operator error and the dose that both radiographers received was not over the reporting limits. Please retract this event. "Summary: On November 3, 2016, the Agency was contacted by the licensee's radiation safety officer (RSO). The RSO was reporting that two radiographers had experienced a radiation dose causing pocket dosimeters to go off scale. The crew were working at a temp job site on a power plant. The device was a Spec 150, serial 1500, Spec source G60, serial XG2601 with of Ir-192 with 36 curies of activity. The monitoring badges were sent for processing with results of 317 and 309 mrem doses. The annual dose for both radiographers was below the 5 rem limit. The calculations for the extremity dose (hand, foot, and knee) were below the 50 rem overexposure limit. The annual dose for both radiographers was provided with results of 2053 mrem and 2761 mrem. A re-enactment investigation was conducted on November 29, 2016 due to limited details provided by the RSO. The dose was calculated at 29 rem to the extremities which is under the limit 50 rem for reportable event. The cause of the incident was not retracting the source completely into the shielded position and not using a survey meter to ensure the source was shielded. To prevent recurrence, the company had a meeting (training) with employees stressing the importance of safety, following procedures, and being aware of surroundings. One violation cited to the company and each radiographer." Notified the R4DO (Kramer) and NMSS Events Notification via email | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-11-11
52344 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2016-11-03 03:00 | 2016-11-03 08:54 | 2016-11-03 | SERVICE WATER LEAK IDENTIFIED IN THE VAPOR CONTAINMENT BUILDING "At 0300 EDT on November 3, 2016, it was identified that a Service Water leak existed in the Vapor Containment Building of Indian Point Unit 3. The leak was determined to be from 31 Fan Cooler Unit and was subsequently isolated at 0344 EDT by shutting the Service Water isolation valves to 31 Fan Cooler Unit. This isolation meets the Technical Specification 3.6.1 Condition A Required Action. The leaking defect could have resulted in post-LOCA air leakage out of containment in excess of that allowed by Technical Specification 3.6.1 (Containment) which requires leakage rates to comply with 10 CFR 50, Appendix J. This event had no effect on the health and safety of the public. "This event is being reported under 10 CFR 50.72(b)(3) and the guidance of NUREG 1022, section 3.2.7 as a loss of safety function." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-11-03
52343 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-11-02 08:45 | 2016-11-02 15:35 | 2017-01-03 | RESIDUAL HEAT REMOVAL VALVE INOPERABLE FOR CONTAINMENT ISOLATION "During panel walkdown, it was discovered that a tag out for the 'C' Residual Heat Removal pump suction valve was active and the valve was open with its breaker open. This rendered the valve inoperable and Technical Specification 3.6.1.3 Action C for penetration with one inoperable PCIVs was entered. The action was to isolate the penetration by closing the valve within (4) hours or restore power. The event was discovered at 0845 [EDT] and the breaker was closed at 0925 [EDT]. Technical Specification 3.6.1.3 Action C (Isolate penetration within 4 hrs.) was entered at 0130 [EDT] (time breaker was opened per tagout) and exited at 0925 [EDT]. This condition of non-compliance existed from 0530 [EDT] on 11/02/16 until 0925 [EDT] on 11/02/16. This event is being reported under 10CFR50.72 (b)(3)(v)(C). "NRC Resident has been notified." * * * RETRACTION AT 1653 EST ON 1/3/2017 FROM MARK HAWES TO MARK ABRAMOVITZ * * * "In accordance with Technical Specification (TS) 3.6.1.3, Primary Containment Isolation Valves, the TS Basis states that one or more barriers are provided for each penetration so that no single credible failure or malfunction of an active component can result in a loss of isolation or leakage that exceeds limits assumed in the safety analyses. When two or more barriers are provided, one of these barriers may be a closed system. "During this event, one of the barriers in the penetration became inoperable: 'C' Residual Heat Removal (RHR) pump suction valve 10MOV-13C. After the initial NRC notification, it was confirmed that the RHR system piping is classified as a closed system outside containment. The integrity of the closed-loop RHR system is verified by monitoring the keep-full system. Since the piping is maintained full of water during normal and post-accident modes of operation, a barrier against post-accident, gaseous, containment leakage is provided. Therefore, the affected penetration could have performed its intended safety function since there was redundant equipment in the same system which was operable. This event is not reportable under 10 CFR 50.72(b)(3)(v)(C) and the original notification may be retracted. "Finally, the primary containment penetration with 10MOV-13C is with a closed system and the completion time per TS 3.6.1.3 Required Action C is 72 hours. The valve was restored to operable prior to exceeding this time." The licensee notified the NRC Resident Inspector. Notified the R1DO (Dentel). | 70 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-11-02
52342 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-11-02 10:34 | 2016-11-02 15:05 | 2016-11-02 | UNANALYZED CONDITION FOR CONTROL ROD DROP ACCIDENT AT LOW POWER "On November 2, 2016, while performing a re-evaluation of the radiological consequences of the Fermi 2 control rod drop accident (CRDA), DTE Electric Company (DTE) identified a non-conservatism in the current Fermi 2 design and licensing basis of the CRDA. As described in the Updated Final Safety Analysis Report (UFSAR) Section 15.4.9, the current design and licensing basis assumes that the post-CRDA release pathway consists of carryover with steam to the turbine condenser. The re-evaluation has identified that a forced release from the gland seal exhausters (GSEs) could also occur which could result in post-CRDA radiological consequences that exceed the current 10 CFR 100.11 offsite dose limits and Standard Review Plan 6.4 (General Design Criterion 19) main control room dose limits when operating at low power conditions. "The unanalyzed condition described above only applies to low power operating conditions (i.e. less than 10% power) since the fuel damage postulated as a result of a CRDA is only credible under low power operating conditions when an individual control rod worth is high. Fermi 2 is currently at 97% power and, therefore, the plant condition is currently bounded by the design and licensing basis such that the condition currently does not exist and no immediate actions are required. "However, Fermi 2 has operated at low power levels several times in the past three years. Those periods of operation at low power represent unanalyzed conditions that significantly degraded plant safety since the occurrence of a CRDA during those periods could have resulted in offsite and main control room doses exceeding regulatory limits. Therefore, this 8-hour notification is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). There was no adverse impact to public health and safety or to plant employees. "The licensee has notified the NRC Resident Inspector." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-11-02
52341 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-10-21 | 2016-11-02 11:38 | 2016-11-02 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION TO INCORRECT SITE The following report was received from the State of Georgia via email: "Northside Hospital's Radiation Safety Officer called the Department [Georgia Radioactive Materials Program Environmental Protection Division] on 10/21/2016, informing us of a misadministration with the HDR [High Dose Rate] that occurred approximately two weeks ago. The patient was to receive 5 vaginal treatments consisting of 1 cylinder, 1 capri and 3 capris. The misadministration occurred during the second treatment. The capri was inserted into the rectum instead of the vagina. The Authorized User (AU) was not certain if a misadministration occurred until 2 weeks after the treatment. The AU requested the assistance of the radiologist who confirmed that the rectum was treated instead of the vaginal area. Based on the calculations, the rectum received approximately 350 cGy, what is to be considered a low dose. Additional information from the licensee will be forthcoming." Treatment material used: Varian Medical Systems, model: Gamma Medplus iX, with an Ir-192 source of less than 22 Ci. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2016-11-10
52340 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2016-11-01 17:43 | 2016-11-01 19:01 | 2016-11-02 | ALERT DECLARED AT FARLEY UNIT 1 DUE TO AMMONIA EXCEEDING IDLH LEVELS IN THE AUXILIARY BUILDING "At 1743 CDT on 11/1/16, readings were obtained that indicated ammonia above IDLH [Immediately Dangerous to Life and Health] values in the Unit 1 Auxiliary Building and an Alert was declared by the Emergency Director. The plant is stable with Unit 1 at 2% power. Unit 2 is at 100% power [and stable]. The site is currently investigating to determine the source and ventilate the area." The licensee has informed the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, EPA EOC, FEMA National Watch Center (email), FDA EOC (email), Nuclear SSA (email). * * * UPDATE FROM BLAKE MITCHELL TO STEVEN VITTO ON 11/02/2016 AT 0443 EDT * * * "The following is the Emergency Preparedness 8-hour report for the Plant Farley ALERT declaration. An ALERT was declared at 1743 CDT on November 1, 2016, based on Emergency Action Level (EAL) HA3 (Release of toxic, asphyxiant, or flammable gases within vital areas which jeopardizes operation of systems required to maintain safe operations or establish or maintain safe shutdown) due to an ammonia discharge into the Auxiliary Building. Farley Unit 1 was in Mode 2 at 2 percent power and Unit 2 was in Mode 1 at 100 percent power throughout the event. "Actions completed during and leading up to termination from the event included walkdown of the area to locate the ammonia source, and isolating the ammonia source while atmospheric monitoring was performed in all affected and adjacent areas. Installation of additional ventilation fans was completed. This event has been entered into the Farley Corrective Action Program under Condition Report 10293519 (Ammonia levels in 100 Feet Radside). "A review of the Alert classification has determined that the classification was timely and accurate. All required notifications were completed accurately and in a timely manner. The ERO [Emergency Response Organization] notification system functioned as expected and all emergency response facilities were activated in a timely manner. There were no missing or injured personnel during the event. There is no evidence of tampering or sabotage of plant equipment leading to this event." At 2202 CDT on 11/1/2016, the ammonia source was identified as Valve N1P20V913. At 2228 CDT, the ammonia source was isolated. Final assessment of the Auxiliary Building showed that the ammonia levels were less than 5 ppm. It was determined that a deficiency in the valve component was the cause of the ammonia leak. The Alert was terminated on 11/1/2016 at 2340 CDT. The Licensee has notified the NRC Resident Inspector. Notified R2DO(Ernstes), IRD (Stapleton), NRR EO (Miller). Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, EPA EOC, FEMA National Watch Center (email), FDA EOC (email), Nuclear SSA (email). | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Startup; FMode1: Startup | ALERT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-11-01
52339 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-11-01 | 2016-11-01 18:15 | 2016-11-01 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received from the State of California via email: "On November 1, 2016, the RSO [Radiation Safety Officer] of RMA Group, contacted RHB ICE [State of California, Radiation Health Branch, Inspection, Compliance, and Enforcement Section] to report the theft of a moisture density gauge from the gauge user's pickup truck while he was home for lunch [in Grand Terrance, CA]. The nuclear gauge was inside a Type A transportation box was reportedly chained and secured properly but the chains were found cut. Troxler Labs model 3430, # 24568, contains 0.3 GBq of Cs-137 and 1.48 GBq of Am-241/Be. A power generator and other assorted equipment was also stolen. "[The RSO] will notify the local newspaper to place a Reward Notice for information leading to the safe return of the gauge. [The RSO] was asked to obtain a detailed report from the authorized gauge user. "The gauge's theft was reported to San Bernardino Police Dept. as well as the local calibration facilities were alerted of anyone bringing the gauge to them for service. [The State of California] RHB requested a copy of the police report and newspaper notice." California State Report 5010 Number: 110116 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-11-09
52338 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-10-29 | 2016-11-01 14:07 | 2016-11-01 | AGREEMENT STATE REPORT - RADIOGRAPHER DOSIMETRY LEFT NEAR EXPOSURE DEVICE DURING RADIOGRAPHY SHOT This report was received by the State of Washington via email: "During preparation of a radiography exposure, the radiographer and another radiation worker from Bechtel, attempted to untangle their dosimetry from the camera apparatus. In doing so, they left their dosimetry next to the camera during a shot. The radiographer exposed his TLD [Thermo Luminescent Dosimetry] and pocket dosimeter, as well as a client's electronic dosimeter during the exposure. Their dosimetry minus the radiographer's rate alarm was left next to the camera during the exposure. The radiographer wears dosimetry issued by Northwest Inspection and their client, Bechtel, sub contractor of the US Department of Energy. The radiographer's pocket dosimeter was off scale. Bechtel's electronic dosimeter showed an exposure dose of 300 mrem. The radiographer reported the incident to the RSO [Radiation Safety Officer]. The radiographer's TLD was sent to the dosimetry processing facility. Additional training for the radiographer has already taken place. In view of the fact that no 'persons' were overexposed, a spare TLD will be issued to the radiographer and will be allowed to continue to work." The radiography camera is a QSA Model Number A424-9, Serial Number 32886G, containing an Ir-192 34.5 Ci source. Washington State Incident Number: WA-16-045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-11-09
52337 | -1 | WATERFORD | 3 |  |  | [3] CE | 2016-10-31 11:00 | 2016-11-01 12:00 | 2016-11-08 | SUPPLEMENTAL COOLING INOPERABLE DURING MOVEMENT OF DRY CASK STORAGE HI-TRACK TRANSFER CASK This 24 hour report is being made as per 10CFR72.75. "On October 31, 2016, at 1100 [CDT], the Supplemental Cooling System was secured to the Dry Cask Storage Hi-Track Transfer cask, as allowed by Dry Fuel Storage T.S. 3.1.4, in preparation for moving the Hi-Track transfer cask. At approximately 1500, after moving the Hi-Track into position for downloading including securing the cleats to the mating device, the next step in the procedure was to lower the Hi-Track. When lowering the Hi-Track, a crane overload condition occurred. With the crane, attached the Supplemental Cooling System can not be operated and has remained secured. The Supplemental Cooling System is classified as 'Important to Safety Category B' and is required to be utilized, as necessary, to maintain the peak fuel cladding temperature below the allowed limits. T.S. 3.1.4 allows the Supplemental cooling system to be secured for up to 7 hours during the Hi-Track transfer process and then followed by a 7 day allowed outage time. This is being reported based on 10CFR72.75 which states in part that a 24 hour Non-emergency notification is required if; 'An event in which important to safety equipment is disabled or fails to function as designed'. "The Hi-Track is presently in a safe condition with supplemental cooling still secured." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM SCOTT MEIKLEJOHN TO DONG PARK AT 1111 EST ON 11/08/16 * * * "On November 1, 2016 at 1100 CDT Waterford 3 notified the NRC of a 24 hour reportable event per 10CFR72.75. The notification is documented under EN# 52337 based on the information known at that time. Follow up investigation determined that the conditions required per 10CFR72.75 were not met and should not have been reported. "10CFR72.75 states in part that a 24 hour non-emergency notification is required if, 'An event in which important to safety equipment is disabled or fails to function as designed.' It also requires that, 'The equipment is required by regulation, license condition, or certificate of compliance to be available and operable to prevent releases that could exceed regulatory limits, to prevent exposures to radiation or radioactive materials that could exceed regulatory limits, or to mitigate the consequences of an accident.' Based on a review of the bases for Certificate of Compliance, T.S. 3.1.4 thermal analysis shows that the fuel cladding temperature would not exceed the short term temperature limits applicable to an off normal condition. The bases further states that because the thermal analysis is a steady-state analysis, there is an indefinite period of time available to make repairs to the Supplemental Cooling System. The completion time of 7 days to restore the system per T.S. 3.1.4 is considered an appropriate and reasonable amount of time to plan the work and complete repairs. Based on this information there was no possibility of exceeding regulatory limits or the need to mitigate the consequences of an accident. "Waterford 3 is retracting event notification EN 52337. " The licensee has notified the NRC Resident Inspector. Notified R4DO (Campbell). | 45 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2016-11-01
52336 | 0 | WATERFORD | 3 |  |  | [3] CE | 2016-10-31 15:50 | 2016-10-31 18:07 | 2016-10-31 | OFFSITE NOTIFICATION FOR TRITIUM CONTAMINATED WATER SPILLED TO STORM DRAIN "On October 31, 2016, an informal, voluntary communication was made to the Louisiana Department of Environmental Quality (LDEQ) and the Saint Charles Parish Emergency Operating Center concerning a spill of greater than 100 gallons (estimated 150 gallons total) of tritium contaminated water to the storm drains located within the protected area. Tritium activity was 8.201E-06 micro Ci/ml and no detectable gamma activity. The spill lasted approximately 5 minutes before the pump moving the tritium contaminated water was secured. The contaminated water came from the Condensate Polisher Backwash Storage Tank and discharged from a [loose] hose connection going to a baker tank located within the protected area." The licensee has notified the NRC Resident Inspector. | 45 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-10-31
52335 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-10-26 11:42 | 2016-10-31 16:39 | 2016-10-31 | CONTAINMENT SUMP SUCTION VALVE OPENED DURING CONTAINMENT SPRAY PUMP TESTING "On October 26, 2016, the Harris Nuclear Plant was in Mode 6 with core reload complete, the reactor head removed, and reactor cavity water level greater than 23 feet. The refueling water storage tank (RWST) was less than 23.4% level as expected for the refueling conditions. "During surveillance testing to adjust the eductor flow throttle position, the containment spray pump was started in recirculation mode with the discharge valve shut. With RWST level less than 23.4%, logic was satisfied to actuate Engineered Safety Features Actuation System (ESFAS) Functional Unit 8, containment spray switchover to containment sump. The containment sump suction valve opened in accordance with the design, however the action was unexpected by the operators. Therefore, operators secured the containment spray pump and shut the containment sump suction valve. ESFAS Functional Unit 2, Containment Spray, was not actuated and water did not flow through the containment spray nozzles. This event is reported as a specified system actuation in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to the opening of the containment sump suction valve. "This event did not impact the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-10-31
52334 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2016-10-31 02:39 | 2016-10-31 09:27 | 2016-12-05 | HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABLE "On October 31, 2016, at 0239 hours [CDT], a defect (minor audible through-wall leak) was identified on the steam line drain valve 1-2301-55, HPCI Steam Line Drain Line Steam Trap Outlet Valve. The defect was identified by Operations personnel traversing through the HPCI room as part of normal rounds. HPCI was declared inoperable under Tech Specs 3.5.1, Condition G. The Reactor Core Isolation Cooling (RCIC) system was verified operable. HPCI remains available [but not operable]. The leak has been isolated. The 1-2301-55 is a manual valve downstream of the HPCI steam line drain trap. In a standby line-up, this line drains condensation from the HPCI steam supply line to the main condenser. During operation in an accident scenario, this line drains condensation from the HPCI steam supply line to the Torus via a drain pot. The location of the defect is in class 2 safety related piping. "HPCI is a single train safety system and this notification is being made in accordance with 10CFR50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." Technical Specification 3.5.1, condition G requires that HPCI be Operable within 14 days. * * * RETRACTION ON 12/05/2016 AT 1505 EST FROM MARK BRIDGES TO STEVEN VITTO * * * "The purpose of this notification is to retract the ENS Report made on October 31, 2016, at 0239 hours CDT (ENS Report #52334). "Upon further investigation, a pinhole through-wall leak was discovered in the body of the 1-2301-55 valve (HPCI Steam Line Drain Line Steam Trap Outlet Valve). The defect was characterized as a 1/32-inch rounded hole due to a manufacturing defect in the casting located on the downstream side of the valve near the piping connection. "A subsequent evaluation performed by Quad Cities Station considering the defect size, location, and characterization, confirmed the Unit 1 High Pressure Coolant Injection (HPCI) system would have performed its safety function when required. Based on this subsequent evaluation, ENS Report 52334 is being retracted. "Note: On November 1, 2016, at 1624 hours CDT, the 1-2301-55 valve (HPCI Steam Line Drain Line Steam Trap Outlet Valve) was successfully repaired and HPCI was returned to Operable status. "The NRC Resident Inspector has been notified." Notified R3DO (Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-10-31
52333 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-04-18 | 2016-10-31 09:09 | 2016-10-31 | AGREEMENT STATE REPORT - TWO MISSING TRITIUM EXIT SIGNS The following report was received via e-mail: "On October 26, 2016, the Agency was notified that two exit signs had been found missing during inventory. The licensee was contacted and asked to provide additional information including when the discovery was made and activity contained. The licensee's subsequent email revealed that the signs contained 0.426 TBq each of tritium. The signs had been discovered missing in April of 2016. The disposition of these signs is unknown. Additional information will be provided in accordance with SA-300." Texas event : I-9436 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-11-08
52332 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2016-10-29 10:32 | 2016-10-29 15:31 | 2016-10-29 | TECHNICAL SUPPORT CENTER (TSC) AND EMERGENCY OPERATIONS FACILITY (EOF) VENTILATION SYSTEM OUT OF SERVICE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A deficiency with the TSC and EOF ventilation system was discovered on October 29, 2016 at 1032 [EDT]. The deficiency involved a fire alarm unable to be reset impeding the ability to place the TSC and EOF in recirculation mode in the event of a radiological release. The fire alarm was reset at 1204 [EDT] on October 29, 2016, restoring capability to perform full emergency assessment to the TSC and EOF. "If an emergency had been declared while the fire alarm was unable to be reset requiring TSC or EOF activation during this period, the TSC and EOF would be staffed and activated using existing emergency planning procedures unless the TSC or EOF became uninhabitable due to ambient temperature. radiological, or other conditions. If relocation of the TSC or EOF became necessary, the Emergency Response Manager would relocate the TSC and/or EOF staff to an alternate location in accordance with applicable site procedures. "This condition had no impact on the health and safety of the public. "The NRC Resident Inspector has been notified." A malfunctioning smoke detector was removed from the system. Compensatory measures are being employed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-10-29
52331 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-10-28 15:00 | 2016-10-28 21:58 | 2016-10-28 | STANDBY LIQUID CONTROL TECHNICAL SPECIFICATION NOT MET "On October 28, 2016, at 1500 EDT, the Standby Liquid Control system was declared inoperable. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.7 Condition B was entered due to sodium pentaborate concentration not within limits. "Standby Liquid Control sodium pentaborate concentration was found to be low outside of the acceptable region following a Standby Liquid Control system tank high level alarm in the Main Control Room. Sodium pentaborate was added to the Standby Liquid Control tank by chemistry personnel and the concentration was then verified to be acceptable. Standby Liquid Control was declared Operable on 10/28/16 at 1935 EDT. The cause of the out-of-acceptable concentration was due to make-up water leaking by a closed valve. [The licensee cycled this valve and closed an upstream valve.] "Declaring the Standby Liquid Control system inoperable is reportable under 10 CFR 50.72(b)(3)(v)(A), (C), and (D) as an event or condition that could have prevented the fulfillment of a safety function of a system needed to shut down the reactor and maintain it in a safe shutdown condition, control the release of radioactive material, and mitigate the consequences of an accident." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2016-10-28
52330 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-10-28 12:17 | 2016-10-28 17:42 | 2016-10-28 | COLORADO AGREEMENT STATE REPORT - PANORAMIC IRRADIATOR DISABLED DUE TO STUCK SAMPLE DRAWER "The Department [Colorado Department of Public Health and Environment] was notified via phone on 10/28/16 at 1309 MDT by the Radiation Safety Officer [RSO] of Colorado State University (license # CO 002-19) that an irradiator room with a panoramic irradiator (J.L. Shepherd and Associates Model 81-14A irradiator, Cs-137 sealed source, 6000 Ci at 11/01/1976) has been disabled. The reason to disable the irradiator is because the sample drawer is stuck. The licensee reports the source is [apparently] fully in the shielded position because: the incident occurred before operating the irradiator, Primalert monitors are not alarming, and surveys do not suggest the source is exposed. "At approximately 1217 MDT, the licensee was to perform a monthly check of the safety system. It was a normal entry into the irradiator room. The irradiator source was not exposed. The licensee checked the operation of the sample drawer and it was found to be stuck, and cannot be opened. The sample drawer is to be used to place a sample into the housing closer to the source for irradiation. The irradiator source was not moved at any point. The RSO was then notified. "The keys to the irradiator room are currently secured in a locked box where no authorized operators to the irradiator can access. An e-mail was sent out to authorized operators that the irradiator is out of service. The RSO will be contacting J.L. Shepard & Associates on Monday 10/31/16 for service options. The Department will be notified on Monday 10/31/16 after J.L. Shepard & Associates communication." Colorado Event Report ID No.: CO16-I16-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-11-07
52329 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-10-28 09:40 | 2016-10-28 17:36 | 2016-12-27 | UNANALYZED CONDITION DUE TO FIRE BARRIER/HELB DOOR INOPERABLE The licensee reported an unanalyzed condition under 10 CFR 50.72(b)(3)(ii)(B) due to a fire barrier/HELB (high energy line break) door being inoperable during maintenance. This resulted in two of five safe shutdown panels to be declared inoperable. The door, located between the Turbine and Administrative Buildings, was opened for approximately two minutes for 'tool pouch work'. When Operations discovered the door was opened for maintenance, they declared the door inoperable until Operations performed the surveillance required to declare the door operable. The total time the door was inoperable was approximately 1 hour and 11 minutes. The licensee has notified the NRC Resident Inspector. * * * RETRACTION AT 1642 EST ON 12/27/2016 FROM DUSTIN SCURLOCK TO MARK ABRAMOVITZ * * * The condition reported in ENS 52329 pursuant to 10 CFR 50.72(b)(3)(ii)(B) has been evaluated, and determined not to be an unanalyzed condition that significantly degraded plant safety. "NRC Regulatory Issue Summary (RIS) 2001-09, 'Control of Hazard Barriers,' allows breaching of HELB barriers, provided the risk associated with the applicable maintenance activity is assessed and managed in accordance with 10 CFR 50.65(a)(4) of the Maintenance Rule. The hazard barrier controls procedure at JAF [James A. Fitzpatrick] is consistent with this guidance, and includes compensatory measures for opening of the subject HELB door (76FDR-A-272-26). Per the JAF hazard barrier controls procedure the secondary HELB doors are to be verified operable, and the Alternate Shutdown Panels 25ASP-4 and 25ASP-5 declared inoperable. "Based on a review of previous performances of ST-76Y, Fire Door Inspection and Operability Test, and the JAF Paperless Condition Reporting System, all applicable secondary HELB doors were operable prior to and during the 'tool pouch work' on 76FDR-A-272-26. JAF TS LCO 3.3.3.2, Remote Shutdown System (RSS), stipulates a completion time of thirty days to restore one or more required remote shutdown functions to operable. The duration of the 'tool pouch work' and inoperability of 76FDR-A-272-26 is well within this thirty day allowed outage time. In addition, the Alternate Shutdown Panels that were rendered inoperable by this condition are not required for mitigation of a HELB, and steam line break accidents are not discussed in the Technical Specification (TS) Bases for the Remote Shutdown System." The licensee notified the NRC Resident Inspector. Notified the R1DO (Lilliendahl). | 72 | 0 | 0 | 72 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-10-28
52327 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-10-28 09:24 | 2016-10-28 17:14 | 2016-10-28 | SHUTDOWN COOLING SYSTEM DECLARED INOPERABLE "At 0851 [EDT] on October 28, 2016, Division 1 RHR was started in shutdown cooling (SDC) mode of operation. Prior to starting the RHR system, the Alternate Decay Heat Removal (ADHR) system was maintaining RPV and Spent Fuel Pool temperature. "At 0924 on October 28, 2016, RHR [pump A] tripped due to RHR-MOV-17 (SDC suction valve) closing. This is considered to be an event or condition that could have prevented fulfillment of a safety function, and is reportable under 10 CFR 50.72(b)(3)(v)(B). RHR SDC subsystem A was declared inoperable. CNS [Cooper Nuclear Station] entered LCO 3.9.7, Condition A - Required Action A.1: Verify an alternate method of decay heat removal is available within 1 hour and once per 24 hours thereafter; Condition C - Required Action C.1: Verify reactor coolant circulation by an alternate method within 1 hour from discovery of no reactor coolant circulation and once per 12 hours thereafter, and Required Action C.2: Monitor reactor coolant temperature hourly. All LCO conditions specified have been met. "ADHR remained in service throughout the event and the plant remained aligned for natural circulation. Spent fuel pool weir temperature monitoring was commenced to verify natural circulation. No increase in RPV [reactor pressure vessel] temperature has been observed. There was no impact to plant operations. "Initial investigation indicates that installation of PCIS relay K27 during a maintenance activity physically agitated the adjacent relay, K30, which actuated and caused RHR-MOV-17 to close. "The NRC Resident Inspectors have been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2016-10-28
52326 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-10-27 | 2016-10-28 10:55 | 2016-10-28 | AGREEMENT STATE REPORT - SHUTTER ON GAUGE WOULD NOT CLOSE The following report was received from the Texas Department of State Health Services via email: "On October 27, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that the shutter on a Berthold model LB7440-D-CR gauge containing a 10 millicurie (original activity) cesium - 137 source would not close. The RSO stated they verified the shutter not closing by performing dose rate surveys around the gauge as they can not see the shutter. The shutter is in the open position which is the normal operating position for the gauge. The RSO stated the gauge does not create an exposure risk to their employees or any member of the general public. The RSO stated a service provider has been contacted to repair the gauge. Additional information will be provided in accordance with SA-300." Texas Incident #: I - 9435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [10 empty] | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-11-07
52325 | 0 | INTERTEK ASSET INTEGRITY MANAGEMENT |  |  |  |  | 2016-09-21 11:00 | 2016-10-27 17:01 | 2016-10-27 | SAFETY EQUIPMENT FAILED TO FUNCTION - RADIOGRAPHY SOURCE FAILED TO RETRACT "On 09/21/2016, a radiography crew was working on a pipeline ROW [right of way] located off of Wolf Run-Poplar Springs Road near Cameron, WV. After developing film shot earlier in the morning, the crew reattached the control cables and guide tube to the exposure device and moved to the next weld. After setup an attempt to make an exposure was made. The radiographer recalled the source assembly felt slightly obstructed upon entry into the guide tube. Upon verification that the guide tube was not kinked, an attempt to retract the source was made. Based on survey meter readings, it was determined the source was not retracting back into the camera, and somehow became disconnected. At this point the radiographer 'pushed' the source out to the collimator to provide some shielding. The crew then established a new 2 mR/hr boundary, advised site personnel of the situation, and notified [the] Pittsburgh site [Radiation Safety Officer] RSO. The [Corporate Assistant RSO] was notified and immediately dispatched [a source retriever] to the site for source retrieval. "At approximately 1430 EDT [the source retriever, who is also] the site RSO in Dover, OH, arrived at the location. After reviewing the circumstances leading to the disconnect and an inspection of the area, a plan to safely retrieve the source was [successfully] enacted. "All personnel involved acted as safely as possible considering the situation. The radiographer and their assistant immediately established a restricted area around the source and maintained visual surveillance of the area. At no time was any member of the public exposed to greater than 2 mR/hr. The three technicians involved with the monitoring and retrieval of the source followed company procedures and all were wearing the required radiation PPE. No one received a dose greater than 100 mrem during the entire operation. Film badge readings for the period were all within normal range." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-11-04
52324 | 0 | EMERSON FISHER CONTROLS INTL LLC |  |  |  |  | 2016-08-30 | 2016-10-27 16:43 | 2017-02-24 | PART 21 - POTENTIAL ISSUE WITH SEISMIC QUALIFICATION OF TYPE 546NS ELECTRO-PNEUMATIC TRANSDUCERS The following was received via email: "Pursuant to 10 CFR 21.21(a)(2), Fisher Controls International LLC ('Fisher') is providing required written interim notification of a potential failure to comply concerning Type 546NS Electro-Pneumatic Transducer Qualification Reports. "On August 30, 2016, Fisher became aware of a potential issue with the past qualification of the Type 546NS Transducers. Fisher's published seismic literature and certifications, based on testing by a 3rd party laboratory, exhibit inconsistencies when compared to more recent testing completed by Fisher. Regardless of these discrepancies, the Type 546NS Transducer remains qualified to perform before and after seismic loading. The scope of this investigation pertains only to operability during seismic events. "An extent-of-condition investigation is underway and 546NS testing data is being evaluated to determine if further testing is required. Fisher will complete the investigation by November 27, 2016 and, if necessary, will complete additional testing by February 10, 2017. "Should there be any further questions concerning this matter, please contact Benjamin Ahrens, Manager, Quality by email at Benjamin.Ahrens@Emerson.com or via phone at 641-754-2249." * * * UPDATE AT 0919 EST ON 11/23/16 FROM KIM SAGAR TO JEFF HERRERA * * * The following was received via email: "Pursuant to 10 CFR 21.21(a)(2), Fisher Controls International LLC ("Fisher") is providing an update to a previous written interim notification of a potential failure to comply concerning Type 546NS Electro-Pneumatic Transducer Qualification Reports. "On August 30, 2016, Fisher became aware of inconsistencies exhibited by prior qualification reports of the 546NS. A review of all previous Type 546 qualifications has been completed to reaffirm the qualification of the device for operation during seismic events. Based on this review, the 546NS remains qualified to perform before and after seismic loading. Additional testing is required to confirm if the device is capable of operating during an event. This additional testing is scheduled to be completed by February 10, 2017. "Once this additional testing has been completed and operability status determined, an appropriate announcement will be made pursuant to 10CFR21 reporting requirements. "Should there be any further questions concerning this matter, please contact Benjamin Ahrens, Manager, Quality by email at Benjamin.Ahrens@Emerson.com or via phone at 641-754-2249." Notified the R1DO (Dwyer), R2DO (Heisserer), R3DO (McCraw), R4DO (Taylor), Part 21/50.55 Reactors (via email) and Part 21 Materials (via email). * * * UPDATE PROVIDED BY KIM SAGAR TO JEFF ROTTON AT 1704 EST ON 02/24/2017 * * * The following is a summary of information that was received via email: "Pursuant to 10CFR21.21(a)(2), Fisher Controls International LLC ('Fisher') is providing required written interim notification of a potential failure to comply concerning Type 546NS Electro-Pneumatic Transducer Qualification Reports. This notification serves as a follow-up to a similarly titled report dated October 27, 2016. "Fisher initiated in-house seismic testing to analyze the performance of the device and associated mounting hardware when exposed to high-level seismic activity. These tests concluded on February 10, 2017. "Test data analysis is still underway. However, at the time of this publication, preliminary observations and conclusions can be made. The device itself, when rigidly mounted, does not exhibit natural frequencies in the tested frequency range consistent with previous qualification literature. When mounted to the standard 546 mounting bracket, the tested assemblies do not exhibit natural frequencies below 60 Hz. "During the course of testing, additional questions were raised regarding the configuration of the mounting bracket. These questions are currently being investigated. Questions regarding 546NS mounting will be addressed on a case-by-case basis with individual customers. "Further analysis and verification of the test data is needed before Fisher can make specific claims regarding the operability of the 546NS during high-level seismic loading. Fisher will complete the investigation by April 13th, 2017. "Should there be any further questions concerning this matter, please contact Benjamin Ahrens, Manager, Quality by email at Benjamin.Ahrens@Emerson.com or via phone at 641-754-2249." Notified the R1DO (Powell), R2DO (Bartley), R3DO (Jeffers), R4DO (Pick), Part 21/50.55 Reactors (via email) and Part 21 Materials (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-10-27
52323 | 0 | COLORADO DEPT OF PUBLIC HEALTH |  |  |  |  | 2016-06-01 | 2016-10-27 12:26 | 2016-10-27 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received by the State of Colorado, Department of Public Health and Environment (CDPHE) via email: "The Waste Water Treatment Plant at the City of Lamar was in construction during the time period the tritium exit sign was ordered by the contractor on the project. An intermediary electrician was brought in to help with the installation of the exit signs. Two signs were ordered and shipped separately. The City of Lamar responded to the annual general license notifications and explained the 2nd exit sign was never received. No further information is available. The tritium exit sign that is lost was manufactured by: Best Lighting Products Inc. AKA Forever Lites, Model #SLXTU1GW20, Serial Number #318952, Isotope: H-3, Activity: 11470 mCi. Date shipped 2-3-2011. "The City of Lamar was not able to locate the contractor or electrician who worked on the project. Sign is reported lost. The remaining tritium sign will be tracked and annual reports to CDPHE, General License, will be sent in. Should the city decide to remove the sign, notification will be sent in to Radioactive Materials Unit at CDPHE." Colorado Event Report ID No.: CO16-I16-25 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-11-04
52322 | 0 | NJ DEPT OF ENVIRONMENTAL PROTECTION |  |  |  |  | 2016-10-26 14:00 | 2016-10-27 12:20 | 2016-12-06 | AGREEMENT STATE REPORT - RESEARCH IRRADIATOR SAMPLE DOOR FAILED TO OPEN "A specific licensee reported a malfunction with one self-shielded irradiator, J.L. Shepherd model Mark I-68A, Serial # 1083 containing two Cs-137 sources with a total current activity of 6822 Ci. At approximately 2PM [EDT] on 10/26/16 [the licensee performed] an irradiation of 8 mice and were unable to open the sample port. They reported that both visual indicators and survey instruments show the source in the safe, shielded position. "The licensee is in contact with the manufacturer to assist with a repair. "This is a 24-hour reportable incident under N.J.A.C. 7:28-51.1 (10 CFR 30.50(b)2). NJDEP is tracking this incident internally as incident ID# C620765. NMED Report No. is yet to be assigned and will be reported later." * * * UPDATE ON 12/06/16 AT 1431 EST FROM JAMES MCCULLOUGH TO STEVEN VITTO * * * "The licensee provided a timely update on 11/18/2016 and a final report on 11/30/2016. On November 21, 2016, the device manufacturer replaced a component of the interlock system, a solenoid with spring and lockdown bolt. A preventative maintenance inspection was also performed, confirming the device was restored to normal operation." NJ Event # NJ-C620765, NMED Item Number: 160448 Notified R1DO (Burritt) and NMSS Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-11-04
52321 | -1 | WATERFORD | 3 |  |  | [3] CE | 2016-10-27 00:21 | 2016-10-27 08:26 | 2016-11-23 | LOSS OF CHARGING AND LETDOWN SYSTEMS FROM THE REACTOR COOLANT SYSTEM "At 0021 [CDT] on 10/27/16, Waterford 3 (WF3) experienced a loss of the charging and letdown systems from the Reactor Coolant System (RCS). Technical Specification (TS) 3.0.3 was entered due to the loss of all three charging pumps. Charging Pump AB was restored and aligned to replace Charging Pump A and WF3 exited TS 3.0.3 at 0055 on 10/27/16. "The cause of the loss of charging pumps was due to Refueling Water Storage Pool to Charging Pumps Suction Isolation, CVC-507, not opening as expected following a loss of Static Uninterruptible Power Supply (SUPS) 014AB during electrical troubleshooting. The cause of CVC-507 not opening is being investigated. Power was restored to SUPS 014AB at 0022. "WF3 is currently stable in Mode 3 with decay heat being removed by the Steam Bypass Control System. Pressurizer Level was maintained throughout the event. WF3 was previously shut down for reasons unrelated to this event. "The NRC Resident Inspector has been notified." Valve CVC-183 closed when the power supply was lost. CVC-183 is the Volume Control Tank outlet isolation valve. Waterford 3 will remain in mode 3 until the issue has been corrected. * * * RETRACTION AT 1005 EST ON 11/23/16 FROM SCOTT MEIKLEJOHN TO JEFF HERRERA * * * "This is a retraction of EN 52321 which was reported as an 8 hour Non-Emergency on October 27th at 0826 EST. "At 0021 [EST] on 10/27/16, Waterford 3 (WF3) experienced a loss of the charging and letdown systems due to an electrical transient on a Static Uninterruptable Power Supply that was being worked under a maintenance work order. The cause of the loss of charging pumps was due to Refueling Water Storage Pool to Charging Pumps Suction Isolation, CVC-507, not opening as expected following a loss of Static Uninterruptible Power Supply (SUPS) 014AB. Both operating charging pumps automatically secured due to low suction pressure trips as designed. "Post event investigation determined that a relay that had failed affected only the normal suction path isolation valves to the charging pumps and did not impact the safety related flow path that is required during a Safety Injection Actuation Signal (SIAS). Had an SIAS occurred during the period when no active suction path was aligned, the low pressure trip would have been blocked and the pumps selected to start on an SIAS would have auto started. The SIAS would have aligned the Boric Acid Make-up system for Emergency Boration. This would have resulted in the Charging Pumps being aligned to take suction from the Boric Acid Make-up pumps and/or Boric Acid Gravity Feed valves. "A function of the charging systems is to inject concentrated boric acid into RCS upon an SIAS. As discussed in FSAR Section 6.3.3.3.1, the injection flow from the charging pumps is not credited in the small break LOCA analysis. Charging is however credited for natural circulation cooldown without letdown in order to meet the safe shutdown requirements of NRC Branch Technical Position (RSB) 5-4. This analysis assumes that the charging source is initially Boric Acid Makeup Tanks followed by Refueling Water Storage Pool. Both sources were available. The charging system was fully capable of performing its safety function following the relay failure. The charging pumps remained capable of starting on an SIAS and the flow path from the Boric Acid Management system remained operable. In addition the flow path from the RWSP was not affected since the outlet isolation valve could be manually opened. "The NRC Resident Inspector has been notified." Notified the R4DO (Taylor). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-10-27
52320 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-10-26 23:00 | 2016-10-27 00:49 | 2017-03-17 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On October 26, 2016, at 2300 EDT, high wind conditions encountered on site resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met numerous times. The duration of time that the secondary containment Technical Specification was not met was approximately one second for each instance. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. At 2300 EDT, secondary containment vacuum was greater than the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) and steady, and the LCO was exited. There were no radiological releases associated with this event. A review indicates that this condition occurred earlier this shift during the high wind condition. "Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector ." * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-10-27
52319 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-10-26 14:39 | 2016-10-26 16:35 | 2016-10-26 | TORNADO MISSILE VULNERABILITIES "During the evaluation of tornado missile vulnerabilities and the potential impacts to Technical Specification (TS) plant equipment, it was concluded that the following SSCs [Structures, Systems, and Components] were vulnerable to tornado generated missiles: "The Turbine Driving Auxiliary Feedwater (TDAFW) pump exhaust vent is not adequately protected from tornado generated missiles. A tornado could generate missiles capable of striking the exhaust piping on the Turbine Driven Auxiliary Feedwater Pump, crimping the piping resulting in reduced flow capacity and rendering the TDAFW pump inoperable. "The Condensate Storage Tank (CST) vents are not adequately protected from tornado generated missiles. A tornado generated missile could strike the vent piping rendering it unable to relieve vacuum on the top of the CST and allow adequate water flow to the Auxiliary Feedwater Pumps and rendering the CST inoperable. "These conditions are reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with EGM-15-002 and DSS-ISG-2016-01 (enforcement discretion and interim guidance documents). The NRC Resident lnspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-10-26
52318 | 0 | HEMLOCK SEMICONDUCTOR CORPORATION |  |  |  |  | 2016-10-25 07:00 | 2016-10-25 16:00 | 2016-10-25 | SOURCE HOLDER STUCK SHUTTER "At approximately 0700 EDT, October 25, 2016, the RSO [Radiation Safety Officer] and Assistant RSO attempted to open the shutter on source holder 10071961 (Hemlock identifier), while preforming routine maintenance. The shutter operation failed, the shutter is stuck in the closed position. There were no exposures as a result of the failed shutter operation. Operating the shutter was part of a routine preventative maintenance plan. The process is currently shut down, therefore this incident caused no loss of production. The source holder is located on site. Hemlock Semiconductor Operations is in contact with Vega Americas, the manufacturer." Vega America Source Holder Model SHF 2-B Radionuclide: Cesium 137 - 800mCi Source holder serial number: 13544057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-11-02
52317 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-10-25 | 2016-10-25 15:53 | 2016-10-25 | AGREEMENT STATE REPORT - NUCLEAR GAUGE STUCK SHUTTER The following was received from the State of Texas via email: "On October 25, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee that while preparing to leak test a VEGA Americas, Inc. model SH-F1 nuclear gauge the shutter on the gauge could not be fully closed. Open is the normal operating position of this gauge. The gauge contains a 60 millicurie (original activity) cesium-137 source. The gauge is on the third floor of a vessel and does not present a exposure hazard to workers or members of the general public. The licensee has contacted a service provider to repair the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-11-02
52316 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2016-10-21 08:15 | 2016-10-24 11:18 | 2016-10-24 | AGREEMENT STATE REPORT - SOURCE DISCONNECT The following was received from the State of Minnesota via email: "At approximately 0815 CDT on Friday, 10/21/16, radiographers for Midwest Industrial X-Ray experienced a source disconnect while working on a project for Excel. The project was taking place outside of Waverly, MN, in a rural area. A 34 Ci source (serial number XF2112, model G60) of Ir-192 experienced a disconnect from a SPEC 150 exposure device. The RSO for Midwest Industrial X-Ray, was dispatched to the site and arrived at 1345 CDT on 10/21. Source retrieval was completed by 1445 CDT. Exposures were checked on all involved, with a maximum exposure of 3 mR. Midwest Industrial X-Ray is performing an analysis to determine the cause of the disconnect and will submit a written report within 30 days. More information from the Minnesota Department of Health is forthcoming." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2016-11-01
52315 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-10-23 19:08 | 2016-10-23 23:41 | 2016-10-23 | CONTROL ROOM EMERGENCY VENTILATION FAN INOPERABLE DUE TO ELEVATED VIBRATION "At 1908 CDT on 10/23/16, elevated vibration readings were identified on Cooper Nuclear Station [CNS], Control Room Emergency Filter System (CREFS) supply fan A. Vibration readings were evaluated by Engineering and were determined to be indicative of bearing failure on supply fan A. The Control Room declared CREFS inoperable and entered LCO 3.7.4, Condition A, which requires restoration of CREFS to operable status in 7 days. Repair activities have been initiated for this condition. "The plant is currently in Mode 5, with refueling activities and OPDRVs [Operation with Potential to Drain Reactor Vessel] in progress. CNS is not currently in the mode of applicability for a USAR defined accident. This condition is being conservatively reported under 10 CFR 50.72(b)(3)(v)(D) as a single train safety system that is required to be OPERABLE during situations under which significant radioactive releases can be postulated." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-10-23
52314 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-10-20 | 2016-10-21 15:31 | 2016-10-21 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The State of Texas provided the following report via email: "On October 21, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee that one of its radiography crews were unable to retract a 71 curie iridium-192 source into a QSA 880D radiography device. The radiographers had placed the guide tube stand on a wooden box to complete an exposure when, during the exposure, the stand fell off the box and landed on the guide tube crimping it enough that the source would not pass by it. "The radiographers contacted the licensee's radiation safety officer who sent a team of individuals to recover the source. The recovery team placed lead shielding over the source and was able to remove the crimp enough to retract the source back into the exposure device. No one involved in the event received an exposure that exceeded any limit. No member of the general public was exposed due to this event. Additional information on this event will be provided in accordance with SA-300." The event location was Exxon Mobil in Beaumont, TX. Texas Incident #: I-9433. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-10-31
52313 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-06-21 | 2016-10-21 10:16 | 2016-10-21 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received via e-mail: "Planned Parenthood purchased the exit sign when they sold the building. No transfer information was provided. The principals of Dunkeld-Broadway purchased the building and had the interior demolished. All the material was placed in dumpsters and removed by waste management providers." Source Description: SRB Technologies Inc., tritium exit sign H-3, Model # BX10BK, Serial Number CO16875, 9210 mCi. Colorado Report ID: #CO16-I16-24 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-10-31
52312 | 0 | AGILENT |  |  |  |  | 2016-09-21 | 2016-10-21 08:28 | 2017-01-27 | LOST ELECTRON CAPTURE DEVICE Four electron capture detectors (ECDs) were shipped at the same time from Shanghai to Wilmington, DE. The ECDs were shipped by air freight and three of the ECDs arrived at the beginning of October. The remaining ECD has not arrived and a search is ongoing. Source: Ni-63, 15 mCi fully encapsulated * * * UPDATE ON 1/27/17 AT 1457 EST FROM DAVID BENNETT TO DONG PARK * * * As a corrective action, the licensee has changed warehouse operations to a different warehouse used to receive devices manufactured in China. Notified R1DO (Welling) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-10-31
52311 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2016-10-13 | 2016-10-20 15:16 | 2016-12-15 | AGREEMENT STATE REPORT - DIAGNOSTIC RADIOACTIVE SOURCE MISSING On the morning of 10/13/16, a patient received a diagnostic 0.297 mCi I-125 seed implant to characterize a breast lesion. That afternoon, the tissue and implanted seed were removed and sent to pathology for assessment. The bio-waste was received in pathology as a non-radioactive sample contrary to hospital procedures. A subsequent search of the pathology lab could not locate the missing source. The State of Nebraska was notified of the incident on 10/19/16. * * * UPDATE ON 12/15/16 AT 0958 EST FROM BRYAN MILLER TO DONG PARK * * * The following was received from the State of Nebraska via email: "A Radioactive Seed Localization (RSL) procedure was performed on Thursday October 13, 2016, and contrary to procedures, the seed was sent to Pathology without an escort from the radiation safety office. Since there was no presence from radiation safety, pathology treated the excised sample as non-radioactive. It was not until the next day on Friday, the Thursday's RSL procedure was made known to the Radiation Safety Office. During Friday's procedure, the CNMT inquired why the paperwork from the Thursday's procedures was not picked up. This alerted Radiation Safety that a seed was sent to pathology without their presence to retrieve the seed and that there may be a misplaced seed. With the help from a radiologist, Radiation Safety reviewed the x-ray from the excised tissue to ensure the seed was removed from the patient. The x-ray did in fact indicate the seed was removed from the patient. Since the tissue is sent to the pathology lab, Radiation Safety surveyed the pathology lab and it's personnel intensively. They source could not be found. Radiation Safety has two theories where the source may have ended up. Down the sink or in a 20 gallon biological waste container. The Licensee is changing the name of the lumpectomy procedure to make a clear distinction between a non-radioactive lumpectomy and a lumpectomy that includes a radioactive material source. This will alert the staff that the radioactive seed needs to have Radiation Safety escort the seed to pathology. It will also alert the pathology staff of the radioactive seed and to ensure to locate and separate the seed from the sample prior to dissecting the tissue. Another precaution is that the mammography tech is going to label the sample container/slide with a 'Caution, Radioactive Materials' label to confirm the seed has been found and to also alert the pathology staff of the presence of the radioactive seed. Training of these changes has been performed and Radiation Safety will keep a close watch on the next procedures to ensure the new procedure has been implemented." Item Number: NE160001 Notified R4DO (Kellar) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2016-10-28
52310 | 0 | NEXTERA ENERGY SEABROOK, LLC |  |  |  |  | 2016-08-31 11:26 | 2016-10-20 11:45 | 2016-10-20 | WESTINGHOUSE LIFE LINE D TYPE LAC INDUCTION MOTOR FAILURE The following Part 21 Report was received from the licensee via facsimile: 10 CFR Part 21 Notification - Westinghouse Life Line D Type LAC Induction Motor Model HSDP 4000V, 700hp. "This is a non-emergency facsimile notification required by 10 CFR 21.21(d)(3)(i). A written notification in accordance with 10 CFR 21.21(d)(3)(ii) will be provided within 30 days. "NextEra Energy Seabrook, LLC has determined there is evidence that the Westinghouse Life Line D Type LAC Induction Motor Model HSDP 4000V, 700 hp motors, original to plant construction, have a deviation from expected quality of construction. Of the four motors purchased for Unit 1, Primary Component Cooling Water (PCCW) pumps CC-P-11-D and CC-P-11-C failed after approximately 87,000 hours of operation on July 23, 2008, and November 21, 2008, due to a short caused by localized heating. On June 13, 2015, CC-P-11-B failed due to shorted windings following approximately 32,000 hours of operation. Failure analysis determined the heating was most likely caused by a turn-to-turn short circuit which led directly to the eventual failure of the entire coil-to-ground. Forensic examination identified that the coil insulation was not tightly wrapped, resulting in less than 100% resin penetration throughout the stator insulation system (i.e., voids). The voids led to poor thermal conductivity and localized hot spots that accelerated the degrading of insulation properties over time. "Based on the failure analysis, it can be concluded that the undesirable coil quality is most likely attributed to workmanship, not motor design. The failure of motor insulation could cause phase-to-phase and phase-to-ground faults which ultimately would prevent motor and PCCW pump from performing their intended safety function. "The identified condition appears to be a deviation from expected quality of construction and the three failures indicate that the condition is likely applicable to all the motors manufactured at the same time. "The NRC Senior Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-10-20
52309 | -1 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2016-10-19 18:30 | 2016-10-20 00:09 | 2016-11-10 | SAFETY INJECTION PIPING WELD FLAW "While performing a scheduled inservice inspection on a section of safety injection system piping, a flaw was identified in a circumferential weld on the 14 inch safety injection line from the 2A safety injection tank to the 2A reactor coolant loop. Examination results indicate that the flaw constitutes a welding defect that cannot be found acceptable under ASME Section XI, IWB-3600, or Table IWB-3410-1. Further analysis is being conducted. "The unit had been shutdown for its 19th refueling outage (3R19) on October 8, 2016, at 0000. "The NRC Resident Inspectors have been informed of this condition." This piping is required to be operable in modes one through four. * * * RETRACTION ON 11/10/16 AT 1640 EST FROM ROBERT CHU TO MARK ABRAMOVITZ * * * "Subsequent engineering examination of the weld on the 14" safety injection line from the 2A safety injection tank to the 2A reactor coolant loop using enhanced examination techniques concluded the indication in the circumferential weld does not represent a flaw constituting a weld defect. The indication was the result of a metallurgical weld interface in the area of a previously documented weld repair. Therefore, the indication is acceptable under ASME Section XI with no further analysis required. "Based on the above information, PVNGS has determined the indication does not represent a degraded condition of a principal safety barrier as defined by 10CFR 50.72(b)(3)(ii)(A) and event notification #52309 is retracted. "The NRC Resident Inspectors have been notified." Notified R4DO (Campbell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Defueled; FMode3: Defueled | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-10-20
52308 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-10-19 | 2016-10-19 18:25 | 2016-10-19 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following was received from the State of Colorado via email: "The radiography source disconnect occurred on 10/19/2016 at a metal fab yard in Berthoud, CO. No members of the public are believed to have been exposed to radiation from the incident at this time. The source isotope was Ir-192 with an activity of 40 Ci. The source was successfully retrieved by the licensee. The licensee reported the following dose estimates for those involved in the incident. "Radiation Safety Officer: 50 mR "Radiographer: 28 mR "Assistant: 10 mR "A written report from the licensee is pending; and will be followed-up by a formal investigation." Event Report ID No.: CO16-I16-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-10-27
52307 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-10-19 14:50 | 2016-10-19 16:42 | 2016-10-21 | SAFEGUARDS REPORT - CONTRABAND FOUND NOT IDENTIFIED IN THE INVENTORY DURING REMODELING ACTIVTIES Discovered contraband in the protected area. Compensatory actions were taken. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1215 EDT ON 10/21/16 FROM MATTHEW McCORMACK TO S. SANDIN * * * The licensee is retracting this report based on the following: After further review the licensee concluded that this incident did not met the reporting criteria. The licensee informed the NRC Resident Inspector. Notified R3DO (Orth) and 73.71 Safeguards Group via email | 0 | 100 | 78 | 0 | 100 | 78 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-10-19
52306 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2016-10-18 15:35 | 2016-10-19 16:27 | 2016-10-19 | TECHNICAL SPECIFICATION VIOLATION "On October 18th, 2016, the logarithmic channel was rendered inoperable when a ground wire became detached from the log pre-amp. This, in combination with the pre-amps close proximity to other electrical wires, created enough noise to make the log channel reading unreliable. The reactor was operated for over an hour before the malfunction was identified. At that point, the reactor was scrammed and secured. The compromised ground was discovered and replaced, and the pre-amp was placed on a platform away from the interference of the other electrical components. This log channel reading returned to normal, but operations were still suspended until the channel could be more thoroughly tested. A Corrective Action Report (CAR) was initiated. This is a violation of Technical Specifications 3.2.2, 3.2.3 and 4.2(e). This report to the NRC Operations Center is required by Technical Specification 6.2.2." The licensee has notified the NRC Project Manager (Wertz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | OR | NPR | [5 empty] | 0 | 2016-10-19
52305 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-10-18 15:51 | 2016-10-19 15:23 | 2016-10-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the State of Colorado via email: "During the time the St Julien [Hotel and Spa] was under construction, the fire marshal indicated additional exit signs were needed. The subcontractor working as the intermediary service provider was Riviera Electric. They ordered 3 tritium exit signs to be used on the property. After several discussions, it was determined the tritium exit signs posed a hazard and liability issues. The final decision was not to install them on the property. The disposition of the 3 tritium exit signs is unknown. They are being reported as lost. Riviera Electric is no longer in business." Event Report ID No.: CO16-I16-22 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-10-27
52304 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-10-17 | 2016-10-19 10:34 | 2016-10-19 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following report was received via fax: "Radiation Safety Staff from a hospital in New York called on 10/18/2016 to report that for a patient who was treated with SIR Spheres [containing Y-90] on 10/17/16, it was estimated that about 22.5% less than intended had been delivered. 4.05 mCi was ordered. Assayed at 4.2 mCi. Post treatment survey of the device and residuals showed 1.06 mCi left over. Which means 3.14 mCi was administered, instead of the intended 4.05 mCi. They will mail a report within a week." New York state Event #NYDOH-NY-16-07 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-10-27
52303 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-10-18 17:50 | 2016-10-18 22:18 | 2016-10-18 | FITNESS FOR DUTY A non-licensed supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test.. Unescorted access to the plant has been denied. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2016-10-18
52302 | 0 | C&D TECHNOLOGIES INC |  |  |  |  | 2016-09-13 | 2016-10-18 16:23 | 2016-10-18 | PART 21 - EVALUATION REGARDING TERMINAL WELDING FAILURE IN 3DCU-9 BATTERIES The following information is a synopsis of information received via E-mail: On August 8, 2016 a user of commercial grade (non-Class 1E) 3DCU-5 batteries notified C&D of an issue with two units that exhibited high on-charge voltage and sulfated positive plates. The batteries were returned and analyzed. On September 13, 2016 C&D's laboratory issued a report showing that the batteries had failed welds between the terminal posts and the external battery terminals. This weld has the function of carrying current between the battery energy storage elements and the customer load. Failure of the welds could interrupt the current flow to customer loads during discharge. Although the batteries were not sold or used in a nuclear safety related application, C&D conducted an extent of condition analysis to determine whether this condition could exist in DCU products sold into safety related products. Although no similar reports have been made from users of Class 1E DCU batteries, based on the results of this analysis, there is a risk that this condition may exist in safety related products. The batteries in question are DCU Batteries, manufactured from April 2010 to August 2016. The battery manufacturing date is on the label. The following nuclear plants were supplied DCU batteries for use in 1E applications, with shipment dates of April 2010 to August 2016: Energy Northwest - Columbia, Exelon - Nine Mile, Talen Energy - Susquehanna, Entergy - Grand Gulf, and Exelon - Limerick. As corrective actions, C&D has implemented a discharge test to detect and eliminate any improperly made welds prior to shipment to end users. C&D has also performed additional training and qualification work with employees responsible for terminal welding on DCU products. These actions were implemented prior to shipment of Class 1E nuclear products in September 2016, and now are complete. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-10-18
52301 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-10-14 09:00 | 2016-10-18 14:37 | 2016-10-18 | AGREEMENT STATE REPORT - RADIOGRAPHY CREW ARRESTED The following information was received via E-mail: "At 0900 CDT on Oct. 14, 2016, the Oklahoma Department of Environmental quality was informed by Desert NDT dba Shawcor (OK-32104-01) that a radiography crew had been arrested in Ardmore, OK and the truck, with source on board, had been impounded by the local police. Initial notification to NRC was made that day via NMED, though it has not been posted on the NMED site yet. The source was picked up by the licensee about 1300 CDT that afternoon." No further information is known at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-10-26
52300 | 0 | ITT ENIDINE INC. |  |  |  |  | 2016-08-19 | 2016-10-18 10:08 | 2016-10-18 | PART 21 REPORT - DEFECTIVE CURRENT TO PRESSURE TRANSDUCERS The following was received by facsimile: "The ITT Conoflow models GT25CA1826 and GT25CD1826 current to pressure (l/P) transducers produce a calibrated 3.0 to 15.0 psi output pressure from a 4.0 to 20.0 mA DC (input) signal. Other dedicated l/P transducer part numbers are available with different output pressure ranges and input signal values. "On August 19, 2016 a defective model GT25CA1826 (s/n 628894) was received for evaluation. This transducer would only achieve 0-9 psi output pressure, falling short of the specified 3-15 psi output range. The failure was caused by misalignment of a key internal sub-assembly component as a result of shipping damage (mechanical shock). The product has been repaired, calibrated/tested, and is being returned to the customer (Arizona Public Service Co.). "The following is a list of customers, and the specific l/P transducer part numbers procured from ITT since 2006. These customers will be notified by November 1, 2016. "ACSYR SL GT25CA1826 ALABAMA POWER COMPANY GT25CA1826 AMERGEN ENERGY, LLC GT25CA1826 ARIZONA PUBLIC SERVICE CO GT25CA1826 ASIAM INT'L (TAIWAN) INC. GT25CA1826 CALVERT CLIFFS NUCLEAR POWER PLANT, INC GT25CD1826 CATAWBA NUCLEAR STATION GT25CA1826 GT25CD1826 CCNPP STOREROOM GT25CD1826 CENTRAL NUCLEAR DE ALMARAZ GT25CD1826 CONTROL COMPONENTS INC GT25CD1826 DETROIT EDISON GT25CD1826 DTE ENERGY GT25CD1826 ENERGY NORTHWEST GT25CA1826 ENERTECH CURTISS-WRIGHT GT25CA1826, GT25CD1826 ENRICO FERMI POWER PLANT 2 GT25CD1826 ENTERGY OPERATIONS GT25CA1826, GT25CD1826 ERGYTECHINC GT25CD1826 EXELON BUSINESS SERVICES GT25CA1826 FLOWSERVE GT25CA1826 GEFRAN BENELUX NV GT25CA1826 GT25CD1826 KOREA HYDRO & NUCLEAR PWR GT25CA1826 NEBRASKA PUBLIC POWER GT25CA1826 NUCLEAR POWER PLANT KRSKO GT25CA1826 OMAHA PUBLIC POWER DIST GT25CA1826 GT25CD1826 ONTARIO POWER GENERATION GT25CA1826 GT25CD1826 SPX MCKEAN GT25CA1826 TVA NUCLEAR ASSURANCE AND LICENSING GT25CA1826 GT65CD1826 WATTS BAR UNIT 2 CONSTRUCTION GT25CD1826 WEIR VALVES & CONTROLS UK GT25CA1826 ZVONIMIR ZEC GT25CA1826" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-10-18
52299 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2016-10-18 04:56 | 2016-10-18 06:11 | 2016-10-18 | CONTRABAND SUBSTANCE FOUND INSIDE PROTECTED AREA "This report is being made pursuant to 10 CFR 26.719(b). "At 0305 [CDT] today an unknown substance was identified inside the protected area (inside an emergency light fixture in the emergency escape hatch for containment). At 0456, local law enforcement determined [the substance] was likely a prohibited substance (marijuana). The substance was obviously very old, so is surmised to be from a preoperational period and unable to be positively tested. "The item (a bag of leafy material, round metal tube, rope with washer, light bulb) was under the control of the site security department upon discovery and was turned over to local law enforcement for disposal. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | KS | POW |  | 26.719 |  |  |  | 0 | 2016-10-18
52298 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-10-15 | 2016-10-17 14:40 | 2016-10-17 | AGREEMENT STATE REPORT - DENSITY GAUGE SHUTTER STUCK IN OPEN POSITION The following information was received via facsimile: "The licensee discovered this event on October 15, 2016 and notified the Department [PA Department of Radiation Protection] on October 15, 2016 via voice message after business hours. It is reportable within 24 hours per 10 CFR 30.50(b)(2). "During normal daily operations, a density gauge was found to have a shutter that was nonresponsive and stuck in the open position. No overexposures have occurred and the gauge has been taken out of service. A service provider has already made the necessary repairs as of today, October 17, 2016. The gauge is an Ohmart/Vega Model SHLG. The serial number of the device is unknown at this time. The device originally contained 1200 millicuries of Cs-137. "The cause of the event is unknown at this time. "A reactive inspection is planned by the Department. More information will be provided upon receipt." Pennsylvania Event Report ID No: PA160031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-10-25
52297 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-10-15 08:57 | 2016-10-15 15:46 | 2016-10-16 | REACTOR VESSEL HEAD PENETRATION NOZZLE FLAW "On October 15, 2016, while the Harris Nuclear Plant was shut down for a scheduled refueling outage, the reactor vessel head penetrations were being examined in accordance with the lnservice Inspection Program. Ultrasonic examinations identified a flaw in a head penetration nozzle. The unit is in a safe and stable condition. The flaw will be repaired prior to startup from the refueling outage. "The flaw and repair have no impact on the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." The flaw is located on the J groove weld of Nozzle 40. No boric acid deposits were located near the nozzle. * * * UPDATE FROM JOHN CAVES TO STEVEN VITTO ON 10/16/2016 AT 1549 EDT * * * "Subsequent inspections identified an additional nozzle that will require repairs (Nozzle 51) prior to startup. Inspections continue and are expected to be completed by October 18. The additional inspection indication and repair have no impact on the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." The flaw is located on the J groove weld. No boric acid deposits were located near the nozzle. Notified R2DO(Ehrhardt). * * * UPDATE FROM JOHN CAVES TO STEVEN VITTO ON 10/16/2016 AT 1844 EDT * * * "Subsequent inspections identified an additional nozzle that will require repairs (Nozzle 30) prior to startup. Inspections continue and are expected to be completed by October 18. The additional inspection indication and repair have no impact on the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." Notified R2DO(Ehrhardt). * * * UPDATE FROM INGRID NORDBY TO DONG PARK ON 10/19/2016 AT 1756 EDT * * * "On October 19, 2016, a liquid penetration examination was performed on the weld of the previously repaired Nozzle 23. The examination indicated that the weld will require repair prior to startup. Inspections on repaired welds have been completed. This additional inspection indication and repair have no impact on the health and safety of the public or of station employees. The NRC Resident Inspector has been notified." Notified R2DO (Masters). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-10-15
52296 | 0 | BAYER CORPSCIENCE LP |  |  |  |  | 2016-10-13 15:00 | 2016-10-14 14:17 | 2016-10-14 | STUCK SHUTTER ON A DENSITY GAUGE The licensee Radiation Safety Officer (RSO) determined that the shutter to a Berthold Model LB7442 gauge with a 1 Ci Cs-137 source (serial number: 012\06) did not shut during biannual maintenance checks. Personnel is informed about the gauge with proper signage, and the RSO does not believe any exposure to personnel occurred, because the shutter is normally in the open position. A licensed Berthold technician has been contacted and will come to the site to repair the gauge. The licensee notified NRC Region 3 (Nieves). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-10-24
52295 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-10-12 13:38 | 2016-10-12 15:17 | 2016-10-12 | MANUAL REACTOR TRIP DUE TO SPURIOUS FEEDWATER ISOLATION "At 1338 CDT, a spurious electrical fault on a unit substation motor control center caused a spurious feedwater isolation and required a manual reactor trip on Unit 2 Byron Station due to lowering steam generator level. Auxiliary feedwater automatically actuated to supply feedwater flow and is maintaining steam generator level within procedurally required levels." The motor control center fault resulted in feedwater isolations on two of four steam generators. All rods inserted during the trip. Decay heat is being removed via the steam dumps to condenser. Plant response to the trip was uncomplicated. Unit 2 is in a normal shutdown electrical lineup with power available from offsite. The grid is stable. Byron Station Unit 1 is at 95% power and stable and was unaffected by the transient on Unit 2. The cause of the motor control center fault is under investigation. The licensee has notified the NRC Resident Inspector and will be issuing a press release concerning the manual reactor trip. | 0 | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-10-12
52294 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-10-11 09:38 | 2016-10-11 16:48 | 2016-12-12 | UNANALYZED CONDITION DUE TO FAILURE OF A WATERTIGHT DOOR TO CLOSE "At 0938 [EDT], the watertight door in the Unit 1 Inboard Service Water Penetration Area was unable to be closed. The watertight door serves as a High Energy Line Break (HELB) and Medium Energy Line Break (MELB) barrier between the mechanical penetration room and the service water penetration room. A HELB/MELB event occurring in a room with its barrier door open could adversely affect equipment in an adjacent room. Consequently, a HELB/MELB event could have rendered equipment in the adjacent room inoperable. "At 1005, station maintenance was able to successfully close and latch the door restoring the barrier. "This event is being reported under the requirements of 10CFR50.72(b)(3)(ii)(B) as, 'the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' An ENS notification is required if an unanalyzed condition occurred within 3 years of the date of discovery even if the event is not on-going at the time of discovery." The licensee notified Lower Alloways Creek Township and the NRC Resident Inspector. * * * RETRACTION FROM JOHN OSBORNE TO JOHN SHOEMAKER AT 1545 EST ON 12/12/16 * * * "The purpose of this notification is to retract event report number 52294 made on 10/11/2016 at 1648 (ET). Previously PSEG reported that Salem Unit 1 was determined to be in an unanalyzed condition due to being unable to close the Unit 1 Inboard Service Water Penetration Area Water Tight Door. The watertight door was reported to serve as a High Energy Line Break (HELB) and Medium Energy Line Break (MELB) barrier between the mechanical penetration room and the service water penetration room. "Subsequent review identified that the condition did not meet the reporting criterion. "Engineering evaluation determined that the service water penetration room had been previously evaluated for the impact due to a HELB event occurring in the adjacent mechanical penetration area with the watertight door open and that the event would not impact the operability of the service system. "Engineering evaluation also determined that the Salem Unit 1 Design Basis does not require analysis of a MELB event occurring in the service water penetration room. This is due to the timing of the Unit 1 operating license issue date. At the time of the issuance of the Unit 1 operating license analysis of a MELB event was not required. Therefore an unanalyzed condition for a MELB event did not exist. "Additionally while the door was difficult to close, it was able to be closed and dogged in a reasonable time interval (27 minutes), therefore, any potential internal flooding which would have been detected immediately by the attendant with required actions taken to close the door and isolate the leak rapidly. "Therefore PSEG is retracting the notification made under 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector was notified of this retraction by the licensee." Notified R1DO (Schroeder). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-10-11
52293 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-10-10 10:32 | 2016-10-10 14:07 | 2016-10-10 | OFFSITE NOTIFICATION DUE TO A SPILL OF A REPORTABLE QUANTITY OF HYDRAULIC OIL ONSITE "At 1032 [CDT] on October 10, 2016, it was determined that a spill of hydraulic oil that occurred earlier in the morning on the site was of sufficient quantity (approximately 60 gallons) to warrant a notification to the Louisiana Department of Environmental Quality. This report will be made within 24 hours of the determination. The spill was the result of a hydraulic system failure on a truck that was on site to pick up non-radioactive trash. The truck was on company property but outside the Security Owner Controlled Area (SOCA). There are no radiological or off-site impacts arising from this event. The spill did not reach surface water and is now contained. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(xi) as a condition requiring the notification to State environmental authorities. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-10-10
52292 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-10-09 02:54 | 2016-10-09 06:09 | 2016-10-09 | AUTOMATIC REACTOR TRIP FOLLOWING MAIN GENERATOR DIFFERENTIAL LOCKOUT TURBINE TRIP "Surry Unit 2 reactor automatically tripped at 0254 hours on 10/09/2016, due to a Main Generator Differential Lockout Turbine Trip. The cause of the generator differential lockout is under investigation at this time. Reactor Coolant System temperature is currently being maintained at 547 degrees Fahrenheit on the main steam dump valves. All three Auxiliary Feedwater Pumps automatically started as designed on Low-Low Steam Generator Water Level following the trip. Auxiliary feedwater pumps have since been secured and Main Feedwater is in use. "All systems operated as required. The source range nuclear instruments had to be manually reinstated following the reactor trip due to indications of undercompensation on Intermediate Range Nuclear Instrument channel N-36. Off site power remains available. There is no impact on Surry Unit 1. "This notification is being made pursuant to 10CFR50.72(b)(2)(iv)(B) for 4-hour notification of Reactor Protection System activation and 10CFR50.72(b)(3)(iv)(A) for 8-hour notification of automatic actuation of the Auxiliary Feedwater System. "The NRC Resident Inspector has been notified and is responding to the site. "There were no radiation releases, personnel injuries, or contamination events due to this event." All control rods fully inserted. Secondary reliefs lifted and reseated as expected following a reactor trip from 100% power. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-10-09
52291 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-10-08 13:28 | 2016-10-08 14:23 | 2016-10-10 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER "Loss of all offsite power capability, Table S-5, to 6.9kV emergency buses 1A-SA and 1B-SB for greater than or equal to 15 minutes." At 1328 EDT, while shutdown in Mode 4 (Hot Shutdown), Harris declared an Unusual Event due to a loss of offsite power. Following the loss of offsite power (LOOP), the Emergency Diesel Generators started and loaded onto their respective emergency buses. The reactor remains stable and shutdown in Mode 4. The licensee is currently investigating the cause of the LOOP and the emergency buses will continue to be powered by the EDGs until the licensee has determined the cause for the LOOP. Offsite power is currently available into the switchyard. The licensee notified the state government, the local government, and the NRC Resident Inspector. Notified DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM RALPH DOWNEY TO DONALD NORWOOD AT 1658 EDT ON 10/8/16 * * * "The cause [of the LOOP] is not known. Duke Energy Control Center has evaluated the grid and is comfortable with Harris connecting emergency buses back to the grid. Harris Plant is evaluating restoration. Faults were validated on the 115kV Cape Fear North and South supply lines into the Harris switchyard. "This notification also addresses various valid actuations of safety systems, including the Emergency Diesel Generators, as well as, potential loss of Emergency Assessment Capabilities due to the LOOP impacting Emergency Planning equipment." The licensee notified the NRC Resident Inspector. Notified R2DO (Bonser), IRD (Grant), and NRR EO (King). * * * UPDATE FROM RALPH DOWNEY TO DONALD NORWOOD AT 1755 EDT ON 10/8/16 * * * The cause of the LOOP has been determined to be a momentary electricity loss on the 115kV Cape Fear North and South supply lines into the Harris switchyard. "This event notification also addresses the loss of safety function of the offsite power system which occurred as a result of grid perturbations." The licensee notified the NRC Resident Inspector. Notified R2DO (Bonser), IRD (Grant), and NRR EO (King). * * * UPDATE FROM DUSTIN MARTIN TO DONALD NORWOOD AT 2055 EDT ON 10/8/16 * * * Based on the grid being stable and the 115kV Cape Fear North and South lines being available, the licensee terminated the Unusual Event at 2049 EDT on 10/8/16. The licensee notified the NRC Resident Inspector. Notified R2DO (Bonser), IRD (Grant), and NRR EO (King). Notified DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM SARAH McDANIEL TO DONALD NORWOOD AT 1330 EDT ON 10/9/16 * * * 10 CFR 50.72(b)(2)(XI) - OFFSITE NOTIFICATION "At approximately 1305 EDT on October 9, 2016, Duke Energy personnel notified the North Carolina Department of Environment and Natural Resources of a spill of untreated sanitary wastewater. During a significant rainfall event associated with Hurricane Matthew, wastewater was released from the overflow of a lift station that did not function as a result of a power outage. The untreated sanitary wastewater entered the plant's storm drain system. The release has been stopped and the lift station power is restored. An investigation is in progress to further determine the cause and additional corrective actions. "There is no impact to public health and safety or the environment due to this incident. "This event is reportable per 10 CFR 50.72(b)(2)(xi), an event related to protection of the environment for which a notification to other government agencies has been made. "The NRC Resident Inspector has been notified." Notified R2DO (Bonser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE | ACCIDENT MITIGATION | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) | 50.72(b)(3)(v)(D) | 0 | 2016-10-08
52290 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2016-10-08 13:17 | 2016-10-08 13:44 | 2016-10-09 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER "UE SU1.1 declared due to momentary loss of power from the qualified off-site source. Both Emergency Diesel Generators started and loaded to supply power to both of the Emergency Buses. "'A' Service Water Pump did not start on Blackout sequencer. Sufficient Service Water flow is available from the other three operating pumps. All other systems operated as designed." At 1304 EDT Robinson Unit 2 experienced a momentary grid voltage drop that lowered the 4kV bus voltage and initiated an automatic reactor trip. All rods inserted and decay heat is being removed by steam generator PORVs. In response to the reduced bus voltage, the Emergency Diesel Generators (EDGs) automatically started and loaded onto the emergency busses. At 1317 EDT, the licensee declared an Unusual Event (EAL SU1.1) due to the loss of offsite power. The licensee is currently investigating the cause of the grid voltage instability. The emergency busses will continue to be powered by the EDGs until the licensee has determined the cause for the voltage drop. All offsite power sources and all equipment is available. The licensee has notified the state government and Darlington County. The NRC Resident Inspector has been notified. Notified DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM ALEX CURLINGTON TO DANIEL MILLS AT 1658 EDT on 10/08/16 * * * "At 1303 EDT on 10/08/2016, a reactor trip occurred. The cause was under voltage to the plant 4kV buses due to an offsite grid disturbance. The cause of the disturbance is under investigation. Following the reactor trip, the Auxiliary Feedwater System actuated as expected on low steam generator level. At the time of the trip, the plant was in Mode 1. Currently, the Plant is in Mode 3. The current RCS Temperature is 550 degrees F (Average), and the Steam Generator Levels are in the range of 42 to 53% (normal range) with levels controlled by the Auxiliary Feedwater System. Decay heat removal is being controlled by the steam generator PORVs. 'A' Service Water Pump did not start on Blackout sequencer. Sufficient Service Water flow is available from the other three operating service water pumps 'B', 'C', and 'D'. All other systems operated as designed. "Due to the Automatic Actuation of the Reactor Protection System, this event is being reported as a 4-hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B). Due to the valid actuation of Auxiliary Feedwater System, this event is also being reported as an 8-hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A)(B)(6). At no time during this occurrence was the public or plant staff at risk as a result of this event. "The Resident Inspector has been notified." * * * UPDATE FROM BOBBY STUCKEY TO DANIEL MILLS AT 2347 EDT on 10/08/16 * * * "At 2323 [EDT] Emergency Bus E-2 powered from off-site power." The NRC Resident Inspector will be notified. Notified R2DO (Bonser), IRD (Grant), NRR EO (Miller). * * * UPDATE FROM BOBBY STUCKEY TO JOHN SHOEMAKER AT 0028 EDT ON 10/09/16 * * * "At 0011 [EDT] Robinson Nuclear Plant has terminated the Unusual Event." Basis for the Unusual Event termination was restoration of power to Emergency Bus E-2 from off-site power. The licensee has notified the NRC Resident Inspector. Notified R2DO (Bonser), NRR EO (Miller), IRD (Grant), DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM GEORGE CURTIS TO JOHN SHOEMAKER AT 0253 EDT ON 10/09/16 * * * "At approximately 2323 EDT on 10/08/2016, an auto-start of the Auxiliary Feedwater (AFW) Motor-Driven pumps occurred during the transfer of Emergency Bus power from the 'B' Emergency Diesel Generator (EDG) to offsite power. AFW system auto-start logic associated with Main Feed Pump (MFP) breakers being open is defeated when the EDG output breaker is closed. As such, when the EDG output breaker was opened during the power transfer while the MFP breakers were open, the auto-start logic was thereby met causing the AFW auto-start. "Due to the valid actuation of the AFW System, this event is being reported as an 8-hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A). At no time did this occurrence pose undue risk to the health and safety of the public. "The NRC Senior Resident Inspector has been notified of this event." H.B. Robinson Unit 2 was in Mode 3 during this event. Notified R2DO (Bonser). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-10-08
52289 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-10-08 01:50 | 2016-10-08 05:47 | 2016-10-08 | UNPLANNED REACTOR TRIP AND SAFETY INJECTION DUE TO TURBINE CONTROL VALVE TRANSIENT "On October 8, 2016, while reducing power for a planned refueling outage, the unit was taken offline by opening the main generator output breakers. With the reactor at approximately 7 percent power in MODE 1, an unplanned actuation of the reactor protection system occurred. At 0150 [EDT], an unexpected steam valve transient occurred while main turbine valve control was being transferred from throttle valve to governor valves during main turbine overspeed testing. This resulted in an automatic low steamline pressure Safety Injection and Reactor Trip. All safety systems functioned as expected. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load reactor coolant system (RCS) temperature and pressure following the reactor trip, with decay heat being removed using steam generator power operated relief valves. Steam generator water levels are being maintained using auxiliary feedwater. All emergency core cooling system (ECCS) equipment is available. "The cause of the steam valve transient is under investigation. This condition is being reported as an ECCS discharge to RCS, an unplanned reactor protection system actuation, and a specified system actuation in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B). and 10 CFR 50.72(b)(3)(iv)(A). "This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." The Safety Injection occurred for approximately 6 minutes and Pressurizer level increased to approximately 71%. The Main Steam Isolation Valves closed as a result of the Safety Injection and Decay Heat is being removed using the Steam Generator Atmospheric Relief Valves. There is no known primary to secondary leakage. | 0 | 0 | 0 | 7 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-10-08
52288 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2016-10-07 16:20 | 2016-10-07 18:28 | 2016-10-07 | FITNESS FOR DUTY REPORT - DISCOVERY OF PROHIBITED SUBSTANCE "This report is being made pursuant to 10 CFR 26.719(b). "At 1620 EDT today, a prohibited substance [marijuana] was identified inside the protected area. The substance was obviously very old, so is surmised to be from a preoperational period. "The item [a small remainder, or butt, of a marijuana joint] is currently under the control of the site security department and will be turned over to local law enforcement for disposal. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 26.719 |  |  |  | 0 | 2016-10-07
52287 | -1 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2016-10-07 | 2016-10-07 16:58 | 2016-10-13 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED RADIOACTIVE GAUGE The following information was obtained from the state of Mississippi via email: "Licensee's RSO [Radiation Safety Officer] notified DRH [Mississippi Division of Radiation Health] on 10/7/2016 that a Berthold Model LB7440D level/density gauge had a stuck shutter. The shutter malfunction was discovered while performing a calibration for the gauge. The gauge is located twelve (12) foot off the ground and away from any personnel. The licensee contacted Berthold for repair of the shutter mechanism on 10/7/2016." The gauge serial number is 69-0545, containing 30 mCi of Cs-137; source model P2623-100; source serial number 2762; last swipe tested on 9/30/16. The source was manufactured in September of 1992. Mississippi Report number: MS-16005 * * * RETRACTION FROM JAYSON MOAK TO STEVEN VITTO ON 10/13/2016 AT 1204 EDT * * * The following information was obtained from the state of Mississippi via email: "On 10/10/2016, the licensee reported that the gauge shutter was not stuck. Licensee stated the shutter was hard to open and close. The gauge service company was called in to replace the shutter mechanism on the gauge to prevent a possible stuck shutter." Notified R4DO (Gepford) and NMSS Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2016-10-17
52286 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-10-06 | 2016-10-07 13:09 | 2016-10-07 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received via facsimile: "On October 6, 2016, at approximately 0200 EDT, a loader backed over the licensee's portable gauge during work in Fairfax County, Virginia. The gauge was a Troxler Model 3400, s/n 31366, with an 8 millicurie cesium-137 source, s/n 750-6052, and a 40 millicurie americium-241:Be source, s/n 47-28023. The operator secured the gauge and cordoned the accident area. Radiation surveys by the licensee's Radiation Safety Officer confirmed the sources were in their shielded positions and that no contamination resulted from the accident. The damaged gauge has been shipped to a licensed service provider for repair." Virginia Event Report ID No.: VA-16-014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-10-17
52285 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-10-06 15:48 | 2016-10-06 16:33 | 2016-10-06 | SAFEGUARDS REPORT - DISCOVERY OF SPECIAL NUCLEAR MATERIAL STORED OUTSIDE OF THE MATERIAL ACCESS AREA The licensee discovered special nuclear material outside of the material access area. The material has been properly secured. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-10-06
52284 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2014-09-26 | 2016-10-06 16:06 | 2016-10-06 | PRESCRIBED DOSAGE INCORRECTLY WRITTEN "This is a notification, pursuant to 10 CFR 35.3045(a)(1), of a medical event that occurred on September 26, 2014, at the VA Palo Alto Health Care System, Palo Alto, California. "On September 26, 2014, a dosage of about 110 microCuries (æCi) of radium-223 dichloride was administered to a patient. The prescribed dosage on the written directive was incorrectly written by the authorized user physician as 113.8 milliCuries (mCi). The basis for identifying this as a medical event is that the administered dosage differed from the prescribed dosage, as written on the written directive, by more than 20 percent. The authorized user physician was interviewed and stated that the intended prescription for injection was 113.8 æCi of radium-223 dichloride. Another authorized user physician, the Chief, Nuclear Medicine Service, who administered the dosage, confirmed that this was an appropriate dosage for this patient. No harm to the patient is expected since the treatment was successfully performed with the administration of a dosage nearly identical to the intended dosage. The medical event was discovered October 5, 2016, during an unannounced inspection of this facility conducted by the National Health Physics Program (NHPP). The permittee is required to submit a written report to NHPP within 15 days of discovery. NHPP will, in turn submit the report to NRC per regulatory requirements. The NHPP inspection is ongoing to determine overall compliance with 10 CFR 35.40, 10 CFR 35.41, and 10 CFR 35.3045." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-10-14
52283 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2016-10-06 14:15 | 2016-10-06 14:26 | 2016-10-07 | SAFEGUARDS REPORT - SECURITY MEASURES MODIFIED DUE TO HURRICANE MATTHEW "Upon receipt of tropical force winds, specific security measures have been temporarily suspended or modified in accordance with 10 CFR 73.55(p)(1)(ii) due to imminent severe/hazardous weather conditions associated with Hurricane Matthew." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ANDY TEREZAKIS TO DONALD NORWOOD AT 1352 EDT ON 10/7/2016 * * * "This notification is to advise the NRCOC that severe weather conditions have subsided and all suspended or modified security measures have been restored as required by 10 CFR 73.55(p)(2)." The licensee notified the NRC Resident Inspector. Notified R2DO (Bonser) and via E-mail the 73.71 Safeguards Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Hot Standby |  | Refueling | Hot Standby |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-10-06
52282 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-10-05 16:00 | 2016-10-06 13:21 | 2016-10-06 | AGREEMENT STATE REPORT: STOLEN NUCLEAR DENSITY GAUGE The following was received from the State of California via email: "At 1600 [PDT] on October 5, 2016, the RSO [Radiation Safety Officer] for C. Y. Geotech Inc. reported to RHB [Radiation Health Branch] that one of their nuclear density gauges (CPN model MC-1DR-P; #MD90404953 containing 10 mCi of Cs-137 and 50 mCi of Am-241/Be) had been stolen from a temporary job site. RHB informed the RSO to file a police report and place a notice into the local newspaper offering a reward for information leading to the safe return of the gauge. The RSO will require the gauge operator to make a report of exactly what happened and specifically if the Cs-137 handle was locked in the safe mode. "The gauge was not discovered missing until the morning of October 5, 2016 and the operator returned to look for the gauge. The RSO posted a lost gauge sign at the job site notifying personnel of the loss of the gauge and C. Y. Geotech's contact information for its safe return. "On Oct. 4, 2016, around 1300 [PDT], the gauge operator had finished his work with the CPN gauge and was completing paperwork at his vehicle. He forgot about the gauge and failed to secure it into the transport case before departing the job site. He believes he left the gauge on the curbside. The gauge had been recently leak tested in May 2016." 5010 Number: 100416 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-10-14
52281 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-10-04 | 2016-10-06 13:24 | 2016-10-06 | AGREEMENT STATE REPORT - STUCK CLOSED SHUTTER ON FIXED RADIOACTIVE GAUGE The following information was obtained from the State of Illinois via email: "On October 4, [2016], the licensee's radiation safety officer contacted the Agency [Illinois Emergency Management Agency] to report a defective fixed gauge. While performing routine operational checks of fixed gauges at the site, the shutter on a device appears to have become disconnected from its handle and will not operate properly. It was determined from radiation measurements that the shutter is currently in the 'closed' position. Radiation levels are less than 2 mR/h surrounding the device and it is in an area that is routinely inaccessible. The gauge is mounted on a reaction process vessel and is subject to the ambient weather conditions with no prior operational issues for 27 years until now. Arrangements are pending with a manufacturer's representative to investigate the matter and repair/replace the device. "Source/Radioactive Material: SEALED SOURCE GAUGE Radionuclide: Cs-137, 0.064 Ci, 2.368 GBq Manufacturer: VEGA AMERICAS, INC. Model Number: A-2102 Serial Number: M3107 IAEA Category: 4" Illinois Report No.: IL16009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-10-14
52280 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2016-10-04 22:53 | 2016-10-04 23:18 | 2016-10-07 | UNUSUAL EVENT DUE TO A HURRICANE WARNING "A Hurricane Warning is in effect for St. Lucie County including the Plant Site. A Hurricane Warning was issued by the National Weather Service at 2250 [EDT]. St. Lucie Nuclear Power Plant entered an Unusual Event Classification for the Hurricane Warning. State and local officials have been notified by the licensee. "The NRC Resident Inspector was notified of this by the licensee. "This report is submitted in accordance with 10CFR50.72(a)(1)(i) due to the Notice of Unusual Event and 10CFR50.72(b)(2)(xi) due to the Offsite Notification." Notified DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). * * * UPDATE FROM ANDY TEREZAKIS TO VINCE KLCO ON 10/7/16 AT 1112 EDT * * * "The Hurricane Warning was downgraded to a Tropical Storm Warning by the National Weather Service for St. Lucie County including the Plant Site. At time 1044 [EDT] on 10/7/16, St. Lucie Nuclear Power Plant has terminated from the Unusual Event Classification." The licensee notified the NRC Resident Inspector, State and local authorities. Notified R2 (Jones) NRR EO (King), IRD (Grant), R2DO (Bonser), DHS SWO, FEMA OPS Center, FEMA National Watch (email only), DHS NICC, Nuclear SSA (email only). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2016-10-04
52279 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-10-04 15:30 | 2016-10-04 18:16 | 2016-10-04 | COOPER NUCLEAR STATION LOSS OF TONE ALERT RADIOS "At 1530 CDT on I0/4/20l6, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in the event of an emergency condition. This is considered to be a major loss of the Public Prompt Notification System capability, and is reportable under 10CFR50.72(b)(3)(xiii). "Nemaha County, NE, Richardson County, NE, and Atchison County, MO authorities within the 10 mile EPZ [Emergency Planning Zone] were notified by Cooper Nuclear Station of the condition and the effect on the tone alert radios. The first county was notified at 1540 CDT and the last was notified at 1550 CDT. A backup notification method will be utilized. Notification of other government agencies makes this condition reportable under 10CFR50.72(b)(2)(xi). "Estimated return to service time is unknown. The cause of failure is unknown. "The NRC Senior Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2016-10-04
52278 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-10-04 09:10 | 2016-10-04 16:57 | 2016-10-19 | AGREEMENT STATE REPORT - POTENTIAL EXCESSIVE EXPOSURE OF RADIOGRAPHER The following report was received from the Louisiana Department of Environmental Quality via facsimile: "On October 4, 2016, at approximately 0910 CDT, the Radiation Safety Office of CB&I Walker LA, LLC notified LDEQ [Louisiana Department of Environmental Quality] of a potential excessive exposure to a radiographer working in the licensee's permanent radiographic facility. After making a proper radiation survey, the above radiographer moved his exposure device with 100.6 Ci of Ir-192 and then noticed the rear fitting had come loose from the crank-out control, which showed approximately three inches of drive cable exposed. The radiographer pushed the fitting forward and tightened it back into the connector of the crank-out control. The licensee believes that at this point the source was inadvertently pushed out of the front of the camera approximately three to four inches. The radiographer did not notice this at the time and continued setting up for the next exposure. "Upon exiting the shooting cell, the radiographer observed the red revolving warning light. The radiographer also observed sounding of the shooting cell alarm upon his exiting the cell. The radiographer stated that he was inside the shooting cell for a period of between five to seven minutes. The radiographer read his direct reading pocket dosimeter and observed an off-scale reading. The radiographer immediately notified his RSO [Radiation Safety Officer], who immediately sent his whole body badge in for rush processing subsequent to the dosimetry processor being notified by the RSO. The RSO used the radiographer's information of occupancy time and his statement that he was standing while the exposure device was stationed on the shooting cell floor throughout the incident to estimate the radiographer's whole body exposure of between 5 and 25 R. The radiographer was then immediately sent to a local medical laboratory to have his blood drawn. There is no potential for off-site exposure. The licensee was advised by this inspector to contact the REAC/TS facility for guidance on blood chromosomal analysis. This is a preliminary report in an on-going investigation." Louisiana Event Report ID No.: LA160010 * * * UPDATE AT 1648 EDT ON 10/19/16 FROM RUSSELL S. CLARK TO S. SANDIN * * * The State of Louisiana corrected the licensee to show CB & I Walker, LLC. Notified R4DO (Kramer), NMSS Events Notification, NMSS (Collins) and NSIR (Milligan) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [10 empty] | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-10-12
52277 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-09-29 14:45 | 2016-10-04 10:58 | 2016-10-04 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION EVENT The following was received by fax from the Tennessee Division of Radiological Health: "While emptying a 55 gallon drum of lead for reuse into a B-12 box, unknown and unsuspected contamination levels in bottom of drum resulted in a contamination of the area to max levels of 2,000,000 dpm/100 cm2 beta. Contamination levels in drum determined to be 2,000,000 dpm/100 cm2 max post event. Pre job surveys identified no elevated contamination levels in top of drum. Isotope and activity are unknown at this time. Isotope is a weak pure beta emitter. Analysis is underway for isotopic determination. [Three] 3 persons with skin contamination were deconned. Bioassays are underway for internal dose assessment. Area is being recovered, however, not within 24 hours resulting in reporting of event. Dose assessments are forthcoming." State Event Report ID No.: TN-16-138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-10-12
52276 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2016-10-03 10:08 | 2016-10-03 16:49 | 2016-10-03 | LOSS OF SECONDARY CONTAINMENT VACUUM FOR FOUR MINUTES "On October 3, 2016, at 1008 PDT a Reactor Building Exhaust Valve (REA-V-1) unexpectedly closed, which caused the Technical Specification (TS) for secondary containment pressure boundary to not be met. The duration of time that the secondary containment TS was not met was approximately 4 minutes. "Secondary containment differential pressure was restored within TS requirement of greater than or equal to 0.25 inches of vacuum water gauge at approximately 1012 PDT by manually starting Standby Gas Treatment (SGT) system (SYS) A. The cause of the REA-V-1 closure is currently under investigation. "This condition is being reported under 10CFR50.72(b)(3)(v)(C) for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-10-03
52275 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-10-02 16:00 | 2016-10-03 00:02 | 2016-10-03 | LIQUID PENETRATION EXAMINATION RESULTS IN INDICATIONS ON REACTOR VESSEL HEAD PENETRATION "On October 2, 2016 during the Braidwood Station Unit Refueling outage (A1R19), an in-service Liquid Penetration examination was performed on the previously repaired control rod drive mechanism (CRDM) penetration 69. During the examination on the weld build up for CRDM penetration 69, two indications were discovered. A 7/32 inch rounded indication was discovered located at 359 degrees on the reactor head portion of the weld buildup, and it is 4 inches from the transition of the head to penetration. A 1/4 inch rounded indication was also discovered located at 200 degrees at the transition of the head to penetration. 0 degrees is located at the outermost portion of the penetration on the flange side. The transition is the point where the vertical portion of the penetration meets the horizontal area of the reactor head. "Rounded indications that exceed 3/16 inch are rejectable per ASME Code Case N-729-1. "This is reportable pursuant to 10CFR50.72(b)(3)(ii)(A), 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded' since the as found indication did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-10-03
52274 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2016-10-01 05:12 | 2016-10-01 09:42 | 2016-10-01 | AUTOMATIC REACTOR TRIP DUE TO INADVERTENT CLOSURE OF MAIN STEAM ISOLATION VALVE "At 0512 [CDT] on October 1, 2016, Farley Nuclear Plant Unit 1 automatically tripped from 99 percent reactor power due to the inadvertent closure of a main steam isolation valve (MSIV). The closure of the MSIV caused a turbine trip resulting in an automatic reactor trip. Concurrent with the reactor trip, a safety injection (SI) occurred. The plant is stable in Mode 3 (Hot Standby) and auxiliary feedwater (AFW) autostarted as expected. The cause of MSIV closure and SI actuation is under investigation. "Cooldown will continue to Mode 5 (Cold Shutdown) as planned for entry into a scheduled refueling outage. Restart is not planned until the completion of the refueling outage. Unit 2 was not affected. "The NRC Resident Inspector has been notified." The MSIVs are open with the steam generators discharging steam to the main condenser using the turbine bypass valves. SI was from high head injection which has been secured. | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-10-01
52273 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-09-29 19:00 | 2016-09-30 16:19 | 2016-10-03 | FITNESS FOR DUTY REPORT - LICENSED OPERATOR CONFIRMED POSITIVE FOR ALCOHOL A licensed operator had a confirmed positive for alcohol on a random fitness for duty test. The employee's access to the plant has been terminated. The licensee has informed the NRC Resident Inspector. | 81 | 100 | 100 | 81 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2016-09-30
52272 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-09-27 15:40 | 2016-09-30 14:30 | 2016-09-30 | LOST STATIC ELIMINATOR The following report was received via fax: "Telephonics Corporation reported that an NRD static eliminator, Model P-2031, S/N A2GM255 containing 20 milliCuries of Polonium-210 was missing. Loss of the device was discovered while double checking an inventory sheet provided by NRD for purchases and returned devices. Telephonics has been instructed to submit a written report within 30 days of the telephone report, requesting a description of the circumstances under which loss or theft of the NRD device occurred and what actions will be taken to recover the missing device and what measures will be taken to prevent further loss of licensed material." Event Report ID: NYDOH-NY-16-06 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-10-10
52271 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2016-09-29 21:00 | 2016-09-30 04:01 | 2016-09-30 | UNISOLABLE LEAK ON DECAY HEAT REMOVAL PIPING DUE TO WELD FAILURE ON A 1" COMMON PIPE "At 2100 CDT on 09/29/16, while in Mode 6, both trains of Decay Heat (Residual Heat Removal) were declared inoperable due to a cracked weld on a 1" common pipe. The leak developed in a USAS B31.7, Class1 pipe at a weld upstream of pressure indication isolation valve DH-1037. The leak is not isolable from the common 8-inch Decay Heat piping and encompasses approximately 1/3 [one third] of the pipe circumference. "At the time of discovery, the unit was in Lowered Inventory with both Loops of Decay Heat in service. Subsequently, one train of Decay Heat has been secured to reduce the likelihood of crack propagation. One Train of Decay Heat remains in service providing the function of removing Decay Heat and the other train is readily available. The leakage impacts redundant equipment required to fulfill a safety function. In the current condition, both trains are required to be operable to meet Technical Specification LCO 3.9.5, Decay Heat Removal (DHR) and Coolant Circulation-Low water Level. "This condition is reportable per 10 CFR 50.72(b)(3)(v)(B) for any event or condition that results in a loss of Safety Function associated with the Decay Heat System (Residual Heat Removal System). "The licensee has notified the NRC Resident Inspector." The leak is approximately 0.25 gallons per minute and pipe pressure is 140 psi. Compensatory measures are in place and include an individual posted to watch the pipe in case plugging is necessary. Repairs to the pipe will be completed once pipe is able to be drained. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2016-09-30
52270 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-09-29 17:00 | 2016-09-30 02:11 | 2016-09-30 | TSC VENTILATION INDICATION ISSUE IDENTIFIED FOLLOWING SURVEILLANCE TESTING "On 9/29/2016 at 1700 [EDT] the MCR [Main Control Room] was notified of a potential Technical Support Center [TSC] emergency ventilation indication issue following surveillance testing. At 2350 troubleshooting revealed a blown control power fuse which affected functionality of TSC HVAC emergency mode. The system was restored to operable as of 0043 on 9/30/16. "If an emergency had been declared and TSC activation was required, the TSC would have been staffed and activated unless the TSC became uninhabitable due to ambient temperatures, radiological or other conditions. The Station Emergency Director would assess habitability in accordance with station procedures. If TSC relocation becomes necessary, then personnel would be directed as required until such time that the TSC emergency ventilation system was returned to service." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-09-30
52269 | 0 | WECTEC LLC |  |  |  |  | 2016-09-28 | 2016-09-28 14:57 | 2017-03-15 | PART 21 REPORT REGARDING PIPE SPOOL FLANGES FOR VOGTLE UNIT 3 The following was excerpted from an email received from WECTEC LLC: "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "The two flanges identified with deviations on Passive Core Cooling System pipe spools for the Vogtle Unit 3 AP1000r project had incorrect raised-face dimensions. This appears to have been caused by the two flanges being transposed due to an inadvertent fabrication error that occurred at the pipe spool supplier's facilities (CB&I Laurens). The error was subsequently discovered after delivery to the fabrication facility (Aecon Industrial). "This error resulted in conditions where the two flanged connections would not have met the design configuration. If the flanged connections had been assembled in the delivered configuration, it is not known if system integrity and operability would have been maintained during operation. The incorrect configuration could have also led to subsequent failure after installation and operation. Hydrostatic testing of these connections is required, but had not yet been performed because the condition was discovered prior to the assembly and testing of these portions of the system. The condition is being corrected prior to the performance of that hydrostatic testing, therefore it is not known if the flanges in the incorrect configuration would have been able to pass hydrostatic testing. "Due to the possibility that system integrity and operability could have been impacted by the use of the incorrect flanges, it has been conservatively concluded that this condition should be reported under 10 CFR Part 21. This conservative conclusion is based on the possibility that the Passive Core Cooling System could have been adversely impacted by the identified deviations, if the deviations had been left uncorrected. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. ". . . The flange configuration was corrected and the Q223 Mechanical Module was delivered to the Vogtle Unit 3 site on September 23, 2016. A corrective action report has been entered into the Westinghouse/WECTEC system to further evaluate the circumstances that led to the identified deviations." * * * UPDATE FROM DAVID DURHAM TO HOWIE CROUCH VIA EMAIL AT 1535 EDT ON 3/15/17 * * * WECTEC LLC determined that additional pipe spools with incorrect flange configurations were fabricated for V.C. Summer Unit 3 and Vogtle Unit 4. None of the pipe spools were installed in either of the facilities. Corrective actions have been taken to prevent re-occurrence. Notified R2DO (Ehrhardt) and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-09-28
52268 | 0 | MONSANTO |  |  |  |  | 2016-09-27 14:00 | 2016-09-28 13:51 | 2016-09-30 | SAFETY EQUIPMENT POTENTIALLY FAILS TO FUNCTION Maintenance was being performed on a Berthold moisture analyzer in a coke bin vessel because a moisture tube inside of the vessel was damaged. Two maintenance technicians took the source holder off the vessel and then proceeded to work on the vessel. The source holder was placed nearby the work area and the source was not able to be fully retracted back into the gauge during the maintenance evolution. Maintenance then re-mounted the source holder back onto the vessel. The licensee contacted the manufacturer in order to investigate the maintenance evolution and assist estimating dosage to the two technicians. The licensee contacted Region 4 (Janine Katanic). The licensee investigation continues. * * * UPDATE AT 1115 EDT ON 09/30/16 FROM DAVE MATYUS TO S. SANDIN * * * On 09/29/16 Berthold Technologies was onsite to assist in the investigation. A leak test was performed and the contractors involved were interviewed. The information will be provided to the Berthold RSO in order to estimate the dose received. NRC R4 (Dykert) was also present to observe the investigation. The licensee does not anticipate receiving the results until next week. Notified R4DO (Groom) and NMSS Events Notification by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-10-06
52267 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2016-09-28 07:45 | 2016-09-28 09:46 | 2016-09-28 | UNIT 2 SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO INOPERABLE DIESEL GENERATOR "On September 16, 2016, at 0036 [CDT], during a 24-hour Technical Specification (TS) endurance run, the Arkansas Nuclear One, Unit 2 (ANO-2) red train Emergency Diesel Generator (EDG) became inoperable when its inboard generator bearing failed. ANO-2 TS 3.8.1.1, 'AC Sources', requires an inoperable EDG to be restored to service within 14 days or actions to place the unit in a shutdown condition initiated. "It has been determined that repair options cannot be completed within the Allowed Outage Time (AOT) due to unforeseen circumstances which evolved during recovery efforts. At 0745 [CDT], ANO-2 initiated plant shutdown due to the inability to restore the red train EDG. ANO-2 will be shutdown and cooled down to Mode 5." The licensee informed the NRC Resident Inspectors. | 0 | 65 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-09-28
52266 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-09-27 16:44 | 2016-09-27 22:27 | 2016-11-23 | SECONDARY CONTAINMENT LEAKAGE EXCEEDING REQUIREMENTS "On September 27, 2016 at 1644 [EDT], damaged ductwork was identified in the secondary containment boundary associated with reactor building zone 3 (Units 1 and 2) recirculation plenum. The size of the hole in the secondary containment boundary was determined to be 22.5 square inches. Due to exceeding allowable total leakage in the current secondary containment isolation configuration, a violation of SR 3.6.4.1.5 [occurred]. Action to establish a tested configuration with sufficient inleakage margin to restore compliance with SR 3.6.4.1.5 was completed September 27, 2016 at 2115 hrs. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022, Rev 3, Section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1444 EST ON 11/23/2016 FROM MANU SIVARAMAN TO MARK ABRAMOVITZ * * * "Following the 8-hour 10 CFR 50.72 notification made on September 27, 2016 (EN 52266), further engineering analysis determined that the as-found tear in the Zone 3 ductwork did not impact the ability of Secondary Containment to perform its safety function and that Secondary Containment was not inoperable as a result of the condition. To support the determination, a drawdown test was conducted in a limiting configuration (i.e. least inleakage margin). No substantial change in drawdown testing results were observed over the last three tests. These tests spanned over seven years. Additionally, repairs were promptly made to the affected area. As a result, this event notification is being retracted as it is not reportable pursuant to 10 CFR 50.72(b)(3)(v)(C)." The licensee notified the NRC Resident Inspector. Notified the R1DO (Dwyer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-09-27
52265 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2016-09-26 | 2016-09-27 12:52 | 2016-09-27 | KENTUCKY AGREEMENT STATE REPORT - STOLEN THEN RECOVERED MOISTURE DENSITY GAUGE The following information was obtained from the Commonwealth of Kentucky via facsimile: "KY RHB [Kentucky Department for Public Health & Safety, Radiation Health Branch] was notified on September 27th, 2016 by the Radiation Safety Officer of Gem Engineering, Inc. that a theft of material had occurred sometime during the night of September 26th unto the morning of the 27th. A Troxler 3411 series moisture density gauge that was stored in the back of a vehicle was stolen along with the vehicle. The licensee reported the theft to the police on the morning of the 27th when it was noticed by the authorized user that the vehicle was missing. The device has been recovered by police and returned to the licensee. The individuals responsible have been apprehended as well. The State will continue to keep NRC informed of the status of our investigation." The Troxler contains a nominal 9 mCi of Cs-137 and 44 mCi of AmBe. KY Event Report ID No.: KY160008 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2016-10-05
52264 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2016-09-26 18:45 | 2016-09-27 00:20 | 2016-09-27 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On 9/26/16 at approximately 1845 EDT, investigation of an identified water leak on one of the two Unit 3 HPCI turbine exhaust drains to the drain pot determined that there was through wall leakage of approximately 2 drops per minute. Operations promptly declared the HPCI system inoperable and entered Technical Specification 3.5.1 Condition C for HPCI being inoperable. Other standby systems (Reactor Core Isolation Cooling and low pressure emergency core cooling systems) are operable. "HPCI is a single train system. Therefore, per NUREG-1022, this condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system required to mitigate the consequences of a design event. "This condition has been entered into the corrective action program (IR 2720241). Investigation of the exact flaw location is in progress so that repairs can be made. "The NRC resident has been informed of this notification." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-09-27
52263 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2016-09-22 | 2016-09-26 | 2017-12-12 | AGREEMENT STATE REPORT - SHUTTER ON DENSITY GAUGE The following information was provided by the State of Arkansas via email: "On September 23, 2016 at 1300 CDT, the licensee contacted the Department [Arkansas Department of Health] reporting that during operations on September 22, 2016, the licensee discovered that the shutter on a Vega Americas Model BAL density gauge would not open. The gauge contains 300 milliCuries of Krypton-85. "The gauge was replaced with a spare gauge and has been placed in a secure storage area and radiation exposure is maintained at less than 2 mR/hr. "The licensee is contacting the manufacturer to request repair or disposal of the gauge. "In accordance with RH-1502.f.2 (10 CFR 30.50(b)(2)) the malfunctioning shutter is reportable within 24 hours. "The State of Arkansas is awaiting a written report from the licensee. The State's event number is AR-2016-011." * * * UPDATE AT 1021 EST ON 12/12/2017 FROM STEVE MACK TO MARK ABRAMOVITZ * * * The following update was received via e-mail: "The licensee stated that the shutter solenoid was 24 years old and had been in continuous service over that time. The shutter failed to open on September 22, 2016 and the gauge was removed from service and placed in storage. On November 28, 2017, the manufacturer took possession of the gauge for disposal. "The Department considers this event to be CLOSED." Notified the R4DO (Deese) and NMSS Events Notification (E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2016-10-04
52262 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-09-25 09:15 | 2016-09-25 12:58 | 2016-09-25 | COOPER NUCLEAR STATION LOSS OF TONE ALERT RADIOS "At 0915 CDT on 9/25/2016, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in the event of an emergency condition. This is considered to be a major loss of the public prompt notification system capability and is reportable under 10 CFR 50.72(b)(3)(xiii). "Nemaha, NE, Richardson, NE, and Atchison, MO county authorities within the 10 mile EPZ were notified by Cooper Nuclear Station of the condition and the effect on the tone alert radios and will utilize the backup notification method making this condition reportable under 10 CFR 50.72(b)(2)(xi) for notification of other government agencies. "Estimated return to service time is unknown. The cause of the failure is unknown. "The NRC Senior Resident Inspector has been notified of this condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2016-09-25
52261 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-09-25 01:03 | 2016-09-25 04:23 | 2016-09-25 | ACTUATION OF GROUP 1 ISOLATION SIGNAL "At 0103 CDT a Group 1 Isolation signal was received on Main Steam Line (MSL) A High Flow while attempting to un-isolate MSL A. "During plant cooldown for refueling outage, all inboard MSIV's were closed to minimize steam flow to control cooldown rate. With all inboard MSIV's closed and all outboard MSIV's open, MSL drains in-service, and reactor pressure at approximately 330 psig, an attempt was made to un-isolate MSL A by opening A inboard MSIV. This resulted in a MSL high flow signal on MSL A as the valve was being opened, resulting in a Group I Isolation and closure of all MSIV's and MSL Drain Valves. Pressure was equalized to less than 200 psid across MSIV A prior to attempting to open the valve in accordance with plant procedures. All valves actuated as expected and the cause of the event is under investigation. There are no indications of a leak. The Group I Isolation has been reset." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-09-25
52260 | -1 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-09-20 20:47 | 2016-09-23 20:10 | 2016-11-18 | STEAM LINE PIPE WHIP RESTRAINT COUPLING SLEEVE FOUND NOT ENGAGED "On 9/20/2016, a coupling sleeve on a pipe whip restraint located on the 119 foot elevation of the turbine building associated with Unit 2 main steam line 4 was found to be not engaged. As a result of the detached coupling, the restraint was not capable of performing its restraint function for a postulated pipe whip event on the main steam line. The coupling was reconnected on 9/20/2016, restoring its functionality. An extent of condition walkdown was subsequently performed for the other Unit 1 and Unit 2 steam line restraints and no similar issues were identified. "This concern did not result in any adverse effect on the radiological health and safety of the public. "The purpose of this whip restraint is to restrain the steam line for a postulated loss at the G-line anchor (east side of Turbine Building above the 104 foot elevation). The restraint protects the floor slab at the 104 foot elevation, which extends over the Unit 2 component cooling water heat exchangers. "With the detached coupling, equipment in the area may have been vulnerable to damage if a pipe whip event occurred. Further analysis is needed to conclude whether the heat exchangers and other equipment would have remained protected in such an event and whether this would have significantly affected the designed plant response to a pipe event. "Based on the need for further analysis, this event is being reported as an unanalyzed condition that may have significantly degraded plant safety in accordance with 10 CFR 50.72(b)(3)(ii)(B). "The NRC Senior Resident Inspector was notified." * * * RETRACTION FROM FRANK LEE TO DONALD NORWOOD AT 1953 EST ON 11/18/2016 * * * "The purpose of this notification is to retract a previous report made on EN #52260, reported 9/23/2016. NRC notification was initially made as a result of a condition that required further analysis to determine whether the condition would have significantly degraded plant safety in accordance with 10 CFR 50.72(b)(3)(ii)(B). "Further analysis of the condition concluded that PG&E Design Class I equipment located inside the Turbine Building would have remained undamaged and capable of performing their safety functions. The Turbine Building would not have experienced failure of major structural elements or adverse impact to the overall building stability. "Therefore, the coupling sleeve on a pipe whip restraint located on the 119 foot elevation of the Turbine Building associated with Unit 2 main steam line 4 that was found to be not engaged did not constitute an unanalyzed condition that may have significantly degraded plant safety in accordance with 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." Notified R4DO (Azua) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-09-23
52259 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-09-22 | 2016-09-23 17:57 | 2016-09-23 | AGREEMENT STATE REPORT - PATIENT UNDERDOSAGE OF YTTRIUM-90 The following report was received from the California Department of Public Health via email: "On September 23, 2016, the Radiation Safety Officer of the University of California, Los Angeles (UCLA), contacted the Brea office of the Radiologic Health Branch to report a medical event. "A patient was treated with Nordion TheraSpheres containing yttrium-90 (Y-90) on September 22, 2016. The prescribed dose was 100 gray (Gy) to the left lobe of the liver. Upon completing the dose assessment after the treatment, it was discovered that only approximately 50 percent of the intended dosage of Y-90 was delivered to the patient (left lobe of the liver). The remainder of the Y-90 dosage appears to have remained in the delivery system, primarily in the system waste container. The licensee performed surveys to confirm that the areas surrounding the delivery system and patient were not contaminated. "The patient has been notified, and the licensee is investigating to determine the cause of the event." CA 5010 Number: 092316 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-10-03
52258 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-09-21 | 2016-09-23 12:29 | 2016-09-23 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received by the State of Illinois via email: "The Radiation Safety Officer (RSO) at Equistar Chemical notified the Agency [Illinois Emergency Management Agency] via email that while performing routine shutter tests of fixed gauges at their Morris, IL location, it became known that for one of the gauges, a shutter was stuck in the 'open' position. The affected Ohmart Vega model SH-F2 gauge contains 300 milliCi of Cs-137 and is mounted on a reactor vessel within a secure area at the plant. The associated process line for the vessel does not have any maintenance scheduled to occur until next year, therefore, no entry into the vessel should be necessary and the gauge is expected to remain in the 'on' position due to operational need. The gauge manufacturer has been contacted and advised of the situation. Equistar and Vega Americans are currently attempting to schedule a field service engineer to come on site to investigate the matter and make necessary repairs/replacement. The licensee has previous experience with events of this type due to the large number of devices in use and the stressful environment that exists at this site. The licensee is prepared to respond to any further deterioration that, although not likely, may occur. Plant personnel have been advised of the matter and the process line supervisors have been instructed to contact the RSO should any abnormal events associated with the reactor processes becomes known. No on-site investigation is planned by the Agency at this time." Illinois Item Number: IL16008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-10-03
52257 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2016-04-20 | 2016-09-22 17:56 | 2016-09-22 | AGREEMENT STATE REPORT - NUCLEAR GAUGE STUCK SHUTTER The following report was received from the North Carolina Department of Health and Human Services via email: "The Agency [North Carolina Department of Health and Human Services] was notified of service contract reciprocity 0003-R Ronan to arrive at NC [North Carolina] Licensee Chemours in Fayetteville on 9/21/16. Ronan to work on a Ronan SA-1, Gauge SN:M1713, Cs-137, 20 mCi (decayed to approx 10 mCi) with a stuck shutter. "[The North Carolina Radioactive Materials Branch Health Physicist] went to Chemours 0109-7 to conduct a reciprocity inspection, and conducted an investigation regarding [Chemours] failing to notify the Agency [North Carolina Department of Health and Human Services] of a stuck shutter on a radioactive gauge. The stuck shutter was identified during scheduled leak test and shutter testing by Chemours workers in June, 2016. This was confirmed with the RSO [Radiation Safety Officer]. "Shutter was in the open position. No members of the public or workers were at risk of exposure (due to facility design). "Source: Cs-137 Activity: 0.020 Ci Manufacturer: Ronan Engineering Model Number: sa-1 Serial Number: m1713 "NC Item Number: NC160030" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2016-09-30
52256 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-09-21 | 2016-09-22 11:21 | 2016-09-22 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following was received from the Commonwealth of Pennsylvania via fax: "A Troxler nuclear gauge was hit by an asphalt road compactor while on a temporary job site. Impact rendered the gauge unusable. The area was secured and the licensee Radiation Safety Officer determined that the gauge was not leaking. The gauge was then secured for shipment back to Troxler for possible repair or replacement. There was no exposure to workers or the public. "The gauge has been secured for transport to Troxler. The Department [PA Department Bureau of Radiation Protection] was also onsite to verify radiation measurements and perform a reactive inspection. More information will be provided when available. "Radionuclides: Cs-137 / Am-241:Be Manufacturer: Troxler Model: 3430 Serial Number: 21864 Activity: 9 mCi (Cs-137) / 44 mCi (Am-241) "Event Report ID No: PA 160026" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-09-30
52255 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-09-22 03:20 | 2016-09-22 10:58 | 2016-09-22 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "On September 22, 2016, at 0320 [EDT], Secondary Containment Zone 2 (Unit 2 Reactor Building) differential pressure lowered to 0.15 [inch] WG due to a stuck non-safety related exhaust damper on the in service Zone 2 exhaust fan. Required differential pressure per SR 3.6.4.1.1 could not be maintained. Zone 2 differential pressure recovered to greater than 0.25 [inch] WG on September 22, 2016 at 0342 [EDT] by starting the standby Zone 2 exhaust fan. Zone 1 (Unit 1 Reactor Building) and Zone 3 (Unit 1&2 Reactor Buildings) ventilation remained in service and stable. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The Licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-09-22
52254 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-09-21 02:21 | 2016-09-21 09:20 | 2016-11-18 | DISCHARGE CHECK VALVE FAILURE TO SEAT CAUSES TRIP OF COMPONENT COOLING WATER PUMP "At 0221 [EDT] on 9/21/16, Operators at Unit 2 Secured the 21 Component Cooling Water (CCW) Pump for planned maintenance while 22 and 23 CCW pumps were in operation. When the 21 pump was secured, the discharge check valve failed to seat. This resulted in a low system pressure and reverse rotation of the 21 CCW Pump due to the discharge of the 22 and 23 CCW pumps to a common header. When system pressure dropped below 107 psig the 21 CCW pump received an auto start signal. Due to the reverse rotation, the 21 CCW pump tripped on overcurrent. Reactor Operators directed Field Operators to manually shut the 21 CCW Pump discharge valve. The 21 CCW pump Discharge Valve was closed at 0223 [EDT]. This action was successful in stopping the reverse flow and restoring system parameters. During this two minute period the CCW system was declared inoperable and LCO 3.0.3 was entered. Unit 2 exited LCO 3.0.3 at 0223 [EDT] after observing system pressure and flow return to normal. The declaration of inoperability on the CCW system is considered a Loss of Safety Function for purposes of reporting under 50.72(b)(3)(v)(D). There was no reduction in power while in LCO 3.0.3 and no other issues arose." The Licensee notified the NRC Resident Inspector. The Licensee notified the Public Service Commission. * * * RETRACTION FROM CHARLES ROKES TO HOWIE CROUCH AT 1108 EST ON 11/18/16 * * * "Indian Point Unit 2 is retracting the 8-hour non-emergency notification made on September 21, 2016, at 0920 EDT (EN#52254). The notification on September 21, 2016, reported a safety system functional failure (SSFF) as a result of declaring the Component Cooling Water System (CCW) inoperable due to failure of the 21 CCW pump discharge check valve (761C) to close. This condition was discovered during planned maintenance after securing the 21 CCW pump while the 22 and 23 CCW pumps were in operation. When the 21 CCW pump was secured, the discharge check valve failed to seat. This resulted in a low system pressure and reverse rotation of the 21 CCW pump due to the discharge of the 22 and 23 CCW pumps to a common header. Condition was reported as a safety system functional failure (SSFF) under 10 CFR 50.72(b)(3)(v)(D). "After further investigation of the condition, a revised calculation was prepared for the CCW hydraulic model which is used to analyze CCW system performance for normal and DBA [design basis accident] modes of operation and documented in a calculation. The new calculation included the as-found condition of the 21 CCW pump discharge check valve failure to seat. Based on the results of the new calculation, the CCW system is capable of performing its design basis heat removal function during a design basis accident. Calculated flow rates with CCW aligned for Post-LOCA recirculation demonstrates that with failed open check valve 761C, the 22 CCW pump and 23 CCW pump have adequate NPSH margin, are operating below analyzed pump run out and deliver flow to the CCW system that is significantly greater than the flow required for post-LOCA recirculation. Therefore the CCW system was operable and a safety system functional failure (SSFF) did not occur as a result of failed open 21 CCW pump discharge check valve 761C." The licensee has notified the NRC Resident Inspector and will be notifying the New York Public Service Commission. Notified R1DO (Bickett). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-09-21
52253 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-09-19 15:50 | 2016-09-19 21:40 | 2017-03-23 | CONTROL ROOM EMERGENCY VENTILATION CHARCOAL NOT MEETING ACCEPTANCE CRITERIA "At 1550 [CDT] on September 19, 2016, Dresden received the Methyl Iodide Penetration test results for the Control Room Emergency Ventilation (CREVS) charcoal. The test results did not meet technical specification acceptance criteria. This results in the inoperability of CREVS. CREVS is a single train system and therefore is reportable per 10CFR50.72(b)(3)(v)(D). The Air Filtration Unit (AFU) is required to operate during a design basis accident to maintain Main Control Room habitability. This places unit 2 and unit 3 in a 7 day LCORA [Limiting Condition of Operation Required Action] per Tech Spec 3.7.4 Required Action A.1." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1635 EDT ON 03/23/17 FROM HENRY WATERS TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this notification is to retract ENS notification 52253 made on September 19th, 2016, for Dresden Nuclear Power Station. After further evaluation and testing, it has been determined that the Control Room Emergency Ventilation System (CREVS) charcoal would have fulfilled its safety function given the Methyl Iodide Penetration test results. The initial tests were performed with a 2 inch bed depth due to a difference in batches used in each charcoal filter, but testing at a 4 inch bed depth is the correct testing methodology for Dresden's configuration. At a 4 inch bed depth, the test results met the Technical Specification acceptance criteria with significant margin. Therefore, this event does not meet the criteria of 10 CFR 50.72(b)(3)(v)(D) and the ENS report is being retracted." The NRC Resident Inspector has been notified. Notified R3DO (Orlikowski). | 0 | 100 | 87 | 0 | 100 | 87 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-09-19
52252 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2016-09-19 12:30 | 2016-09-19 18:17 | 2016-09-19 | OFFSITE NOTIFICATION TO SAN DIEGO REGIONAL WATER QUALITY CONTROL BOARD "At 1230 [PDT] on 9/19/16, SONGS [San Onofre Nuclear Generating Station] made an offsite notification to the San Diego Regional Water Quality Control Board in regards to an oily waste water release to the environment in excess of allowable limits. "On 9/15/16, the Unit 3 oily waste sump overflowed. An estimated 1500 gallons was released to the intake which is pumped to the outfall. A sample was taken during the end of the overflow; no visual indication of oil and grease was noted. The sample analysis completed on 9/19/16 indicated a result that exceeded SONGS' NPDES [National Pollutant Discharge Elimination System] instantaneous maximum limit of 20 ppm; results were 34.4 ppm." The licensee will inform NRC Region IV staff. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-09-19
52251 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2016-09-19 06:00 | 2016-09-19 14:30 | 2016-09-19 | UF6 SCRUBBER EXHAUST SYSTEM NOT OPERATING AS REQUIRED "EVENT DESCRIPTION: It was determined at approximately 6 AM today (Eastern) that an Item Relied on for Safety (IROFS) associated with a Fuel Manufacturing Operation (FMO) exhaust system was not operating as required. An FMO scrubber exhaust system blower was determined to be not operating and resulted in a failure to meet performance requirements. "The safety function of the scrubber exhaust system is to limit the release of uranium hexafluoride (UF6) and its byproducts to the environment in the unlikely event of an accidental airborne release in a process area. Other upstream controls remained available and reliable and prevented significant quantities of UF6 and its byproducts from being released into the scrubber exhaust system. There was no release of material and at no time was an unsafe condition present. "The Dry Conversion Process has been shutdown. An investigation is continuing which will provide additional corrective actions and extent of condition. "While this did not result in an unsafe condition, the event is being reported pursuant with the reporting requirements of 10CFR70 Appendix A (b)(2) within 24 hours of discovery. "SAFETY SIGNIFICANCE OF EVENT: At no time was an unsafe condition present "SAFETY EQUIPMENT STATUS: The Dry Conversion Process (DCP) was shutdown. "STATUS OF CORRECTIVE ACTIONS: Additional corrective actions, extent of condition, and extent of cause are being investigated. There was no offsite release of UF6 as a result of the IROF failure. The licensee will inform the State of North Carolina, New Hanover County and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2016-09-19
52250 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-09-07 | 2016-09-19 13:33 | 2016-09-19 | AGREEMENT STATE REPORT - RADIOACTIVE SEED PACKAGE FAILED TO REACH FINAL DESTINATION The following information was received from the State of Illinois by email: "The radiation safety officer, (RSO) at GE Healthcare, called to advise that a package of I-125 seeds which had been given to [a common carrier] to deliver to Sydney, Australia had not reached their destination by the desired date. The package is 6x6x6 inches box of 'excepted package - limited quantity' which contains 10 sealed sources with a total activity of 6.8 milliCi (actual) in a box calibrated for Saturday, 8/27/16, at noon. The RSO has been in touch with [common carrier] since September 3, 2016 when GE's customer service became concerned while routinely performing package tracking. [The common carrier] last had positive tracking for this package in San Francisco, CA on August 28th. [The common carrier] is still conducting visual surveys in San Francisco and Sydney in an attempt to locate the box and has no evidence to indicate the materials have been delivered to an outside entity. Surveys conducted at O'Hare Airport in Chicago where the package was initially offered for transport were negative. [The common carrier] reports that it is still conducting searches and has put a 'world wide tracer' into effect to locate the material as it still believes it is within their delivery system." Illinois Event: IL 16007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-09-27
52249 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-09-16 | 2016-09-19 13:19 | 2016-09-19 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILURE The following information was received from the State of Illinois by email: "The licensee's radiation safety officer contacted the Agency [Illinois Emergency Management Agency] on September 16, 2016 to advise that while a licensed contractor was conducting calibration of sensors, the shutter failed on an older KayRay fixed gauge. The gauge is mounted on a process line in a remote location that is normally not accessible. Workers were putting the gauge back into service when it appeared that a shear pin broke on the lever that controls the shutter position. The area was cleared of workers and radiation measurements performed. Those measurements showed the shutter was not completely closed. No exposures to workers were noted. Arrangements are being made with a specifically licensed contractor to make repairs to the gauge as soon as can be managed." Fixed gauge is manufactured by KayRay/Sensall; Model 7063P; Serial Number S98L2001; Sealed Source Gauge (.331 Ci of Cs-137). Illinois Event: IL 16006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-09-27
52248 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-09-19 12:05 | 2016-09-19 12:21 | 2016-09-19 | 10 CFR PART 21 NOTIFICATION - JOSLYN CLARK OVERLOAD HEATER ELEMENT PART NUMBER 2455 "This is a non-emergency facsimile notification required by 10 CPR 21.21(d)(3)(i). A written notification in accordance with 10 CFR 21.21(d)(3)(ii) will be provided within 30 days. "Duke Energy McGuire Nuclear Station (McGuire) has determined there is evidence of a departure from technical requirements, a Deviation, associated with Joslyn Clark overload heater element Part Number (PIN) 2455. This part was procured in accordance with the Duke Energy Commercial Grade Program (CGP) and dedicated for use in safety related applications. Three of 18 overload heater elements, purchased as a lot, had insufficient top weld material. One failed in-service during a post maintenance test, the second and third failed during a visual and mechanical inspection. An extent of condition review inspected over 500 similar Joslyn Clark overload heater elements. No other inventory was found with a top weld issue. "These overload heater elements are used in motor starters for the Emergency Diesel Generator (EDG) ventilation fans. This condition was discovered during post maintenance testing of the 2A EDG on July 27, 2016. None of the suspect overload heater elements were installed in Operable EDG ventilation fan motor starters. The dedicated overload heater elements, from this lot, were not transferred or sold to any third party customers. Specialty Product Technologies, manufacturer of the Joslyn Clark overload heater elements, has been notified of the deviation and is investigating their welding process. "The Evaluation of the deviation determined that a Substantial Safety Hazard would have been created if the overload heater elements were installed and left uncorrected. "The NRC Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2016-09-19
52247 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2016-09-16 16:57 | 2016-09-16 23:35 | 2016-11-09 | ESSENTIAL BUSSES NOT ALIGNED TO POWER TRANSFORMERS DURING PLANT STARTUP "At 1657 Eastern Daylight Time (EDT) the plant entered Mode 4 (from Mode 5), and subsequently, at 1710 EDT, it was discovered that 480V AC essential busses E1 and F1 were being supplied from the shutdown operations transformers. The essential busses E1 and F1 are required to be aligned to the power operations transformers in Mode 4 for operability in accordance with TS 3.8.9. "With both E1 and F1 essential busses aligned to the shutdown operations transformers with the plant in Mode 4, both trains of the essential electrical power distribution system were inoperable, resulting in a loss of safety function. At 1733 EDT both E1 and F1 essential busses were aligned to the power operations transformers as required by TS 3.8.9. "This issue is being reported as a loss of safety function of the essential electrical busses. "The NRC Resident Inspector has been notified of the event." * * * RETRACTION AT 1315 EST ON 11/09/2016 FROM ANDY MILLER TO JEFF HERRERA * * * "Engineering reviewed the actual conditions during the approximate 36 minutes the 480V AC essential busses were being supplied from the shutdown operations transformers. Grid voltages were higher than assumed minimum voltages, and electrical loading during Mode 4 conditions were reduced from expected full power operation loading. As a result, Engineering determined that all equipment remained capable of performing its required functions while connected to the shutdown operations transformers. "Because the equipment remained capable of satisfying the requirements for Operability, no condition existed that could have prevented the fulfillment of a safety function. Therefore, no loss of safety function existed for the 480V AC essential buses, and the notification made per 10 CFR 50.72(b)(3)(v)(A-D) by the Davis-Besse Nuclear Power Station on 9/16/2016 (EN# 52247) is being retracted. "The NRC Resident Inspector has been briefed on the evaluation results and informed of this retraction." Notified the R3DO (Jeffers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2016-09-16
52246 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2016-09-15 14:00 | 2016-09-16 16:26 | 2016-09-16 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK IN OPEN POSITION The following information was received by the Commonwealth of Massachusetts: "The licensee called the Agency [Massachusetts Radiation Control Program] to report a fixed fill level gauge stuck in the open position. The gauge is a Berthold LB7400 Series gauge, Model LB7440, and contains a 150 mCi Cs-137 source [S/N:1476]. "The gauge is mounted to a liquid holding tank which was emptied and was scheduled for routine cleaning. Before cleaning of the tank could begin, the gauge shutter was attempted to be put into the closed position. When attempting to close the shutter, the handle broke off and left the gauge stuck in the open position. Cleaning was not able to be performed and no one was able to enter the tank. The gauge remains in the installed position and is in an inaccessible area with safety controls in place to prevent access. The manufacturer was contacted and will be servicing the gauge 09/27/16 thru 09/28/16 by either repairing or replacing the shielding as necessary. "The Agency continues to investigate and considers this event to be open. "Manufacturer of gauge notified and will respond to assess the device; repair or replacement as necessary." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2016-09-26
52245 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-09-16 09:13 | 2016-09-16 12:17 | 2016-09-16 | HYDRAULIC FLUID (FISH OIL) SPILL "At 0858 [EDT] on September 16th, 2016, approximately 3 ounces of hydraulic fluid (fish oil) was spilled in front of the Unit Two Circulating Water System (CWS) Intake trash racks at the Salem Generating Station. The spill of hydraulic fluid (fish oil) was caused by a leak from the crane used to rake debris from the Unit Two trash racks. The crane was stopped and the leak terminated at the time of discovery. "Nuclear Environmental Affairs Department determined a 4 hr report to the NRC, under RAL 11.8.2.a, was warranted due to the 15 minute notification to the New Jersey Department of Environmental Protection at 0913 [EDT]. Nuclear Environmental Affairs Department intends to retract the report to the New Jersey Department of Environmental Protection based on the fluid remained within the Circulating Water System (CWS) Intake Structure." The licensee has notified the New Jersey Department of Environmental Protection, the NRC Resident Inspector, and will notify the Lower Alloways Creek Township. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-09-16
52244 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-09-15 15:40 | 2016-09-16 00:14 | 2016-11-14 | POTENTIAL DEGRADATION OF ECCS PUMP PRESSURE INDICATORS "During a review of commercial grade dedication records for a Unit 1 [Emergency Core Cooling System ECCS] Centrifugal Charging Pump discharge pressure gauge, it was identified that the process side of the diaphragm seal utilizes a Teflon (PTFE) gasket. Further review found Teflon (PTFE) to be installed in the pressure gauge seal assembly for all four of the Centrifugal Charging Pumps and both of the Positive Displacement Charging Pumps on Units 1 and 2. "Teflon (PTFE) is a restricted material normally prohibited from use in contact with reactor coolant or in radiation environments. Teflon (PTFE) is not radiation tolerant and significantly degrades in a radiation environment. The Teflon (PTFE) used in these pressure gauges could fail during a LOCA [Loss of Coolant Accident] which could cause the [ECCS] Centrifugal Charging Pumps and both of the Positive Displacement Charging Pumps on Units 1 and 2 to be inoperable, and exceed system leakage limits. Excessive leakage from systems which would contain post-LOCA recirculation fluid would challenge onsite and offsite dose estimates and in-plant post-accident accessibility. This represents an unanalyzed condition. "Currently, the pressure gauges for all four of the [ECCS] Centrifugal Charging Pumps and both of the Positive Displacement Charging Pumps on Units 1 and 2 have been isolated until this issue can be further evaluated. Luminant Power believes that the Teflon (PTFE) has existed in the pressure gauges since initial plant licensing. Luminant Power is currently investigating the extent of the condition and repair techniques. "The NRC Resident Inspector has been notified." * * * RETRACTION AT 1634 EST ON 11/14/16 FROM DANNY BRADFORD TO JEFF HERRERA * * * "On 09/16/2016, Comanche Peak reported an ENS Report (no. 52244) related to the identification of teflon-containing pressure-seal assemblies installed on the suction and discharge sides of the centrifugal charging pumps and on the suction side of the positive displacement pump. The technical concern was the potential for the teflon-containing assemblies to leak if subjected to post-LOCA recirculation fluid and associated radiation levels. "Subsequent investigations by Engineering have determined: (1) the centrifugal charging pumps were operable for all postulated non-LOCA design bases events which required their operation and (2) for postulated LOCA scenarios which would involve radiation levels sufficient as to call into question the ability of the teflon-containing assemblies to maintain system pressure boundary, the ECCS function would be fulfilled in the event one or all of the charging pumps had to be removed from service (due to system leakage) and limiting (control room) doses would have remained below applicable regulatory limits. "Based on the above, the condition described in ENS report no. 52244 is not considered to be an un-analyzed condition as described in10 CFR 50.72(b)(3)(ii)(B), nor is it considered to be a condition which could have led to a potential uncontrolled radiation release per 10CFR 50.72(b)(3)(v)(C), nor is it considered to be a condition which could have prevented fulfillment of a safety function under 10 CFR 50.72.(b)(3)(v)(D). "The NRC Resident Inspector has been notified." Notified the R4DO (Azua). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2016-09-16
52243 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-09-12 15:00 | 2016-09-15 16:10 | 2016-09-15 | AGREEMENT STATE REPORT - DAMAGED PORTABLE GAUGE The following information was received from the State of Oklahoma via email: "On 9/12/2016 at approximately 1500 CDT, a portable gauge was struck by a private vehicle at a jobsite. This is preliminary information, and [The Oklahoma Environmental Agency] has not received a full report yet from the licensee. There does not appear to be any leakage or exposures from this incident. Licensee: Oklahoma Department of Transportation (OK-15794-01) Reported by: Larry Hawkins, ODOT RSO Device: Troxler Model 4640 Isotope: 8 mCi Cesium-137 Location: Intersection of Highways 183 & 152, Cordell, OK "Description: Licensee reports that worker was using the gauge to take surface density measurements on an asphalt highway. The gauge shield was open, but the rod was not extended. A vehicle travelling approximately 25 mph ignored warnings, 'straddled' the highway centerline, and struck the gauge. The driver who struck the gauge left the scene after discovering what had happened. "The licensee reports that there was no contamination found on the highway or the gauge. The gauge sustained damage to the case and circuit board. The licensee stated that debris was cleared from the shield area and then the shield was closed. The gauge was shipped to Troxler. The licensee is waiting on leak test results, and will submit an incident report to the DEQ [Oklahoma Department of Environmental Quality]." NMED Item Number: OK160005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-09-23
52242 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2016-09-15 09:08 | 2016-09-15 11:18 | 2016-09-15 | POTENTIAL UNANALYZED CONDITION BASED ON IDENTIFIED NON-CONFORMING CONDITIONS "During performance of an extent of condition evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornadoes, Arkansas Nuclear One, Unit 1, identified non-conforming conditions in the plant design such that specific TS equipment on Unit 1 is considered not [to] be adequately protected from tornado missiles. The reportable condition is postulated by tornado missiles entering vital switchgear rooms 99 and 100 and striking vital switchgears in the rooms. A tornado could generate multiple missiles capable of striking the Unit 1 vital switchgear and rendering both safety related AC electrical trains inoperable. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) safe shutdown capability, (B) residual heat removal capability, or (D) accident mitigation. "This condition was identified as part of an on-going extent of condition review of potential tornado missile related site impacts. Licensee Event Report (LER) 50-313/2016-002-00 was recently submitted addressing previously identified tornado missile vulnerabilities at the Unit 1 plant. "Enforcement discretion per Enforcement Guidance Memorandum EGM 15-002 has been implemented and required actions taken. Corrective actions will be documented in a follow-on licensee event report. "The licensee has notified the NRC Resident Inspector." | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2016-09-15
52241 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-09-15 | 2016-09-15 11:19 | 2016-09-15 | AGREEMENT STATE REPORT - LOST TRITIUM SIGN The following report was received from the State of Texas via email: "On September 15, 2016, the Agency [Texas Department of State Health Services] was notified by an Operation Specialist (OS) at the Chevron corporate office in Houston, Texas, that during an inventory of a storage room in their building, an 'EXIT' sign containing 7 curies of tritium was not located. The sign was manufactured by Isolite in October of 2002. The OS stated they have search the building and interview all their personnel who had accessed the room since the last inventory. He stated that it is possible that the sign may have been disposed of in their waste, but he does not believe that happened. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: I-9429 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [10 empty] | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-09-23
52240 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2016-09-13 20:30 | 2016-09-14 01:02 | 2016-09-14 | STEAM PROPAGATION BARRIER DOOR FOUND OPEN "During routine operator rounds at 2030 EDT, a steam propagation barrier door (SPBD) was discovered propped open for maintenance activities without appropriate station controls. This condition was in existence from approximately 1720 EDT to 2042 EDT when the SPBD was restored to its normal configuration. Throughout the approximate 3 hours and 22 minutes, when the SPBD was propped open, both trains of chill water were rendered non-functional due to a potential high energy line break. This subsequently rendered both trains of high-head safety injection inoperable, which placed the plant in Technical Specification 3.0.3. This condition was corrected prior to commencing a Technical Specification 3.0.3 plant shutdown. This condition is reportable under 10 CFR 50.72(b)(3)(v) as any event or condition that at the time of discovery could have prevented the fulfillment of a safety function. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-09-14
52239 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-09-13 17:30 | 2016-09-13 22:28 | 2016-12-22 | UNANALYZED CONDITION INVOLVING STATION SERVICE WATER TRAINS "Based on a walk down in the Service Water Intake Structure (SWIS) with the NRC Resident [Inspector], it was observed that a vertical section of 4 inch Fire Protection pipe that provides a normally pressurized source of fire water supply to the overhead sprinkler system in the SWIS is not Moderate Energy Line Break (MELB) shielded similar to the horizontal segment of the same line near the ceiling. In the event of a MELB crack along any portion of the unshielded pipe, the MELB has a potential impact to the function of any one of the 4 Service Water pumps. Only one train at a time would be affected during the event. This is due to the physical characteristics of the postulated MELB and the configuration/separation relative to the source line and target pumps and/or associated Motor Control Centers (MCCs) that support pump operation. "Since the Service Water trains have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, if the MELB were to have occurred during these times and affected the opposite train, then two Service Water trains could have been inoperable and this represents an unanalyzed condition. At the time of discovery, all four Service Water trains were operable, therefore, this condition is not reportable as a loss of safety function per 10 CFR 50.72(b)(3)(vi). "Currently, Service Water Train B on each Unit has been declared inoperable per Technical Specification (TS) 3.7.8. This condition will be corrected within the 72-hour Completion Time of TS 3.7.8. "Currently, Emergency Diesel Generator B on each Unit has been declared inoperable per Technical Specification (TS) 3.8.1. This condition will be corrected within the 72-hour Completion Time of TS 3.8.1. "The NRC Resident Inspector was informed." * * * UPDATE ON 10/6/2016 AT 2009 EDT FROM DAMON SCHROEDER TO DONG PARK * * * "This is an update to Event Number 52239. On September 13, 2016 at 2228 EDT, Comanche Peak reported an unanalyzed condition involving station service water trains per 10CFR50.72(b)(3)(ii)(B). Specifically, the reported condition involved a vertical section of 4 inch Fire Protection pipe in the SWIS that was not adequately shielded for a Moderate Energy Line Break (MELB). In the event of a MELB crack along any portion of the unshielded pipe, the MELB had a potential impact to the function of any one of the 4 Service Water pumps. "On October 6, 2016 at 1410 hours CDT, a section of eyewash station pipe in the Unit 2 Safeguards Building was identified as a result of extent of condition walkdowns that was not adequately shielded for a Moderate Energy Line Break (MELB). In the event of a MELB crack along any portion of this unshielded pipe, the MELB had the potential to impact Unit 2 Train B 480V Motor Control Center (MCC) 2EB2-1. This MCC provides power to Unit 2 Train B Emergency Core Cooling, Battery Charger, Containment Spray, and Containment Isolation Valve equipment. The affected eyewash station pipe was isolated shortly after it was discovered to not be adequately shielded for a MELB. "Since 480V MCC 2EB1-1 and the Unit 2 Train A Emergency Core Cooling, Battery Charger, Containment Spray, and Containment Isolation Valve equipment trains have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, if the MELB were to have occurred during these times and affected the opposite train, then 2EB1-1, 2EB2-1 and both trains of the Unit 2 Emergency Core Cooling, Battery Charger, Containment Spray, and Containment Isolation Valve equipment could have been inoperable and this represents an unanalyzed condition. At the time of discovery, 2EB1-1 and the Unit 2 Train A Emergency Core Cooling, Battery Charger, Containment Spray, and Containment Isolation Valve equipment was operable. Therefore, this condition is not reportable as a loss of safety function per 10 CFR 50.72(b)(3)(vi). "The NRC Resident Inspector was informed." Notified R4DO (Werner). * * * UPDATE FROM ROBERT DANIELS TO DONALD NORWOOD AT 2233 EDT ON 10/10/2016 * * * "This is an additional update to Event Number 52239. On September 13, 2016 at 2228 EDT and again on October 6, 2016 at 2009 EDT, Comanche Peak reported unanalyzed conditions involving Station Service Water System trains and a 480V Motor Control Center (MCC) per 10 CFR 50.72(b)(3)(ii)(B). The reported conditions involved sections of piping that were not adequately shielded for a Moderate Energy Line Break (MELB). In the event of a MELB crack along any portion of the unshielded piping, the MELB had a potential impact to the function of safety-related equipment in the Service Water Intake Structure and the Unit 2 Safeguards Building. "On October 10, 2016 at 1708 CDT, as a result of ongoing extent of condition walkdowns, a section of fire protection pipe in the Unit 1 Safeguards Building was identified that was not adequately shielded for a MELB. In the event of a MELB crack along any portion of this unshielded pipe, the MELB had the potential to impact Unit 1 Train B Switchgear 1EA2, Unit 1 Train B 480V MCC 1EB4-2, and Unit 1 Train B Distribution Panel 1ED2-2. Only one of these power supplies at a time would be affected. 1EA2 provides 6.9KV electrical power to various Unit 1 Train B safety-related pumps, panels, sequencer, and transformers. 1EB4-2 provides 480V electrical power to various Unit 1 Train B safety-related pumps, valves, fans, panels, and transformers. 1ED2-2 provides 125VDC electrical power to EDG 1-02 channel 1 starting circuit. The affected fire protection pipe was isolated shortly after it was discovered to not be adequately shielded for a MELB. "Since Unit 1 Train A Switchgear 1EA1, Unit 1 Train A 480V MCC 1EB3-2, and Unit 1 Train A Distribution Panel 1ED1-2 have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, if the MELB were to have occurred during these times and affected the opposite train, then both trains of Unit 1 6.9KV power (1EA2 and 1EA1), both trains of Unit 1 480V power (1EB4-2 and 1EB3-2), and both trains of Unit 1 125VDC power (1ED2-2 and 1ED1-2) along with the safety-related equipment they supply could potentially have been inoperable and this represents an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B). At the time of discovery, none of the affected Train A equipment was inoperable. Therefore, this condition is not reportable as a loss of safety function per 10 CFR 50.72(b)(3)(v). "The NRC Resident Inspector was informed." Notified R4DO (Werner). * * * UPDATE FROM HUNTER SCHILL TO DONALD NORWOOD AT 1457 EST ON 11/7/2016 * * * "This is an update to Event Number 52239. On November 17, 2016 at 0730 CST, during ongoing extent of condition walkdowns in the Boric Acid Transfer Pump Area of the Auxiliary Building, two pressurized fire protection pipe segments were identified that did not contain Moderate Energy Line Break (MELB) shielding. In the event of a MELB crack along the unshielded portion of these pipes, the MELB had the potential to impact Unit 1 Train B 480V Motor Control Center (MCC) 1 EB4-1. This MCC provides 480V electrical power to various Unit 1 Train B safety-related pumps, valves, fans, battery chargers, and transformers. "At 0743 CST, Technical Specification 3.8.9 Condition A was entered for one AC electrical power distribution subsystem inoperable. At 1021 CST, MCC 1 EB4-1 was declared Operable after MELB shielding was installed on the affected fire protection lines. "Since Unit 1 Train A 480V MCC 1 EB3-1 and the associated Unit 1 Train A safety-related pumps, valves, fans, battery chargers, and transformers have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, given the MELB condition, 1 EB4-1, 1 EB3-1 and both trains of the Unit 1 safety-related pumps, valves, fans, battery chargers, and transformers they supply could have been inoperable and this represents an unanalyzed condition. At the time of discovery, 1 EB3-1 and the associated Unit 1 Train A safety-related pumps, valves, fans, battery chargers, and transformers were operable. Therefore, this condition is not reportable as a loss of safety function per 10 CFR 50.72(b)(3)(v). "The NRC Resident Inspector was informed." Notified R4DO (Azua). * * * UPDATE ON 12/05/2016 AT 1730 EST FROM HUNTER SCHILL TO STEVEN VITTO * * * "This is an update to Event Number 52239. On December 5, 2016 during ongoing extent of condition walk downs in the Auxiliary Building, pressurized fire protection pipe segments (a flange and a pipe elbow) were identified which did not contain Moderate Energy Line Break (MELB) shielding. In the event of a MELB crack along the un-shielded portion of the pipes, a MELB had the potential to impact Unit 2 Train B 480V Motor Control Center (MCC) 2EB4-1. This MCC provides 480V electrical power to various Unit 2 Train B safety-related pumps, valves, fans, battery chargers, and transformers. "At approximately 1355 CST Technical Specification 3.8.9 Condition A was entered for one AC electrical power distribution subsystem inoperable. At 1459 CST, MCC 2EB4-1 was declared Operable after MELB shielding was installed on the affected fire protection line locations. "Since Unit 2 Train A 480V MCC 2EB3-1 and the associated Unit 2 Train A safety-related pumps, valves, fans, battery chargers, and transformers have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, given the MELB condition, 2EB4-1 , 2EB3-1 and both trains of the Unit 2 safety-related pumps, valves, fans, battery chargers, and transformers they supply could have been inoperable and this represents an un-analyzed condition. At the time of discovery, 2EB3-1 and the associated Unit 2 Train A safety-related pumps, valves, fans, battery chargers, and transformers were operable. Therefore, this condition is not reportable as a loss of safety function per 10CFR 50.72(b)(3)(v). "The NRC Resident Inspector was informed." Notified R4DO (Gaddy). * * * UPDATE ON 12/22/2016 AT 1649 EST FROM HUNTER SCHILL TO DONG PARK * * * "This is an update to Event Number 52239. On December 22, 2016 at approximately 1046 [CST] during ongoing extent of condition walk downs in the common Auxiliary Building (AB) corridor room (X-179), several normally pressurized Waste Processing (WP) pipe segments and one Vent & Drain (VD) segment which are greater than 1" nominal pipe diameter, did not contain MELB shielding. In the event of a MELB crack along the unshielded portion of these pipes, a MELB could have had the potential to impact Unit 1, Train B 480V Motor Control Center (MCC) 1EB4-1. This MCC provides 480V electrical power to various Unit 1 Train B safety-related pumps, valves, fans, battery chargers, and transformers. "Prior to the field walkdown, the subject WP and VD line segments were either isolated and depressurized (WP lines) and/or the AB sump discharges realigned (VD) such that the subject lines would pose no threat to the MCC 1EB4-1 if confirmed that shielding is required. As such, the identified condition does not adversely affect operability of 1EB4-1 and entry into a Technical Specification action statement was not required. Field activities continue to install MELB shielding in the affected locations. "Since Unit 1 Train A 480V MCC 1EB3-1 and the associated Unit 1 Train A safety-related pumps, valves, fans, battery chargers, and transformers have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, given the MELB condition, 1EB4-1, 1EB3-1 and both trains of the Unit 1 safety-related pumps, valves, fans, battery chargers, and transformers they supply could have been inoperable and this represents an unanalyzed condition. At the time of discovery, 1EB3-1 and the associated Unit 1 Train A safety-related pumps, valves, fans, battery chargers, and transformers were operable. Therefore, this condition is not reportable as a loss of safety function per 10CFR 50.72(b)(3)(v). "The NRC Resident Inspector was informed." Notified R4DO (Hay). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-09-13
52238 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-09-13 09:10 | 2016-09-13 17:00 | 2016-09-13 | AGREEMENT STATE REPORT - DENSITY GAUGE EQUIPMENT MALFUNCTION The following was received from the State of Louisiana via email: "On September 13, 2016, at approximately 0910, Central Standard Time, Radiation Safety Officer (RSO) of ExxonMobil notified LDEQ [Louisiana Department of Environmental Quality] of a potential equipment malfunction. A Ronan Model SA-1-C5 level/density gauge, device serial number LA8122A, containing a 100 mCi sealed source of Cs-137 and installed on D-Line Low Pressure Separator Vessel, V-231, was undergoing a routine annual shutter test when the gauge shutter became stuck in the open position. The RSO called Ronan and left the manufacturer a message requesting service and repair of the gauge. This is not an emergency. ExxonMobil Radiation Safety Office staff are monitoring the vessel condition and have the situation under control. There is no potential for off-site exposure." Event Report ID NO.: LA160009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-09-21
52237 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-09-01 | 2016-09-13 11:00 | 2016-09-13 | AGREEMENT STATE REPORT - PATIENT DOSE TO THE SKIN THAT EXCEEDED 50 REM The following report was received from the Pennsylvania DEP Bureau of Radiation Protection via email: "On September 12, 2016, the Department [Pennsylvania Department of Environmental Protection] was notified by Ephrata Community Hospital that while injecting technetium-99m (Tc-99m) into a patient, a leak occurred in the delivery system resulting in skin contamination and a dose to the patient's skin estimated to be greater than 50 rem. It is reportable per 10 CFR 35.3045(a)(3). "A 29 millicurie (mCi) Tc-99m dose was ordered for a patient bone scan. While injecting the dose into the patient's IV port the technologist noticed leakage and immediately stopped the injection. The patient's arm was wiped and cleaned with gauze several times. Ephrata Hospital estimates the skin contamination from that (unknown) residual activity to be approximately 15.8 mCi, resulting in a dose to the patient's skin greater than 50 rem." Event Report ID No.: PA160025 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-09-21
52236 | 0 | GREENBERRY INDUSTRIAL |  |  |  |  | 2016-05-06 | 2016-09-12 18:03 | 2016-09-12 | PART 21 FINAL REPORT- DEVIATIONS ON STRUCTURAL MODULE VOGTLE UNIT 3 AP1000 PROJECT The following was received via fax and is summarized below: "The attachment to this letter provides a report in accordance with 10 CFR 21.21 pertaining to deviations and potential defects in structural module CA33 for the Vogtle Unit 3 AP 1000r project. This issue was previously described in interim reports submitted by Greenberry in letters dated June 24, 2016 (NRC Log No. 2016-36-00, Accession No. ML16188A160) and July 26, 2016 (NRC Log No. 2016-36-01, Accession No. ML16229A180). "During fabrication of other submodules for CA35, it was discovered by Greenberry personnel that some weld cracking had occurred. During metallurgical examination, a second condition was discovered of presence of a heat affected zone and cracks in plate edges induced by plasma cutting in an area not to be welded. In order to evaluate the extent of the condition, Greenberry Industrial requested that the purchaser, WECTEC LLC, return the CA33 submodules that had already been delivered. The returned components have been inspected and it was determined that weld deviations were also present in the previously delivered submodules. Due to the use of the same plasma cutting method on CA33, it is expected that the plate edges on the returned CA33 modules also have cracks on the unwelded edges from the plasma cutting. The plasma cutting induced cracks on subsequently welded edges are typically mitigated by the welding processes for the affected edges. The cracks remaining in unwelded edges may not be a detrimental condition. This will be determined as part of further analysis of the identified conditions. "The affected material with weld defects has been returned by the purchaser, WECTEC LLC, to the supplier, Greenberry Industrial. Identification and resolution of other affected modules due to plate edge cracking will be performed when the technical evaluation of that condition is complete. The plate edge cracking may not be detrimental to the component performance. "If you have any questions pertaining to this information, please contact Mark Stapleton, Nuclear Operations Manager, at 360-567-0006 Ext. 1018." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-09-12
52235 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2016-09-09 14:00 | 2016-09-12 15:03 | 2017-11-16 | AGREEMENT STATE REPORT - MALFUNCTIONING SHUTTER ON DENSITY GAUGE The following information was provided by the State of Arkansas via email: "During routine shutter checks performed by the licensee on September 9, 2016, the licensee noted higher than normal readings when closing the shutter on a Ohmart Model SH-100 BS, weight gauge. The gauge contains 50 milliCuries of Cesium-137. "The gauge is in a secure storage area and radiation exposure is maintained at less than 2 mR/hr. "The licensee has contacted the supplier and requested disposal as the gauge in question was in storage and not being used. "In accordance with RH-1502.f.2 (10 CFR 30.50(b)(2)) the malfunctioning shutter is reportable within 24 hours. "The State of Arkansas is awaiting a written report from the licensee and final disposition information for the gauge. The State's event number is AR-2016-010. " The Licensee notified the State of Arkansas of the event on September 9, 2016, at 1430 CDT. * * * UPDATE FROM STEVE MACK TO DONALD NORWOOD VIA E-MAIL AT 1606 EST ON 11/16/2017 * * * The following information was received via E-mail: "Upon examination by the licensee's RSO it was determined that the shielding material for the gauge had been slid past the detent or retaining pins until it was removed for the source holder. This is part of the design of these gauges. The RSO returned the shielding material to the normal operating position, engaging the retaining pins and the gauge is now shielded. The shutter is working as designed. "The Department considers this event to be closed." Notified R4DO (KOZAL) and NMSS EVENTS NOTIFICATION. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2016-09-20
52234 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2016-09-11 14:51 | 2016-09-11 17:44 | 2016-09-11 | INADEQUATE DESIGN PROTECTION OF SAFETY-RELATED EQUIPMENT IDENTIFIED DURING TORNADO MISSILE IMPACT EVALUATION "During performance of an extent of condition evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Arkansas Nuclear One, Unit 1, identified non-conforming conditions in the plant design such that specific TS equipment on Unit 1 is considered not be adequately protected from tornado missiles. The reportable condition is postulated by tornado missiles entering the Unit 1 Controlled Access area, elevation 386', Upper North Electrical Penetration Room (UNEPR) through penetrating a hollow metal door and then striking safety related cables. A tornado could generate multiple missiles capable of striking the Unit 1 UNEPR and rendering both safety related emergency feedwater trains inoperable. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(B) and (D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (B) Remove residual heat, or (D) Mitigate the consequences of an accident. "This condition was identified as part of an on-going extent of condition review of potential tornado missile related site impacts. Licensee Event Report (LER) 50-313/2016-002-00 was recently submitted addressing previously identified tornado missile vulnerabilities at the Unit 1 plant. "Enforcement discretion per Enforcement Guidance Memorandum EGM 15-002 has been implemented and required actions taken. Corrective actions will be documented in a follow-on licensee event report. "The licensee has notified the NRC Resident Inspector." A similar evaluation is on going for Unit 2. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2016-09-11
52233 | 0 | THRASHER ENGINEERING, INC. |  |  |  |  | 2016-09-10 | 2016-09-10 15:45 | 2016-09-10 | THEFT OF TROXLER MOISTURE-DENSITY GAUGE Sometime between midnight and 2:30 AM on 09/10/16, a Troxler Moisture-Density Gauge Model 3440, S/N 69105, was stolen from the back of a pickup truck parked at the Sleep Inn in Beaver, WV. The Troxler Model 3440 typically contains two sources; 8 mCi Cs-137 and 40 mCi Am-241/Be. Surveillance video provided to the LLEA (Raleigh Police Department) shows an individual parking a white pickup truck next to the truck containing the gauge and subsequently transferring the gauge box to the white pickup. The licensee confirmed that the gauge was locked and properly secured prior to the theft. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-09-19
52232 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2016-09-10 03:43 | 2016-09-10 07:23 | 2016-09-10 | AUTOMATIC UNIT TRIP DUE TO MAIN GENERATOR LOCK-OUT "At 0343 EDT, with the unit operating at approximately 100% full power, an automatic reactor trip occurred due to a Main Generator lock-out. The cause of the generator lock-out is being investigated at this time. All control rods fully inserted. Post trip, the Steam Feedwater Rupture Control System was actuated due to high Steam Generator 1 level. The cause of the high Steam Generator 1 level is being investigated at this time. "The unit is currently in Mode 3 (Hot Standby) and stable, at approximately 550 degrees F and 2155 psig. Steam is being discharged through the Atmospheric Vent Valves for decay heat removal. There is no known primary to secondary leakage, and all safety systems functioned as expected. "The NRC Resident Inspector has been notified of the event." The licensee notified the State of Ohio, Ottawa and Lucas County. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-09-10
52231 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-09-09 17:39 | 2016-09-09 20:01 | 2016-09-14 | OFFSITE NOTIFICATION - RELEASE OF HYDROGEN GAS IN EXCESS OF THE REPORTABLE QUANTITY OF TEN POUNDS "At 1739 [EDT] on Friday September 9, 2016 the Massachusetts Department of Environmental Protection and the Plymouth Massachusetts Fire Department were notified of a Hydrogen release in accordance with plant procedures and 310CMR40.300, Massachusetts Contingency Plan Notification for Oil and Hazardous Material; Identification and Listing of Oil and Hazardous Material, due to a release of hydrogen gas to the environment exceeding the reportable quantity of ten pounds. The Massachusetts DEP Tracking Number is RTN4-26311. The release was from the generator hydrogen cooling system. There was no plant damage. Hydrogen system pressure has been restored to the normal operating band with the Main Generator secured and is stable. The cause of the event is under investigation. "This event posed no danger to the health and safety of plant personnel or members of the general public. "The NRC Resident Inspector has been notified.'' * * * UPDATE FROM ROBERT O'NEILL TO STEVEN VITTO AT 1724 EDT ON 09/14/2016 * * * "The Plymouth Massachusetts Fire Department was notified on Monday, September 12, 2016, at 1411 EDT. This clarifies information applicable to the local notification as identified in the original notification." Notified R1DO(Noggle) and NSIR (Stapleton) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-09-09
52230 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-09-09 10:23 | 2016-09-09 12:55 | 2016-09-09 | OFFSITE NOTIFICATION TO LOCAL AUTHORITIES DUE TO OUT-OF-SERVICE SEWAGE RADIATION MONITOR "Oyster Creek Nuclear Station made notifications to local authorities that a sewage radiation monitor was out of service due to an equipment deficiency for greater than 24 hours. Alternate sampling methods are being utilized." The licensee notified Ocean County Utilities Commission, Lacey Municipal Utilities, and the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-09-09
52229 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2016-09-08 18:56 | 2016-09-09 03:59 | 2016-09-09 | LOSS OF THE SEISMIC MONITORING SYSTEM COMPUTER "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for a loss of emergency assessment capability at the Palo Verde Nuclear Generating Station (PVNGS). On September 8, 2016 at 1856 [MST], seismic monitoring (SM) system computer AJSMNXYQI0001**INSTRU was determined to be non-functional due to a power spike which caused a temporary loss of power to the seismic instrumentation and resulted in a locked in the Control Room alarm. At 2305, I&C technicians re-booted the computer and verified the SM system was functioning. "On September 8, 2016, at approximately 2353, further review of this equipment failure and the related impact to the capability of the SM system determined that this was a reportable loss of emergency assessment capability during the period between 1856 and 2305. "This specific SM functions to provide indication that the Operational Basis Earthquake threshold has been exceeded following a seismic event and is used in the PVNGS Emergency Plan to perform classification for emergency action level HA1.1, Natural or Destructive Phenomena affecting Vital Areas. As a compensatory measure, PVNGS procedures for seismic event evaluation provide alternative methods for HA1.1 event classification with the SM out of service. Maintenance to correct the condition has been completed. "The NRC Resident Inspector has been informed of this condition." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Power Operation | Power Operation | Hot Standby | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-09-09
52228 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2016-07-12 05:50 | 2016-09-08 16:12 | 2016-09-08 | INVALID ACTUATION OF BOTH TRAINS ESSENTIAL SPRAY POND SYSTEM "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This telephone notification is being made pursuant to the reporting requirements of 10CFR50.73(a)(2)(iv)(A) and 50.73(a)(1) to describe an invalid actuation of both trains of the Palo Verde Nuclear Generating Station (PVNGS) Unit 2 essential spray pond (SP) system. The SP system serves as an emergency service water system that does not normally run and serves as an ultimate heat sink as described in 10CFR50.73(a)(2)(iv)(B)(9). "On July 12, 2016, at approximately 0550, Mountain Standard Time, Unit 2 experienced a manual actuation of both trains of the SP system. Approximately 20 minutes earlier, the failure of a +15VDC power supply on the containment purge isolation actuation signal (CPIAS) module resulted in a trip of the B train CPIAS and a momentary cross trip of the A train CPIAS, and both trains of the control room essential filtration actuation system (CREFAS). These brief actuation signals resulted in starting of some but not all essential equipment because the actuation signals cleared before most of the equipment received a start signal. Both trains of the SP system were started manually in accordance with the alarm response procedure. The A train CPIAS and both trains of CREFAS were reset. The B train CPIAS remained in a partially tripped state because of the failed power supply. "The manual actuation of both A and B trains of the SP system was complete. Both trains of the SP system started and functioned successfully. The invalid actuation was the consequence of a failed +15VDC power supply on the B train CPIAS module which resulted in momentary trips of both trains of CPIAS and CREFAS. The containment building radiation monitors that actuate CPIAS exhibited normal radiation levels which would not have required CPIAS actuation. The event was entered into the PVNGS corrective action program. There was no adverse impact to public health and safety nor to plant employees. "The NRC Resident Inspectors have been informed." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-09-08
52227 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2016-07-11 04:30 | 2016-09-08 14:50 | 2016-09-08 | INVALID ACTUATION OF DIVISION 1 PRIMARY CONTAINMENT ISOLATION LOGIC DUE TO A BLOWN FUSE "On July 11, 2016, at approximately 0430 CDT, while Unit 1 was operating at 100% power, the 1A Reactor Protection System (RPS) Motor Generator (M/G) set tripped causing a loss of the A RPS bus. This caused the complete actuation of the Division 1 (outboard) primary containment isolation logic. The isolation logic actuation resulted in successful closure of the Division 1 primary containment isolation valves. This was an event that resulted in the actuation of a general containment isolation signal affecting more than one system. However, as this event meets the definition of an invalid actuation (i.e., not a response to an actual plant parameter exceeding a trip set-point), this notification is being made in accordance with 10CFR50.73(a)(2)(iv)(A) in lieu of a Licensee Event Report. "In response to the trip of the 1A RPS M/G Set, operators swapped the A RPS bus to the alternate power supply using the applicable response procedure. The containment isolation signal was reset and the systems were restored to their normal lineup. Reactor power was not affected by this event. All safety related equipment controlled by the affected primary containment isolation circuits operated as designed. "The 1A RPS M/G Set trip was due to a blown power fuse for the 1A RPS M/G Set. This was the result of worn insulation on one of the generator output leads. The generator output leads were repaired and rerouted to prevent future problems on 07/15/16. Restoration of the normal power supply to the 1A RPS function was completed on 7/19/16." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-09-08
52226 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2016-09-07 21:31 | 2016-09-08 04:27 | 2016-09-08 | MANUAL REACTOR TRIP DUE TO STUCK OPEN PRESSURIZER MAIN SPRAY VALVE "On September 7th, 2016 at approximately 2131 Mountain Standard Time (MST), Palo Verde Unit 1 was manually tripped due to a stuck open main spray valve. Unit 1 was operating at 100 percent power at normal operating temperature and pressure prior to the event. A 120 VAC non-class instrument distribution panel was being transferred to its alternate power supply to establish maintenance conditions. The distribution panel failed to transfer. The panel remained energized from its normal power supply; however, multiple components powered from the distribution panel began to exhibit uncharacteristic behavior. At this time, it was noted that a reactor coolant system main spray valve was open. The alarm response procedure was followed; however, the actions taken were unsuccessful at closing the main spray valve. The plant was then manually tripped due to pressurizer pressure continuing to lower. The reactor coolant pumps were turned off to terminate main pressurizer spray flow to control pressurizer pressure due to the inability to close the main spray valve. No ESF [Engineered Safety Features] actuations occurred and none were required. No emergency classification was required per the emergency plan. Safety related buses remained energized during and following the reactor trip. The emergency diesel generators did not start and were not required. The offsite power grid is stable. Limiting condition for operation 3.4.1 was entered due to low pressurizer pressure. No major equipment was inoperable prior to the event that contributed to the event. "Unit 1 is stable at normal operating temperature and pressure in Mode 3. Reactor coolant pumps are secured and natural circulation has been verified. Primary pressure is being maintained at its normal operating pressure manually with pressurizer heaters and auxiliary spray, from the charging system. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The minimum RCS pressure was approximately 2070 psia (normal 2250). The event did not adversely affect the safe operation of the plant or the health and safety of the public." All rods inserted and the trip was uncomplicated. Units 2 and 3 were not affected and continue to run at full power. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-09-08
52225 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2016-09-08 03:00 | 2016-09-08 04:27 | 2016-09-08 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO LOSS OF RESIDUAL HEAT REMOVAL PUMP "On September 4, 2016 at 0258 [CDT], Grand Gulf Nuclear Station entered three [Technical Specification] Limiting Conditions for Operations (LCOs) due to residual heat removal pump 'A' (RHR 'A') being declared inoperable. "LCOs entered: 1) 3.5.1 for one low pressure ECCS injection/spray subsystem, 2) 3.6.1.7 for one RHR containment spray subsystem, and 3) 3.6.2.3 for one RHR suppression pool cooling subsystem. "Station management has made the decision to shutdown the plant to repair the RHR 'A' pump prior to the end of the 7 day LCO completion time based on troubleshooting and testing performed on the RHR 'A' pump. "Grand Gulf Nuclear Station initiated plant shutdown required by Tech Spec Actions 3.5.1, 3.6.1.7, and 3.6.2.3, at 0300 CDT on 09/08/2016 due to expected inability to restore RHR 'A' to operable status prior to exceeding the LCO time of 7 days." The unit is currently at 82 percent power. There are no other systems out of service that would complicate the orderly shutdown to Mode 4. The licensee will notify the NRC Resident Inspector. | 82 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-09-08
52224 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-09-06 13:47 | 2016-09-07 16:47 | 2016-09-23 | NON-ESSENTIAL SERVICE WATER HEADER DECLARED INOPERABLE "At 1347 EDT on September 6, 2016, the non-essential service water header was declared inoperable due to what appeared to be a leak on a filet weld on a slip-on flange upstream of the 23 service water pump discharge valve SWN-2-2. [Operators] entered LCO 3.0.3 based on Engineering input with no code case to support an immediate determination of operability. The 23 service water pump was secured and the discharge valve SWN-2-2 was closed isolating the leak and restoring the non-essential SW header to operable status. With the discharge valve closed, LCO 3.0.3 was exited at 1417 EDT on September 6, 2016. The declaration of the inoperability of the non-essential service water header is considered a loss of safety function for purposes of reporting under 10 CFR 50.72(b)(3)(v). Further investigation of the leak revealed [that the leak had occurred at] a pipe flaw rather than at the weld location. An operability evaluation is ongoing. There was no reduction in power while in LCO 3.0.3 and no other issues arose." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM CHARLES ROKES TO JOHN SHOEMAKER AT 0839 EDT ON 9/23/16 * * * "Indian Point Unit 2 is retracting the 8-hour non-emergency notification made on September 7, 2016, at 1647 hours EDT (EN #52224). The notification on September 7, 2016, reported a safety system functional failure (SSFF) as a result of declaring the non-essential service water (SW) header inoperable due to discovery of a through wall leak on the discharge line from the 23 SW Pump. The leak appeared to be on the downstream fillet weld on the north side of the pipe spool piece. At the time the exact location of the leak could not be established due to the geometry of the area and its carbon fiber coating. Because there is no qualified NDE inspection technique for fillet welds and the analytical methods provided in ASME code Case N-513-3 are not applicable to fillet welds, operability of the effected section of the SW System could not be demonstrated and the SW piping was conservatively considered inoperable. "Further investigation of the leak determined the leak occurred mid-pipe 1/2 inch upstream from a slip-on flange socket weld and not on the weld itself. The weld location is ASME Section XI Class 3, nuclear safety-related, Seismic Class 1. An engineering evaluation was performed of the pipe defect and concluded the identified through-wall defect on the pipe spool piece did not result in any structural, flooding, spraying condition or SW system capacity issues which would adversely impact any normal or accident design functions of the SW system or any other nuclear safety-related equipment or component to perform their design safety functions from the time of the leak occurrence to the isolation of the pipe. The structural portion of the evaluation was performed using the ASME CC N-513-3 methodology but the code case was not invoked because the flaw was isolated and a code repair was made. The 23 SW Pump discharge line spool piece is a 14 inch NPS schedule STD cement-lined carbon steel pipe having a nominal wall thickness of 0.375 inches with slip-on flanges welded on both sides with fillet welds on the exterior. The function of this spool piece is to connect the 23 Zurn Strainer outlet to the isolation valve SWN-2-2. The degradation mechanism was likely due to corrosion of the carbon steel on the underside of the cement lining due to a lining defect." The licensee will notify the NRC Resident Inspector. Notified R2DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-09-07
52223 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-09-06 08:27 | 2016-09-06 11:24 | 2016-09-06 | MANUAL REACTOR SCRAM DUE TO HIGH REACTOR WATER LEVEL "On Tuesday, September 6, 2016 at 0827 [EDT], with the reactor at 91% core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) operators initiated a manual reactor scram due to high reactor water level resulting from feedwater level control oscillation. Other than the feedwater level control oscillations, all other plant systems responded as designed. Plant cooldown is in progress using the High Pressure Coolant Injection System in the pressure control mode. "The plant is in hot shutdown. The cause of the feed water level control oscillations is under investigation. This event has no impact on the health and safety of the public. "Subsequent to the manual reactor scram the plant experienced the following isolation signals: Group 1 Isolation: Main Steam Isolation Valves Group 2 Isolation: Miscellaneous containment isolation valves Group 6 Isolation: Reactor Water Clean-up Reactor Building [Ventilation] Isolation Actuation "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'any event that results in actuation of the reactor protection system (RPS) when the reactor is critical...'. This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section...' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).'" All rods were inserted. The plant is stable with normal off-site power line-up. The licensee will notify the Commonwealth of Massachusetts. | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-09-06
52222 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-09-03 09:02 | 2016-09-03 12:47 | 2016-11-02 | UNIDENTIFIED LEAKAGE GREATER THAN TECHNICAL SPECIFICATIONS "At 0902 EDT, on September 3, 2016, a leak developed from 13 Charging Pump seals that resulted in an unidentified leak rate of 1.3 gpm. Salem Unit 1 entered Technical Specification 3.4.6.2.b for unidentified leakage greater than 1 gpm. The Technical Specification requires the leak rate to be restored to below 1 gpm in a 4 hour period or place the Unit in Hot Standby in the next 6 hours and Cold Shutdown within the following 30 hours. In addition there is an allowable total ECCS leakage outside of Containment value of 0.45 gpm associated with Control Room habitability to comply with GDC-19 [General Design Criteria] limits. 12 Charging Pump was placed in service and 13 Charging Pump was removed from service and isolated. The unidentified leak rate lowered to below the 0.45gpm requirement for the total ECCS leakage outside of containment and the Technical Specification value of 1 gpm. "This event is being reported under the requirements of 10CFR50.72(b)(3)(ii)(B) as 'the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety' for exceeding the 0.45gpm total ECCS leakage allowable in accordance with GDC-19 limitations. "The Licensee has notified the NRC Resident and the Lower Alloways Creek Township." * * * RETRACTION FROM MATT MOG TO STEVEN VITTO ON 11/02/2016 AT 0916 EDT * * * "The purpose of this notification is to retract event report number 52222 made on 09/03/2016 at 1247 (EDT). Previously PSEG reported that Salem Unit 1 was in an unanalyzed condition due to a leak from the 13 Charging Pump seals exceeding the 0.45 gpm limit for total ECCS leakage outside containment associated with the Control Room Habitability analysis. "A subsequent engineering evaluation determined that the post-accident ECCS leak rate from the 13 Charging Pump seals that would have existed is 0.33 gpm. This is within the limits of the existing Control Room Habitability analysis and no unanalyzed condition existed. "Therefore, PSEG is retracting the notification made under 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector was notified of this retraction by the licensee." Notified R1DO (Schroeder). | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-09-03
52221 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-09-03 07:10 | 2016-09-03 08:44 | 2016-09-03 | UNUSUAL EVENT DECLARED DUE TO SEISMIC EVENT ALARM At 0710 CDT, Cooper Nuclear Station declared a Notification of Unusual Event under EAL HU1.1 due to the station seismic event alarm registering a response to an earthquake (epicenter near Pawnee, OK). The reactor was not affected by the earthquake and remains at 93 percent power. The licensee is performing walkdowns of structures and equipment to verify that the site is unaffected. Notified the DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (E-mail) and Nuclear SSA (E-mail). * * * UPDATE FROM ZACH HYDE TO STEVEN VITTO AT 1704 EDT ON 9/3/2016 * * * At 1547 CDT, Cooper Nuclear Station terminated the Notice of Unusual Event. All inspections and walkdowns of the plant have been completed. No damage or injuries were reported. The seismic event caused no impact to the plant. The Licensee has notified the NRC Resident Inspector. Notified R1DO (Warnick), NRR EO (Miller), IRDMOC (Stapleton), DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (E-mail) and Nuclear SSA (E-mail). | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-09-03
52220 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-09-03 01:20 | 2016-09-03 01:54 | 2016-09-03 | SAFEGUARDS REPORT - UNAUTHORIZED ENTRY INTO CONTROLLED ACCESS AREA An actual entry of an unauthorized licensee employee into a controlled access area. The Licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2016-09-12
52219 | -1 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-09-02 19:22 | 2016-09-02 23:33 | 2016-09-04 | SPENT FUEL POOL AREA RADIATION MONITOR LOST SIGNAL "Unit 1 Spent Fuel Pool Area Radiation Monitor (1EMF17) lost signal resulting in off scale high indications. Subject EMF provides alarm functions and indication which are used for assessment of EAL classifications. Failure response conducted per applicable Alarm Response Procedures and subsequent actions performed per applicable license commitment required actions. Temporary dose rate monitor has been set up for area monitoring with alarm setpoint commensurate with subject EMF. Issue entered into corrective action program and prioritized to restore subject EMF to functional status within required 30 days." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM PHILIP BALES TO STEVEN VITTO AT 2323 EDT ON 9/4/2016 * * * "This notification is being made to retract event EN 52219, which was reported on September 2, 2016. Upon further investigation, the loss of radiation monitor 1EMF17 did not prevent the evaluation of all EALs [Emergency Action Level] for the associated emergency initiating conditions. Additionally, it has been determined 1EMF17 is not utilized for performing radiological assessments. "Therefore, no actual or potential major loss of emergency assessment capability existed per 10 CFR 50.72(b)(3)(xiii). This is consistent with NUREG 1022, Rev. 3, Supplement 1 and NEI 13-01, Rev. 0. The NRC Resident Inspector will be notified of the retraction." Notified R2DO (Bartley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-09-02
52218 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2016-09-02 08:08 | 2016-09-02 11:29 | 2016-10-21 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "While operating in MODE 1 at 100 percent rated thermal power and placing Excess Letdown in service for Reactor Coolant System (RCS) leak detection, RCS operational leakage exceeded 1 gpm [gallon per minute] unidentified leakage as identified by performing RCS Water Inventory Balance using the Nuclear Plant Information System Computer. This required the entry into Technical Specification (TS) Limiting Condition of Operation (LCO) 3.4.13 Condition B at 0808 [CDT] on 9/2/16. The associated action is to place the unit into Mode 3 in 6 hours. Trending of containment sump level indicates the leakage is inside containment with the exact location within containment unknown. Containment inspection is being performed to try and identify the source of Reactor Coolant System leakage. NRC Resident Inspector has been notified. Re-alignment of the Letdown System back to its normal arrangement has subsequently reduced RCS leak rate to 0.521 gpm at 0652 CDT on 9/2/16. "Unusual or Not Understood - Leak Location is not known at this time." Maximum leak rate recorded was 1.358 gpm. The leak was first discovered at 08/31/16 at 1519 CDT. Safety Related Equipment not operational - Reactor Vessel Level Indicating System (TS 3.3.3). * * * RETRACTION AT 1101 EDT ON 10/21/2016 FROM LARRY HAUTH TO JEFF HERRERA * * * "Wolf Creek Nuclear Operating Corporation is retracting the 10 CFR 50.72(b)(2)(i) notification based on subsequent review of the event. The calculation of unidentified leak rate which triggered entry into the Mode 3 Required Action Statement was performed immediately after placing RCS Excess Letdown in service. An evaluation of the leak rate calculation determined that the leak rate was invalid due to performance of the RCS water inventory balance during non-steady state operating conditions. This was contrary to the requirements of TS Surveillance Requirement 3.4.13.1, as this test was performed while charging and letdown flows were being stabilized following the alignment of excess letdown. A walk down of the Excess Letdown system while in-service determined no leakage. Subsequent RCS water inventory balances performed with Excess Letdown in service under steady state operating conditions while in Mode 3 at normal operating pressure and temperature determined the maximum calculated unidentified leak rate was 0.675 gpm. "After the plant entered Mode 3 a non-RCS pressure boundary leak was identified during equipment walk downs on a seal weld from the reactor vessel head core exit thermocouple nozzle assembly 77. "The leakage did not impact the ability to shut down the unit. No TS limits were exceeded during this event. "Therefore, the plant shutdown to investigate and correct leakage past the seal weld of a threaded connection does not meet the reporting requirements of 10 CFR 50.72. "The NRC Resident Inspector has been notified." Notified the R4DO (Kramer). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-09-02
52217 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-09-01 10:25 | 2016-09-01 18:39 | 2016-10-27 | UNANALYZED CONDITION ON TURBINE DRIVEN AUXILIARY FEEDWATER PUMP "During a review of ongoing analyses related to postulated tornado missiles, a question was raised about the sentinel valve on the turbine driven auxiliary feedwater pump (TDAFW). The sentinel valve is designed as a warning system on steam equipment to warn personnel of increased back pressure. The valve is not an ASME component and its operation is not required to support TDAFW operation. "The draft analysis predicts the TDAFW exhaust stack could be partially crimped by a tornado missile and the resultant back pressure on the turbine would increase to approximately 40 psi. This is higher than the set point for the sentinel valve (nominally 27 and 29 psi for Units 1 and 2, respectively). Therefore, in a design basis tornado with a design basis tornado missile striking the TDAFW exhaust stack, and in a condition where the TDAFW is demanded to run, the sentinel valve is expected to lift and allow steam to flow into the room. "Vendor correspondence indicates that at approximately 40 psi the sentinel valve will conservatively pass 600 lbm/hr. Thus, it is conservatively considered operation of the TDAFW under such conditions would create an adverse steam environment which would be beyond that which the TDAFW pump has been analyzed to operate. Actions planned to alleviate the above condition would eliminate the potential for adverse environmental conditions. "The steam supplies to the TDAFW have been isolated to affect repairs, which are expected to be limited to removal of the sentinel valve from each Unit and installation of a plug. Said activities are expected to be completed within the Allowed Out-of-Service Time (AOT) of the TDAFW of seventy-two hours per Technical Specification 3.7.5." NRC Resident Inspector has been informed. * * * RETRACTION ON 10/27/2016 AT 1353 EDT FROM DANNY BRADFORD TO BETHANY CECERE * * * "On 09/01/2016 Comanche Peak reported an ENS Report (no. 52217) related to unanalyzed conditions related to the sentinel valve on the turbine driven auxiliary feedwater pump (TDAFW) during postulated tornado-based scenarios and non-tornado based scenarios. The technical concern was the potential for the sentinel valve to release steam into the TDAFW room and result in adverse environmental conditions within the room and potentially external to the TDAFW room for both tornado-based and non-tornado based scenarios. "Subsequent investigations by Engineering have determined the sentinel valve would not be demanded to open during tornado based scenarios and would not result in adverse environmental conditions internal or external to the TDAFW room in any design bases scenario." The licensee has notified the NRC Resident Inspector. Notified the R4DO (Farnholtz). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-09-01
52216 | 0 | ENERSYS |  |  |  |  | 2016-09-01 | 2016-09-01 14:51 | 2016-09-02 | PART 21 - POTENTIAL FAILURE OF BATTERY SYSTEM CONNECTIONS "This letter will serve as notification from EnerSys to the United States Nuclear Regulatory Commission of an identified deviation in published literature information. The literature defines requirements for resistance in both cell to cell and cell to terminal connections in supplied battery systems. High connection resistance causes increased cell voltage drop and a potential failure to meet run time requirements. "Internal investigation by EnerSys confirms that no defects exist in systems tested before shipment to customer utilities as internal documented procedures define correct parameters. However, the potential of less than desired performance exists if the values noted in the literature are used during installation and test at utility sites. "EnerSys does not have the ability to evaluate if a defect exists at customer utilities so per the provisions of Part 21, notification is being made to both the Commission and affected EnerSys customers." POC: 800-538-3627 ext. 1974 * * * UPDATE FROM WILLIAM ROSS TO STEVEN VITTO AT 1339 EDT on 09/02/2016 * * * "The literature in question is the EnerSys Safety, Storage, Installation, Operation and Maintenance Manual for Flooded Lead-Acid Batteries C, D, E, F and G, number US-FL-IOM-002 dated January 2007. The errors are located in Section 7.4.3.8c line 2. The current wording of '... connection is more than 30 percent or 5 Mohms above the average...' should read 'connection is more than 10 percent or 5 micro-ohms, whichever is greater, above the average'." Licensees affected are Dominion North Anna, Dominion Surry Nuclear Power Plant, Energy Northwest Columbia Generating Station, Entergy Nuclear Operations IP2, First Energy Beaver Valley NPP, NextEra Energy Point Beach Nuclear Plant, Perry Nuclear Power Plant, and San Onofre Nuclear Generating Station. Notified R1DO(Powell), R2DO (Bartley), R3DO (Dickson), R4DO (Warnick), and Part 21Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-09-01
52215 | 0 | INTEGRITY TESTLAB |  |  |  |  | 2016-09-01 11:15 | 2016-09-01 13:11 | 2016-09-01 | UNABLE TO RETRACT SOURCE INTO SHIELDED POSITION "At 1122 [EDT], the RSO [Radiation Safety Officer] for Integrity Testlabs [ITL], LLC, received a telephone notification from the field radiographer at the client's location that he was unable to retract the source fully into the shielded position. The radiographer attempted to retract the source twice. The radiographer realized the source was not going to get shielded because he noticed that the control cable housing was laying on equipment which was later determined to be approximately 500 degrees F. This melted the control cable housing and in turn prevented the complete retraction of the source into the shielded position. The radiographer kept the source to the fully exposed position within the 4HVL collimator and proceeded to extended the posted radiation area boundaries to 2mR/hr or less, then contacted the RSO at 1122 [EDT]. The RSO was approximately 50 miles away and stated he was on his way to assist in the recovery process. The company and RSO are authorized to perform recovery of sources. "The radiographer then contacted his supervisor, who was the senior radiographer onsite. The supervisor also attempted to retract the source into the shielded position. The supervisor contacted the RSO and explained the situation. By direction from the RSO via telephone communication, the supervisor was able to disconnect the control housing at the remote control crank and pull the control cable so that the source was retracted into the shielded position. The radiography operations were terminated for the day. Surveys were performed after the source was shielded with no unusual readings. All equipment was returned to ITL's facility. "The following self-reading pocket dosimeter readings were recorded at the conclusion of this event. The radiographer and assistant radiographer had performed 6 exposures for the day. The 6 exposures included the event. Radiographer 100mR Assistant 20mR Supervisor 23mR during the recovery process No radiographic personnel or member of the pubic was overexposed during the entire event. "The affected equipment will be inspected, repaired or replaced, as needed. "A follow report will be submitted to Region I as soon as practical. "Equipment: QSA Global Model 880s #S1667 w/ IR-192 #32053G - 56.5Curies 25Ft Extreme Control Cables with two extreme guide tubes, each guide tube 7ft long and the outer most guide stop having a source stop. One - 4HVL Tungsten collimator" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-09-09
52214 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-08-31 19:50 | 2016-08-31 23:32 | 2016-10-20 | UNANALYZED CONDITION WITH A POTENTIAL TORNADO "In Event Notification (EN) 52202 on August 25, 2016, Fermi 2 identified an unanalyzed condition related to the inoperability of Mechanical Draft Cooling Tower (MDCT) fans due to nonfunctionality of the associated brakes that occurred on April 6, 2016. The MDCT fan brake is required to prevent fan over speed from a design basis tornado. The MDCT fans are required to support the operability of the Ultimate Heat Sink (UHS) reservoir and associated Emergency Diesel Generators (EDGs). The EN noted that a past operability review was in progress to determine if declaring a MDCT fan inoperable due to a fan brake being nonfunctional resulted in additional instances of unanalyzed conditions within the: three years prior to August 25, 2016. "On August 31, 2016 at 1950 EDT, the past operability review identified five additional instances of unanalyzed conditions within the past three years. These five instances are being reported in one EN since they are related and were all discovered and reported within 8 hours. Although these instances are related to the one previously reported in EN 52202, they are being reported in a new EN due to the time elapsed since EN 52202. The MDCT fans and fan brakes are currently operable. "1) February 2016 - The Division 1 MDCT fan 'A' brake nitrogen bottle pressure was below the required limit from 0936 EST to 1344 EST on February 25, 2016. This nonfunctionality of the MDCT fan 'A' brake coincided with a High Pressure Coolant Injection (HPCI) system outage in Division 2. "2) March 2015 - The Division 1 MDCT fan 'A' brake nitrogen bottle pressure was below the required limit from 1000 EDT on March 23, 2015, until 1447 EDT on April 9, 2015. There is reasonable expectation that the nonfunctionality of the MDCT fan 'A' brake coincided with various Division 2 systems, structures, or components (SSCs) out of service during a forced outage. "3) February 2014 - The Division 2 MDCT fan 'B' brake nitrogen bottle pressure was below the required limit from 1118 EST to 1529 EST on February 20, 2014. There is reasonable expectation that the nonfunctionality of the MDCT fan 'B' brake coincided with various Division 1 SSCs out of service during a refueling outage. "4) February 2014 - The Division 1 MDCT fan 'A' brake nitrogen bottle pressure was below the required limit from 1747 EST on February 14, 2014, until 1514 EST on February 24, 2014. There is reasonable expectation that the nonfunctionality of the MDCT fan 'A' brake coincided with various Division 2 SSCs out of service during a refueling outage. "5) January 2014 - The Division 1 MDCT fan 'A' brake nitrogen bottle pressure was below the required limit from 0915 EST on January 24, 2014, until 1537 EST on January 31, 2014. This nonfunctionality of the MDCT fan 'A' brake coincided with approximately 30 hours where various Division 2 safety-related SSCs were inoperable. "The occurrences discussed above resulted in unanalyzed conditions because the plant configuration when equipment in one division was inoperable while a MCDT fan brake was nonfunctional in the opposite division would not support safe shutdown capability in the event of a tornado. This condition is reportable under 10 CFR 50.72(b)(3)(ii)(B), as an event or condition that results in an unanalyzed condition that significantly degrades plant safety. There was no adverse impact to public health and safety or to plant employees. "The NRC Resident Inspector has been notified." * * * UPDATE FROM JEFF YEAGER TO JOHN SHOEMAKER AT 1508 EDT ON 10/20/2106 * * * The licensee is RETRACTING item 1 only of the 5 events listed above: 1) February 2016 - The Division 1 MDCT fan 'A' brake nitrogen bottle pressure was below the required limit from 0936 EST to 1344 EST on February 25, 2016. This nonfunctionality of the MDCT fan 'A' brake coincided with a High Pressure Coolant Injection (HPCI) system outage in Division 2. "Fermi 2 is retracting item 1 of the 8-hour event notification made on August 31, 2016, at 2332 EDT, (EN #52214). EN #52214 originally reported a non-functionality of the Division 1 MDCT fan 'A' brake on February 25, 2016, as an unanalyzed condition due to it coinciding with a Division 2 High Pressure Coolant Injection (HPCI) system outage. Subsequent engineering evaluation has determined that although the intermediate nitrogen bottle pressure was below its required limit, the pressure in the main nitrogen bottle was sufficient to ensure that the MDCT fan 'A' brake could have performed its intended function in the event of a tornado. Since the MDCT fan 'A' brake was determined to be functional, the MDCT fan 'A', the associated Division 1 UHS reservoir, and the Division 1 EDGs were all operable at that time. Therefore, no unanalyzed condition existed on February 25, 2016. The other four items [2-5] included in EN #52214 are not being retracted and are still considered unanalyzed conditions. "The licensee notified the NRC Resident Inspector." Notified R3DO (Orth). | 74 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-08-31
52213 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-31 15:11 | 2016-08-31 18:12 | 2016-08-31 | AUTOMATIC REACTOR TRIP ON LOW REACTOR COOLANT FLOW "This 4-hour and 8-hour notification is being made to report that Salem Unit 2 had an unplanned automatic reactor trip and automatic actuation of the auxiliary feedwater system. The trip occurred due to the loss of the 21 reactor coolant pump [RCP] resulting in a reactor trip on low reactor coolant flow. The 21 RCP remains unavailable. The cause of the loss of the 21 reactor coolant pump is unknown at this time. "All control rods inserted on the reactor trip. All emergency core cooling systems and engineered safety feature systems functioned as expected. The auxiliary feed pumps started as expected. "Salem Unit 2 is currently in Mode 3. Reactor coolant system pressure is at 2235 psig and temperature is 547 degrees Fahrenheit with decay heat removal via the main steam dumps and auxiliary feedwater systems. Unit 2 has no active technical specification action statements in effect requiring a lower mode of operation due to the transient. "The 21 and 22 containment fan coil units (CFCU) were out of service for surveillance testing prior to the event. There was no major secondary equipment tagged for maintenance prior to the event. There were no personnel injuries as a result of this event. "Normal offsite power is available to the site. There is no effect on Unit 1." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-08-31
52212 | 0 | FLOWSERVE |  |  |  |  | 2016-08-31 | 2016-08-31 16:00 | 2016-08-31 | PART 21 NOTIFICATION - FLOWSERVE SWING CHECK VALVES The following is an excerpt of the part-21 notification: "Susquehanna Nuclear reported two size 3 class 900 Anchor Darling swing check valves were not passing LLRT [local leak rate tests]. After disassembly there appeared to be wear between the hinge arm and seat ring of the valve body apparent on the hinge. The interference was not severe enough to stop hinge arm motion of the disk, but did affect ability of the valve to seal during LLRT." Affected Serial Numbers: BQ752, BQ753, and BO809 Affected Sites: Ginna, Diablo Canyon, Brunswick, Davis Besse, Kewaunee, Conn Yankee, Monticello, Susquehanna, Framatome, Chin Shan, and Kuosheng Engineering Evaluation 10CFR21 No. 91 POC: Wade Shephard: 919-832-0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-08-31
52211 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-08-30 | 2016-08-31 13:33 | 2016-08-31 | AGREEMENT STATE REPORT - DAMAGED PROCESS NUCLEAR GAUGE The following report was received via fax: "On August 30, 2016, the licensee's Radiation Safety Officer reported that two cap screws used to secure the shutter handle on a fixed gauge (Ohmart Model SH-F2-C; serial number 70929; 1000 milliCuries cesium-137) had sheared off during a routine test of the on-off mechanism earlier in the day. The failure left the shutter in the on or open position. The gauge is used to provide density measurements of product traveling through a stainless steel pipe and is normally left in the on position. Personnel entry into the pipe is not possible, eliminating potential personnel exposure to radiation. The licensee has contacted a licensed service company to repair the gauge." Virginia Report: VA-16-013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-09-08
52210 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-30 21:20 | 2016-08-30 21:49 | 2016-08-31 | NOTICE OF UNUSUAL EVENT - FIRE IN A MAIN BANK TRANSFORMER A fault occurred on the unit 2 "B" main bank transformer resulting in an oil fire. The main turbine tripped resulting in a reactor trip. All control rods fully inserted and no safety or relief valves lifted. Decay heat is being removed via steam dumps to the main condenser and feeding steam generators with auxiliary feedwater. Electrical power is through the normal shutdown electrical lineup. Offsite assistance was requested from the county and off duty fire brigade members. At 2228, the fire was reported as out. Spray is continuing and a reflash watch is being set. Unit 1 continued to operate at 100% power throughout the event. Notified the DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (E-mail) and Nuclear SSA (E-mail). * * * UPDATE AT 2352 EDT ON 08/30/2016 FROM MICHAEL BOTTORFF TO JEFF HERRERA * * * "On August 30, 2016, at 2110 EDT, Watts Bar Nuclear Plant Unit 2 reactor tripped due to an electrical fault affecting the 2B Main Bank Transformer, resulting in a fire in the transformer. "Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and main steam dump systems. Unit 2 is in a normal shutdown electrical alignment. "The fire was out at 2230 EDT. The cause of the fire is currently under investigation. "The fire was reported at 2149 EDT. Local Fire Departments responded to the site as requested. "The reactor trip and system actuation is being reported under 10CFR50.72(b)(3)(iv)(A) and 10CFR50.72 (b)(2)(iv)(B). "There was no effect on WBN Unit 1. "The NOUE was exited at 2342. "The NRC Senior Resident Inspector has been notified." The Licensee notified the State of Tennessee. Notified the R2DO (Bartley), IRD MOC (Stapleton), NRR EO (Miller), DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (E-mail) and Nuclear SSA (E-mail). | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  | 0 | 2016-08-30
52209 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2016-08-30 09:35 | 2016-08-30 18:07 | 2016-08-30 | FITNESS-FOR-DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2016-08-30
52208 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2016-08-30 11:04 | 2016-08-30 16:05 | 2016-08-30 | FITNESS-FOR-DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2016-08-30
52207 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-08-25 19:15 | 2016-08-29 16:29 | 2016-08-29 | AGREEMENT STATE REPORT - LOST X-RAY FLUORESCENCE ANALYZER The following report was received from the New York Department of Health: "An employee of TRC [TRC ENVIRONMENTAL CORPORATION] put a Niton XLP-300, XRF [X-Ray fluorescence analyzer] containing 40 milliCuries of Cadmium 109 on the overhead shelf of New Jersey Transit bus #8306 and then forgot to collect the case when he got off the bus and went home. The employee contacted the NJT [New Jersey Transit] offices at approximately 0845 [EDT] on Friday, 8/26/2016, to inquire about the lost case. He provided a description of the case and a photo of a similar case. Claim number L487457 was assigned to the matter by NJT. As of 1730 on 8/26/2016, NJT staff had not located the case. A TRC Project Manager visited the PABT [Port Authority Bus Terminal] in New York City at approximately 1430 on Friday 8/26/2016. When the bus arrived, the TRC Project Manager inquired with the driver if the case had been found and double checked the bus, but did not locate the case. The TRC Project Manager also went to Customer Service/Lost and Found at PABT for NJT and made an additional claim, number L487502, with his mobile contact number should device be returned to PABT. The TRC employee will check in with the NJT lost and found department later in the evening on 8/26/2016 to ask if the case has been located." See also EN-52206. New York Event # NY-16-05 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-09-06
52206 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-08-25 18:45 | 2016-08-27 21:06 | 2016-09-06 | AGREEMENT STATE REPORT - LOST X-RAY FLUORESCENCE ANALYZER The following was received from the State of New Jersey via email: "NJDEP [New Jersey Department of Environmental Protection] received notification from New Jersey Transit Police at 1426 EDT on Saturday, 8/27/16, that a Niton xlp 300 series XRF with serial number 7710 belonging to New York licensee TRC Environmental Corporation was left on a New Jersey Transit bus on Thursday, 8/25/16 at approximately 1845 EDT. The licensee reported the loss of the device to New York State Department of Health on Friday, 8/26/16. The Cadmium-109 source in the device has a maximum activity of 50 mCi (per sealed source registry). This is being reported under 10 CFR 20.2201(a)(1)(i) because it exceeds 1000 times the value for Cd-109 in Appendix C. The licensee employee who left the device on the bus was taking it home to have it for a job in New York the next day. They did not plan to use the device in New Jersey. "NY DOH [New York Department of Health] officials indicated that they will provide NJDEP with more information on Monday, 8/28/16." State Report #: NJ-16-02 * * * UPDATE FROM KAREN FLANIGAN TO DONALD NORWOOD AT 1134 EDT ON 9/6/2016 * * * "The device was found on a New Jersey Transit bus in Weehawken, New Jersey and was picked up by the licensee on 9/1/16. "New York Department of Health provided New Jersey DEP with the following information from their licensee: New York License Number - C3264. Source S/N - TR3464. Device S/N - 22323. Activity at time source was lost - 26.8 mCi [Cd-109]. "This event is the same event as EN 52207 which was reported by NY DOH." Notified R1DO (Gray), ILTAB (Whitney), and NMSS Events Notification (E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-09-05
52205 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-08-27 15:00 | 2016-08-27 17:48 | 2017-03-17 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On August 27, 2016, at 1500 EDT a severe thunderstorm occurred in Monroe County, including the Fermi 2 site. Due to high winds encountered during the thunderstorm, the Technical Specification (TS) for secondary containment pressure boundary was not met numerous times. The duration of time that the secondary containment Technical Specification was not met was approximately 1 second for each event. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. At 1540 EDT, secondary containment vacuum was greater than the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) and steady, and the LCO was exited. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter). | 53 | 0 | 0 | 53 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-08-27
52204 | 0 | CRANE NUCLEAR, INC. |  |  |  |  | 2016-08-03 | 2016-08-26 18:00 | 2016-09-30 | PART 21 - SAFETY RELATED COMPONENT WELDING BY AN UNQUALIFIED WELDER The following was excerpted from a letter by Crane Nuclear, Inc.: "Shielded metal arc welding (SMAW) with F-5 filler metal was welded on safety related components by an unqualified welder. "Crane Nuclear Quality Assurance Manual, 12th Edition Rev. 2, dated 8/8/16 requires that welder performance qualification shall conform to the requirements of ASME Section IX for processing ASME B&PV Section Ill and safety related valve and valve part orders. During processing of a safety related order, it was identified that one welder was missing the required qualification documentation to perform weld repairs with F-5 filler metals (as defined in ASME Section IX) using the shielded metal arc welding process (SMAW). The safety hazard which could be created by such a defect could be a potential weld failure. "Crane Nuclear has completed a review of all applicable welding records based on the welder hire date of September, 2011. We identified a total of 10 orders that were supplied with welding performed by an unqualified welder. Notification has been made to the purchasers of the affected safety related orders on the same date as this notification. "Should you have any questions regarding this matter, please contact Burt Anderson, Site Leader, at (630) 226-4990, Rosalie Nava, Director of Safety and Quality at (630) 226-4940, or Jason Klein, Engineering Manager at (630) 226-4953." The following facilities received these safety related orders: Duke-McGuire, Exelon-Byron, Duke-Brunswick, Entergy-ANO, Exelon-TMI, Exelon-Quad Cities, Exelon-Dresden. * * * UPDATE AT 2004 EDT ON 9/30/2016 FROM ROSALIE NAVA TO MARK ABRAMOVITZ * * * The following information was received via fax: "This letter is intended to inform the U.S. Nuclear Regulatory Commission of actions taken to complete the Part 21 evaluation on the above referenced item. All of the following actions have been completed: 1) The welder has been qualified on the SMAW process utilizing F-5 filler metal and documented in accordance with ASME Section IX requirements. 2) The affected purchasers were provided with an initial 10CFR21 notification on August 26, 2016. 3) The affected purchasers were provided with the documentation detailing the scope of the welding performed on the affected components. 4) The affected purchasers were provided an investigation summary closure letter. 5) Crane Nuclear, Inc. Corrective Action Report 16-35 generated to determine root cause and implement appropriate corrective actions to prevent recurrence was completed and closed on September 30, 2016. "Should you have any questions regarding this matter, please contact, Rosalie Nava, Director Safety and Quality at (630) 226-4940, or Burt Anderson, Site Leader. at (630) 226-4990." Notified R1DO (Cook), R2DO (Desai), R3DO (Stone), R4DO (Groom), and the Part 21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-08-26
52203 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-08-24 | 2016-08-26 10:34 | 2016-08-26 | AGREEMENT STATE REPORT - DAMAGED SOURCE ROD The following information was received from the Commonwealth of Pennsylvania via facsimile: "Notifications: On August 25, 2016, the Department [Pennsylvania Bureau of Radiation Protection] was notified that a licensee had a cobalt-60 (Co-60) source rod that became bent and unusable during installation into a gauge at a work location. This is reportable per 10 CFR 30.50(b)(2). "Event Description: During the process of installing a Co-60 source rod and moving it from a transfer shield to a gauge and industrial process mold, the licensee observed difficulty in getting the source rod to insert into the mold. Using a remote handling device, the Co-60 source was partially removed from the transfer shield and briefly (about 30 seconds) inspected. It was noted that the rod was partially bent. The rod was immediately retracted into the fully shielded position in the transfer shield. The transfer shield containing the Co-60 rod was then taken to a designated storage area where it is secured from unauthorized access. The calculated dose to the workers was estimated to be 0.44 millirem. No exposures over regulatory limits occurred. "Radionuclide: Co-60; Manufacturer: Berthold Technologies; Source Model: P 2608-100; Gauge Model: LB 300 ML; Source Serial Number: 1766-10-13; Activity: 3.8 milliCuries "ACTIONS: The rod has been securely stored and placed out of service until repairs or return can be accomplished by a licensed service provider. The Department has scheduled a reactive inspection. More information will be provided when available." Pennsylvania Event: PA160024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-09-05
52202 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-08-25 16:29 | 2016-08-25 21:39 | 2016-08-25 | MECHANICAL DRAFT COOLING TOWER DECLARED INOPERABLE "At 1629 EDT on August 25, 2016, it was determined that a Mechanical Draft Cooling Tower (MDCT) fan should be declared inoperable if its associated fan brake is nonfunctional. The MDCT fan brake is required to prevent fan over speed from a design basis tornado. The MDCT fans are required to support the operability of the Ultimate Heat Sink (UHS). Currently, the MDCT fans and fan brakes are operable. A past operability evaluation is being performed and has initially identified that from 0855 EDT to 1738 EDT on April 6, 2016, the Division 1 'A' fan brake was nonfunctional due to a nitrogen bottle being below the required pressure. Additionally, from 0856 EDT on April 6, 2016, to 1641 EDT on April 7, 2016, the Division 1 'C' fan brake was also nonfunctional due to a nitrogen bottle being below the required pressure. Therefore, the Division 1 UHS and associated Emergency Diesel Generators (EDGs) would have been inoperable. During this time, at 1347 EDT on April 6, 2016, the Division 2 EDG 14 was inoperable for 22 seconds for a planned testing. "This resulted in an unanalyzed condition because the plant configuration during the 22 seconds when EDG 14 was inoperable would not support safe shutdown capability in the event of a tornado. A past operability review is in progress to determine if declaring a MDCT fan inoperable due to a fan brake being nonfunctional results in any additional instances of unanalyzed condition within the past three years. This condition is reportable under 10 CFR 50.72(b)(3)(ii)(B), as an event or condition that results in an unanalyzed condition that significantly degrades plant safety. There was no adverse impact to public health and safety or to plant employees. "The NRC Resident Inspector has been notified." | 53 | 0 | 0 | 53 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-08-25
52201 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2016-08-25 15:23 | 2016-08-25 21:11 | 2016-08-25 | UNANALYZED CONDITION INVOLVING POTENTIAL TORNADO MISSILE DAMAGE "On August 25, 2016, Engineering staff were reviewing a proposed modification to install additional internal flooding protection for the Intake Building staircase down to the Raw Water Pump vault. Fort Calhoun Station determined that the existing Intake Building internal flooding and tornado-borne missile analyses did not sufficiently account for the potential of tornado-borne missiles striking Fire Protection piping in the Intake Building. A tornado-borne missile strike could potentially cause a double-ended rupture of Fire Protection piping in the vicinity of the stairwell down to the Raw Water Pump vault, which could cause flooding and subsequent failure of all four Raw Water Pump motors more quickly than bounded by the Engineering Analysis. The Engineering Analysis uses a postulated crack from a Moderate Energy Line Break per USNRC Branch Technical Position MEB 3-1, vice postulating a double ended pipe rupture. The resulting flow rate from this postulated crack is less than that possible from a tornado-borne missile strike. "This condition creates a potential loss of safety function from the Fort Calhoun Station Raw Water System (ultimate heat sink). All four Raw Water Pump motors could potentially become inoperable from flooding caused by a tornado-borne missile impacting the Fire Protection System Piping near the Raw Water vault stairwell prior to operator action to secure both Fire Pumps. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "Interim compensatory measures are to isolate the Fire Protection piping in the vicinity of the Raw Water Pump vault stairwell when severe weather is forecast." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-08-25
52200 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-08-25 08:30 | 2016-08-25 14:29 | 2016-08-25 | AGREEMENT STATE REPORT - TRANSPORTED PACKAGE EXCEEDED CONTAMINATION LIMITS The following was received from the Commonwealth of Pennsylvania: "On August 25, 2016, the Department [Commonwealth of Pennsylvania] was notified by Lancaster General Hospital that a package was received in which 5 of the 6 sides exceeded the contamination limits in 10 CFR 71.47. This is reportable per 10 CFR 20.1906(d)(1). "A package containing a vial of 5 milliCuries of iodine-123 in liquid form was received from GE Healthcare at approximately 0830 [EDT] this morning. The package was undamaged. The receipt survey was performed and noted removable contamination as follows: Front and handle 10,108 dpm; Right side 2,131 dpm; Front handle 4,977 dpm; Front 4,426 dpm; Top background; Top strap 4,577 dpm; Back/bottom 1,997 dpm. "After completing wipe testing, the technologist performed an area survey. The area background was found to be 0.04 mR/hr. At 1 meter, the package was found to be 0.05 mR/hr. At the package surface the reading was found to be 0.4 mR/hr. The contamination identified as technetium-99m. Given this finding, package [was] opened to verify it was I-123. The contamination is believed to have been transferred from somewhere else. Upon return to the originator (GE) pharmacy, a survey of the delivery driver's hands, vehicle, and all packages in the vehicle was performed. None showed contamination. All hospital personnel involved and surrounding areas were surveyed and found to be contamination free. No one received a dose above regulatory limits." Cause of the event is unknown at this time. The Department has an inspector onsite. More information will be provided when available. Event Report ID No: PA160023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-09-02
52199 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-08-24 | 2016-08-24 17:14 | 2016-08-24 | AGREEMENT STATE REPORT - POTENTIAL RADIOGRAPHER OVEREXPOSURE The following report was received from the Texas Department of State Health Services via email: "On August 24, 2016, the licensee reported a potential overexposure of an employee to the Agency [Texas Department of State Health Services]. The licensee reported one of its radiographers had received 5.5 rem on the July monthly monitoring report resulting in a total dose of 6.4 rem for the year. The radiation safety officer [RSO] is investigating the cause of the overexposure although believes the radiographer has not been following procedures. The RSO stated the radiographer is working in an enclosed area and not distancing himself from the source as required when the source is exposed. The RSO will provide a detailed report within the next few days. An update will be sent in accordance of SA300 guidelines." Texas Incident #: I 9426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-09-01
52198 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2016-08-24 13:38 | 2016-08-24 16:55 | 2016-08-24 | REACTOR TRIP DUE AUTOMATIC TURBINE TRIP FROM 100 PERCENT POWER "At 1338 [EDT] on 08/24/2016, a turbine trip, and a subsequent reactor trip occurred. The cause is under investigation. Following the reactor trip, the Auxiliary Feedwater System actuated as expected on low steam generator level. At the time of the trip, the plant was in Mode 1. As of 1643 [EDT], the Plant is in Mode 3. The current RCS [Reactor Coolant System] Temperature is 548 degrees F (Average), and the Steam Generator Levels are in the range of 40 to 45% (normal range) with levels controlled by the Main Feedwater System. All systems and equipment operated as expected. "Due to the automatic actuation of the Reactor Protection System, this event is being reported as a 4 hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B). Due to the valid actuation of Auxiliary Feedwater System, this event is also being reported as an 8 hour Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A)(B)(6). At no time during this occurrence was the public or plant staff at risk as a result of this event. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-08-24
52197 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-08-23 | 2016-08-24 15:47 | 2016-08-24 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the California Department of Public Health via email: "On August 23, 2016, NRC [Nuclear Regulatory Commission] contacted RHB [California Radiation Health Branch] to inform of an incident involving missing Tritium signs. According to NRC report, the AT&T EH&S RSO [Environmental Health and Safety Radiation Safety Officer], Kim Kantner, contacted NRC to report six missing H-3 [Tritium] signs from one of their locations at 730 Carolina Street, Vallejo, CA. Each sign contained 2.7 Ci of H-3. "These six signs were in a box to be returned to the vendor, stored inside a locked basement at the Vallejo AT&T facility. Some renovations were going on at this site. According to Kim, AT&T still believes that the box may have been misplaced by the workers. The investigation is still ongoing. "RHB will be following up on this matter." CA 5010 Number: 082316 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-09-01
52196 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-08-24 13:45 | 2016-08-24 14:42 | 2016-08-24 | DISCOVERED A VULNERABILITY IN A SAFEGUARD SYSTEM The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2016-09-01
52195 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2016-08-24 08:41 | 2016-08-24 12:15 | 2016-08-24 | UNANALYZED CONDITION ASSOCIATED WITH DAMAGING EFFECTS OF TORNADOS "During performance of an extent of condition evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Arkansas Nuclear One, Unit 1, identified non-conforming conditions in the plant design such that specific TS equipment on Unit 1 is considered to not be adequately protected from tornado missiles. The reportable condition is postulated by tornado missiles entering the Unit 1 Cable Spreading Room through penetrating the hollow metal door or potentially from spalling of the block wall separating Room 96 and 97. A tornado could generate multiple missiles capable of striking the Unit 1 Cable Spreading Room and rendering both safety related electrical trains inoperable. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) Shut down the reactor and maintain it in a safe shutdown condition, (B) Remove residual heat, or (D) Mitigate the consequences of an accident. "This condition was identified as part of an on-going extent of condition review of potential tornado missile related site impacts. Licensee Event Report (LER) 50-313/2016-002-00 was recently submitted addressing previously identified tornado missile vulnerabilities at the Unit 1 plant. "Enforcement discretion per Enforcement Guidance Memorandum EGM 15-002 has been implemented and required actions taken. Corrective actions will be documented in a follow-on licensee event report. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2016-08-24
52194 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-23 13:56 | 2016-08-23 15:30 | 2016-08-23 | MANUAL TRIP DUE TO A LOSS OF MAIN FEEDWATER "On August 23, 2016, at 1356 EDT, Watts Bar Nuclear Plant [WBN] Unit 2 reactor was manually tripped due to a loss of main feedwater. "Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All control and shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and main steam dump systems. Unit 2 is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72(b)(2)(iv)(B). "There was no effect on WBN Unit 1. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 43 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-08-23
52193 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-07-13 | 2016-08-22 16:59 | 2016-08-22 | AGREEMENT STATE REPORT - MISADMINISTRATION DURING A THYROID ABLATION PROCEDURE The following was reported by the Colorado Department of Health Radioactive Materials Unit via email: "CDPHE [Colorado Department of Public Health and Environment] became aware of the misadministration on the morning of Monday August 22, 2016. The event was reported to CDPHE on Friday August 19, 2016 at approximately 1630 [CDT] via a message that was left on an office voicemail inbox. "The misadministration occurred during a thyroid ablation procedure on July 13, 2016. The prescribed dose was 75 milliCuries of I-131, and 78 milliCuries was delivered to the patient. The patient became aware that she was pregnant at the time of the procedure and notified St. Mary's Hospital and Medical Center on Tuesday, August 16, 2016. The gestation at time of procedure was estimated to be 9 days post conception. The Hospital's RSO reported an estimated dose to fetus of approximately 20 centiGray. "The patient was given a pregnancy test prior to the procedure and the test results were negative. The licensee is claiming the misadministration was a result of patient non-compliance because the patient was instructed not to have sexual contact prior to the procedure. A written report from the licensee is pending; and will be followed-up by a formal investigation." Colorado Event Identification Number: CO16-I16-17 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-08-30
52192 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-08-21 22:51 | 2016-08-22 06:49 | 2016-09-08 | LOSS OF CONTROL ROOM HVAC "At 2251 EDT on 8/21/2016, the 'A' Train of Control Room ventilation was inoperable for scheduled testing and the 'B' Train of Control Room ventilation was declared inoperable due to a thermal overload of a cooling fan. This resulted in not meeting the limiting condition for operation in accordance with Technical Specification 3.7.6. No action statement exists for having two trains of Control Room Ventilation inoperable and Technical Specification 3.0.3 was applied. At 2255 on 8/21/2016 the 'A' Train of Control Room Ventilation was declared operable and Technical Specification 3.0.3 was exited. "The licensee notified the NRC Resident Inspector." * * * UPDATE AT 1355 EDT ON 09/08/16 FROM CHUCK YARLEY TO S. SANDIN * * * "Event notification 52192 is being retracted. Upon further evaluation, Harris determined that the 'A' train of Control Room Emergency Filtration was Operable at the time 'B' train became Inoperable. Therefore, there was no loss of safety function. "The NRC Resident Inspector has been informed of this retraction." Notified R2DO (Rose). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-08-22
52191 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2016-08-21 19:37 | 2016-08-21 20:14 | 2016-08-22 | UNUSUAL EVENT - LOSS OF OFFSITE POWER At 35 percent power, a main generator lockout caused the main generator to trip, resulting in a reactor trip of Unit 1. Because of the lockout, power did not transfer to the startup transformers. Both emergency diesel generators started and aligned to the emergency busses. During the trip all control rods fully inserted and no safety or relief valves lifted. The plant is in Mode 3 steaming through the atmospheric relief valves and feeding the steam generators using auxiliary feedwater. There is no reported primary to secondary leakage. Primary coolant is being moved using natural circulation cooling. The trip of Unit 1 had no effect on Unit 2. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC, and Nuclear SSA (via e-mail). * * * UPDATE AT 2140 EDT ON 08/21/2016 FROM GREG KRAUTZ TO MARK ABRAMOVITZ * * * The Unusual Event was terminated at 2125 EDT after the plant restored normal offsite power. The licensee notified the NRC Resident Inspector. Notified the R2DO (Sandal), IRD (Gott), NRR EO (Miller), DHS SWO, FEMA, DHS NICC, and Nuclear SSA (via e-mail). * * * UPDATE AT 2315 EDT ON 08/21/2016 FROM ANDREW TEREZAKIS TO MARK ABRAMOVITZ * * * "On August 21, 2016 at 1926 EDT, St. Lucie Unit 1 experienced a reactor trip and a loss of offsite power due to a main generator inadvertent Energization Lockout Relay actuation. The cause of the lockout is currently under investigation. Coincident with the loss of offsite power, the four reactor coolant pumps deenergized. Both the 1A and 1B Emergency Diesel Generators started on demand and powered the safety related AC buses. All CEAs [Control Element Assemblies] fully inserted into the core. Offsite power to the switchyard remained available during the event, and at 2036, restoration of offsite power to St. Lucie Unit 1 was completed. Decay heat removal is being accomplished through natural circulation with stable conditions from Auxiliary Feedwater and Atmospheric Dump Valves. Currently maintaining pressurizer pressure at 1850 psia and Reactor Coolant System temperature at 532 degrees F. "St. Lucie Unit 2 was unaffected and remains in Mode 1 at 100% power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip and 10 CFR 50.72(b)(3)(iv)(A) for the Specified System Actuation." The licensee notified the NRC Resident Inspector. Notified the R2DO (Sandal). * * * UPDATE AT 0048 EDT ON 08/22/2016 FROM ANDREW TEREZAKIS TO DANIEL MILLS * * * "On August 21, 2016 at 2330 EDT, St. Lucie Unit 1 started two Reactor Coolant Pumps to establish Forced Circulation in order to enhance Decay Heat removal. Plant conditions remain stable with Auxiliary Feedwater and Atmospheric Dump Valves in service. "This report is submitted in accordance with 10 CFR 50.72(c)(2)(ii) as a follow up notification of protective measures taken." The licensee notified the NRC Resident Inspector. Notified the R2DO (Sandal). | 0 | 0 | 0 | 35 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-08-21
52190 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-08-17 17:39 | 2016-08-18 16:32 | 2016-08-18 | FAILURE OF A SPEAKER IN AN AREA POTENTIALLY REQUIRING PERSONNEL EVACUATION "On August 17, 2016 at approximately 1739 hours (EDT), one speaker in Building 120 was identified as non-operational while performing a functional test of the system. This speaker is designed to annunciate alarms generated from the Criticality Accident Alarm System (CAAS) required by 10CFR70.24, alarms generated from the Fire Alarm Control Panel, and Public Address System announcements. Additional functional testing identified that no redundant speaker could adequately provide speaker coverage for all affected areas of this building. Special Nuclear Materials are not processed, handled, or stored within the area where the speaker failed; however, this area requires evacuation in the unlikely event of a nuclear criticality accident as described in the NFS Emergency Plan. There were no actual radiological or other nuclear safety consequences. The potential consequence was that in the event of a nuclear criticality accident, evacuation could have been delayed for those personnel within Building 120 with a resultant increase of postulated doses. A series of compensatory actions were taken to restore compliance including installation of a temporary speaker and limiting equipment operation to limit background noise. On August 18, 2016, at approximately 1100 hours (EDT), full compliance was restored as demonstrated by successfully performing a speaker test in the affected area. "The licensee notified the NRC Resident Inspector on August 18, 2016." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2016-08-26
52189 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2016-08-11 | 2016-08-18 13:23 | 2016-08-18 | AGREEMENT STATE REPORT - TWO MOISTURE-DENSITY GAUGES STOLEN "On August 11, 2016 at 1240 [PDT], it was reported to the State of Nevada, Radiation Control Program (RCP) that two Troxler model 3440, Serial No. 24693 and model 3430, Serial No. 31409 portable gauges had been stolen from a storage location in Las Vegas, Nevada. The storage location is in a residential location. The RSO [Radiation Safety Officer] reported that at 0800 he removed the gauges from storage for routine maintenance. The gauges were in the lab with the door open and not secured or under surveillance for approximately three hours. When he returned the gauges were missing, no other equipment was missing. The RSO is the only employee. The Las Vegas Metropolitan Police, ARMOR division went to the storage address and took a police report. The RCP is following the incident and working with local authorities to recover the missing/stolen portable gauges. Follow-up information will be provide to the NRC as it becomes available. A press release was dispersed through law enforcement and the media." Troxler 3440: 40 mCi Am-241 and 8 mCi Cs-137 Troxler 3430: 40 mCi Am-241 and 8 mCi Cs-137 NMED NV160013 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2016-08-26
52188 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2016-08-17 18:26 | 2016-08-17 21:30 | 2016-08-17 | OFFSITE POWER SOURCE BELOW THE OPERABILITY LIMIT "At 1826 [CDT], Operators identified that off-site 161 kV power source predicted post-trip voltage was below the operability limit of 161.3 kV. [Operators] entered AOP-31, 161 kV Grid Malfunctions, Section 1, 161 kV Grid Instability, and declared House Service Transformers T1A-3 and T1A-4 inoperable. [Operators] entered Technical Specification 2.7(2)c. Per Technical Specification 2.7(2)c, 'Both house service transformers T1A-3 and T1A-4 (4.16kV) may be inoperable for up to 72 hours. The loss of the 161kV incoming line renders both transformers inoperable. The NRC Operations Center shall be notified by telephone within 4 hours after inoperability of both transformers.' "Per OPPD [Omaha Public Power District] Transmission, grid conditions are currently stable. OPPD Transmission has successfully raised predicted post-trip 161 kV voltage with all predicted voltages meeting or exceeding operability requirement of 161.3 kV as of 1834. Current post-trip predicted voltage is 162.2 kV as of 2029. "Lowest observed actual voltage was 163.7 kV. The 161 kV line and transformers T1A-3 and T1A-4 remained available at all times." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2016-08-17
52187 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-17 17:22 | 2016-08-17 17:46 | 2016-08-17 | UNANALYZED CONDITION DUE TO NOT MEETING SINGLE FAILURE CRITERIA "At 1722 [EDT] on 8/17/16, a Past Operability Evaluation (POE) determined the configuration of the Emergency Gas Treatment System (EGTS) flow controllers that existed prior to 0420 on 8/6/16 constituted an Unanalyzed Condition due to not meeting single failure criteria. This POE examined the condition where EGTS may auto-swap from the flow control path in A-Auto to the Standby flow control path upon the start of a Design Basis Event (DBE). The intended design of the EGTS swap over flow control path in Auto to Standby was to detect and respond to an actual failure of the A-Auto flow control path. The unnecessary auto-swap to Standby could prevent the EGTS train configured in Auto from performing its required safety function during a DBE. The POE performed a detailed calculation to determine the release effects due to the failure of the redundant trains of EGTS controllers. These calculations concluded that failure of both trains of EGTS controllers would not result in exceeding the 10CFR100 limits, however this condition was unanalyzed and failed to meet single failure criteria. "This condition is reportable under 10CFR50.72(b)(3)(ii)(B), Unanalyzed Condition due to a system required to meet the single failure criterion does not do so. "This condition had no impact to the health and safety of the public. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-08-17
52186 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-08-15 21:00 | 2016-08-16 15:49 | 2016-09-14 | AGREEMENT STATE REPORT - DAMAGED FIXED GAUGE The following information was received from the State of New Jersey by email: "Event Narrative: During a walkthrough of the facility, the night shift RSO [Radiation Safety Officer] discovered that an ABB Industrial Systems, Ltd model LS100 fixed measuring gauge had fallen off of a coal feeder to which it was attached. The area, which is not normally accessed by staff, was cordoned. Readings were taken directly on top of the device, and measured 0.5 to 1.0 mR/h. The device does not have a shutter mechanism. The direct beam was surrounded with lead that was available for shielding. "Root cause(s) and contributing factors: Vibration from coal feeder caused the metal mounting bracket to shear. Semiannual preventative maintenance did not identify the issue. Scaffolding is required to reach the gauge for maintenance, which makes it difficult to do more regularly. "Isotope and activity; manufacturer, model and serial number: Ra-226, 0.5 mCi, ABB Industrial Systems, Ltd model LS100, serial number R868." New Jersey Incident Number: C612607 * * * UPDATE FROM JOE POWER TO STEVEN VITTO AT 1357 EDT ON 09/14/2016 * * * The following was received from the State of New Jersey via email: "On September 14, 2016, a 30-day written report from BL England Generating Station was received by NJDEP [New Jersey Department of Environmental Protection]. This report outlined the corrective actions and the current status of the gauge. As a corrective step, BL England updated their maintenance schedule to include more frequent checks of their gauges. The device has been secured on a lead plate, and staged in a labeled 55-gallon steel drum to be disposed of at a later date when disposal of other site sources is scheduled. It will remain in storage under lock and key until that time. The licensee's next inspection will include a review of the implanted changes. "This incident can be closed." NMED incident Number: 160359. Notified R1DO(Noggle) and NMSS Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-08-24
52185 | 0 | NIST |  |  |  |  | 2016-08-15 16:15 | 2016-08-16 15:50 | 2016-08-16 | IRRADIATOR SAFETY EQUIPMENT FAILURE The NIST (National Institute of Standards and Technology) irradiator has several Cs-137 sources used to calibrate instruments. During a calibration process, a 3.6 Ci source did not return to its shielded position. The event occurred in a portion of the building where such events are expected, therefore there were no health or safety consequences to employees, public or the environment. Licensee corrective actions include manually installing a lead plug into the beam port (opening) of the irradiator. The licensee is contacting the manufacturer in order to assist with troubleshooting and repairs. The irradiator (Model 81-12; JL Shepherd; S/N 7132) is currently in a safe and stable configuration. It is noted that the irradiator is NOT a Part 36 irradiator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 70.50(b)(2) |  |  |  | 0 | 2016-08-24
52184 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2016-08-16 11:00 | 2016-08-16 15:43 | 2016-08-16 | FAILURE OF ALL EMERGENCY SIRENS "On 8/16/2016, while operating at 100% in Mode 1, routine testing of the off-site sirens for Wolf Creek was scheduled. The county dispatcher was unable to actuate any sirens. The dispatch supervisor was contacted to ensure there was not a personnel qualification issue. Both the dispatcher and the supervisor were unable to actuate any sirens, either manually or using the normal computer controls. "Coffey county personnel, assisted by Wolf Creek personnel, determined that a battery had failed causing a fuse to blow and de-energizing the equipment needed to actuate the sirens. The battery has been replaced, the fuse has been replaced, and the system has been tested satisfactorily. The emergency sirens were restored to service at 12:20 CDT 8/16/2016. "NRC resident has been notified. "No plant systems were affected by this failure of notification equipment. "The plant remained at 100% power Mode 1 throughout this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-08-16
52183 | 0 | ZION |  |  |  | ISFSI | 2016-08-15 15:20 | 2016-08-16 09:14 | 2016-08-17 | OFFSITE NOTIFICATION "On 8/12/16 at 1356 CDT, an ISFSI security officer noticed that two male children were walking west on the railroad tracks on the south end of the OCA, approximately 50 yards onto the property. The children appeared to be between 7 and 10 years of age. The children, presumably upon noticing Security's presence, then ran northeast and back towards the beach fence line. It appeared that the children somehow left the property through the east fence line back onto the beach. Industrial Security and shift RP tech began vehicle and foot patrols to search for the children and ensure that they did, in fact, leave the property. The children were not seen again. "In accordance with 49 CFR 1580.105 - Reporting Significant Security Concerns, at 1520 on 8/15/16, the Radioactive Waste Group supervisor contacted the designated Transportation Safety Administration inspector to discuss the trespassing incident from 8/12/16. After the discussion with the inspector, the Radwaste supervisor was informed to contact the Department of Homeland Security Freedom Center and provide details of the incident. This contact was made at 1540 on 8/15/16. "The notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) notification to offsite government agency." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OFFSITE NOTIFICATION | [9 empty] | NON EMERGENCY | 3 | IL | ISF |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-08-17
52182 | 0 | KNIK CONSTRUCTION |  |  |  |  | 2016-08-15 16:30 | 2016-08-15 21:13 | 2016-08-16 | DAMAGED MOISTURE DENSITY GAUGE While at a construction jobsite at Kenai Airport, a technician using a Troxler moisture density gauge observed a large equipment grader approaching in reverse mode. The technician retreated from the area and the gauge was run over by the grader. Personnel roped off the damaged gauge area and proceeded to monitor for any contamination. The gauge is a Troxler, Model 3440; S/N 37310; Sources: Cs-137 (8 mCi) and Am-241/Be (44 mCi). * * * UPDATE FROM ERYN JONES TO VINCE KLCO ON 8/16/2016 AT 1348 EDT * * * The licensee placed the damaged gauge into an over pack container loaded with sand and transported the damaged gauge to a local office permanent storage facility. The storage area is barricaded and is being monitored. The licensee is consulting with the manufacturer for final damaged gauge disposition. Notified the R4DO (Proulx) and NMSS Events via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-08-23
52181 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-08-15 15:52 | 2016-08-15 17:48 | 2016-08-15 | SALT SERVICE WATER SYSTEM DECLARED INOPERABLE "On Monday, August 15, 2016 at 1552 [EDT], with the reactor at [about] 70 percent core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) entered a 24-hour shutdown Limiting Condition for Operation Action Statement (LCO-AS) for Salt Service Water (SSW) inlet temperature exceeding the Technical Specification (TS) limit in TS 3.5.B.4. The LCO-AS was subsequently exited at 1651 hours when the temperature of SSW trended to below the TS limit. "Under certain design conditions, the SSW system is required to provide cooling water to various heat exchangers such as the Reactor Building Closed Cooling Water (RBCCW) and Turbine Building Closed Cooling Water (TBCCW) systems. When the inlet temperature to these supplied loads exceeds the 75 degrees F limit established in the TS, the SSW system is conservatively declared inoperable until the temperature trends below this value. This condition existed for approximately 60 minutes. "The SSW temperature is being closely monitored and trended on a continuous basis. "This event has no impact on the health and safety of the public. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(B) and 10 CFR 50.72(b)(3)(v)(D) due to an event or condition that could have prevented fulfillment of a safety function. "The licensee will be notifying the Commonwealth of Massachusetts Emergency Management Agency." | 62 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-08-15
52180 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-15 10:30 | 2016-08-15 15:32 | 2016-08-15 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO FACILITY UPGRADE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. "The Technical Support Center (TSC) was removed from service on 08/15/2016 at 1030 [EDT] for a scheduled facility upgrade project, which will improve the overall functionality of the facility. The duration of the upgrade is expected to be 26 days. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii), as the TSC will be unavailable for greater than 72 hours. "In the event of an emergency, McGuire's alternate TSC will be used while the TSC is upgraded. During this period, the alternate TSC will be staffed and activated using existing emergency planning procedures. "The Emergency Response Organization team has been notified that the TSC will be unavailable during the upgrade and to report to the alternate TSC in the event of an emergency. This upgrade does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-08-15
52179 | 0 | WATERFORD | 3 |  |  | [3] CE | 2016-08-12 17:04 | 2016-08-15 14:10 | 2016-08-15 | LOSS OF BOTH LOOPS OF ESSENTIAL SERVICES CHILLED WATER "This is a non-emergency notification from Waterford 3. On August 12, 2016, at 1704 CDT, the shift operating crew entered Technical Specification (TS) 3.0.3 due to both trains of Essential Services Chilled Water being inoperable. Essential Services Chilled Water Loop A had previously been declared inoperable for maintenance on August 11, 2016. On August 12, 2016, at 1704, the shift operating crew noted that Loop B Essential Services Chilled Water outlet temperature exceeded the allowed TS limit of 42 degrees Fahrenheit. Essential Chiller AB was subsequently aligned to Loop B and TS 3.0.3 was exited on August 12, 2016 at 1802 when outlet temperature was verified less than or equal to 42 degrees Fahrenheit. "On August 15, 2016, subsequent review of this event determined that this event was reportable under 10 CFR 50.72(b)(3)(v)(D), 'event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to (D) mitigate the consequences of an accident' due to both Essential Services Chilled Water Loops being inoperable. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-08-15
52178 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2016-08-13 23:59 | 2016-08-14 01:59 | 2016-08-14 | UNUSUAL EVENT DECLARED DUE TO EXCESSIVE REACTOR COOLANT SYSTEM LEAKAGE Prairie Island Unit 1 declared an Unusual Event at 2359 CDT on 8/13/2016 based on Reactor Coolant System (RCS) identified leakage being greater than 25 gpm. The RCS leakage was 40 gpm for three (3) minutes. The RCS leakage was stopped when letdown flow was isolated. Minimum charging flow has been established and Excess Letdown was placed in service. Prairie Island Unit 1 is currently stable and continues to operate at 100 percent power. There was no impact on Prairie Island Unit 2. "CV-31339 (Letdown Line Containment Isolation Valve) failed closed. VC-26-1 (Regenerative Heat Exchanger Letdown Line Outlet Relief to Pressurizer Relief Tank [PRT]) lifted with 40 gallons per minute to the PRT for three (3) Minutes. Operators entered procedure 1C12.1 AOP3, Loss of Letdown Flow to VCT. Letdown was isolated per 1C12.1 AOP3, relief valve VC-26-1 reseated and leakage to the PRT stopped. Charging flow was reduced to one (1) charging pump at minimum speed (16 GPM). Excess letdown was placed in service to maintain pressurizer level between 32 - 34 percent. The cause for CV-31339 closing has not yet been determined. "The NRC Resident Inspector has been notified." Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. * * * UPDATE FROM PAUL FINHOLM TO DONALD NORWOOD AT 0525 EDT ON 8/14/2016 * * * "At 0329 CDT the Notice of Unusual Event was terminated based on confirmation that conditions meet all termination criteria. RCS conditions are stable. RCS leakage is less than Technical Specification limits. The current value [of RCS identified leakage] is 0.038 gpm. No classification criteria is currently met. "The NRC Resident Inspector has been notified." Notified R3DO (Kozak), NRR EO (Miller), and IRD (Stapleton). Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-08-14
52177 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-13 03:36 | 2016-08-13 08:51 | 2016-08-13 | AUTOMATIC START OF TURBINE DRIVEN AUXILIARY FEED WATER PUMP "On August 13, 2016 at 0330 EDT, Watts Bar Nuclear Plant Unit 2 (WBN2) was being stabilized following a pre-planned reactor trip. Both motor driven auxiliary feed water pumps and the turbine driven auxiliary feed water pump (TDAFW pump) were in operation maintaining steam generator water level 6 - 50 percent in accordance with the Reactor Trip Response Procedure. "At 0333 EDT the TDAFW pump was secured by procedure and steam generator water level lowered to the Low Low Alarm setpoint (17 percent). The trip time delay at 0 percent power is three (3) minutes. At 0336 EDT, the TDAFW pump automatically started with steam generator water levels less than the Low Low alarm setpoint (lowest level reached was 15 percent). "Steam generator water level was restored to the normal shutdown control band (38 percent). "Unit 1 remains in Mode 1 at 85 percent. "Unit 2 is stable in Mode 3 with normal shutdown power alignment. The reactor coolant system is being cooled down to 400 degrees F for a planned maintenance period, with decay heat removal via the Main Condenser Steam dumps and the AFW system. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(iv)(A). "TVA has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-08-13
52176 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2016-08-11 10:00 | 2016-08-12 14:53 | 2016-08-12 | AGREEMENT STATE REPORT - UNDERADMINISTRATION OF Y-90 MICROSPHERES The following was received from State of Maryland via email: "Greater than 20 percent underadministration of the prescribed activity was administered to the left lobe of the patient's liver. Underadministration may have been up to 60 percent less than the prescribed written activity (preliminary estimate). Prescribed written directive activity to left lobe of liver was 25 mCi. Preliminary assessment of administered activity is 14 mCi. Radioactive material ended up in the patient catheter, chucks, and on the floor. All areas were cleaned and evaluated by the licensee. The licensee states that both the patient and referring doctor have been notified of the event. The licensee has history of many successful therapies of this type. The licensee is investigating the event, but has not yet determined a root cause. The licensee is sending a detailed written report to the State." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2016-08-22
52175 | -1 | DTE ENERGY |  |  |  |  | 2016-08-11 18:20 | 2016-08-11 22:15 | 2016-08-12 | FIRE AT LICENSEE FACILITY At approximately 1820 EDT on 8/11/16, St. Clair Power Plant, a coal-fired generation unit, caught fire in East China Township, Michigan. The Radiation Safety Officer (RSO) reported that 22 nuclear gauges (Texas Nuclear Model 5181, 5193, 5180A, 5192 and Ohmart Model SHGS-2, SH-100, SR-A) are used at the site which all contain Cs-137. The RSO will conduct an assessment of all the nuclear gauges on 08/12/16. * * * RETRACTION AT 2127 EDT ON 08/12/16 FROM ROBERT TOZZIE TO JEFF HERRERA * * * "On 8/11/16 at approximately 1820 EDT, the DTE Energy St. Clair Power Plant experienced a mechanical failure in the Unit 7 Turbine that resulted in a fire. The DTE Energy Radiation Safety Officer conservatively made an immediate report (within 4 hours) to the NRC on 8/11/16 at 2215 EDT based on the immediate reporting requirements of 10 CFR 30.50(a) due to, at the time, unknown conditions of nuclear gauges located in the area of the fire. The nuclear gauges are used for level measurement purposes. "On 8/12/16, the DTE Energy Radiation Safety Officer completed an assessment of all nuclear gauges associated with the unit 7 fire. No gauges were found damaged or compromised. All unit 7 gauges were visually inspected with no structural damage identified. Radiological surveys were performed on all unit 7 gauges. Results of the radiological surveys showed normally expected dose rates and no loose surface contamination. Shutter mechanisms were closed and locked closed on all gauges in unit 7. Nuclear gauges in other units of the St. Clair Power Plant were not impacted by the fire event. These gauges were visually inspected and no signs of damage were identified. Based on the results of this assessment, DTE Energy retracts notification 52175." Notified R3DO (Kozak) and NMSS Events Notification (via E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PROTECTIVE ACTION PREVENTED | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(a) |  |  |  | 0 | 2016-08-19
52174 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2016-08-11 15:05 | 2016-08-11 18:41 | 2016-08-11 | ROBINSON DAM TAINTER GATES UNANALYZED CONDITION "During testing it was discovered that the H. B. Robinson Steam Electric Plant, Unit 2 (RNP) Lake Robinson Dam Tainter Gates A and B were in degraded condition. The Tainter Gates are non-technical specification features of design that control Lake Robinson water level. RNP was not able to achieve full opening of the Tainter Gates. Subsequent analysis has concluded that the degraded condition of the Tainter Gates adversely impacts their UFSAR credited safety function. On 8/11/2016, at 1505 EDT, it was determined this places RNP in an unanalyzed condition that significantly degrades plant safety [per] 10 CFR 50.72 (b)(3)(ii)(B). The Tainter Gates have been repaired, tested and rendered complaint with their original licensing basis function. The current plant status does not pose undue risk to the health and safety of the public. "The NRC Senior Resident Inspector has been notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-08-11
52173 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-08-11 15:45 | 2016-08-11 17:37 | 2016-08-11 | AGREEMENT STATE REPORT - MISSING GAUGE WITH 100 MILLICURIE CO-60 SOURCE The following report was received from the Tennessee Department of Environment and Conservation Division of Radiological Health via email: "Licensee reported that a gauge with a 100 mCi Co-60 source was missing from a shipment with a carrier. Licensee accounted for the source upon leaving the licensee's facility. Licensee states that source is still in carrier's warehouse in Knoxville, TN, or in route to another site in Louisiana. Licensee is investigating warehouse and transport. A follow-up report will be sent upon receiving further information; this will include model number, activity, and shipping information." TN State Event Report ID No.: TN-16-111 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-08-19
52172 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-11 10:15 | 2016-08-11 16:35 | 2016-08-11 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM DECLARED INOPERABLE "At 1015 [EDT] on August 11, 2016, it was discovered that a Fire Protection damper associated with the Control Room Emergency Ventilation System had closed unexpectedly due to component failure. The closure rendered both trains of the Control Room Emergency Ventilation System (CREVS) inoperable requiring both Unit 1 and 2 to enter Technical Specification Limiting Condition of Operation (LCO) 3.7.10 Condition G. Condition G requires immediate entry into LCO 3.0.3. At 1159 on August 11, 2016, actions were taken to block the deficient damper in the open position restoring both trains of CREVS to a fully operable condition and allowing exit of LCO 3.0.3 and 3.7.10 Condition G. "The purpose of CREVS is to provide a protected environment from which occupants can control the [respective] unit following an uncontrolled release of radioactivity, hazardous chemicals, or smoke. In the event of a design basis accident, emergency ventilation components realign to supply filtered air and to pressurize the Control Room Envelop (CRE). While the damper was closed both trains of CREVS were incapable of supplying the Relay Room as well as the Technical Support Center and its associated support spaces. These locations constitute part of the CRE, therefore both trains of CREVS were inoperable. "Both trains of CREVS being inoperable affected the habitability of the TSC where the assessment capability of the facility for all emergencies was adversely effected. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(xiii) |  |  | 0 | 2016-08-11
52171 | 0 | TEXAS COMMISSION ON ENV QUALITY |  |  |  |  | 2016-08-09 16:14 | 2016-08-11 15:56 | 2016-08-11 | AGREEMENT STATE REPORT - UNPLANNED FIRE WITHIN LICENSE AREA The following is an excerpt from a report received from the Texas Commission on Environmental Quality via email: "A fire occurred within the Mestena Uranium LLC License Area in the vicinity of PAA-3 on August 9, 2016. The fire was discovered at approximately 1545 CDT by US Border Patrol agents who were conducting activities in the vicinity. Mestena personnel discovered the fire at about the same and upon investigation determined the fire required additional support at which time the local fire department was notified and arrived on site at approximately 1620 CDT to battle the fire. "Fire crews declared the fire out/controlled by 2000 [CDT]. No injuries occurred during the firefighting activities. "[The licensee] contacted [The Texas Commission on Environmental Quality] by telephone at approximately 2110 [CDT] to inform [them] that the fire was declared out and that an investigation into the fire will be initiated which will include follow-up actions required to remediate any impacts caused by the fire. "The fire burned approximately 60 acres, most of which was within the PAA-3 Mine Area. The fire damaged or destroyed surface infrastructure associated with the in-situ mining activities permitted under UIC permit UR03060PA3. "As a precaution, high volume air samples were collected while the firefighting was occurring. Samples were collected from downwind locations along the perimeter of the fire zone. Additional samples were collected on August 10th . Bioassay samples were also collected from individuals who participated in the firefighting activities. "A written report that conforms to 30 TAC 336.335(c)(2) will be submitted to TCEQ [Texas Commission on Environmental Quality] within 30 days." Texas State Event Report ID No.: Not assigned yet | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-08-19
52170 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-08-10 | 2016-08-11 15:04 | 2016-09-13 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER COULD NOT BE OPERATED The following report was received from the Texas Department of State Health Services via email: "On August 11, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee that during a routine annual inspection, the shutter on an Ohmart Vega SH-F1 nuclear gauge could not be operated. The gauge contains a 15 millicurie (original activity) source. The shutter's operating handle no longer operates the shutter. It is in the open position which is the normal operating position for the shutter. A service company is on site and will try to repair the gauge. The gauge is mounted on the top of a tall vessel and does not present an exposure hazard to the licensee's workers or members of the general public. This event is similar to EN 52167. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I9425 * * * UPDATE FROM ART TUCKER TO STEVEN VITTO AT 1744 EDT on 09/13/16 * * * The following report was received from the Texas Department of State Health Services via email: "The licensee reported the activity of the source was 50 milliCuries and not 15 milliCuries as initially reported. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Azua) and NMSS Events Resource via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-08-19
52169 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2016-08-11 09:59 | 2016-08-11 11:09 | 2016-08-11 | MANUAL REACTOR TRIP DUE TO LOSS OF TWO CIRCULATING WATER PUMPS Reactor operators manually tripped the reactor due to the loss of two out of four circulating water pumps which caused a drop in condenser vacuum. The trip was uncomplicated. The reactor is shutdown and stable with decay heat removal via steam dumps to the condenser. The cause of the circulating water pump trips is currently unknown, but initial indications are that the pumps tripped due to a lightning strike that caused an electrical perturbation. The reactor will remain shutdown while the licensee investigates the cause. Unit 3 was not affected. The licensee notified the NRC Resident Inspector and the State and Local governments. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-08-11
52168 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-07-26 13:30 | 2016-08-10 18:35 | 2016-08-10 | AGREEMENT STATE REPORT - STOLEN CHECK SOURCES The following was received from the State of California via email: "On July 28, 2016, [the Radiation Safety Officer] RSO at CB&I contacted RHB [Radiologic Health Branch] to report an incident on stolen check sources from their storage location at Hunters Point in San Francisco, CA. Theft occurred in the afternoon of July 26, 2016, between approximately 1330-1400 hours, while CB&I personnel were conducting business in adjacent project trailers. Items stolen included tools, equipment and locked posted radioactive check source safe. No other radioactive materials were stored inside this trailer. "Source description is as follows: Source Date S/N Activity (uCi) Th-230 Plate Jul-92 92TH1002842 0.0061 Th-230 Disk Nov-09 G4-791 0.01566 Tc-99 Disk Nov-09 G4-797 0.03111 Tc-99 Plate Nov-09 G4-788 0.01648 Cs-137 Button Jan-16 216 10 Cs-137 Button Aug-91 1065/91 9.9 Co-60 Metal Nut Unknown Unknown 0.624 "Note: (only Th-230, 0.01566 uCi exceeds 10X Appendix C value)" CA 5010 Number: 072816 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-08-18
52167 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-08-09 | 2016-08-10 16:15 | 2016-08-10 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE STUCK SHUTTER The following was received from the State of Texas via email: "On August 10, 2016, The Agency [Texas Department of State Health Services] was notified by the licensee that during a daily inspection, the shutter on an Ohmart Vega SH-F1 nuclear gauge could not be operated. The gauge contains a 10 millicurie (original activity) source. The shutter is operated by an pneumatic operator. The operating mechanism is located inside a steel box to help prevent foreign material from interfering with the shutter operation. It appears that over time, moisture was being trapped in the box causing the operating rod connecting pin to rust and break. The shutter cannot be moved. It is in the open position which is the normal operating position for the shutter. A service company has been contacted and will be on-site on August 11, 2016, to repair the gauge. The gauge does not present an exposure hazard to the licensee's workers or members of the general public. Addition information will be provided as it is received in accordance with SA-300." Texas Incident #: I9424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-08-18
52165 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-08-08 | 2016-08-10 11:28 | 2016-08-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the Commonwealth of Pennsylvania via email: "On August 10, 2016, the Department [Pennsylvania Bureau of Radiation Protection] was notified by Testing Services, Inc. that a moisture/density gauge had been damaged while on location at a temporary job site. It is reportable per 10 CFR 30.50(b)(2). "While at a temporary job site, a Humboldt Model 5001 gauge was damaged and became unusable after being run over by a compactor. A survey of the gauge indicated that the source was still in its shielded position. A leak test sample has been taken and sent for analysis and the gauge has been removed from service and secured. No over exposures have occurred. A service provider has been contacted to see if repairs are possible or if the gauge will be returned to the manufacturer. "Radionuclides: Cs-137 and Am-241:Be Manufacturer: Humboldt Model: 5001 Serial Number: 2394 Activity: 11 mCi Cs-137, 44 mCi Am-241:Be "The gauge has been securely stored and placed out of service until repairs/return can be accomplished. The Department has scheduled a reactive inspection. More information will be provided when available." PA report # PA160022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-08-18
52164 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2016-08-04 | 2016-08-09 18:41 | 2016-08-09 | AGREEMENT STATE REPORT - MISSING TRITIUM (H-3) EXIT SIGN The following was received from the State of Utah via email: "On July 19, 2016, the licensee [University of Utah] was performing a 6-month inventory of the H-3 exit signs, when the individual performing the inventory noticed that one of the signs was missing. The licensee left a message with the University's facilities management office to see if the sign was removed by them. On August 4, 2016, the licensee was informed by the [facilities] management group that they had not removed the sign. The licensee then determined that the sign was missing and presumed stolen. The licensee notified the DWMRC [Division of Waste Management and Radiation Control] of the missing sign on August 9, 2016. The licensee will continue to investigate the incident, and will submit a written report to the DWMRC. The DWMRC will possibly perform an investigation on August 10, 2016. "Manufacturer: Safety Lite Corporation "Model: unknown "Serial #: 025297 "Activity on manufacture date: 20 Ci of H-3" Utah Event Report Number: UT160003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2016-08-17
52163 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-09 14:15 | 2016-08-09 16:58 | 2016-08-09 | OFFSITE NOTIFICATION DUE TO OIL SHEEN IN COOLING TOWER BASIN "On 8/09/2016 at 1415 EDT, TVA [Tennessee Valley Authority] notified the National Response Center that Watts Bar Nuclear [WBN] Plant has noted an oil sheen in the Unit 2 Cooling Tower Basin. An oil sheen was observed within the Unit 2 Cooling Tower Basin at WBN. The sheen did not cover the entire cooling tower basin. The sheen covered approximately 4 square feet. No oil sheen was visible in the yard holding ponds or Tennessee river from the bank above the diffuser pipes. Notifications were also made to TEMA [Tennessee Emergency Management Agency]. Oil levels from the suspected source did not indicate any change in oil reservoir levels. "Unit 1 remains in Mode 1 at 85 [percent] power - reduced power due to main condenser back pressure limits. Unit 2 remains in Mode 1 at 25 [percent] power - initial startup testing. "This event is reportable under 10 CFR 50.72(b)(2)(xi) as a condition that was reported to an outside Government Agency. "The NRC Resident Inspector has been notified." | 85 | 25 | 0 | 85 | 25 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-08-09
52162 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2016-08-08 10:45 | 2016-08-08 20:31 | 2016-08-08 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSEE CONTRACT SUPERVISOR "At 1045 EDT, on August 8, 2016, it was determined that a non-licensee contract supervisor had failed to provide a urinalysis specimen for a random test and the medical explanation was not sufficient. It was ruled a refusal by the Medical Review Officer. "The individual's access has been permanently denied. This is reportable under 10 CFR26.719(b)(2)(ii). "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2016-08-08
52160 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-08-08 | 2016-08-08 16:32 | 2016-08-08 | AGREEMENT STATE REPORT: LOST IODINE-125 SEEDS The following was received from the State of Illinois via email: "The radiation safety officer, (RSO) at GE Health, called to advise that two identical packages of I-125 seeds which had been given to [common carrier] to deliver to Athens, Greece had not reached their destination by the desired date. The packages are the typical 'shoebox' size of 11x7x10 inches of 'excepted package - limited quantity'. Both contain 15 seeds with 6.5 milliCi (actual) in each box for a total of 13 milliCi calibrated for Friday 7/29/16 at noon. The RSO has been in touch with [common carrier] since the July 26, 2016 when GE's customer service became concerned while routinely performing package tracking. [Common carrier] last had positive tracking for these packages in Newark, NJ on the 23rd. [Common carrier] is still conducting visual surveys in Newark and Athens in an attempt to locate the boxes and has no evidence to indicate the materials have been delivered to an outside entity. Surveys conducted at O'Hare Airport in Chicago were negative. [Common carrier] reports that it is still conducting searches and has put a 'world wide tracer' into effect to locate the material as it still believes it is within their delivery system." Illinois Report Number: IL16005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-08-16
52159 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2016-08-07 01:01 | 2016-08-07 04:45 | 2016-08-07 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "HPCI [high pressure coolant injection] governor valve did not respond as expected. "During performance of a planned HPCI valve functional test the HPCI governor valve (FD-FV-4879) did not reposition as expected. The HCPI system has been declared inoperable based on the response per Technical Specification 3.5.1 action C.1. All other emergency core cooling systems and the reactor core isolation cooling (RCIC) system remain operable. The unit remains at 100% power. "The station has initiated an event response team to identify and correct the cause of the failure. No personnel injuries resulted from the event. "The licensee notified the NRC Resident Inspector and the Lower Alloways Creek Dispatch." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-08-07
52158 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-08-06 14:30 | 2016-08-06 18:29 | 2016-08-10 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following report was received from the State of Texas via email: "On August 6, 2016, the Agency [Texas Department of State Health Services] was contacted by the licensee's radiation safety officer (RSO) who reported one of their crews had lost a Troxler model 3440 moisture density gauge. The gauge contains an 8 millicurie cesium-137 and a 40 millicurie americium-241 source. The crew had returned to their office in Dallas and when they went to get the gauge to place it in storage they realized the gauge had been left on the tailgate of the truck and was no longer there. The RSO was notified and both the crew and the RSO drove the 20 mile route used by the technicians returning to the office in an attempt to find the gauge, but the gauge was not located. The RSO stated the cesium source was located in the fully shielded position, but the operating rod was not locked. Local Law Enforcement in the area where the gauge was being used was notified of the lost gauge. The gauge does have a label on it identifying the licensee and listing the licensee's contact number. This number is to an answering service. Additional information will be provided as it is received in accordance with SA-300. "Local law enforcement has been notified." Texas Report #: I-9423 * * * UPDATE FROM ART TUCKER TO STEVEN VITTO AT 1711 EDT ON 08/10/2016 * * * The following was received from State of Texas via email: "On August 10, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee that it had recovered the missing gauge. The licensee's radiation safety officer (RSO) stated they found the gauge listed on Craig's List web site and contacted the seller. The RSO stated they paid the seller a reward and gained custody of the gauge at 1445 hours on August 10, 2016. The RSO stated the gauge was not damaged and the cesium source was still fully shielded. The RSO stated he was sending the gauge to a service company for inspection. Additional information will be provided in accordance with SA-300." Notified R4DO (O'Keefe), ILTAB (English), NMSS_Events Resource, CNSNS (MEXICO) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-08-15
52157 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-08-05 12:09 | 2016-08-05 20:55 | 2016-08-06 | FIRE DETECTION PANEL FAILURE AND LOSS OF ASSESSMENT CAPABILITY "At 1209 CDT on 8/5/16, during testing of Unit 2 Auxiliary Building Pre-action Sprinkler Systems, all zones on the Unit 2 Pyrotronics Fire Detection Panel went into an alarm state and were unable to be reset. This condition is reportable per 10 CFR 50.72(b)(3)(xiii) as a Major Loss of Assessment capability. "The NRC Resident has been notified." The licensee has initiated all necessary compensatory and corrective actions. * * * UPDATE FROM BLAKE MITCHELL TO VINCE KLCO AT 1718 EDT ON 8/6/2016 * * * "At 1600 CDT on 8/6/16, the Unit 2 Pyrotronics Fire Detection Panel was declared functional following repair of master override reset test switch and supply fuse. The Pyrotronics Fire Detection Panel was successfully tested following maintenance. The emergency assessment capability for the site's Emergency Plan has been fully restored. "The NRC Resident has been notified" Notified the R2DO (Suggs). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-08-05
52156 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-08-05 10:14 | 2016-08-05 13:58 | 2016-08-05 | OFFSITE NOTIFICATION DUE TO DRINKING WATER EXCEEDING LIMITS "On 8/5/2016 at 1014 [CDT], the Monticello Nuclear Generating Plant (MNGP) was notified by the Minnesota Department of Health (MDH) of a notice of violation for exceeding the drinking water limit for carbon tetrachloride in the drinking water well that supplies the Security Access Facility. Additionally the MDH will be notifying the Minnesota Pollution Control Agency regarding the violation. As a result, this issue is being reported under 10CFR50.72(b)(2)(xi) for notifications to other offsite government agencies. There was no impact to the health and safety of the general public as a result of this issue. The drinking fountains in the Security Access Facility have been isolated. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-08-05
52155 | 0 | NC DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2016-08-03 | 2016-08-05 10:37 | 2016-08-05 | AGREEMENT STATE REPORT - DEFECTIVE SHUTTER ON FIXED GAUGE The following was received from the North Carolina Department of Health and Human Services via email: "General Licensee discovered a defective shutter on one of its fixed gauges while performing leak tests. The shutter was discovered as being completely removed and the gauge remains in the open (source exposed) position. Per the licensee, during its previous leak test in May 2016, the shutter was intact on the gauge at that time. From the time of the previous leak test to present it is unknown how long the shutter was removed from the gauge. Per the licensee, the gauge is positioned with the radiation exposure pointing downward toward its product line where density measurements are determined. "Currently, the licensee's operations are continuous and the gauge remains in the open position during operations to support business output. "Discussions with the licensee were held concerning potential radiation exposures to members of the public and its employees. It was determined that due to the design of the licensee's manufacturing process it would be incredibly difficult for anyone to safely come within the immediate vicinity of the gauge with the defective shutter. An entire shut down of the licensee's manufacturing process would have to occur for anyone to gain any safe method of access to the defective gauge, in which the licensee stated, has not occurred since the most recent leak test when the defective gauge was discovered. "This in an ongoing investigation and more details will be forthcoming." Source Material: Am-241 North Carolina Item Number: NC160025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2016-08-15
52154 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-08-04 22:40 | 2016-08-05 06:26 | 2016-08-05 | UNANALYZED FIRE BARRIER "At 2240 CDT on August 4, 2016, it was discovered that the floor between the cable spreading room and the plant administration building (PAB) basement is not a credited Appendix R fire barrier. Because the cable spreading room and the plant administration building are located in the same fire area, a fire in the PAB could spread to the cable spreading room requiring evacuation of the control room. The travel path used to access the Alternate Shutdown Panel following control room evacuation traverses the same fire area in the PAB. Therefore, this event is being reported under 10 CFR 50.72(b)(3)(ii) for Degraded or Unanalyzed Condition as a fire in the PAB could have the potential to impact Division 1 equipment as well as impede the Operators ability to access Division 2 safe shutdown equipment. Fire watches have been established. There is no impact to the health and safety of the public. "The NRC Resident Inspector has been notified." The licensee will notify the State of Minnesota. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-08-05
52153 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-08-04 14:15 | 2016-08-04 22:04 | 2016-08-05 | BATTERY ROOM FIRE DETECTION SYSTEM INOPERABLE "At 1415 CDT on August 4, 2016, while performing a scheduled fire protection surveillance, it was discovered that a component within fire panel FZCP-7, BATTERY ROOM FIRE DETECTION had failed resulting in the inability of the installed fire detectors to detect a fire within the Division 1 and Division 2, 125 VDC battery rooms as well as the Division 2, 250 VDC battery room. This is being reported under 10 CFR 50.72(b)(3)(xiii) for a Loss Of Emergency Assessment Capability as the Control Room would not receive automatic notification of a fire in these areas for evaluation of HU2.1 and HA2.1 for fire within impacted battery rooms which are located within the Protected Area. There is no impact to the health and safety of the public. A 15 minute fire watch has been established for the affected fire zones. "The NRC Resident Inspector has been notified." * * * UPDATE FROM MARTIN RAJKOWSKI TO DANIEL MILLS AT 1050 EDT ON 08/05/2016 * * * "Event Notification 52153 completed at 2204 EDT on 8/4/2016 shown above contains an error. The failure of FZCP-7, BATTERY ROOM FIRE DETECTION, resulted in the inability to detect a fire within the Division 1 and Division 2 125 VDC battery rooms as well as the Division 1 250 VDC battery room. The Division 2 250 VDC battery room was not affected by this issue. Additionally, the State of Minnesota was notified of this issue. The NRC Resident Inspector has been notified of this update." Notified R3DO (Skokowski) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-08-04
52152 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-08-04 11:00 | 2016-08-04 17:54 | 2016-08-04 | TECHNICAL SUPPORT CENTER VENTILATION OUT-OF-SERVICE "This is a non-emergency eight-hour notification for a loss of Emergency Assessment Capability. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality due to a loss of cooling of the Technical Support Center (TSC) Ventilation system was discovered on 8/4/16 at 1100 EDT. Repairs are complete. "If an emergency would have been declared requiring TSC activation during this period, the TSC would have been staffed and activated using existing emergency planning procedures unless the TSC had become uninhabitable. If relocation of the TSC had been necessary, the Site Emergency Coordinator would have relocated the TSC staff to the Alternate TSC in accordance with applicable emergency plan implementing procedures. "The Emergency Response Manager and Site Emergency Coordinator were notified of the condition and the possible need to relocate during an emergency. This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-08-04
52151 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-08-02 09:40 | 2016-08-04 14:28 | 2016-08-04 | AGREEMENT STATE REPORT - FIXED GAUGE WITH SEALED RADIOACTIVE SOURCE RECOVERED AT A SCRAPYARD The following information was received from the Ohio Department of Health (ODH) via email: "A load of scrap metal set off the radiation detectors at a scrapyard in Cleveland, Ohio at approximately 0940 EDT on 8/2/16. A Department of Transportation exemption was issued and the scrap was returned to the supplier, Cleveland Wire, also located in Cleveland. The load was sorted by Cleveland Wire staff and a 'C-arm' fixed gauge was discovered. "ODH investigators arrived at the Cleveland Wire site on 8/3/16 and surveyed the gauge. Highest readings were determined to be 4 mR/hour on contact at the point where the source would be located inside the device, indicating that a source was present and the shutter was closed. Smear wipes taken indicated no removable contamination present. Further investigation showed that a tag was still affixed to the device, indicating the isotope (Sr-90), activity (70 mCi) and assay date (June, 1976). The radiation readings and identifying information are in keeping with what would be expected upon review of the Sealed Source & Device (SS&D) registration for the device. The device is currently in secure storage on site at Cleveland Wire, awaiting plans for transfer or disposal. "The ODH investigators at Cleveland Wire also learned that the device had been received from an industrial equipment reseller, HDR Industrial Surplus, located in Euclid, Ohio. Another ODH inspector was dispatched to that location on 8/3/16 to survey the facility, check for additional items that might contain radioactive materials, and to determine if the original owner/consignor could be located. No radiation levels were detected above background at the Euclid location, and no other items containing radioactive materials appeared to be present. "Research and investigation is ongoing to attempt to determine the owner of the device. "Source/Radioactive Material: SEALED SOURCE GAUGE Manufacturer: AMERSHAM Model Number: S-18 Serial Number: S-1078-7 Radionuclide: SR-90, 0.070 Ci IAEA Category: 5 "Device/Associated Equipment: Device Name: FIXED GAUGE Manufacturer: SANGAMO-WESTON-SCHLUMBERGER Model Number: M-3." Ohio Item Number: OH160008" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-08-12
52150 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-08-03 13:00 | 2016-08-03 21:38 | 2016-08-03 | UNANALYZED CONDITION BASED ON REVIEW OF NATIONAL FIRE PROTECTION ASSOCIATION REQUIREMENTS "On August 3, 2016 at approximately 1300 CDT during review of NFPA 805 requirements, it was determined that the NFPA 805 analysis and Fire Safe Shutdown (FSS) procedures do not consider the potential for fire-induced failure of the 4kV Shutdown Board under-voltage trip functions for Emergency Diesel Generator (EDG) power supply alignments. As such, a condition could possibly exist during a postulated fire where a required EDG's 4kV loads would not trip on an undervoltage condition. Current procedures and timeline analysis do not consider operator actions that could be necessary to manually strip the 4kV Safe Shutdown (S/D) board prior to subsequent EDG restart. As such, a subsequent restart, manual or automatic, of the EDG under these conditions, with its associated loads still connected to the 4kV S/D board, could potentially over load the EDG on restart. "This notification is to report a condition involving a deficiency in FSS procedures affecting restoration of power to safe shutdown busses under certain postulated fire scenarios. The condition could result in an adverse impact on the ability of operators to implement FSS procedures in response to a postulated fire in 6 fire areas. Therefore, this notification is being made pursuant to 10 CFR 50.72(b)(3)(ii)(B), any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "Compensatory fire watches have been established in the affected areas and this deficiency has been added to the current fire protection impairment plan. "The [NRC] Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-08-03
52149 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-08-02 17:10 | 2016-08-02 20:33 | 2016-08-02 | OFFSITE NOTIFICATION DUE TO ONSITE SEWAGE SPILL "At 1612 EDT on 08/02/16, Fermi 2 discovered a sanitary sewer system leak from underground lines beneath the parking lot near Warehouse B. Some of the sewage has entered the storm drain system. The sewage leak was stopped at approximately 1730 EDT. The duration and quantity of the spill is unknown. A local sanitary contractor is currently responding to the site to clean the affected areas. "Reports to the Michigan Department of Environmental Quality (MDEQ), the local health department [Monroe County], and the local news media are in progress. Since these reports are in the process of being made, this is considered a News Release or Notification to Other Government Agencies, therefore this event is reportable under 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-08-02
52148 | -1 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-08-02 09:34 | 2016-08-02 17:55 | 2016-08-29 | WATERTIGHT DOOR DISCOVERED OPEN AND UNATTENDED "On August 2, 2016 at 0934 CDT, Byron Operators entered and exited 1BOL 8.1 Conditions B and F for the 1A and 1B Diesel Generators due to 0DSSD192 (1B DOST Watertight Door) being discovered open and unattended. 0DSSD192 was closed within 5 minutes of discovery. "0DSSD192 protects the DOST [diesel oil storage tank] transfer pumps from the effects of a postulated failure of a Circulating Water expansion joint at the condenser waterboxes in the Turbine Building. An open watertight door associated with one DOST has the potential of making both Diesel Generators inoperable. "This event is reportable per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION FROM SHANE HARVEY TO DONALD NORWOOD AT 1627 EDT ON 8/29/2016 * * * "The purpose of this report is to retract a previous report made on August 2, 2016 at 1755 EDT (EN 52148). Notification of the event to the NRC was initially made for a condition where the station determined that an open watertight door associated with one DOST [Diesel Oil Storage Tank] had the potential to make both Diesel Generators inoperable, and the condition was reported under 10 CFR 50.72(b)(3)(v)(D) for any event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident. "Upon further investigation, Byron Station has concluded that the 1A Diesel Generator was never inoperable, and therefore, no loss of safety function occurred. Based on this, the prior ENS notification is being retracted. "The NRC Senior Resident Inspector has been notified." Notified R3DO (Dickson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-08-02
52147 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2014-12-19 17:39 | 2016-08-02 16:22 | 2016-08-02 | FITNESS-FOR-DUTY REPORT A member of the Fitness-For-Duty (FFD) staff violated the FFD policy in December, 2014 by responding to a call-in for unscheduled work after having consumed alcohol within the prohibited 5 hour period. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2016-08-02
52146 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-08-02 10:15 | 2016-08-02 14:42 | 2016-08-02 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On August 2, 2016 at 1015 EDT, while restoring the east train of Reactor Building HVAC (RBHVAC) after a surveillance test on Division 2 Standby Gas Treatment System (SGTS), the Technical Specification (TS) for the secondary containment pressure boundary was not met for a duration time of approximately 1 second. The maximum secondary containment pressure observed during that time was approximately 0.120 inches of vacuum water gauge. "Secondary containment pressure was returned to within the TS operability limit by RBHVAC and SGTS already in operation. There were no radiological releases associated with this event. "The cause of the event is under investigation. "The TS requirement is to maintain secondary containment vacuum greater than or equal to 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) for secondary containment operability. Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident lnspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-08-02
52145 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-02 06:30 | 2016-08-02 14:22 | 2016-08-02 | TECHNICAL SUPPORT CENTER VENTILATION OUT-OF-SERVICE "This is a non-emergency eight-hour notification for a loss of Emergency Assessment Capability. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality due to a loss of cooling of the TSC (Technical Support Center) Ventilation system was discovered on 8/2/16 at 0630 EDT. Repairs are complete at 1030 EDT on 08/02/16. "If an emergency would have been declared requiring TSC activation during this period, the TSC would have been staffed and activated using existing emergency planning procedures unless the TSC had become uninhabitable. If relocation of the TSC had been necessary, the Emergency Coordinator would have relocated the TSC staff to an alternate location in accordance with applicable emergency plan implementing procedures. "The Emergency Response Organization team was notified of the condition and the possible need to relocate during an emergency. This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-08-02
52144 | 0 | VETERANS HEALTH ADMINISTRATION |  |  |  |  | 2016-07-29 07:00 | 2016-08-02 12:50 | 2016-08-02 | EXTERNAL CONTAMINATION OF PACKAGE CONTAINING MEDICAL ISOTOPE "Per 10 CFR 20.1906(d), Veterans Health Administration (VHA) National Health Physics Program is reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. "The package was received Friday, July 29, 2016, at around 0700 EDT by the North Florida / South Georgia Veterans Health System in Gainesville, Florida. This facility holds permit number 09-12467-02 under the VHA master materials license. "The package was checked-in and surveyed upon receipt around 0700 EDT. Wipe tests performed on the external surface of the package indicated a removable contamination level of around 347 dpm/cm2 as compared to the regulatory limit of 220 dpm/cm2 for beta-gamma emitters. "The package contained one unit dosage of about 57 millicuries of fluorine-18 (as fluorodeoxyglucose) at the time of receipt. The dosage was shipped from PETNET Solutions, Inc., out of Jacksonville, Florida, who was also the delivery carrier. The facility nuclear medicine technologist immediately notified the delivery carrier by phone about the contaminated package around 0710 EDT. "The patient dosage inside the package was not impacted and was able to be used. As corrective actions, the packaging materials were set aside in a restricted area at the facility. "VHA National Health Physics Program, who manages the master materials license, was notified of the incident around 1030 EDT on August 2, 2016. "In addition, we notified our NRC Region III Project Manager of the event." This event was reported to the State of Florida by the shipper, PETNET Solutions, Inc., and entered by the NRC as an Agreement State report (EN 52141). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2016-08-10
52143 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-08-01 | 2016-08-02 08:58 | 2016-08-02 | AGREEMENT STATE REPORT - SHUTTER MALFUNCTION DUE TO HIGH VIBRATION The following information was received via facsimile: "On August 1, 2016, the Department [Pennsylvania Department of Environmental Protection, Bureau of Radiation Protection] was notified by Georgia Pacific that a shutter handle had fallen off. This made the shutter inoperable in the closed position. It is initially reportable per 10 CFR 30.50(b)(2). "During a routine maintenance check, the licensee became aware of a gauge with an inoperable shutter. The gauge is located in a remote area with high vibration and the handle to the shutter seemed to have dislodged due to this, making it unusable. The gauge was put out of service until repairs can be completed by a licensed contractor. No exposures have occurred. "The shutter is in the closed position and the gauge is out of service and secure. There was no other damage to the gauge. A reactive inspection is planned by the Department. "Radionuclide: Cs-137 Manufacturer: Ronan Model: SA-1 Serial Number: M7419 Activity: 40 mCi" Pennsylvania Event Report ID No.: PA160021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-08-10
52142 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-08-01 15:18 | 2016-08-01 17:53 | 2016-08-01 | UNINTENTIONAL RELEASE OF HALON "At 1118 [CDT] during planned maintenance activities there was an unintentional release of approximately 146.5 pounds of Halon gas into an enclosed room in the Unit-2 Electrical Auxiliary Building. There was no impact to plant operations or plant personnel. The room was verified by station Safety Personnel to be safe for normal access. "At 1518, Region 12 (Houston) of the Texas Commission of Environmental Quality (TCEQ) was notified of an event which met the requirements of 'Emission Event' for the TCEQ of a HALON release that exceeded the reportable quantity threshold of 100 pounds in a 24 hour period. No further actions are required by the TCEQ at this time and no press release is planned. The halon discharge was contained within the site protected area. Therefore, this event is not significant with respect to the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-08-01
52141 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-07-29 06:57 | 2016-08-01 16:13 | 2016-08-01 | AGREEMENT STATE REPORT - EXTERNAL CONTAMINATION OF SHIPPING CONTAINER The following was received via email: "The Gainesville VA Medical Center (VAMC) received a unit dose of the F-18 FDG radiopharmaceutical used for PET/CT scans on Friday, July 29, 2016 at 0657 [EDT]. The swipe test performed upon receipt of the package found that the container was contaminated externally with F-18. The radiopharmaceutical was shipped and transported to the VAMC from the company, PETNET Solutions, Inc., 3728 Phillips Highway, Suite 220, Jacksonville, Florida, 32207. The State of Florida RAM license number for the PETNET Solutions laboratory is #3887-3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-08-09
52140 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-08-01 10:55 | 2016-08-01 14:36 | 2016-08-12 | AGREEMENT STATE REPORT - SUSPICIOUS ACTIVITY OBSERVED BY MATERIALS LICENSEE A black Dodge pickup truck was observed driving past a radiography facility with a cell phone extended out of the driver's window of the truck and appeared to be videotaping the facility. The Trainer, Pennsylvania police were called and responded to the licensee site and are conducting an investigation. * * * UPDATE AT 1452 EDT ON 08/12/16 FROM JOSEPH MELNIC TO JEFF HERRERA * * * The Pennsylvania Bureau of Radiation Protection provided additional information concerning the suspicious activity. Notified R1DO (Burritt), NMSS (via email), and ILTAB (Whitney). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 1 | 2016-08-09
52139 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2016-08-01 07:45 | 2016-08-01 09:10 | 2016-08-01 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The licensee reported a stolen Troxler Model 3430 Moisture/Density gauge, Serial Number 27320 between midnight and 0600 CDT. The Troxler gauge was locked and stored at the licensee's facility. The Topeka Police Department was notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2016-08-09
52138 | -1 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2016-08-01 03:42 | 2016-08-01 06:33 | 2016-09-23 | PLANT SHUTDOWN DUE TO PRESSURE BOUNDARY LEAKAGE GREATER THAN ALLOWABLE LIMIT "On August 1, 2016 at 0342 EDT St. Lucie Unit 1 commenced a unit shutdown required by Technical Specifications due to Reactor Coolant System Pressure Boundary Leakage in excess of the allowable limit of zero leakage. The leak was initially identified on July 31, 2016 at 2115 EDT as not Pressure Boundary leakage. After further analysis, the leak was determined to be Reactor Coolant System Pressure Boundary leakage at 0123 on August 1, 2016. The leakage is estimated as less than one tenth of a gallon per minute and is not impacting the ability to shut down the unit. Additional impact of the leak is under evaluation. "This report is submitted in accordance with 10CFR50.72(b)(2)(i) as 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The location of the leak is on the Instrumentation piping welded connection at Flow Element FE-3311 attached to [the] Emergency Core Cooling System Injection header to Reactor Coolant System Loop 1A2. The leak activity is 0.167 microCuries per ml." The NRC Resident Inspector has been notified. * * * RETRACTION AT 1335 EDT ON 09/23/16 FROM RICHARD SCISCENTE TO JEFF HERRERA * * * "The purpose of this notification is to retract a previous report made on EN 52138. NRC notification was initially made as a result of a plant shutdown required by technical specifications (TS) for Reactor Coolant System (RCS) pressure boundary leakage. "Subsequent to the initial report, St. Lucie has determined that the RCS leakage was from a seal weld on a threaded connection that was not pressure boundary leakage. However, the leak was non-isolable and required RCS depressurization to allow immediate investigation to ensure there were no faults in a RCS component body or pipe wall. "The leakage was estimated to be less than one tenth of a gallon per minute and did not impact the ability to shut down the unit. No TS limits were exceeded during this event. "Therefore, the plant shutdown to investigate and correct leakage past the seal weld of a threaded connection does not meet the reporting requirements of 10 CFR 50.72 or 10 CFR 50.73." The NRC Resident Inspector has been notified. Notified the R2DO (Blamey). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-08-01
52137 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2016-07-30 11:52 | 2016-07-30 15:17 | 2016-07-30 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO UNISOLABLE REACTOR COOLANT SYSTEM BOUNDARY LEAKAGE "On July 30, 2016 at 1152 hours [EDT] following a containment walkdown to investigate an increase in RCS unidentified leakage to 0.15 gpm, a leak was identified on the seal return line from 2-RC-P-1C, 'C' Reactor Coolant Pump. The source of the leakage cannot be isolated and is considered RCS pressure boundary leakage. [Technical Specification] LCO 3.4.13, RCS Operational Leakage, Condition B for the existence of pressure boundary leakage was entered. Technical Requirement TR 3.4.6, ASME Code Class 1, 2, and 3 Components is also applicable. Unit 2 is projected to be taken to Mode 5 for repair. "This event is reportable in accordance with 10 CFR 50.72(b)(2) for 'the initiation of any nuclear plant shutdown required by the plant's Technical Specifications' and 10 CFR 50.72(b)(3)(ii)(A) for 'any event or condition that results in the condition of the nuclear plant including its principal safety barriers, being seriously degraded.'" The licensee will be notifying the Louisa County Administrator and has notified the NRC Resident Inspector. | 0 | 35 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2016-07-30
52136 | -1 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2016-07-30 03:33 | 2016-07-30 03:52 | 2016-07-30 | TURKEY POINT UNIT 3 SHUTDOWN DUE TO WATER HAMMER "Power had been reduced for planned maintenance on the 3B feedwater heater. During isolation of the feedwater heaters, a repeated water hammer was experienced. "A normal shutdown of Unit 3 was performed." Unit 4 was not affected by the water hammer. The decay heat is being removed via the condenser and all offsite and onsite electrical power is available. The investigation of the cause is underway. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 2141 EDT ON 07/30/16 FROM ERIC JUERGENS TO S. SANDIN * * * The licensee is retracting this report based on the following: "At 0352 EDT on July 30, 2016, EN #52136 provided notification of a Reactor Protection System (RPS) actuation during a normal shutdown of Unit 3 in response to a secondary system equipment issue. Upon further investigation, the unit shutdown and manual RPS actuation were in accordance with general plant operating procedures. The manual RPS actuation was in accordance with the general operating procedure and not required to mitigate the consequences of the secondary system equipment issue. As such, the notification made by EN #52136 for a valid actuation of a specified system is hereby retracted. "The NRC Resident lnspector will be notified." Notified R2DO (Rose). | 0 | 0 | 0 | 54 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-07-30
52135 | 0 | US AIR FORCE |  |  |  |  | 2016-06-03 | 2016-07-29 15:27 | 2016-07-29 | LOSS OF GENERAL LICENSED MATERIAL CHECK SOURCES On June 3, 2016, the US Air Force determined that two (2) check sources containing Thorium-232 (45 nCi and 13 nCi) were missing at the Aviano Air Base located in Italy. These two generally licensed sources are used as check sources for the ADM-300 survey meter. The licensee contacted NRC RIV (Michelle Simmons) who recommended that the licensee report the loss per 10 CFR 31.5(c)(10). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2016-08-08
52134 | -1 | ADVANCED RADIOLOGY CONSULTING |  |  |  |  | 2016-07-28 | 2016-07-29 15:18 | 2016-08-02 | MEDICAL EVENT - WRONG RADIOPHARMACEUTICAL FORMULATION ADMINISTERED TO PATIENT A nuclear technologist ordered and administered 25 mCi of Technetium 99m-methyl diphosphonate (99mTc MDP) to a patient undergoing a gastric emptying scan. 99mTc MDP is a radioisotope used especially for bone scans. The formulation that should have been ordered and administered is 500 microCuries of Tc 99m Sulfur colloid, which is generally used for the gastric study. Both the patient and prescribing physician have been notified. The dose received by the patient is under evaluation at this time. No harmful effects to the patient are expected. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM DAVID WISHKO TO DANIEL MILLS AT 1323 EDT ON 08/02/2016 * * * Upon further analysis, the dose administered to the patient did not exceed the limits listed in 10 CFR 35.3045, and therefore this event is not reportable. Notified R1DO (Kennedy) and NMSS (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-08-08
52133 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2016-07-28 23:57 | 2016-07-29 06:51 | 2016-07-29 | TEMPORARY LOSS OF POWER TO THE EMERGENCY CONDENSER "On 7/28/2016 at 2357 EDT, Nine Mile Point Nuclear Station Unit 1 experienced a fault in the in-service 11 RPS UPS [Reactor Protective System Ultimate Power Supply], resulting in an isolation of both emergency condensers. Emergency condenser 12 was returned to standby on 7/29/2016 at 0041 EDT and emergency condenser 11 was returned to standby on 7/29/2016 at 0045 EDT. "This 8-hour non-emergency report is being made based upon requirements of 10CFR50.72(b)(3)(v)(B) which states, 'Licensee shall notify the NRC of any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat.' "The state of New York and the NRC Senior Resident Inspector were informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2016-07-29
52132 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-07-28 21:20 | 2016-07-29 01:51 | 2016-09-26 | POSTULATED FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "A review of the Beaver Valley Unit 2 Fire Protection Safe Shutdown Report (FPSSR) found that a postulated fire had the potential to spuriously open all three individual steam generator atmospheric dump valves in addition to a common residual heat release valve. Previous analysis did not consider all of the valves spuriously opening from a fire. The potential impact of these valves spuriously opening is a cooldown that could adversely affect shutdown margin. "Hourly fire tours have been put in place for those fire areas that have the potential to initiate this condition. "This condition is reportable as an 8 hour report in accordance with 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector was notified." This condition is not applicable to Unit 1. * * * RETRACTION FROM DAN SCHWER TO VINCE KLCO ON 9/26/16 AT 1428 EDT * * * "Retraction of EN 52132 'Postulated Fire Event That Could Adversely Impact Safe Shutdown Equipment'. "On 07/29/2016, an 8-hour notification (EN 52132) was made describing the discovery of a postulated fire event that could adversely impact safe shutdown equipment, specifically the spurious opening of the three Atmospheric Steam Dump Valves (ASDVs) and the Residual Heat Release (RHR) Valve, simultaneously. This notification was made pursuant to 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition because of the potential effect on shutdown margin. Further engineering evaluation has determined that the required shutdown margin is not challenged by the event, as bounded by previous analysis of a similar scenario as well as validated operator actions. Therefore, this does not result in a reportable condition. "The Resident NRC Inspector has been notified." Notified the R1DO (Cook). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-07-29
52131 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-07-27 | 2016-07-28 20:00 | 2016-07-28 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN THE PRESCRIBED DOSE OF I-131 The following information was provided by the State of Washington via email: "At approximately 3:50 pm [PDT] on Thursday, July 28th 2016, the Director of Radiology of Virginia Mason Medical Center called the radioactive materials section [WA Office of Radiation Protection] to report a medical event. The event occurred on the previous day, July 27th 2016, but was not noticed until the 28th . A patient was supposed to receive 120.8 mCi of I-131 in the form of two capsules for thyroid treatment. However, the patient only received one capsule resulting in the patient only receiving 53 mCi of the 120.8 mCi. The event was discovered (8:45 am [on] July 28, 2016) when an I-131 capsule was returned to the pharmacy on the 28th and it was noticed that the patient did not get both capsules as intended." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-08-05
52130 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2016-07-28 15:15 | 2016-07-28 19:00 | 2016-07-28 | SAFEGUARDS REPORT Safeguards system degradation related to monitoring and detection of PA boundary. Compensatory action taken. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 1 | 2016-07-28
52129 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-07-28 05:41 | 2016-07-28 09:25 | 2016-09-26 | SOURCE RANGE INSTRUMENTS READING IMPROPERLY DURING A REACTOR STARTUP "This four and eight hour notification is being made to report that at 0541 [EDT] on 7/28/16, Salem Unit 1 initiated a shutdown to comply with Technical Specifications due to the inoperability of both source range nuclear instruments. During a reactor startup, with Unit 1 in Mode 2, both source range instruments were reading approximately one decade lower than expected compared to intermediate range and Gamma-Metric instruments and due to the proximity to the estimated critical condition. The condition could also have prevented the fulfilment of the source range instruments safety function to trip the reactor when required. "Salem Unit 1 is currently stable in Mode 3. Reactor Coolant system pressure is 2235 psig and reactor coolant system temperature is 547 F with decay heat removal via the main steam dump and auxiliary feedwater systems. Unit 1 has one active shutdown tech spec action statement in effect due to the inoperability of the containment radiation monitor 1R11A. The inoperability of this radiation monitor had no effect on the event. All control rods were manually inserted to place Unit 1 in Hot Standby (Mode 3). No ECCS [emergency core cooling system] or ESF [emergency safety features] systems were required to function during this event. "No major secondary equipment was tagged for maintenance prior to this event. No personnel were injured during this event." The reactor was manually shut down and a shutdown margin calculation verified sufficient margin. The licensee notified the NRC Resident Inspector and the local township. * * * RETRACTION FROM MATT MOG TO VINCE KLCO ON 9/26/16 AT 1519 EDT * * * "The purpose of this notification is to retract event report number 52129 made on 7/28/2016 at 0925 (EDT). Previously PSEG reported that Salem Unit 1 initiated a shutdown to comply with Technical Specifications (TS) due to the inoperability of both source range nuclear instruments. Additionally PSEG reported that the condition could have prevented the fulfillment of the safety function needed to, 'Shut down the reactor and maintain it in a safe shutdown condition.' "Subsequent review identified that the condition did not meet either reporting criteria. Maintenance and Engineering evaluation of the source range nuclear instruments determined that the instruments were fully operable at the time of the event. TS 3.3.1.1, Reactor Trip Instrumentation remained met, no TS shutdown was required and the instruments were capable of performing their required function. "Therefore PSEG is retracting the notifications made under 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(3)(v)(A). "The NRC Resident Inspector was notified of this retraction by the licensee." Notified the R1DO (Cook). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) |  |  | 0 | 2016-07-28
52128 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-07-26 | 2016-07-26 18:00 | 2016-08-16 | AGREEMENT STATE REPORT - LOST IODINE-125 SOURCE The following information was received via E-mail: "At approximately 1300 MST on July 26, 2016, the licensee contacted the Agency [Arizona Radiation Regulatory Agency] and reported that a 0.4 millicurie Iodine-125 source, which was being used for localization, was discovered missing. An initial radiation survey of the department did not locate the source. The licensee does not know the exact date or time that the I-125 source went missing. "The agency is continuing to investigate the event. "The Governor's Office and NRC are being notified of this event." Arizona First Notice Number: 16-013 Notified Mexico via E-mail. * * * UPDATE AT 1540 EDT ON 8/16/16 FROM BRIAN GORETZKI TO JEFF HERRERA * * * The following update was received from the Arizona Radiation Regulatory Agency via email: "On August 12, 2016, the licensee notified the Agency [Arizona Radiation Regulatory Agency] that the initial notification was incorrect and that a 0.5 [micro Curie] Cs-137 button source had been lost and not an I-125 seed. The Administrative Director stated that he had assumed it was an I-125 seed because the lost source was from pathology but he did not clarify." Notified R4DO (Proulx), NMSS (email), ILTAB (email), MEXICO(email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-08-03
52127 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2016-07-26 12:52 | 2016-07-26 18:12 | 2016-07-26 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "On July 26, 2016 at 1252 hours (CDT), the Control Room Emergency Ventilation (CREV) system was declared inoperable due to a toxic gas analyzer spurious alarm which resulted in the 'B' Air Filtration Unit (AFU) being inadvertently isolated. In this condition, Control Room Emergency Ventilation (CREV) system cannot be guaranteed to achieve required design flow rate. Tech Spec 3.7.4, Condition A was entered which requires the CREV system to be restored to an operable status in seven (7) days. "The CREV system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions as well as protection of the operators from a high dose environment assumed during a design basis accident. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function,' because the CREV system is a single train system required to mitigate the consequences of an accident. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-07-26
52126 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-07-26 15:36 | 2016-07-26 16:39 | 2016-07-26 | OFFSITE NOTIFICATION DUE TO OIL SHEEN IN COOLING TOWER BASIN "On 7/26/2016 at 1536 EDT, TVA [Tennessee Valley Authority] notified the National Response Center that Watts Bar Nuclear Plant had noted an oil sheen on the Cooling Tower Basin. An oil sheen was observed within the U1 Cooling Tower basin at WBN. The sheen did not cover the entire Cooling Tower basin. The sheen covered approximately two square feet. Estimate of oil released into the Cooling Tower basin is less than four ounces. No oil sheen was visible in the Tennessee River from the bank above the diffuser pipes. "Notifications were also made to TEMA [Tennessee Emergency Management Agency]. Follow-up observations within 20 minutes of the sheen being reported indicated that the oil sheen had dissipated and was no longer visible. Oil levels from the suspected source did not indicate any change in oil reservoir levels. "Unit 1 remains in Mode 1 at 79 percent power - reduced power due to main condenser back pressure limits. Unit 2 remains in Mode 1 at 74 percent power - initial startup testing "This event is reportable under 10 CFR 50.72(b)(2)(xi) as a condition that was reported to an outside Government Agency. "The NRC Resident Inspector has been notified." | 79 | 74 | 0 | 79 | 74 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-07-26
52125 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-06-23 12:00 | 2016-07-26 10:20 | 2016-07-26 | AGREEMENT STATE REPORT - LEAKING ECD SOURCE The following report was received from the State of New York via facsimile: "Pace Analytical Services reported that a leak test of a Varian ECD [electron capture device], model 02- 001972-00, serial no. SP472 indicated removable contamination in excess of 0.005 microcuries. Test results measured 0.0132 millicuries of contamination associated with a 15 millicurie Nickle 63 source manufactured by Isotope Products Laboratory (IPL), model NBCB14746, serial# SP472. The licensee was advised to isolate the source and not to use it. [The licensee was] requested to arrange for retesting and provide results to the NYS DOH [New York State - Department of Health]. Retesting was performed by [a Certified Health Physicist], Massachusetts License #13-3021, on July 14, 2016. The result of the second measurement was 0.0002 microcuries. Pace Analytical Services, Inc. stated that the ECO will be returned back to the manufacturer/ vendor and receipt will be sent to the NYS Department of Health." EVENT REPORT ID NO. NYDOH - NY-16-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-08-03
52124 | 0 | HAKS ENGINEERING |  |  |  |  | 2016-07-26 04:00 | 2016-07-26 06:37 | 2016-07-26 | STOLEN MOISTURE-DENSITY GAUGE A moisture-density gauge (Troxler - Model 3440, Serial Number 34924) was stolen from a technician's vehicle. The vehicle trunk was broken into, the lockdown chains were cut, and the entire gauge was removed. This model Troxler typically contains 8 mCi Cesium-137 and 40 mCi Americium-241:Beryllium. The licensee has notified local law enforcement and an investigation continues. * * * UPDATE FROM JEFF SEMANCIK TO DONALD NORWOOD AT 1702 EDT ON 7/26/2016 * * * The following is a synopsis of information received from the Connecticut Department of Energy and Environmental Protection, Radiation Division (CDEEPRD) via telephone: At 1637 EDT, CDEEPRD received a call from the Connecticut State Police, informing them that the Troxler moisture-density gauge reported stolen this morning, had been located and recovered. It was reported that the gauge was recovered in an intact condition, outside its storage container. Details of how the gauge was located are unknown at this time. Details concerning suspect(s) are unknown at this time. CDEEPRD has an inspector en route to survey the gauge. If the gauge checks out as undamaged, it will be returned to the licensee at that time. Notified R1DO (Welling). Notified via E-mail only - NMSS Events Notification and ILTAB.(Tucker). * * * UPDATE FROM JEFF SEMANCIK TO DONALD NORWOOD AT 1813 EDT ON 7/26/2016 * * * The following is a synopsis of information received from CDEEPRD via telephone: An individual attempted to pawn the moisture-density gauge at a pawn shop in Bridgeport, CT. Pawn shop personnel immediately notified the Bridgeport Police Department. Officers arrived on the seen and arrested the individual who was attempting to pawn the gauge. CDEEPRD performed a leak test on the moisture-density gauge. The gauge passed the leak test. The gauge was then turned over to licensee personnel. The moisture-density gauge was not in its storage box when brought into the pawn shop. The licensee placed the gauge in another storage box which they possessed. Notified R1DO (Welling). Notified via E-mail only - NMSS Events Notification and ILTAB.(Tucker). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-08-09
52123 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-07-21 | 2016-07-25 14:49 | 2016-07-25 | AGREEMENT STATE REPORT - LOST HYDROGEN-3 SEALED SOURCE The following is a synopsis of information received via E-mail: On July 21, 2016, while in the process of performing an inspection at KRISS USA, Inc., during inventory performance, the Radiation Safety Officer discovered that a Hydrogen-3 sealed source (25 milliCuries, mb-microtec Model 400/1, SSDR #NY-1271-S-101-S, source lot #7036) was missing. The Radiation Safety Officer performed an investigation, which included interviewing users, and performed a visual inspection of the work area, of the path from the work area to the storage area, and of the storage area. A visual inspection of these areas was also conducted with the lights off to assist in the ability to locate the source. Upon failure to locate the source, based on information obtained through interviews with the user, the Radiation Safety Officer concluded that the source was likely lost in proximity of the work station. The most recent wipe test (July 6, 2016) of the work station was performed and analyzed by an appropriate service provider. All results found no detectable contamination. More information will be provided as received. Virginia Event Report ID No.: VA-16-11 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-08-02
52122 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-07-25 09:30 | 2016-07-25 13:43 | 2016-07-25 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISORY EMPLOYEE A non-licensed supervisory employee had a confirmed positive test for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 84 | 0 | 0 | 84 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2016-07-25
52121 | 0 | UNIVERSITY OF MISSOURI |  |  |  |  | 2016-07-18 14:40 | 2016-07-22 17:20 | 2016-07-27 | SEALED SOURCE LEAK During a sealed source leak test of two (2) cesium-137 needles, prior to implant into an animal, leakage greater than 0.005 microcuries was measured. The leakage was contained in the source holder. The Cs-137 needles have been stored in shielding pending disposal. There was no contamination or over- exposure. The needles contain 10 mCi of Cs-137 total (for both). The licensee has notified NRC Region 3 and expects to submit a 30 day follow up report. * * * UPDATE FROM JACK CRAWFORD TO DONALD NORWOOD AT 1721 EDT ON 7/27/2016 * * * Follow-up leak tests have been performed on all remaining Cs-137 needles used for equine brachytherapy. One additional leaking needle was identified. The activity for the additional leaking needle, as of 7/18/2016, was 7.1 mCi. The additional leaking needle was manufactured in 1982. The additional leaking needle has been taken out of service, put into secondary containment, and is awaiting waste disposal. The licensee notified NRC Region 3. Notified R3DO (Peterson) and via E-mail NMSS Events Notification. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-08-01
52120 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-07-22 | 2016-07-22 17:09 | 2016-07-22 | AGREEMENT STATE REPORT - SOURCE DISCONNECT The following was received via email: "Qualspec, LLC. Radiation Safety Officer, reported the following source disconnect incident on July 21, 2016, at [1843 PDT] via email. The incident took place at the Valero refinery, located at 3400 East Second St., Benicia, CA, at approximately 1430. During their 4th and last exposure, they were not able to return the radiography source (Ir-192, 63 Ci) to the INC 100, S/N 4848 radiography camera's shielded position. The RSO and ARSO, were notified right away and responded immediately to the location. After their assessment, they determined the source pigtail had become detached from the drive cable due to the drive cable ball connector breaking off. There was no other sign of physical damage to the camera, the crank assembly or related equipment. After phone consultation with the manufacturer, a retrieval method was determined and the source was safely secured back into the exposure device. TLD dosimeters have been sent to Radiation Detection Company for emergency processing. Individuals involved [received] based on their pocket dosimeter [readings] - Radiographer Trainer 20 mR, Radiographer 10 mR, Radiographer Assistant 10 mR [as measured by] 200 mR scale Arrow pocket dosimeter; Radiation Safety Officer 400 mR, Assistant RSO 300 mR [as measured by] 5R scale Arrow pocket dosimeter." California 5010 # 072116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-08-01
52119 | 0 | MASSACHUSETTS RADIATION CONTROL PRO |  |  |  |  | 2016-07-22 | 2016-07-22 14:38 | 2016-07-22 | AGREEMENT STATE REPORT - LOST AND THEN FOUND SHIPMENT OF RADIOACTIVE MATERIALS The following was received via email: "The licensee (QSA Global, Inc.) made telephone notification at 1026 [EDT] on July 22, 2016 followed by written report to the Agency (Massachusetts Radiation Control Program), that the licensee was notified by carrier that one piece of a four piece shipment incoming from Australia and destined for QSA Global, Inc., Burlington, Massachusetts is unaccounted for. The licensee initially identified that it did not know which of the four pieces is the one missing. The licensee provided update by telephone at 1335 on July 22, 2016 that it had determined that the piece missing is a Model 650L source changer, Type B(U) package, UN2916, containing two special form iridium-192 sources, 0.44 TBq (12 curies) total of iridium-192. The missing package is believed by the licensee to possibly be in Memphis, Tennessee at the carrier's hub. "The licensee reports that it initiated a trace yesterday with the carrier and has also requested a ramp search of the Boston (Logan Airport) facility in case it was separated there. "The reporting requirement is immediate and is of 105 CMR 120.281(A)(1), missing licensed radioactive materials in aggregate quantity equal to or greater than 1,000 times quantity specified in 105 CMR 120.297, Appendix C. "The Agency made notification to FBI. "The Agency considers this event to be open. "At 1616 [EDT], on July 22, 2016, the licensee (QSA Global, Inc. of Burlington, MA) notified us (Massachusetts Radiation Control Program) by telephone that the missing package has been located by the carrier at its Memphis, Tennessee hub and that the package is expected to be delivered to the licensee on Monday. The licensee reports that a label had apparently fallen off of the package." THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2016-08-01
52118 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-07-22 08:50 | 2016-07-22 12:05 | 2016-07-22 | AGREEMENT STATE REPORT - LOSS OF LICENSED MEDICAL TREATMENT SEEDS The following information was provided via email from the State of Tennessee: "A patient was treated with 50 I-125 seeds. The patient was apparently not responding well to the treatment so he was brought back to Vanderbilt to have the seeds removed. Today, only 39 of the 50 seeds were recovered from the patient. According to the patient, prior to returning to Vanderbilt to have the seeds removed the patient stated that he 'picked' the 11 seeds out and threw them in the trash can at his home near Huntsville, Al. Total activity of the 11 missing seeds, after decay, equals 1.71 mCi of I-125. Patient is currently still at Vanderbilt Medical Center." "The State of Tennessee has notified the State of Alabama's Office of Radiation Protection." TN State Event Report ID no: TN-16-102 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-08-01
52117 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2016-07-14 | 2016-07-22 11:10 | 2016-07-22 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR SOURCE The following information was received by email: "Event Description: On July 14, 2016, 3M Corporate Health Physics was notified by laboratory personnel that a static eliminator could not be located during a semiannual physical inventory. The static eliminator is an NRD model P-2001 with an initial activity of 9.56 mCi on September 1, 2015 (activity on July 21, 2016 was 1.89 mCi). The room was recently renovated and the contents of the room were moved to another building with some contents moved to a 3M Distribution Center. Both buildings and the distribution center were searched, but the source was not located. 3M Corporate Health Physics notified the Minnesota Department of Health on July 21, 2016 of the missing static eliminator." Minnesota Event: MN160002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2016-08-01
52116 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-07-21 09:45 | 2016-07-21 18:28 | 2016-07-21 | NON-LICENSED SUPERVISORY CONTRACTOR TESTED POSITIVE FOR ALCOHOL Southern Nuclear Operating Company had a non-licensed supervisory contractor employee confirmed positive result for alcohol during a follow-up fitness-for-duty test. The contractor employee's unescorted access to the plant has been revoked. The NRC Senior Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2016-07-21
52115 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-06-10 | 2016-07-21 13:37 | 2016-07-21 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received via email: "Lost/Abandoned Tritium Exit Signs, Manufacturer - Best Lighting Products Inc. (Forever Lite), Model #SXLTU1GB10, Serial # 206112 to 206140 (29 signs), 7.09 Ci of H-3 (tritium) per sign. Date shipped 9-3-2008. "The property [at 1818 Spring Water Point, Colorado Springs, CO] was received through reorganization and has now been assigned to a trustee. Twenty nine exit signs were directed for use by Best Lighting Products at the location listed. Annual general license notifications were sent to SRKO Family LTD Partnership from 2009 thru 2014 with no response. County records provided contact information regarding receivership and further review provided New Crossings Inc. as a contact. The property was inspected by the trustee and no exit signs were located. There were approximately 60 subcontractors on the site at the time the exit signs may have arrived. It is unknown what occurred with them. "In September of 2008 Best Lighting Products Inc. (Forever Lite) shipped 29 exit signs to be installed at 1818 Spring Water Point, Colorado Springs, CO. The site was going to be a commercial building and construction had started. According to the trustee, approximately 60 subcontractors/creditors were involved with the owner when they walked away from the project. It is unknown what occurred with the exit signs. No information has been discovered through years of trying to contact the SRKO Family Partnership LLC. The trustee has provided a statement explaining tritium exit signs will never be used in any project they work on. Should they discover any inadvertently they will immediately contact [The Colorado Department of Public Health] for further guidance." Event Report ID No.: CO160010 / CO16-I16-17 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-07-29
52114 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-07-14 | 2016-07-21 13:20 | 2016-07-21 | AGREEMENT STATE REPORT - SHUTTER FAILED TO CLOSE The following was received via email: "On July 21, 2016 at approximately 1200 [EDT], [Georgia Radioactive Materials Program] received a call from WestRock Southeast, notifying [Georgia Radioactive Materials Program] that a fixed gauge malfunction had occurred and that the shutter was not closing. The shutter malfunction was initially noticed on Thursday July 14, 2016. Thermofisher was contacted about repairing the gauge, but [the licensee] was informed that the fixed gauge cannot be repaired. WestRock Southeast has decided to dispose of the fixed gauge and has contacted Ram Services to handle disposal. No disposal date has been determined. Until such time, the fixed gauge has been tagged with danger signs and instructions not to enter [the area]. The fixed gauge is still in use. "Isotope: Cs-137; Activity: 10 millicuries; Manufacturer: Kay-Ray; Model: 7062B; Source Serial #: 24784A; Leak Test Results: Pass (last tested August 2014)" Georgia Event # 80359. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2016-07-29
52113 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-07-20 12:45 | 2016-07-20 20:33 | 2016-07-20 | HIGH PRESSURE COOLANT INJECTION INOPERABLE "On 07/20/2016 at 1245 CDT, the Browns Ferry Nuclear Plant Unit 1 High Pressure Coolant Injection (HPCI) Steam Line Inboard Isolation Valve was declared inoperable. "HPCI was declared inoperable at 0300 CDT on 7/18/2016 when it was taken out of service for planned maintenance. A 14 day LCO [Limiting Conditions for Operation] was entered and will expire at 0300 CDT on 8/1/2016. "HPCI was being returned to service after the planned maintenance period. The inboard isolation valve and the bypass around the outboard isolation valve were open to warm and pressurize the HPCI steam line. HPCI steam line pressure stabilized at approximately 50 psig. The outboard isolation valve was slowly opened to determine if the inboard isolation valve was actually open. There was no change in steam line pressure or indications of flow at the valves. Based on this information, the HPCI Steam Line Inboard Isolation Valve was declared inoperable for its Primary Containment Isolation function. The appropriate Technical Specification Limiting Conditions for Operation (LCOs) were entered and the HPCI steam line was isolated. "This constitutes an unplanned HPCI system inoperability and requires an 8 hour ENS notification in accordance with 10 CFR 50.72(b)(3)(v)(D), due to the failure of a single train system affecting accident mitigation and a 60 day written report in accordance with 10 CFR 50.73(a)(2)(v)(D). "The Senior NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-07-20
52112 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-07-13 09:44 | 2016-07-20 15:47 | 2016-07-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received via e-mail: "Manufacturer: Isolite, Model # SLX 60, 10 Ci tritium, "[Tritium exit signs were shipped from the] manufacturer on 2/5/2009. The serial number of the isotope was not provided. Further information was requested from the company "In processing the annual general license reports from CDPHE [Colorado Department of Public Health and Environment] one exit sign was not located. The sign is being reported as lost/abandoned. The company contact will continue to search for the sign, however, [the company] is reporting it as lost. "Signs were purchased as part of a construction project in which 2 of the 10 signs ordered were not installed in the building. It may be in storage but it has so far not been located." Colorado Event: CO16-I16-16 CO 160009 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-07-28
52111 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-07-20 12:30 | 2016-07-20 15:48 | 2016-07-20 | AGREEMENT STATE REPORT - LOSS OR THEFT OF DEPLETED URANIUM OXIDE The following report was received via e-mail: "On Monday, July 18, Manufacturing Sciences Corp. [MSC] shipped five pallets (18 drums) of product containing depleted uranium oxide [DU] to a customer, Clariant, in Louisville, KY. On Wednesday, July 20, the customer contacted MSC to report only four pallets containing 14 drums were received by Clariant. When the bill of lading was examined by the customer, 5 and 18 had been marked through by hand and changed to 4 and 14. The carrier, was contacted and is conducting a thorough search of its terminal and investigating to locate the missing material. The carrier is routinely used by MSC for transport of product. Total activity of missing material: 271,285 microcuries DU." Tennessee Report: TN-16-100 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-07-28
52110 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-07-18 17:05 | 2016-07-20 15:14 | 2016-07-20 | AGREEMENT STATE REPORT - RADIOGRAPHER UNPLANNED EXPOSURE The following report was received via e-mail: "On July 18, 2016, at approximately 1705 MT, the Colorado Department of Public Health and Environment received a call on its incident notification phone from the acting Radiation Safety Officer (RSO) for Mistras Group, Inc., (CO License CO 963-01). The acting RSO reported that while a Grand Junction, CO based crew was performing industrial radiography activities at a fabrication shop/area in Coburn, CO on June 18, 2016. A radiographer received an estimated whole body dose of approximately 500 mrem, and an estimated extremity dose of approximately 12 rem (12,000 mrem) due to the radiographer handling the guide tube while the source was still present in the guide tube. The source had reportedly become hung up in the guide tube, but at the time of the exposure the radiographer believed the source had been returned to the shielded position. The radiographer was not reportedly using a survey instrument at the time he approached the source just prior to the exposure event. The assistant radiographer remained near the source crank and did not have direct contact with the source containing guide tube. The assistant radiographer reportedly received approximately 20 mrem (whole body dose), based upon his pocket dosimeter reading. The source in use at the time of the incident was contained in a SPEC 150 imaging device with approximately 60 Ci of Iridium-192. Dosimeters for the radiographer and assistant radiographer have been submitted to the licensee dosimetry provider and results are pending. The radiographer has been restricted from further work involving radioactive materials until the licensee can complete an investigation. The guide tube equipment has been taken out of service and is being evaluated by the licensee for possible defects." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-07-28
52109 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-07-20 | 2016-07-20 12:04 | 2016-07-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following is a synopsis of information received via e-mail: The current property manager for Colorado Springs II Silvercrest Apartments completed an inspection of the facility without locating any tritium exit signs in their buildings. Two fire safety companies provided safety signs over a period of 16 years and no tracking records were kept regarding the disposition of tritium exit signs or their disposal. The current fire safety company has no further information regarding the disposition of the exit signs. Six Tritium Exit signs had been shipped from the manufacturer on 12/13/2000 to Colorado Springs II Silvercrest Apartments. Since these signs could not be located, they are being reported as lost. These six signs were manufactured by Safety Light Corporation, model number - 2040, serial numbers - unknown. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-07-28
52108 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2016-07-19 14:00 | 2016-07-20 11:34 | 2016-07-20 | MOISTURE/DENSITY GAUGE DESTROYED IN A TRUCK FIRE The following report was received via e-mail: "Yesterday, July 19, 2016, at approximately 1400 [CDT], the state of Kansas was notified of damage sustained to a portable moisture/density gauge. The gauge was a Troxler 3430 #32870 containing 8mCi Cs-137 and 40 mCi AM-241:Be. Building Earth Sciences Inc., under reciprocity (Kansas #2016-052/Alabama lic #1266) was in a field 20 miles South of Dodge City, Kansas. Due to high grass and extreme temperatures, the vehicle caught on fire with the portable gauge located in the bed of the truck. The vehicle and gauge were completely destroyed. At that time, no survey meter was onsite so Terracon was contacted in Garden City to utilize a loaner survey meter. The survey meter brought to the site was not in calibration. Surveys were conducted of the wreckage at one meter at around 1500 that showed approximately 0.2 mR/hr exposure rate from all sides. The Senior Project Manager onsite, had contacted the RSO, located in Alabama, who was already on his way to the site. [The Senior Project Manager] stated that a calibrated survey meter and Type A overpack had already been dispatched from the Building Earth Sciences Inc. Tulsa OK office and would be onsite no later than 1900. [The Senior Project Manager] stated that the wreckage had been fenced off and that he was staying onsite until the meter and overpack arrived. It was at this time that the state of Kansas made the determination not to send anyone out to the site as the overpack coming from Tulsa would be arriving well before anyone from Topeka could get to the site. At 2000 [CDT], July 19, 2016, [the Kansas Department of Health and Environment] received notification of confirmatory (calibrated) survey data of no greater than 0.2 mR/hr at one meter as well as the gauge debris having been placed within the overpack. (Survey meter - Troxalert cal date 8/3/15, serial number13385.) Surveys were also conducted of the truck wreckage after the gauge debris had been placed into the Type A overpack, with no contamination found confirming the integrity of the source remained intact. The overpack was then transported to the Building Earth Sciences Inc. Tulsa, OK, office. The RSO, will be submitting a full written preliminary report and timeline as soon as all information becomes available. NMED entry is forthcoming." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2016-07-28
52107 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-07-20 11:30 | 2016-07-20 12:02 | 2016-07-21 | TECHNICAL SUPPORT CENTER VENTILATION OUT-OF-SERVICE FOR PLANNED PREVENTATIVE MAINTENANCE "At 1130 CDT on Wednesday, July 20, 2016, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system will be removed from service for planned maintenance activities. During the maintenance, the TSC ventilation will be shut down. The TSC air filtration fan and dampers will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out-of-service time. The planned TSC ventilation outage is scheduled to be completed in approximately 14 hours. "Contingency plans are in place so that if an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Planning (EP) procedures and checklists. If radiological or environmental conditions require TSC facility evacuation during ventilation system restoration, the Station Emergency Director will relocate the TSC staff in accordance with station procedures." "The NRC Resident Inspector has been notified." * * * UPDATE FROM RYAN CHAMBERLAIN TO DANIEL MILLS ON 07/21/2016 AT 1757 EDT * * * "At 1619 CST on July 21, 2016, Dresden TSC ventilation has been restored and is now functional." The licensee has notified the NRC Resident Inspector Notified R3DO (Stone). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-20
52106 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-07-13 11:00 | 2016-07-19 17:58 | 2016-07-19 | EXERCISE PRESS RELEASES AIRED ON RADIO AS AN ACTUAL EVENT "During the planned NRC/FEMA evaluated drill exercise on 7/13/16, two press releases written in the Joint Information Center (JIC) were published in the Public Information and Emergency Response (PIER) system without 'THIS IS A DRILL' denoted at the top of the page. The original press release was stamped with 'THIS IS A DRILL' at the top of page 1 and at the bottom of page 2. When it was added into the PIER system for publication/faxing, it was not noticed the top of the document denoting 'THIS IS A DRILL' was cut off. "The local radio station affiliate was not aware of STP's [South Texas Project's] exercise on 7/13/16. As a result, the affiliate station thought it was a real event and read the press releases over the airwaves at 1014 [CDT] and again at 1046 [CDT]. "At approximately 1400 [CDT] on the same day, the radio station told their listening audience of the mistake and stated STP was having a training exercise not a real event. The correction was broadcast over the airwaves three times every hour until midnight. "This unplanned media event is being reported in accordance with 10CFR50.72(b)(2)(xi). This event is not significant with respect to the health and safety of the public." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-07-19
52105 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2016-07-17 07:30 | 2016-07-19 17:31 | 2016-09-13 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "At 0730 [CDT], July 17, 2016, an incident occurred at a temporary job site. The incident occurred when a water truck operating on the construction site came into contact with the moisture density gauge, causing damage to the source rod and casing. Licensee and Corporate RSO notified Mississippi Department of Health on July 18, 2016 about the incident. "With Terracon having taken their gauge back to Little Rock, Arkansas, the Mississippi Department of Health sought out inspectors from Arkansas Department of Health to gather information from Terracon's local office. "According to the inspectors sent by Arkansas Department of Health, the individual at the site of the incident had established a 15 foot radius around the gauge. The water truck and driver were requested to stay at the site until the Corporate Radiation Safety Officer was notified. Another employee was sent to the incident site with a TroxAlert meter. The radiation survey meter was current on calibration. "The gauge involved in this incident is a Troxler Model 3440 Serial Number 25123 with an Am-241 [source], Serial Number: 47-21331 and Cs-137 [source], Serial Number: 75-7299. The readings were completed by Arkansas Department of Health with a Ludlum Model 3, SN 62645, and calibration date: 02/03/2016. "Once readings were complete, the Corporate RSO allowed the water truck and driver to leave and to bring the gauge back to Little Rock, AR. The gauge was then put back together and stored in their secured storage location inside the Terracon building. Additional readings were taken on July 18, 2016 at approximately 0830." Sources: Am-241 - 40 mCi: Cs-137 8 mCi Incident Number: MS-16004 * * * UPDATE FROM BENJAMIN CULPEPPER TO STEVEN VITTO ON 09/13/2016 AT 1154 [EDT] * * * The following report was received via e-mail: "The gauge was examined by the Arkansas Department of Health on July 18, 2016, in Terracon's Little Rock office and a leak test was performed by both Terracon and Arkansas Department of Health. The resulting leak tests showed that the source was not damaged, and a copy of those leak tests were provided to the Mississippi State Department of Health. "The gauge technician involved in the incident has been through additional training on gauge usage including transportation and security. Terracon's accountability process was initiated at their Arkansas location as well as the retraining. "Terracon was issued violations for not properly contacting Mississippi State Department of Health and Arkansas Department of Health about the event. The Corporate RSO for Terracon responded to both violations issued from both State Health Departments. Their response was found to be adequate in correcting the items of noncompliance during this investigation. "The Arkansas Department of Health sent Mississippi State Department of Health confirmation that Terracon has addressed the issued violations adequately on September 12, 2016." Notified R4DO (Azua) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2016-07-27
52104 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2016-07-18 14:50 | 2016-07-18 23:29 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "This telephone notification is provided in accordance with the Exelon Reportability manual, 'Major Loss of Emergency Preparedness Capabilities', and 10 CFR 50.72(b)(3)(xiii). "On July 18, 2016 at 1500 CDT, it was determined during testing of the Everbridge ERO [Emergency Response Organization] notification system that the system would not notify the corporate EOF [Emergency Operations Facility] individuals if the system had been activated. This constitutes a loss of offsite communication capability. Exelon and Everbridge have identified and corrected this issue. A follow-up test of the LaSalle Everbridge ERO notification system was completed satisfactorily on July 18, 2016 at 2100. "The Emergency Response Data System (ERDS) capability was not lost. "The licensee has notified the [NRC] Senior Resident Inspector of the issue." Compensatory measures were in place during this event. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52103 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-07-18 15:00 | 2016-07-18 23:20 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "Testing of the Offsite Emergency Response Organization (ERO) notification system (Everbridge) identified that the system cannot notify all ERO individuals. This constitutes a loss of offsite communications capability. "The Offsite ERO notification system (Everbridge) capability loss for Braidwood was identified at approximately 1500 CDT on July 18, 2016, due to an undetermined loss of system communications, which is currently being investigated. "The Offsite ERO notification system (Everbridge) capability loss for the common Emergency Response Facility (ERF), (i.e. the Emergency Offsite Facility at Cantera) was identified at approximately 1500 CDT on July 18, 2016. "The issue has subsequently been reported resolved by the vendor at 1912 CDT and site testing has verified resolution at 2108 CDT. "The onsite communication system was not affected. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a loss of communications capability. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52102 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-07-18 15:00 | 2016-07-18 22:43 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "Testing of the Everbridge ERO [Emergency Response Organization] notification system identified the system cannot notify all ERO individuals. This constitutes a loss of offsite communications capability. The issue has subsequently been reported resolved by the vendor. "Emergency Response Data System (ERDS) capability was not lost. "The Everbridge system capability loss for the common ERF (EOF at Cantera) was identified at approximately 1500 CDT on July 18, 2016. Site and EOF testing verified resolution at 2029 CDT. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a loss of communications capability." The licensee will notify the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52101 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-07-18 16:00 | 2016-07-18 22:43 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "Testing of the Everbridge ERO [Emergency Response Organization] notification system identified the system was not able to notify all ERO individuals. This constitutes a loss of offsite communications capability. The issue was subsequently reported resolved by the vendor and site testing has verified resolution at 2037. "The Everbridge system capability loss for Limerick was identified at approximately 1600 EDT on July 18, 2016, due to a loss of system communications. Emergency Response Data System (ERDS) capability was not lost. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a loss of communications capability. "The NRC Resident inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52100 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-07-18 15:00 | 2016-07-18 22:26 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "During testing of the Everbridge Emergency Response Organization (ERO) notification system, it was found that the system may not have notified corporate ERO members within the required ten minutes from system initiation. This constitutes a loss of offsite communication capabilities. The Everbridge vendor has since restored and successfully tested the system. Additionally, the site successfully conducted an ERO call-in drill using the same Everbridge notification system. "The Emergency Response Data System was not affected. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) as a loss of communications capability. "The NRC Resident Inspector has been notified." The requirement is to have all ERO personnel receive the page within ten minutes. Compensatory measures were instituted while the system was not functional. The system was returned to service at 2100 CDT following repair and testing. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52099 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2016-07-18 14:50 | 2016-07-18 22:21 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "Testing of the Everbridge ERO [Emergency Response Organization] notification system identified that the system cannot notify all ERO individuals. This constitutes a loss of offsite communications capability. The issue has subsequently been reported resolved by the vendor and both site testing and common ERF [Emergency Response Facility] (EOF [Emergency Operations Facility] at Cantera) has verified resolution. "The Everbridge system capability loss for Quad Cities was identified at approximately 1450 (CDT) hours on July 18, 2016, due to an undetermined loss of system communications, which is currently being investigated. Emergency Response Data System (ERDS) capability was not lost. "The Everbridge system capability loss for the common ERF (EOF at Cantera) was identified at approximately 1500 (CDT) on July 18, 2016. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a loss of EP offsite communications capability. "The NRC Resident inspector has been notified." The site was developing compensatory measures when the event was terminated. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52098 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-07-18 15:00 | 2016-07-18 22:07 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "Testing of the Everbridge ERO [Emergency Response Organization] notification system identified that the system cannot notify all ERO individuals. This constitutes a loss of offsite communications capability. Compensatory measures (ERO phone lists) were put in place. "The Everbridge system capability loss for Dresden Station was identified at 1500 CDT on July 18, 2016, due to an undetermined loss of system communications. Emergency Response Data System (EROS) capability was not lost. "This event is reportable under 10 CFR 50.72(b)3(xiii) as a major loss of communication capability. "On July 18, 2016 at 1957 CDT, an Everbridge ERO call in drill was initiated and verified successful at 2030 CDT. "The NRC Resident Inspector has been notified." Some of the ERO personnel did not receive a test page. The requirement is to have all ERO personnel receive the page within ten minutes and to be fully staffed within one hour. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52097 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2016-07-18 16:00 | 2016-07-18 21:41 | 2016-07-18 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "At 1600 EDT, testing of the Everbridge ERO [Emergency Response Organization] notification system identified the system was not able to notify all ERO individuals. This constitutes a loss of offsite communications capability. The issue was reported resolved by the vendor and site testing has verified resolution as of 2130. "This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a loss of communications capability. "The NRC Resident Inspector has been notified." Some of the ERO personnel did not receive a test page. The requirement is to have all ERO personnel receive the page within ten minutes. Compensatory measures were instituted while the system was not functional. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52096 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2016-07-18 07:30 | 2016-07-18 14:48 | 2016-07-20 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY "This 8-hour non-emergency report is being made based upon requirements of 10 CFR 50.72(b)(3)(xiii) which states, 'The licensee shall notify the NRC as soon as practical and in all cases within eight hours of the occurrence of any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system).' "On 07-18-2016 at 0730 [EDT], both Control Rooms were notified by the Emergency Preparedness Manager, that the Everbridge Emergency Response Organization [ERO] Notification System may not notify all ERO individuals within the required 10 minutes of system initiation. This constitutes a loss of offsite communications capability. The Everbridge vendor is working to resolve the issue. Compensatory measures are in place." All ERO personnel received the page but not all received the notification within the required ten minutes. The licensee notified the NRC Resident Inspector and the State. * * * UPDATE AT 1728 EDT ON 7/20/2016 FROM CLARK WILLETT TO MARK ABRAMOVITZ * * * "The Everbridge System was restored and retested at 1930 EDT on 7-19-2016 to provide offsite communications capability." The licensee notified the NRC Resident Inspector and the state. Notified the R1DO (DeFrancisco). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-18
52095 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2016-07-14 19:35 | 2016-07-15 14:21 | 2016-07-15 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL DELIVERED TO PRIVATE RESIDENCE The following was received via facsimile: "[Maine Radiation Control Program (MRCP)] was called by [Chase Environmental] at 1935 [EDT] on 7/14/2016. [Chase Environmental] had been contacted (indirectly) by HAZ-MAT One regarding a radiological emergency in Waterford, Maine. [Chase Environmental] had contacted HAZ-MAT One directly and was told that a radioactive package had been delivered, incorrectly, to a private address. [Chase Environmental] was told the package was intact and that the shipping company (YRC) was going to retrieve the package and get it to its addressed location. When [MRCP] contacted HAZ-MAT One on the morning of 7/15/2016, they reported that the correct delivery address for the package was QSA Global in Burlington, MA and that the private residence had ordered a lawn mower. [MRCP] contacted QSA and informed them of the package that was coming and asked the particulars of the package. [MRCP] contacted YRC Freight to obtain more information regarding the package and got the tracking number for the package and that it had been retrieved and was enroute to the YRC terminal in Westbrook, Maine by roughly 1000 [EDT]. [MRCP] called [QSA Global] and gave them the tracking number, then tracked the package and found that it had been delivered to Waterford Maine on or about 6/15/2016. [QSA Global] called [MRCP] back and informed [MRCP] that the package was a 650 source exchanger, with a six (6) curie Iridium 192 source in it from Guatemala. The package had evidently fallen into the box or crate of a lawn mower during shipment and been delivered to the Waterford, Maine address. Additional information regarding dose reconstruction and leak test/package condition will be forthcoming when the package gets to QSA Global in the next few business days. "Event Report ID: ME-16-001" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2016-07-25
52094 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-06-17 | 2016-07-15 14:24 | 2016-08-08 | AGREEMENT STATE REPORT - RADIOACTIVE NEEDLE FOUND The following was received via email: "On June 17, 2016, RSO, Inc., contacted Virginia Radioactive Material Program (RMP) to arrange an investigation on a lead pig found at Hollins University, Roanoke, Virginia. On June 22, 2016, two inspectors from the RMP went to the University to observe the investigation performed by Health Physicist from the RSO, Inc. The lead pig was found inside the drawer in Dana Science Building Chemistry Lab. A radiation level of 12 mR/hr was measured at about one foot from the pig. The Health Physicist used a hand-held gamma spectrometer (Bicron Identifier) to identify the radionuclide as Ra-226. The health physicist performed calculation and also opened the pig carefully to identify the type of Ra-226. He developed and followed safety procedures to open the pig. Leak tests were performed and no removable contamination was detected. "Based on the Health Physicist's investigation and activity calculation, the pig contains a one millicurie (1 mCi) Ra-226 needle. "RSO, Inc., is currently working with the University to arrange for the disposal of the source. This report will be updated when the RMP received the final disposal report. "Event Report ID: VA-16-11" * * * UPDATE FROM ASFAW FENTA TO STEVEN VITTO AT 1632 EDT ON 08/08/16 * * * The following was received from the Commonwealth of Virginia via email: "The source in the lead pig was found in a desk drawer of a fume hood located in a small room (10' x 10') of the main chemistry lab. The door to the room is only accessed through the chemistry lab. Based on discussions with Hollins University, the professor who used the source left the university 15 years ago. The room and source have not been used since his departure. The pig was kept inside the drawer shielded with lead brick. The drawer and room were labeled 'Caution Radioactive Material' and the room remained locked. "The hired consultant performed radiation surveys while the pig was shielded by the lead brick as found, and confirmed it was less than the unrestricted area limit of 2 mrem in any 1 hour, and would not result in a dose to member of the public of 100 mrem per year. Exposure rates taken by the consultant with the source unshielded indicated a reading of 8.5 mR/hr at 30 cm, and 0.8 mR/hr at 1 m. This corresponds to an activity of approximately 1 millicurie (mCi) using a gamma ray constant of 0.825 (mR m2)/(mCi hr). "Other non-licensable material was found in the desk. "On 07/27/2016, the hired consultant packaged all of the radioactive materials and transferred them for disposal. "This case is considered closed by the [Virginia Radioactive Material Program] VRMP." Notified R1DO (Burritt) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-07-25
52093 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-07-13 | 2016-07-15 14:36 | 2016-07-15 | AGREEMENT STATE REPORT - UNDERDOSE MEDICAL EVENT The following was received via email: "Event Description: A patient was undergoing a Y-90 Therasphere procedure in two separate treatments (to different liver segments). The delivery kits for both administrations passed the standard pre-administration testing. The physician and team noted no other equipment related issues until the administering Interventional Radiologist Physician noted unusual resistance during the first actual administration. After unsuccessful attempts to 'clear the line,' the efforts to complete the administration were terminated. The team then attempted to treat a second site, with essentially the same sequence of events occurring. Both delivery sets came from the same manufacturing lot, and both dosages of Theraspheres came from the same drug lot. The licensee estimates approximately 25 percent of the written directive dose was delivered. "Cause of the Event: Unknown at this time. It is worth noting, another Theraspheres administration on another patient was performed the following day without incident. The delivery system kits were again from the same lot as those used on the previous day, but the Therasphere dosage was from a different lot. "Actions: Licensee notified Nordion of the occurrence. The Department [PA Department of Environmental Protection] will perform a reactive inspection next week. "Event Report ID: PA160019" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-07-25
52092 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-07-13 | 2016-07-15 14:13 | 2016-07-15 | AGREEMENT STATE REPORT - FAILURE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following was received via email: "The lock on a radiography camera did not spring back into place when the radiographer retracted the cable and source into the shielded position. He [the radiographer] was able to crank the source back out and when he retracted it back into the camera the second time, the lock sprung closed and secured the source. There was no unexpected radiation exposure to the employee or to the general public. The entire incident lasted less than 10 seconds. Due to the apparent equipment failure it is reportable under 10 CFR 30.50(b)(2). "The device is identified as: Manufacturer: QSA Global Model #: 880 Delta Device Serial #: 1636 Isotope: lr-192 Activity: 34 Ci "The licensee (System One) is going to conduct an internal investigation to determine the cause of the malfunction. The Department [Pennsylvania Bureau of Radiation Protection] will be scheduling a reactive inspection. "Event Report ID: PA160018" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-07-25
52091 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-07-14 13:51 | 2016-07-15 10:27 | 2016-07-15 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the State of Colorado via email: "Detail: The project manager for a newly constructed apartment complex ordered exit signs to be installed. The distributor (LEI Companies) ordered them from a local supplier (Gexpro). The distributor is unable to locate the exit signs. It is unknown as to what occurred with the signs not being installed at the apartment complex nor being returned to their company. Exit signs are reported as lost. "Manufacturer: SRB Technologies, Winston-Salem, NC; Model # BX-10-WH; Serial # C121961, C121962, C121963, C121964, and C121965; Date Shipped: 4-16-15. "Designated for: Denizen Apartments, Denver, CO. Ordered through Gexpro, Denver, CO by LEI Companies. "Event Description: Gexpro reported the exit signs were picked up by an employee of LEI Companies and were not returned. LEI Companies has documentation to return them, however, no record of exit signs being returned has been located. Denizen Apartments never received nor had exit signs installed." Colorado Event: CO16-I16-12 NMED: C160006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-07-25
52090 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2016-07-13 | 2016-07-14 18:49 | 2017-08-18 | DEGRADED SAFETY ITEMS CAUSED BY URANIUM BUILDUP "On July 13, 2016, it was determined by the Environment, Health and Safety (EH&S) department that scrubber clean-out material, found in the S-1030 scrubber transition section during the annual maintenance shutdown that occurred in late May, potentially exceeded the uranium mass limit for the scrubber transition. "(IROFS [Items Relied on for Safety] VENT-S1030-110) requires annual inspection and removal of significant solids buildup in the transition section. Upon inspection, significant buildup was found, and the ductwork was opened to permit extensive cleanout. 36 containers of material with a total gross weight of 210.4 kg was removed from the inlet transition during the cleanout on May 28th to May 29th. Grab samples were subsequently taken from each container and analyzed for uranium concentration. On July 13th, the EH&S department was made aware that the grab sample results averaged 47.8% U. Although the exact uranium mass cannot be determined until the material is dissolved and representatively sampled, available evidence suggests that the mass limit of 29 kg U in the inlet transition was exceeded. The 29 kg U limit is based on an optimally moderated, fully reflected spherical geometry which very conservatively bounds the conditions in the inlet transition of the scrubber. IROFS remained to limit the quantity of uranium available to the scrubber (IROFS VENT-S1030-101, -102, -103 & -104), which are physical barriers designed to minimize uranium in the airflow entering the transition area. Continuous liquid spraying in the inlet transition section to limit solids accumulation (IROFS VENT-S1030-109) was also in place. "The inlet transition and scrubber were thoroughly cleaned, and the uranium bearing solids were placed into favorable geometry containers. Also, the inspection and cleanout of the transition frequency was increased to monthly. "Based on available but degraded IROFS, this accident sequence was unlikely. Therefore, this mass accident sequence does not meet the performance requirements of 10CFR70.61. The actual configuration remained safe at all times. Also, no external conditions affected the event. "Immediate Corrective Actions: NRC Region II personnel, who were onsite at the CFFF [Columbia Fuel Fabrication Facility], were made aware of the discovery. "The Conversion area was shutdown to plan for a second extensive scrubber clean-out to validate that the accumulation of solids is a slow buildup over time. The last extensive cleanout was performed in 2009. "An extent of condition was performed to determine if other scrubbers potentially had significant uranium buildup. Inspection data indicated that this material accumulation issue was limited to the S-1030 scrubber. "This event has been entered into the facility Corrective Action Prevention And Learning system (CAPAL) #100397353." * * * UPDATE PROVIDED BY NANCY PARR TO JEFF ROTTON AT 1025 EDT ON 07/26/2016 * * * "Onsite chemical analysis confirmed that uranium mass limit for the scrubber transition piece was exceeded. The accumulated material contained 87 kgs of Uranium. "The Criticality Safety Evaluation for this system was revised and implemented on July 20, 2016 to add Items Relied on For Safety to prevent recurrence of a mass exceedance while the causal analysis and additional corrective actions are completed." Notified R2DO (Nease) and NMSS Events Notification Group via email. * * * UPDATE PROVIDED BY NANCY PARR TO HOWIE CROUCH AT 1749 EDT ON 07/31/2016 * * * "On July 31, 2016, it was determined by the Environment, Health and Safety (EH&S) department that clean-out material found in the S-1030 scrubber packing and floor also potentially exceeded the uranium mass limit for the scrubber criticality safety evaluation. Over years of operations, the same available but degraded mass prevention and inspection/clean-out IROFS did not prevent exceedance of the mass limit. "This report is being upgraded to a 1 Hour Event Notification based on 10CFR70 Appendix A(a)(4). "There was no consequence to the public, the workers or the environment. "The scrubber process will remain in a safe shutdown mode until further investigation and corrective actions are completed." Notified R2DO (Rose), IRD (Grant), NMSS EO (Kotzalas) and NMSS Events Notification via email. * * * UPDATE FROM JOHN HOWELL TO VINCE KLCO AT 1620 EDT ON 8/7/2016 * * * "On August 6, 2016 at 1700, it was reported to the Environment, Health and Safety (EH&S) department that residual material located within the abandoned S-1056 scrubber was sampled and confirmed to contain Uranium. "24 Hour Event Notification based on 10CFR70 Appendix A(b)(1) 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10CFR70.61.' "The S-1056 is an out-of-service scrubber. When operational, it scrubbed the acid fumes from the Conversion area. It currently is an unanalyzed system without IROFS or controls. The reported volume of approximately 15 kg is well within safety margins. "It was taken out of service in 2002, when the S-1030 scrubber replaced it. The material in the S-1056 was discovered as an extent of condition for the S-1030 event. "The discovery and sampling were documented in Redbook 71409. At no time was there any actual or potential health and safety consequence to the workers, the public, or the environment." The licensee notified the NRC Regional Inspector (Lopez). Notified the R2DO (Suggs), R2RA (Haney) and NMSS Events Notification Group via email. * * * UPDATE AT 1546 EDT ON 8/23/16 FROM NANCY PARR TO JEFF HERRERA * * * "On August 23, 2016, during the extent of condition for this S-1030 scrubber system event, a review of inspection video for the S-1030 ductwork in Conversion identified material accumulation in an elbow which potentially could exceed the uranium mass limit for the elbow section (36.5 kgU). "This report is being updated based on a potential to meet the 10 CFR 70 Appendix A(a)(4) in the ductwork. "There was no consequence to the public, the workers or the environment. "The scrubber process will remain in a safe shutdown mode until further investigation and corrective actions are completed." The Region IV Project Managers were notified. Notified the R2DO (Michel), IRDMOC (Stapleton) and NMSS Events Notification Group (via email). * * * UPDATE AT 1810 EDT ON 9/15/16 FROM NANCY PARR TO DANIEL MILLS * * * "24-Hour Event Notification based on 10 CFR 70 Appendix A(b)(1) 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10 CFR 70.61.' "On September 15, 2016 at 1204 EDT, it was reported to the Environment, Health and Safety (EH&S) department that residual material was located within the abandoned 3A/3B ventilation system. Based on gamma radiation surveys, the material contains Uranium. "The 3A/3B system was taken out of service in 2002, when the S-1030 scrubber replaced it. When operational, it removed chemical fumes and particulate matter from the Conversion area. The material in the system was discovered as an extent of condition for the S-1030 event. "When taken out of service, the system was isolated from the introduction of any additional material and/or moderator. However, because the system is out of service, it is considered an unanalyzed system without IROFS or controls. The reported depth of material in the duct appears well within analyzed safety margins for similar systems. "At no time was there any actual or potential health and safety consequence to the workers, the public, or the environment. "UPDATED INFORMATION FROM AUGUST 23, 2016 NOTIFICATION: This notification also serves to update previously reported information provided on August 23, 2016 where a review of inspection video for the S-1030 ductwork in Conversion identified material accumulation in an elbow which potentially could exceed the uranium mass limit for the elbow section (36.5 kg U). This report was made based on a potential to meet the 10 CFR 70 Appendix A(a)(4) in the ductwork. The material was removed from the ductwork and weighed. The total weight of the material removed was 5.5 kgs in the elbow and 3.0 kgs in a horizontal section of the duct, which is well below the mass limit in the safety basis. Therefore, the information from the August 23, 2016 potential report is retracted." Notified the R2DO (Walker) and NMSS Events Notification Group (via email). * * * UPDATE AT 1701 EDT ON 10/05/16 FROM NANCY PARR TO JEFF HERRERA * * * "On October 4, 2016 at approximately 1700 EDT, while performing housekeeping and cleanout activities on the out of service 3A and 3B ductwork, degradation was discovered in an area not routinely or readily accessed in the bottom of the out of service filter house system. This discovery was made while performing clean-out activities covered under a Radiation Work Permit (RWP). "The work was stopped, and Health Physics (HP) performed contamination surveys of the area. The degraded area was sealed and isolated. No additional radiological controls were needed, and access to the area was not restricted. "No degradation was found in other out of service systems on the roof. A comprehensive extent of condition is ongoing. "There was no actual or potential health and safety consequence to the workers, the public, or to the environment during this time." Notified the R2DO (Bonser) and NMSS Event Notification Group (via email). * * * UPDATE AT 1113 EDT ON 08/18/17 FROM NANCY PARR TO BETHANY CECERE * * * "On August 17, 2017 at 11:17 a.m., it was reported to the Environment, Health and Safety (EH&S) department that additional residual material located within the out of service S-1056 scrubber was found. Material in this out of service system was previously reported on August 7, 2016. The material was removed and placed into favorable geometry storage. The material has been quantified and determined to contain less than 80 grams of uranium, which is well within safety margins. "This information is being reported in accordance with the 24 Hour Event Notification criterion: 10 CFR 70 Appendix A(b)(1), 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10 CFR 70.61.' "The buildup was not visible until dismantling the abandoned equipment for removal from the roof. Demolition and removal has already been completed for ventilation system filter houses 2A, 2B, 3A, 3B and 7A. "The discovery and sampling were documented in Redbook 72846 and in CAPAL 100488919. At no time was there any actual or potential health and safety consequence to the workers, the public, or the environment." The licensee discussed this report with NRC Region 2 (Vukovinsky and Michel). Notified the R2DO (Sykes) and NMSS Event Notification Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | UNANALYZED CONDITION | [8 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (a)(4) | PART 70 APP A (b)(1) |  |  | 0 | 2016-07-14
52089 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-07-12 | 2016-07-14 17:24 | 2016-07-14 | AGREEMENT STATE REPORT - FIXED GAUGE FOUND AT METAL RECYCLING FACULTY The following report was received from the Commonwealth of Virginia via facsimile: "On July 12, 2016, Sims Metal Recycling, Richmond Virginia, reported to the Virginia Radioactive Material Program (VRMP) that a radioactive source had been found in a shipment of metal. They said the source was a gauge like the one found the previous day in their Petersburg Virginia Facility [see EN #52088]. Refer to VA-16-008. VRMP Radiation Safety Specialists performed an onsite review. Labels indicated that the source was a general license device from EG&G Berthold, model not identified, serial number 001095, with a 100 millicurie (September 1990) cesium-137 source, serial number 3023. Maximum radiation levels at contact at the mounting near the shutter were 2 mR/hr, at three feet, maximum levels were less than 0.1 mR/hr. The gauge was placed in a drum in a secured area. Dose estimates by VRMP health physicists indicated no individual was likely to have received more than 1 mrem whole body or 5 mrem extremity dose. On-site tests for leakage indicated no removable contamination. The recycling facility will contact a waste broker to arrange for disposal. The gauge owner was not identified from review of the VRMP general license database. Berthold Technologies USA is reviewing records to identify the owner of the gauge. Virginia Event Report ID No: VA-16-009 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-07-22
52088 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-07-11 | 2016-07-14 17:20 | 2016-07-14 | AGREEMENT STATE REPORT - FIXED GAUGE FOUND AT METAL RECYCLING FACULTY The following report was received from the Commonwealth of Virginia via facsimile: "On July 11, 2016, Sims Metal Recycling, Petersburg, Virginia, reported to the Virginia Radioactive Material Program (VRMP) that a radioactive source had been found in a shipment of metal. VRMP Radiation Safety Specialists performed an onsite review. Labels indicated that the source was a general license device from EG&G Berthold, model not identified, serial number 001098 with a 100 millicurie (September 1990) cesium-137 source, serial number 3027. The shutter was locked partially open with the opening behind part of the gauge mounting. Maximum radiation levels at contact at the mounting near the shutter were 5 mR; at three feet, maximum levels were less than 0.1 mR/hr. The gauge was placed in a drum using a mechanical hoist and the drum was placed in a secured area. Dose estimates by VRMP personnel indicated no individual was likely to have received more than 1 mrem whole body or 5 mrem extremity dose. On-site tests for leakage indicated no removable contamination. The recycling facility contacted RSO, Inc., a commercial firm, to arrange for disposal. The gauge owner was not identified from review of the VRMP general license database. Berthold Technologies USA is reviewing records to identify the owner of the gauge." Virginia Event Report ID No.: VA-16-008 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-07-22
52087 | 0 | U.S. ARMY |  |  |  |  | 2016-07-13 15:50 | 2016-07-14 15:47 | 2016-07-14 | LOST/STOLEN U.S. ARMY RADIOACTIVE CHEMICAL ALARMS On July 13, 2016, the U.S. Army TACOM Radiation Safety Program Manager in Warren, MI was notified of a misplaced U.S. Army chemical alarm containing 250 microcuries of Am-241 from a U.S. National Guard Unit in North Carolina. The chemical alarm was misplaced on April 21. Since the material has not been recovered, the U.S. Army considers the material lost/stolen. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-07-22
52086 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2016-07-14 07:41 | 2016-07-14 15:15 | 2016-07-14 | VIOLATION OF THE FITNESS FOR DUTY (FFD) PROGRAM POLICY "On 7/14/16, at 0741 [EDT], it was determined that [a contract employee supervisor] violated its FFD policy. The individual's construction site access has been revoked. This event is reportable pursuant to 10 CFR 26.719(b)(2)(ii). "The Units 2 and 3 [NRC] Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2016-07-14
52085 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-07-14 09:15 | 2016-07-14 13:01 | 2016-07-14 | OFFSITE NOTIFICATION OF GOVERNMENT AGENCIES OF AN OIL SPILL TO THE ENVIRONMENT "At 0915 EDT on July 14, 2016, Fermi 2 Environmental Engineering determined that a notification to the State of Michigan Department of Licensing and Regulatory Affairs, Bureau of Fire Services, Storage Tank Division is required regarding discovery of a leaking underground fuel oil storage tank. The underground fuel oil storage tank was unearthed while excavating for 120kv switchyard cable replacements. This is an underground fuel oil storage tank from the 1950s or earlier was not in service at the site, and it is unknown when the tank was last used. The size of the tank is estimated at 2,250 gallons. An unknown quantity of oil has leaked into the immediate surrounding ground and is currently contained in the soil. There is currently no indication of any of the leakage flowing beyond the site boundary or reaching any waterways. Fermi 2 is conducting an investigation to determine the appropriate steps to address the storage tank and impacted soil. "A notification to the U.S. Environmental Protection Agency is not required. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) for an event or situation related to the protection of the environment for which a notification to another government agency will be made. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-07-14
52084 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-07-13 19:55 | 2016-07-13 22:43 | 2017-03-17 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On July 13, 2016, at 19:50 EDT a severe thunderstorm warning was issued for Monroe County. This severe thunderstorm warning included the Fermi 2 site. "Due to high winds encountered during the thunderstorm, the Technical Specification (TS) for secondary containment pressure boundary was not met numerous times. The duration of time that the secondary containment Technical Specification was not met was approximately 1 second for each event. "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned secondary containment pressure within TS limits. At 20:40 EDT secondary containment vacuum was greater than the TS operability limit of 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) and steady, and the LCO was exited. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-07-13
52083 | -1 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2016-07-12 13:00 | 2016-07-12 21:53 | 2016-08-18 | DEGRADED FIRE BARRIER "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "During the performance of a fire seal and barrier surveillance test, a degraded fire seal barrier that provides 1 hour separation between two fire zones containing redundant safe shutdown trains was identified in the 100 foot elevation of the PVNGS Unit 1 Auxiliary Building. "This condition is reportable in accordance with 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition. "Fire protection detection and mitigation systems in both fire zones are operable and compensatory measures (fire watches) have been implemented for affected areas. "The NRC Resident Inspector has been notified." The degraded fire barrier consists of two holes in the through wall fire barrier surrounding two two-inch conduits. The two holes are approximately one to one and a half inches across. * * * RETRACTION FROM SEAN DORNSEIF TO HOWIE CROUCH AT 1356 EDT ON 8/18/16 * * * "Subsequent Engineering evaluation concluded the degraded fire seal in PVNGS Unit 1 reported on July 12, 2016, did not place PVNGS in an unanalyzed condition that significantly degraded plant safety. The degraded fire seal would have continued to provide the required degree of separation for redundant safe shutdown trains. "The evaluation found a fire initiated in a fire zone on either side of the barrier would not propagate within one hour into the adjacent zone with redundant safe shutdown equipment. These conclusions were based on an existing fire analysis which was used to demonstrate that the required degree of separation between safe shutdown equipment remained intact. "Based on the above information, PVNGS is retracting event notification report #52083, as the degraded fire seal did not place PVNGS Unit 1 an unanalyzed condition that significantly degraded plant safety. "The NRC Resident Inspectors have been informed." Notified R4DO (Proulx). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-07-12
52082 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2016-07-12 20:39 | 2016-07-12 21:08 | 2016-07-14 | ALERT DECLARED FOR A FIRE IN THE SERVICE WATER BUILDING At approximately 2039 EDT, there was smoke in the Service Water Building with the trip of the 2C service water pump. In accordance with plant procedures, unit-2 was ramped down to 70 percent power and the "Alert" was declared. EAL (emergency action level) SA8.1 was entered for damage with degraded performance including visible damage to the service water pump. Service water pressure was eventually restored by running both the 2A and 2B service water pumps. At 2118 EDT, the site exited the "Alert" because service water pressure had been restored. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, EPA EOC, FEMA National Watch Center (email), FDA EOC (email), Nuclear SSA (email). * * * UPDATE ON 7/14/16 AT 1456 EDT FROM LEE GRZECK TO DONG PARK * * * The initial notification should read: "At approximately 2035 EDT, there was smoke in the Service Water Building with the trip of the 2C conventional service water pump. In accordance with plant procedures, unit-2 was ramped down to 70 percent power and the 'Alert' was declared at 2039 EDT. EAL (emergency action level) SA8.1 was entered for fire/smoke damage with degraded performance including visible damage to the service water pump. Service water pressure was eventually restored and the plant was stabilized. "At 2118 EDT, the site exited the 'Alert' when service water pressure had been restored, and the fire was confirmed out (i.e., no reflash within 30 minutes)." The licensee notified the NRC Resident Inspector. Notified R2DO (Rich). | 0 | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-07-12
52081 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-07-12 | 2016-07-12 16:41 | 2016-07-12 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A Troxler moisture density gauge was stolen overnight from a locked overpack in a truck. The gauge contained both Am-241 and Cs-137 sources. The licensee contacted local law enforcement. Gauge serial number: 34700 Florida Incident: FL16-079 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-07-20
52080 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-07-11 17:45 | 2016-07-11 19:53 | 2016-07-11 | OFFSITE NOTIFICATION DUE TO NON-WORK RELATED ON-SITE CONTRACTOR FATALITY "At approximately 1614 Eastern Daylight Time (EDT), the Main Control Room was notified of a contracted employee experiencing a non-work related medical issue near the Discharge Weir. First Responders were immediately dispatched and present at the scene in minutes. Off-site assistance was requested and arrived on-site at approximately 1641. Dosher Memorial Hospital officials notified the plant at approximately 1745 that the patient was declared deceased at 1710. The individual was outside of the protected area (within the owner controlled area), and no radioactive material or contamination was involved. The cause of death has not yet been determined. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) for situation related to the health of on-site personnel for which a notification to other government agencies is planned. The Occupational Safety and Health Administration (OSHA) will be notified. "The NRC Resident Inspector has been notified. "This event did not result in any adverse impact to the health and safety of the public." The licensee completed their notification to OSHA at 1835 hours. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-07-11
52079 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2016-07-01 05:42 | 2016-07-10 10:29 | 2016-07-10 | FAILURE TO PERFORM TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 2342 [EDT], June 30, 2016, the Control Room received panel alarms associated with Safety Features Actuation System (SFAS) Channel 2. Subsequent investigation revealed the alarms were due to a loss of supplied power caused, in part, by a level permissive in the Borated Water Storage Tank (BWST) to be inoperable. With SFAS Channel 1 BWST level transmitter previously declared inoperable for maintenance, the on-shift operating crew did not correctly identify that technical specification (TS) 3.3.5, Condition B applied which is a 6-hour shutdown required action. At 0245, following a duty team call when the condition was re-assessed, the crew entered the proper additional Condition B and correctly identified they were approximately 3 hours into a 6-hour shutdown specification. At 0330 the condition was inappropriately exited on the premise that an operable but degraded situation could be justified. The plant did not initiate a shutdown required by technical specification but, in retrospect, should have initiated and completed a shutdown within 6 hours of 2342. " On July 1 at 1351, the BWST level transmitter for SFAS Channel 1 was repaired and declared operable [and exited TS 3.3.5 Condition B], however, the total time exceeded the 6-hour shutdown action. The plant remained stable throughout this event. On July 9, 2016, while internally discussing the event among FENOC senior leadership, it was determined that a 4-hour report would have been made if the shutdown was initiated. Hence, this report is retrospective in that a 10 CFR 50.72(h)(2)(i) required report should have been made upon the initiation of any nuclear plant shutdown required by plant's technical specification. "A Licensee Event Report will be provided pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition that was prohibited by the plant's technical specification. The NRC Resident Inspector has been notified." [At 1325 EDT on July 1, it was determined that the justification for SFAS channel 2 BWST level permissive to be operable but degraded could not be supported and reentered TS 3.3.5 Condition B.] | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-07-10
52078 | 0 | PRIME NDT SERVICES |  |  |  |  | 2016-07-08 19:30 | 2016-07-09 18:11 | 2016-07-09 | SOURCE FAILED TO RETRACT INTO RADIOGRAPHY CAMERA While conducting radiography at a field location in Indiana, the radiographer determined that the source could not be retracted. He immediately contacted the company's radiation safety officer (RSO), located in Pennsylvania. The RSO, who is licensed to retrieve sources, directed the radiographer to establish a 2 mR/hr boundary and await his arrival. Additionally, another crew was dispatched to assist the original crew in maintaining the boundary secure. Upon the RSO's arrival, the RSO and radiographers determined that the source was still in the collimator. They then used sandbags to reduce the work area dose rates. The RSO was able to retrieve the source and return it to the shielded position in the camera. The RSO conducted field testing and found no mechanical issues with the camera and could not replicate the problem. The RSO believes the problem was due to a source misconnect. The camera is currently enroute to the company's Ohio facility for additional testing prior to returning it to service. The RSO received 2 mR during the retrieval. The radiographer and assistant radiographer received 20 mR and 5 mR, respectively, during the retrieval. The camera was a QSA 880 Delta containing a 55 Ci Ir-192 source. No members of the public received any dose due to this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-07-18
52077 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-07-08 16:30 | 2016-07-09 16:44 | 2016-07-11 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following information was received from the State of Texas via email: "On July 9, 2016, the licensee reported that on July 8, 2016, at approximately 1630 hours (CDT), one of its InstroTek 3500 Xplorer (SN: 1845) moisture/density gauges had been lost at a temporary job site. The licensee reported its technician had completed work for the day. The gauge was muddy so the technician placed it inside its transport case in the back of his pickup and left the case's lid up. He then got busy finishing up paperwork and talked to a site supervisor. The technician failed to close the case lid, secure the case in the vehicle, or raise the tailgate before leaving the site. When he got to the main road, he realized this and checked the gauge. It was not in the truck. He backtracked his route and checked at the work site but his search was unsuccessful. The source rod on the device is locked. The licensee stated there is a lot of oilfield traffic in the area the gauge was lost. The licensee's name and phone numbers are on the device and they are hopeful it may have been picked up and will be returned on Monday. More information will be provided as it is obtained in accordance with SA-300. "Event Location: County Road 285, approximately 15 miles northwest of Mentone, Texas. "Notifications: County Sheriff's Offices (both Loving and Reeves Counties)." The State reported that the gauge contains 10 mCi of Cs-137 and 40 mCi of Am-241. * * * UPDATE ON 7/11/16 AT 0919 EDT FROM KAREN BLANCHARD TO BETHANY CECERE * * * The following updated information was received from the State of Texas via email: "Texas has assigned its incident number I-9419 to this event. "Also, correct spelling of gauge manufacturer is InstroTek." R4DO (Gaddy), NMSS Events, and CNSNS (Mexico) have been notified by email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-07-18
52076 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2016-07-08 20:05 | 2016-07-08 23:14 | 2017-03-17 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATION NOT MET "On July 8 2016, at 19:09 [EDT] a severe thunderstorm warning was issued for Monroe County. This severe thunderstorm warning included the Fermi 2 site. Due to the high winds encountered during the thunderstorm, the Technical Specification (TS) for the secondary containment pressure boundary was not met two times during the storm for a duration time of 2 seconds total (one second for each event). "At 20:05:21 Secondary Containment pressure went positive (0.22 inches of water gauge) and at 20:05:22 returned back below plant TS limits (-0.35 inches of water gauge). "At 20:06:33 Secondary Containment pressure went greater than TS limits (-0.10 inches of water gauge) and at 20:06:34 returned below TS limits (-0.28 inches of water gauge). "All plant equipment responded as required to the changing environmental conditions and Reactor Building HVAC returned the secondary containment pressure below the TS limits. There were no radiological releases associated with this event. The severe thunderstorm warning for the area was cancelled at 20:30. "The TS requirement is to maintain secondary containment greater than or equal to 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) for secondary containment operability. Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. The licensee has notified the NRC Resident Inspector. * * * RETRACTION AT 1922 EDT ON 3/17/2017 FROM DEREK ETUE TO BETHANY CECERE * * * "In this event notification, DTE Electric Company (DTE) reported conditions whereby the Fermi 2 secondary containment was believed to have exceeded Technical Specification Surveillance Requirements due to high winds. DTE hereby retracts this event notification as the Fermi 2 secondary containment has been determined to have been operable during this event as described below. "The Fermi 2 secondary containment pressure is maintained at a pressure less than the external pressure to contain, dilute, hold up, and reduce the activity level of fission products prior to release to the environment, and to isolate and contain fission products that are released during a Design Basis Accident or certain operations. Secondary containment pressure is monitored by a number of differential pressure (dP) sensors. High wind gusts have resulted in momentary negative pressure on the leeward side of the building, causing a more positive pressure indication from one or more dP sensors. The secondary containment building pressure remains relatively constant during these 'wind events.' "In December 2016, DTE implemented a software design change to display a 120-second rolling average for secondary containment dP indication. A 120-second rolling average recorded every second provides the operator a more accurate report of actual secondary containment conditions, while mitigating the signal noise and wind gust effects. The conditions associated with the subject event notification were re-reviewed in light of the improved secondary containment dP indication and it was determined that the Fermi 2 secondary containment was operable during this event. Specifically, the secondary containment pressure did not exceed Technical Specification Surveillance Requirements during this event. "In summary, the above event notification is retracted because the Fermi 2 secondary containment was determined to have been fully operable during the conditions identified in the subject report." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-07-08
52075 | 0 | CALIFORNIA DEPT OF PUBLIC HEALTH |  |  |  |  | 2016-07-07 | 2016-07-08 20:53 | 2016-07-08 | AGREEMENT STATE REPORT - TOTAL DOSE DELIVERED DIFFERS FROM THE PRESCRIBED DOSE The following report was received from the California Department of Public Health, Radiation Health Branch (RHB) via email: "RHB North was informed by the Radiation Safety Officer of UC [University of California] Davis Medical Center, of a Medical Event that took place on July 7, 2016. The Medical Event involved a SirSphere case. The patient received 29 per cent more than the prescribed dose. The physicians working on the case as well as the referring physician and the patient have been notified. There are no expected negative impacts on the patient. "Prescribed dosage: 13.5 mCi. Administered dosage: 17.4 mCi. "The apparent reason of the misadministration is that the CNMT [Certified Nuclear Medicine Technologist] miscalculated the dosage required." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-07-18
52074 | 0 | TEAM CORPORATE |  |  |  |  | 2016-05-01 | 2016-07-08 16:25 | 2016-08-31 | PART 21 REPORT - MATERIALS NOT PROPERLY DEDICATED The following information was excerpted from the email received from Team Corporate: "It was discovered during an internal audit that a Line Stop Fitting manufactured at the Furmanite Dixie Drive location and ordered from the Furmanite Charlotte location for nuclear work at Browns Ferry did not have material properly dedicated. "Completion of the [engineering] evaluation [to determine if safety is compromised] to be complete by August 31, 2016. A review of all safety related nuclear orders was performed and only the ones listed below are affected: Browns Ferry - Part number SF-0615-STD for TVA Job 256-MH-131067 (Tee fitting, blank flange, gasket, studs and nuts) Turkey Point - Part number CUS1301044-DWG-01, CUS1304019-DWG-01and CUS1304073-DWG-01(Leak Sealing cup, restraints, and enclosures) for FL&P job numbers 101-LS-104669, 101-LS-401085, and 101-LS-401142 respectively Catawba - Part number CUS1505165-DWG-01for Duke Energy Job 101-LS-403182 (Gamma plug enclosure, studs and nuts) POC: Edward Rich - Director of Quality Team Corporate 200 Herman Drive Alvin, TX 77511 (281) 388-5567 * * * UPDATE AT 0950 EDT ON 08/31/16 FROM EDWARD RICH TO JEFF HERRERA * * * The following is an excerpt from an email received from Team Corporate: Team Corporate determined that the affected orders where the materials were not dedicated as required only applied to the TVA orders. All other orders it was determined material was purchased from a supplier that operated an approved 10 CFR 50 App B Quality Program. Notified the R2DO (Bartley) and Part 21/50.55 Reactors (via E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-07-08
52073 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-07-08 06:45 | 2016-07-08 08:48 | 2016-07-08 | OFFSITE NOTIFICATION DUE TO OIL SPILL "Oil reported in the vicinity of the station's circulating water system effluent after the start of 3rd circulating water pump. The source of the oil is believed to be from oil entrained in the discharge canal from oil leak previously reported in EN#52045. One circulating water pump was removed from service to mitigate the source. The United States Coast Guard Response Center, and the New York State Department of Environmental Conservation have been notified. James A. Fitzpatrick Control Room was notified of the issue at 0645, off site agencies were first notified at 0743." The licensee notified the NRC Resident Inspector. Notified DOE, EPA, USDA, HHS, and FEMA. | 64 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-07-08
52072 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2016-07-07 12:10 | 2016-07-07 14:39 | 2016-07-07 | ACCIDENT MITIGATION - MAIN STEAM SAFETY VALVES NOT ADEQUATELY PROTECTED FROM TORNADO MISSILES "During an evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Harris Nuclear Plant personnel identified conditions in the plant design such that specific TS equipment is considered not adequately protected from tornado missiles. A tornado could generate multiple missiles capable of striking exhaust piping on multiple main steam safety valves (MSSVs), resulting in crimping of the piping that could impact flow capacity and render the MSSVs inoperable. If the tornado caused a loss of offsite power, the MSSVs are credited to remove decay heat to achieve cold shutdown. Compensatory measures have been implemented to ensure safety in the event of a tornado. "Enforcement discretion per Enforcement Guidance Memorandum EGM 15-002 and Interim Staff Guidance DSS-ISG-2016-01 has been implemented and required actions taken. Corrective actions will be documented in a follow-on licensee event report." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-07-07
52071 | 0 | QAL-TEK ASSOCIATES |  |  |  |  | 2016-06-29 | 2016-07-07 11:45 | 2016-07-07 | LEAKING Ni-63 SOURCES "On June 29th, 2016 around 10:00 [MDT] a Qal-Tek Associates radiation technician identified two Varian ECD's [electron capture devices] (both registered Ni-63 electro-plated sealed sources) with positive leak tests results above the critical levels of the gas flow proportional counter (sn: 44643 - 7.1% efficiency for Ni-63). The net cpm for the 8 mCi ECD (model: 02-001972-00, serial number: A544) was 1840 cpm (0.0117uCi) and for the 15 mCi ECD (model: 02-001972-00, serial number A8118) the net cpm was 4060 cpm (0.026 uCi). "The radiation technician was verifying the contents of a client's package in the Building 3 confinement facility that was shipped to Qal-Tek Associates address at: 3998 Commerce Circle, Idaho Falls, ID 83401. The outside of the package did not indicate any contamination when Qal-Tek received the package. Only the inside bottom face of the box indicated contamination of 60 net cpm. This portion of the box was removed for proper DAW [dry active waste] disposal at a licensed facility. "The radiation technician halted work, notified her co-worker, contacted the supervisor and confirmed that contamination was not present on her person or on surfaces of the work area, per the procedure, in order to prevent the spread of contamination. The Varian ECD (sn: A544) sealed source was decontaminated, the port holes in the device where taped shut, sealed in a plastic bag labeled with caution-radioactive material: Ni-63 leaker, and isolated from the work area in the biosafety cabinet. When no contamination was confirmed on personnel or facilities, the RSO was notified. The RSO re-checked facility surfaces for contamination. The work bench still had some contamination of about 105 net cpm. This was communicated to the RT's [radiation technicians] and their manager for further decontamination. The radiation technician took extra personal protective precautions to isolate the contamination and proceeded with verifying the rest of the package contents (14 ECD's). Once again, during the package content verification process, a 15 mCi Varian ECD (sn: A8118) also had a positive leak test above the instrument critical level. The radiation technician halted work, notified her co-worker, contacted the supervisor and confirmed that contamination was not present on her person or on surfaces of the work area, per the procedure, in order to prevent the spread of contamination. The source was sealed in a plastic bag labeled with caution-radioactive material: Ni-63 leaker, and placed in the biosafety cabinet for isolation from the work area. When no contamination was confirmed on personnel or facilities the RSO was notified by the manager. The RSO asked the Qal-Tek client manager to notify them of the leaking Ni-63 sources with a strong recommendation that they survey their facilities for contamination. The sources will be sealed in another bag and placed in a drum for proper disposal at a licensed LLRW [low level radioactive waste] disposal facility." The package was received from a client in Arcade, New York. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2016-07-15
52070 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-07-07 06:10 | 2016-07-07 09:48 | 2016-07-07 | LOSS OF TONE ALERT RADIO SYSTEM TOWER "At 0610 CDT on 7/7/2016, Cooper Nuclear Station confirmed that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in the event of an emergency condition. This is considered to be a major loss of the public prompt notification system capability and is reportable under 10CFR50.72(b)(3)(xiii). "Nemaha, Richardson and Atchison county authorities within the 10 mile EPZ were notified of the condition and the effect on the tone alert radios and will utilize the backup notification method making this condition reportable under 10CFR50.72(b)(2)(xi) for notification of other government agencies. "Estimated return to service time is unknown. The cause of the failure is unknown. "The NRC Resident Inspector has been notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-07
52069 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-07-06 18:07 | 2016-07-06 21:33 | 2016-07-06 | OFFSITE NOTIFICATION TO THE UNITED STATES DEPARTMENT OF TRANSPORTATION "In accordance with 10 CFR 50.72(b)(2)(xi), Duke Energy is notifying the NRC of a report made to the Department of Transportation concerning the identification of removable contamination in excess of 49 CFR 173.443(a) limits. This report was made at 1807 Eastern Daylight Time (EDT). "On July 6, 2016, an EnergySolutions 3-60B Transportation Package was received onsite. As a result of receipt surveys, Brunswick Health Physics personnel confirmed removable surface contamination on the transportation package in excess of 49 CFR 173.443(a) limits. The package was shipped as UN2910, Radioactive material, excepted package-limited quantity of material, 7, and was consigned as a non-exclusive use shipment. "Surveys identified mixed beta/gamma contamination ranging from approximately 2500 to 4500 dpm/100 sq cm on the surface of the transportation package. All other smears taken on the cask raincover, trailer bed and tires were less than minimum detectable activity for removable contamination. "The transportation package is located in a radiological controlled area and access is controlled by Radiation Protection. Surveys have confirmed that the contamination is limited to the surface of the cask. In addition, no personnel contamination events have been attributed to the contamination found on the transportation package. "This event did not result in any adverse impact to the health and safety of the public. "The NRC Resident [Inspector] has been notified. "The safety significance of this condition is minimal. There is no indication of onsite or personnel contamination as a result of this event. "The transportation package is controlled in a radiological controlled area and access is controlled by Radiation Protection." The originator of the empty cask arriving at the site (Westinghouse-Pittsburgh) was notified of the contamination. The cask is used for control rod blades and local power range neutron monitoring string shipping. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-07-06
52068 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-07-06 | 2016-07-06 16:48 | 2016-07-06 | AGREEMENT STATE REPORT - MISSING GENERALLY LICENSED DEVICE The following information was received from the State of Tennessee via email: "A licensee reported a generally licensed device as missing. Further details will be reported as the information becomes available. The specifics on the device are as follows: Manufacturer- Industrial Dynamics, Model-FT-50B, Serial-113439, Isotope-Am-241, Activity-100 mCi." State Event Report ID No.: TN-16-098 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-07-14
52067 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-07-06 09:38 | 2016-07-06 13:16 | 2016-07-06 | AUTOMATIC REACTOR TRIP WHILE PERFORMING TESTING "On July 6, 2016 at 0938 EDT Indian Point Unit 2 experienced a trip from 100% steady state power during the performance of reactor protection testing. The cause of the trip is under investigation. "All control rods fully inserted and all systems responded as expected. The auxiliary feedwater system actuated as expected on a low level in the steam generators which occurs as a result of a trip from full power. Auxiliary feedwater is maintaining steam generator levels and decay heat removal is via the steam generators to the main condenser. "Offsite power and plant electrical line ups are normal with the exception of 13.8kV feeder 33332 which remains out of service during the replacement of breaker BT4-5. "No primary or secondary code safety relief valves lifted. The reactor is in Mode 3 and stable. "Indian Point Unit 3 was unaffected and remains at 100% steady state power. "The NRC Resident Inspector has been notified." The licensee notified the New York Public Service Commission and the New York Independent System Operator. Indian Point indicated they have issued a press release regarding the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-07-06
52066 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-07-06 | 2016-07-06 11:27 | 2016-07-06 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was received from the State of Texas via email: "On July 6, 2016, the licensee reported to the Agency [Texas Department of State Health Services] that one of its moisture density gauges had been run over and damaged, a Troxler Model 3411 containing 10 millicurie cesium-137 source and a 40 millicurie americium-241/beryllium source, serial number 10471 [at a highway construction site near Robstown, TX]. The technician had started the test and the source rod was extended into the ground. While the test was in progress the step-up grader hit the gauge, causing the source rod to bend. The technician stopped all work at the jobsite and setup a boundary of fifteen feet because the source rod could not be retracted. The technician called the RSO [Radiation Safety Officer] and RSO contacted a service company, Qual-Tek, to respond to the site to retrieve the gauge. The site foreman moved the road crew down the highway to avoid the gauge. The technician will stay at the site near the gauge until it is collected by Qual-Tek. [The RSO is investigating.] No member of the public or worker received any exposure as a result of this event. An update will be provided as obtained in accordance with SA300." Texas Incident: I-9417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-07-14
52065 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-07-06 00:38 | 2016-07-06 01:02 | 2016-07-06 | MANUAL REACTOR TRIP AND UNUSUAL EVENT DECLARATION DUE TO STEAM LEAK IN TURBINE BUILDING "On July 6, 2016, at 0038 [EDT], DC Cook Unit 2 Reactor was manually tripped and at 0050 [EDT] an Unusual Event (N-7 'Unanticipated Explosion') Emergency Declaration was made due to steam leak and associated damage to the turbine building. "In accordance with Emergency Plan procedures, notifications of Berrien County and State of Michigan were completed. The licensee has notified the NRC Senior Resident Inspector. The Unusual Event was terminated at 0207 [EDT]. "This notification is being made in accordance with 10 CFR 50.72 (a)(1)(i) due to declaration of an emergency class. Original notification to NRC made at 0100 EDT via ENS. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation and 10 CFR 50.72(b)(2)(xi) Offsite Notification, as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. The DC Cook NRC Resident Inspector has been notified. A press release is planned. "Unit 2 is being supplied by offsite power. All control rods fully inserted. Decay heat is being removed via Steam Generator PORVs [Power Operated Relief Valve]. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the Post Trip Review. No radioactive release is in progress as a result of this event." Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) | 0 | 2016-07-06
52064 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2016-07-05 16:40 | 2016-07-05 20:01 | 2016-07-05 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE "On July 5, 2016, at 1640 Eastern Daylight Savings Time (EDT) the Unit 2 HPCI system was declared inoperable due to apparent failure of the HPCI Auxiliary Oil Pump after the 'HPCI Aux Oil Pump Motor Overload' control room annunciator was received. Failure of the HPCI Auxiliary Oil Pump prevents the HPCI system from performing its design safety function. As such, this event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. "This event did not result in any adverse impact to the health and safety of the public. "The NRC Senior Resident Inspector has been notified. "The safety significance of this condition is minimal. All other Emergency Core Cooling Systems and the Reactor Core Isolation Cooling (RCIC) system remain operable. "Troubleshooting activities are in progress. The HPCI system will remain inoperable until the cause of the failure has been corrected." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-07-05
52063 | 0 | GEORGETOWN HOSPITAL |  |  |  |  | 2016-05-19 | 2016-07-05 16:03 | 2016-07-05 | MEDICAL EVENT - WRITTEN DIRECTIVE NOT FOLLOWED The following is excerpted from the report sent via email: "On June 16, 2016 [the licensee's Director of Radiation Safety] was notified by the Authorized User (AU) of an issue regarding the May 19, 2016 radioembolization of a patient. During the subsequent review of the patient's treatment plan in preparation for an additional radioembolization of the Right Hepatic Lobe (scheduled for June 16, 2016) the AU observed the May 19, 2016 Written Directive/treatment plan was completed for the Right Hepatic Lobe, but treatment had been delivered to the Left Hepatic Lobe. "Review of the physician notes for the caseú reveal the intended primary treatment site, as noted by the Interventional Radiologist (IR) was the Left Hepatic Lobe, however, communication between the IR and AU requested a treatment plan for the Right Hepatic Lobe. On 16 June 2016 the AU confirmed with the IR that the Left Hepatic Lobe was indeed the intended treatment site for the 19 May 2016 procedure. Of note, the 19 May 2016 delivery was not completed as stasis was achieved. "The AU and Medical Physicist (MP) recalculated the 19 May 2016 treatment plan based on the administered activity and the treatment volume for the Left Hepatic Lobe. The resultant delivered dose was 119.4% of the prescribed dose. The AU determined there was no harm to the patient. "After review of the circumstances relative to the requirements stipulated in 10 CFR 35.3045 Report and Notification of a Medical Event, it does not appear this is a Medical Event and therefore, does not meet the reporting requirements of 10 CFR 35.3045. The dose was delivered to the Left Hepatic Lobe prior to the planned delivery to the Right Hepatic Lobe, i.e. both lobes were intended for treatment at different times; the original Written Directive was reviewed and corrected to account for the delivery to the Left Hepatic Lobe and the resultant dose did not exceed any thresholds specified in 10 CFR 35.3045. "Although not believed to be reportable as a Medical Event, this incident may be a violation of 10 CFR 35.40, Written Directives, paragraph (c) and/or 10 CFR 35.41, Procedures for Administrations Requiring a Written Directive, paragraphs (a)(2) and (b)(2). Therefore, I am submitting this report for your review. "Actions taken to preclude a recurrence: 1. A Time Out will occur wherein the AU, Medical Physicist and Interventional Radiologist (IR) communicate the specifics of the treatment plan by asking open-ended questions requiring more than a 'yes/no' answer. The Time Out will be documented via signatures from each of the aforementioned team members. 2. After the mapping study, the IR will clearly indicate the preferred treatment site(s) in his notes so the AU is clear as to the development of the treatment plan. These have been incorporated into the Radiation Medicine Sirsphere Policy and each member of the team has been instructed regarding the changes. Additionally, this incident is being tracked through our internal Risk Management system for further review and potential improvements to the program. These actions/reviews have been conducted and implemented prior to the next case, which is scheduled for 30 June 2016. "Details of Incident 1. Original Written Directive for Right Hepatic Lobe (19 May 2016) a. Activity prescribed: 25.49 mCi b. Dose to Lobe prescribed: 32.13 Gy c. Activity delivered: 23 .48 mCi d. Dose to Lobe delivered: 29.59 Gy 2. Revised Written Directive for Left Hepatic Lobe (16 June 2016) a. Activity prescribed: 19.67 mCi b. Dose to Lobe prescribed: 43.37 Gy c. Activity delivered: 23.48 mCi d. Dose to Lobe delivered: 51. 77 Gy e. Percent variation of administered activity to that prescribed = 19 .4%" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-07-13
52062 | 0 | U. S. GEOLOGICAL SURVEY |  |  |  | 1000 KW TRIGA MARK I | 2016-07-01 09:14 | 2016-07-05 14:56 | 2016-07-05 | USGS RESEARCH REACTOR SCRAM DUE TO ONE OF THREE POWER INSTRUMENTS NOT FUNCTIONING "At 0914 MDT on 7/1/16, a routine GSTR [Geological Survey TRIGA Reactor] startup and ascent to 900 kW was initiated after successful completion of the daily prestart checks and an excess reactivity check. At 0919 as power was passing through approximately 50 kW, it was clear to the operator that one of the three power instruments (the NP1000) was not functioning since it was still reading 0 percent when it should have been reading >5 percent. The reactor was scrammed, Reactor Supervisor notified, and troubleshooting commenced. Shortly after this, the NP1000 signal cable was found to have an intermittent connection through a tee connector that was installed at the instrument box. The connector was replaced to resolve the problem and tested satisfactorily. At 1050 the reactor was started up again. All power instrumentation operated correctly and the daily power operation was performed without further problems. "The NP1000 is a required safety instrument for operation of the reactor, so malfunction of the instrument is a violation of the facility's Technical Specifications. "Specifically, Specification E.7 states: 'The type and minimum number of safety systems which shall be operable for reactor operation are shown in Table I.' Table I requires the NP1000 to provide a high power scram at 110 percent power, but the connector problem would have prevented a high power scram from occurring in that instrument." The licensee notified the NRC Project Manager and the NRC SME (Subject Matter Expert) for Research and Test Reactors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | CO | NPR | [5 empty] | 0 | 2016-07-05
52061 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-07-01 12:05 | 2016-07-01 17:00 | 2016-07-01 | INADVERTENT ACTUATION OF EMERGENCY SIRENS "On 7/1/16, the Houston County Dispatch (911 Center) was conducting a monthly weather siren test. At approximately 1205 CDT, there was an inadvertent actuation of 41 emergency sirens in Houston County. The emergency sirens were deactivated at approximately 1208 CDT. Houston Country EMA issued a press release to notify the public of the inadvertent actuation. This is being reported under 10 CFR 50.72(b)(2)(xi) due to the inadvertent actuation and subsequent press release. There was no impact to the health and safety of the public as a result of this event as the offsite response capabilities remain functional. The site is operating normally with no emergency conditions present. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-07-01
52060 | 0 | YALE UNIVERSITY |  |  |  |  | 2016-06-30 19:30 | 2016-07-01 09:36 | 2016-07-01 | WHOLE BODY BADGE EXPOSURE READING OF 31 REM The following report is a summary of information provided via email: "We [Yale University] received notification from our dosimetry vendor (Mirion Dosimetry) of the following unusually high results on three dosimeters for individuals who all work at our PET [Positron Emission Tomography] Research Center, for the month of May: "Nuclear Medicine Technologist - Whole Body Badge - 31 Rem; Contract Nurse - L Extremity Dosimeter - 35 Rem; Radiochemist - L Extremity - 37 Rem "The Nuclear Medicine Technologist (NMT) was only at work for six days in May. She only handled radioactive material 4 of those 6 days. She used routine NMT amounts (milliCuries) of C-11 on those 4 days and reports nothing unusual about her work those days. She wears extremity monitors as well and although I [Yale University Radiation Safety Officer (RSO)] don't have the official report from Mirion on these rings, the raw data I have indicates 50 to 85 mRem on her rings. These readings would be considered typical for her work. She is currently on medical leave and has not been at work since May 10th. She does not believe the reading to her whole body badge can be accurate. She does not recall anything unusual for the time period in question. "The Contract Nurse only worked three days in May. Her other ring badge and her whole body badge recorded no exposures. She does not recall anything unusual for the time period in question and questions the validity of the result. "The Radiochemist worked his typical schedule in May and handled radioactive materials as part of his work most days. He recalls nothing unusual. His other ring badge and his whole body badge recorded no exposures. "We [Yale University] immediately collected all [the] PET Research Center staff June monthly badges and have sent in these three individual's badges (and several others) for emergency reads and the remaining for quick reads. [The RSO] expects to get the emergency results today and the remainder early next week. We [Yale University] also reviewed dosimetry of others in the facility, reviewed surveys conducted in May in the facility and conducted a radiation survey at the facility yesterday and find nothing unusual or out of the ordinary. "We [Yale University] are in contact with several dosimetry experts at Mirion Dosimetry and they are assisting in our investigation. [The RSO] has asked for several pieces of information in writing as related to their processing of the badges including: "Verification that the results of the three high readings have been scrutinized and reanalyzed for validity and accuracy. "A description of the type of radiation believed to have caused the exposure on the whole body badge and the energy range of this radiation. "Can any information about the orientation of the whole body badge when exposed be determined? Was it exposed upside down or backwards, for instance? If you can make any judgments about this please indicate in report. "Review and confirmation that the TLD chips from each of the dosimeters in question were tracked correctly and are indeed from the badge and rings from the individuals reported. "Verification that nothing unusual happened with the badges once received by Mirion. Please include the dates the badges were received by Mirion and track them each through processing. I'd like to know when each of the TLD's were analyzed at your facility and if they were analyzed on the same readers and such. "[The RSO doesn't] believe that any of the three readings reflect actual doses to people. Nonetheless, We [Yale University] are taking the situation very seriously and are expending significant time and effort to try to determine the cause in a timely manner. Our RSC [Radiation Safety Committee] is aware of the situation as is senior Yale leadership." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2016-07-01
52059 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-06-30 | 2016-07-01 16:44 | 2016-07-01 | AGREEMENT STATE REPORT - TROXLER GAUGE RUN OVER BY A DRUM ROLLER The following report was received from the Washington State Department of Health, Office of Radiation Protection via email: "On June 30, the operator of a Troxler 3411-B portable moisture-density gauge temporarily left the gauge unattended at a construction site in Chelan, Washington, and the gauge was run over by a drum roller. The top of the gauge housing was damaged, but there was no apparent damage to the sealed sources. At the time of the impact, the source rod was retracted inside the gauge and the handle was locked. After the licensee's radiation safety officer and the Washington State Department of Health were notified about this incident, the gauge was placed back into its transport case and transported to the licensee's licensed storage location in East Wenatchee, Washington. Then a leak test wipe was conducted on each of the sources, and the leak test wipes were mailed to a laboratory for analysis. The gauge is being stored at the licensee's storage location until the leak test results have been received, and then the gauge will be either repaired or sent for disposal. "Device type: Troxler portable gauge Model Number: 3411-B Serial Number 14853 Activity: Cesium-137, 8 milliCuries; Americium-241/beryllium, 40 milliCuries" Washington Item Number: WA160003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-07-11
52058 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-06-30 15:00 | 2016-07-01 16:07 | 2016-07-01 | AGREEMENT STATE REPORT - TROXLER CRUSHED BY CONSTRUCTION VEHICLE The following report was received from the California Department of Public Health via email: "On June 30, 2016, around 2 pm [PDT], a Troxler model 3440 # 20303 (reference date 12/1979) containing 40 mCi of Cs-137 and 8 mCi of Am-241:Be was involved in an accident and was crushed by a construction vehicle. The gauge operator cordoned off the area and notified the San Bernardino County Fire/HazMat office and the CA Warning Center - Event # 16-3978. The gauge's housing was crushed and the Cs-137 source handle was bent and loose. A photograph of the damaged gauge was sent to Radiologic Health Branch (RHB) [California Department of Public Health] for evaluation. An RHB inspector responded to the construction site to assist with shielding the source rod and ensuring all radioactive material is placed into the Type A transportation box to travel to the licensee's storage area. Upon arrival, the inspector noted that the bottom plate had broken off of the shield assembly and the sliding block had fallen out of the assembly, exposing the source. The sliding block was placed back in the assembly and the bottom plate taped back onto the bottom of the shield assembly. The top and bottom halves of the gauge body were taped back together, allowing the gauge to be placed back into the transport case for transport back to storage. A survey of the area of the incident after the gauge was placed in the transport vehicle was at background, indicating the no radioactive material remained at the site. The licensee was notified to contact their service provider to arrange for the gauge to be evaluated and possibly disposed. "Radiation level on the damaged gauge was 4 mR/hr on contact. Radiation level on the loaded Type A case was 0.6 mR/hr on contact." California 5010 Number: 063016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-07-11
52057 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2016-06-30 17:15 | 2016-06-30 22:54 | 2016-06-30 | MULTIPLE VALID SPECIFIED SYSTEM ACTUATIONS DUE TO LOSS OF SERVICE TRANSFORMER 21 "On June 30, 2016 at 1715 CDT, Grand Gulf Nuclear Station (GGNS) experienced an electrical power supply loss from Service Transformer 21 which resulted in power supply being lost to Division 2 (16AB Bus) and Division 3 (17AC Bus) ESF buses. This resulted in a valid actuation of Division 2 and Division 3 Diesel Generators on bus under voltage. They both automatically started and energized their respective ESF buses as designed. "During this event, the loss of power to the Division 2 (16AB Bus) resulted in a Division 2 RPS bus power loss, which actuated a Div 2 RPS half SCRAM signal. "The power loss also resulted in a loss of the Instrument Air pressure resulting in some Control Rod Scram Valves to drift open. This in turn caused the Scram Discharge Volume to fill to the point where a Div 1 RPS half SCRAM signal was initiated from Scram Discharge Volume level high on Channel 'A'. This resulted in a valid full RPS Reactor SCRAM while not critical. Instrument Air pressure was restored and the SCRAM signal was reset at 1733 CDT. "Appropriate off normal event procedures were entered to mitigate the transient. No ECCS initiation signals were reached. All safety systems performed as expected. "GGNS was in Mode 4, Cold Shutdown, with MSIVs closed at the time of the event. Reactor water level was maintained in the normal water level band by Control Rod Drive system throughout this event. RHR 'A' was maintained in Shutdown Cooling operation and it was not affected by this event." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-06-30
52056 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-06-30 14:30 | 2016-06-30 18:19 | 2016-08-29 | BOTH PRIMARY CONTAINMENT ISOLATION VALVES FOR A PENETRATION POTENTIALLY INOPERABLE "On June 30, 2016 at 1430 [EDT], with the reactor at 100 [percent] and the mode switch in RUN, Pilgrim Station determined both Primary Containment Isolation Valves (PCIVs) CV-5065-91 and CV-5065-92 for Drywell Penetration X-32A were inoperable due to the potential failure of relays relied on to perform the primary containment isolation function. "The valves have been closed and deactivated in the isolated condition in accordance with Technical Specification Limiting Condition For Operation Action Statement 3.7.A.2.b. "Preparations are in progress to replace the relays to restore the valves to operable status. "This 8-hour notification is being made in accordance with 10 CFR 50.72 (b)(3)(v)(C) and 10 CFR 50.72 (b)(3)(v)(D). "The licensee has notified the NRC Senior Resident Inspector. "The licensee will notify the Commonwealth of Massachusetts." * * * RETRACTION FROM KEN GRACIA TO DONALD NORWOOD AT 1720 EDT ON 8/29/2016 * * * "This notification is being made to retract event notification EN 52056 made by Pilgrim Nuclear Power Station on June 30, 2016, that reported the potential failure of relays that could have prevented the fulfillment of the safety function of primary containment isolation valves (PCIVs) needed to control the release of radioactive material and mitigate the consequences of an accident. "Post replacement testing of the removed relays associated with PCIV CV-5065-91 and CV-5065-92 demonstrated the ability of these relays to perform the required safety function. Based on the test results, no loss of PCIS safety function occurred while the relays were physically installed and operating. Therefore, Event Number 52056, made on June 30, 2016, is being retracted. "The NRC Senior Resident Inspector has been notified." Notified R1DO (Powell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-06-30
52055 | 0 | CURTISS WRIGHT |  |  |  |  | 2016-05-02 | 2016-06-30 16:52 | 2016-06-30 | PART 21 - INADEQUATE SWAGING AND ADHERENCE OF SILICONE O-RING AND SILICONE PAD IN SOFT SEAT MAIN DISC AND PILOT DISC ASSEMBLIES The following is a summary of the information from the email provided: "[The] soft seat main disc and pilot disc assemblies are installed in certain process solenoid operated valves, some of which perform safety related functions such as containment isolation. These designs include a soft seat insert in the main and/or pilot disc that could loosen and potentially result in excessive leakage or failure of the valve to operate properly. "Supplier: Target Rock, Business Unit of Curtiss-Wright Flow Control Corporation 1966E Broadhollow Road, East Farmingdale, NY 11735 "Should you have any questions regarding this matter, please contact Michael Cinque, General Manager at (631) 293-3800. "Plant Site Locations: Arkansas Nuclear One, Grand Gulf, Peach Bottom, Sequoyah, Browns Ferry, Hatch, Perry, Shearon Harris, Brunswick, Limerick, Pilgrim, South Texas, Dresden, Millstone, Quad Cities, Susquehanna, Duane Arnold, Nine Mile Point, River Bend, Three Mile Island, Fermi, Palo Verde, Saint Lucie, Watts Bar." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-06-30
52054 | 0 | U. S. GEOLOGICAL SURVEY |  |  |  | 1000 KW TRIGA MARK I | 2016-06-30 07:15 | 2016-06-30 10:34 | 2016-06-30 | REACTOR SHUTDOWN AFTER TECHNICAL SPECIFICATION VIOLATION "At 0712 [MDT] on 6/30/16 a routine GSTR [Geological Survey TRIGA Reactor] startup and ascent to 900 kW was initiated after successful completion of the daily prestart checks and an excess reactivity check. At 0715 [MDT], as power was passing through [approximately] 200 kW, it was clear to the operator that one of the three power instruments (the NP1000) was not functioning since it was still reading 0% when it should have been reading [approximately] 20%. The reactor was then shutdown, Reactor Supervisor notified, and troubleshooting commenced. Shortly after this, the NP1000 signal cable was found to have the coaxial cable pulled out of one of the connectors in the signal path. Repair, troubleshooting, and testing were performed to resolve the problem. At 0804 [MDT] the reactor was started up and all power instrumentation operated correctly and the daily power operation was performed without further problems. "The NP1000 is a required safety instrument for operation of the reactor, so malfunction of the instrument is a violation of the facility's Technical Specifications. "Specifically, specification E.7 states: 'The type and minimum number of safety systems which shall be operable for reactor operation are shown in Table I.' Table I requires the NP1000 to provide a high power scram at 110% power, but the cable problem would have prevented the high power scram from occurring in that instrument." The licensee will notify the NRC Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | CO | NPR | [5 empty] | 0 | 2016-06-30
52053 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2016-06-29 09:40 | 2016-06-29 17:21 | 2016-06-29 | SECONDARY CONTAINMENT INOPERABLE "At 0940 CDT on 6/29/2016, both doors of a Secondary Containment Airlock were reported to be open simultaneously for a period of less than 5 seconds. The brief time that the doors were simultaneously open constituted an inoperable condition of Secondary Containment. Secondary Containment was immediately restored to operable by closing the airlock doors. The airlock interlock was repaired and verified to operate correctly. "This event is being reported pursuant of 10 CFR 50.72(b)(3)(v)(C). "The Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-06-29
52052 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-06-29 | 2016-06-29 13:01 | 2016-06-29 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was received from the State of Colorado via email: "Details: The corporate office of Extended Stay America responded to the 2016 General License Annual reports. In their letter, it is stated, after a full investigation of the property, the exit signs were not found. There were 17, B100 Series, SN 625444 to 625460, with 9.2 Ci and 9 BXU10WS, SN 631179 to 631186, with 9.2 Ci not located. The total lost exit signs being reported are 26. Due to employee turnover from date reported shipped 4-23-1998 and 7-20-1998 to 2016 no records were maintained as the company had no knowledge of the status of Tritium Exit Signs associated with the site. "Event Description: The Company will be conducting a special project to determine if Tritium Exit Signs exist at any of their facilities in Colorado when fire inspections are completed. Should they locate any Tritium Exit Signs the signs will be properly disposed. The company will notify the Radioactive Materials Unit [State of Colorado] that the signs were removed and properly disposed." CO Event Report ID No.: CO16-I16-10 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-07-07
52051 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2016-05-09 06:26 | 2016-06-29 12:30 | 2016-06-29 | INVALID ACTUATION OF PRIMARY CONTAINMENT ISOLATION VALVES (PCIVs) "This 60-day telephone notification is being made in lieu of a Licensee Event Report (LER) submittal in accordance with 10 CFR 50.73(a)(1) to notify the NRC of an invalid actuation of PCIVs, reportable under 10 CFR 50.73(a)(2)(iv)(A). "On May 9, 2016, at 0626 Eastern Daylight Time (EDT), an unexpected trip of the Unit 1 Reactor Protection System (RPS) Bus A occurred, resulting in closure of several PCIVs on loss of power, per design. In addition, the following actuations also occurred per design: - insertion of a half reactor scram signal. - initiation of the standby gas treatment (SBGT) system . - isolation of the secondary containment. - initiation of the control room emergency ventilation (CREV) system smoke and radiation mode. - trip of the operating reactor water cleanup system (RWCU) pump due to closure of its isolation valve. "The event resulted from a failed relay coil in the drive motor run logic for the RPS power supply motor-generator (MG) set. The failed relay blew a fuse, which de-energized the RPS drive motor contactor and MG set. This resulted in de-energizing the RPS power supply in the 'A' channel and produced the actuations listed previously, per design. Affected systems and components were restored to their normal configurations by 1000 EDT on May 9, 2016. "Since no plant or process conditions existed that required the PCIV isolations (e.g., high drywell pressure or low reactor water level), this event is being reported per 10 CFR 50.73(a)(1) as an invalid actuation. This issue has been entered into the site Corrective Action Program (CR 2027653) for evaluation and implementation of further corrective actions. This event did not result in any adverse impact to the health and safety of the public. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-06-29
52050 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2016-05-18 | 2016-06-29 10:15 | 2016-06-29 | AGREEMENT STATE REPORT - PATIENT OVERDOSE OF IODINE-125 DURING MEDICAL TREATMENT The following report was received from the Kentucky Department of Public Health and Safety, Radiation Health Branch via email: "The KY Radiation Health Branch [RHB] was notified on 6/28/16 by the RSO at the University of Louisville that a patient received 297.7 cGy (rad), instead of the prescribed 31 cGy (rad). The patient was implanted with a 7.4 MBq (200 uCi) I-125 localization seed for treatment of non-palpable breast cancer on 3/18/16. The seed was to be removed within five days after implant. However, shortly after induction of anesthesia on the day of removal the patient became unstable, surgery was cancelled, the patient was placed in ICU, and the seed wasn't removed until 5/18/16. The dose was calculated by the radiation oncologist with a reference point of 1 cm around the seed. KY RHB has been in contact with the licensee and expects additional information to be provided by the licensee." KY Event Report ID No.: KY160006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2016-07-07
52049 | -1 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2016-06-28 10:55 | 2016-06-28 17:50 | 2016-08-22 | BOTH A & B TRAINS HPI INOPERABLE DUE TO VOID IN COMMON SUCTION LINE RESULTING IN LOSS OF SAFETY FUNCTION "At 1055 [EDT] on 06/28/16 a gas void was found during the monthly surveillance inspection located in the common suction line to the High Pressure Injection / Makeup (HPI / MU) pumps. At 1150 on 06/28/16 the HPI suction line cross-connect valves were closed to isolate and separate the 'A' & 'B' Trains of HPI. The 'A' train of HPI was declared degraded and initiated a 72 hour LCO [Limiting Condition of Operation] under TS [Technical Specification] 3.3.2. Investigation and analysis by Engineering determined that the size of the void did not meet the acceptance criteria for system operability. Due to the size of the void and location at time of discovery, both trains of HPI were determined to be inoperable until the suction cross connect valves were closed. "This condition is reportable under 10 CFR 50.72(b)(3)(v)(D) as a Condition That Could Have Prevented Fulfillment of a Safety Function to mitigate the consequences of an accident. The void is being vented to restore a water-solid condition. The last successful surveillance was conducted on 05/31/16. The cause of the void is being investigated. "The NRC Resident Inspector has been informed." * * * RETRACTION FROM CRAIG SMITH TO DANIEL MILLS AT 1056 EDT ON 08/22/16 * * * "Following the 8-hour 10 CFR 50.72 notification made on 06/28/16 (EN 52049), further engineering analysis determined that the as-found void size was insufficient to cause the high pressure injection pumps to become inoperable or unable to fulfill their safety function. The cause for the void continues to be under investigation including the development of actions to prevent recurrence. Void checks are being performed at an increased frequency until cause is determined, and actions to prevent recurrence are in place. As determined through analysis, both trains of HPl were operable and available such that the safety function was never lost. Therefore, this event notification is being retracted as it is not reportable pursuant to 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified R1DO (Dimitriadis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-06-28
52048 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-28 04:23 | 2016-06-28 06:58 | 2016-06-28 | AUTOMATIC REACTOR TRIP ON MAIN GENERATOR PROTECTION SIGNAL "This 4 and 8 hour notification is being made to report that Salem Unit 2 suffered an unplanned automatic reactor trip and subsequent automatic auxiliary feedwater system actuation. The trip was initiated due to a Main Turbine Trip above P-9 (49% power). The Main Turbine trip was caused by a Main Generator Protection signal. "Salem unit 2 is currently stable in Mode 3. Reactor coolant system pressure is 2235 psig and Reactor Coolant System temperature is 547 F with decay heat removal via the main steam dump and auxiliary feedwater systems. Unit 2 has no active shutdown tech spec action statements in effect. All control rods [fully] inserted on the reactor trip. All ECCS [Emergency Core Cooling System] and ESF [Emergency Safety Features] systems functioned as expected. "No safety related equipment or major secondary equipment was tagged for maintenance prior to this event. No personnel were injured during this event." The main generator protection signal was either a ground fault or a differential current trip. The plant is in its normal shutdown electrical lineup. No safeties or relief valves lifted during this event. Unit 1 is defueled and was not affected by this event. The licensee notified the NRC Resident Inspector and will notify the Lower Alloways Creek Township. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-06-28
52047 | -1 | SAN ONOFRE | 1 | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2016-06-27 07:29 | 2016-06-27 22:14 | 2018-04-18 | FITNESS FOR DUTY A non-licensed contract employee had a confirmed positive for alcohol following a for-cause fitness-for-duty test. The employee's access to the plant has been terminated. This information will be sent to the NRC Region 4 Office as San Onofre no longer has a resident. * * * RETRACTION ON 4/18/2018 AT 1308 EDT FROM TIM CUSICK TO STEVEN VITTO * * * "In the event report, the individual was described as a contract supervisor, thus meeting the reporting threshold. (the violation of the FFD policy was that he failed a for-cause test for alcohol). Recently, an NRC review of SONGS' 2016 Annual Fitness for Duty report found that SONGS described that test failure as 'not reportable' and that the labor category was 'Maintenance (Craft).' After reviewing the data, Access Authorization confirmed that the individual was a Union Maintenance Foreman (not a supervisor). The event was not reportable." SONGS will be notifying NRC Region 4. Notified R4DO (O'KEEFE) and FFD E-mail Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Decommissioned | Defueled | Defueled | Decommissioned | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2016-06-27
52046 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-06-27 10:50 | 2016-06-27 12:21 | 2016-06-27 | DRESDEN UNIT 3 DECLARES ALERT "At 1050 CDT, [on 6/27/16], an Alert was declared at Dresden Unit 3. The Alert is due to Unit 3 experiencing a fire in the HPCI (High Pressure Coolant Injection) system, auxiliary oil pump motor. The fire is out. "This notification is being made per 10 CFR 50.72(a)(1)(i)." Dresden Unit 3 is stable and continues to operate at 100% power and HPCI has been declared inoperable. There is no impact on Dresden Unit 2. The licensee has notified the NRC Resident Inspector Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and FEMA National Watch Center, FDA EOC, NuclearSSA via email only. * * * UPDATE FROM MICHAEL HAYES TO JOHN SHOEMAKER AT 1433 EDT ON 6/27/16 * * * "Termination of MA-5 [Alert]. Fire in HPCI room verified extinguished. HPCI system is inoperable. [Technical Specification] TS 3.5.1 condition G in effect, per 10 CFR 50.72(c)(i) - notification of termination of Alert." Dresden Unit 3 terminated the Alert at 1319 CDT, on 6/27/16. Dresden Unit 3 continues to operate at 100% power. The licensee will notify the NRC Resident Inspector. Notified R3DO (Kunowski), NRR (Miller), IRD (Grant), DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, and FEMA National Watch Center, FDA EOC, NuclearSSA via email only. * * * UPDATE FROM MICHAEL CSERNAK TO JOHN SHOEMAKER AT 1755 EDT ON 6/27/16 * * * "At 1042 [CDT] on 6/27/16, the U3 High Pressure Coolant Injection (HPCI) system was declared inoperable after the Auxiliary Oil Pump failed. "This event is reportable per 10CFR50.72(b)(3)(v)(D); any event or condition that at the time of discovery could have prevented fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This is an eight hour reporting requirement. "The Dresden NRC Resident [Inspector] has been notified." Notified R3DO (Kunowski). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | ALERT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-06-27
52045 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-06-26 21:15 | 2016-06-26 23:08 | 2016-06-27 | OFFSITE NOTIFICATION DUE TO AN OIL SPILL "The United States Coast Guard reported an oil sheen in the vicinity of the station's circulating water system effluent. Investigation by station personnel has not determined the source. The circulating water pumps were secured to mitigate the potential source. The United States Coast Guard response Center, and New York State Department of Environmental Conservation have been notified." The licensee notified the NRC Resident Inspector. Notified DOE, EPA, USDA, HHS, FEMA. * * * UPDATE ON 06/27/2016 AT 02:52 FROM DUSTIN SCURLOCK TO DAN LIVERMORE * * * "The source of the oil sheen has been identified. The source, main turbine lubricating oil, has been stopped and cleanup efforts are underway." Notified R1DO (Gray), DOE, EPA, USDA, HHS, and FEMA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-06-26
52044 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2016-06-25 14:07 | 2016-06-25 18:30 | 2016-06-25 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "At 1407 [CDT], during power ascension to 100 percent, turbine control valves closed unexpectedly causing reactor protection trip signals that in turn caused a reactor scram. Reactor scram, turbine trip ONEPs [Off Normal Event Procedure], and EP2 [Emergency Procedure for Level Control] were entered. Reactor water level was stabilized at 36 inches narrow range on startup level and reactor pressure stabilized at 935 psig using bypass valves. No other safety system actuations occurred and all systems performed as designed." All control rods inserted. Reactor level is maintained by feedwater. Normal electrical shutdown configuration is through offsite electrical power sources. The Safety Relief Valves lifted, then closed. The plant is stable at normal level and pressure and remains in Mode 3. The event is under licensee investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-06-25
52043 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-06-24 15:11 | 2016-06-24 19:45 | 2016-06-24 | LOSS OF SECONDARY CONTAINMENT "On 06/24/2016 at 1511(CDT), an unexpected trip of a Fuel Building ventilation supply fan occurred followed by an exhaust fan trip and secondary containment differential pressure became positive. "At 1512 (CDT), the standby fuel building ventilation fans auto started and secondary containment differential pressure was restored to Technical Specification required conditions. "Secondary containment was declared INOPERABLE when Technical Specification-required differential pressure was not being maintained and LCO 3.6.4.1 Action A.1 was entered and exited for the given time period. Emergency Operating Procedure (EOP) - 8 was entered due to Secondary containment differential pressure reading positive (greater than 0 inches of water). "This loss of secondary containment is reportable under 10CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "The cause of the fuel building supply fan trip is under investigation. The NRC Resident Inspector has been informed." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-06-24
52042 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-06-24 12:15 | 2016-06-24 16:06 | 2016-06-24 | MANUAL REACTOR SCRAM DUE TO REACTOR RECIRCULATION PUMPS DEGRADATION "At 1215 [EDT] on 6/24/2016, James A. FitzPatrick (JAF) was at 100% power when Breaker 710340 tripped and power was lost to L-gears L13, L23, L33, and L43. These provide non-vital power to Reactor Building Ventilation (RBV), portions of Reactor Building Closed Loop Cooling (RBCLC), and 'A' Recirculation pump lube oil systems. Off-site AC power remains available to vital systems and Emergency Diesel Generators (EDG) are available. "Due to the loss of RBV, Secondary Containment differential pressure increased. At 1215 [EDT], Secondary Containment differential pressure exceeded the Technical Specifications (TS) Surveillance Requirement SR-3.6.4.1.1 of greater than or equal to 0.25 inches of vacuum water gauge. The Standby Gas Treatment (SBGT) system was manually initiated and Secondary Containment differential pressure was restored by 1219 [EDT]. "The 'A' Recirculation pump tripped at 1215 [EDT] and reactor power decreased to approximately 50%. 'B' Recirculation pump temperature began to rise due to the degraded RBCLC system. At 1236 [EDT], a manual scram was initiated. Reactor Pressure Vessel (RPV) water level shrink during the scram resulted in a successful Group 2 isolation. All control rods have been inserted. The RPV water level is being maintained with the Feedwater System and pressure is being maintained by main steam line bypass valves. A cooldown is in progress and JAF will proceed to cold shutdown (Mode 4). Due to complete loss of RBCLC system, the Spent Fuel Pool (SFP) cooling capability is degraded but the Decay Heat Removal system remains available. SFP temperature is slowly rising and it is being monitored. The time [duration] to 200 degrees is approximately 117 hours. "The initiation of reactor protection systems (RPS) due to the manual scram at critical power is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The general containment Group 2 isolations are reportable per 10 CFR 50.72(b)(3)(iv)(A). In addition, the temporary differential pressure change in Secondary Containment is reportable per 10 CFR 50.72(b)(3)(v)(C), as an event that could have prevented fulfillment of a safety function." The licensee notified the NRC Resident Inspector and the State of New York. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-06-24
52041 | 0 | ABB INC. |  |  |  |  | 2016-04-26 | 2016-06-24 13:20 | 2016-06-24 | PART 21 - DEVIATION FOR CLASS 1E SOLID STATE RELAYS (47H AND 60Q) The following information was excerpted from a received licensee fax: On April 26, 2016, ABB confirmed a customer complaint regarding a 60Q relay received with an internal short circuit. The cause was determined to be a manufacturing deviation from specification. Records show a total of 53 suspect relays were provided to 2 customers (Prairie Island and Tennessee Valley Authority). Based on the nature of the deviation, any installed relay would have failed upon application of power in the relay. Therefore, the primary concern is that any relay, either in storage or installed with no power applied, may have this defect and will create a system malfunction upon power application. If you have any questions regarding this notice, please contact the ABB Technical Support at (954) 752-6700. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-06-24
52040 | 0 | ROMEO RIM INC. |  |  |  |  | 2016-06-23 | 2016-06-24 07:52 | 2016-09-08 | SCRAPPED EQUIPMENT CONTAINED A CS-137 SOURCE During the last month, Romeo Rim had been scrapping older equipment. They received a call from a steel recycler (Steel Dynamics Inc. in Columbia City, Indiana) that their scrap material contained a cesium source. The equipment had been used to measure the amount of nucleation in the plastic manufacturing process. Romeo Rim is currently contacting a company to dispose of the cesium source which is at Steel Dynamics. Source: Cesuim-137 (originally 200 mCi in April 1986, currently 100 mCi) Equipment Manufacturer: Texas Nuclear (now Thermo Fisher Scientific) Equipment Model: 5202 Serial Number: B425 * * * UPDATE AT 0830 EDT ON 7/11/16 FROM WADE SPURLIN TO S. SANDIN * * * The device was recovered by a licensed hauler RAM Services. A wipe test was performed which indicated that the source was not leaking. The device will be transported to Texas for disposal. Notified R3DO (Pelke) and NMSS Events Notification via email. * * * UPDATE AT 1006 EDT ON 09/08/2016 FROM WADE SPURLIN TO JEFF ROTTON * * * The device was disposed of by Waste Control Specialists, LLC at the Compact Waste Facility in Andrews, TX on August 26, 2016. Notified R3DO(Stoedter) and NMSS Events Notification group via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-07-04
52039 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-06-24 04:00 | 2016-06-24 04:05 | 2016-06-24 | TS REQUIRED SHUTDOWN DUE TO LEAKING SERVICE WATER WELD ON CCW HX "At 0400 (EDT) on June 24, 2016, Indian Point Unit 2 initiated actions to commence reactor shutdown to comply with Technical Specification (TS) LCO 3.7.7, Condition B. TS LCO 3.7.7, Condition A had been entered at 0230 on June 21, 2016 in order to repair a leaking weld on the 20 inch service water pipe to nozzle weld on the 21 Component Cooling Water Heat Exchanger (CCW HX). Condition A allows 72 hours to restore the inoperable CCW train to service or Condition B is entered which requires the plant to be in Mode 3 in 6 hours and Mode 4 in 12 hours. "The initiation of a nuclear plant shutdown required by TS requires a 4-hour report in accordance with 50.72(b)(2)(i) which is being made by this notification." The licensee notified the New York Independent System Operator and the New York Public Service Commission. The licensee notified the NRC Resident Inspector. | 92 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2016-06-24
52038 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-06-23 | 2016-06-23 19:46 | 2016-06-23 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED The following information was received by the State of Washington via email: "The operator of a portable moisture-density gauge temporarily left the gauge unattended at a construction site in Redmond, Washington, and the gauge was run over by the wheel of a roller. The top of the gauge handle was broken off, but both radioactive sources are in safe condition inside the body of the gauge. The gauge operator is maintaining security around the damaged gauge, and has called a nuclear gauge calibration and servicing company to come to the construction site to assess the scene, package the gauge for transport to a safe location, and conduct radiation surveys to verify that there is no radioactive contamination of the construction site and the roller equipment, and to verify that the radioactive sources are undamaged and inside the gauge case." The portable gauge is a Campbell Pacific Nuclear; Model MC-1-DR; Serial Number MD51008063; Sources-Cs-137 (.010 Ci), Am/Be (.050 Ci). Washington Item Number: WA160002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-07-01
52037 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-06-22 | 2016-06-23 17:13 | 2016-06-23 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA COMPONENT FAILURE The following information was received from the State of Texas by email: "On June 23, 2016, the licensee notified the Agency [Texas Department of State Health Services] that a radiography camera had failed to lock in position after retracting the source. The ball stop moved about 3/16 of an inch causing the camera to not lock in position after the source was retracted into position. The licensee's radiation safety officer (RSO) obtained the following information about this component failure. The camera was a delta 880 source serial number S7340 at an activity of 52.6 curies. No overexposures were reported to the RSO. An investigation into this event is being conducted by the RSO. The camera has been secured and is located at one of the licensee's sites. Updates will be provided as obtained in accordance with SA300." Texas Incident: I-9415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-07-01
52036 | 0 | U.S. AIR FORCE |  |  |  |  | 2016-06-20 | 2016-06-23 11:45 | 2016-06-23 | LOST/MISSING DETECTION SOURCE The following was received by email: "Per your request, I'm sending this email as a follow-up to my telephonic notification to your office that occurred earlier today (re: 10 CFR 20.2201). "We're reporting the apparent loss (presently unknown whereabouts) of an aggregate quantity of approximately 95 mCi of Ni-63 housed in the following seven generally licensed devices (GLDs): - 3 ea. x Smiths Detection SABRE 2000s (up to 15 mCi Ni-63 ea.) - 2 ea. x Smiths Detection SABRE 4000s (up to 15 mCi Ni-63 ea.) - 2 ea. x GE VaporTracers (up to 10 mCi Ni-63 ea.) - 19 May 2016: Tinker AFB installation RSO attempted to schedule semiannual swipe sample collection for May 2016. The unit possessing/using GLDs indicated that the GLDs had been transferred. Installation RSO advised unit to present documentation. - 23 May 2016: Unit reported to installation RSO that they were still looking for paperwork. - 13 Jun 2016: After an exhaustive search of records and information management systems, neither the installation RSO or the unit found any documentation for GLD transfer. - 16 Jun 2016: Installation RSO notified the unit commander; continues to investigate. - 20 Jun 2016: Installation RSO notified the USAF Radioisotope Committee Secretariat by telephone and then by email to report situation." The above report of a possible lost or missing source involves sources not specifically licensed under the MML (Master Material License). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | OK | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-07-01
52035 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2016-06-17 | 2016-06-22 17:46 | 2016-06-22 | AGREEMENT STATE REPORT - CONTAMINATION OF BRACHYTHERAPY PATIENT The following was received from Wisconsin via email: "On Friday, June 17, 2016, a licensee discovered contamination on a package that was used to ship I-125 prostate brachytherapy seeds. The post procedure survey of the packaging revealed elevated levels of radiation. After wipes were taken, the licensee determined that there was I-125 contamination on the inside of the packaging. There was no other contamination in the operating room. The licensee had the patient return to the facility to perform a urine bioassay. The bioassay revealed elevated levels of I-125 in the patient's urine. However further analysis will be required to determine activity concentrations. The licensee has also administered Lugols solution to the patient to block the thyroid. The department and the licensee are still collecting data to determine if this is a medical event. Site visits and updates will be performed as needed." Wisconsin Report ID # WI160004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2016-06-30
52034 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-06-22 | 2016-06-22 13:28 | 2016-06-22 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from Colorado via email: "The facility manager completed the documentation for the 2016 Annual General License reports. During his inspection, only 2 of the 4 Tritium exit signs were reported. It is unknown as to what may have occurred with the other two signs as staff has changed since the signs were designated to be used at the facility. "Pictures were submitted showing the labels on the existing two signs located within the modern fold doors at the school. No serial number was provided on the label from the manufacture Shield Source. The distributor, Isolite, did report serial numbers on the quarterly report to the state." Colorado Report # CO16-I16-09 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-06-30
52033 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2016-06-22 08:41 | 2016-06-22 13:02 | 2016-06-22 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0841 [CDT] an automatic turbine trip occurred, resulting in an automatic reactor protective system (RPS) actuation due to loss of turbine load. The source of the turbine trip was from the distributed control system (DCS) and is being investigated via a root cause analysis. This was an uncomplicated trip, all systems responded as expected post trip, and the reactor trip recovery procedure was entered at 0852 [CDT]." The plant is stable in Mode 3 with a normal electrical line up and decay heat removal via steam dumps to the condenser. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-06-22
52032 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-12-31 | 2016-06-22 11:00 | 2016-06-22 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the State of Colorado via email: "Event Report ID No.: CO16-I16-08 "Detail: The facility hired a contractor to remodel space within the hospital. During the construction pedestrian traffic was routed around the area. According to the facility environmental health safety office the Tritium exit signs were only in use during the project. "Event Description: It is unknown due to the extensive passage of time and the departure of employees who were involved with the project. No further information is available related to the use or the disposition of the 6 Tritium exit signs, Model # SLXTUIGW10, Serial # 162229 to 162234, H-3, 7.3 CI." THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-06-30
52031 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-06-21 14:00 | 2016-06-21 19:03 | 2016-06-23 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory have not been employed. Immediate compensatory measures taken upon discovery. The licensee will inform the NRC Resident Inspector. * * * RETRACTION ON 6/23/16 AT 0744 EDT FROM PHILLIP BEABOUT TO BETHANY CECERE * * * This event has been retracted because it did not meet the threshold for reporting as a one hour report. The licensee will notify the NRC Resident Inspector. The R1DO (Dentel) has been notified. The 73.71 Safeguards Group has been notified via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-06-21
52030 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-06-21 16:46 | 2016-06-21 18:12 | 2016-06-21 | SODIUM HYPOCHLORITE SPILL "Today at 1646 EDT a reportable spill of approximately 1 liter of Sodium Hypochlorite 15 percent solution reached the soils of New Jersey. The leak was able to be isolated and the area is being cleaned up. "This event is reportable within 4 hours per 10 CFR 50.72(b )(2)(xi) any event or situation related to protection of the environment for which a notification to other government agencies has been made." The licensee notified the New Jersey Department of Environmental Protection and has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-06-21
52029 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2016-04-29 | 2016-06-21 14:50 | 2016-06-21 | PART 21 - INSUFFICIENT VALVE CAGE HARDFACING The following is excerpted from an email provided by the supplier: "Items subject to this Fisher Information Notice (FIN) are confined to the equipment and orders referred to in Table 1 [see original submission]. Specifically, 'Equipment' refers to the eight inch sized hardfaced HPNS cages supplied per the order numbers listed in Table 1. "The purpose of this FIN is to alert affected customers that, as of 29 April 2016, Fisher Controls International LLC ( Fisher) became aware of a situation which may affect the performance of the aforementioned Equipment, including its safety-related function. "Fisher is informing affected customers of this circumstance in accordance with Section 21.21(b) of 10 CFR 21. "The Equipment in question is subject to CoCr-A hardface overlay requirements. The CoCr-A overlay deposit thickness must be 0.060 inch minimum after machining. However, the cages supplied in fulfilment of the orders listed in Table 1 may have insufficient hardfacing depth on the inside bore diameter at the top of the cages (approximately 1.50 inches from top). "This issue first came to Fisher's attention when a material grade inspection revealed insufficient cobalt. Subsequent PMI testing confirmed the upper section at the top of the cage fell short of expected CoCr-A. Two in-stock cages were sent to a third party accredited laboratory for macroetch examination and hardness survey. The results of this survey confirmed the top of the cages did not meet the minimum hardness requirement of 34 HRC and further confirmed the insufficiency is limited to the uppermost 1.50 inches of the inside bore diameter of the cages. "The absence of hardfacing at the mating surface between cage and plug creates the potential for galling, which could prevent the valve from performing its intended safety function. Testing has been conducted to analyze the risk of galling. Typically, galling is observed in cycle tests well exceeding the 600 cycle recommended lifetime for the equipment. However, testing has proven galling to be an unpredictable phenomenon and could occur prior to the recommended lifetime of the equipment. There are no known field issues with the affected equipment. "The problem of post-hardfacing material shrinkage is associated with the ratio of bore diameter to cage wall thickness. Large bore diameter thin-walled cages are at greater risk for material shrinkage. A third party accredited laboratory performed additional macroetch supplemental tests and evaluations on similar cages of varying bore sizes. It was determined that this issue is unique to the 8 inch sized HPNS cages. "Fisher will provide the affected customers with a properly coated cages at Fisher's cost. In addition, a Corrective Action Request (CAR 1804) has been initiated by Fisher to prevent reoccurrence of this issue." The US reactor sites affected by this issue include VC Summer and Vogtle. The foreign reactor sites include Sanmen and Haiyang. FIN 2016-06 dated 20 June, 2016. Point of Contact: Ben Ahrens Quality Manager Emerson Process Management Fisher Controls International LLC 30 1 South First Avenue Marshalltown, IA 50 1 58 Phone: (64 1 ) 754-2249 Benjamin.ahrens@emerson.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-06-21
52028 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-06-21 10:00 | 2016-06-21 14:28 | 2017-08-07 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from California via email: "The RSO of Nova Engineering and Environmental notified RHB [Radiologic Health Branch] in Brea that a Troxler yellow transport case containing a Troxler model 3411B # 18840 moisture density gauge containing 8 mCi of Cs-137 and 40 mCi of Am-241/Be was stolen from a technician's pickup truck today. The technician stated that he had loaded and secured the Type A case into his pick-up truck from a storage facility in Irvine, CA then stopped at a coffee shop before traveling to his work location. He went to unlock the gauge case and found that it had been stolen. He returned to the coffee shop, but was unable to find his gauge. He is contacting the Irvine Police Dept. to make a theft report. The RSO indicated that they lock and chain each side of the case to the truck independently and once again around the top of the case to prevent it from opening. Nova E&E does have contact information on the gauge and the case and they use a small padlock on the Cs-137 source rod handle to prevent accidental deployment." CA 5010 # 062116 * * * UPDATE ON 8/7/17 AT 1608 EDT FROM ROBERT GREGER TO DONG PARK * * * The following was received from California via email: "A moisture density gauge that had been reported stolen on 6/21/16 (see NMED Item # 160262) was recovered this morning, after it was dropped off at a construction site where it was not being used. The gauge was not in its transportation container, and the source rod was not locked, although it was in the shielded position. Survey measurements confirmed that both sources (Cs-137 and Am-241) are present. The gauge is presently in the California radiation control program's possession pending return to its licensed owner (Nova Environmental Engineering, license # CA 7732-37)." Notified R4DO (Gepford), NMSS Events Notification, and Mexico via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-06-29
52027 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2016-06-20 09:30 | 2016-06-21 11:37 | 2016-06-21 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following was received from Minnesota via email: "On June 20, 2016 at 0930 [CDT] Midwest Industrial X-Ray, Inc. (License number 1086-89) had a source disconnect event. Their Radiation Safety Officer notified the Minnesota Department of Health [MDH] of the event at 0925 [CDT] on June 21, 2016. "Initial details: - The event happened on a jobsite in Lakeville, MN. - The Camera was a QSA 880 Delta. - Source was 47.5 curies of I-192. - The cause has been initially determined to be a worn drive cable. The licensee stated that the drive cable passed the go-no-go test prior to hooking up. - They were able to retrieve the source and get it back in the shielded position. - All equipment was inspected after the retrieval. - The faulty drive cables were brought back to the licensee's corporate office in Fargo, ND for repair. - Pocket dosimeter readings following the retrieval were: 41 mrem, 20 mrem, 11 mrem, and 10 mrem. "The licensee is in the process of preparing a written report that will be submitted within 30 days as required. MDH will continue to investigate this event. MDH Inspectors will be on-site at the licensee's office in Albertville MN on June 23, 2016 to perform a follow-up inspection." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2016-06-29
52026 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-20 15:40 | 2016-06-20 17:19 | 2016-06-20 | AUTOMATIC REACTOR TRIP "On June 20, 2016 at 1540 EDT, Watts Bar Nuclear Plant Unit 2 reactor tripped due to [reaching the] automatic Lo-Lo steam generator trip [setpoint] on [the] #4 steam generator. Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. "All control and shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and main steam dump systems. The station is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72 (b)(2)(iv)(B). "The NRC Senior Resident has been notified." There was no effect on Unit 1. | 0 | 0 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-06-20
52025 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-06-17 12:22 | 2016-06-20 15:27 | 2016-06-20 | OFFSITE NOTIFICATION DUE TO ELEVATED TRITIUM DETECTED ONSITE "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) because the Tennessee Valley Authority (TVA) is in the process of informing the Alabama Radiological Protection Department, Alabama Department of Environmental Management, Limestone County Emergency Management Department, and Nuclear Energy Institute (NEI) of recent groundwater monitoring results at the Browns Ferry Nuclear Plant in accordance with NEI 07-07, Industry Ground Water Protection Initiative. "There are no indications of any impacts to any off-site drinking water source as indicated by Browns Ferry's off-site groundwater monitoring well samples. "TVA has taken immediate action to address the apparent leak following the detection of elevated tritium levels from on-site groundwater monitoring wells and will be monitoring affected wells on an increased frequency. No elevated tritium levels have been detected from off-site monitoring locations, and the public is not at risk. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-06-20
52024 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-06-07 | 2016-06-20 10:29 | 2016-06-20 | AGREEMENT STATE REPORT - STOLEN STATIC ELIMINATOR GUN The following report was received by the Tennessee Division of Radiological Health via email: "During an inspection [by Tennessee Division of Radiological Health] on 06/07/16 the device could not be located, inspector called [Dennis Hall's Body Shop owner] back on 06/13/16 to find out if they had found the device. At that time she stated that she had been told that a painting contractor had taken the device by a former employee. They had several painting contractors and could not remember which one had taken the device." The Tennessee Division of Radiological Health stated that the device owner did not know when the device had been taken. Device: Static Eliminator Gun NRD Model P-20510AB Serial Number: 156990 Activity: 10mCi Po-210 TN Event Report ID No.: TN-16-091 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-06-28
52023 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-20 03:20 | 2016-06-20 07:08 | 2016-06-23 | SAFEGUARDS REPORT Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. * * * EVENT RETRACTION FROM DAN PHILLIPS TO JOHN SHOEMAKER AT 1740 EDT ON 6/23/2016 * * * The licensee is retracting this report based upon further review of the reporting criteria and entering the incident into their security log. The licensee will notify the NRC Resident Inspector. Notified R4DO (Rollins) and 73.71 Safeguards Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-06-20
52022 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2016-06-19 15:33 | 2016-06-19 21:38 | 2016-06-19 | SECONDARY CONTAINMENT INOPERABLE "At 1533 CDT on 06/19/2016, while performing Tech Spec Secondary Containment Airlock verification testing, both doors of a Secondary Containment Airlock were reported to be open simultaneously. The identified condition caused Secondary Containment to be considered inoperable. Upon discovery, immediate action was taken to close the doors restoring Secondary Containment. Airlock doors were under control of plant personnel throughout the event. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(C)." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-06-19
52021 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-18 11:06 | 2016-06-18 14:05 | 2016-06-18 | OFFSITE NOTIFICATIONS TO USCG NATIONAL RESPONSE CENTER AND TEMA "On 6/18/16 at 1106 EDT, TVA [Tennessee Valley Authority] notified the National Response Center that Watts Bar Nuclear Plant has an oil sheen on the Cooling Tower Basin. "1. Oil sheen was observed within the Cooling Tower basin at WBN [Watts Bar Nuclear]. Sheen was light brown to red and did not cover the entire Cooling Tower basin. Estimate of oil released into the Cooling Tower basin is less than 1 quart. "2. No oil sheen was visible in the Tennessee River from the bank above the diffuser pipes. "3. Notifications were also made to TEMA [Tennessee Emergency Management Agency]. "4. Follow-up observations within one hour of the sheen being reported indicated that the oil sheen had dissipated and was no longer visible. Oil levels from the suspected source did not indicate any change in oil reservoir levels. "Unit 1 remains in Mode 1 at 92% power - reduced power due to main condenser back pressure limits "Unit 2 remains in Mode 1 at 33% power - initial startup testing "This event is reportable under 10 CFR 50.72(b)(2)(xi) as a condition that was reported to an outside Government Agency. "The NRC Resident Inspector has been notified." | 92 | 33 | 0 | 92 | 33 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-06-18
52020 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-06-18 02:59 | 2016-06-18 06:25 | 2016-06-18 | SPURIOUS EMERGENCY SIREN ACTIVATION "On 6/18/16 at approximately 0259 CDT, the Monticello Nuclear Generating Plant was notified by the Wright County Sheriffs Office of a spurious actuation of one emergency siren in the city of Monticello. As a result, this issue is being reported under 10CFR50.72(b)(2)(xi) for notifications to other off site government agencies as the licensee was notified by the Wright County Sheriff's Office. The source of the siren activation has not been determined. Wright County Sheriff's Office successfully deactivated the siren at 0322 CDT. There was no impact to the health and safety of the public as a result of this event as the offsite response capabilities remain functional with a single siren failure. The site is operating normally with no emergency conditions present. The NRC Resident Inspector has been notified." The licensee will notify the State of Minnesota concerning this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-06-18
52019 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-06-17 21:35 | 2016-06-18 05:49 | 2016-06-18 | HIGH PRESSURE COOLANT INJECTION SYSTEM RENDERED INOPERABLE "On 6/17/2016, 2-SR-3.3.6.1.6(3) HPCI [High Pressure Coolant Injection] system time delay relay calibration periodic surveillance was being performed. During a section in the procedure a fuse cleared for the logic bus B power at 2135 [CDT]. This rendered the HPCI system unable to be manually or automatically initiated. At 2239 the fuse was replaced and the HPCI system was restored to a standby lineup. "HPCl is a single train safety system and this notification is being made in accordance with 10CFR50.72 (b)(3)(v)(D). "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-06-18
52018 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-06-09 | 2016-06-17 20:46 | 2016-06-17 | AGREEMENT STATE REPORT - PATIENT RECEIVED THREAPEUTIC DOSE AT LOCATION NOT AUTHORIZED BY FACILITY LICENSE The following information was received from the State of California via email: "Cedar Sinai called LA County Radiation Management on Friday 6/17/16 at 4:25pm [PDT] to report that Cardinal Health delivered Xofigo (Ra-223) to a Los Angeles clinic which is not authorized to have the material. The therapy dose was then given to the patient. Cedar Sinai has a broad scope license and is authorized to have the material, the location that received the material is not an authorized use location, and the doctor who administered the material is not an authorized user for the material. The current assumption which is being verified is the clinic (previously Targenix RML#7145) had its own license prior to a merge and was allowed to have the material and the doctor was previously authorized to administer the material. The patient records have been reviewed by an authorized doctor and [the patient] would have received the treatment at an authorized location by an authorized user if referred. The balance of the treatments will be at an authorized location with an authorized user. Cedar Sinai will continue to investigate and report their findings." 5010 Number: 061716 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-06-27
52017 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-06-17 00:30 | 2016-06-17 18:36 | 2016-06-20 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE DAMAGED BY VEHICLE AT WORKSITE IN ALASKA The following information was received from the State of Washington via email: "At about 1230 Pacific time an AECOM employee and authorized user of the nuclear density gauge backed a pickup truck into the gauge. The gauge was not in operation at the time and the rod was in the up and shielded position. The rod was not bent however the outside case of the gauge was damaged. Observation of the gauge indicated that the damage appeared to be confined to the outer casing and the electronic controls. The sealed sources did not have any visible signs of damage. "The incident occurred at the Red Dog Mine in Alaska where [AECOM] was using the gauge under a reciprocity agreement with the NRC. "A radiation detection instrument was used to confirm that the sources were not leaking and to check the area of the incident for any radiation. This survey indicated that the gauge was not leaking and that the area of the incident did not show any indication that the sources had leaked." Nuclear Density Gauge involved: CPN, MC Series containing two (2) sources; 0.01 Ci or 0.37 GBq Cs-137 and 0.05 Ci or 1.85 GBq Am-241. Incident Number: WA-16-028. * * * UPDATE FROM FRED MERRILL (AECOM) TO DANIEL MILLS AT 1810 EDT ON 06/20/2016 * * * The licensee, AECOM, contacted NRC to report that the damaged device was being securely stored onsite at the mine until it can be shipped back to the manufacturer. The licensee also corrected the license number. Notified R4DO (Rollins) and NMSS (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-06-27
52016 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-06-16 | 2016-06-17 17:15 | 2016-06-17 | AGREEMENT STATE REPORT - TWO SOURCES STUCK IN DIP TUBES DURING ANNUAL SHUTTER TEST The following information was received from the State of Louisiana via fax: "On June 16, 2016, at approximately 1500 CDT, [the] Radiation Safety Officer of ExxonMobil notified LDEQ [Louisiana Department of Environmental Quality] of a potential equipment malfunction. A custom built Berthold level/density gauge installed on G-Line Reactor Vessel, V5300 and possessing seven 10 mCi Co-60 sealed sources, was undergoing a routine annual shutter test in which the sealed sources were pulled upwards in their dip tubes via connecting cables to the top of the source holder. The sources in dip tubes #2 and #6 became stuck in the dip tubes and could not be pulled upward further. The other sources were pulled up to the top of the source holder successfully. All sources were successfully returned to their normal operating positions. [The RSO] called Berthold contract service engineer [at] Radcon, LLC and discussed the potential malfunction. [The service engineer] stated that differential thermal expansion between the source capsules and dip tubes under heating within the reactor vessel likely caused the sources to begin sticking as they were being pulled upward in their dip tubes. The licensee placed another service call to [the service engineer] on June 17, 2016, but was unable to contact him, but left a message. Radcon, LLC will conduct a maintenance inspection and repair of the gauge which is tentatively planned for July 11, 2016. This is not an emergency situation. ExxonMobil Radiation Safety Office staff are monitoring the vessel condition and have the situation under control. There is no potential for off-site exposure." Event Report ID No.: LA160007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-06-27
52015 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-06-16 | 2016-06-17 14:24 | 2016-07-08 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON NUCLEAR GAUGE The following information was received from the State of Texas via email: "On June 17, 2016, the Agency was notified by the licensee that it had discovered the shutter on a Ohmart model SH-F1 nuclear gauge containing a 50 millicurie (original activity) Cs-137 source would not close. Open is the normal position for the gauge. The licensee stated the gauge does not create an exposure risk to it's employees or members of the general public. The licensee stated a service company will be on site the week of June 27, 2016 to repair the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9413 * * * UPDATE FROM ARTHUR TUCKER TO RICHARD SMITH AT 0814 ON 07/08/16 * * * The following update was received via email from the state of Texas: "Update to correct licensee's name. "Should have been recorded as Flint Hills Resources Longview. Additional information will be provided as it is received in accordance with SA-300." The R4DO (Drake) was notified and NMSS Event Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-06-27
52014 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-06-16 | 2016-06-17 12:06 | 2016-07-07 | AGREEMENT STATE REPORT - DOSE ADMINISTERED TO WRONG PATIENT The following information was received from the State of California via email: "On June 16, 2016, [the] Radiation Safety Officer of the University of California, Los Angeles (UCLA), contacted the Brea office of the Radiologic Health Branch to report a medical event. The event resulted in a dose to the wrong patient that exceeded 20 percent of the prescribed dose (the dose that was likely to be given to another patient scheduled to be treated on June 17, 2016). The patient was given an activity of 4.02 GBq of Yttrium 90 (Nordion TheraSphere), resulting in a dose to the liver of 226.3 Gray. This dose exceeded the prescribed dose of 120 Gray. This activity was later discovered to be the activity that was most likely to have been ordered for a patient that was to be treated on June 17, 2016. The patient that was treated on June 16, 2016 has been notified. The investigation is ongoing to determine the cause of the event." 5010 Number: 061616 * * * UPDATE AT 1740 EDT ON 06/21/16 FROM ANDREW TAYLOR TO S. SANDIN VIA EMAIL * * * "This is a revision/update of EN #52014. "On June 16, 2016, [the] Radiation Safety Officer of the University of California, Los Angeles (UCLA), contacted the Brea office of the Radiologic Health Branch to report a medical event. "Two patients were scheduled to be treated with Nordion TheraSpheres containing yttrium 90, one on June 16 and the other on June 17. The first treatment occurred on June 16; however, the treatment dosage of 4.02 GBq (108.6 mCi) was approximately 1.9 times the prescribed dosage, apparently because the dosage for the second patient was given to the first patient. As a result, the first patient received a liver dose of 226.3 gray (22,630 rad) instead of the prescribed dose of 120 gray (12,000 rad). "The patient has been notified, and the licensee is investigating to determine the cause of the event." Notified R4DO (Rollins) and NMSS Events Notification via email. * * * UPDATE AT 0611 EDT ON 07/07/16 FROM ROBERT GREGER TO S. SANDIN VIA EMAIL * * * "This is a revision/update of EN #52014. "On 7/1/16 UCLA submitted a written report of this medical event. That report noted that in addition to the incorrect treatment dosage, the incorrect liver lobe was treated. As a result, the dose to the incorrect liver lobe was calculated as 328 Gy (32,800 rad). This differs from the previously reported liver dose of 226.3 Gy (22,630 rad) due to the difference in the sizes of the liver lobes." Notified R4DO (Drake) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-06-27
52013 | -1 | KING COMPANY, INC |  |  |  |  | 2016-06-17 | 2016-06-17 08:01 | 2016-06-21 | LOST NUCLEAR DENSITY GAUGE During the process of license renewal of a nuclear density gauge, the owner of King Company, Inc. could not find the density gauge in the storage location in the company warehouse. The time frame the density gauge was lost could not be determined and is currently being investigated. The gauge model, activity and quantity of sources could not be provided by the licensee when the report was made. "We [the licensee] have searched file archives, and were unable to find the original purchase documents for Device Key 497158, however, we did find the purchase documents for the Device Key 497157. We believe these devices with purchase dates of 5/15/1993 and 8/27/1995, contained identical components." The "identical" equipment was a digital density gauge with a 2 Ci Cs-137 source. Whereabouts of the Device Key 497158, Serial No. B880, are unknown. * * * RETRACTION ON 6/21/16 AT 0723 EDT FROM RANDY KING TO BETHANY CECERE * * * The following is a synopsis of information received via a telephone conversation. When this condition was initially reported, the database for the original supplier of the gauge, TN Technologies, was unavailable. Following a review of the database, when it became available, it was discovered that this gauge (Device Key 497158) was never sold to the licensee and was never in their possession. According to the TN Technologies database, Device Key 497158 had been sold to another company outside the United States. Notified R1DO (Dentel) and R3DO (Orlikowski). Notified NMSS Event Notification Group and CNSC (Canada) by email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-06-27
52012 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2016-06-17 02:57 | 2016-06-17 06:21 | 2016-06-17 | AUTOMATIC REACTOR SCRAM DURING TESTING "During planned stop and control valve testing, two main turbine high pressure stop valves closed instead of the expected one (stop valve 'B'). This caused the main turbine control valves, power, reactor pressure to swing and a division 2 half SCRAM. Control rods were inserted to reduce power and the power swings. At 0257 [CDT] the reactor automatically SCRAMMED. Reactor SCRAM, Turbine Trip [procedures] ONEPs and EP-2 were entered. Reactor water level was stabilized at 34 inches narrow range on startup level control and reactor pressure stabilized at 884 psig using main turbine bypass valves. No other safety related systems actuated and all systems performed as expected." The plant is in its normal shutdown electrical lineup using normal feedwater and turbine bypass valves for decay heat removal. Reactor pressure is slowly trending down. The licensee is investigating the cause of the second stop valve shutting. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 56 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-06-17
52011 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-16 07:45 | 2016-06-16 16:19 | 2016-06-16 | FITNESS FOR DUTY - UNOPENED HERBAL TEA IDENTIFIED IN THE PROTECTED AREA An employee self-reported possession of an unopened herbal tea containing naturally occurring alcohol in the protected area. The drink was removed from the protected area. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM MATTHEW PLEASANT TO DONALD NORWOOD AT 1955 EDT ON 6/16/2016 * * * "While investigating the incident for EN #52011, it was determined that 'cooking wine' used in the cafeteria should be removed from the protected area." The licensee will notify the NRC Resident Inspector. Notified R4DO (Proulx) and FFD Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2016-06-16
52010 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2016-06-16 11:37 | 2016-06-16 14:59 | 2016-06-16 | UNANALYZED CONDITION OF EMERGENCY DIESEL GENERATOR DURING TORNADO LOW PRESSURE "Upon review of recent industry operating experience, an issue was identified for the potential impact of the low barometric pressure associated with a tornado on the Emergency Diesel Generators (EDGs). The Davis-Besse Nuclear Power Station EDGs are equipped with a crankcase positive pressure trip with a set point of approximately 1 inch of water. This crankcase pressure trip is bypassed during an emergency start signal of the EDG from the Safety Features Actuation System or from an essential bus under voltage condition. Engineering has determined that a design basis tornado could create sufficient low pressure to potentially actuate the crankcase positive pressure trip due to different vent paths between the EDG Room and the EDG crankcase. If the crankcase pressure trip occurs before the EDG starts on an emergency signal due to the tornado, the crankcase pressure trip would cause an EDG lockout condition. The EDG lockout condition would then prevent either normal or emergency start of the EDG until operators could manually reset the lockout condition locally at the EDG. This condition could potentially affect both EDGs simultaneously. "No severe weather warnings or watches are forecast in the local areas that could challenge the crankcase pressure trip. Compensatory measures are being established that upon notification of a Tornado Watch or Tornado Warning that would be implemented to defeat the crankcase pressure trip function and allow the EDGs to perform their required safety function during a potential tornado." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-06-16
52009 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-06-14 | 2016-06-15 18:44 | 2016-06-15 | AGREEMENT STATE REPORT - LOST AND FOUND BRACHYTHERAPY SEEDS The following was received from the State of Washington via email: "[A common carrier] lost 252 IsoRay Cesium-131 brachytherapy seeds intended for four patient implants. On Friday, 6/9/2016, radioactive materials licensee, IsoRay (WN-L0213-1) sent four orders of cesium-131 brachytherapy seeds. The four orders contained a total of 252 seeds at a total air kerma activity level of 522.8 U. The total apparent activity is approximately 1 Ci (the actual activity is between 1 - 2 Ci). The absorbed dose from the 252 seeds would be approximately 52,280 rad (522.8 Gray). Early Tuesday morning, 6/14/2016, the Memphis hub of [the common carrier] informed IsoRay that they were unable to locate these packages, and they would not be delivered on time as contracted. They were scanned in and out at both the Pasco and Spokane airports. The Spokane flight to Memphis arrived, but [the common carrier] could not locate them. IsoRay notified the state of the loss of radioactive material that same day. "On 6/15/2016, IsoRay notified the state that [the common carrier had] found the missing shipments and are returning them to IsoRay. They were not delivered to the intended physicians. There are no details yet on how they became misplaced. IsoRay has scheduled a senior management meeting with [the common carrier's] Priority Alert team to trouble shoot the missing shipments. "This incident is one of several incidents in which [the common carrier] played a role within the last 4 months." Incident Number: WA-16-027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-06-23
52008 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-06-15 07:00 | 2016-06-15 16:19 | 2016-06-17 | AGREEMENT STATE REPORT - VEHICLE CONTAINING A TROXLER GAUGE INVOLVED IN AN ACCIDENT The New Jersey Department of Environmental Protection was informed that a vehicle containing a Troxler gauge Model 3411B, S/N 19870, was involved in an accident. New Jersey Department of Environmental Protection responded to the scene. The gauge was damaged, but radiation levels around the gauge were normal. The licensee's Radiation Safety Officer took possession of the gauge. * * * UPDATE AT 0944 EDT ON 6/17/16 FROM KAREN FLANIGAN TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "Local HAZMAT notified the New Jersey Department of Environmental Protection (NJDEP) that a vehicle that was towed from the scene of a motor vehicle accident was found to contain a portable [nuclear] gauge. NJDEP staff responded to the towing yard and identified the device as a Troxler 3411-B moisture-density gauge belonging to New Jersey licensee Atlantic Engineering Laboratories, Inc. The source rod was fully retracted, but the sliding block on the bottom of the gauge was stuck open. The exposure rate at the opening in the plate was 5.2 mR/hr. The licensee's RSO came to the site, closed the sliding block, performed a leak test, and returned the device to its Type A package. The RSO took possession of the gauge for transport to the licensee's licensed storage location." Am-241/Be source - 44 mCi Cs-137 source - 9 mCi Notified the R1DO (Kennedy) and NMSS Resources (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-06-23
52007 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-04-17 21:04 | 2016-06-15 15:14 | 2016-06-15 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATOR "This is to report the Salem Unit 1, 1B Emergency Diesel Generator (EDG) actuation due to an invalid signal. "This report is being made per paragraphs 10CFR50.73 (a)(1) and 10CFR50.73(a)(2)(iv)(A) to address the invalid actuation of the 1B EDG on April 17, 2016, during replacement of an indicating bulb. "Plant conditions; Salem Unit 1 was in mode 6 at the time of the invalid actuation. "On April 17, 2016, at approximately 2055 [EDT] while performing Solid State Protection System (SSPS) testing of the 1B Safeguards Equipment Cabinet (SEC), operators identified that an input test light was not lit as expected. "At approximately 2104 [EDT] while attempting to replace the light bulb, the 1B EDG unexpectedly automatically started. "The 1B EDG responded properly to the auto start signal and started in SEC Mode 1, accident only, and did not load. "The cause of the inadvertent start was determined to be a loss of the block circuit which allowed an output to the logic module which then caused the EDG to auto start. Subsequent testing of the input block switches demonstrated that, due to switch degradation, slight pressure applied to the switch was enough to allow the block signal to be momentarily interrupted, even without repositioning of the switch. It was determined that the loss of the block was most likely due to the operators finger coming in contact with the switch during the bulb replacement." The licensee has notified the NRC Resident Inspector. The licensee will notify the State of New Jersey and Delaware. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-06-15
52006 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2016-06-13 | 2016-06-14 13:44 | 2016-06-17 | AGREEMENT STATE REPORT - FOUND RADIOACTIVE SCRAP METAL This was reported from the State of Alabama via facsimile: "On June 13, 2016, the Radiation Safety Officer for Nucor Steel in Decatur, Alabama notified the Alabama Office of Radiation Control in regards to a piece discovered in scrap metal received via railcar. The piece appears to be a retaining ring approximately the diameter of a dime. The piece is reading over 5,000 mRad/hr at contact using a Ludlum model 15 survey meter. The piece has been secured in a building within the site boundary and away from employees. The licensee is continuing to research where and when the piece arrived onsite. The [Alabama] Office of Radiation Control plans to meet with site personnel on June 16, 2016. As of today, [6/14/16] 1235 CDT, this incident remains open until further investigation can be completed." Alabama Incident # 16-23 * * * UPDATE AT 1131 EDT ON 06/17/16 FROM MYRON K. RILEY TO S. SANDIN VIA FAX * * * "On June 16, 2016, [representatives from the Alabama] Office of Radiation Control visited the site to conduct measurements and spectrum analysis. The retaining ring read 13.5 mR/hr at contact, 3.6 mR/hr at one foot, and 0.5 mR/hr at three feet with a Fluke 451P #2644, calibrated 12/10/15. Spectrum analysis using a Thermo IdentiFINDER revealed the isotope to be Co-56. This was confirmed through the Joint Analysis Center Collaborative Information System. "As of today [06/17/16], 1025 CDT, this incident remains open until disposal options have been completed." Notified R1DO (Kennedy) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2016-06-22
52005 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-06-13 | 2016-06-14 10:27 | 2016-06-14 | AGREEMENT STATE REPORT - MEDICAL EVENT "On Monday June 13, 2016, the licensee's radiation safety officer contacted the Agency [Illinois Emergency Management Agency] to advise that a seed localization procedure utilizing a radioactive source was not going to be completed as planned. An I-125 seed had been implanted on June 9, 2016 to mark an area of the breast for subsequent examination and surgical explantation on June 13, 2016. However, the patient experienced a stroke during the interim days and the planned surgery for explantation aborted. Given the patient's condition it was determined that the risk associated with surgery to the patient was greater than the risk associated with not performing the seed retrieval. Initial estimates of the effective whole body dose are 3.7 Rem and dose to the breast 73 Rad. No permanent functional damage to the organ/tissue is expected as a result of the inability to remove the source. If the patient's condition improves and the opportunity arises, the seed may still be explanted at a much later date." IL Item Number: IL16004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-06-22
52004 | -1 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-06-13 17:33 | 2016-06-13 22:13 | 2016-07-08 | ALERT SIRENS FAILED TO ROTATE "At 1845 CDT on June 13, 2016, TVA Corporate Emergency Preparedness notified the Shift Manager at Browns Ferry Nuclear Plant that eight of the BFN [Browns Ferry Nuclear] Alert & Notification Sirens (19, 39, 55, 59, 60, 61, 69, 95) failed to rotate. The sirens were activated at 0915 CDT. Post sounding siren feedback indicated thirteen sirens that failed to rotate. BFN EP [Emergency Preparedness] Senior Instrument Mechanics were dispatched to inspect the thirteen sirens and determined, through field inspections that only eight sirens would not rotate. The field inspection was completed and communicated to Corporate Emergency Preparedness at 1733 CDT. "Per NPG-SPP-03.5.1, the affected sirens which were lost affect 25.1 percent of the Emergency Planning Zone (EPZ) population and the sirens are not expected to be returned to service within 24 hours. Per NPG-SPP-03.5.1, a Loss of Alert and Notification System Capability exists when there is an unplanned or planned loss of primary Alert and Notification System (ANS) equipment for greater than one hour resulting in a loss of capability to alert 25 percent or more of the total Emergency Planning Zone (EPZ) population and either the Federal Emergency Management Agency (FEMA) approved backup alerting method cannot be implemented for the area affected by the lost primary ANS equipment OR the primary ANS equipment is not expected to be returned to service within 24 hours. "TVA Corporate Emergency Preparedness is redirecting a team from Watts Bar Nuclear Plant to commence repairs on Wednesday 6/15/2016. "This 8 hour notification is being made per the reporting requirements specified by 10 CFR 50.72(b)(3)xiii. "The NRC Resident Inspector has been notified. "This event has been entered in the Corrective Action Program." * * * EVENT RETRACTION FROM MARK MOEBES TO RICHARD SMITH AT 0538 EDT ON 7/08/2016 * * * "The licensee is retracting this event notification. "Upon further evaluation using siren modeling software, back-up route alerting was deemed unnecessary since the overlap from neighboring sirens provided the required minimum siren coverage over all populated areas within the EPZ. The TVA siren system provides significant acoustic overlap that is not completely accounted for in the population factors used to initially determine the impacted population for the purposes of reportability. During the event, BFN remained capable of providing adequate siren coverage, and the loss of ANS equipment impacted less than 25 percent of the population within the EPZ. Therefore, this was not a reportable event. "The NRC Resident Inspector has been notified." Notified the RII RDO (Seymour). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-06-13
52003 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2014-08-06 | 2016-06-13 14:03 | 2016-06-13 | PART 21 - SWITCHES NOT ENVIROMENTALLY QUALIFIED "TopWorx Information Notice: TIN 2016-01 "13 June 2016 "Subject: C7 Switches "Equipment Affected By This Information Notice: (4) C7-14521-E25 shipped on 6 August 2014 "Purpose: The purpose on this TopWorx Information Notice (TIN) is to alert Fisher that, as of 27 May 2016, TopWorx was made aware of a situation which may affect the performance of the aforementioned equipment. TopWorx is informing Fisher of this circumstance in accordance with Section 21.21 (b) and 50.55 (e) of 10 CFR 21. "Applicability: This notice applies only to (4) TopWorx C7-14521-E25 shipped on 6 August 2014 to Fisher on Fisher Purchase Order 4123318082. "Discussion: Fisher Purchase Order 4123318082 specified that TopWorx SV7-14521-E25 were to be provided. Although the C7 switches provided to Fisher in error are also Nuclear-qualified switches, they do not have the same qualification pedigree and therefore cannot be considered qualified for HELB [High Energy Line Break] applications (zones 5 and 10). TopWorx has no indication that the switches provided are defective, yet TopWorx is unable to determine the application or status of use and therefore submits this notice. "Extent of Condition: Fisher Purchase Orders were reviewed and no other order was found where an incorrect switch was provided. "Actions Required: If the units mentioned above are to be installed in a zone for which the C7 switch is not qualified, then the units must be replaced. In addition, TopWorx has initiated a Non Conformance Report (NCR 05192016-01) to prevent reoccurrence of this issue. "10 CFR 21 Implications: TopWorx requests that the recipient of this notice review it and take appropriate action in accordance with 10 CFR 21. "If there are any technical questions or concerns, please contact: John Conrad Manger, Quality TopWorx 3300 Fern Valley Road Louisville, KY 40213 Fax: (502) 969-8000 Phone: (502) 873-4661 John.conrad@emerson.com" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-06-13
52002 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-06-13 09:42 | 2016-06-13 13:21 | 2016-06-13 | FITNESS-FOR-DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been denied. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2016-06-13
52001 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-04-14 14:06 | 2016-06-13 08:40 | 2016-06-13 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID CONTAINMENT VENT ISOLATION ACTUATION "This 60-day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report an invalid Containment Vent Isolation (CVI) actuation at Watts Bar Nuclear Plant (WBN) Unit 2. "On April 14, 2016 at 1344 Eastern Daylight Times (EDT), Unit 2 technicians performing calibration checks on the Auxiliary Building general supply fan, connected test equipment to the wrong intake temperature switch, causing an invalid train B auxiliary building isolation (ABI) signal in both Unit 1 and Unit 2. "Because the Unit 2 containment purge system was, at that time, configured in the 'refuel' mode, the invalid train B ABI concurrently initiated a train B CVI in WBN Unit 2. Consequently, the train B CVI caused the Unit 2 containment lower compartment radiation monitor to trip and control room operators entered Technical Specification Limiting Condition for Operation (LCO) 3.4.15 RCS Leakage Detection Instrumentation at 1344 EDT. "By 1422 EDT, Unit 2 control room personnel had reset the containment purge system and by 1854 EDT had completed procedural steps to restore auxiliary building ventilation to its normal alignment. By 1858 EDT, Unit 2 control room personnel had completed the procedural steps to restore the containment purge system. "During this event, the train B ABI and CVI actuations were complete and equipment functioned as designed. Upon identification of the train B ABI/CVI condition, the calibration activities were halted and a prompt investigation was initiated. WBN evaluators determined the apparent cause of the event was incorrect work instructions, with a contributing cause that technicians failed to use human performance error prevention tools to ensure they were calibrating the correct equipment. Personnel responsible for performing the calibration checks have been coached and corrective actions have been taken to correct the work instructions." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-06-13
52000 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2013-06-12 20:13 | 2013-06-12 23:51 | 2016-06-13 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN AND REACTOR TRIP At 2013 EDT on 6/12/16, Millstone Unit 3 commenced a Technical Specification (TS) required shutdown due to excessive Reactor Coolant System leakage from the "A" Reactor Coolant Pump (RCP) third stage seal. The leakage from the third stage seal was approximately two gpm which is greater than the Technical Specification (TS) limit of less than one gpm. During the shutdown, oscillations developed in the Main Feedwater which required the operator to initiate a manual reactor trip. Unit 3 is currently stable in Mode 3. Decay heat is being released via the Steam Dumps to the Main Condenser. Normal offsite power is available and the unit is in a normal shutdown electrical line-up. The cause of the Main Feedwater oscillations is being investigated. The licensee notified the NRC Resident Inspector. The licensee notified State and local government agencies. * * * UPDATE FROM WALTER ORF TO DONALD NORWOOD AT 0129 EDT ON 6/13/2016 * * * The following clarifies Feedwater isolation vs. Feedwater oscillation: "At 2337 EDT on 6/12/16, a manual reactor trip was initiated on Unit 3 following feedwater isolation. As expected, Aux Feedwater system (AFW) initiated on the reactor trip. The trip was uncomplicated and the plant is currently in Mode 3 with a normal electric line-up and decay heat is being removed via steam dumps to the condenser. This is reportable under 10 CFR 50.72(b)(2)(iv)(B) - RPS Actuation - Critical and 10 CFR 50.72(b)(3)(iv)(A) - Valid Specific System Actuation." "The Feedwater isolation occurred due to high Steam Generator water level." The licensee notified the NRC Resident Inspector. Notified R1DO (Arner). | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-06-13
51999 | 0 | GRACE PACIFIC LLC |  |  |  |  | 2016-06-10 03:00 | 2016-06-10 16:38 | 2016-06-10 | MOISTURE DENSITY GAUGE DAMAGED BY CONSTRUCTION EQUIPMENT A Troxler Model 4640B gauge was run over by a steam roller and damaged at a jobsite at the Kona, HI airport. The licensee established a perimeter around the damaged gauge and the RSO approached using a radiation survey meter. The RSO placed the damaged gauge in its case and will transfer it to a secure location until it can be returned to the manufacturer. The gauge contains 0.8 mCi of Cesium-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-06-20
51998 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-06-09 13:30 | 2016-06-10 12:02 | 2017-06-09 | UNANALYZED CONDITION DUE TO A CHEMICAL PROCESSING MALFUNCTION "I. EVENT DESCRIPTION: High enriched scrap fuel material is processed in BWXT NOG-Lynchburg's Uranium Recovery facility to reclaim as much of the uranium as possible. The material is dissolved in acid and transferred to a series of horizontal columns where the acid is neutralized. The solution may be transferred to a set of accountability weigh columns for measurement prior to entering the uranium extraction process. The solution is subsequently transferred to a series of horizontal feed columns. Process water is used to periodically flush the horizontal columns during cleanup for materials accountability. "On June 9, 2016, a BWXT Nuclear Criticality Safety (NCS) engineer was notified that a bluish tint had been observed in the favorable geometry process water connection to the horizontal columns. By procedure, a blue dye is added to the acid to aid in its identification in the event of a spill. Further evaluation determined that the favorable geometry process water line was directly connected to the horizontal column system and the presence of the blue dye indicated a potential backflow of uranium bearing solution into the water line. The favorable geometry water line is under constant water pressure. The valves controlling the water flow are normally closed. There is also a check valve in the line to prevent backflow. The line is supplied from a favorable geometry header on the mezzanine above. The header supplies water to other processes in Uranium Recovery, including an unfavorable geometry hot water heater. "The Integrated Safety Analysis (ISA) was reviewed and an accident sequence for this potential backflow could not be identified. On June 9, 2016 at 1330 [EDT] it was the determined the accident sequence was unanalyzed and not properly documented in the ISA. Although IROFS [Items Relied on for Safety] listed for other accident sequences were applicable to the backflow scenario, the performance requirements of 10 CFR 70.61 were not maintained. As documented in the ISA, criticality was not 'highly unlikely.' "II. EVALUATION OF THE EVENT: Backflow into the favorable geometry water line can only be achieved by a forced flow to overcome the water pressure in the line. The only source for this pressurized flow is during the transfer from the accountability weigh columns to the horizontal column system. The solution is transferred using an air diaphragm pump. A trained and qualified operator opens the valve to initiate the transfer of solution from the accountability weigh columns to the horizontal columns (an uncredited control). The transfer of solution to the horizontal columns is monitored by a trained and qualified operator (an uncredited control). The water heater is substantially upstream of the supply line to the horizontal columns. The direction of flow of the process water in the supply header is away from unfavorable geometry hot water heater. The process water header is a favorable geometry (a credited IROFS). An operator checks the process water pressure on a daily basis (a credited IROFS). If the above existing IROFS and uncredited controls were considered in an ISA accident sequence, the likelihood of a criticality could be demonstrated to be highly unlikely. However, these uncredited controls are not designated as IROFS. Although the as-found condition presented no safety concern, the scenarios as documented in the ISA did not demonstrate that the performance requirements of 10 CFR 70.61 were maintained. There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. "Ill. NOTIFICATION REQUIREMENTS: BWXT is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(1), 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61.' "IV. STATUS OF CORRECTIVE ACTIONS: A section of the piping from the process water supply header was removed to physically isolate the process water supply from the horizontal columns. Criticality is no longer credible. The hot water heater is the only unfavorable geometry connected to the process water system in the Uranium Recovery facility. The hot water heater was assayed with a gamma survey instrument in several locations along the bottom and up the sides. No counts above background were detected. In addition, multiple liquid samples were taken from the bottom of the water heater and a cartridge filter housing prior to the hot water heater. All samples were well counted and determined to be below the Minimum Detectable Activity (MDA). An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation." The licensee has notified the NRC Resident Inspector and Region II personnel. * * * UPDATE AT 0944 EDT ON 06/09/17 FROM ROBERT JOHNSON TO S. SANDIN * * * "I. EVENT DESCRIPTION: On June 10th, 2016 BWXT NOG-Lynchburg notified the NRC of an improperly analyzed condition involving the potential backflow of uranium bearing solution from a fissile solution processing system into the Uranium Recovery process water system. This notification was recorded as Event Notification Number 51998. One of the corrective actions in response to Apparent Violation 70-27/2016-004-01 was to conduct an Extent of Cause review of 'tasks involving ancillary systems (e.g., process water, nitric acid, HF acid, compressed air, steam, etc.) in our Uranium Recovery and Specialty Fuel Facility to verify these systems have documented accident scenarios as needed to meet the requirements of 10 CFR 70.' "During the review of a waste processing system in the Specialty Fuel Facility (SFF), an additional potential backflow scenario was identified for a waste processing system. The system consists of a series of four favorable geometry columns. Waste solution is transferred to the columns using a less than or equal to 2.5 liter pump. The transfer of solution to the columns is monitored by a trained and qualified operator. Waste solution transferred to the columns is limited to a concentration of 5 grams 235U/liter as a Routine Operating Limit. A process water line is directly connected to the column system. The water is used to further dilute the concentration of the waste solution to a level that is acceptable for discharge into the hot waste drain (less than 0.04 grams 235U/liter). The column system is equipped with vent lines that overflow to the floor. The pump is capable of over-pressurizing the columns and possibly forcing waste solution into the favorable geometry process water system if the overflow vent lines were to fail. An unfavorable geometry hot water heater is located a significant distance downstream of the connection to the process water system. The Integrated Safety Analysis (ISA) was reviewed and an accident sequence for potential backflow of solution from the waste columns into the process water system could not be identified. "II. EVALUATION OF THE EVENT: Administrative IROFS were identified in other accident sequences of the ISA that are applicable to the waste column backflow scenario. These IROFS include the operator control of solution concentration initially transferred to the waste processing system, and the daily check of the process water pressure which limits backflow into the system. Although these IROFS were available and reliable, additional IROFS are needed to meet the performance requirements of 10 CFR 70.61. Neither the operator's monitoring of the solution transfer or the overflow through the column vent lines are credited as IROFS in the ISA. They are considered uncredited safety controls. "If either of the uncredited safety controls and the currently existing IROFS could be considered in an accident sequence, the likelihood of a criticality could be demonstrated to be highly unlikely. However, only IROFS documented in the ISA can be credited as preventing a criticality accident. Although the as-found condition presented no safety concern, the scenarios as documented in the ISA did not demonstrate the performance requirements of 10 CFR 70.61 were maintained. On June 8, 2017 at 10:00 am it was the determined the potential backflow of solution from the waste processing system was improperly analyzed and not documented in the ISA. As documented in the ISA, criticality was not highly unlikely. The SFF waste processing system was not in operation at the time of discovery. There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. "Ill. NOTIFICATION REQUIREMENT: BWXT is making this 24 hour report to update Event Notification Number 51998 in accordance with 10 CFR 70, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61. "IV. STATUS OF CORRECTIVE ACTIONS: The process water line connected to the SFF waste processing system was locked out and posted as 'Out of Service.' Additional corrective actions are to be determined. "The Extent of Cause review for AV 70-27/2016-004-01 is complete and the results are being finalized." The licensee informed the NRC Resident Inspector. Notified R2DO (Suggs), NMSS Events Notification, and Fuels Group by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2016-06-20
51997 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2016-05-31 | 2016-06-09 15:56 | 2016-06-09 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following was received from Iowa via email: "The licensee [Quad City Testing Lab] reported a source disconnect on a QSA Global 880 Delta radiography camera containing 66.3 curies of lr-192. The RSO was able to retrieve the source and return it to the shielded position. The time from disconnect to retrieval was less than two hours. During the RSO investigation, it was determined that the radiographer trainee did not properly connect the source pigtail to the drive cable and this action was not noticed by the radiographer trainer. Total doses during the event as indicated by pocket dosimeters were: RSO 130 mRem, radiographer trainer 55 mRem, and radiographer trainee 30 mRem. No member of the public received any dose from this event." Incident Number IA160001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2016-06-17
51996 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-06-08 10:37 | 2016-06-08 17:51 | 2016-06-08 | HIGH PRESSURE COOLANT INJECTION INOPERABLE "At 0800 CDT on 6/8/2016, 3-SR-3.5.1.7, 'HPCI [High Pressure Coolant Injection] Main and Booster Pump Set Developed Head and Flow Rate Test at Rated Reactor Pressure' periodic surveillance was being performed. As part of the surveillance procedure, HPCI was declared inoperable per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.1 Emergency Core Cooling Systems (ECCS) - Operating, Condition C at 0925. At 1037, the HPCI turbine was started and a turbine trip alarm was received as well as large swings observed on the suction pressure indicator and slow turbine response. The control room operator then manually tripped the HPCI turbine due to the abnormal indications received. "HPCl is a single train safety system and this notification is being made in accordance with 10 CFR 50.72 (b)(3)(v)(D). "The NRC Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-06-08
51995 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-08 15:26 | 2016-06-08 17:23 | 2016-06-08 | UNANALYZED CONDITION THAT COULD POTENTIALLY DEGRADE PLANT SAFETY "At 1526 Eastern Daylight Time on 6/8/2016, a determination was made involving the potential impact of a tornado on the Emergency Diesel Generators (EDGs). The EDGs are required to be operable to provide power to ensure that acceptable fuel design limits, reactor coolant system pressure boundary limits, and containment integrity are not exceeded during abnormal transients. Further, the EDGs are designed with a crankcase pressure trip (setpoint = 1 inch water), which is bypassed during an emergency start. Engineering has determined that a tornado could potentially cause actuation of the crankcase pressure trip due to a low barometric condition. If an emergency start signal has NOT previously occurred, then during a tornado, actuation of the crankcase pressure trip would energize the shutdown relay causing an EDG lockout condition. The EDG lockout condition prevents subsequent EDG starts (normal or emergency) until operators manually reset the lockout condition locally at the EDG. This condition could potentially affect all four EDGs simultaneously. "The EDGs are operable but degraded. All EDGs have successfully passed their required surveillances within the appropriate frequency. No severe weather warnings or watches are forecast in the local areas, which could challenge the crankcase pressure trip. "This condition places both units in an unanalyzed condition that potentially significantly degrades plant safety, 10 CFR 50.72 (b)(3)(ii)(B). "A compensatory measure has been established, that upon notification of a Tornado Warning, the EDGs would be 'emergency started' and run during the time the Tornado Warning was in effect. This action bypasses the crankcase pressure trip function and allows the EDGs to perform their required safety function. "The NRC Senior Resident Inspector has been notified." | 100 | 8 | 0 | 100 | 8 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-06-08
51994 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-08 15:26 | 2016-06-08 17:10 | 2016-06-08 | UNANALYZED CONDITION THAT COULD POTENTIALLY DEGRADE PLANT SAFETY "At 1526 Eastern Daylight Time on 6/8/2016, a determination was made involving the potential impact of a tornado on the Emergency Diesel Generators (EDGs). The EDGs are required to be operable to provide power to ensure that acceptable fuel design limits, reactor coolant system pressure boundary limits, and containment integrity are not exceeded during abnormal transients. Further, the EDGs are designed with a crankcase pressure trip (setpoint = 1 inch water), which is bypassed during an emergency start. Engineering has determined that a tornado could potentially cause actuation of the crankcase pressure trip due to a low barometric condition. If an emergency start signal has NOT previously occurred, then during a tornado, actuation of the crankcase pressure trip would energize the shutdown relay causing an EDG lockout condition. The EDG lockout condition prevents subsequent EDG starts (normal or emergency) until operators manually reset the lockout condition locally at the EDG. This condition could potentially affect all four EDGs simultaneously. "The EDGs are operable but degraded. All EDGs have successfully passed their required surveillances within the appropriate frequency. No severe weather warnings or watches are forecast in the local areas, which could challenge the crankcase pressure trip. "This condition places both units in an unanalyzed condition that potentially significantly degrades plant safety, 10 CFR 50.72 (b)(3)(ii)(B). "A compensatory measure has been established, that upon notification of a Tornado Warning, the EDGs would be 'emergency started' and run during the time the Tornado Warning was in effect. This action bypasses the crankcase pressure trip function and allows the EDGs to perform their required safety function. "The NRC Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-06-08
51993 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-05-25 | 2016-06-08 16:11 | 2016-06-08 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER WILL NOT FULLY OPEN The following report was received via e-mail: "On May 27, 2016 the Virginia Radioactive Material Program (VRMP) received a reciprocity notification from Heuft USA, Inc., to perform maintenance on a fixed gauge which was not properly functioning. The gauge is a Heuft Model 45US, serial number 1254AR containing 45 mCi of Am-241. "On May 31, 2016 the Heuft service engineer arrived at the Anheuser-Busch facility to investigate the gauge not functioning. The shutter was able to be fully closed but would not fully open. The engineer determined this to be due to a thin piece of material present in the shutter assembly which is not normal, and which interfered with the shutter opening fully. The engineer reported that the root cause of the problem appears that a cylindrical portion of the liner has broken off, perhaps as a result of cyclical thermal stress. "The shutter assembly was replaced and is working properly. There was no public health exposure or environmental release from this event." Virginia report: VA-16-006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-06-16
51992 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2015-01-16 | 2016-06-08 14:32 | 2016-06-08 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following report was received via e-mail: "Memorial Sloan-Kettering Cancer Center reported that a pediatric male patient only received 64.38 MBq (1.74 mCi) of I-124 labeled monoclonal 8H9 on 1/16/2015, instead of the prescribed 120.25 MBq (3.25 mCi). The patient had been diagnosed with pontine glioma. The incident occurred because the infusion process along the gauze at the site of the catheter connector leaked. The leak was not obvious on visual inspection. The cause was determined to be a procedure problem. Corrective actions included generating a new procedure and improvements to radioactive material labeling and handling." NMED: 150094 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-06-16
51991 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2015-08-13 | 2016-06-08 14:32 | 2016-06-08 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following report was received via e-mail: "Mount Sinai Medical Center (MSMC) reported that a patient only received 62 percent of their prescribed Y-90 microsphere (BTG International / Nordion model TheraSpheres) dose during treatment performed on 8/13/2015. The patient was prescribed to receive 1.81 GBq (48.92 mCi) of Y-90 microspheres for an exposure of 15,000 cGy (rad) to the liver. Access to the liver was gained through the femoral artery, with catheterization performed using a reverse curve catheter and coaxial micro-catheter. Following completion of the treatment procedure, radiation surveys using a Rados detector revealed 0 mR/hour. The microsphere delivery kit was then taken to the hot laboratory for further radiation surveys. At that time MSMC discovered a residual activity of approximately 33.7 percent of the microspheres in the vial. The cause was determined to be a procedure problem. Corrective actions included procedure modifications." NMED: 150485 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-06-16
51990 | 0 | PARAGON MEDICAL |  |  |  |  | 2016-06-01 | 2016-06-08 14:14 | 2016-06-08 | LOST GENERAL LICENSED MATERIAL The licensee lost two general licensed devices containing Po-210 sources. These were lost between 2011 and 2014. Manufacture: NRD Inc. Model Number: P-2021-8101, P-2101-8101 Device Serial Number: A2HW030, A2JJ603 Original activity per device: 10.00 mCi, 10.00 mCi Current activity: 0.0 mCI, 0.0 mCi Original ship date: 10/4/2011, 1/7/2013 The licensee notified R3 (Sulaiman). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-06-16
51989 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-06-06 | 2016-06-08 10:03 | 2016-06-08 | AGREEMENT STATE REPORT - CABLE ON BERTHOLD LB 300 MODEL FAILED The following report was received from the Texas Department of State Health Services via facsimile: "On June 7, 2016, the Agency [Texas Department of State Health Services] was notified by the Licensee's consultant that on June 6, 2016, the licensee found the cable on a Berthold LB 300 model gauge that connects the operating rod to a 500 milliCurie cobalt 60 source had failed. The source is currently inserted in the in source well in the normal operating position and cannot be removed. The failure does not create any additional exposure risk to the licensee's workers or members of the general public. The licensee stated there is no access to the vessel the source is located in during operation. The licensee intends to work with the manufacturer to repair the gauge during its next outage. Additional information on this event will be provided in accordance with SA-300." Texas Incident Report No.: I-9410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-06-16
51988 | 0 | CURTISS WRIGHT |  |  |  |  | 2016-06-08 | 2016-06-08 09:27 | 2016-07-08 | PART-21 REPORT - NONCONFORMANCE ON STRUTHERS-DUNN RELAY FOR PSEG NUCLEAR LLC "This letter serves as an interim report in accordance with 10 CFR 21.21 pertaining to a potential deviation associated with Struthers-Dunn relays P/N B255XCXPFHSC125V supplied to PSEG Nuclear LLC. Based upon information obtained from PSEG, a defect may exist with the reset coil of the Struthers-Dunn relay listed above. Preliminary observations indicate the reset coil had shorted (opened) during operation, and that no other sub-components of the relay are believed to be associated with this failure. PSEG is aware of Curtiss-Wright's investigation into this failure. "Evaluation of reportability in accordance with 10 CFR Part 21 is not able to be completed within the 60-day evaluation period due to the need for additional time to collect and evaluate the necessary information. It is currently expected that the evaluation of this defect will be completed by July 22, 2016." POC: Timothy Franchuk Director, Quality Assurance 4600 East Tech Drive Cincinnati, Ohio 45245 (513) 528-7900 The licensee indicated that the current list of affected plants are being evaluated. * * * UPDATE ON 07/08/16 AT 1511 EDT FROM MARGIE HOVER TO BETHANY CECERE * * * The following is excerpted from the submitted report: "Struthers-Dunn Relay P/N: B255XCXP125V. Note that the original interim report identified the part number as B255XCXPFHSC125V, which contains designators 'FHSC', which are an internal Curtiss-Wright numbering scheme." "The following facilities were supplied the components: Salem Nuclear Generating Station/Hope Creek Generating Station Total Quantity: 104 Wolf Creek Generating Station Total Quantity: 10 "Evaluation: Findings as a result of the Curtiss-Wright Failure Analysis indicated that the reset coil failure was linked to the magnet wire insulation, the coil winding process, and the attachment of the coil leads to the magnet wire "Corrective Action: Struthers-Dunn has revised their reset coil assembly procedure such that the reset coil receives two wraps of insulation tape prior to laying the magnet wire terminations which are then soldered to the relay leads which connect to the pins at the base of the relay. Based on testing by Struthers-Dunn this two wrap process greatly increases dielectric strength which should eliminate the failure modes identified. Affected relays were returned to Struthers-Dunn to have the reset coil replaced using the revised reset coil assembly method. After the coils have been replaced they are sent to Curtiss-Wright Nuclear Division to be re-dedicated prior to being returned to the end user." Notified the R1DO (Bower), R4DO (Drake), and Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2016-06-08
51987 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2016-06-08 02:26 | 2016-06-08 07:01 | 2016-06-08 | DISCOVERY OF UNISOLABLE REACTOR PRESSURE BOUNDARY LEAKAGE "Susquehanna Unit 1 identified RPV [reactor pressure vessel] pressure boundary leakage from [local power range monitor] LPRM 24-09 housing above the flange during an under vessel leak inspection on 06/08/2016 at 0226 EDT. The leakage point is a through wall indication on the ASME Class 1 LPRM stub tube. The leakage is not isolable from the reactor vessel. The reactor was in Mode 4 at the time of discovery. "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii)(A)." A repair plan is being formulated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-06-08
51986 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2016-06-07 07:30 | 2016-06-07 14:10 | 2016-06-07 | FITNESS FOR DUTY A non-licensed contract supervisor had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2016-06-07
51985 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-06-07 10:30 | 2016-06-07 13:07 | 2016-06-07 | BOTH SECONDARY CONTAINMENT DOORS OPEN SIMULTANEOUSLY "At 1030 EDT on 6/7/2016, both doors of a secondary containment airlock were reported to be simultaneously open for approximately 2 seconds during the normal passage of personnel. The brief time that the doors were simultaneously open constitutes an inoperable condition of secondary containment. Secondary containment differential pressure was maintained throughout the time period that the doors were open. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG-1022, Rev. 3, 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.'" The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-06-07
51984 | 0 | NASA AMES RESEARCH CENTER |  |  |  |  | 2016-06-06 | 2016-06-06 18:25 | 2016-06-06 | MISSING SINGLE TRITIUM EXIT SIGN The licensee reported the loss of a single tritium exit sign at Moffett Field, CA. The sign was an SRB Technologies sign with an initial activity of 20 Ci. The serial number is 154848. At this time, the licensee is still investigating the disposition of the sign. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-06-14
51983 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2016-06-06 05:56 | 2016-06-06 08:13 | 2016-06-06 | ISOLABLE LEAKAGE IDENTIFIED FROM SEAL WATER LINE WELD INSIDE RCS PRESSURE BOUNDARY "Susquehanna Unit 1 commenced a manual shutdown on 06/05/2016 for a maintenance outage. At 2202 hours [EDT] on 06/05/2016, operators began reducing power in accordance with plant procedures. At 0352 hours on 06/06/2016, the Main Turbine was tripped with reactor power at approximately 15%. "The Mode switch was taken to 'STARTUP/HOT STANDBY' (Mode 2) at 0515 hours on 06/06/2016. Manual insertion of control rods was paused as scheduled for entry into the drywell for inspections. There were no ESF actuations. "At 0556, the licensee identified leakage from a weld on seal water line piping connected to the 1B reactor recirculation pump seal area. The location is within the reactor recirculation loop isolation valves, therefore is isolable from the reactor vessel. The piping is ASME Class 2 and is reactor coolant pressure boundary. The reactor was in Mode 2 at the time of discovery. "This event is being reported as a plant shutdown required by technical specifications pursuant to 10CFR50.72(b)(2)(i) and degraded condition pursuant to 10CFR50.72(b)(3)(ii)(A). "Activities are continuing to achieve cold shutdown." The licensee informed the Commonwealth of Pennsylvania and the NRC Resident Inspector. | 8 | 0 | 0 | 9 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2016-06-06
51982 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-06-05 12:27 | 2016-06-05 16:22 | 2016-06-05 | REACTOR TRIP AND ECCS ACTUATION CAUSED BY TURBINE GOVERNOR VALVE FAILURE "On June 5, 2016 at 1227 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) Unit 2 was in MODE 1 at approximately 12.5% power when a safety injection actuation occurred, followed by an automatic reactor protection system (RPS) trip. Preliminary data suggests that the #1 high pressure turbine governor valve failed open causing a steam header pressure rate of decrease safety injection [SI] actuation signal. As designed, the safety injection actuation caused both trains of the shared Emergency Gas Treatment System (EGTS) to align to Unit 2, requiring WBN Unit 1 to enter Technical Specification (TS) LCO 3.0.3 at 1227 [EDT]. Also as designed, Unit 1 annulus pressure momentarily increased, causing operation personnel to enter LCO 3.6.15 Condition B at 1240 [EDT]. At 1242 [EDT], after annulus pressure normalized, operations personnel exited LCO 3.6.15. At 1245 [EDT], Operations personnel secured safety injection and Unit 2 was stabilized in MODE 3 at normal operating pressure and temperature. By 1349 [EDT], Unit 1 Operations personnel had restored both trains of EGTS to standby readiness, and exited TS 3.0.3. No primary safety barriers (RCS, containment and fuel clad) were challenged and no primary or secondary safety or relief valves actuated during the event. The Unit 2 plant trip was uncomplicated and safety equipment operated as expected. "Unit 2 is stable in Mode 3 at normal operating temperature and pressure, in normal shutdown power alignment. Unit 1 is stable in Mode 1 at 100% power. "The Senior Resident Inspector has been notified of this event." The MSIVs are shut with the steam generators (SG) discharging steam using the atmospheric dump valves. There is no primary to secondary leakage. Motor driven AFW pumps are running to maintain SG levels. RCS pressure remained above ECCS (Emergency Core Cooling System) discharge pressure. | 0 | 0 | 0 | 0 | 13 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-06-05
51981 | 0 | PERRY COUNTY MEMORIAL HOSPITAL |  |  |  |  | 2016-06-03 07:30 | 2016-06-03 16:17 | 2016-06-03 | PATIENT ADMINISTERED THE WRONG BYPRODUCT MATERIAL The following was received via email: "This is a report and notification of a medical event for Perry County Memorial Hospital, located in Perryville, Missouri, which occurred today June 3, 2016 at approximately 7:30 a.m. CST. This medical event is being reported as required under 10 CFR Part 35.3045 (a)(2)(i), administration of a wrong radioactive drug containing byproduct material resulting in an effective dose equivalent of greater than 0.05 Sv or 5 rem. "At approximately 8:15 a.m. today, [The Diagnostic Radiological Physicist] received a call from Perry County Memorial Hospital, that one of his nuclear medicine technologists had inadvertently administered a 63 y/o female patient a bulk unit dose of approximately 128 mCi of Tc-99m Sodium Pertechnetate intravenously. This female patient was scheduled to receive a 25 mCi dose of Tc-99m Medronate intravenously for bone scintigraphy. Using a Tc-99m Sodium Pertechnetate package insert provided by the unit dose supplier, [the Diagnostic Radiological Physicist] estimated that the resultant effective dose equivalent to the patient will be approximately 0.06 Sv or 6 rem. The resultant highest dose to any organ or tissue is estimated to be approximately 27 rads, which would be to the patient's upper lower intestinal wall. "The patient has been notified with regards to this medical event. In addition, the RSO [Radiation Safety Officer] / Authorized User for Perry County Memorial Hospital has also been notified." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(2) |  |  |  | 0 | 2016-06-13
51980 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-04-26 | 2016-06-03 15:34 | 2016-06-03 | AGREEMENT STATE REPORT - MISSING SOURCE The following information was received by the State of Ohio via email: "On 4/26/2016, Physics reported that during prepping a return shipment the dosimetrist discovered one I-125 prostate seed was missing from the lead pig. The lead pig contained loose/broken seeds from the implant performed on 4/6/2016. There were three seeds in the vial where there should've been four. The RSO interviewed the dosimetrist and the physicist who worked this case. Inventory log and loading summary were audited. Inventory log recorded 28 seeds returned to storage. Of the 28 seeds returned, 24 were in the cartridge and 4 were loose/broken seeds stored in the lead pig. It was not until 4/26/2016 when Physics discovered only 3 seeds were in the lead pig. Radiation surveys records were audited. Surveys were performed accordingly and readings were background level. "At this time, the seed has not been located. Based on the information provided by the medical physicist and the dosimetrist, it is still unclear as to precisely determine when and how the seed became missing. Licensee believes there was no radiation exposure to the individual(s) involved. To prevent a recurrence, two individuals shall visually count the seeds in the lead pig before leaving the operating room. Furthermore, two individuals shall review loading summary to confirm all seeds are accounted for. "Licensee has previously observed that 1-125 seeds are prone to static buildup and have the tendency to cling to plastic, glass walls, and other surfaces. Most likely, the lost seed was swept up and discarded with normal trash. Based on the relatively low activity and low energy of the 1-125 seed and measured background readings in the operating room, there was no radiation exposure to workers or members of the public due to this loss." Source/Radioactive Material: Sealed source brachytherapy Manufacturer: Theragenics Model Number: AgX100 Radionuclide: I-125, 0.000396 Ci Ohio Item Number: OH160007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-06-13
51979 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-04-21 | 2016-06-03 15:34 | 2016-06-03 | AGREEMENT STATE REPORT - MISSING SOURCE The following information was received by the State of Ohio via email: "On 4/21/2016 in OR [Operating Room] 11, during seed loading, the dosimetrist noticed that one seed was missing from the transferring stylet as he was transferring the seeds to the loading needle. He immediately notified the physicist in the room. The physicist then checked the sterile area around the cartridge with a survey meter and picked up radiation reading by the luer - lock hub of the cartridge. The physicist assumed that the source had fallen in the sterile towel under the cartridge and determined loading should continue, and they will retrieve the dislodged seed after all needles have been loaded. After all needles were loaded and while implantation was still in progress the physicist and the dosimetrist went to retrieve the dislodged seed but they were not able to locate it. They resurveyed the spot where it was and there was no radiation detected. The physicist emptied the cartridge to verify the number of seeds remaining in the cartridge and the count was as stated in the loading summary. The dislodged seed was missing. "To prevent a recurrence, surgical drapes will be used to cover the area under and around the cartridge/loading area instead of sterile hand towels. This would make it easier to identify any seed that may have fallen out during loading. Loose/broken seed(s) will be placed in the lead pig immediately. If there is a dislodged/loose seed that could not be recovered immediately, the physicist will ensure that everyone leaving the room is surveyed. "Licensee has previously observed that I-125 seeds are prone to static buildup and have the tendency to cling to plastic, glass walls, and other surfaces. Most likely, the lost seed was swept up and discarded with normal trash. "Based on the relatively low activity and low energy of the I-125 seed and measured background readings in the operating room, there was no radiation exposure to personnel or members of the public due to this loss." Source/Radioactive Material: Sealed source brachytherapy Manufacturer: Theragenics Model Number: AgX100 Radionuclide: I-125, 0.000382 Ci Ohio Item Number: OH160006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-06-13
51978 | -1 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-05-31 | 2016-06-03 15:34 | 2016-06-03 | AGREEMENT STATE REPORT - LEAKING SOURCE The following information was received by the State of Ohio via email: "Leak test of sealed source indicated greater than 185 Bq (0.005 microCi) of removable contamination. "Cs-137 vial source, 177 microCi, 44,000 cpm removable. "Several wipes were performed as well as a measurement with a multi-channel analyzer to confirm the radioisotope. The source was placed in a lead pig, taped closed, labeled as a leaking sealed source, and placed in the main hot lab hot-waste storage container. Area wipes were performed to verify that no contamination was present in the vicinity. The source has been removed from service." Serial Number: 1074-22-5 Ohio Item Number: OH160005 * * * RETRACTION ON 6/3/16 AT 1624 EDT FROM STEPHEN JAMES TO DONG PARK * * * After further review, report OH160005 previously submitted to the Ops Center was not subject to 24-hour notification. Notified R3DO (Hills) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-06-13
51977 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-05-27 | 2016-06-03 15:34 | 2016-06-03 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received by the State of Ohio via email: "Shutter stuck in open (normal operating) position on Berthold Model LB300L Fixed Gauge, containing approximately 20 microCi Co-60. Service provider has been contacted to repair. Gauge is not accessible to personnel and continues to operate in process line." Berthold Gauge Serial Number: 623/3-04-04 Ohio Item Number: OH160004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-06-13
51976 | 0 | ABB, INC. |  |  |  |  | 2016-06-03 | 2016-06-03 13:14 | 2016-06-03 | PART 21 - NOTIFICATION OF DEVIATION OF K-LINE CIRCUIT BREAKER SECONDARY TRIP LATCH The following was excepted from a report from ABB, Inc. via email: "This letter provides notification of a defect associated with the secondary trip latch, P/N: 716789E00, which is used in the 167710T01 & 167710T03 secondary latch bar assembly and assembly kit, respectively. These assemblies are used in low voltage K-Line 225-800 Amp and 1600-2000 Amp circuit breakers. The reported failure was caused by the pin in the secondary trip latch that the return spring attaches to not being installed properly. The pin hit the tab on the tripper bar when the latch returned to the reset position. This caused the breaker to trip open. This failure was reported by Xcel Energy Prairie Island Nuclear Plant and it is the only reported occurrence of a failure caused by the return spring pin being out of position. The secondary trip latch has been cast by the same since 1996. No other field failures or failures in the ABB Service facilities have been reported as a result of this pin being out of position. Information is provided as specified in 10CFR21 paragraph 21.21(d)(4). "Notifying individual: Andrew Wall, Vice President & General Manager, ABB (Electrification Products Medium Voltage Service US), 2300 Mechanicsville Road, Florence, SC 29501 "Identification of the Subject component: ABB part numbers 716789E00 (secondary latch bar) and 167710T01 & 167710T03 (secondary latch bar assemblies). The secondary latch bar is available as an individual component and the secondary latch bar assemblies are utilized as components, as part of refurbishment kits, in K-Line operating mechanisms, in new K-Line breakers, and they may be replaced during a K-Line breaker refurbishment. "Nature of the deviation: The pin that holds the return spring in place was not properly installed. The defect is believed to have occurred during the assembly process of the latch bar. The latch used in the Prairie Island Nuclear Plant circuit breaker was fabricated in 2013. "Corrective actions include: Quarantined and inspected PIN: 716789E00 and 167710T01/167710T03 assemblies in inventory. (Action complete) Notified vendor of the issue via the ABB Supplier Corrective Action Request process. (Action complete) Revised Critical Characteristic card for PIN: 716789E00 to incorporate measurement of the pin in question. (Action complete) Conducted training with QA and Operations personnel for awareness (Action complete) "Recommendations: Because of the large potential variety of usages of the potentially affected circuit breakers, ABB (Medium Voltage Service) cannot determine if the potential for a substantial safety hazard exists at any licensee's facility if the circuit breaker fails to operate. It is recommended the Licensees inspect the in-service components at the next convenient maintenance opportunity and components in stock prior to installation. The pin should protrude 0.26 ( +/- 0.02) inches out of both sides of the section of the latch bar assembly. If the latch is installed on a K-Line circuit breaker, the latch can be inspected from the bottom side of the mechanism without disassembly. "Questions concerning this notification should be directed to the Quality Manager at the Medium Voltage Service Center in Florence, SC at (843) 413-4782 or Fax (843) 413-4853." HOO Note: See EN #51975 for Part 21 received from Prairie Island Nuclear Generating Station. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-06-03
51975 | 0 | PRAIRIE ISLAND NUCLEAR GENERATING |  |  |  |  | 2016-05-31 | 2016-06-03 13:02 | 2016-06-03 | PART 21 - NOTIFICATION OF DEVIATION OF K-LINE CIRCUIT BREAKER SECONDARY TRIP LATCH The following was received from Prairie Island Nuclear Generating Plant via fax: "Name and address of the individual or individuals informing the Commission: Thomas A. Conboy Director of Site Operations Prairie Island Nuclear Generating Plant Northern States Power Company - Minnesota 1717 Wakonade Drive East Welch, MN 55089 "Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: ABB Inc. BREAKER, CIRCUIT, SWITCHGEAR, 480, 3, 600 Type: K-600S EO "Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: Address on original purchase order: ABB Power Distribution 455 Century Point Lake Mary, FL 32772 Address on current Qualified Supplier List: ABB, Inc. - Protective Relays & Switches 4300 Coral Ridge Dr. Coral Springs, FL 33065 "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply: During surveillance testing of the D5 emergency diesel generator, Prairie Island Nuclear Generating Plant (PINGP) observed the diesel room cooling fan (21 D5 DSL RM CLG FAN) did not start. The fan did not start because the supply breaker (BKR 211D) did not close to provide power to the fan. Visual inspection of the breaker identified the Secondary Trip Latch Assembly had an abnormal pin installation. The diesel room cooling fan assures operability of the emergency diesel generator that is necessary to assure the capability of shutting down the reactor and indefinitely maintaining it in cold shutdown. "The date on which the information of such defect or failure to comply was obtained: May 31, 2016. "In the case of a basic component which contains a defect or fails to comply, the number and location of these components In use at. supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part: Eleven ABB K-600S EO breakers with 86 Lock Out are on the Prairie Island Nuclear Generating Plant (PINGP) site: BKR 211D, 21 D5 DSL RM COOLING FAN BKR 221D, 22 D6 DSL RM COOLING FAN BKR 112C, MCC 1S1 & PRZR HTRS GRP A BKR 212C, MCC 2S1 & PRZR HTRS GRP A BKR 122C, MCC 1R1 & PRZR HTRS GRP B BKR 222C, MCC 2R1 & PRZR HTRS GRP B Five spares not Installed in plant. "The corrective action which has been. is being. or will be taken: the name of the individual or organization responsible for the action: and the length of time that has been or will be taken to complete the action: PINGP entered the breaker failure into the Corrective Action Program. PINGP replaced the two diesel cooling room fan breakers with breakers having no abnormally positioned pins in the secondary trip latch assemblies. PINGP inspected BKR 221D and found a satisfactory Secondary Trip Latch Assembly. PINGP performed extent of condition inspections on the four pressurizer heater circuit breakers and found satisfactory Secondary Trip Latch Assemblies. PINGP will revise Electrical Maintenance Procedure PE 4824, Receipt Inspect 480 Volt Breaker, to visually inspect K-600S EO circuit breakers for Secondary Trip Latch Assembly pin alignment. The revised inspection procedure will prevent recurrence since PINGP performs the inspection prior to installing 480V circuit breakers in the plant. The procedure change is expected to be completed by end of August. Site Transmission and Distribution Coordinator and lead breaker (relay) technician are informed on this issue. PINGP performed a past operability review and determined that the D5 emergency diesel generator would have performed its specified safety function for the time period reviewed. PINGP returned the failed breaker to the manufacturer for evaluation. Additional corrective actions will be taken as necessary. "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been. is being, or will be given to purchasers or licensees: Verify alignment of Secondary Trip Latch Assembly pins on K-6008 EO circuit breakers with 86 Lock Out. Contact the K-600S EO manufacturer for additional advice. "In the case of an early site permit. the entities to whom an early site permit was transferred: Not applicable." HOO Note: See EN #51976 for Part 21 received from ABB, Inc. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-06-03
51974 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2016-06-02 12:45 | 2016-06-03 11:44 | 2016-06-03 | ADMINISTRATIVE VERIFICATIONS OF VENTILATION CLEAN-OUT CONTAINERS WERE NOT PERFORMED "Description of the Event: On June 2, 2016 at 1245 [EDT], it was reported to the Environment, Health and Safety (EH&S) department that the two administrative verifications of ventilation clean-out containers were not performed. "The Conversion Area nitric acid scrubber was scheduled for annual inspection and cleaning May 27 thru June 1. On May 18th, 25 disposable clean-out containers were obtained from the storeroom in preparation for the annual scrubber cleaning. The clean-out containers are used to collect special nuclear material (SNM) from scrubber and filter house cleanings. After obtaining new clean-out containers from the storeroom and prior to using them with SNM, one container from each lot is required to be measured by an operator to assure proper dimensions (IROFS STORAGE-GEN-126). An independent measurement by a process engineer to assure proper dimensions is also required prior to use with SNM (IROFS STORAGE-GEN-127). An additional 20 clean-out containers were obtained from the storeroom on May 31st. "On June 2nd, a process engineer discovered that the measurement verifications were not performed. EH&S was notified of the event by phone and the 'Redbook' reporting system. (Redbook Issue #71225). At no time was there any actual or potential health and safety consequence to the workers, the public, or the environment. "The safety function of these IROFS [Items Relied on for Safety] is to preclude using an incorrect container size. The ventilation clean-out containers are a standard stocked storeroom item. They have an approximate volume capacity of 1.5 gallons, providing a substantial safety margin to the minimum requirement of 5.7 gallons in the Criticality Safety Evaluation (CSE) which assumes an optimum uranium/water mixture and full 12-inch water reflection. The CSE also requires more than 64 close packed containers with an optimum uranium/water mixture; while the containers are limited to maximum array of 25 (IROFS STORAGE-GEN-112). Additionally, the clean-out containers remained spaced 18 inches apart at all times. "Based on available IROFS, this accident sequence was unlikely, a failure probability of [10E-3], and not highly unlikely, a failure probability of [10E-4] or less. Therefore, this geometry accident sequence does not meet the performance requirements of 10CFR70.61. As stated above, the actual configuration remained safe at all times. Also, no external conditions affected the event. "Immediate Corrective Actions: The clean-out container dimensions were verified as correct. "This event has been entered into the facility Corrective Action Prevention And Learning system (CAPAL) #1003888517." The Licensee will notify NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2016-06-03
51973 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-05-27 | 2016-06-02 20:22 | 2016-06-02 | AGREEMENT STATE REPORT - BRACHYTHERAPY UNDERDOSE The following was received from the State of California via email: "The RSO [Radiation Safety Officer] of Loma Linda Medical Center notified the RHB [Radiologic Health Branch] Brea ICE [Inspection, Compliance and Enforcement] office that they believe a medical event occurred on Friday, May 28, 2016. "A patient was admitted to the hospital for treatment of carcinoma. The treatment plan involved [10 CFR] 35.400 use of Cs-137 sealed sources for brachytherapy with a tandem and ovoid applicator. The patient's written directive called for 3,460 cGy to target area A (left side tandem), but only approximately 1,500 cGy was delivered. The lower rectum and vaginal areas received more than expected dose, but is believed to be within tolerance. Critical organs of bladder and mid-rectum also received less than expected incidental exposure. "The cause of the under dose was human error. The applicator tube used to place the source into the tandem had become crimped by the lead pig during transport to the patients room. During application by the resident physician and medical physicist, the resistance felt during the application process lead them to believe the source was fully deployed to the end of the tube. "The chief physicist notified the RSO on Tuesday, May 31, 2016 at 1630 pm, of his dose calculations, in which the hospital began medical event notifications." 5010 Number: 060216 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-06-10
51972 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2016-06-02 | 2016-06-02 16:30 | 2016-06-03 | PART 21 - NOT APPROVED CURRENT TRANSFORMERS INSTALLED IN SAFETY RELATED EQUIPMENT The following was excerpted from the Ametek Part 21 Report received via email: "Ametek inverter manufactured with Signal Transformer R-10607, Ametek part number 80-310879-90 was inadvertently installed in several units from an unapproved supplier. The potential for this situation to occur exists for new equipment delivered between July of 2015 and May of 2016. Affected utilities and equipment serial numbers are identified below. "Dominion Nuclear Connecticut, Millstone 96000067-0411, 96000067-0511, 96000067-0611, 96000067-0711 "Krsko Nuclear Power Plant 96000068-0211, 96000068-0311, 96000068-0411 "Exelon, Byron Station 96000075-0311, 96000075-0411, 96000075-0511, 96000075-0611 "Ametek Solidstate Controls is submitting the following Report of a Potential Defect in accordance with the requirements of 10CFR Part 21. "To replace the transformers, Ametek Solidstate Controls will work with you to arrange replacements. Please our Client Services group at 1-614-846-7500. mailto: eric.phillips@ametek.com" The potential problems include: - Mag wire terminated with improper lug and tooling which may cause loss of feedback to static transfer function. - Spot welded band around the core which has not been adequately seismically evaluated. - 180 degree Celsius insulation system provided instead of the approved 200 degree Celsius and unapproved materials used which impacts the aging analysis. * * * UPDATE FROM ETHAN SALSBURY TO VINCE KLCO ON 6/3/2016 AT 1103 EDT * * * Serial numbers for KRSKO and Millstone are corrected as follows: Dominion Nuclear Connecticut, Millstone 96000068-0211 96000068-0311 96000068-0411 KRSKO Nuclear Power Plant 96000067-0411 96000067-0511 96000067-0611 96000067-0711 Notified the R1DO (Schroeder), R3DO (Hills) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-06-02
51971 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-06-01 | 2016-06-01 15:46 | 2016-06-28 | AGREEMENT STATE REPORT - TWO RADIOACTIVE MATERIALS PACKAGES NOT LOCATED AFTER CARRIER ACCIDENT The following report was received from the Texas Department of State Health Services via facsimile: "On June 1, 2016, the licensee notified the Agency [Texas Department of State Health Services] that one of its shipments was involved in a transportation accident. A carrier was transporting two type A packages, each containing a vial of fluorodeoxyglucose (F-18), 10 mCi, when it was involved in an accident on an unreported freeway. Emergency responders arrived at the scene, the driver was taken to a hospital. The vehicle was cleared from the roadway. It is uncertain at this time where the vehicle or the packages are located. The licensee is obtaining information to recover the radioactive materials. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9408 * * * UPDATE AT 1703 EDT ON 6/1/16 FROM ART TUCKER TO JEFF HERRERA * * * The following report was received from the Texas Department of State Health Services via email: "Agency [Texas Department of State Health Services] received call 1529 CDT from licensee. He informed us [Texas] that the packages were intact, not damaged, and recovered from the accident vehicle. The packages are currently located at the original pharmacy location in Dallas. The vial activity amount was 15 mCi each instead of the reported 10 mCi. The licensee stated that since the driver was not his employee he could not obtain information on the driver. "The packages were intact and no exposures occurred." Notified the R4DO (Deese), NMSS Events, and Mexico (via email). * * * UPDATE AT 1023 EDT ON 6/28/2016 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following report was received from the Texas Department of State Health Services via email: "On June 23, 2016, the licensee provided updated information to the Agency [Texas Department of Health Services]. This information stated the activity of the radionuclide was 62 and 56 millicuries instead of the 15 millicuries previously reported." Notified the R4DO (Hipschman), NMSS Events Resource (via e-mail) and Mexico (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-06-09
51970 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-05-24 | 2016-06-01 15:17 | 2016-06-01 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE TO THE LEFT LOBE OF LIVER The following report was received from the New York State Department of Health, Bureau of Environmental Radiation Protection via facsimile: "Radiation safety staff from a hospital called on 5/24/2016 to report a medical event that meets the reportability criterion on the borderline. 79.5 percent of intended dose is believed to have been delivered to the left lobe of the liver of a patient receiving Y90 treatment. The patient had received treatment to the right lobe a month ago. The left lobe was smaller with small vessels. The waste measured after the procedure showed that only about 79 .5 percent had been delivered. The licensee usually is able to administer 95 percent of intended dose in this procedure. We were informed that since the amount retained in the device is about the same, smaller doses tend to show a greater percent in retained in the device. They will send a report within 7 days." NYS NRC Event Report ID No.: NYDOH-16-02 NY State Incident No.: 1146 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-06-09
51969 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2016-06-01 10:46 | 2016-06-01 14:33 | 2016-06-01 | NINE MILE POINT UNIT 1 MOMENTARY LOSS OF SECONDARY CONTAINMENT "Nine Mile Point Unit 1 (NMP1) experienced a momentary loss of Secondary Containment due to both Reactor Building (RB) airlock doors being opened at the same time. "At 1046 [EDT] on 06/01/16, both RB airlock doors were opened simultaneously for less than 5 seconds. This resulted in Secondary Containment being declared Inoperable (TS 3.4.3). The airlock doors were closed and Secondary Containment was restored to Operable. "The event is reportable in accordance with 10 CFR 50.72(b)(3)(v)(c), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the NRC Resident Inspector has been notified." The licensee notified the State of New York. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-06-01
51968 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2016-06-01 09:00 | 2016-06-01 10:40 | 2016-06-01 | MANUAL REACTOR SCRAM DUE TO UNEXPECTED CORE FLOW CHANGE "Limerick Unit 2 was manually scrammed from 100 [percent] power at 0900 [EDT] on 6/1/2016 in accordance with plant procedure OT-112 'Unexpected/Unexplained change in core flow' when both 2A and 2B Recirculation Pump Adjustable Speed Drives (ASDs) tripped due to an electrical fault. The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Steam Bypass valves to the Main Condenser and normal level control using Feedwater. The Manual RPS actuation is reportable under 10 CFR 50.72 (b)(2)." All rods inserted fully on manual scram and the plant is in a normal shutdown electrical line up. Unit 1 was not affected by this event. The licensee plans to issue a press release. The licensee notified local counties and Pennsylvania Emergency Management Agency (PEMA). The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-06-01
51967 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2016-05-31 16:26 | 2016-05-31 18:12 | 2016-05-31 | CALVERT CLIFFS LOSS OF LOAD TURBINE/REACTOR TRIP FROM 100 PERCENT POWER "On 05/31/2016 at 1626 [EDT], a Reactor Trip occurred on Loss of Load RPS [Reactor Protection System] actuation. The Turbine Trip was apparently caused by a failed ESFAS [Engineered Safety Feature Actuation System] logic module. The failed NSR [Non Safety Related] logic module was associated with 11 Steam Generator High Level Turbine Trip. All systems responded as designed. Normal decay heat removal is to the condenser. All offsite power sources remained in service." The NRC Resident Inspector was notified. | 0 |  | 0 | 100 |  | 0 | -1 | -1 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-05-31
51966 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-05-29 | 2016-05-30 22:31 | 2016-05-30 | AGREEMENT STATE - STOLEN TROXLER NUCLEAR DENSITY GAUGE The following report was received from the State of Florida Bureau of Radiation Control via email: "[A] Troxler nuclear density gauge model 3440, device serial number 24596, was checked out from [the licensee's] office on Saturday afternoon, May 28th, to take it for repairs. The locked vehicle containing the gauge was parked in a secured parking garage. The vehicle was stolen at 0708 [EDT] according to surveillance video. The vehicle was discovered missing at approximately 1100 [EDT]. [The] City of Miami Police were called immediately. "Case #160529-161287 filed by [Miami Police]." Troxler gauge source: Am-241/Be - 40mCi, Cs-137 - 8mCi (originally). Florida Incident Number: FL16-069 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-06-07
51965 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-30 09:30 | 2016-05-30 19:11 | 2016-05-30 | MANUAL OPENING OF REACTOR TRIP BREAKERS DUE TO ROD POSITION ERROR GREATER THAN 12 STEPS "On 5/30/2016 at 0930 [PDT], Unit 2 was in its 19th refueling outage in Mode 4 (hot shutdown, reactor subcritical). Routine post-maintenance testing of digital rod position indication (DRPI) was in progress in accordance with Surveillance Test Procedure (STP) R-1C. Rod Shutdown Bank A was being withdrawn. With Shutdown Bank A Group 1 demand indicating 14 steps, and Group 2 demand indicating 13 steps, Bank A DRPI indicated 12 steps but control rod B4 DRPI indication remained at Step 0. With the bank demand position exceeding rod B4's DRPI indication by greater than 12 steps, Operators manually opened the Reactor Trip Breakers, placing all the rods in a known position due to an inoperable DRPI system. All systems actuated as required and rods fully inserted. "Manual initiation of a reactor trip where the actuation is not part of a pre-planned evolution is reportable under 10 CFR 50.72 (b)(3)(iv)(A). While the reactor trip was initiated in accordance with the STP's instructions, the manual actuation was not a preplanned outcome of the STP. "Subsequently, it was determined that rod B4 had remained on the bottom at Step 0 as indicated by DRPI. A moveable gripper fuse was blown, preventing that rod from being withdrawn. The blown fuse was replaced and testing continued in accordance with the procedure. "There was no impact to public, employee, or plant safety. "The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-05-30
51964 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-27 20:46 | 2016-05-27 23:17 | 2016-05-27 | OFFSITE NOTIFICATION DUE TO AN INADVERTENT ACTUATION OF ONE EMERGENCY SIREN "A South Texas Project offsite emergency notification siren was inadvertently going off. The Matagorda County Sheriff's Office notified Site Security that a siren had actuated. At the time of the inadvertent siren actuation the area was experiencing lightning and rain. Suspect lightning caused the inadvertent siren actuation. Station Personnel are addressing the issue with the siren. "The Matagorda County Sheriff's Office was the only offsite agency that was contacted during the event." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-05-27
51963 | 0 | JANX INTEGRITY GROUP |  |  |  |  | 2016-05-27 | 2016-05-27 16:56 | 2016-05-27 | RADIOGRAPHY CAMERA SOURCE UNABLE TO BE RETRACTED Radiographers were performing an exposure when the guide tube disconnect failed and the guide tube disconnected from the camera. This prevents the source from being fully retracted into the camera. The division manager, trained in source retrieval, was able to get the source into the camera and into its shielded position. No overexposures occurred. The quick disconnect was replaced and tested and the camera was returned to service. The camera was a SPEC-150 using a 62 Ci Ir-192 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-06-06
51962 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2016-03-28 13:20 | 2016-05-27 09:22 | 2016-05-27 | INVALID SPECIFIED SYSTEM ACTUATION "This 60-day report, as allowed by 10 CFR 50.73(a)(1), is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of containment isolation valves in more than one system. "On 3/28/16, at approximately 1320 [EDT], a loss of power occurred on the Unit 2 E124 480 volt load center due to an equipment operator inadvertently opening the main feed breaker during the process of applying a clearance to de-energize the E124-P-A motor control center for planned maintenance. Loss of the E124 load center resulted in Group II and Group III primary containment isolations due to an invalid ESF actuation signal. Systems impacted by the containment isolations included containment instrument nitrogen, containment atmospheric monitoring, reactor water cleanup, and secondary containment. "Balance of plant impacts included partial loss of feedwater heating and a reduced condenser vacuum. Reactor power lowered to 86% as a result of the event and further decreased to approximately 80 percent when re-establishing the 3A, 4A and 5A feedwater heaters. "Following direction from the control room, the E124 main feed breaker was promptly re-closed by equipment operators. Affected equipment was restored to its normal or planned configuration and containment isolations were reset at 1406. "The containment isolation signal was generated as a result of the loss of power to the E124 load center and was not due to actual plant conditions or parameters meeting design criteria for containment isolation. Therefore, this is considered to be an invalid actuation." The licensee has notified the NRC Resident Inspector. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-05-27
51961 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2016-05-17 | 2016-05-26 16:35 | 2016-07-29 | MISSISSIPPI AGREEMENT STATE REPORT - STUCK SHUTTER ON LEVEL GAUGE The following information was obtained from the state of Mississippi via email: "Licensee reported a stuck shutter on an Ohmart/VEGA Model SH-F1 level gauge, during semi-annual checks of shutter operation. The failure was identified on 05/17/2016 by the licensee and was immediately reported to RSO. The RSO supposes stuck shutter failure was caused by age and oxidation. Licensee has contacted the manufacturer, Ohmart, for repair of shutter mechanism. Gauge remains in its normal operating position. "Isotope(s): Cs-137 Activity: 10 mCi Source Serial No. 0441GK Source Model No. A-2102" Mississippi Report Number: MS-16003 * * * UPDATE AT 1655 EDT ON 07/29/16 FROM H. BENJAMIN CULPEPPER TO S. SANDIN VIA EMAIL * * * "The stuck shutter has been closed and equipment involved removed and placed into a secure storage facility, on site, by an Ohmart Vega representative. There are no plans to put the unit back into service." Mississippi closed this case as of July 29, 2016. Notified R4DO (Pick) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2016-06-03
51960 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-05-25 11:18 | 2016-05-25 19:26 | 2016-05-25 | AGREEMENT STATE REPORT - RADIOGRAPHY TRUCK ACCIDENT The following information was received from the State of Oklahoma by email: "Approximately [1300 CDT] today, [Oklahoma was] notified by Advanced Inspection Technologies [AIT] (OK-27588-02) that a radiography truck belonging to them had been involved in a collision with a tractor/trailer truck at [1118 CDT] today at mile marker 178 on I-44 near Stroud, OK. The driver of the radiography truck was killed and the truck partially burned. At the time it was carrying a 30 Ci Ir-192 source and a 25 Ci Ir-192 source. The truck was taken to the Oklahoma Highway Patrol facility in Stroud where [Oklahoma personnel] arrived at about [1400 CDT]. The darkroom, where the cameras were stored (QSA Model 880s), was partially burned but had not been opened. Initial surveys of the exterior indicated the cameras, which were normally secured near the darkroom door, had been thrown forward and come to rest just behind the cab. Shortly after [Oklahoma personnel] arrived, the AIT RSO arrived and the darkroom door was forced open. The cameras were recovered and surveys indicated the shielding was intact. Wipe tests of each were also collected. One camera was damaged but the sources were secure inside each [camera]. The cameras have been returned to the AIT facility in Sand Springs, OK and will be returned to QSA for repair or disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-06-02
51959 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-25 14:15 | 2016-05-25 17:10 | 2016-05-25 | DISCOVERY OF NON-CONFORMING CONDITIONS DURING TORNADO HAZARDS ANALYSIS "On May 25, 2016, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Braidwood Station identified non-conforming conditions in the plant design such that specific TS equipment on both units is considered to not be adequately protected from tornado missiles. Each of the following reportable conditions is postulated by tornado missiles entering openings through the wall that separates the Auxiliary Building and the Turbine Building: "The following items could be impacted by tornado missiles entering the 0A and 0B [common] MCR [main control room] turbine building intake openings: Main control room pressurization, main control room ductwork and dampers, chilled water to the VC [control room ventilation] coils, main control room radiation monitors. "The following items could be impacted by tornado missiles entering the Division 11 and 21 MEER [miscellaneous electrical equipment rooms] rooms: Exhaust from the MEER (affects room cooling and MCR pressure), exhaust from a battery room, conduits and cabinets associated with the battery chargers and DC bus. "The following items could be impacted by tornado missiles entering the Division 12 and 22 MEER rooms: Exhaust from the MEER (affects room cooling and MCR pressure), MEER supply fan and ductwork, battery room exhaust, and the instrument inverter cabinets. "The Auxiliary Feed Diesel exterior exhaust stacks (which extend from the roofline) could be impacted by tornado missiles. While we have analyses on these impacts, they do not use a NRC accepted methodology to evaluate the impact and effects. "The RWST [refueling water storage tank] roof access opening Bilco hatch is fabricated from sheet metal that is not designed to prevent all postulated tornado missiles from entering the tank. The tank pressure boundary is 24" thick concrete and is designed to withstand an external tornado missile impact. Thus a missile that enters the tank will not adversely impact the tank pressure boundary. The following items could be impacted by tornado missiles entering the RWST roof access: The 6" RWST recirculation pipe, 3" overflow pipe, and 24" suction pipe. This piping is located inside the tank and they are approximately 130 degrees around the tank away from the hatch opening. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "These conditions are being addressed in accordance with EGM 15-002 and DSS-ISG-2016-01 [enforcement discretion and interim guidance documents]. The licensee has notified the NRC Resident Inspector." . :ú. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-05-25
51958 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-25 13:00 | 2016-05-25 16:00 | 2016-05-25 | DISCOVERY OF NON-CONFORMING CONDITIONS DURING TORNADO HAZARDS ANALYSIS "On May 25, 2016, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Byron Station identified non-conforming conditions in the plant design such that specific TS equipment on both units is considered to not be adequately protected from tornado missiles. Each of the following reportable conditions is postulated by tornado missiles entering openings through the wall that separates the Auxiliary Building and the Turbine Building: "The following items could be impacted by tornado missiles entering the 0A and 0B [common] MCR [main control room] turbine building intake openings: Main control room pressurization, main control room ductwork and dampers, chilled water to the VC [control room ventilation] coils, main control room radiation monitors. "The following items could be impacted by tornado missiles entering the Division 11 and 21 MEER [miscellaneous electrical equipment rooms] rooms: Exhaust from the MEER (affects room cooling and MCR pressure), exhaust from a battery room, conduits and cabinets associated with the battery chargers and DC bus. "The following items could be impacted by tornado missiles entering the Division 12 and 22 MEER rooms: Exhaust from the MEER (affects room cooling and MCR pressure), MEER supply fan and ductwork, battery room exhaust, and the instrument inverter cabinets. "The RWST [refueling water storage tank] roof access opening Bilco hatch is fabricated from sheet metal that is not designed to prevent all postulated tornado missiles from entering the tank. The tank pressure boundary is 24" thick concrete and is designed to withstand an external tornado missile impact. Thus a missile that enters the tank will not adversely impact the tank pressure boundary. The following items could be impacted by tornado missiles entering the RWST roof access: The 6" RWST recirculation pipe, 3" overflow pipe, and 24" suction pipe. This piping is located inside the tank and they are approximately 130 degrees around the tank away from the hatch opening. "This condition creates a potential LOSF [loss of safety function] with the Byron Essential Service Water Cooling Towers (UHS) [ultimate heat sink] with the discovery that the power and control cables to four of eight cooling tower fans can be damaged by tornado missiles penetrating through wall openings. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "These conditions are being addressed in accordance with EGM 15-002 and DSS-ISG-2016-01 [enforcement discretion and interim guidance documents]. The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-05-25
51957 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2012-04-20 | 2016-05-25 15:55 | 2016-05-25 | AGREEMENT STATE REPORT - PORTABLE GAUGES DAMAGED BY FIRE The following information was received from the Commonwealth of Virginia by email: "Event description: On May 23, 2016 a Virginia Radioactive Material Program (VRMP) inspector performed a routine unannounced inspection of Superior Paving Corporation. The inspector discovered that on April 20, 2012, two Troxler Model 4640-B Portable Gauges (serial numbers 1384 and 845) containing 8 mCi of Cs-137 each, were damaged by fire. The fire burnt the storage box which contained the two gauges. The transport containers and plastics on the gauges were melted. However, according to the Radiation Safety Officer statement, the integrities of the sources were intact. On May 10, 2012 the two gauges were transported by the licensee to North East Technical Services (NETS) for disposal. "A transfer record was available for review. The licensee will provide the agency (VRMP) a detailed report for review. There was no public health exposure or environmental release from this event." Virginia Event Report: VA-16-005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-06-02
51956 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-25 02:06 | 2016-05-25 04:54 | 2016-05-25 | AUTOMATIC REACTOR TRIP ON LOWERING STEAM GENERATOR WATER LEVEL "At 0206 EDT 5/25/16, Vogtle Unit 2 tripped from 100% when SG [Steam Generator] #1 Level began to lower for an unknown reason. Cause for level issue is under investigation. All control rods fully inserted and AFW [Auxiliary Feedwater] and FWI [Feedwater Isolation] actuated as expected. "Unit 2 is in Mode 3 and stable with decay heat being removed by Aux Feedwater." Prior to the trip, I & C [Instrumentation & Calibration] was performing a loop #1 narrow range instrument calibration. Unit 2 is in a normal post trip electrical lineup with all source of offsite power available. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-05-25
51955 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-24 10:22 | 2016-05-24 17:48 | 2016-06-02 | UNPLANNED LOSS OF EMERGENCY ASSESSMENT CAPABILITY "CPNPP [Comanche Peak Nuclear Power Plant] experienced an unplanned loss of the seismic monitoring instrument on May 24, 2016 at 1022 [CDT]. The unplanned loss of the seismic monitor resulted in a loss of assessment capability for the HA1.1 (seismic event greater than operating basis earthquake) Alert emergency classification. The seismic monitor was restored to service on May 24, 2016 at 1043. "This loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. * * * UPDATE ON 6/2/16 AT 1630 EDT FROM ANTHONY PATE TO DONG PARK * * * "On May 24, 2016 at 1748 [EDT], Comanche Peak reported an unplanned loss of emergency assessment capability per 10 CFR 50.72(b)(3)(xiii) [EN# 51955]. Specifically, Comanche Peak reported an unplanned loss of the seismic monitoring instrument. The unplanned loss of the seismic monitor would have resulted in a loss of assessment capability for the HA 1.1 (seismic event greater than operating basis earthquake) Alert emergency classification. The seismic monitor was restored to service on May 24, 2016 at 1043 [CDT]. "The engineering review determined that the alarms displayed on the seismic monitoring screen provides Operations awareness of the system status. Signals were still being received from the sensor and if there was an OBE [Operating Basis Earthquake] during the time the alarms were in, it would have displayed on the monitoring screen and on the Main Control Board by providing an OBE Exceedance alarm, maintaining emergency assessment capability. Therefore, Comanche Peak requests that the May 24, 2016, 10 CFR 50.72(b)(3)(xiii) reportable event for Units 1 & 2 be retracted." The licensee will notify the NRC Resident Inspector. Notified R4DO (Deese). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-05-24
51954 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2016-05-24 12:50 | 2016-05-24 15:28 | 2016-05-24 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY NOT RELATED TO WORK "At approximately 1250 [EDT], a contract employee was found unresponsive in [their] personal vehicle located in the parking lot outside of the owner controlled area. The Fairfield County Coroner arrived on-site and declared the individual deceased at 1345. The fatality was due to an apparent personal medical issue and not work related." The licensee has notified the NRC Resident Inspector. The licensee has notified State of South Carolina Department of Labor - OSHA. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-05-24
51953 | 0 | DBI, INC. |  |  |  |  | 2016-05-23 13:15 | 2016-05-24 14:57 | 2016-05-24 | RADIOGRAPHY CAMERA SOURCE CABLE NOT ENGAGED TO SOURCE "On May 23, 2016 DBI Inc. (Lic# 15-29301-02) had an Industrial radiography crew working outside of Elmer, MO (Approx. 3hrs from Overland Park, KS Office). At approximately 1315 [CDT] during the crews first source retraction it was determined that the source had become disconnected from the driver cable. The crew immediately recognized the situation though the use of their dosimetry equipment. The Corporate Radiation Safety Officer [RSO], was immediately notified of the issue. [The RSO] informed the crew to establish the emergency barricades and to not attempt anything further with the exposure device. [The RSO] arrived at the job site at approximately [1620] to retrieve the source. The source was secured back into the exposure device by [1645]. "Dosimeter readings were taken immediately upon discovery of the disconnect and monitored throughout the end of the day. Total recorded dose for the individuals involved was as follows: [Worker 1] 18mR [Worker 2] 12mR [RSO] 3mR "Doses recorded fall within the normal expectations for the work that was performed. "Listed below are the relevant materials & equipment involved: QSA Global 880 Delta exposure device. (S/N D6707) QSA Global model A424-9 lr-192 Source (S/N 27422G) 33 Curies QSA Global extreme weather 35' cranks (S/N KC-009) QSA Global extreme weather 7' source tube with a 4hvl collimator (S/N KC-009)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | KS | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-05-24
51952 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2016-03-28 01:50 | 2016-05-24 10:12 | 2016-05-24 | INVALID ACTUATION OF INBOARD ISOLATION LOGIC "On Monday, March 28, 2016, Unit 1 was in OPCON 5 (Refueling) conducting a refueling outage. A modification was being installed for an NSSSS [Nuclear Steam Supply Shutoff System] Test Box on Division 1A Group 1 NSSSS logic. At 0150 hours, a logic jumper was removed as directed by the work order and a logic fuse failed. The fuse failure caused an unplanned invalid actuation of the inboard isolation logic. The isolations were reset and the valves were restored to initial conditions at 0246 hours. On Sunday, April 3, 2016, at 0134 hours, one additional logic fuse opening event occurred during the testing which also caused an invalid actuation which was reset at 0405 hours. The fuse openings occurred during jumper manipulations as the modification was tested on the Division 1A and 1D logic during the refuel outage. The investigation determined the fuse openings were due to the testing process. The suspected devices that caused the condition are not permanent plant equipment and there is no degradation of the actual circuit. They were part of a temporary configuration that was installed to support modification installation and acceptance testing. The temporary devices have been removed. "The portion of the primary containment isolation system that received an actuation signal functioned successfully. All of the affected open isolation valves automatically closed. The isolation was a partial actuation. "This 60-day ENS report is being made per 10CFR 50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to report invalid automatic actuations of systems listed in paragraph (a)(2)(iv)(B). The listed system that actuated was general containment isolation signals affecting containment isolation valves in more than one system. Primary containment isolation valves (PCIVs) closed on reactor water cleanup (RWCU), drywell chilled water (DWCW), primary containment instrument gas (PCIG), drywell sumps and the suppression pool cleanup systems." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-05-24
51951 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2016-05-18 | 2016-05-24 09:11 | 2016-05-24 | AGREEMENT STATE REPORT - FAILED SHUTTER DEVICE The following report was excerpted from an email from the Commonwealth of Kentucky, Department for Public Health, Radiation Health Branch: On May 18, 2016, a fixed gauge was discovered to have a failed shutter device at the licensee's site at West Centertown, Kentucky. There was a failure of on/off mechanisms on one fixed gauge to function as designed. Failure discovered during routine testing of on/off mechanism by licensee. The licensee has contacted a service provider to schedule removal/repair. The licensee notified the Kentucky Department for Public Health on May 24, 2016. The fixed gauge is in a remote area of the plant and no overexposures of personnel have occurred. Kentucky Event Report ID: KY160005. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2016-06-01
51950 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2016-05-23 10:09 | 2016-05-23 17:02 | 2016-05-23 | PLANT HATCH UNIT 2 CONTAINMENT ISOLATION VALVE ACTUATION "On May 23, 2016, at 1009 EDT, while personnel were performing turbine testing with Unit 2 offline for planned maintenance, an event resulted in the actuation of containment isolation valves in more than one system. In response to this unexpected signal, 2B21F016 (Steam Line Drain Line Inboard Isolation Valve), 2B21F019 (Steam Line Drain Line Outboard Isolation Valve), and 2B31F019 (Reactor Water Sample Inboard Isolation Valve) went closed, all of which are primary containment isolation valves actuated by Group 1 Isolation. The Group 1 Isolation signal initiated based on low condenser vacuum during the turbine testing procedure, a valid condition that was expected to have been bypassed in the logic during the performance of this procedure. Human performance is believed to be the cause of these systems having actuated in a way that was not part of the planned evolution. Although the Unit was shut down when this signal was received, and primary containment isolation was not required to mitigate the consequences of an event, this Isolation signal has been determined to have been valid due to the initiation in response to actual plant conditions or parameters which satisfy the requirements for initiation of the system. "The event is reportable as required by 10 CFR 50.72(b)(3)(iv)(A)(2): (A) Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. (2) General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam Isolation valves (MSIVs). "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-05-23
51949 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2016-05-23 11:16 | 2016-05-23 15:36 | 2016-05-23 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED EMPLOYEE SUPERVISOR "A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.719 |  |  |  | 0 | 2016-05-23
51948 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-05-20 15:31 | 2016-05-20 18:40 | 2016-05-20 | OFFSITE NOTIFICATION DUE TO INADVERTENT SOUNDING OF THE EMERGENCY NOTIFICATION SIRENS "At approximately 1531 [EDT] hours, a tornado signal was inadvertently activated from Hancock County, West Virginia which sounded 118 out of 120 Emergency sirens. The remaining 2 sirens do not receive a tornado signal. The sirens alarmed for approximately 3 minutes. A silent test was subsequently performed for all 120 sirens and validated the emergency siren system remains functional. "In accordance with 10 CFR 50.72(b)(2)(xi), News Release or Notification of Other Government Agency, a 4 hour notification is required. "The [NRC] Senior Resident Inspector has been notified. No press releases are planned." The licensee notified state and local agencies. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-05-20
51947 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2016-05-20 | 2016-05-20 16:17 | 2016-08-03 | FIXED NUCLEAR GAUGE READINGS HIGHER THAN EXPECTED The following information was received via E-mail: "While performing routine shutter tests of fixed gauges, the licensee noted higher than expected readings from a fixed gauge when the shutter was closed. The expected reading was 2 millirem per hour and the readings during the shutter check were found to be 6 millirem per hour. The licensee has contacted the manufacturer and a field engineer is expected on Monday, May 23, 2016. "The gauge is identified as an Ohmart SR-2, Serial Number M-2688, containing 4500 milliCuries of Cesium-137. "The State of Arkansas is awaiting a written report from the licensee with a report of the findings of the field engineer." Arkansas Event Number: AR-2016-002 * * * UPDATE FROM STEVE MACK TO DANIEL MILLS AT 1217 EDT ON 08/03/2016 * * * The following was received via email: "A field service engineer was on site on June 20, 2016. Using multiple survey meters, including the licensee's meter, the higher radiation readings could not be duplicated. The field service engineer surveyed other gauges of the same type and found the radiation readings with the expected range of readings. The cause of the abnormal readings on the day of the shutter checks is unknown. The Department [Arkansas Department of Health] has asked the licensee to make notification if abnormal readings are detected in the future and the Department will follow up during future inspections. The Department considers this event to be closed." Notified R4DO (Haire) and NMSS (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2016-05-30
51946 | 0 | UNITED STATES AIR FORCE |  |  |  |  | 2016-05-18 08:30 | 2016-05-20 15:25 | 2016-05-20 | LOST AM-241 SOURCE "A B-52 bomber crashed shortly after take-off at Andersen AF base in Guam at 0830 local time (2230 GMT, Wednesday, 18 May 2016). The B-52 had a Sniper Pod which contained 12 microcuries of Am-241. So far the safety team could not locate the Sniper Pod at the incident spot. "The value for Am-241 listed in Appendix C to [10 CFR] Part 20 is 0.001 microcuries. Each Sniper Pod carries 12 microcuries of Am-241. Hence, we [USAF] reported the incident to the NRC Operations Center in accordance with 10 CFR 20.2201. We will provide you [NRC with a written] incident report within 30 days." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | GU | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-05-30
51945 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-05-19 | 2016-05-19 22:08 | 2016-05-19 | AGREEMENT STATE REPORT - NUCLEAR GAUGE STUCK SHUTTER The following information was received via E-mail: "Event Type: 30.50(b)(2), Events in which equipment is disabled or fails to function as designed. "Event Narrative: On May 19, 2016 the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that while performing routine shutter checks, the shutter on an Ohmart model SHLM-BR4 could not be closed. The gauge contains a 5.0 curie cesium-137 source. Open is the normal operating position of the gauge. The source does not create any additional risk of exposure to the workers or members of the general public. The RSO stated they will call their service company to repair the gauge. The RSO stated the gauge is scheduled to be replaced during their next outage this fall. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9405. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-05-27
51944 | 0 | NUCLEAR LOGISTICS INC |  |  |  |  | 2016-05-18 | 2016-05-19 19:17 | 2016-06-21 | PART 21 - INTERIM EVALUATION OF A DEVIATION - CONTACTOR FAILURE The following was received via FAX: On May 18, 2016, Nuclear Logistics INC. (NLI) determined that a contactor failure that occurred at the Shearon Harris plant had failed due to an auxiliary contact chatter present on the seal-in circuit for the coil voltage. The auxiliary contact chatter was caused by the loss of the shading coils. NLI will be submitting a full report on the issue to the NRC within 60 days. The contactor that failed was a Size 4 Eaton Freedom Series with a special coil for degraded voltage condition. Reference Number: P21-05192016 NLI reported that the following plants have these types of contactor's: Region 2: Oconee, Turkey Point, Shearon Harris and North Anna Region 4: Columbia and Waterford * * * UPDATE AT 1832 EDT ON 06/20/16 FROM TRACY BOLT TO DANIEL MILLS * * * The following is excerpted from the licensee submission: "The specific part which fails to comply or contains a defect: The Contactor that failed in service is a Size 4 Eaton Freedom Series with an AZZ/NLI special coil for meeting specific degraded voltage conditions. "Extent of condition: Size 3, 4 and size 5 Eaton Freedom Series contactors or starters with an NLI special degraded voltage coil that have been supplied by AZZ/NLI since December 2010. "NLI procured the commercial grade contactors and installed the special coil that was required to achieve the specific degraded voltage condition. The units were qualified, dedicated and supplied for safety related applications. The contactors were commercially procured from Eaton, the Original Equipment Manufacturer (OEM). "For contactors/starters utilized in continuous duty applications. the OEM shading coils on the contactor core ... have the potential to become loose and fall off. If the shading coils are not in the intended location on the core, there is the potential for excessive chatter to occur on the normally open auxiliary contacts that are closed when the contactor is energized. "The safety function of the contactor is to reliably supply uninterrupted power (no contact chatter) to a load on demand. For special degraded voltage applications, the NLI supplied contactor is equipped with an NLI special coil that replaces the OEM coil. "When the contactor/starters that have the special coil installed are utilized in a continuous duty operation (continuously energized greater than 60 minutes) the special coil reaches a higher temperature than the original manufacturer's coil. The increased heat is potentially causing degradation of the acrylic resin that is utilized by the manufacturer to hold the OEM shading coils onto the OEM core. After the acrylic resin is no longer providing a secure hold on the shading coils, the shading coils can then become loose from the iron core. "Name and address of the individual or individuals informing the Commission. "Tracy Bolt, Director of Quality Assurance "Nuclear Logistics, Inc. "7410 Pebble Drive "Ft. Worth, TX 76118" AZZ/NLI Part 21 Report No: P21-05192016, Rev. 0 Plants potentially impacted include Oconee, Shearon Harris, Columbia, Turkey Point, North Anna, and Waterford. Notified R4DO (Rollins), R2DO (Musser) and Part 21/50.55 Reactors group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2016-05-19
51943 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2016-05-19 | 2016-05-19 19:10 | 2016-05-19 | AGREEMENT STATE REPORT - MEDICAL EVENTS - MISADMINISTRATION The following was reported to the NRC via phone notification and email: "As a result of a routine health and safety inspection, Taylor Regional Hospital has reported 13 medical events which occurred [from] 2006 [to] 2011. These medical events are the result of permanent prostate brachytherapy where post implant dosimetry for each of the 13 patients revealed the total dose delivered to the target organ differed from the prescribed dose by 50 REM and 20% or more. The Kentucky Cabinet for Health and Family Services is continuing to communicate with the licensee to ascertain all relevant information related to these events. "Event report ID No: KY160004" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2016-05-27
51942 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-05-18 | 2016-05-19 14:47 | 2016-05-24 | AGREEMENT STATE NOTIFICATION - TRANSPORTED PACKAGE EXCEEDS LIMITS The following was received via FAX: "The licensee notified the Department [Pennsylvania Bureau of Radiation Protection] by telephone on May 18, 2016, of an event that required reporting based on 10 CFR 20.1906(d)(2). "Event Description: On May 18, 2016, a PETNET courier mistakenly picked up a white [shielded container] from a PA licensee which he assumed was empty because it was near other PET cases he was returning to the PETNET North Wales Pharmacy. As he was loading the cases into his trunk, the lid of the white [shielded container] opened and two rods fell out on the ground. He did not realize they were radioactive material. He placed them in his trunk using his hands, leaving the rods unshielded, and proceeded to return to the pharmacy. He placed the [shielded container] and 2 rods on top of the empty cases in PETNET's loading area. The PETNET Radiation Safety Officer (RSO) found the rods and surveyed them, noting the dose rate > [greater than] 200 mRem/hour on the surface. She immediately placed the sources in a shielded [container], and began her investigation. Survey/wipes were taken of the rods, the courier vehicle, the area in which the rods were discovered, and the courier's hands. No removable contamination was found. Dose modeling by the RSO determined there was enough interposed shielding with the large number of other [shielded containers] in his vehicle to reduce his exposure to below regulatory limits. Rods are going to be properly packaged and shipped back to the PA licensee. "Cause of the Event: Human Error. "Actions: A reactive inspection is planned by the Department [PA Bureau of Radiation Protection]. More information will be provided upon receipt. "Media Attention: None at this time. "Event Report ID No: PA160015" * * * UPDATE FROM JOSEPH MELNIC TO VINCE KLCO ON 5/24/16 AT 1217 EDT * * * The following information was received from the State of Pennsylvania via facsimile: "EVENT DESCRIPTION: On May 18, 2016, a PETNET courier mistakenly picked up a white pig from a PA licensee which he assumed was empty because it was near other PET cases he was returning to the PETNET North Wales Pharmacy. As he was loading the cases into his trunk, the lid of the white pig opened and two rods fell out on the ground. He did not realize they were radioactive material. The rods were two Ge/Ga-68 calibration sources containing 2.16 mCi each. He placed them in his trunk using his hands, leaving the rods unshielded, and proceeded to return to the pharmacy. He placed the pig and 2 rods on top of the empty cases in PETNET's loading area. The PETNET Radiation Safety Officer found the rods and surveyed them, noting the dose rate >200 mr/hr on the surface, 1.4 mR/hr at one meter. She immediately placed the sources in a shielded pig, and began her investigation. Surveys/wipes were taken of the rods, the courier vehicle, the area in which rods were discovered and the courier's hands. results of the wipes were 0 dpm, all surveys were background. No removable contamination was found. A survey by the RSO has shown no overexposure to the courier's hands as a result of picking up the rods and the RSO determined there was enough interposed shielding with the large number of other pigs in his vehicle to reduce his exposure to belowú regulatory limits. The rods are going to be properly packaged and shipped back to the PA licensee. The courier's whole body badge was sent for analysis. No finger extremity badge was worn. "ACTIONS: A reactive inspection has been performed by the Department [State of Pennsylvania]. Dose modeling of the courier's hands will be requested to determine dose to the hands More information will be provided upon receipt." Notified R1DO (Lilliendahl) and NMSS Events via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-05-27
51941 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2016-05-17 12:49 | 2016-05-18 08:13 | 2016-05-18 | FITNESS-FOR-DUTY CONFIRMED POSITIVE A contract supervisor had a confirmed positive for illegal drugs during a for-cause fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Construction Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2016-05-18
51940 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-17 16:30 | 2016-05-17 23:06 | 2016-05-17 | SPECIFIED SYSTEM ACTUATION - LOSS OF 1 B-B ELECTRICAL BUSS "On May 17, 2016, at 1630 hours while restoring from a plant modification related to new 'loss of phase' circuitry, the 1 B-B 6.9kV buss de-energized resulting in a loss of voltage on the buss. The loss of voltage was caused by the loss of voltage relays that separated offsite power from the 1 B-B 6.9kV buss. At the time, the 1 B-B emergency diesel generator was removed from service for planned maintenance. "In response to the loss of power on the 1 B-B 6.9kV buss, the operators entered abnormal operating instruction, AOI 43.02, Loss of Unit 1 Train B Shutdown Boards, and started emergency diesel generators 1 A-A, 2 A-A, and 2 B-B. All equipment operated properly. The emergency diesel generators were not required to be paralleled to the boards. "Offsite power was restored to the 1 B-B 6.9kV buss at 1802 hours on May 17, 2016. This condition did not result in any adverse impact on the health and safety of the public. This event is reportable under 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.'" The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-05-17
51939 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-05-17 09:45 | 2016-05-17 18:43 | 2016-05-17 | REACTOR COOLANT LEAKAGE WITH THE REACTOR IN COLD SHUTDOWN "On May 17, 2016 with the plant in Mode 4 [Cold Shutdown] during a refueling outage, personnel entered the drywell to perform a walkdown. At 0945 CDT, water was identified leaking from flexible hoses located at the inner elbow of MSL [Main Steam Line] B and MSL C. It was concluded that the leakage was from an elbow tap welded to the flexible hoses associated with flow instrumentation on MSL C and MSL B. Due to the refueling outage, the plant subsequently entered Mode 5 at 0955 and is currently in Mode 5 [Refueling] and 0 percent rated thermal power. The degraded component on MSL B was previously replaced in 2008 and on MSL C in 2007. The station has determined that this event is reportable under the provisions of 10 CFR 50.72 (b)(3)(ii)(A) as an event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, as an 8-hour notification. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-05-17
51938 | 0 | NUTHERM INTERNATIONAL, INC |  |  |  |  | 2016-05-17 | 2016-05-17 15:51 | 2016-05-17 | PART 21 REPORT - DEFECT IN A SIGNAL CONVERTER TRANSFORMER The following report was received from the manufacturer via fax: Nutherm International, Inc. reported on a defect found in "Moore Industries SCT Signal Converter (Part Number SCT/4-20MA/10-50MA/117VAC/UB) based upon the failure analysis of a failed component. The conclusion was that the wire insulation in T2 transformer was damaged by the transformer manufacturing facility during assembly. This damage reduced the insulation resistance and dielectric breakdown between the windings of the transformer. These damaged transformers were subsequently installed by Moore Industries into the signal converters. The failure of the transformer resulted in early, catastrophic failure of the signal converter. "Moore Industries tested the transformers remaining in stock and found one (1) of the remaining two-hundred nineteen (219) transformers exhibited this condition. In all documented cases involving failure of this transformer, the impacted units had passed pre-installation functional testing but failed within four months after installation." Affected nuclear power stations include: Peach Bottom Atomic Power Station and the Sequoyah Nuclear Station. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-05-17
51937 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-05-13 | 2016-05-17 11:54 | 2016-05-17 | AGREEMENT STATE - LOST BRACHYTHERAPY SOURCE The following was reported verbally and via email from the Illinois Bureau of Radiation Safety: "On Friday, May 13, 2016, the licensee's radiation safety officer (RSO) contacted the Agency [Illinois Bureau of Radiation Safety] to advise that one source from a Medi+Physics sealed source brachytherapy device [44 mCi, Cs-137, Model Number CDCT1, Serial Number GA301] was missing following the treatment of a patient. During the unloading of the applicator that afternoon, only 2 of the 3 sources were recovered. Surveys were immediately conducted of the patient, the patient's room, the trash, bed and linen that remained present as well as several potential paths to and from the hot lab where the sources are stored. The facility expanded its surveys to additionally include dumpsters, roll off containers of biohazard waste and soiled linen storage without retrieving the source. Interviews with attending nursing staff showed that the patient had been cooperative throughout the 3 day treatment, did not have any visitors and had no complications where she had been found out of bed or otherwise unattended. Agency representatives were sent to the facility the following Monday to conduct confirmatory measurements of the same areas and equipment and expanded the search again to other outlying areas of the facility with no unexpected elevated readings detected in any area. Waste processing facilities were contacted and advised of the potential of a missing radioactive source in their waste stream beginning on the previous Wednesday. All indicated that they had functioning portal detection units for incoming trash/waste and that no anomalous readings had been noted. "The Agency is continuing its investigation at this time and conducting additional surveys at out lying waste facilities. Hospital staff have been made aware of the event and been given a description of the source and appropriate action to take should it be discovered. This item remains open at this time." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-05-25
51936 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2016-05-16 | 2016-05-16 22:39 | 2016-05-16 | PART 21 NOTIFICATION - FOR PRINTED CIRCUIT BOARDS The following was received by email: "Required information as per 10CFR Part 21.21(d)(4) follows: "(i) Name and Address of the individual or individuals informing the Commission "Luis Sanchez, Vice President United Controls International 205 Scientific Drive NORCROSS, GA 30092 "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. "Thomas & Betts Power Solutions/Cyberex Printed Circuit Boards (Gate Drive Assemblies P/Ns: 41-01-229677 & 41-01-229678, Reference Oscillator Module P/N: 41-01-808901) & Mersen (formerly Ferraz Shawmut) Fuses P/N: A30QS400-4 items were installed in PSEG [Public Service Enterprise Group] inverter unit and resulted in opening of P/N: A30QS400-4 fuses. When the original equipment was installed this issue was not present. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. "United Controls International 205 Scientific Drive Norcross, GA 30092 "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "Opening of the subject fuses prevents operation of the host inverter unit. "(v) The date on which the information of such defect or failure to comply was obtained. "March 17,2016 "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured or being manufactured for one or more facilities or activities subject to the regulations in this Part. "The following is a compilation of UCI supplied items with like part numbers as the subject components. Only the printed circuit boards identified by the end-user [supplied under purchase orders 4500576271 (Qty. 1), 4500728702 (Qty. 1), and 4500625591 (Qty. 1)] along with the subject fuses supplied under purchase orders 4500810474 (Qty. 10) and 4500772093 (Qty. 6) are considered to possibly be affected by the end-user's reported issue. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "UCI is not capable of performing additional evaluation of the subject printed circuit boards because UCI does not have the capability to simulate the in-service condition of these items. UCI suggests that the end-user perform additional evaluations with the subject printed circuit boards installed in their training inverter unit. UCI has requested that the end-user supply additional fuses supplied under purchase orders 4500810474 and 4500772093 for evaluation of current carrying performance since the fuses already provided were open. "(viii) Any Advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "None "(ix) In the case of an early site permit, the entities to whom an early site permit was transferred. "Not Applicable." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-05-16
51935 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-16 21:05 | 2016-05-16 21:17 | 2016-05-16 | UNANALYZED CONDITION THAT SIGNIFICANTLY DEGRADES PLANT SAFETY "On May 16, 2016 at 2105, Sequoyah Nuclear Power Plant identified a nonconforming condition involving the Emergency Diesel Generator (EDG) fire dampers installed in Units 1 and 2. Specifically, it has been identified that if a tornado causes a differential pressure across the east and west sides of the EDG Building, this could create a high airflow rate through the EDG Building ventilation path. The fire dampers for each EDG bay (required to isolate the space for CO2 fire suppression per SQN Fire Protection Report) have not been analyzed to withstand high air flows resulting from a tornado and could possibly fail in a way that impedes airflow for EDG cooling. This is an unanalyzed condition that could prevent all EDGs from supplying electrical power as designed during a tornado or other similar weather events. "All 4 EDGs are required to be operable by both units' Technical Specifications to provide electrical power to safe shutdown/safety related equipment following accident conditions coincident with a loss of offsite power. The Current Licensing Basis (CLB) requires that tornado effects be considered in the design of safety related SSCs [Systems, Structures, and Components], and it cannot be demonstrated at this time that the described SSCs will withstand the design basis tornado. It has been determined that the CLB may not adequately address possible design basis tornado scenarios. "The EDGs are located inside the power plant structure and are currently capable of performing their safety function. The occurrence of such an event is highly unlikely and there is no imminent concern regarding severe weather involving tornadoes. Compensatory measures have been developed to address the associated nonconformance. "The condition described above is being reported as an unanalyzed condition that significantly degrades plant safety per 10 CFR 50.72(b)(3)(ii)(B)." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-05-16
51934 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-05-16 14:57 | 2016-05-16 19:56 | 2016-05-16 | ACCIDENT MITIGATION - HPCI DECLARED INOPERABLE "At 1457 [CDT] on 5-16-16, U-2 [Unit 2] High Pressure Coolant Injection (HPCI) system was declared inoperable after isolation of the system due to a steam leak on the HPCI steam inlet drain pot drain line. "The event is reportable per 10CFR50.72(b)(3)(v)(D), Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences an accident. This is an eight hour report requirement. "The Dresden NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-05-16
51933 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-05-16 | 2016-05-16 17:12 | 2016-05-16 | AGREEMENT STATE REPORT - SHUTTER FAILED TO OPERATE The following information was received via E-mail "On May 16, 2016 the Agency [Texas Department of State Health Service] was notified by the licensee's radiation safety officer that the facility was unable to isolate a gauge for maintenance when the shutter failed to operate. The gauge is an Ohmart Vega model SHF2 containing a 200 millicurie cesium - 137 source, serial number 7548GK. The shutter was left in the normal operating, unshielded position. The source does not pose any additional risk of exposure to the workers or members of the general public. The RSO stated they have called TechStar to repair the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-05-24
51932 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2016-05-16 03:00 | 2016-05-16 02:02 | 2016-05-26 | SEISMIC MONITORING SYSTEM OUT OF SERVICE FOR PLANNED UPGRADE "At 0300 EDT on May 16, 2016, Seabrook Station's seismic monitoring instrumentation will be removed from service for a planned upgrade to the Seismic Monitoring Control Panel and its accelerometers. Modifications are expected to be complete on May 27, 2016. Proceduralized compensatory measures are in place and have been communicated to applicable emergency response decision makers. This preplanned action is being reported in accordance with 10 CFR 50.72(b)(xiii)." The NRC Resident Inspector has been notified. * * * UPDATE ON 5/26/16 AT 2049 EDT FROM MIKE TAYLOR TO HOWIE CROUCH * * * At 2045 EDT on 5/26/16, the seismic monitoring system was returned to service. The licensee notified the NRC Resident Inspector. Notified R1DO (Lilliendahl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-05-16
51931 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-15 11:18 | 2016-05-15 12:34 | 2016-05-15 | UNUSUAL EVENT DECLARED DUE TO EXCESSIVE UNIDENTIFIED LEAKAGE DURING PLANT STARTUP "Unit 2 experienced RCS Leakage, potentially pressure boundary leakage, or Unidentified Leakage greater than 10 gpm for [greater than] 15 minutes. Reactor Vessel Flange Temperature High Leakoff alarm was received. This met threshold for declaration of an Unusual Event at 1118 CDT per MU6. Unit 2 is currently in MODE 3. Investigation is in progress to identify specific leakage location." The plant is stable, leakage indicates about 32 gpm and the startup has been stopped. There is no impact on Unit 1. The licensee notified the NRC Resident Inspector and State authorities. Notified DHS SWO, FEMA Ops Center, DHS NICC,. Notified FEMA National Watch and Nuclear SSA via email. * * * UPDATE FROM RICARDO ROSAS TO VINCE KLCO ON 5/15/16 AT 1626 EDT * * * "At 1459 CDT, the conditions under MU6 are no longer met. The site has terminated the Unusual Event. In addition, a press release will be made of this event." Unit 2 is stable and in Mode 3 pending further evaluation. The leak stopped when a loop drain isolation valve was closed. The licensee notified the NRC Resident Inspector and State and local authorities. Notified the R3DO (Duncan), NRR EO (Morris), IRD MOC (Grant), DHS SWO, FEMA Ops Center, and DHS NICC. Notified the FEMA National Watch and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2016-05-15
51930 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-05-13 | 2016-05-15 09:24 | 2016-05-24 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was received via E-mail: "On May 14, 2016, the Agency [Texas Department of State Health Services] was informed by the licensee's radiation safety officer (RSO) that a radiography crew had experienced a source disconnect at a temporary field site on May 13, 2016. The RSO stated the crew was working on a pipeline and after 3-4 welds were completed the source could not be retracted into the Spec 150 camera containing a 90.4 Curie iridium-192 source. The RSO, who was authorized to perform source retrieval, responded. He determined that the source cable had parted right next to the ball connector and that the source would not slide out of the source tube since the frayed cable was catching on the inside of the tube. He cut the source tube in order to recover the source. The RSO received 1300 mRem on his pocket dosimeter and is sending in his film badge for emergency processing. No member of the general public received an exposure due to this event. The licensee is conducting an investigation into the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9403 * * * UPDATE FROM ART TUCKER TO VINCE KLCO ON 5/24/16 AT 1643 EDT * * * The following information was received from the State of Texas by email: "On May 24, 2016, the licensee's radiation safety officer (RSO) contacted the Agency and reported they just received the results of his badge worn during the source recovery. The RSO stated his badge was reading 1,348 millirem. The RSO stated he had previously received 100 millirem while performing radiography work prior to retrieving the source. Therefore, the dose received from retrieving the source was 1,248 millirem. Additional information will be provided as it is received in accordance with SA 300." Notified the R4DO (Werner) and NMSS Events via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-05-23
51929 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2016-05-15 06:38 | 2016-05-15 07:08 | 2016-05-15 | UNUSUAL EVENT DUE TO MAIN GENERATOR HYDROGEN LEAK IN TURBINE BUILDING At 0638 EDT on 5/15/2016, an Unusual Event (EAL GU.2) was declared on Millstone Unit 3 due to a Main Generator hydrogen gas leak into the Turbine Building. At 0645 EDT, operators manually tripped the reactor. All rods inserted. All systems functioned as expected following the reactor trip. Operators are currently venting the remaining hydrogen from the generator through the normal vent path. There is no safety related equipment out-of-service. The plant is in a normal post-trip electrical line-up. All Emergency Diesel Generators are available. The licensee notified the State of Connecticut and the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, and DHS NICC Watch Officer. Notified via E-mail FEMA National Watch Center and NuclearSSA. * * * UPDATE FROM MIKE CICCONE TO HOWIE CROUCH AT 1044 EDT ON 5/15/16 * * * At 0949 EDT, the licensee terminated the Unusual Event. "At 0645 EDT on 5/15/16, a manual reactor trip was initiated at Millstone Unit 3 due to a hydrogen leak from the main generator. As expected, Auxiliary Feedwater System (AFW) initiated on the reactor trip. The trip was uncomplicated and the plant is currently in Mode 3 with a normal electric lineup and decay heat is being removed via steam dumps to the condenser. The cause of the hydrogen leakage is under investigation. This is reportable under 10 CFR 50.72(b)(2)(iv)(B) - RPS actuation while critical, and 10 CFR 50.72 (b)(3)(iv)(A) - valid specified system actuation." The licensee has notified Waterford Township, the State of Connecticut and the NRC Resident Inspector. Notified R1DO (Burritt), NRR ET (McDermott), NRR EO (Morris), IRD (Grant), DHS SWO, FEMA Ops Center, DHS NICC, FEMA National Watch Center (email) and NuclearSSA (email). | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  | IMode3: Power Operation; FMode3: Hot Standby | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  | 0 | 2016-05-15
51928 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-05-13 12:00 | 2016-05-13 20:02 | 2016-05-17 | EXISTING DESIGN INADEQUACY COULD PREVENT STANDBY GAS TREATMENT SYSTEM OPERABLITY "At 1200 [CDT] May 13, 2016, while the plant was operating at 100% power, it was brought to the attention of the River Bend Station Main Control Room staff that an existing design inadequacy could prevent both trains of the Standby Gas Treatment System (GTS) from performing its design function. Under certain specific conditions, the installed Masterpact breakers may not close to allow energization of the filter train exhaust fans. A start signal (reactor level 2, drywell pressure 1.68 psid, annulus high radiation, annulus low flow) combined with a trip signal within a certain time differential, could result in a failure of the breakers to close. As a result of this condition, both Standby Gas Trains were declared inoperable, which required entry into LCO 3.6.4.3 Condition C (requires entering Mode 3 in 12 hours). Declaring both trains of Standby Gas Treatment System inoperable resulted in loss of the safety function since a system that has been declared inoperable is one in which the capability has degraded to the point where it cannot perform with reasonable expectation or reliability. "The Standby Gas Treatment System (GTS) limits release to the environment of radioisotopes, which may leak from the primary containment, ECCS systems, and other potential radioactive sources to the secondary containment under accident conditions. "At 1240 [CDT] May 13, 2016, one division of GTS, GTS 'A', was manually started from the Main Control Room. This action prevents the breaker failure mode, restored the operability of one train and restored the safety function of the GTS system. LCO 3.6.4.3 Condition A (restore Operability in 7 days) is currently entered for Standby Gas Train 'B'. During the 40 minutes of inoperability, both trains of Standby Gas remained available. At no time was the health or safety of the public impacted. "This condition is being reported in accordance with 10CFR50.72(b)(3)(v)(C) as an event that could have caused a loss of safety function to control the release of radioactive material. The Senior NRC Resident was notified." * * * UPDATED AT 1341 EDT ON 05/17/16 FROM DAN PIPKIN TO RICHARD SMITH * * * "Further review has determined that the design inadequacy discussed in EN #51928 could adversely effect the ability of the main control building heating, ventilation, and air conditioning (HVAC) system to perform its design safety function, based upon a particular sequence of events occurring within a short window of time (approximately 75 milliseconds). River Bend has implemented compensatory actions to ensure operability of the main control building HVAC system." The Resident Inspector has been notified by the licensee. Notified the R4DO (Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-05-13
51927 | 0 | CURTISS-WRIGHT NUCLEAR DIVISION |  |  |  |  | 2016-05-11 | 2016-05-13 14:35 | 2016-05-13 | PART 21 NOTIFICATION - POTENTIAL DEFECT APPLICABLE TO HYTORK XL1126 PNEUMATIC ACTUATORS The following information was provided by Curtiss-Wright Nuclear Division via fax: "On March 16, 2016, Curtiss-Wright was notified by one of our commercial suppliers that they had received an Important Product Safety Notice (safety notice) from Emerson Valve Automation/Hytork concerning Hytork models XL1371 and XL1126 pneumatic rack and pinion actuators, manufactured after 2005 and before June 2015. Curtiss-Wright began evaluating any possible impact at that time. On May 11, 2016 Curtiss-Wright made the decision that the defect was reportable under 10 CFR Part 21. A total of four (4) Hytork XL1126 pneumatic actuators had been dedicated by Curtiss-Wright and provided as safety-related. Two (2) of the actuators were supplied to the PSEG, Salem Generating Station and the other two (2) were supplied to MOX Services. Both Salem Generating Station and MOX Services have been notified of this potential defect. Curtiss-Wright has not supplied any of the XL 1371 actuators. "Emerson Valve Automation/Hytork states that there is a small possibility that a crack may develop in the actuator body under normal operation. The Emerson/Hytork investigation determined that a combination of actuator body structural design and material specifications along with manufacturer processes, could lead to material properties that are not within stated specifications. This condition may cause higher than allowable stresses to occur in the actuator body, which could lead to crack initiation. If a crack does develop and the actuator continues to operate, the crack may propagate to the end of the body and the end caps could be forcefully ejected. In addition to operational concerns, this condition may present a personnel safety hazard. "Based on phone conversations with Hytork it was learned that only one model XL1126 actuator failure has been reported out of approximately 10,000 supplied. Hytork stated that the failed actuator was in a 'severe' (mechanical, operational) application with very high cycle frequency and likely experienced high impact loading. "The list below identifies the affected customers, approximate ship dates, applicable purchase orders and actuator details. PSEG/Salem, approximate date of shipment November, 2011, Customer PO Number 4500606542, Affected Equipment One Hytork EIA-XL1126-S80AH0 Actuator Damper Tag 1CAA14 MOX, approximate date of shipment June, 2014, Customer PO Number 10888-P-6374, Affected Equipment Two Hytork XL1126SR80 Actuators Catalog ID 14306 (HDE*AOD 0142B) & Catalog ID 14309 (HDE*AOD 0197B) PSEG/Salem, approximate date of shipment September 2015, Customer PO Number 4500826720, Affected Equipment One Hytork EIA-XL1126-S80-A00 Actuator Damper Tag 2CAA14 "Hytork ceased production of the XL1126 and XL1371 actuators in June 2015 due to the described problem. Hytork is revising the design to connect the defect and will issue new model numbers for the re-designed actuators. "Hytork expects to begin production of the new models in June of this year. Although Curtiss-Wright has successfully seismically tested two Hytork model XL1126 actuators under load, providing reasonable assurance that the actuators will survive and operate under normal and seismic loading, it is still recommended that the actuators be replaced as soon as practical. In the interim it is recommended that operating plants perform periodic (recommend weekly or if infrequently operated, following each operation) visual and/or soap-bubble inspections. The recommended actions provided below are considered to provide adequate indication of onset of this potential condition since instantaneous failures have not been identified and are not projected. a) For all persons who are or could be in the area where the affected equipment is present, ensure they are warned of the potential danger. b) Visually inspect all affected models for cracks, especially underneath the dual stroke adjustment pad and on top of the actuator body in the pinion area. c) If you are unsure whether a crack is present, perform a soap bubble test. d) If you identify a crack or leak, immediately remove this actuator from service. "For additional information please contact the following personnel. "Steve Willard, Engineering: 256-924-7463 (office); swillard@curtisswright.com (e-mail) Tony Gill, QA Manager: 256-924-7438 (office); 256-426-4558 (cell); tgill@curtisswright.com (e-mail)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-05-17
51926 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-05-12 14:00 | 2016-05-13 10:22 | 2016-05-13 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED The following information was obtained from the State of New Jersey via fax: "[The New Jersey Department of Environmental Protection was informed that in Galloway Township, New Jersey], a Troxler [gauge] Model 3440, S/N 17337, was run over by the company pickup truck. This gauge contained 9 mCi of Cs-137 and 44 mCi of Am-241/Be. The gauge was not in its transport container, so the outer housing of the gauge was badly cracked and fell off." The licensee reported no release of licensed material or contamination and no overexposure. State Event Report ID No.: NJ #16-05-12-1410-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-05-23
51925 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2016-05-13 01:10 | 2016-05-13 05:00 | 2016-05-13 | MANUAL REACTOR SCRAM DUE AFTER LOSS OF AN ESSENTIAL MOTOR CONTROL CENTER "At approximately 0110 hours [EDT] on May 13, 2016, Susquehanna Steam Electric Station Unit Two reactor was manually scrammed by plant operators due to a sustained loss of AC power to essential plant loads. Power to MCC 2B246 was lost at 2355 on May 12, 2016, resulting in a loss of Drywell cooling. Drywell pressure increased to 1.3 psig when operators placed the mode switch to the shutdown position to manually SCRAM the reactor. All rods inserted as expected. Reactor water level lowered to -27 inches and was immediately restored by normal feedwater level control. Level 3 (+13 inch) PCIS isolations occurred, along with an initiation of the RCIC system (-30 inches). Once adequate level was verified, RCIC was overridden. Pressure was controlled with turbine bypass valves, and subsequently main steam line drains. All safety systems functioned as expected. "The power loss also tripped Reactor Building HVAC, causing a loss of secondary containment differential pressure resulting in a loss of safety function. "Due to the loss of drywell cooling, high drywell pressure actuations and a second reactor SCRAM signal, this signal was automatic, occurred at 0314 hours. HPCI [which automatically initiated on high drywell pressure] was subsequently overridden and declared inoperable, resulting in a loss of safety function. [HPCI did not inject into the vessel]. "The reactor is currently stable in Mode 3. Initial reports from the field indicate a phase to phase fault on the MCC 2B246 bus bars." The licensee has notified the NRC Resident Inspector and will be issuing a press release. | 0 | 0 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | POT UNCNTRL RAD REL | ECCS INJECTION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(2)(iv)(A) |  | 0 | 2016-05-13
51924 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-05-12 16:47 | 2016-05-12 20:01 | 2016-05-12 | DETERIORATION OF SPENT FUEL POOL RACK NEUTRON ABSORBING MATERIAL "On May 12, 2016, at 16:47 EDT with the reactor at 100% power and the mode switch in RUN, an assessment of the Spent Fuel Pool racks containing neutron absorbing material concluded that some degradation had occurred. The result is that we cannot assure we are maintaining Keff < 0.95 as required per design. Conservative measures have been implemented to ensure public health and safety. "Recent planned testing conducted in the spent fuel pool determined that one rack panel had degradation of the neutron absorbing material in excess of what had been analyzed. An extent of condition review indicated additional potential at-risk locations may exist. Analyses are being performed to determine the potential impact and mitigating actions. Fuel pool conditions are safe and stable. Conservative measures have been implemented and spent fuel safety is maintained. "Based on the above, the condition is reportable to the NRC as an Unanalyzed Condition under 10 CFR 50.72(b)(3)(ii), and requires an 8 hour notification. The condition is also reportable in accordance with 10 CFR 50.73 (a)(2)(ii). "The licensee has notified the NRC Senior Resident Inspector. "The licensee will notify the Commonwealth of Massachusetts." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-05-12
51923 | 0 | AZZ - NUCLEAR LOGISTICS, INC. |  |  |  |  | 2016-05-10 | 2016-05-12 19:23 | 2016-09-22 | PART 21 - INITIAL NOTIFICATION OF MASTERPACT BREAKER FAIL TO CLOSE The following information was a licensee received facsimile; "Pursuant to 10CFR 21.21(d)(3)(ii), AZZ/NLI is providing written notification of the identification of a potential defect or failure to comply. "On the basis of our evaluation, it has been determined that there is sufficient information to determine if the subject condition is left uncorrected could potentially create a Substantial Safety Hazard or could create a Technical Specification Safety Limit violation as it relates to the subject plant applications. The plants will need to evaluate their application to determine if the identified condition could have an impact to the plant operation. "The following information is required per 10CFR 21.21(d)(4): "(i) Name and address of the individual or individuals informing the Commission. Tracy Bolt, Director of Quality Assurance Nuclear Logistics, Inc. 7410 Pebble Drive Ft. Worth, TX 76118 "(ii) Identification of the facility, activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. "Masterpact NT and NW style circuit breakers. -The failure of the breaker being ready to electrically close after being subjected to an 'Anti-Pump condition'. Note: The specific application where the failures have occurred is when the breaker is being utilized as a starter for closing into an inductive load like a fan motor. "(iii) Identification of the firm constructing or supplying the basic component which fails to comply or contains a defect. AZZ/ Nuclear Logistics Fort Worth, Texas 76118 "(iv) Nature of defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "Possible 'failure to close' condition of Masterpact breakers NT and NW style, that are being used with specific logic schemes that are subjected to 'anti-pump' conditions during normal operation. These breakers have a higher susceptibility to not return to the ready to close position after the close signal has been removed. "PSEG reported approximately 14 instances with different breakers in different cubicles where they initiated an electric close order, and the breakers failed to close. All of the 14 instances were in applications of being used to start an inductive load. "NLI inspected three of the breakers (all NWs) that were returned by PSEG and could not fully replicate the problem as described by the plant. NLI was only able to repeat the failure to close when performing an 'anti-pump' test. The failure to close was intermittent, but could be duplicated. When the anti-pump condition was not present, NLI could not duplicate a failure to close. Visual inspections of the tested breakers did not reveal any visible damage to the breaker linkages, latches, shunt close or shunt trip assemblies. "Schneider Electric (SE) performed testing of three Masterpact NW08 breakers (operated to beyond design life) and duplicated the fail to close condition as described by the plant. It was determined that a standing close signal with a trip/open signal applied is determined to be the root cause of the fail to close issue. The SE testing confirms that the presence of this condition can cause the breaker anti-pump latch to receive excessive forward pressure. When the nose of the latch impacts the close coil plunger, it will 'rock' up in the rear, catching on the top of the mechanism plate. Once the close voltage is removed, and the plunger retracts, the latch may or may not let go. If the latch does not release, then application of the close coil voltage will simply activate the close coil plunger and without the latch underneath the plunger, the breaker will not close. "PSEG performed extensive troubleshooting at the Hope Creek plant and discovered that all of the affected breakers were in an anti-pump condition when the breakers failed to close. "(v) The date on which the information of such defect or failure to comply was obtained. "This revised notification is being submitted based on the information gathered on 5/10/2016 after additional testing, at the request of River Bend, was performed. This additional testing was requested following the notification that was provided to the plants listed below, in the original issue of this letter in February 2016. "The evaluation of the condition was originally completed in September of 2012. The issue was originally determined at that time to not be a reportable condition based on the breaker not containing a defect and the condition was believed to be attributed to the specific logic scheme at the plant. To date, this issue has only been reported to NLI from the following plants, PSEG Hope Creek and River Bend Station. No other plants have reported this specific fail to close condition. NLI was in direct communication with the plants when this issue was first being evaluated and the failure analysis were being conducted. The two affected plants were knowledgeable of the condition. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for being supplied for, or may be supplied for, manufactured or being manufactured for one or more facilities or activities subject to the regulations In this part. "Plants which have been supplied the Masterpact circuit breakers. "PSEG Hope Creek - Issue Identified for NW style River Bend - Issue identified for NT style Callaway - This issue has not been identified however, the potential should be evaluated. St. Lucie - This issue has not been identified however. the potential should be evaluated. Turkey Point - This issue has not been identified however, the potential should be evaluated. Beaver Valley - This issue has not been identified however, the potential should be evaluated. Davis Besse - This issue has not been identified however, the potential should be evaluated. Three Mile Island - This issue has not been identified however, the potential should be evaluated. Calvert Cliffs - This issue has not been identified however, the potential should be evaluated. Hatch -This issue has not been identified however, the potential should be evaluated. STP - This issue has not been identified however, the potential should be evaluated. SONGS - This issue has not been identified however, the potential should be evaluated. KHNP Ulchin - This issue has not been identified however, the potential should be evaluated. KHNP Kori - This issue has not been identified however, the potential should be evaluated. Duke Oconee - This issue has not been identified however, the potential should be evaluated. Duke McGuire - Non-safety (not supplied by NU), This issue has not been identified. "(vii) The corrective action which bas been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "NLI originally created a technical bulletin to address the issue and recommendations. However, since new information has been recently identified, NLI TB-12-007 will be revised, as the proposed solution will not reliably solve the problem for all postulated events. Upon completion of the revised technical bulletin, it will be re-submitted to the plants which have been supplied the Masterpact breakers from NLI. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "NLI is currently working with the OEM of the circuit breaker to determine the permanent solution to correct the possible failure to close event after the breaker is subjected to an Anti-Pump condition. "Advice for plants with breakers currently installed: Evaluate the applications where the breakers may be potentially subjected to an Anti-Pump condition; where the close coil will be energized for an extended period of time. "The circuit breaker will continue to operate if this condition is present however there may need to be human interaction with the circuit breaker by manually pressing the trip/open button on the front of the circuit breaker to free the mechanism. "Please contact NLI with any questions or comments. Sincerely, Tracy Bolt Director of Quality Assurance" * * * UPDATE ON 5/13/16 AT 1153 EDT FROM TRACY BOLT TO BETHANY CECERE * * * "Added 4 additional plants that were inadvertently left off the list. "Browns Ferry - This issue has not been identified however, the potential should be evaluated. Fort Calhoun - This issue has not been identified however, the potential should be evaluated. Wolf Creek - This issue has not been identified however, the potential should be evaluated. Seabrook - This issue has not been identified however, the potential should be evaluated." Notified R1DO (Burritt), R2DO (Heisserer), R3DO (Duncan), R4DO (Campbell), and Part 21 Group via email. * * * UPDATE AT 1612 EDT ON 7/13/16 FROM TRACY BOLT TO JEFF HERRERA * * * The following information was received via facsimile: Additional information in attachment has been updated since the original report provided on 5/13/2016. Additional facility identified as impacted: St. Lucie - Issue identified For additional information contact: Tracy Bolt Director of Quality Assurance AZZ/NLI Nuclear Logistics 7410 Pebble Drive Fort Worth, Texas 76118 Notified the R1DO (Ferdas), R2DO (Rich), R3DO (Kunowski), R4DO (Gaddy) and Part 21 Reactor group (via email). * * * UPDATE AT 1907 EDT ON 9/22/16 FROM TRACY BOLT TO JEFF HERRERA * * * "On the basis of our evaluation, it has been determined that there is sufficient information to determine if the subject condition is left uncorrected could potentially create a Substantial Safety Hazard or could create a Technical Specification Safety Limit violation as it relates to the subject plant applications. The plants will need to evaluate their application to determine if the identified condition could have an impact to the plant operation. "Plants which have been supplied the Masterpact circuit breakers: "PSEG Hope Creek - Issue Identified for NW style River Bend - Issue identified for NT style Callaway - This issue has not been identified however, the potential should be evaluated. St. Lucie - This issue has been identified. Turkey Point - This issue has not been identified however, the potential should be evaluated. Beaver Valley - This issue has not been identified however, the potential should be evaluated. Davis Besse - This issue has not been identified however, the potential should be evaluated. Three Mile Island - This issue has not been identified however, the potential should be evaluated. Calvert Cliffs - This issue has not been identified however, the potential should be evaluated. Hatch - This issue has not been identified however, the potential should be evaluated. STP - This issue has not been identified however, the potential should be evaluated. SONGS - This issue has not been identified however, the potential should be evaluated. KHNP Ulchin - This issue has not been identified however, the potential should be evaluated. KHNP Kori - This issue has not been identified however, the potential should be evaluated. Duke Oconee - This issue has not been identified however, the potential should be evaluated. Duke McGuire - Non-safety (not supplied by NLI). This issue has not been identified. Browns Ferry - This issue has not been identified however, the potential should be evaluated. Fort Calhoun - This issue has not been identified however, the potential should be evaluated. Wolf Creek This issue has not been identified however, the potential should be evaluated. Seabrook This issue has not been identified however, the potential should be evaluated. "NLI originally created a technical bulletin to address the issue and recommendations. However, since new information has been recently identified, NLI TB-12-007 has been revised. The solution for this potential problem is to replace the XF (shunt close assembly) with the XFCOM shunt close assembly. "The part numbers are: 847323 (100-130VAC/DC) 847324 (200-240VAC/DC) Additional details regarding the replacement device are contained in the NLI technical bulletin TB-12-007." Notified the R1DO (Krohn), R2DO (Blamey), R3DO (Jeffers), R4DO (Deese) and Part 21 Reactor group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-05-12
51922 | 0 | PALISADES | 1 |  |  | [1] CE | 2016-05-12 07:55 | 2016-05-12 13:35 | 2016-05-12 | FITNESS-FOR-DUTY POLICY VIOLATION "A non-licensed contractor supervisor violated the fitness-for-duty policy [for alcohol] during a random fitness-for-duty test. The contractor's access to the plant has been terminated. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2016-05-12
51921 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-05-11 | 2016-05-11 18:48 | 2016-05-13 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO RAD WORKER The following information was received via E-mail: "On May 11, 2016, the licensee called the Agency [Texas Department of State Health Services] to report a potential overexposure. The licensee's radiation safety officer (RSO) had only initial information at the time of the report. He reported one of the licensee's radiographers had taped the guide tube (with collimator attached) to a jig in order to perform an exposure. During the exposure, the guide tube fell. The radiographer failed to retract the source before he walked to the end of the guide tube, picked it up, and taped it back on the jig. The RSO is investigating to get the details of the event. The radiographer's dosimetry badge has been sent for immediate processing. The radiographer was using a QSA 880D device with a 34.8 Curie iridium-192 source. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9402 * * * UPDATE FROM KAREN BLANCHARD TO VINCE KLCO AT 5/13/16 AT 1700 EDT * * * The following information was received from the State of Texas by email: "UPDATE: Licensee completed a re-enactment of the situation using video tape and empty camera with attachments. The re-enactment demonstrated that the person placed his left hand on the collimator and included inserting his middle finger into the port hole on the collimator. The RSO completed dose calculations of 467 Rem to the finger. The badge results displayed 307 mRem whole body dose. The badge was worn for approximately eight days for this month. The finger appears to show slight redness, otherwise no visible effects at present time (3 days after event). Blood work was drawn and the person is scheduled for another doctor visit on Monday. The Agency has not received the detailed calculations and has not concurred with this dose estimate. Another update will be provided as information is acquired." Notified the R4DO (Campbell). Notified NMSS Events, Angela McIntosh and Patricia Milligan via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-05-19
51920 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-04-14 | 2016-05-11 17:37 | 2016-05-11 | AGREEMENT STATE REPORT - THEFT AND RECOVERY OF A PORTABLE GAUGE The following information was received by email: "On 4/13/16 CPN Model MC Series gauge was left in marked licensee vehicle parked outside technician's home in Columbus at end of work day, reportedly properly secured in vehicle with two independent locking devices. Gauge contains 10 mCi Cs-137 and 50 mCi Am-241:Be sources. "Technician found gauge missing when came out to go to work on 4/14/16. Technician claims RSO was notified, RSO does not recall. No police report was filed and no report was made to ODH [Ohio Department of Health] at that time. "On 5/10/16, gauge was found in vacant lot during separate police investigation. Police called fire department HAZMAT unit. Transport case was not locked, but gauge rod was locked. Licensee was identified by paperwork in the transport case. Licensee was contacted by fire department to retrieve gauge. Licensee RSO took possession of gauge and returned it to office in Columbus. "On 5/11/16 licensee reported theft and recovery of gauge to ODH. ODH investigators visited site to determine cause of incident and reasons for lack of notifications." Ohio Item Number: OH160003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-05-19
51919 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-12-02 | 2016-05-11 19:11 | 2016-05-11 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION EVENT The following information was received via E-mail: "On May 11, 2016, the licensee's radiation safety officer reported an unplanned contamination event which occurred on December 2, 2015. The RSO stated he did not think this was a reportable event until his medical physicist instructed him to report the incident. During treatment of a patient, a radioactive capsule of I-131 was provided to a patient. The patient had problems swallowing the capsule. The patient eventually chewed the capsule and in the minutes following had an episode, expelling the capsule and other bodily fluids. The bodily fluid was collected in a bag, although some of the fluid dripped onto the floor. The droplets which fell on the floor were collected and placed in a collection bag. The floor was cleaned and the bag containing all the waste items was taken to nuclear medicine for decay prior to disposal. The area was covered with an adsorbent pad. Readings on the surface were 38 mR/hr and 1.8 mR/hr at one meter. A mobile lead wall/shield was put in place to restrict the area. Radiation caution signs were also placed in the area with a do not enter sign on the door leading to the room. The room remained restricted for more than 24 hours. On February 25, 2016 the area was released at background readings. As of March 25, 2016 the waste bag remains in storage awaiting disposal. "The Agency [Texas Department of State Health Services] has withheld the name of the licensee in accordance with Texas state law." Texas Incident #: I-9401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-05-19
51918 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-05-11 06:53 | 2016-05-11 10:56 | 2016-05-11 | FARLEY UNIT 2 TRIP ON HI HI STEAM GENERATOR LEVEL "At 0653 [CDT] on 5/11/16, Farley Unit 2 reactor was manually tripped from 29 [percent] power. The initiating event was hi-hi Steam Generator level. Steam Generator levels began to rise following the start of a second condensate pump. The hi-hi steam generator level setpoint was reached causing the only running main feedwater pump to trip, a main feedwater isolation, and an automatic turbine trip. Auxiliary feedwater automatically started as expected. The reactor was manually tripped per procedure. All other systems responded properly for the event and there were no complications. "The plant is currently stable in Mode 3. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 29 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-05-11
51917 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2016-05-10 11:38 | 2016-05-10 19:38 | 2016-06-15 | CONTAINMENT COOLING WATER SYSTEM INOPERABLE DUE TO UNANALYZED CONDITION "During scheduled maintenance, at 1138 CDT, the Fort Calhoun Station Shift Manager was notified via phone call and condition report of an unanalyzed condition which was the result of the maintenance on Shutdown Cooling Heat Exchanger valves. This condition could have led to the inability of the Component Cooling Water (CCW) system to perform its design function of providing a cooling medium for the Containment atmosphere under Loss of Coolant Accident (LOCA) conditions. This was identified by OPPD [Omaha Public Power District] staff engaged in Design Basis Reconstitution. "As part of the maintenance, HCV-484, Shutdown Cooling Heat Exchanger AC-4A CCW Outlet Valve, and HCV-481, Shutdown Cooling Heat Exchanger AC-4B CCW Inlet Valve, were opened. Under these conditions, with the assumed single failure loss of DC control power and accident conditions of a LOCA, CCW would be allowed to flow through both shutdown cooling heat exchangers, effectively bypassing flow to the Containment Cooling Units. These conditions are not assumed under plant design basis calculations, and therefore placed the plant in an unanalyzed condition. "Following clearance removal at 1535 CDT, both HCV-484 and HCV-481 were returned to service and the condition described above no longer exists." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 6/15/16 AT 1836 EDT FROM JOHN BLALOCK TO DONG PARK * * * "Discovered 6/15/2016 at 1330 CDT: During the extent of condition review for the above ENS notification, it was discovered that the unanalyzed condition that occurred on 5/10/2016 also occurred five other times during the past 3 years. Details for these additional occurrences will be included in the 60-day Licensee Event Report associated with the original 5/10/2016 ENS notification." The licensee has notified the NRC Resident Inspector. Notified R4DO (Taylor). | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-05-10
51916 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-05-09 | 2016-05-10 17:03 | 2016-06-10 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE STUCK SHUTTER The following information was received via E-mail: "On May 10, 2016, the Agency [Texas Depart of State Health Services] received notification from the licensee's radiation safety officer (RSO) that the shutter on a Thermo Fisher Scientific Model 5176-SN B2578 density gauge, containing a 500 millicurie cesium-137 source SN MA3200, was found open during inventory/operational checks. It appears the weld had failed on the gauge. Open is the normal operating position of the gauge shutter. The gauge does not create an exposure hazard to the licensee's employees or a member of the general public. The licensee has contacted the service company who will inspect the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9399 * * * RETRACTION FROM CHRIS MOORE TO RICHARD SMITH ON JUNE 10, 2016 AT 1541 EDT * * * The following was received from the State of Texas via email: "I-9399, EN51916 is retracted. The manufacturer inspected the gauge and shutter. All components were fully operational. The transmitter in the density detector failed, giving an erroneous reading on the meter. The licensee incorrectly assumed it was due to a broken shutter." Notified R4DO(Kramer) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-05-18
51915 | 0 | ELECTROSWITCH |  |  |  |  | 2016-05-10 | 2016-05-10 15:59 | 2016-10-21 | PART 21 REPORTING OF DEFECTS AND NONCOMPLIANCE The following is a synopsis of information received via fax: "Various Electroswitch products - Series 24 Instrument & Control (Part #24XX, 24XXX, 243XX, 74XXX), Series 24 LOR (part #78XX), Series 24 LOR/ER (part #78XX), Series 24 CSR (part #88XX), Series 24 LSR (part #92XX), Series 31 Instrument & Control (part #31XXX, 65XXX, 75XXX), Series 31 TR/LSR (part #93XX), Series 20 Cam (part #20KB, 20KD, 20LB, 20LD, 20MB, 20MD, 20MF, 20MG, 20PF, 20PG, 20PH, 20PJ, 20PL, 20PY), Series 20 Module (part #10XXX, 17XXX, 18XXX, 19XXX, 29XXX, 30XXX, 32XXX,38XXX,40XXX, 60XXX, 61XXX, 62XXX, 63XXX) [have a potential deviation (departure from the technical requirements included in the procure document)] "It was determined on May 10, 2016 that Electroswitch does not have the capability to perform the evaluation to determine if a defect, which could create a substantial safety hazard, exists. "Any Electroswitch product that has a part number listed above and was sold as a Safety-Related Class 1E product [may contain the deviation]. The two nonconformance issues are: "Initial Product Qualification Tests for Dielectric Withstanding Voltage, Insulation Resistance and Contact Resistance as defined in Electroswitch's ESC-STD-1000 Rev. 3 dated 9/3/1984 General Specifications for Rotary Switches and Auxiliary Relays for Utility Applications including Class 1E Equipment for Nuclear Power Generating Stations was found to be in contradiction to IEEE C37.90-1978 Relays and Relay Systems Associated with Electric Power Apparatus. "Electroswitch did not procure materials, parts, equipment and/or services from an Appendix B supplier nor were applicable Commercial Grade Surveys, Source Inspections and Material Analyses performed for the following materials: Precious metal blade overlay material Red metal blade material Precious metal overlay thickness of switch blade material Molding compound of switch insulators (terminal decks and barriers) Carbon steel for securing rods Solenoids Relays Services (test labs) pertaining to product qualification Electroswitch is attempting to determine which NRC licensees are potentially affected. "The following personnel may be contacted regarding this notification: Larry Friedman Quality Assurance Manager 781-607-3309 Ed Reszenski Engineering Manager 781-607-3341" * * * UPDATE FROM LARRY FRIEDMAN TO DONALD NORWOOD AT 1656 EDT ON 5/11/2016 * * * The following information was received via fax: Below is the list of utilities (and plants where specified) which were notified of Electroswitch's decision to end the Appendix B Quality Assurance Program: Ameren Energy Dominion Energy Duke Energy Energy Northwest Entergy Nuclear (Waterford 3 Nuclear) Entergy Nuclear (Pilgrim Power Plant) Entergy Nuclear (Indian Point Energy) Xcel Energy (Monticello Nuclear) MPR Associates for FPL Nebraska Public Power (Cooper Nuclear) Nextera (Point Beach Nuclear) Xcel Energy (Prairie Island Gen) Southern Power (Hatch) Southern Power (Vogtle) TVA TVA (Watts Bar Nuclear) Wolf Creek Nuclear Notified R1DO (Burritt), R2DO (Heisserer), R3DO (Duncan) and R4DO (Campbell) and via E-mail Part 21/50.55 Reactors Group. * * * UPDATE FROM LARRY FRIEDMAN TO DONG HWA PARK AT 1617 EDT ON 8/25/2016 * * * The following information was received via fax: "Electroswitch is formally requesting a thirty (30) day extension to complete the evaluation by Sept. 24, 2016 in order to provide detailed answers to the questions and provide any needed updates to the Part 21 notification report." Notified R1DO (Dimitriadis), R2DO (Michel), R3DO (Cameron) and R4DO (Kellar) and Part 21/50.55 Reactors Group via E-mail. * * * UPDATE FROM LARRY FRIEDMAN TO JOHN SHOEMAKER AT 1349 EDT ON 10/21/2016 * * * The following information was received via fax: "Subject: Response to questions about Electroswitch's response to the U.S. Nuclear Regulatory Commission Inspection Report NO. 99900833/2016-201 and Notice of Nonconformance (Letter from Terry W. Jackson, Branch Chief dated August 5, 2016." Notified R1DO (Cahill), R2DO (Masters), R3DO (Orth) and R4DO (Kramer) and Part 21/50.55 Reactors Group via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-05-10
51914 | 0 | ACUREN INSPECTION |  |  |  |  | 2016-05-07 11:22 | 2016-05-10 11:18 | 2016-05-10 | SUSPICIOUS ACTIVITY RELATED TO TRANSPORT OF CATEGORY 2 RADIOACTIVE MATERIAL Suspicious activity related to the transport of category 2 quantities of radioactive material. The licensee informed the LLEA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SUSPICIOUS ACT INVOLV CAT 1/2 RAD MATL | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 37.57(b) |  |  |  | 1 | 2016-05-10
51913 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-05-07 23:50 | 2016-05-09 17:34 | 2016-05-09 | OFFSITE NOTIFICATION - REPORTING THAT SITE WAS NOTIFIED OF SIREN SOUNDING "At approximately 1430 CDT on 5/9/2016, the Dresden Station Main Control Room was notified by Exelon Corporate Emergency Preparedness of the inadvertent actuation of all 27 Full Sounding Sirens in Will County, Illinois. Exelon Emergency Preparedness was notified at 1309 CDT on 5/9/2016. The inadvertent actuation occurred on 5/7/16 at 2350 CDT during a training activity performed by Wescom (Western Will County Communications Center). "This event is reportable per 10 CFR 50.72(b)(2)(xi), News Release or Notification of Other Government Agencies. This is a 4-hour reporting requirement. "The Dresden NRC Resident has been notified." |  | 100 | 100 |  | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-05-09
51912 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-07 23:50 | 2016-05-09 17:18 | 2016-05-09 | OFFSITE NOTIFICATION - REPORTING THAT SITE WAS NOTIFIED OF SIREN SOUNDING "At approximately 1420 CDT on 5/9/2016, the Braidwood Station Main Control Room was notified by Exelon Corporate Emergency Preparedness of the inadvertent actuation of all 27 Full Sounding Sirens in Will County, Illinois. Exelon Emergency Preparedness was notified at 1309 CDT on 5/9/2016. The inadvertent actuation occurred on 5/7/16 at 2350 CDT during a training activity performed by Wescom (Western Will County Communications Center). "This event is reportable per 10 CFR 50.72(b)(2)(xi), News Release or Notification of Other Government Agencies. This is a 4-hour reporting requirement. "The Braidwood NRC Resident has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-05-09
51911 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2016-05-06 09:15 | 2016-05-06 10:24 | 2016-07-05 | ALABAMA AGREEMENT STATE REPORT - LOST GENERALLY LICENSED PROCESS GAUGE The following information was obtained from the State of Alabama via facsimile: "On May 5, 2016, it was determined that Millennium Resources, LLC, Graysville, Alabama had lost control and possession of a generally licensed device (Ronan SA1-C5 #2255GO containing 5 mCi of Cs-137). "During a requested visit by the new owner Cane Creek, LLC on April 7, 2016, it was determined that they possessed a new generally licensed device. The new owners only knew that the site once contained a similar plant which contained a device with radioactive material. The old plant was constructed in 1997, and our [Alabama Department of Public Health - Office of Radiation Control] records show that device being received by Millennium Resources, LLC on November 14, 1997. The plant was torn down and sold for scrap during the year of 2006. The new owners had no information in regards to whom the scrap was sold or the whereabouts of the device. "On April 7, 2016, the Agency [Alabama Department of Public Health - Office of Radiation Control] contacted Ronan and their records indicated no transfer for disposal. During the next few weeks, several calls were made to the Alabama Department of Environmental Management and the Alabama Surface Mining Commission to determine if any new information could be obtained. None of the representatives could provide any additional information. "As of today [5/6/16], 0915 CDT, the device containing radioactive material has not been recovered. This incident remains open until further investigation can be completed." Alabama Incident 16-15 * * * UPDATE FROM MYRON RILEY TO VINCE KLCO ON 7/5/2106 AT 1257 EDT * * * The following information was received from the State of Alabama via facsimile: "SUBJECT: Update - Lost Gauge Containing Radioactive Material - Alabama Incident 16-15 "On May 5, 2016, it was determined that Millennium Resources, LLC, Graysville, Alabama had lost control and possession of a generally licensed device (Ronan SA1-C5 #2255GO containing 5 mCi of Cs-137). "On April 7, 2016, the Agency contacted Ronan and there records indicated no transfer for disposal. During the next few weeks, several calls were made to the Alabama Department of Environmental Management and the Alabama Surface Mining Commission to determine if any new information could be obtained. None of the representatives could provide any additional information. "On June 9, 2016, the Agency could not determine any information on the whereabouts of the Ronan device from manufacturers, service companies, waste brokers or past employees. As of today, [1245 CDT], the device containing radioactive material has not been recovered." Notified the R1DO (Bower) and NMSS Events via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2016-05-16
51910 | -1 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2016-05-05 05:00 | 2016-05-05 15:39 | 2016-06-29 | HIGH PRESSURE SAFETY INJECTION VALVE BONNET LEAKAGE IDENTIFIED DURING REFUELING OUTAGE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "At 0500 MST on May 5, 2016, engineering personnel determined that leakage from the bonnet seal weld of the Train B High Pressure Safety Injection (HPSI) system loop 2A injection valve, SIBUV0616, constituted reactor coolant system pressure boundary leakage. This is being reported as a degradation of a principal safety barrier pursuant to 10 CFR 50.72(b)(3)(ii)(A). "The leak was identified during a planned activity in which Operations was filling the refueling pool using HPSI pump B. Leakage was stopped when a plant operator closed SIBUV0616. "PVNGS Unit 1 was shut down for its 19th refueling outage (1R19) on April 9, 2016, at 0000 MST and is in Mode 6. "The NRC Resident Inspectors have been informed of this condition." * * * RETRACTION PROVIDED BY JORGE RODRIGUEZ TO JEFF ROTTON AT 1732 EDT ON 06/29/2016 * * * "Subsequent engineering evaluation of the leak condition concluded the leakage from the bonnet seal weld of SIBUV0616 was not reportable reactor coolant system pressure boundary leakage. This conclusion was based on further reviews of the PVNGS licensing bases, ASME Code requirements, and design features of the valve with vendor assistance, which determined that the body-to-bonnet threads provide the structural support for the mechanical joint and the seal weld is not required for structural integrity of the component. "Based on the above information, PVNGS has determined the leakage did not represent a degraded condition of a principal safety barrier as defined by 10 CFR 50.72(b)(3)(ii)(A) and Event Notification No. 51910 is hereby withdrawn. "The NRC Resident Inspectors have been informed." Notified R4DO (Werner) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-05-05
51909 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-05-05 | 2016-05-05 15:02 | 2016-05-05 | AGREEMENT STATE REPORT - DISCOVERY OF VACUUM GAUGE The following was received from the Commonwealth of Pennsylvania via email: "On May 5, 2016, the Blair County Emergency Management Agency notified the Department [of Environmental Protection] of the discovery of a NRC Equipment Corporation Model 530 Alphatron vacuum gauge. This gauge was located in a wooded area in Blair County, Pennsylvania. The gauge was manufactured with approximately 100 microcuries of radium-226. The manufacturer is no longer in business. The Department has retrieved the gauge and will safely store it until its annual collection of radium sources in September, 2016. No exposures have occurred with this discovery. It is reportable under 10 CFR 20.2201(a)(1)(i)." Event Report ID No: PA160013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-05-13
51908 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2016-05-04 14:00 | 2016-05-05 11:36 | 2016-05-05 | FITNESS FOR DUTY POLICY VIOLATION "An individual failed to comply with the NextEra Energy fitness-for-duty policy during a follow-up fitness-for-duty test. The individual's access to the plant has been terminated. This is reportable under 10 CFR 26.719(b)(2)(ii). "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.719 |  |  |  | 0 | 2016-05-05
51907 | 0 | ROTORK CONTROLS, INC. |  |  |  |  | 2016-01-25 | 2016-05-04 14:56 | 2016-10-31 | PART 21 - ANOMALY RELATED TO MICRO SWITCHES The following report was received via email: "Based on test data, Rotork believes an unsafe condition may exist as defined under 10 CFR 21. The adhesive formulation used for the construction of V12 and K5 safety related micro switches was altered by the switch maker's sub-supplier. K5 switches have no reported failures, but are affected because of construction. The altered adhesive formulation outgases an insulating material at elevated temperatures, which coats the switch contacts as it cools and can prevent the conduction of electricity." * * * UPDATE AT 0938 EDT ON 10/31/16 FROM PATRICK A. SHAW TO S. SANDIN VIA FAX * * * "This letter provides an update to the Rotork Controls Inc. Part 21 filing submitted May 4th 2016; documented in U.S.NRC Event Number 51907. "Rotork have developed versions of the V12 & K5 switches that eliminate adhesive from the materials of construction. "Evaluation of pre-production V12 switches, by thermal aging for 10 days at 125øC (257F), demonstrate the switch non-metallic housing and plunger also outgas materials that contributed to the accumulated contamination observed on switch electrical contacts as reported in Event 51907. The cause of the new outgassing sources and extent of condition is currently being investigated. For the moment suitable replacement switches remain unavailable that correct the issue reported in Event 51907. "At this point in time, Rotork do not have grounds to believe the extent of condition is altered from that reported in Event Number 51907." Notified R1DO (Schroeder), R2DO (Guthrie), R3DO (Daley), R4DO (Vasquez) and PART 21/50.55 REACTORS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-05-04
51906 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-04-07 | 2016-05-04 09:27 | 2016-05-04 | FLORIDA AGREEMENT STATE REPORT - LOST RADIOACTIVE THICKNESS GAUGE The following information was obtained from the State of Florida via email: "An audit conducted on James Hardie Building Products on April 4th, 2016 discovered a thickness gauge (NDC Model 102) was unaccounted for. The company was in the process of transferring equipment and under going an expansion. The auditor gave the company time to search for the device. As of 5/4/2016 all nine (9) of their facilities have been searched and the gauge has not been found. The last positive 'eyes on' sighting of device occurred in 2013 at the Plant City facility. The device was locked down to a wooden pallet. New policies and procedures are being implemented by James Hardie Building Products." Although the audit was completed on April 4, 2016, the licensee did not conclude their search of all their facilities until April 7, 2016. The gauge was an NDC Systems Model 102, serial number 11838, containing 25 mCi of Am-241. Florida Incident Number: FL16-059 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-05-12
51905 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2016-02-23 | 2016-05-03 18:25 | 2016-05-03 | AGREEMENT STATE REPORT - RECEIVED DOSE FROM BRACHYTHERAPY TREATMENT DIFFERENT THAN PRESCRIBED DOSE The following was received from the Commonwealth of Kentucky via facsimile: "KY RHB [Kentucky Department for Public Health & Safety, Radiation Health Branch] was notified by telephone on 5/3/16 at approximately 1600 [EDT] by a representative from Taylor Regional Hospital, of a medical event involving 2 separate patients that had permanent prostate implants using Pd-103. Both patients had implants on 2/23/16 and post implant CT's [computed tomography] on 3/22/16. Post implant dosimetry for one patient revealed the dose received to 90 percent of the prostate was 83.19 Gy and the prescribed dose was 125 Gy (66.55 percent of prescribed). The second patient received 89.06 Gy of the 125 Gy prescribed (71.25 percent of the prescribed). Additional information expected from the licensee. "Event Report ID No.: KY160002" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2016-05-11
51904 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2015-11-11 | 2016-05-03 15:45 | 2016-05-03 | AGREEMENT STATE REPORT - POTENTIAL RADIATION WORKER OVEREXPOSURE The following was received from New York via email: "Possible [overexposure] event occurred when a radiochemist employed by Weill Cornell Medical College recorded an exposure of 1675 mRem during the October 1-October 31 monitoring period. This caused his year to date exposure for the year 2015 to exceed the annual maximum permissible personnel exposure of 5000 mRem per year. His year to date dose equivalent through October 31, 2015 is 5546 mRem. The radiochemist synthesizes radiopharmaceuticals for PET and PET/CT. He works primarily with Carbon-11 with a 511 keV gamma energy. Investigation was performed by the licensee [New York Presbyterian Hospital]. They analyzed his workload, procedure methods and the quantities of the radiopharmaceuticals he worked with in October and confirmed that it did not vary from previous months in this year. Also other radiochemists working with him did not receive any elevated exposures nor were there any contaminations in the radiochemistry area. Since the radiochemist October exposure was 43 percent of what he had received in his previous 9 months, the licensee concluded that the dosimeter may have been accidentally contaminated. The investigation concluded that the radiochemist did not receive an overexposure of 1675 mRem." New York Incident # NY150008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-05-11
51903 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2016-05-03 | 2016-05-03 15:41 | 2016-05-03 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following was received from the Commonwealth of Virginia via email: "Honeywell International is authorized by general licenses to possess a number of tritium exit signs. It was discovered during an internal physical inventory that eight tritium signs were unaccounted. All were distributed by Safety Shield, Inc., and included one Model L3, s/n T8543, 11.5 curies; one Model XT, s/n S1075, 7.5 curies; and six Model 2040's, s/n 207011 through 207016, 7.5 curies each. The signs were received several years ago. Honeywell was unable to locate the signs despite a search of the facility and additional record review. Honeywell has submitted a procedural change in an effort to better track the remaining tritium signs at the facility. The licensee will keep the agency informed of any additional information. "Event Report ID No.: VA-16-002" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-05-11
51902 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-05-03 13:01 | 2016-05-03 16:04 | 2016-05-03 | ANOMALIES IDENTIFIED DURING VISUAL INSPECTION OF REACTOR VESSEL INTERNALS "With Salem Unit One in a defueled condition during a planned refueling outage, anomalies were identified on baffle-former bolts while conducting a scheduled visual inspection of reactor vessel internals. Due to the visual anomalies, PSEG commenced ultrasonic inspection of the baffle-former bolts to determine the extent of condition and determine a repair plan. "Based on initial results of ultrasonic inspections received on May 03, 2016, this condition was determined to be reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B), since the as-found conditions were not previously analyzed. "Additional details regarding the extent of condition will be supplied in the 60 day report. "The NRC Resident Inspector has been informed. The licensee will notify State and local government agencies as appropriate." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-05-03
51901 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-03 11:30 | 2016-05-03 15:40 | 2016-05-03 | FITNESS FOR DUTY POLICY VIOLATION A non-licensed employee supervisor violated the fitness-for-duty policy during a random fitness-for-duty test. The employee's access to the plant has been denied. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2016-05-03
51900 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-05-03 08:33 | 2016-05-03 15:13 | 2016-05-03 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 0833 [EDT] on May 3, 2016, security received an alarm on a Main Control Room (MCR) door. At 0847 [EDT], security notified the MCR staff of the door alarm and that the door was incapable of closure. At this time, both control room ventilation filtration trains (CREVS) were declared inoperable in accordance with Technical Specification 3.7.10, Condition B, due to the inoperability of the Control Room Envelope (CRE). Attempts to close the door were made, and it was identified that a screw had become wedged at the base of the door preventing it from latching. At 0855 [EDT], the screw was removed and the door verified to close as designed. CREVS was determined to be operable and LCO 3.7.10, Condition B was exited. "The safety function of the CRE boundary is to ensure the in-leakage of unfiltered air into the CRE will not exceed the in-leakage assumed in the licensing basis analysis of Design Basis Accident (DBA) consequences to CRE occupants. In addition to an intact CRE boundary maintaining CRE occupant dose from a large radioactive release below the calculated dose in the licensing basis consequence analysis for DBAs, it also ensures the occupants are protected from hazardous chemicals and smoke. "This condition had no impact to the health and safety of the public. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-05-03
51899 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-05-02 22:29 | 2016-05-03 01:50 | 2016-06-22 | HIGH PRESSURE CORE SPRAY SYSTEM INOPERABLE DUE TO A CONTROL ROOM CHILLER TRIP "At 2229 [CDT] on 05-02-2016, River Bend Station declared the High Pressure Core Spray system INOPERABLE in accordance with Technical Specification 3.8.9, Condition E (Declare High Pressure Core Spray System and Standby Service Water System Pump 2C inoperable immediately) due to Division 1 Control Room Air Conditioning System HVK-CHL1C being INOPERABLE due to a trip of the chiller on high inboard bearing temperature. "Actions taken to exit the LCO: Alternated divisions of Control Room Air Conditioning System to Division 2 HVK-CHL1D in service and Division 1 HVK-CHL1A in standby." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/22/16 AT 1137 EDT FROM JACK MCCOY TO DONG PARK * * * "Supplement: An operability evaluation has been performed based on system operating procedures in place at the time of this event, and on calculations regarding heat-up rates of the spaces served by the main control room air conditioning system. Operating procedures already in place on May 2 specified the operator actions required to restore the air conditioning system to service following the unanticipated trip of a chiller. The normal shift complement was on duty at the time of the event, and could have provided an adequate number of operators to accomplish this task. The operability evaluation made no new assumptions regarding availability of operators. The manual actions to be performed for the start of an alternate chiller following a trip of an in-service chiller system have been determined to require 2.15 hours, based on ANSI 58.8 guidance. (ANSI/ANS 58.8, Time Response Design Criteria for Nuclear Safety Related Operator Actions, provides the industry guidance In this regard.) "Calculations of building heat-up rates have demonstrated that the loss of the air conditioning system can be sustained for 19 hours before temperatures in the rooms containing the Division 3 electrical equipment that support operability of the HPCS system exceed their maximum allowable ambient value. "Based on the conclusions of the operability evaluation, the trip of the 'C' HVK chiller on May 2 had no actual adverse effect on the ability of the electrical distribution systems in the main control building to support the safety function of the HPCS system. Event Notification No. 51899 is hereby withdrawn." The licensee has notified the NRC Resident Inspector. Notified R4DO (Rollins). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-05-03
51898 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-05-02 05:30 | 2016-05-02 17:07 | 2016-05-02 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of Texas via email: "On May 2, 2016, the licensee notified the Agency [State of Texas] that one of its technicians had discovered at approximately 0530 CDT, that a Troxler Model 3430 moisture/density gauge had been stolen out of the back of the licensee's pickup while it was parked at the technician's residence. The licensee's radiation safety officer (RSO) reported the technician had checked out the gauge on Saturday, April 30, 2016, to do a job in another town. After traveling to the job site, the job was cancelled. The technician failed to follow the licensee's procedures and went home instead of returning the gauge to the facility. The gauge was left chained inside the back of the company pickup. The technician told the RSO that the trigger lock was on the device. The technician told the RSO he heard noise outside his house at approximately 0300-0400 CDT this morning and suspects that was when it was being stolen. He found the chains had been cut and the transport case and gauge were gone along with another concrete testing device. Local law enforcement was notified and the technician drove around searching the area. The RSO contacted multiple pawn shops in the area. "Device: Troxler Model 3430 moisture/density gauge Serial #: 31528 Sources: Cesium-137 - 8 millicuries; Americium-241 - 40 millicuries "More information will be provided as it is obtained in accordance with SA-300." Texas Incident No.: I-9395 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-05-10
51897 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-05-01 20:21 | 2016-05-01 22:14 | 2016-05-01 | AUTOMATIC REACTOR TRIP DUE TO GENERATOR LOCKOUT "At 2021 [CDT] on 05/01/2016 Unit 1 automatically tripped due to a generator lockout. Relay 86/G1 actuated. The generator lockout resulted in a Unit 1 turbine trip and a reactor trip. "Auxiliary Feedwater and Feedwater Isolation actuated as designed. All Control Rods fully inserted. No primary or secondary relief valves opened. There were no electrical problems. Normal operating temperature and pressure is [being maintained]. There were no significant TS LCO's entered. This event was not significant to the health and safety of the public based on all safety systems performed as designed. Unit 2 was not affected." Unit 1 is stable in Mode 3, with decay heat being removed via dump valves to the condenser. The cause of the generator lockout is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-05-01
51896 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2016-05-01 08:47 | 2016-05-01 12:25 | 2016-05-01 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY NOT RELATED TO WORK "On May 1, 2016, at 0847 [EDT], an individual experienced a personal medical emergency during a break. The onsite fire brigade and emergency medical technicians administered first aid, but the individual was unresponsive. The individual was transported to the local hospital. The station was notified at 1008 that the hospital has declared the individual deceased. The individual was outside of the radiological controlled area and not contaminated. "Nine Mile Point Unit 2 is shut down for the scheduled refueling outage." The individual was a contractor employee. The licensee has notified the NRC Resident Inspector. The State of New York will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-05-01
51895 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-04-30 18:04 | 2016-04-30 19:14 | 2016-04-30 | MANUAL SCRAM DURING REACTOR STARTUP DUE TO INCREASE IN UNIDENTIFIED LEAK RATE "Today at 1804 EDT, a manual scram was processed during startup due to rising unidentified leak rate. The rise in unidentified leak rate was identified to be coming from the D Reactor Recirc Pump seal cavity. All rods inserted into the core and all systems functioned as expected during the scram. "The event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." The reactor is stable in hot shutdown. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-04-30
51894 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-04-29 | 2016-04-30 14:31 | 2016-04-30 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following was received from Arizona via email: "On April 29th, the licensee [Tucson Medical Center] discovered that a patient had received 37 percent more than the prescribed dose of Xofigo (Radium-223). The licensee had received two doses of Ra-223 for two patients the day prior. The technologist usually asks a patient their weight in order to re-calculate the dose, but forgot and accidently grabbed another Xofigo patient's dose on April 28th. The technologist realized the mistake when she went to inject the second patient on the 29th and the name on the patient's dose did not match the current patient's name. The prescribed dose was 86.7 microcuries and the actual administered dose was 119.3 microcuries. "The investigation into this event is ongoing. "The U.S. NRC and Arizona Governor's office are being notified of this event." Arizona Incident # 16-008 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-05-09
51893 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-04-27 | 2016-04-30 13:53 | 2016-04-30 | AGREEMENT STATE REPORT - IMPLANTED IODINE 125 SEED NOT ACCOUNTED FOR The following was received from Arizona via email: "On April 27th, the licensee [Mayo Clinic Arizona] discovered that one (1) I-125 seed was missing with an approximate activity of 0.3 millicuries. The breast tissue from a patient was analyzed by the licensees' surgical staff on April 26th and one seed was removed and then brought down to the nuclear medicine department on the morning of the 27th. The nuclear medicine staff quickly realized that there should have been two seeds, since two seeds were initially implanted. The licensee's radiation safety staff surveyed both the hospital surgical path area as well as the pathology/histology area and no source was discovered. "The investigation into this event is ongoing. "The U.S. NRC and Arizona Governor's office are being notified of this event." Arizona Incident # 16-007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-05-09
51892 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2016-04-29 22:14 | 2016-04-30 00:48 | 2016-04-30 | LOSS OF OFFSITE POWER TO THE A RESERVE STATION SERVICE TRANSFORMER "At 2214 [EDT] on 4/29/16, with Unit 1 and Unit 2 operating at 100 [percent] power, the North Anna 34.5 kV Bus 5, off site power feed to the 'A' Reserve Station Service Transformer, was lost which resulted in the loss of power to the Unit 1 'J' Emergency Bus. Loss of Bus 5 is still undergoing investigation. As a result of the power loss, the 1J Emergency Diesel Generator automatically started as designed and restored power to the 1J Emergency bus. During the event, the Unit 1 'A' Charging Pump (1-CH-P-1A) automatically started as designed due to the loss of power event. "The valid actuation of these ESF components due to the loss of electrical power is reportable per 10 CFR 50.72(b)(3)(iv)(A). "The Unit 1 'J' Emergency Bus off-site power source was restored to service and the 1J Emergency Diesel Generator was secured and returned to automatic. Restoration of offsite power to Operable is complete. The Unit 1 'A' Charging Pump has been secured and returned to automatic. "Both units are currently stable. An investigation is underway to determine the cause of the Bus 5 loss of power." The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-04-30
51891 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2016-04-29 06:15 | 2016-04-29 10:48 | 2016-04-29 | OFFSITE NOTIFICATION OF ONSITE CHEMICAL SPILL "The licensee notified the Arkansas Department of Emergency Management, National Response Center, and Local Emergency Planning Committee regarding an onsite spill of 12 [percent] Sodium Hypochlorite (bleach solution). Approximately 2000 gallons of Sodium Hypochlorite solution leaked from a bulk tank within the protected area, outside the tank containment berm. Approximately 100 gallons were estimated to have entered the nearby storm drain. The estimate was based on preliminary chemistry samples. The quantity released exceeded the Reportable Quantity (RQ) for Sodium Hypochlorite (RQ of 100 pounds) and was therefore reported. "There is no impact to the operation of the ANO units or personnel onsite or offsite. No harm to the environment is expected. No offsite emergency response is required. "This event is reportable under 10 CFR 50.72(b)(2)(xi) as an event or situation related to the protection of the environment for which a notification to other government agencies have been made. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-04-29
51890 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-04-23 | 2016-04-28 12:49 | 2016-04-28 | AGREEMENT STATE REPORT - EMPLOYEES POTENTIALLY EXPOSED TO RADIATION The following was received via email from Arizona: "On April 26th, the Agency [Arizona Radiation Regulatory Agency] was contacted by the licensee who indicated that seventeen employees had been exposed to ionizing radiation by a nuclear gauge while working on Crusher Number Three. The nuclear gauge was mounted on the shoot above the crusher. The workers involved worked in the area of concern from Saturday April 23rd until Tuesday April 26th, when the Radiation Safety Officer was notified of the incident. "The gauge involved is used for level detection in the shoot and contains 150 millicuries of Cesium-137. Radiation levels in the work area have yet to be determined. "The investigation into this event is ongoing. "The U.S. NRC and Arizona Governor's office are being notified of this event." Arizona Incident number 16-006. * * * UPDATE FROM AUBREY GODWIN TO DONALD NORWOOD AT 1611 EDT ON 5/10/2016 * * * The following information was received via E-mail: "The current gauge decayed estimate is 95.2 millicuries of cesium-137 as of April, 2016. "The Licensee contracted a medical physicist to estimate the exposure received by the involved employees. Due to the complexity of the work positions and the small beam diameter produced by the gauge, the physicist calculated maximum possible exposures. His results in mRem were: 2 workers - 187 mRem, 2 workers - 140 mRem, 5 workers - 94 mRem, 2 workers - 47 mRem, 7 workers - 23 mRem. Actual exposures are believed to be less than these calculated estimates." Notified R4DO (Campbell) and NMSSRC (McIntosh) and NMSS Events Notification (via E-mail). Arizona Supplement: 16-006-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-05-06
51889 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2016-04-27 20:07 | 2016-04-28 00:15 | 2016-04-28 | HIGH ENERGY LINE BREAK DOOR DISCOVERED OPEN "On April 27, 2016 at 20:07 [EDT], a high energy line break (HELB) door between the turbine driven auxiliary feedwater pump and the motor driven auxiliary feedwater pump rooms was discovered open and unattended. In the event of a HELB, this condition could have rendered both trains of auxiliary feedwater inoperable. The boundary was not operable for approximately 1 hour. Upon discovery, the door was closed restoring the boundary. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v) as any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat; and (D) Mitigate the consequences of an accident. "The NRC Senior Resident Inspector has been notified." The Licensee notified the Connecticut DEEP and Waterford Dispatch. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-04-28
51888 | 0 | SPECTRUM HEALTH |  |  |  |  | 2016-04-27 14:05 | 2016-04-27 17:09 | 2016-04-27 | MEDICAL EVENT - DOSE GIVEN TO INCORRECT SEGMENT OF THE LIVER During a Y-90 TheraSphere treatment (hepatocellular carcinoma) to the right lobe of the liver segments 5, 6, 7, and 8 (estimated volume of 1290 ml), the catheter moved and the dose was actually given to medial segment 4 (estimated volume of 330 ml). The prescribed dose was 120 Gy (3.3 GBq) and the delivered dose was approximately 118.5 Gy as determined by bremmstrahlung imaging. Segment 4 was previously treated and there was some residual cancer at this location. This dose is not expected to have detrimental effects on the patient. It is anticipated that segments 5,6,7,8 will be treated at some future time. The patient has been notified and the prescribing physician will be notified. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(2) |  |  |  | 0 | 2016-05-05
51887 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-04-27 08:23 | 2016-04-27 12:25 | 2016-04-27 | LOSS OF TONE ALERT RADIO SYSTEM TOWER "At 0823 CDT on 4/27/2016, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in the event of an emergency condition. This is considered to be a major loss of the public prompt notification system capability and is reportable under 10CFR50.72(b)(3)(xiii). "Nemaha, Richardson and Atchison county authorities within the 10 mile EPZ [Emergency Planning Zone] were notified of the condition and the effect on the tone alert radios and will utilize local route notification (backup notification method) making this condition reportable under 10CFR50.72(b)(2)(xi) for notification of other government agencies. "Estimated return to service time is unknown. The cause of the failure is a loss of communication with the tower. "The NRC Senior Resident Inspector has been notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2016-04-27
51886 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-04-26 17:54 | 2016-04-27 01:17 | 2016-04-27 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "At 1736 [CDT] on 26 April 2016, a licensed operator performing a control room panel walkdown noted the green standby light for the HPCI [High Pressure Coolant Injection] Auxiliary Oil Pump (AOP) was not illuminated. The bulb was replaced and the replacement bulb did not illuminate. A non-licensed operator (NLO) was dispatched to the local 250VDC starter rack. The NLO discovered the green standby light on the 250VDC starter rack had failed. An attempt was made to start the AOP with the control switch. The pump did not start. The AOP is required to start in order to open the steam admission valves for the HPCI turbine. "HPCI was declared inoperable at time 1754 [CDT] on 26 April 2016. Tech Spec LCO Conditions were entered and required actions completed. "HPCI is a single train system. This report is submitted as a condition that at time of discovery could prevent the fulfillment of the safety function of an SSC [Structure, System, and Component] needed to mitigate the consequences of an accident. "A similar condition was discovered on 25 April 2016 [see NRC Event #51882]. Corrective maintenance was performed and HPCI was declared operable following satisfactory completion of post work testing of the AOP. "Initial investigation indicates that the fault which occurred on 26 April is not the same as that which occurred 25 April. "Investigation is on going." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-04-27
51885 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-04-26 22:13 | 2016-04-27 00:01 | 2016-04-29 | ALERT AND NOTIFICATION SYSTEM FEEDBACK SYSTEM INOPERABLE "On April 26, 2016 at 2213 EDT, Watts Bar Nuclear Plant authorized notification of State agencies for the partial loss of the WBN Alert and Notification System (ANS) feedback system. The ANS feedback system provides monitoring capability of the off-site sirens surrounding the facility in the event of a plant Emergency. Without the feedback system in service, sirens may be activated remotely from State and local facilities but verification of successful activation is impaired. State agencies were notified to evaluate if other methods of alerting the public were warranted. "No compensatory methods are required for this failure, as the ANS activation feedback systems remain fully functional at the State and local facilities. "The cause for the loss of the ANS feedback system is under investigation. "This is being reported under 10 CFR 50.72(b)(2)(xi) and 10 CFR 50.72(b)(3)(xiii). "The NRC Senior Resident has been notified." * * * UPDATE ON 4/29/16 AT 1103 EDT FROM MATTHEW MILLER TO BETHANY CECERE * * * "The cause of the partial loss of WBN ANS Feedback System was determined to be an equipment failure. AT&T has completed the work and the modem has been reset. The Corporate TVA Operational Duty Specialist (ODS) has been monitoring [the system] and there have been no issues identified with the feedback system. Therefore, the issue has been repaired. "In addition, further confirmation from the State of Tennessee and Rhea County was received that the sirens were fully functional at all times. The Feedback Monitoring System for the ANS was not available to the ODS only. Therefore, TVA Watts Bar is retracting the 10 CFR 50.72 (b)(3)(xiii) notification for Loss of Emergency Preparedness Capabilities. "The licensee has notified the NRC Resident Inspector." Notified the R2DO (Ehrhardt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2016-04-27
51884 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-04-21 | 2016-04-26 16:12 | 2016-04-26 | AGREEMENT STATE REPORT - SHUTTER STUCK OPEN The following report was received from the State of Georgia via email: "On Tuesday, April 26, 2016 our department [Georgia Department of Natural Resources, Radioactive Materials Program] received a report from GA Pacific, Cedar Springs, Georgia, that the shutters were stuck in the open position on a Kay Ray fixed gauge with 2000 mCi of Cs-137 and a Berthold fixed gauge with 30 mCi of Cs-137. Georgia Pacific maintenance personnel were doing a 6 month service check and realized that the shutters would not close. The incident occurred on 4/21/16. On 4/22/16, [the licensee RSO] received the report and was trying to determine reporting requirements. On 4/25/16, [the RSO determined] that they needed to do a notification report but our office was closed. Our department was notified on 4/26/16. Tag devices are being used but work cannot be performed around the area near the tank/pipeline. Berthold has been contacted but Kay Ray is out of business. A complaint has been opened in CTS [Complaint Tracking System] and our office has an ongoing investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2016-05-04
51883 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-04-25 03:45 | 2016-04-26 12:16 | 2016-04-26 | AGREEMENT STATE REPORT - RELEASE OF LICENSED MATERIAL AND CONTAMINATION The following information was obtained from the State of Tennessee via email: "The Tennessee Division of Radiological Health received a call at 1350 CDT on 4/25/2016 from a consultant for Clinical Pharmacy Services in Gray, Tennessee. He stated that a vial containing 290 milliCuries of stabilized Iodine-131 had been dropped in the pharmacy onto the floor. The vial broke, splattering the liquid onto two pharmacists and objects in the room. Employees were stripped of their clothing. Thyroid count results are zero for both individuals. The Iodine-131 had been stabilized with a buffering agent making it non-volatile. Plastic sheeting and thick pieces of lead were placed over the contaminated areas. All personnel badges were overnighted to Landauer. The corporate compliance officers for Clinical Pharmacy were contacted and will arrive today. The consultant stated that the maximum dose rate at the point where the vial hit the floor was 66 mR/hr. through the lead sheeting. He stated a dose rate at 6 to 7 R/hr. Personnel were placing surface contaminated objects into a large leaded disposal bin." Tennessee Report No.: TN-16-059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-05-04
51882 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-04-25 21:17 | 2016-04-26 01:54 | 2016-04-26 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "8-hour report due to HPCI inoperability. "At approximately 2109 [CDT] on 04/25/16, a licensed operator performing a control room panel walkdown noted the green light for HPCI Auxiliary Oil Pump (AOP) was not illuminated. The bulb was replaced and the replacement bulb did not illuminate. A non-licensed operator was dispatched to the local 250VDC starter rack. Both the green and red power indicating lights on the starter rack were found extinguished. An attempt was made to start the AOP with the control switch. The pump did not start. The AOP is required to start in order to open the steam admission valves for the HPCI turbine. "HPCI was declared inoperable at time 2117 [CDT], resulting in entry into Tech Spec LCO 3.5.1 Condition C - HPCI System Inoperable. Required Actions for Condition C are to verify by administrative means RCIC System is operable within 1 hour and restore HPCI System to operable status within 14 days. RCIC was verified operable by administrative means concurrent with HPCl declaration. "Troubleshooting activities for HPCI are being planned. "HPCI is a single train system. This report is submitted as a condition that at time of discovery could prevent the fulfillment of the safety function of an SSC [Structures, Systems, and Components] needed to mitigate the consequences of an accident." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-04-26
51881 | 0 | JEROME CHEESE COMPANY |  |  |  |  | 2016-04-25 14:10 | 2016-04-25 16:20 | 2016-06-03 | LOST DENSITY GAUGES The licensee has determined that two food product density gauges, previously in storage, cannot be accounted for and are considered lost. The density gauges, installed by Berthold in January, 1992, were last inventoried in April, 2015. They were removed from service in 2008. An extensive search of the facility was conducted and the devices were not located. It is believed they were sent out as scrap metal. Each gauge contained 30 mCi Cs-137 sources. Their serial numbers are 920-2-92 and 59-1-92. * * * UPDATE ON 6/3/16 AT 1009 EDT FROM PEGGY DORTCH TO BETHANY CECERE * * * Following an extensive licensee search of the warehouse, the gauges were found undamaged. Notified R4DO (Deese) and NMSS EVENTS via email; notified CNSC (CANADA) via fax. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2016-05-03
51880 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2016-04-25 06:07 | 2016-04-25 12:39 | 2016-04-25 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On April 25, 2016, at 0607 hours [CDT], HPCI [High Pressure Coolant Injection] was isolated via the HPCI MO 2-2301-4 (HPCI Inboard Main Steam Isolation Valve) to stop a packing leak on the HPCI MO 2-2301-5 (HPCI Outboard Main Steam Isolation Valve). The packing leak was causing a steam plume potentially impacting the motor operator on the 2-2301-5 valve. HPCI was declared inoperable and T.S. 3.5.1 Condition G was entered. "Since HPCI is a single train safety system, this notification is being made in accordance with 10CFR50.72 (b)(3)(v)(D), as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-04-25
51879 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-04-20 | 2016-04-22 20:00 | 2016-05-18 | AGREEMENT STATE REPORT - MISSING STATIC IONIZATION SOURCE The following report was received from the State of Washington via email: "On 4/21/2016, the Radiation Safety Officer at University of Washington reported by phone and by email that a Po-210 static ionization source was missing from a lab at the Southlake Union [SLU] Campus. The static ionization source had been placed in a cardboard box in preparation for shipment back to NRD [manufacturer]. Someone in the lab thought the box was empty and placed it in the recycling. This was discovered on Monday, and the lab had been searching for it for a couple of days before notifying the Radiation Safety Officer. "The immediate report value for Po-210 is 100 microCi and the 30 day report value is 1 microCi. Source information: Isotope: Po-210, Manufacturer: NRD, Model: P-2001, Initial Activity: 5 mCi (May 2015), Current Activity: approximately 1 mCi Device information: Nuclespot - Static Eliminator, Manufacturer: NRD, Model: P-2042-1000, Serial Number: Not reported. "The facilities personnel are currently trying to find out from [the recycling company] where the recycling is taken for processing. [The recycling company] picks up recycling from the SLU campus twice a week on Friday and Tuesday. University of Washington Principal Investigator lab informed NRD of the loss. Once their investigation is complete, UW will provide us [WA Office of Radiation Protection] with a written report as required by WAC 246-221-240(2). "Incident Number: WA-16-018" * * * UPDATE AT 1541 EDT ON 05/18/16 FROM ANINE GRUMBLES TO S. SANDIN * * * The following information was received from the State of Washington via email: "WA-16-018 Po-210 static ionization source missing from University of Washington "Update and Closure "University of Washington submitted their final report on the lost Po-210 static eliminator. University of Washington is a Broad Scope A Licensee. "Their [University of Washington] Radiation Safety staff performed a thorough investigation and search for the source. "There are a total of six possible routes the source may have taken; all of which end up overseas. Initially, three potential avenues were explored at Recology CleanScapes: 1. If source stayed inside the box with the paper - processed as corrugated cardboard and sent overseas for recycling processing 2. If paper came out of the box and source stayed with paper - processed as mixed paper and sent overseas for recycling process 3. If paper came out of box and source came out of the paper - source would have filtered out into glass recycling stream (includes metal), which is sent to Strategic Materials. The RSO contacted Strategic Materials and identified an additional three possible outcomes for the source, if it made it to the Strategic Materials facility. 4. All incoming material is first passed by a large magnet, if the source housing was ferrous enough the source would have been transferred to a metal recycler. The source model is believed to have an aluminum housing. 5. If the source was not pulled out by the magnet, it was either manually removed by a picker and thrown in the trash, or 6. The source was pulled out by an Eddy Current device and would be in one of the device collection bins. This also would have been thrown in the trash. Staff at both facilities were shown photos of the source and interviewed, and no one had seen or moved the source. "Ultimately, it is believed that the source, thoroughly wrapped in in paper, in a corrugated box was processed and sent overseas in a bulk cardboard or mixed paper recycle bundle. "The Registry of Radioactive Sealed Sources and Devices - Safety Evaluation of Device (Number: NY 502 D 108 G) for the P-2042 model indicates an maximum external exposure rate of 0.05 mR/hr on contact with the source. This is equivalent to background radiation levels. It should be noted that the principle emission of Po-210 is an alpha particle, so the exposure falls off rapidly with increasing distance from the source. Therefore, the exposure to any individual handling the source would be negligible. Since Po-210 is an alpha emitter, the highest risk would be to a person who ate the radioactive foil. However, this scenario is extremely unlikely due to the fact that the individual would have to first remove the foil from the housing, and then have a desire to eat the foil. "Some new additions to the information: Manufacturer: NRD Inc. Device Type: Nuclespot - Static Eliminator Device Model: P-2042-1000 Sealed Source Model Designation: P-2001 Serial Number: A2KG893 NRD Lease Number: 059345 Shipped to UW: 5/21/2015 Original Activity: 5 millicuries Activity when lost: 1 millicurie "This source is considered lost and unrecoverable. The assessed health and safety risk is very low. This incident is considered CLOSED." Notified R4DO (Miller) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-05-02
51878 | 0 | BROWNS FERRY | 1 | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-04-22 13:59 | 2016-04-22 18:22 | 2016-04-22 | PARTIAL LOSS OF POWER EXPERIENCED DURING ELECTRICAL BUS TRANSFER "At 1359 CDT on April 22, 2016, Browns Ferry Units 1 & 2 experienced a partial loss of power during the transfer of Shutdown Bus 2 from the alternate power source back to the normal power source. During the transfer, the normal feeder breaker failed to close and provide power to the Shutdown Bus, resulting in an auto actuation of two Emergency Diesel Generators (EDGs). Power to Shutdown Bus 2 was immediately restored using the alternate feeder breaker. The EDGs did not tie to the boards. "All systems responded as expected for the loss of power, and both Units 1 & 2 maintained 100% Rx Power. All systems have been restored to a normal lineup, and both Units 1 & 2 remain at 100% Rx Power. "This event requires an 8 hour report per 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (8) Emergency AC electrical power systems, including: Emergency diesel generators (EDGs).' "The NRC resident inspector has been notified." The cause of the normal feeder breaker failure is being investigated. There was no impact on Unit 3. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-04-22
51877 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2016-04-21 15:50 | 2016-04-22 00:03 | 2016-04-22 | MISSING FIRE BARRIERS "Missing fire barrier between Fire Area (FA) 59 and 85. "During a walk down of fire barriers for the NFPA 805 project, it was determined that the fire barrier between Fire Area 59 (Unit 1) and 85 (common) is not a rated barrier due to unsealed penetrations in the barrier. Evaluation FPEE 12-006 evaluated the acceptability of the barrier being unrated based on separation of safe shutdown equipment however a review of equipment credited for Appendix R safe shutdown identified that the redundant credited Appendix R equipment is on either side of the fire barrier which is not 3 hour rated. The conclusion of the FPEE is therefore no longer valid. "Fire Hazard Analysis Drawings Do Not Match Boundary Description. "The plant layout in F5 Appendix F, Rev. 28, Fire Hazard Analysis (FHA), does not agree with the boundary description in the FHA for the Unit 1 and 2 Containment Annulus fire areas, Fire Area (FA) 68 and 72. The layout should but does not show the fire area boundary between the annulus and adjacent fire areas, FA 60 and 75 on 735 [foot] and 61A on 755 [foot], as an Appendix R boundary. The annulus airlock doors are 3-hour fire rated and the airlock is constructed of concrete thick enough to qualify as a 3 hour fire barrier however, there are penetrations in the barrier that are not sealed with fire rated materials or inspected as required by the Fire Protection Program. "Therefore, this is an unanalyzed condition reportable under 10 CFR 50.72(b)(3)(ii)(B). This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-04-22
51876 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-04-21 | 2016-04-21 21:19 | 2016-04-25 | AGREEMENT STATE REPORT - RADIATION LEVEL ON PACKAGE GREATER THAN LIMITS The following information was obtained from the State of Texas via email: "On April 21, 2016, the Agency [Texas Department of State Health Services] was contacted by the Environmental Protection Agency in response to a notice it had received regarding excessive dose rates coming from a package in shipment. The package was being carried by [a common carrier] and was located at one of its facility in Houston, Texas. The Agency contacted the radiation safety officer (RSO) for [the common carrier]. He stated they had been informed by Customs and Border Patrol that one of their packages was reading higher than expected and they had responded. The RSO stated their surveys indicated dose rates at three feet were 41 mrem per hour and 7 rem per hour on contact with the package. The RSO stated their surveys were not consistent with the dose rates reported by Customs. The RSO stated the package contained a 2.79 (11.84 original activity) curie iridium 192 source being returned to the manufacturer. The source was from a high dose rate after loader being returning from outside the United States. The shipping container was opened and the source was found sitting on top of the shield. The source was placed in a different shield and returned to a safe storage location. "While the shipper was investigating the event, a person inside the facility called 911. When the hazmat team arrived they performed a radiation survey and decided the dose rates warranted evacuating all the workers from the building. The building was evacuated for more than an hour, but less than two hours. "[The common carrier] is investigating the event and any possible exposures to their workers. The RSO stated he did not believe any individual of the general public would have exceeded any limits. The RSO and this Agency has scheduled a call on April 22, 2016, to exchange additional information. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-9391 * * * UPDATE AT 0907 EDT ON 04/25/16 FROM ART TUCKER TO S. SANDIN VIA EMAIL * * * "The Agency contacted the Houston Texas Hazmat Team leader (HTL). They stated their surveys at 200 feet indicated the radiation readings were background. The HTL stated when they arrived the bucket containing the source was on a pallet held in place with plastic wrap and a cinch strap. The HML stated the bucket containing the source was the only item on the pallet. The Hazmat Team (HMT) removed the plastic wrap from the bucket and removed the bucket from the pallet. The bucket (containing the source) was then placed in a 30 gallon container. The container was filled with a dry material containing clay. That container was sealed and placed in a 55 gallon drum. The 55 gallon drum was filled with water and the top placed on the drum. The manufacturer's representative who retrieved the source was contacted. They stated dose rate on the side of the 55 gallon drum was 7 rem/hr (this dose rate was reported as on the side of the package in the initial report.) The dose rate on the top of the source container (package) was 15 rem/hr. He stated he noted the end of the drive cable near and past the source had been damaged. He found that the source was not inside the shield and both security seals were missing from the shipping container." Notified R4DO (Groom) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-04-29
51875 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2016-04-21 14:03 | 2016-04-21 18:18 | 2016-04-21 | FITNESS FOR DUTY - CONTRACTOR SUPERVISOR ATTEMPTS TO SUBVERT FITNESS FOR DUTY TEST "A non-licensed supervisory contractor admitted to attempting to subvert a Fitness for Duty test. The contractor's site access has been terminated. The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2016-04-21
51874 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2016-04-20 14:05 | 2016-04-20 22:04 | 2016-04-20 | UNANALYZED CONDITION DUE TO ESSENTIAL SERVICE WATER PRESSURE TRANSIENT "Recent Operating Experience at Callaway has shown that the pressure transient experienced in the Essential Service Water (ESW) system during Engineered Safety Feature Actuation System (ESFAS) testing can result in gasket failure on the Control Room Air Conditioners rendering the units nonfunctional. Previously, this pressure transient was considered to be the result of the system alignment used to perform the surveillance test, which is not the same as the system lineup which would occur on an actual Loss of Offsite Power (LOOP) or Safety Injection Signal Design Basis Accident (DBA) event. However, on April 20th, 2016, Callaway received preliminary analysis results that predict the Control Room Air Conditioners would actually experience a greater pressure transient during a DBA than what is currently experienced during ESFAS testing. This condition could result in the Control Room Air Conditioners not being capable of performing their safety function following a DBA event, and challenge Control Room Habitability. Therefore, this condition meets the reporting criteria of 10 CFR 50.72(b)(3)(ii)(B). "Based on current conditions (i.e., the plant is not in Power Operation), this condition does not present an immediate safety concern. "The analysis of the pressure transient experienced by the ESW system during a postulated DBA event is preliminary and further evaluation of the analysis is ongoing. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-04-20
51873 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-04-20 | 2016-04-20 15:44 | 2016-04-20 | AGREEMENT STATE REPORT - POLONIUM 210 SOURCE MISPLACED The following report was received via email: "On April 20, 2016 an employee Thermo Fisher (Thermo Finnigan LLC-Round Rock, Texas) reported that an anti-static nozzle containing polonium 210 had been misplaced at his facility. The activity of the source was 10 mCi (serial number A2JY896). The source was inside the spray nozzle control which screws onto the spray gun used for electronic cleaning. During the process of collecting the nozzles to return to manufacture it was found that one was missing. A company wide search is in progress to find the missing source. More information will be sent as obtained from the licensee." Texas Incident #: I 9390 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-04-28
51872 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-04-19 21:59 | 2016-04-20 01:52 | 2016-04-20 | INOPERABLE SECONDARY CONTAINMENT "On April 19th, 2016 at 2159 [EDT], Secondary Containment became inoperable due to failure to meet Surveillance Requirement (SR 3.6.4.1.1) on Unit 1 and Unit 2. "The inoperability was caused when Reactor Building differential pressure was discovered to be less than Technical Specification requirements [-0.25 inches of water gauge]. "Secondary Containment was restored April 19, 2016 at 2222 by adjusting intake louvers in accordance with off normal operating procedure ON-RBHVAC-201. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-04-20
51871 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-04-19 13:43 | 2016-04-19 19:54 | 2016-04-19 | MAIN STEAM LINE RADIATION DETECTOR DETERMINED TO BE NON FUNCTIONAL "While performing a monthly check source on radiation monitor 1-RE-2328 (Main Steamline 1-04 Radiation Detector), the monitor was determined to be non-functional. With this radiation monitor non-functional, all of the emergency action levels for a steam generator tube rupture in steam generator 1-04 could neither be evaluated nor monitored. This unplanned condition is reportable as a major loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant [CPNPP] has assurance of steam generator integrity and fuel cladding integrity and there is a negligible safety significance to the current condition from a public health and safety perspective. "Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. "Until this radiation monitor can be restored, Operations has implemented compensatory measures to monitor main steamline 1-04 N16 Radiation Monitor for early signs of a steam generator tube leak/rupture, pre-brief radiation protection technicians on taking local readings with a geiger-mueller tube on main steam line 1-04 and reporting the reading to the Control Room. "Corrective actions are being pursued to restore 1-RE-2328 to functional status." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-04-19
51870 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-04-13 | 2016-04-19 17:48 | 2016-04-19 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following report was received via e-mail: "On April 15, 2016, at approximately 1930 [MST], the [Arizona Radiation Regulatory] Agency received notification from the licensee of a possible medical event involving Sir-Spheres (Yttrium-90) that occurred on April 13, 2016. The prescribed dose was 0.95 GBq and the administered dose was 0.74 GBq, which is 77.8 percent of the prescribed dose. The [Arizona Radiation Regulatory] Agency has requested additional information and continues to investigate the event. "The U.S. NRC and Governor's office are being notified of this event." First Notice: 16-005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-04-27
51869 | 0 | EMERSON PROCESS MANAGEMENT, FISHER |  |  |  |  | 2016-03-21 | 2016-04-19 17:31 | 2016-04-19 | PART 21 FISHER 3582G POSITIONERS ESSENTIAL TO FUNCTION TRAVEL PIN LOCK PROVIDED AS COMMERCIAL GRADE "Items subject to this Fisher Information Notice (FIN) were provided to Public Service Electric and Gas Company (PSEG) per PSEG Order 4500798699 (Fisher Order Number 003 - V028245881) (Order). Specifically, this FIN pertains to Fisher Controls International LLC (Fisher) supplied safety-related Type 3582G positioners, serial numbers F000516516-517 ('Equipment') provided per the Order. In these assemblies, the essential-to-function travel pin lock was erroneously provided as commercial-grade." Fisher information Notice: (FIN) 2016-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-04-19
51868 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2016-04-18 14:00 | 2016-04-18 18:02 | 2016-04-18 | AGREEMENT STATE - POSSIBLE PATIENT UNDERDOSAGE OF YTTRIUM-90 The following report was received from the Arizona Radiation Regulatory Agency via email: "On April 12, 2016, at approximately [1630 MST], the Agency [Arizona Radiation Regulatory Agency] received notification from the licensee of a possible medical event involving Yttrium-90. The patient received approximately 3 [percent] of the prescribed dose. The Agency [Arizona Radiation Regulatory Agency] has requested additional information and continues to investigate the event. "The U.S. NRC and Governor's office are being notified of this event." Arizona incident #: 16-004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-04-26
51867 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-04-14 | 2016-04-15 16:07 | 2016-04-15 | AGREEMENT STATE REPORT - SHUTTER FAILURE ON A FIXED GAUGE The following information was obtained from the State of Washington via email: "[The Washington Department of Health - Office of Radiation Protection] investigation continues on the Kay Ray Sensall fixed gauge shutter failure. The licensee identified, during a routine shutdown, that the handle moves on the fixed gauge but fails to open and close the shutter. The licensee reported they believe the problem is a drift pin that allows the handle to turn the shaft of the shutter to its open/close position. The shutter is in the open position and is unable to be closed. The gauge is operating normally and correctly otherwise [and is] correctly mounted." The gauge is a Kay Ray Sensall model number 7063S with serial number S94J2306. NMED Incident Number: WA-16-014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-04-25
51866 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-04-11 | 2016-04-15 15:00 | 2016-04-15 | AGREEMENT STATE REPORT - RA-226 SOURCE FOUND IN GARBAGE TRUCK The following information is a summary of the information received from the State of California: On April 11, 2016, a City of Los Angeles garbage route truck alarmed the radiation monitors at the Athens Waste Services Sunland transfer station. The transfer station supervisor notified the California Department of Health - Radiologic Health Branch. The State dispatched an inspector to the facility. Upon arrival, the inspector was notified that the truck had returned to the City of Los Angeles East Valley Complex. The inspector travelled to the East Valley Complex. Upon arrival at the East Valley Complex, where the truck had been isolated, the inspector was able determine the approximate location of the device in the rear of the truck. The inspector was informed that a crew was not available to dump the contents to search for the item at that time. Arrangements were made for the inspector to return when a crew was available. The truck remained isolated. On April 14th, the inspector returned to the East Valley Complex to search for the source. A crew was assembled and the contents of the truck were dumped. Using a survey meter, the inspector was able to locate a 2.61 mCi Ra-226 radiation oncology treatment needle. No other sources or radioactive devices were discovered. The inspector secured the source in a lead pig and placed it into the State's inventory. Prior to the removal of the source, the highest radiation reading outside the truck was 1.2 mR/hr. on contact. California Report number: 5010-041116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-04-25
51865 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-04-13 13:00 | 2016-04-14 08:50 | 2016-04-14 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA FELL OFF TRUCK AND LATER RECOVERED "On April 13, 2016, the licensee reported to the Agency [Texas Department of State Health] that a radiography crew had failed to secure a QSA 880 Delta industrial radiography camera (SN: D9092), which contained a 98.7 Curie Iridium-192 source (SN: 30367G), inside their truck before leaving their facility to go to a temporary job site. The crew left the facility with the camera on the tailgate of their truck. A member of the public saw the camera in the street at an intersection approximately 100 yards from the facility. He knew what the camera was and that the licensee had a facility there. He moved the camera out of the street and into the ditch and called the licensee. The licensee responded immediately. The licensee inspected the camera and found no damage. They surveyed and confirmed the source was still in the fully shielded position. The licensee's radiation safety officer reported initial estimate is that the camera was out of their possession approximately 5 minutes and no one received any exposure above regulatory limits. The licensee will complete its investigation of the incident and will confirm or correct this initial information. Since the licensee has not yet submitted a dose assessment for the member of the public, we are making this report. More information will be provided as it is obtained in accordance with SA-300." Texas Incident: #I 9388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-04-22
51864 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2016-04-13 14:30 | 2016-04-13 17:57 | 2016-04-13 | UNANALYZED CONDITION "At approximately 1430 hours EDT on 4/13/2016, it was determined that the source document for the mass and energy release parameters used to determine the containment pressure and temperature response to a Main Steam Line Break (MSLB) does not adequately account for all possible single active failure scenarios in the steam or feedwater line isolation provisions. The source document addresses the active failure of the Main Feedwater Control valves to close in the faulted steam generator feed line, but not the failure of a feedwater bypass valves to close in the faulted steam generator feed line. An active failure of a feedwater regulating bypass valve whereby the valve fails to close will increase the secondary mass available for release to the containment structure. This can result in a higher peak containment pressure that could challenge the containment design pressure. This condition is only a concern when the feedwater regulating bypass valves are in the open position in modes 1, 2 or 3, and they fail to close on a engineered safeguards actuation signal. The feedwater regulating bypass valves are currently closed. "This determination is being reported as an unanalyzed condition in accordance with 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-04-13
51863 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2016-04-12 12:35 | 2016-04-12 14:36 | 2016-04-12 | COURTESY OFFSITE NOTIFICATION MADE TO STATE AND COUNTY OFFICIALS "On April 12, at 1235 CDT, Duane Arnold Energy Center contacted officials with the State of Iowa (Bureau of Radiological Health and Department of Natural Resources) and Linn County Public Health Department in accordance with the nuclear industry voluntary reporting criteria contained in NEI 07-07 'Industry Ground Water Protection Initiative'. The site contacted the agencies as courtesy to notify them about the identification of low levels of tritium found within the site's protected area from a potential new source. Samples were taken, and no regulatory limits were exceeded. The site team is working with industry experts on pinpointing the cause and installing an extraction well to remediate the situation. "This report is being made in accordance with 10 CFR 50.72(b)(2)(xi), as a result of notification to offsite agencies. "The Licensee has notified the NRC Resident Inspectors. "There is no risk to plant employees, the public or drinking water." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-04-12
51862 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-04-12 00:50 | 2016-04-12 07:47 | 2016-04-12 | LOSS OF BOTH EMERGENCY DIESEL GENERATORS "On April 12, 2016, with the reactor at 100 percent power and the mode switch in RUN, Pilgrim Nuclear Power Station entered an unplanned 24-hour Limiting Condition for Operation (LCO) action statement due to both emergency diesel generators (EDG) being inoperable (Technical Specification 3.5.F.1). At 0050 [EDT] this morning, with EDG B out of service for a planned LCO maintenance window, EDG A was declared inoperable due to a 130 drop per minute leak on a line to a jacket water pressure indicator. "Repairs to EDG A are underway at this time. "The following plant equipment has been verified operable: both 345 Kv transmission lines; 23kV transmission line; Station Blackout EDG. "This condition is reportable to the NRC Staff as an Event or Condition that Could Have prevented Fulfillment of a Safety Function (Mitigate the consequences of an accident) under 10 CFR 50.72(b)(3)(v)(D), and requires an 8-hour notification. "The licensee has notified the NRC Senior Resident Inspector. "The licensee will notify the Commonwealth of Massachusetts." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-04-12
51861 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2016-04-11 05:35 | 2016-04-11 15:37 | 2016-04-11 | REACTOR PRESSURE BOUNDAY LEAKAGE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "At approximately 2335 [MST] on April 10, 2016, while performing planned routine visual examinations of Unit 1 components in the Containment Building, engineering personnel identified white residue on the piping instrument nozzle for the reactor coolant system (RCS) 2B cold leg resistance temperature detector, 1JRCET121Y. The white residue was dry and no active leakage was noted on the instrument nozzle. "Preliminary chemical analysis for radionuclide and boron content of the white residue determined the existence of boron and the isotopic content was consistent with RCS fluid. At 0535 [MST] on April 11, 2016, it was determined the residue resulted from RCS pressure boundary leakage, based on results of the chemical analysis and additional examination of the piping and instrument nozzle by qualified engineering personnel. Technical Specifications Limiting Condition of Operation (LCO) 3.4.14 permits no RCS pressure boundary leakage and therefore, the discovery of leakage from the instrument nozzle represents a degradation of a principal safety barrier. This notification is being made for a degraded condition pursuant to the requirements of 10CFR 50.72(b)(3)(ii)(A). "The unit has been shut down for its 19th refueling outage since 4/9/16 at 0000. "The NRC resident inspectors have been informed of this condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-04-11
51860 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2016-04-09 15:23 | 2016-04-09 23:14 | 2016-04-09 | SECONDARY CONTAINMENT DETERMINED TO BE INOPERABLE DURING SURVEILLANCE TESTING "During pre-planned surveillance testing of the Supplementary Leak Collection and Release System (SLCRS), an issue was found affecting the Secondary Containment boundary. Millstone Unit 3 is being moved to Mode 5 for a refuel outage where investigation and repairs will be made. This is reportable under 10CFR50.72(b)(3)(v)(C), a condition that could have prevented the fulfillment of a safety function for systems or structures to control the release of radioactive material, and 10CFR50.72(b)(3)(v)(D) to mitigate the consequences of an accident." The surveillance testing was being performed while Millstone 3 was being removed from service for an upcoming Refueling Outage. The licensee has notified the NRC Resident Inspector and State and Local authorities. | 0 | 0 | 20 | 0 | 0 | 52 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-04-09
51859 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-04-08 18:20 | 2016-04-08 20:50 | 2016-04-08 | OFFSITE NOTIFICATION DUE TO OIL LEAK IN A SWITCHYARD TRANSFORMER OIL SYSTEM "At 1657 EDT on April 8, 2016, an oil leak developed from the station's switchyard transformer no. 4. Approximately 25,000 gallons of oil has leaked within the transformer's containment berm. At 1820 EDT on April 8, 2016, DC Cook environmental personnel determined that approximately 2000 gallons of oil had leaked outside of the containment berm onto the ground. None of the oil has made it to any nearby drains. Leak has stopped and cleanup is ongoing. D.C. Cook has notified the State of Michigan and local authorities. The NRC Resident Inspector was notified. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of offsite agencies." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-04-08
51858 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-04-13 | 2016-04-08 14:22 | 2016-04-08 | AGREEMENT STATE REPORT - INCORRECT DOSE PRESCRIBED BUT CORRECT DOSE ADMINISTERED The following report was received from the Commonwealth of Pennsylvania via email: "Notifications: The Licensee notified the Department April 1, 2016 of an event that occurred on April 13, 2015. It was discovered almost a year later upon routine review of written directives at the hospital. It is reportable under 10 CFR 35.3045. "Event Description: A Xofigor patient was scheduled for their 6th and final treatment on April 13, 2015. The Authorized User (AU) prescribed 0.98 millicurie (mCi) on the written directive (WD). On the prescription form from the radiopharmacy, the 'dispensed amount' of Ra-223 was labeled as 99.40 microCuries (or 0.0994 mCi). The Nuclear Medicine Technologist measured '0.099 mCi' in the dose calibrator just before injecting the Xofigor into the patient (intravenously). The technologist failed to observe that the AU prescribed an activity of 0.98 mCi making the percent error between the measured vs. prescribed activity at -89.9% based upon what was documented in the WD. The hospital believes the intent of the AU was to prescribe '0.098 mCi' which is a typical dose; however, they cannot directly confirm that with the AU since the AU is no longer employed by Geisinger Health System. Another Geisinger AU who is qualified to prescribe Xofigor confirmed that 0.098 mCi would be the correct amount when calculated from the patient's weight. Consequently, if the intent was to prescribe 0.098 milliCuries, there would be no expected harm to the patient as they received the proper Xofigor activity. "Cause of the event: Human error. "Actions: None at this time. The licensee will submit a final report which will provide corrective actions. Notifying the patient would serve no beneficial purpose." PA Report #: PA160012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-04-18
51857 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-04-07 | 2016-04-08 13:10 | 2016-04-08 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received from the State of California via email: "On April 7, 2016, [the licensee gauge operator] for Geo-Advantec, Inc., contacted the California Office of Emergency Services to report a moisture density gauge, a CPN Model MC3 Elite (10 mCi Cs-137, 50 mCi Am:Be-241, S/N30625), was run over by an unknown type of vehicle. The incident occurred at 2003 Speyer Lane, Redondo Beach, CA. After taking the report, the report was forwarded to the Los Angeles County Radiation Management which was then forwarded to Brea office of Radiologic Health Branch (RHB). "[The licensee gauge operator] was contacted by a RHB inspector and stated that the gauge had been run over and that the source rod had been broken. He was also asked if the Cs-137 source had been exposed, and he stated that he was taking a standard count and that the source was in the shielded position at the time of the incident. [The licensee gauge operator] was then asked to take pictures of the gauge so that it could be evaluated to determine if the sources were still intact and to determine the extent of the damage to the gauge. The pictures indicated that the source rod was broken approximately 1-2 inches below the bottom of the guide tube, which had broken off the source shield, and that the rest of the source rod appeared to be inside the opening on the top part of the source shield. The Am:Be-241 source appeared to be intact and still attached to the body of gauge. [The licensee gauge operator] was instructed to place the body of the gauge into the transport case in its normal position and then place the rest of the pieces of the gauge into the case. He was also instructed to lock the case and secure it into the transport vehicle as normal. He was then instructed to check ground below the gauge to verify that the source was not exposed during the incident. After [the licensee gauge operator] verified that there were no signs of the source having been extended during the incident, he was instructed to mark the area where the gauge was damaged to ensure that area could be found if a survey was needed and then he was allowed to transport the gauge to Maurer Technical Services (MTS) to be inspected and surveyed to ensure the sources were still in the gauge and to verify they were intact. "When the gauge arrived at Maurer Technical Services, a survey was performed by the MTS RSO [Radiation Safety Officer] (meter type not reported). The gauge had contact reading of 8.5 mR/hr, which was consistent with a CPN MC3 moisture/density gauge with both sources in their shielded positon. The RSO also took swipes of the device, the hands of the operator and the trunk of the operator's car. An RHB inspector arrived at MTS to perform a count of the swipes with a Ludlum general purpose meter and a 44-9 Geiger-Mueller probe and found all of the swipes were at background, indicating that there was not leakage and the sources were intact. The gauge will be stored at MTS until disposal of the gauge can be arranged. "The investigation is on-going and any citations will be determined at a later date." CA 5010 # 040716. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-04-18
51856 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2016-04-07 17:30 | 2016-04-07 22:32 | 2016-04-07 | BOTH DOORS OF SECONDARY CONTAINMENT OPEN SIMULTANEOUSLY "Nine Mile Point Unit 2 (NMP2) experienced a momentary loss of Secondary Containment due to both Reactor Building (RB) airlock doors being opened at the same time. "At 1730 [EDT] on 04/07/16, both RB airlock doors were opened simultaneously for less than 5 seconds. This resulted in Secondary Containment being declared Inoperable (TS 3.6.4.1). Secondary Containment was restored to Operable when the doors were closed. "The event is reportable in accordance with 10 CFR 50.72(b)(3)(v)(C), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the NRC Resident Inspector has been notified." There is no interlock on these doors, just lights to verify the opposite door is open or shut. An Operator was entering secondary containment as another Operator was leaving. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-04-07
51855 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-04-06 | 2016-04-07 19:38 | 2016-04-07 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "On April 6, 2016, a portable moisture/density nuclear gauge from Earth Solutions NW, LLC was damaged at a construction site near Monroe, Washington. "The technician from Earth Solutions NW, LLC restricted the area around the damaged nuclear gauge and reported the incident using our [Washington Office of Radiation Protection] 206-NUCLEAR emergency number. "Our [Washington Office of Radiation Protection] nuclear engineer assessed the condition of the nuclear gauge over the telephone and determined that the nuclear gauge should be safe to transport, so the nuclear gauge was transported to the Snohomish office of Northwest Technical Services, which is the company that typically maintains and calibrates the gauges for Earth Solutions NW, LLC. "Northwest Technical Services personnel inspected the damaged nuclear gauge and determined the nuclear gauge is intact, and that both radioactive sources are present in their normal locations inside the nuclear gauge. The cesium-137 source [10 mCi] is attached to its source rod, which is bent a bit, but the source is inside the gauge in its shielded position. The americium-241:beryllium source [50 mCi] is not compromised and is also inside the gauge in its normal position. "Based on the professional opinion of Northwest Technical Services personnel, there would not be any radioactive contamination at the construction site where the nuclear gauge was damaged. So, we [Washington Office of Radiation Protection] advised Earth Solutions NW, LLC personnel that it would no longer be necessary to restrict the part of the construction site where the nuclear gauge was damaged. "The next steps that will be taken are: 1) Northwest Technical Services personnel will conduct leak tests of the two sealed radioactive sources in the damaged nuclear gauge, to verify that no radioactive materials have leaked from the two sealed radioactive sources. They will send a written report, including photographs of the sealed radioactive sources and the damaged nuclear gauge. 2) The damaged nuclear gauge will be properly disposed of by Northwest Technical Services personnel. 3) Earth Solutions NW, LLC will send us a written report about the incident." Gauge model: CPN-131 from Campbell Pacific Nuclear Washington Incident: WA160001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-04-15
51854 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-04-07 15:07 | 2016-04-07 18:01 | 2016-04-07 | UNANALYZED CONDITION - HIGH PRESSURE FIRE SUPPRESSION ISOLATED FROM CONTAINMENT "This notification is being made as the result of the review of an occurrence on March 30, 2016 at 2220 [EDT] that resulted when a major portion of the site high pressure fire protection (HPFP) system, including fire suppression capabilities for the Main Turbine Building, Auxiliary Building, Control Building, Diesel Generator Buildings, and both Unit 1 and Unit 2 Containments were isolated without having the required compensatory suppression systems established. Upon discovery of the non-functional HPFP system, compensatory fire watches were established and an alternate means to provide water to the HPFP system was aligned. "A review of the Sequoyah Nuclear Plant (SQN) Safe Shutdown Analysis identified this loss of fire suppression may not have ensured the required equipment remained available under certain postulated fire scenarios. The analysis determined that the effects of a postulated fire in specific fire areas could have prevented critical systems or components from performing their intended functions, potentially resulting in the inability to achieve and maintain safe shutdown. "Analysis identified areas which credit the availability of fire suppression to assure that the safe shutdown capability could have been achieved, the site did not have fire suppression for approximately 45 hours. "No actual fire occurred or existed during the time the fire suppression system was not functional. Installed fire detection equipment and communication to the Main Control Room remained available. "The condition has been corrected and the HPFP system is functional. "At the time of the non-functional HPFP system, it was not recognized that an unanalyzed condition that could have significantly degraded plant safety existed. The condition placed both Unit 1 and Unit 2 in an unanalyzed condition that significantly degraded plant safety and is reportable under 10 CFR 50.72(b)(3)(ii)(B). This 8-hour non emergency notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(B). The condition has been entered into the licensee's corrective action program (CR 1155763) and a License Event Report will be submitted. "The NRC Resident Inspector has been notified of this condition." The original clearance that created this event was satisfactory as written, however, one of the valves was leaking and the clearance boundaries were expanded. The clearance was issued at 1411 EDT on 3/29/2016. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-04-07
51853 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-04-06 14:15 | 2016-04-07 08:00 | 2016-05-12 | FITNESS FOR DUTY An employee was reported to the Fitness for Duty Coordinator due to improper prescription medicine handling. The employee's site access has been suspended pending outcome of a drug test and investigation. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM CHRIS TERRY TO STEVE VITTO ON 05/11/2016 AT 0726 EDT * * * The licensee has completed the investigation. The licensee has notified the NRC Resident Inspector. Notified Heisserer (R2DO), Erlanger (FCSE), FFD Group (email), NMSS Events Notification Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2016-04-07
51852 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-11-16 | 2016-04-06 16:46 | 2016-04-06 | AGREEMENT STATE - LOST TRITIUM EXIT SIGN The following report was received from the Colorado Department of Public Health and Environment via email: "An audit of the radioactive materials general license files was conducted on the site at 800 W 84th Avenue. Inventory report showed Carquest - Denver had 6 Tritium exit signs registered in 2014. The report received from Carquest in December of 2015 showed a transfer of 5 Tritium exit signs being shipped to TritiumDisposal.com. An inquiry was made with the corporate office to obtain clarification as to lost exit sign. The property was further inspected to try and locate the missing sign however it was not discovered. "The corporate office [Advanced Auto Parts] contacted the location to obtain further clarification regarding the report of shipping the exit signs to TritiumDisposal.Com. The notification of lost exit sign was mailed to the corporate office Advanced Auto Parts to obtain a corrective action." "Model: SLX TURW10 Source Serial: #175174 Isotope: H-3, Activity Activity: 7300 mCi" Event Report ID No.: CO16-I16-06 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-04-14
51851 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-04-06 13:37 | 2016-04-06 17:27 | 2016-04-06 | REACTOR BUILDING AIRLOCK DOORS OPENED SIMULTANEOUSLY "On April 6th, 2016 at 1337 [EDT] and 1343 [EDT] Secondary Containment became inoperable due to failure to meet a Surveillance Requirement (SR 3.6.4.1.3) on Unit 1 and Unit 2. "The inoperability was caused when two separate sets of Reactor Building airlock doors were sequentially opened during a medical emergency to transport an individual. Each set of airlock doors was opened momentarily to allow passage. "Secondary Containment was restored April 6, 2016 at 1344 [EDT] when the transport evolution was complete. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-04-06
51850 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2016-04-06 15:45 | 2016-04-06 17:07 | 2016-04-07 | UNUSUAL EVENT DECLARED DUE TO MAIN STEAMLINE HIGH HIGH RADIATION CONDITION At 1545 CDT on 04/06/16 Browns Ferry Unit 3 declared and exited the declaration of an unusual event due to a main steam line high high radiation condition. Power to Unit 3 was reduced to 91 percent power. The high radiation condition alarm cleared at 1526 CDT. Browns Ferry Unit 3 reported that the high radiation conditions were due to resin intrusion from the condensate demineralizers into the reactor and hydrogen water chemistry was a potential contributor to the event. The cause is still under investigation. The NRC Resident Inspector has been notified. State and Local notifications were made. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, FEMA NWC and Nuclear SSA (email). * * * UPDATE FROM BILL BALL TO DANIEL MILLS AT 0034 EDT ON 04/07/2016 * * * "At 1941 [CDT] BFN [Brown's Ferry] determined this notification to be potentially newsworthy due to receiving notification that counties [surrounding the plant] were alerted of this event. No plant conditions changed." The licensee may issue a press release. The licensee will notify the NRC Resident Inspector. Notified R2DO (Nease). | 0 | 0 | 91 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode3: Power Operation; FMode3: Power Operation | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2016-04-06
51849 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-03-31 | 2016-04-06 14:24 | 2016-04-23 | AGREEMENT STATE - PACKAGE CONTAINING 40 MILLICURIES OF NI-63 REPORTED MISSING The following report was received from the Washington Department of Health via email: "[The] RSO [Radiation Safety Officer] of UW [University of Washington] reported on 4/6/2016, that a package containing four 10 mCi electron capture devices (ECDs), a total activity of 40 mCi, went missing on 3/31/2016, while being transported from Sydney airport to Tasmania, Australia on a Quantas flight. Quantas has put a trace out for the missing package. The ECDs were being sent to the Marine National Facility, CSIRO [Commonwealth Scientific and Industrial Research Organization] Marine Laboratories. The ECDs were to be used in gas chromatographs (GC) on board a marine vessel by a University of Washington researcher for obtaining research results. The GCs were shipped separately and these are not missing. The Radiation Safety Office did obtain an import permit from Australia for the ECD shipment, and can provide that documentation if needed. "Device Manufacturer: Shimazdu Scientific Instruments Mini-2 GC Serial Number: 500401 Activity: 0.010 Ci Radionuclide: Ni-63 "Device Manufacturer: Shimazdu Scientific Instruments GC-8A Model Number: ECD-8A Serial Number: SS1932 Activity 0.010 Ci Radionuclide: Ni-63 "Device Manufacturer: Shimazdu Scientific Instruments GC-8A Model Number: ECD-8A Serial Number: SS1953 Activity: 0.010 Ci Radionuclide: Ni-63 "Device Manufacturer: Shimazdu Scientific Instruments GC-8A Model Number: ECD-8A Serial Number: SS2047 Activity: 0.010 Ci Radionuclide: Ni-63" Package was shipped from University of Washington to Australia on 3/23/16. Washington Incident # WA-16-010 * * * UPDATE AT 1840 EDT ON 04/22/16 FROM JAMES KILLINGBECK TO JOHN SHOEMAKER * * * The following update was received from the State of Washington via email: "On 4/6/2016, the University of Washington (UW) reported the loss of a package containing four electron capture detectors (ECDs). Each ECD contained a 370 MBq (10 mCi) Ni-63 source. The package was being sent from UW to the Marine National Facility, Commonwealth Scientific and Industrial Research Organization (CSIRO) Marine Laboratories. The shipment was initiated on 3/23/2016. The package was delivered to the Sydney, Australia, airport on 3/24/016 and was checked in by the airline on 3/24/2016 and 3/26/2016. "The airline booked the package on a flight on 3/28/2016. The package became missing on the flight from Sydney to Tasmania, Australia, on 3/31/2016. The airline put a trace on the package. The ECDs were to be used in gas chromatographs (GCs) onboard a marine vessel by a UW researcher. The GCs had been shipped separately and are not missing. "The package containing the four electron capture detectors was found on 20 April 2016, and will be shipped to its intended destination. "Apparently, the package was misplaced in Sydney, Australia or while in transit in Melbourne, Australia, and it ended up at a freight forwarding company at the Melbourne, Australia airport. The package is being retrieved from the freight forwarding company, will be cleared by customs, and will be shipped to its intended destination in Hobart, Australia." Washington NMED Item Number 160160. Notified R4DO (Gepford) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-04-14
51848 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-04-05 09:50 | 2016-04-05 12:54 | 2016-04-05 | OFFSITE NOTIFICATION DUE TO EMPLOYEE FATALITY "This is a non-emergency four hour notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "At approximately 0908 Eastern Daylight Time (EDT) on April 5, 2016, an employee developed a personal medical condition in the Protected Area at the Brunswick Nuclear Plant. The Brunswick County Sherriff and local Emergency Medical Services were notified and they responded and attempted to resuscitate the unresponsive employee. These efforts were unsuccessful and the individual was declared deceased at approximately 0950 EDT on April 5, 2016. The fatality was not work related and the individual was inside of the Radiological Controlled Area and was not contaminated. No news release by Duke Energy is planned. "Notifications to the Occupational Safety and Health Administration are planned. "The NRC Senior Resident Inspector has been notified." | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-04-05
51847 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-04-04 13:30 | 2016-04-04 16:49 | 2016-04-04 | OFFSITE NOTIFICATION DUE TO COOLING TOWER WATER RELEASED TO A NON-PERMITTED OUTFALL "Notified the Pennsylvania Department of Environmental Protection that Limerick Cooling Tower water was released to a non-permitted outfall through the spray pond (Ultimate Heat Sink) due to system lineups associated with emergent maintenance activities. There was no radioactive material contained within the water released. Corrective actions are being taken to prevent further release via this outfall." The NRC Resident Inspector will be notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-04-04
51846 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2016-04-02 23:02 | 2016-04-03 07:13 | 2016-04-04 | REACTOR PROTECTION SYSTEM ACTUATION WHILE REACTOR SHUTDOWN "At 2302 [CDT] on April 2, 2016, with the plant shutdown, [with] all control rods inserted in the reactor and while attempting to reset the reactor trip breakers to support outage activities (reset of the main turbine), the reactor trip breakers reopened. This was identified to be due to having both trains of Solid State Protection System (SSPS) out of service while in Mode 5. With both trains of SSPS out of service, a condition was met that would cause a reactor trip signal due to having a general warning condition on both trains. Per procedure, the control rods were incapable of withdrawal and fully inserted. Reactor Coolant System boron was 2280 ppm. There were no actuations as a result of the reactor trip breakers opening due to SSPS being removed from service." The licensee will be notifying the NRC Resident Inspector. * * * RETRACTION AT 1635 EDT ON 4/4/16 FROM TIM HOLLAND TO JEFF HERRERA * * * "At 0713 EDT on April 3, 2016, EN #51846 provided notification of a Reactor Protection System actuation as revealed by the reactor trip breakers opening. Upon further investigation, it has been determined that the system actuated during maintenance activities due to a reactor trip signal caused by both trains of the Solid State Protection System (SSPS) being in test. This signal was not in response to actual plant conditions or parameters satisfying the requirements for initiation of the system and was therefore invalid. As such, the notification made by EN #51846 for a valid actuation of a specified system is hereby retracted. "In addition, an editorial change to the first sentence of the original notification description is hereby made. The first sentence is revised to read as follows: "At 2303 EDT on April 2, 2016, with the plant shut down and all control rods inserted into the reactor, while attempting to reset the reactor trip breakers to support outage activities (reset of the main turbine), the reactor trip breakers reopened." The NRC Resident Inspector will be notified. Notified the R4DO (Kellar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-04-03
51845 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-04-02 12:57 | 2016-04-02 18:27 | 2016-04-02 | INSULATOR FAILURE ON RESERVE AUXILIARY TRANSFORMER "At approximately 1257 [CDT] on 4/02/16, the Main Control Room received numerous annunciators that indicated a trip of the Reserve Auxiliary Transformer (RAT) Static VAR Compensator (SVC) that was caused by an insulator failure of the 'A' phase 345kV Circuit Switcher. As a result of the voltage transient, the Division 1 Fuel Building Ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no running VF fans, secondary containment differential pressure rose to slightly greater than 0 inches water gauge which exceeded the Technical Specification requirement of greater than 0.25 inches vacuum water gauge. The Control Room entered EOP-8, Secondary Containment Control. This event is being reported as a 'Condition that Could Have Prevented Fulfillment of a Safety Function' under 10CFR50.72(b)(3)(v)(C). Secondary Containment differential pressure was restored within Technical Specification requirements at 1300 [CDT] by starting the Standby Gas Treatment HVAC (VG) system. "The NRC Resident Inspector has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-04-02
51844 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2016-04-01 22:29 | 2016-04-02 03:50 | 2016-04-02 | OFFSITE NOTIFICATION DUE TO SODIUM HYPOCHLORITE SPILL ON SITE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "At approximately 2229 [MST] on April 1, 2016, Arizona Public Service Company completed an offsite notification to the Environmental Protection Agency's National Response Center to report a spill of approximately 8000 gallons of sodium hypochlorite (8% solution) in the vicinity of the Unit 3 cooling towers at the Palo Verde Nuclear Generating Station (PVNGS). Additional notifications were made to Arizona State and Maricopa County environmental authorities. "The Unit 3 cooling towers are located in the Security Owner Controlled Area at PVNGS and are outside of the protected area. The leak, which resulted from a failed hose on the main hypochlorite distribution header, was stopped by closing a valve to isolate the header. The immediate area has been barricaded. The quantity released exceeded the Reportable Quantity for sodium hypochlorite (RQ of 100 pounds) and was therefore reported. There was no impact to the operation of the PVNGS units or personnel onsite or offsite. "The NRC Senior Resident has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-04-02
51843 | 0 | CHRISTIANA CARE HEALTH SYSTEM |  |  |  |  | 2016-04-01 10:30 | 2016-04-01 13:57 | 2016-04-01 | MEDICAL EVENT - DOSE 75% OF PRESCRIBED DOSE A patient was receiving a Y-90 Therasphere treatment to the cancer patient's liver. During the infusion, there was resistance in the tubing. The tubing was disconnected, flushed with a saline solution, and then reattached to the transfer system. The company representative was present during the procedure. After the procedure, the residual activity in the waste was determined to be approximately 25 percent of the total activity. The intended dose to the treatment area was 125 Gy with the actual dose being 94.8 Gy. The prescribing physician and the patient will be notified. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-04-11
51842 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-03-31 | 2016-03-31 20:03 | 2016-03-31 | AGREEMENT STATE REPORT - STOLEN PORTABLE NUCLEAR GAUGE The following excerpted information was received from the State of Washington by email: "Event Narrative: The Washington Department of Health received a call today (3/31/2016) at noon from the RSO of the licensee, to report a stolen gauge from their conex unit at their SeaTac location. The RSO first noticed the missing gauge (the only one stored at this facility) when he went to check it out at 1030 PDT this morning. There was no indication of it being checked out by other users, and the RSO called the other users to make sure. The RSO also noticed the broken lock on the conex door. The licensee's contractor called police for this incident as well as other containers that had been broken into. More information to come. "Make/Model/Serial Number- Troxler 3440, SN 31182. Isotopes/Activity - Cesium 137/0.37 GBq and Americium 241 Beryllium/1.85 GBq" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-04-08
51841 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-03-24 | 2016-03-31 17:58 | 2016-03-31 | MEDICAL EVENT - DOSE MISADMINISTRATION The following information was received from the State of Colorado via email: "The Colorado Department of Public Health and Environment - Radioactive Materials Unit was notified on March 25, at [1041 MDT] of a misadministration that occurred on the evening of March 24, 2016. The licensee is Presbyterian St. Luke's Medical Center. A patient was given approximately 70% of the prescribed SIR-Spheres dose due to a clogged catheter. "The investigation is ongoing and a corrective action has not yet been determined." Colorado Report: CO16-M16-02 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-04-08
51840 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2016-03-31 03:24 | 2016-03-31 16:12 | 2016-03-31 | FITNESS FOR DUTY - PROHIBITIED ITEM IN THE PROTECTED AREA "On 3/31/2016 at approximately 0342 CDT, a worker within the Protected Area self-reported a can of beer had been packed in the worker's lunchbox. The worker reported after opening the can and taking a sip it was discovered to be a beer. This event is reportable under 10 CFR 26.719(b)(1). "The worker notified Security who immediately escorted the worker from the Protected Area and disposed of the beer. The worker is not an Operator or a Supervisor. The investigation of this event is in progress. "The public health and safety are not impacted. "The NRC Resident Inspector was notified." | 40 | 100 | 0 | 40 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2016-03-31
51839 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-03-30 | 2016-03-31 14:07 | 2016-03-31 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA STUCK SOURCE The following information was received from the State of Ohio by email: "On March 30, 2016 at approximately [1250 EDT] the Bureau of Environmental Health and Radiation Protection (BEHRP) received a phone call from licensee's RSO that an industrial radiography crew working on a water tank construction job in Groveport, Ohio had a source stuck in the guide tube of a QSA Model 880D camera and were unable to retrieve the back into the camera. The source in use was 75 Curies of Iridium-192. The incident occurred at approximately [1225 EDT]. The stuck source was discovered after a shot time had ended and the radiography crew attempted to crank the source back in to the camera. The radiography crew conducted surveys of the area and moved boundaries out 2 mR/hr or less. The cause of the stuck source was due to a magnetic stand becoming dislodged during radiography operations, which fell onto the guide tube, crimping it, and preventing retraction of the source." * * * UPDATE:FROM STEPHEN JAMES TO VINCE KLCO ON 3/31/2016 AT 1631 EDT VIA EMAIL * * * "A BEHRP inspector was immediately dispatched to the job-site and arrived there at approximately [1320 EDT]. The inspector met with the licensee's customer and reviewed the actions taken by the radiography crew to establish new barriers and prevent access to the site. The licensee's trained retrieval personnel dispatched to the site arrived a short time later. After a thorough review of the incident and work area, the licensee's response team was able to retrieve the source, which was completed at approximately [1600 EDT] that afternoon. The maximum dose received by any individual involved in the recovery effort was 50 mR. The camera and guide tube will be returned to manufacturer for repair. "QSA Global Camera,Serial Number-D8042; Source Serial Number-29222G. "Ohio Event- OH160002" Notified the R3DO (Pelke) and the NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-04-08
51838 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-03-31 06:03 | 2016-03-31 12:45 | 2016-03-31 | VALID ISOLATION SIGNAL DUE TO A HUMAN PERFORMANCE ERROR "On March 31, 2016 at 0603 [EDT], with Susquehanna Unit 1 in its 19th Refueling and Inspection Outage, Unit 1 received a valid isolation signal. Preliminary investigation indicates the isolation signal was the result of a human performance error. "The systems affected by the isolation signal responded as designed for the current shutdown plant conditions. "This isolation of multiple primary containment isolation systems is being reported under 10CFR50.72(b)(3)(iv)(A) and per the guidance of NUREG 1022, Rev. 3, section 3.2.6 as a system actuation." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-03-31
51837 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2016-03-30 17:15 | 2016-03-31 00:14 | 2016-03-31 | DEGRADED CONDITION DUE TO DISCOVERY OF PRESSURE BOUNDARY LEAKAGE "On March 30, 2016, at 1715 EDT, with the Unit shutdown and in Mode 6 for refueling, evidence of leakage was identified on a 3/4-inch flexible braided piping connection on Reactor Coolant Pump (RCP) 1-1, and this issue was determined to be reactor coolant system pressure boundary leakage. This flexible piping is for RCP 1-1 first stage seal cavity vent line, and is categorized as ASME Section III Class 2 piping. The leakage was identified due to the discovery of a small amount of boric acid (approximately 1/2 teaspoon) on the welded end connection of the flexible piping. No active leakage was identified at the time of discovery with the Reactor Coolant System depressurized and approximately 110 degrees F. "Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.13, 'RCS Operational Leakage,' does not apply in the current plant condition (Mode 6). The cause and resolution of the leakage are under evaluation. This event is reportable within 8 hours per 10 CFR 50.72(b)(3)(ii)(A). The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-03-31
51836 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-03-30 15:45 | 2016-03-30 20:45 | 2016-03-30 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE OUTSIDE REQUIRED TECHNICAL SPECIFICATION VALUE "At approximately 1545 CDT on 3/30/16, the Main Control Room received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) caused by a voltage transient on the 138 kV feed due to thunderstorms in the area. As a result of the voltage transient, the Division 1 Fuel Building ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no running VF fans, secondary containment differential pressure rose to slightly greater than 0 inches water gauge which exceeded the Technical Specification requirement of greater than 0.25 inches vacuum water gauge. The Control Room entered EOP-8, Secondary Containment Control. This event is being reported as a condition that could have prevented fulfillment of a safety function under 10 CFR 50.72(b)(3)(v)(C). Secondary Containment differential pressure was restored within Technical Specification requirements at 1550 CDT by starting the Standby Gas Treatment HVAC (VG) system. "The NRC Resident has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-03-30
51835 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-03-29 | 2016-03-30 17:18 | 2016-03-30 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received from the State of California via email: "On 03/29/16, the California Office of Emergency Services (OES) contacted the RHB [Radiation Health Branch] via an email to notify them of a damaged moisture/density gauge. The gauge was a Troxler gauge, Model 3440, S/N 38618 containing 9 mCi of Cs-137 and 44 mCi of Am-241. The gauge had been run over by an excavator while the operator was taking a reading along the side of the road where the incident occurred. Per the licensee, the Cs-137 source was in the shielded position (at the time of the incident readings were taken over a standard block for counts) when the gauge was damaged. The licensee stated that a 20 foot area was cordoned off until the gauge was removed. Fire Department personnel were at the scene. "Per the licensee, a Pacific Nuclear Technology (PNT) RSO arrived at the site, and confirmed a survey meter reading of 0.5 mRems at one meter from the gauge, which is considered normal for this type of gauge. It was also noted that the Cs-137 and Am-241 sources were intact. Survey of the area after removal of the gauge indicated background readings. The gauge was placed inside the transit cage and returned to the licensee's storage location. A leak test will be performed and the gauge will be disposed of in the near future. RHB will be following up on this incident." California 5010 Number: 032916 / Kleinfelder | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-04-07
51834 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-03-29 | 2016-03-30 16:12 | 2016-03-30 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the State of California via email: "Torrance Unified School District (TUSD) reported to the RHB [Radiation Health Branch] via email on March 29. 2016 regarding nine tritium exit signs the school district is unable to account for after construction at two of their sites (5 signs at South High School located at 4801 Pacific Coast Highway, Torrance, CA 90505 and 4 signs at North High School located at 3620 W 182nd St, Torrance, CA 90504). TUSD has notified the contracted construction company, Balfour Beatty Construction, regarding the incident and requested removal documentation for the 9 exit signs, which to date has not been provided. "The four Tritium Exit Signs from North High School located at 3620 W. 182nd St Torrance, CA 90504: ISOLITE 2040-50G-20-BK Expiration date 1/1/23 received around 2/27/02 11.5 Curies Tritium ISOLITE 2040-50G-20-BK Expiration date 1/1/23 received around 2/27/02 11.5 Curies Tritium ISOLITE 2040-50G-20-BK Expiration date 1/1/23 received around 2/27/02 11.5 Curies Tritium ISOLITE 2040-50G-20-BK Expiration date 1/1/23 received around 2/27/02 11.5 Curies Tritium "The five Tritium Exit Signs from South High School located at 4801 Pacific Coast Hwy Torrance, CA 90505: ISOLITE 2040-70G-20-BA Expiration date 4/20/22 Received around 1/15/02 11.5 Curies Tritium ISOLITE 2040-70G-20-BA Expiration date 4/20/22 Received around 1/15/02 11.5 Curies Tritium ISOLITE 2040-70G-20-BA Expiration date 4/01/22 Received around 1/15/02 11.5 Curies Tritium ISOLITE SLX-60-S-G-20-B Expiration date 4/01/25 Received around 3/22/05 Est. 11.5 Curies Tritium ISOLITE SLX-60-S-G-20-B Expiration date 4/01/25 Received around 3/22/05 Est. 11.5 Curies Tritium" California 5010 Number: 032916 / TUSD THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-04-07
51833 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-03-30 | 2016-03-30 16:05 | 2016-03-30 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following information was received from the State of Florida via email: "A Troxler Gauge was run over by heavy equipment at a construction site. The Type B container case was broken open exposing the source. [A Florida State] Inspector was sent to the scene to investigate." State of Florida Incident Number: FL16-047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-04-07
51832 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-03-29 | 2016-03-30 15:35 | 2016-03-30 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received from the State of New York via facsimile: "The Licensee's Radiation Safety Officer called on March 29, 2016 to report that during the administration of Y90 to the liver of patient in the Interventional Radiology suite earlier in the day, only 3.9 mCi of the intended 11.7 mCi was administered due to a clogged catheter. [NY State Department of Health] will update after receiving report from the licensee." NY State Incident No.:1136 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2016-04-07
51831 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2016-03-29 17:50 | 2016-03-30 11:58 | 2016-03-30 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed, licensee supervisory employee had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been removed. The licensee notified the NRC Region I. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | VT | POW |  | 26.719 |  |  |  | 0 | 2016-03-30
51830 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-03-29 22:56 | 2016-03-30 02:13 | 2016-03-30 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "On March 29, 2016 at 2256 [EDT], Secondary Containment Zone 2 (Unit 2 Reactor Building) differential pressure lowered to 0.0 [inches] WG [water gauge] due to a failed closed discharge damper on the in service Zone 2 exhaust fan. Required differential pressure per SR 3.6.4.1.1 could not be maintained. Zone 2 ventilation was restored by starting the standby Zone 2 exhaust fan. Zone 2 differential pressure recovered to [greater than] 0.25 [inches] WG at 2321 hours. Zone 3 (Unit 1&2 Reactor Buildings) ventilation remained in service and stable. Zone 1(Unit 1 Reactor Building) ventilation remained in service however it is not required in this mode of Operation. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-03-30
51829 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-03-29 16:45 | 2016-03-29 17:04 | 2016-03-29 | BAFFLE BOLT INDICATIONS IDENTIFIED DURING INSERVICE INSPECTION "This is a non-emergency report. Indian Point Unit 2 is shut down for a scheduled refueling outage and is performing an industry required MRP-227-A inspection of the reactor vessel internals. During this inspection, Entergy identified baffle/former bolts with either visual anomalies or ultrasonic indications. All vessel internal examinations have been successfully completed with no anomalies other than the baffle/former bolts. Entergy will be developing a repair plan that will be implemented prior to startup. The unit is in a safe and stable condition. No leakage was detected as a result of this condition. "On March 29, 2016, this event was determined to be reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B), since the as-found conditions were not previously analyzed. "Entergy is planning a press release to communicate this condition to our stakeholders. Therefore this is also being reported under 10 CFR 50.72(b)(2)(xi) since a news release is planned. "The NRC Resident Inspector has been informed." The licensee will notify State and local government agencies as appropriate. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | UNANALYZED CONDITION |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2016-03-29
51828 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-03-28 19:00 | 2016-03-29 16:31 | 2016-04-19 | LOSS OF POWER TO METEOROLOGICAL TOWER "At approximately 1900 EDT on March 28, 2016, an unplanned loss of retail power to the McGuire Meteorological tower occurred. This loss of power impacted communication between the Meteorological tower and the control room, which resulted in a major loss of emergency assessment capability. Compensatory measures existed within the site's emergency planning procedures to obtain meteorological data from the National Weather Service. Meteorological information could have been provided via the emergency notification system to the NRC operations center. "Power was restored at 2245 EDT on March 28, 2016. "The NRC Resident Inspector has been notified. There was no impact to the public." * * * RETRACTION AT 1423 EDT ON 4/19/2016 FROM SCOTT SLIETER TO MARK ABRAMOVITZ * * * "This notification is being made to retract event EN 51828 that was reported March 29, 2016. Based on further investigation, Emergency Plan Implementing Procedures provide acceptable alternative methods to perform emergency assessment that are in addition to the control room indications from the meteorological tower. Furthermore, it was determined that the meteorological tower data was valid and available in the control room during the applicable period. It was therefore determined that no actual or potential major loss of emergency assessment capability existed per 10CFR50.72(b)(3)(xiii). This is consistent with NUREG 1022, rev 3, supplement 1 and NEI 13-01, rev 0. The NRC Resident Inspector has been notified of the retraction." Notified the R2DO (McCoy). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-03-29
51827 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2016-03-29 11:23 | 2016-03-29 14:06 | 2016-03-29 | REACTOR SCRAM DUE TO TURBINE TRIP "A Reactor Scram occurred at 1123 CDT on 03/29/2016 from 35% CTP [core thermal power]. The cause of the Scram appears to be a Turbine Generator trip. The station's procedures, '05-S-01-EP-2 RPV [Reactor Pressure Vessel] Control, 05-1-02-I-1 Reactor Scram ONEP [Off Normal Event Procedure] and 05-1-02-l-2 Turbine Generator Trip ONEP,' were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF [engineered safety feature] power occurred. No ECCS [emergency core cooling systems] initiation signals were reached and no ESF or Diesel Generator initiations occurred. All control rods fully inserted. MSIVs [main steam isolation valves] remained open, no SRVs [safety relief valves] lifted, and no containment isolation signals were generated. "Currently, reactor water level is being maintained by the Condensate and Feedwater System in normal band and reactor pressure and temperature are being maintained by the Reactor Water Cleanup System. The main condenser is available. There are no challenges to Primary or Secondary Containment at this time. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 35 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-03-29
51826 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2016-03-28 13:22 | 2016-03-28 19:44 | 2016-03-28 | MANUAL SCRAM FOLLOWING LOSS OF REACTOR CLOSED COOLING "At 1322 PDT on Monday, March 28, 2016, Columbia Generating Station was manually scrammed from 100% thermal power due to the loss of Reactor Closed Cooling (RCC). Manual scram of the unit is procedurally required upon loss of RCC. The cause of the loss of RCC is being investigated. "Regulation 10 CFR 50.72(b)(2)(iv)(B) requires reporting within 4 hours of any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical. "All control rods were fully inserted. Valve RWCU-V-4 automatically closed upon high water temperature due to loss of RCC flow. No other safety system actuations were reported. All systems operated as expected. Reactor decay heat is being removed via bypass valves to the Main Condenser. The station is in normal shutdown electrical lineup. "The NRC Resident Inspector has been informed." No safety/relief valves lifted and no emergency core cooling systems injected following the reactor scram. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-03-28
51825 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2016-03-26 | 2016-03-28 15:58 | 2016-03-29 | AGREEMENT STATE REPORT - MISSING SHIPMENT OF RADIOACTIVE MATERIALS The following information was received from the Commonwealth of Massachusetts via email: "The licensee (QSA Global, Inc.) made telephone notification at 1156 EDT on March 28, 2016 to the Agency (Massachusetts Radiation Control Program) that the licensee was notified by the carrier (Lufthansa Cargo Airlines) on the same day at 1050 EDT that a shipment of one package for export containing 73.1712 TBq (1,977.6 curies) of iridium-192 shipped from QSA Global, Inc. (Burlington, Massachusetts) on March 23, 2016 to a QSA Division in Prague, Czech Republic was missing and that the licensee was working with carrier to find the package containing the missing materials. The licensee additionally reports that its QSA Division in Prague is closed for business today, March 28, 2016. "After initial telephone notification made by the licensee to the Agency, the licensee forwarded to the Agency tracking information from the carrier indicating that the missing package was tracked by the carrier to have been shipped from New York's JFK Airport (airport station JFK) through Frankfort, Germany airport (airport station FRA) and had arrived at the Prague, Czech Republic airport (airport station PRG) on March 26, 2016. According to carrier tracking, the package was not recorded as actually being received from the flight arriving to PRG on March 26, 2016 and then declared missing by the carrier on same day. Additional information received by the licensee indicated that upon arrival to FRA, the pallet that licensee's shipment was built on was offloaded from the aircraft at FRA and taken to a break down area and the shipment was re-built on a different pallet for movement on the flight from FRA to PRG. "The package is described as a Type B(U) package, RQ UN2916, containing 23 (twenty-three) total QSA Global, Inc. Model 87501 radiography sources, each source special form. "The reporting requirement is immediate and is of 105 CMR 120.281(A)(1), missing licensed radioactive materials in aggregate quantity equal to or greater than 1,000 times quantity specified in 105 CMR 120.297, Appendix C. "The Agency made notification to FBI. "The Agency considers this event to be open." Notified DHS (SWO) and Department of State Ops Center. * * * UPDATE FROM CHARLES ELLARS WITH QSA GLOBAL TO JOHN SHOEMAKER AT 0715 EDT ON 3/29/16 * * * "Notified by QSA Global, via email, at 0715 EDT 03/29/2016, of the following; Please be advised that QSA Global has been notified officially by Lufthansa that the shipment was located and is currently in Prague, Czech Rep. Arrangements are being made for final delivery. Charles Ellars, RSO QSA. Global, Inc." Notified R1DO (Dwyer), NMSS (Collins and McIntosh), IRD (Gott), ILTAB (Hahn), OIP (Mamish), and DHS (SWO), Department of State OPS Center, and NMSS Events Notification via email. * * * UPDATE FROM EDWARD SALOMON TO RICHARD SMITH AT 1027 EDT ON 3/29/2016 * * * "The Agency (Massachusetts Radiation Control Program) received an update at 0715 EDT on Tuesday, 3/29/2016, from the licensee (QSA Global). The licensee stated that they were officially notified by Lufthansa Cargo Airlines that the Iridium-192 missing material (Shipment) had been located and is currently in Prague, Czech Republic with arrangements being made for final delivery. "The Agency made this updated notification to the FBI. No further Agency action will be taken as a result of this event. "The Agency considers this event CLOSED." Notified R1DO (Dwyer), and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2016-04-05
51824 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-03-28 10:48 | 2016-03-28 15:43 | 2016-03-28 | FITNESS-FOR-DUTY REPORT INVOLVING A LICENSEE SUPERVISORY EMPLOYEE A non-licensed, licensee supervisory employee had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2016-03-28
51823 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2016-03-23 | 2016-03-25 13:15 | 2016-03-25 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER STUCK IN CLOSED POSITION The following information was provided by the State of South Carolina via email: "The licensee [International Paper] provided notification [to the SC Department of Health and Environmental Control] of a stuck shutter on a Berthold Model LB7440 fixed gauging device. The shutter is stuck in the closed position. The gauging device contains 15 mCi of Cs-137. A licensed contractor has been contacted and will proceed with corrective maintenance on the shutter mechanism within the next 30 days. Updates to this event will be made through the NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2016-04-04
51822 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-03-24 | 2016-03-24 16:13 | 2016-03-24 | AGREEMENT STATE REPORT - FIXED INDUSTRIAL GAUGE SHUTTER BROKEN The following information was received via e-mail: "On Thursday, March 24, 2016, it was reported to the Department [Georgia Department of Radioactive Materials] by Shaw Industries Group, Inc., Plant SI in Chickamauga, GA that the shutter on a fixed industrial gauge is broken. The gauge was shielded, removed from its fixed location, and transferred to a secure storage location. The manufacturer has been contacted and will repair the gauge. A complaint has been opened in CTS [ Complaint Tracking System] and our office [Georgia Department of Radioactive Materials] has an ongoing investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2016-04-01
51821 | 0 | CASTLEROCK GEOTECHNICAL ENGINEERING |  |  |  |  | 2016-03-23 14:45 | 2016-03-24 11:10 | 2016-05-18 | TROXLER DENSITY GAUGE DAMAGED BY SOIL COMPACTOR While preparing to take a soil density measurement, a soil compactor operator backed up and ran over the Troxler density gauge, damaging the casing of the density gauge. The gauge was examined and inspected and the top of the case was cracked, however, the plunger and source appeared to be intact. The gauge was isolated and returned to its protective case. The gauge was subsequently sent for leak testing to Qual-Tech in Idaho Falls. The gauge has been quarantined and isolated pending the results of the leak testing. Density gauge information: Troxler model 3430 containing Am-241 - 40 milliCuries and Cs-137 - 8 milliCuries * * * UPDATE AT 1205 EDT ON 05/18/16 FROM ANDREW TILSKALUS TO S. SANDIN * * * Qual-Tech replaced the top cover and leak tested the gauge satisfactorily. The gauge was returned to the licensee and placed back in service. Notified R4DO (Miller) and NMSS Events Notifications via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-03-24
51820 | 0 | PALISADES | 1 |  |  | [1] CE | 2016-03-24 02:11 | 2016-03-24 08:58 | 2016-03-24 | CONTROL ROOM VENTILATION DECLARED INOPERABLE "At approximately 0211 [EDT], on March 24, 2016, both control room ventilation filtration trains were declared inoperable in accordance with Technical Specification 3.7.10, Condition B, due to a control room boundary door not being fully closed. Following routine security rounds, the door was unable to be fully closed due to the door's locking bolts not retracting back into the door body, causing interference between the door and door frame. "Mitigating actions have been implemented that ensure control room envelope (CRE) occupant radiological exposures will not exceed limits, and CRE occupants are protected from chemical and smoke hazards. Repairs to the door are currently in progress. "Technical Specification 3.7.10 allows control room boundary doors to be opened intermittently, under administrative control for preplanned activities, provided the doors can be rapidly restored to the design condition. Previous evaluations of the door not being fully closed for a limited time concluded no loss of safety function had existed. "This condition had no impact on the health and safety of the public. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-03-24
51819 | 0 | PALISADES | 1 |  |  | [1] CE | 2016-03-23 18:30 | 2016-03-23 19:28 | 2016-03-23 | POTENTIAL SAFEGUARDS SYSTEM DEGRADATION DISCOVERED Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-03-23
51818 | 0 | BOTSFORD CANCER CENTER |  |  |  |  | 2016-03-22 | 2016-03-23 16:12 | 2016-03-23 | BRACHYTHERAPY EQUIPMENT MALFUNCTION On 3/22/16, a medical event occurred from a high dose rate brachytherapy treatment of the prostate. After the first catheter was delivered, the treatment console reported an error. The medical physicist went inside the treatment room with the survey meter to verify that the source retracted and the connections were fine. The vendor was called out to the facility, and parts had to be replaced. The treatment was stopped, and the patient was notified. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-03-31
51817 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-03-22 19:34 | 2016-03-22 23:33 | 2016-03-22 | DEGRADED CONDITION FOUND IN REACTOR COOLANT SYSTEM PIPING "On Tuesday, March 22, 2016, while performing planned inspections of Unit 1 Reactor Coolant System piping welds, a flaw indication was identified on a 3 inch Charging Line connection to the Reactor Coolant System piping. "NDE [Non-Destructive Evaluation] results showed a change in the flaw since the previous outage inspection and the condition is now determined as not meeting the acceptance criteria specified in ASME Code Section XI. As such, this indication is reportable under 10 CFR 50.72(b)(3)(ii)(A) as a degraded condition. "An action plan is being developed. There is no impact on current Unit 1 refueling operations. This condition and the action plan have no impact to the health and safety of the public or employees. "The NRC Resident [Inspector] has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-03-22
51816 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2016-02-20 | 2016-03-22 15:11 | 2016-03-22 | PART 21 REPORT - DEFECTIVE FUSES The following information is a synopsis of information received via E-mail: "On February 20, 2016 United Controls International issued a Return Material Authorization (RMA) request to First Energy - Perry Nuclear Power Plant. The RMA was issued to request the return of general purpose fuses of part number OT15 that were provided to First Energy - Perry Nuclear Power Plant under purchase order 45225736. The customer identified a fuse that had intermittent electrical continuity during resistance checks. The customer performed an evaluation which included dissection of the subject fuse and the cause of the issue was identified as being due to a lack of or inadequate solder connection of the fuse element to the fuse ferrules. "If you have any questions or wish to discuss this matter or this report, please contact: Wesley Hickle Engineering Manager whickle@unitedcontrols.com 770-496-1406 x 165" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-03-22
51815 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-03-22 11:31 | 2016-03-22 13:59 | 2016-03-22 | WATTS BAR AUTOMATIC REACTOR TRIP "On March 22, 2016, at 1131 EDT, the Watts Bar Nuclear Plant Unit 1 (WBN1) reactor tripped due to the actuation of the Over Temperature Delta Temperature bistables. Concurrent with the reactor trip, the Auxiliary Feedwater (AFW) system actuated. All control rods inserted upon the reactor trip. Engineered Safety Function systems functioned as expected. "WBN1 is currently stable in Mode 3. The Reactor Coolant system is being maintained at normal operating pressure and no-load temperature with decay heat removal via the Main Condenser steam dumps and the AFW system. The station is in a normal shutdown electrical alignment. Watts Bar Unit 2 is in mode 4 preparing for power ascension testing and was unaffected by the WBN1 event. "The cause of the event is under investigation. This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-03-22
51814 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2016-03-22 09:14 | 2016-03-22 12:43 | 2016-03-22 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR TESTED POSITIVE DURING RANDOM TESTING "A non-licensed supervisor tested positive for alcohol during a random fitness for duty test. The individual's access to the facility has been denied. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2016-03-22
51813 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-01-22 12:00 | 2016-03-22 11:07 | 2016-03-22 | AGREEMENT STATE REPORT - CONTAMINATION FOUND ON SHIPMENT The following report was excerpted from an Oklahoma Department of Environmental Quality via email: "On January 22, 2016 the RSO [Radiation Safety Officer] reported that a package received by the University of Oklahoma Health Science Center pharmacy (OK-03176-04MD) was found to have 2,118,858 cpm of removable contamination. The outside of the package was surveyed at 30 mR/hr, the reading at 1 meter was 0.12 mR/hr. The contaminant was identified as Tc-99m and was confined to the outside of the package. The package contained a number of empty unit dose syringes in lead pigs and had been returned from HCA Health Services of Oklahoma which administers the University of Oklahoma Medical Center. The package was transported by the pharmacy." Refer to NRC Event #51661. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-03-30
51812 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2016-03-22 01:04 | 2016-03-22 06:38 | 2016-03-22 | HIGH PRESSURE COOLANT INJECTION (HPCI) OIL LEAK "On 3/22/2016 during performance of HPCI FLOW CONTROL SYSTEM DYNAMIC TEST PROCEDURE, an oil leak was discovered on the hydraulic control oil piping. HPCI had previously been declared INOPERABLE due to planned maintenance, however as a result of the oil leak HPCI remains INOPERABLE. This oil leak would have cause HPCI to be declared INOPERABLE had it been found outside of the planned maintenance. The plant remains at 100% power with no challenges to the health and safety of the public." HPCI is in a 14 day technical specification to repair the oil leak. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-03-22
51811 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-03-21 12:10 | 2016-03-21 17:28 | 2016-03-21 | OFFSITE MEDICAL TREATMENT REQUIRED "At 1152 EDT, a contractor employee working in the Containment Building in a potentially contaminated area was found passed out and unresponsive. At 1210 EDT, the individual was transported to Carolinas Medical Center, Charlotte, NC. Radiation Protection had not yet fully determined if the individual was contaminated. At 1300 EDT, Radiation Protection determined the individual was not contaminated. The determination was made after arrival to the hospital. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2016-03-21
51810 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2016-01-22 | 2016-03-21 14:02 | 2016-03-21 | PART 21 - PLUG/STEM ASSEMBLY The following is a summary of an email provided by Fisher Controls International: "Items subject to this Fisher Information Notice (FIN) were provided to Tennessee Valley Authority (TVA) Watts Bar Nuclear Plant per TVA Order 702507 (Fisher Order Number 025-N230331922). Specifically, this FIN applies to a plug/stem assembly that Fisher Controls International LLC (Fisher) supplied to TVA, item number 15A2560X072 (Equipment). In this equipment, the essential-to-function groove pin was erroneously provided as commercial-grade. "Fisher Information Notice: FIN 2016-03 "Fisher requests that the recipient of this FIN review it and take appropriate action in accordance with 10 CFR 21. If there are any technical questionsú or concerns, please contact: Ben Ahrens Quality Manager Emerson Process Management Fisher Controls International LLC 301 South First Avenue Marshalltown, lA 50158 Phone: (641) 754-2249 Benjamin.ahrens@emerson.com" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [10 empty] | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-03-21
51809 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2016-03-20 21:54 | 2016-03-20 23:51 | 2016-03-21 | TECHNICAL SPECIFICATION (TS) REQUIRED SHUTDOWN DUE TO PRESSURE BOUNDARY LEAKAGE "During a planned Unit 1 shutdown for a refueling outage, a 0.5 gpm 'pressure boundary leak' was identified on a 1 inch pipe connected to the '1A' RHR-Shutdown Cooling return line by the drywell leak inspection team during a drywell inspection at approximately 15% power. The leak exceeded the TS 3.4.3.2 'Operational Leakage' LCO of no pressure boundary leakage. TS action 'a' was entered which requires to be in at least Hot Shutdown within 12 hours and Cold Shutdown within the next 24 hours. Therefore, the event is reportable within 4 hours per 10CFR50.72(b)(2)(i) due to the initiation of a plant shutdown required by the plant's TS. "The event is also reportable within 8 hours per 10CFR50.72(b)(3)(ii) due to an event that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. "TS 1.28 defines Pressure Boundary Leakage as leakage through a nonisolable fault in a reactor coolant system component body, pipe wall or vessel wall; therefore, the leak is a 'pressure boundary leak' as defined in TS." The licensee notified the NRC resident Inspector. | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2016-03-21
51808 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2016-03-19 17:10 | 2016-03-19 22:51 | 2016-03-22 | UNANALYZED CONDITION THAT COULD CHALLENGE RHR EQUIPMENT DURING FLOOD CONDITIONS "Two (2) potentially degraded flood barriers at penetrations 0073-01-0034 and 0073-01-0063 were identified in the area between the Unit 1 Turbine Building and Auxiliary Building. The deficient barriers are a 'blockout section' of the floor designed to house multiple penetrations that transition from the Turbine Building to the Auxiliary Building. Attempts have been made to investigate the status of the flood barrier with no definitive results. Investigations and additional evaluations are continuing, however, it is currently unknown if the aggregate of these two flood barriers could potentially overwhelm and flood the Auxiliary Building which would challenge equipment necessary to remove residual heat and constitute an unanalyzed condition. "Based on current conditions (i.e., no forecast flooding conditions), this condition does not present an immediate safety concern. "This condition has been determined to be reportable per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(B). This condition is a non-emergency condition. This condition has been entered into the Corrective Action Program. "Compensatory measures have been prepared to allow placement of a seal over the identified deficient barriers. If required these seals can be installed well in advance of forecast flood conditions. Permanent repairs are currently being designed for installation." The NRC Resident Inspector has been notified. * * * UPDATE AT 0044 EDT ON 3/22/2016 FROM KEITH LEDBETTER TO MARK ABRAMOVITZ * * * "This is an 8 hour non-emergency supplemental notification to previously issued Event Notification number 51808. In EN 51808, two non-functional barriers were identified and reported, and during an extent of condition review, a third barrier has been identified that does not conform to expected flood barrier standards "A potentially degraded flood barrier at 'blockout' penetration 0073-01-9018 was identified in the area between the Unit 1 Turbine Building and Auxiliary Building. The deficient barrier is a 'blockout section' of the floor designed to house multiple penetrations that transition from the Turbine Building to the Auxiliary Building. Attempts have been made to investigate the status of the flood barrier with no definitive results. Investigations and additional evaluations are continuing; however, it is currently unknown if this flood barrier could potentially be overwhelmed and flood the Auxiliary Building which would challenge equipment necessary to remove residual heat and constitute an unanalyzed condition. "Based on current conditions (i.e., no forecast flooding conditions), this condition does not present an immediate safety concern. "This condition has been determined to be reportable per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(B). This condition is a non-emergency condition. This condition has been entered into the Corrective Action Program. "Compensatory measures have been prepared to allow placement of a seal over the identified deficient barrier. If required this seal can be installed well in advance of forecast flood conditions. Permanent repairs are currently being designed for installation." The NRC Resident Inspector was notified earlier in the evening that this event would be updated. Notified the R4DO (Haire). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2016-03-19
51807 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2016-03-18 11:28 | 2016-03-18 18:43 | 2016-05-16 | SHUTDOWN COOLING PIPE VOID "During a scheduled surveillance test on 3/18/2016 at 1128 [CDT], Fort Calhoun ultrasonic testing technicians discovered a void on the common shutdown cooling heat exchanger discharge piping. This piping is normally isolated during power operation, and the void does not adversely affect the Containment Spray function, Low Pressure Safety Injection function, or High Pressure Safety Injection function. "This isolated piping with the void is placed in service only during shutdown cooling operation. The fluid height measured was 10.8 inches, compared to the required height of 11.7 inches for the surveillance test. The void could potentially complicate the initiation of shutdown cooling in the required mode of operation. "This piping was last tested satisfactory on 12/31/2015. The source of the void is still under investigation. "Fort Calhoun maintenance was successful in venting the void on 3/18/2016 at 1704 CDT." The NRC Resident Inspector has been notified. * * * RETRACTION AT 1701 EDT ON 05/16/16 FROM JAKE WALKER TO KARL DIEDERICH * * * "Following the 8-hour 10 CFR 50.72 notification made on 3/18/16 (EN 51807), further engineering analysis has determined that the ensuing water hammer transient would not have prevented the shutdown cooling system from performing its required safety functions. Specifically, it was found that the resulting system pressure transient would not cause any relief valves to lift and that piping and supports would not be significantly challenged. "Therefore, the common shutdown cooling heat exchanger discharge piping remained operable by the detailed analysis. As such, the safety function was not lost and the event notification is being retracted as it is not reportable pursuant to 10 CFR 50.72(b)(3)(v)(B)." Notified the R4DO (G Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2016-03-18
51806 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-03-18 09:37 | 2016-03-18 16:37 | 2016-03-18 | FITNESS FOR DUTY - CONFIRMED POSITIVE TEST FOR ALCOHOL "In accordance with 10 CFR 26.719(b)(2)(ii), this notification reports a non-licensed contracted employee supervisor had a confirmed positive for alcohol during a random fitness for duty test. The employee's access to the plant has been suspended. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2016-03-18
51805 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-03-17 | 2016-03-18 14:48 | 2016-03-18 | AGREEMENT STATE REPORT - ABANDONED RADIUM 226 SOURCE FOUND The following was received from Pennsylvania via email: "Lost or abandoned licensed material in a quantity greater than or equal to 1000 times the Appendix C quantities in part 20, reportable as per 10 CFR 20.2201(a)(1)(i). "A new owner of a facility in Collingdale, Pennsylvania came across a locked room that contained an old lead pig, stamped with a label stating radium-226, 100 mg. The owner contacted Ecology Services, a local radioactive waste management company, who confirmed a dose rate outside the pig. Ecology Services called the Department [PA Bureau of Radiation Protection]. "The previous occupant of this facility, Universal Technical Equipment Inc., was licensed by the Department (PA-0187) to possess up to 110 mCi of Ra-226 sealed sources and contracted the removal of the radium source. The Certificate of Disposition documentation was submitted to the Department for license termination. The license was ultimately terminated on January 14, 2015. "[PA Bureau of Radiation Protection] Southeast regional inspectors visited the facility today, March 18, 2016, and verified there is a source within the locked pig. A smear test revealed no leakage was detected on the outside of the pig. The source remains in a secured and locked location. More information will be provided upon receipt." PA incident # PA160011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-03-28
51804 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-03-15 | 2016-03-18 11:43 | 2016-03-18 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following was received from Pennsylvania via email: "On March 15, 2016 a written directive for 18.1 mCi of yttrium-90 (Y-90) was written by the authorized user (AU) and referring physician for this procedure. The entire content of the syringe was injected and the residual activity in the vial measured 13.3 mCi, or 73.5% of the prescribed dose. No harm is expected to the patient. "A different AU wrote the initial written directive based on incorrect dose calculation. The discrepancy was not realized until after the administration was completed. "A reactive inspection is planned by the Department [PA Bureau of Radiation Protection]. More information will be provided upon receipt." PA Incident # PA160010 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-03-28
51803 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-03-02 12:30 | 2016-03-18 10:44 | 2016-03-18 | AGREEMENT STATE - RADIOGRAPHY CAMERA SOURCE UNABLE TO BE RETRACTED The following was received from the State of Louisiana via email: "On March 17, 2016, Acuren Inspection, Inc. notified LDEQ [Louisiana Department of Environmental Quality] during a telephone discussion, about a source retrieval on March 2, 2016, but did not use our 24-hour hotline number for these types of notifications within the regulatory guidelines prescribe time limits of 24 hours. The event occurred at Exxon Mobil Baton Rouge, 4045 Scenic Hwy., Baton Rouge, LA. "The source could not be retracted due to a crimped guide tube. The total amount of Ir-192 for the industrial radiography camera was 64.7 Ci. The camera was: "QSA Global: 880D, S/N: D4022, Curies: 64.7, Source S/N: 27719G." Louisiana Event Report Identification Number: LA160006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-03-28
51802 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-03-16 07:30 | 2016-03-18 09:12 | 2016-03-18 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE DAMAGED ON A CONSTRUCTION SITE The following report was received from the State of Ohio via email: "At approximately 1315 [EDT] on 3/16/16, ODH [Ohio Department of Health] was notified that a licensee had a nuclear density gauge run over on a construction site. The incident occurred at about 0730 that morning. The licensee's technician instructed site personnel to stay 20 feet from the damaged gauge and contacted the RSO [Radiation Safety Officer] via telephone. The RSO arrived on site at approximately 0810 and determined that both sources were intact within the gauge housing. Readings attained around the damaged gauge with a radiation monitor and indicated normal levels. The gauge was placed back in the case and additional readings were [obtained] from the soil at the accident location with negative results. The gauge was then transported to a licensed service provider for inspection and storage. The service provider inspected the gauge and performed a leak test which indicated that the sources were not leaking. "Investigation is ongoing." Sealed Source Gauge. Manufacturer: QSA GLOBAL, Model Number: X.2084, Serial Number: A-7879, 0.050 Ci Am/Be-241 source and Model Number: X.8, Serial Number: C-7879, 0.010 Ci Cs-137 source. Ohio: Item Number: OH160001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2016-03-28
51800 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2016-03-17 15:15 | 2016-03-17 23:15 | 2016-03-17 | VALID ENGINEERED SAFETY FEATURE SYSTEM ACTUATION DUE TO LIGHTNING STRIKE "At 1515 [CDT] on March 17th 2016, Grand Gulf Nuclear Station received a valid actuation signal of the Division 2 Engineered Safety Feature (ESF) Load Shedding and Sequencing system. The actuation signal was most likely caused by a lightning strike to the offsite power source supplying this ESF bus. This caused a loss of the in service shutdown cooling system and associated system actuations. "Grand Gulf Nuclear Station (GGNS) was in Mode 5 at 85 [degrees] F coolant temperature. Reactor Cavity was flooded to High Water Level with a time to reach 200 [degrees] F of 7.5hrs. GGNS is conducting a planned refuel outage with core alterations in progress. Systems were aligned as follows: "Division 2 Diesel Generator was OPERABLE and the associated ESF bus aligned to transformer ESF12 (115KV Port Gibson offsite feeder). Residual Heat Removal (RHR) system 'B' was in service in shutdown cooling being supplied from this ESF bus (16AB) with Alternate Decay Heat Removal available as a backup. "Division 3 Diesel Generator was unavailable due to planned maintenance on support systems. The associated ESF bus was also aligned to transformer ESF12 (115KV Port Gibson offsite feeder). "Division 1 Diesel Generator was available and the associated ESF bus aligned to the transformer ESF 11 (Switchyard offsite power feeders Baxter-Wilson and Franklin). Power was never lost to this bus. RHR 'A' and Low Pressure Core Spray (LPCS) were not available due to planned maintenance (tagged out of service). "ESF 21 Transformer was out of service for planned maintenance. "A suspected lightning strike caused a momentary perturbation in power in the 115KV Port Gibson line causing the Division 2 Load Shedding and Sequencing (LSS) system to actuate. This actuation caused a loss of Residual Heat Removal system 'B' due to being shed (expected). The Division 2 Diesel Generator started and tied onto the bus as expected, restoring power in 7 seconds. Shutdown cooling was restored at 1518 [CDT] and was out of service for 3 mins 13 sec. Reactor coolant and spent fuel pool temperatures remained at 85 [degrees] F throughout this scenario. Core Alterations were suspended and fuel placed in its designated location per the approved movement plan. Division 3 systems; High Pressure Core Spray, Standby Service Water System 'C', and Division 3 Diesel Generator were tagged out of service for planned maintenance. Division 3 Diesel Generator received a valid actuation signal but did not start due to being out of service. The Division 3 bus was restored manually to ESF 11. "All safety systems operated as expected for the loss of power to ESF 12 and Division 2 LSS actuation. "This is being reported under: 1. 10CFR50.72(b)(3)(iv)(A)-Specified system actuation; Division 2 LSS and Division 3 Diesel Generator start logic. 2. 10CFR50.72(b)(3)(v)(B)-RHR Capability; Loss of shutdown cooling." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | POT RHR INOP |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2016-03-17
51799 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-03-15 | 2016-03-17 17:28 | 2016-03-17 | AGREEMENT STATE REPORT - RADIOACTIVE SOURCE SHIPMENT IN EXCESS OF LICENSED QUANTITY The following was received from Louisiana via email: "On 03/16/2016, the RSO for A&O [Alpha Omega] called in a report of a HDR [high does rate brachytherapy] source being shipped to Texas Oncology PA (TOP) in excess of licensed quantities. The source was 12.8 Ci Ir-192 source intended as a replacement source for the Texas Oncology PA Center 3550 Northeast Loop 285, Paris, TX 75460. License # L04664, Amendment #28, Expiration date: February 28, 2025. "[The RSO] was enroute to the facility to return the 12.8 Ci Ir-192 source and replace it with an additional 11.2 Ci Ir-192 source. He stated that the 12.8 Ci source was being retrieved and placed in a storage pig/container by the Service Engineer until it could be packaged and returned by common carrier to A&O 03/16/2016. Their intent was to install the 11.2 Ci source so the TOP facility could receive the source and resume patient care. "A&O is a source supplier for Elekta HDR units. Elekta notifies A&O when sources should be shipped/supplied their licensees. The error was the wrong source was inadvertently shipped to TOP. The source received by TOP exceeded the licensed activity limit. The sources were Elekta Model 105.002s. The source S/N16-0505 12.8 Ci of Ir-192 was shipped when the source S/N 16-0504 11.8 Ci of Ir-192 should have been shipped. When TOP received the 12.8 Ci source, they knew it was too 'HOT' to treat patients. They called A&O at [1700 EDT] on 03/15/2016 to report the error. "The incorrect source, 12.8 Ci of Ir-192 was returned to A&O by common carrier" A&O explained that the mix-up was caused by reference numbers that were switched after the sources were calibrated. Louisiana incident # LA-160005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-03-25
51798 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-03-15 | 2016-03-17 17:33 | 2016-03-17 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following was received from Florida via email: "On Tuesday March 15, 2016, a patient being treated for skin cancer on the right side of his mandible using a Valencia applicator was treated using the plan time from another patient who is being treated for the left leg also using a Valencia applicator. The short fall difference in time was 8.2 seconds, meaning that the patient treated for the right mandible was given 3.2% less radiation than what was correctly calculated for. "As a plan of action, the patient as well as the attending physician will be notified of the occurrence, and a 'time-out' policy will be implemented for all HDR [high does rate brachytherapy] treatments to ensure that the correct patient, date of birth, patient number, plan number, date of the plan, and treatment location are being treated prior to the actual treatments. A policy will be formally drafted to this effect and placed into the departmental policy and procedures manual. "[The prescribing physician] will decide whether or not to make up the short fall in the treatment dose after consultation with the patient." Florida Incident # FL16-043 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-03-25
51797 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2016-03-16 | 2016-03-17 16:54 | 2016-03-17 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED The following report was received from the State of Maryland via email: "March 16, 2016 about 1600 [EDT]: [The GeoConcepts field representative] notified [the licensee's Radiation Safety Officer] (RSO) of the incident and that the gauge had been damaged. [The field representative] informed [the RSO] that a John Deere Dozer 700 had back up over the gauge. [The field representative], had just completed taking a compaction and moisture test. When the site foreman called to [the field representative] to ask about failing test results, [the field representative] placed the trigger lock back onto the gauge and walked over to the site foreman who was approximately 8-10 feet from where the gauge was located. The John Deere Dozer 700 operator was grading soil and placing it onto an onsite stockpile. The John Deere Dozer 700 operator proceeded to back up, in the vicinity of the gauge. When [the field representative] noticed the operator in close proximity to the gauge, he began to try and get the operators' attention. The operator was not able to see [the field representative's] attempts to gain his attention nor was he able to hear [the field representative] or the site foreman. At that time, the gauge was struck by John Deere 700, which resulted in cracking of the gauge case and breaking of the source rod. "March 16, 2016 about 1620: The RSO called the assistant CS [Construction Site] manager and RSO, INC., to inform them of the incident and to immediately get RSO, Inc. to the site and address the issue. [The assistant CS manager] also placed a call to NRC and was informed to call Maryland NRC to notify them of the incident. "March 16, 2016 about at 1630: The RSO, left our Ashburn [VA] office for the project in Maryland. [The RSO] arrived onsite at 1730 [EDT] to meet [the representative] of RSO Inc. RSO Inc. proceeded to perform a leak test and take readings of surrounding areas and construction equipment. [The source did not leak and there were no reports of radiation exposures.] "March 16, 2016 about 1700: The RSO Inc. representatives were able to retract the source rod into the gauge case shielding. They packaged the gauge back into the carrying case; [The licensee's RSO] took the gauge back to the Ashburn office to secure it. "March 17, 2016: The RSO, picked up the gauge and transported it to NETS (North East Technical Services), for the gauge to be disposed." The gauge is a Humboldt model number 5001 EZ, serial number 4704. The licensee is licensed in the Commonwealth of Virginia, VA License #45-25467-01 and MD Material License # MD-13-020-01. Maryland Case Number: 1654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2016-03-25
51796 | 0 | BOTSFORD CANCER CENTER |  |  |  |  | 2016-03-16 14:30 | 2016-03-17 16:19 | 2016-03-17 | BRACHYTHERAPY DOSE LESS THAN PRESCRIBED DUE TO EQUIPMENT MALFUNCTION The following was received from the licensee via email: "Medical Event on a Prostate HDR [high dose rate brachytherapy] Fraction #2. The patient was previously treated to Fraction #1 2 weeks earlier without any issue. "A patient was under spinal anesthesia for a treatment to the prostate to a prescribed dose of 13.5 Gy. The plan called for 19 interstitial catheters to the 30 cc prostate gland. The V100 of the prostate was expected to be 99.75% (100% dose of 13.5 Gy covered 99.75% of the prostate volume). All coverage and critical organ sparing criteria were met and physician approved the plan. "However during treatment and after completion of 9 catheters the treatment console reported an error (and subsequently retracted the source after 2 dwell positions were treated of the 10th catheter). The error code 9 message was source has moved from dwell position and a reset of the treatment console was required. "[The medical physicist] went inside the treatment room with the survey meter to ensure the source indeed retracted and transfer tube and applicator appropriately connected. Which they were. Attempts were made to continue with the treatment as the error code direction was cancel the error and try again. "However, the afterloader would not resume treatment and the treatment console reported an another error code 117 error during check out-drive in channel (driving out the check cable). "Several attempts were made with help of Elekta field service and phone support to troubleshoot the issue as the message on the treatment console with these errors is that if the problem persists, contact your local Elekta service representative. Troubleshooting continued afterwards with the field service engineer coming on site. We were later informed by the engineer that parts had to be ordered to resolve the issue and that they would arrive early the next morning. "The procedure was eventually halted due to the service issue and patient was sent to recovery and family informed. "[The licensee is] now assessing what dose was delivered. "The total treatment time called for 386.6 s. However, only 158.5 s was treated. On the treatment planning system using the catheters and dwell positions and time of 158.5 s the v100 to the prostate is showing as 12.52% (100% of the dose of 13.5 Gy covered 12.52% of the prostate volume) of the partially treated procedure. There was no excessive dose anywhere i.e. to critical structures, just lack thereof to the intended treatment volume of the prostate. The dosimetrist is working with the plan to put on dose points near treated catheters to provide us further details. "[The licensee] wanted to take the appropriate direction going forward in regards to documentation, reporting and planning for treatment for the patient on a subsequent date. The machine issue initially occurred at approximately [1430 EDT on 3/16/16]. Service on the unit is ongoing so exact details of the repair are not yet available. Remaining prostate patients scheduled for this week been rescheduled for a later date." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-03-25
51795 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-03-17 01:15 | 2016-03-17 08:02 | 2016-04-19 | LOSS OF EMERGENCY AND AUXILIARY GAS TREATMENT SYSTEMS "On March 17, 2016, at 0115 [EDT], Watts Bar Unit 1 (WBN1) entered Technical Specification Limiting Condition of Operation (TS LCO) 3.0.3 due to the inoperability of both trains of the Emergency Gas Treatment System (EGTS). TS LCO 3.7.12 Condition B was also entered at this time due to the inoperability of both trains of the Auxiliary Gas Treatment System (ABGTS). The train B EGTS and train B ABGTS had been removed from service for scheduled maintenance, when at 0115, the train A Auxiliary Air Compressor became inoperable. On March 17, 2016, at 0133, the train A Auxiliary Air Compressor was declared OPERABLE, and TS LCO 3.0.3 and 3.7.12 Condition B were exited. "The auxiliary air system supports the EGTS by providing a safety grade air supply. When train A auxiliary air became inoperable, the supported train A EGTS and ABGTS became inoperable, creating a condition where both trains of EGTS and ABGTS were unavailable. In the event of an accident, the EGTS establishes a negative pressure in the annulus between the shield building and the steel containment vessel and the ABGTS establishes a negative pressure in the Auxiliary Building Secondary Containment Enclosure (ABSCE). Filters in these system mitigate the release of radioactive contaminants to the environment. "WBN1 remained in Mode 1 at 100% power and no safety functions were required during the event. "This event is reportable under 10 CFR 50.72(b)(3)(v)(C) and (D) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." * * * RETRACTION AT 1518 EDT ON 04/19/16 FROM BRIAN MCILNAY TO JEFF HERRERA * * * "The purpose of this notification is to retract event report no. 51795 made on 3/17/16 at 0802 (EDT). Previously, Tennessee Valley Authority (TVA) reported a loss of the Emergency and Auxiliary Building Gas Treatment Systems (EGTS/ABGTS) at Watts Bar Nuclear Plant Unit 1 (WBN1). Both trains of EGTS and ABGTS were declared INOPERABLE when the train A auxiliary air system cooling water supply bypass valve was isolated, prior to completing the requisite post maintenance testing following repairs to the normal cooling water supply solenoid valve. Upon recognition, WBN1 operations personnel declared the train A auxiliary air system INOPERABLE, resulting in inoperability of Train A EGTS and ABGTS and forcing entry into TS LCO [Limiting Condition for Operation] 3.0.3 (from TS LCO 3.6.9 EGTS) and 3.7.12 Condition B for ABGTS. At the time the condition was recognized, train B EGTS and train B ABGTS were INOPERABLE for scheduled maintenance. "Subsequently, TVA completed the post maintenance testing of the train A auxiliary air system ERCW [Emergency Raw Cooling Water] normal supply solenoid valve and determined that the valve, while not fully qualified at the time, was in fact operable and capable of performing its safety function. Therefore, entry into TS LCO 3.0.3 and 3.7.12 Condition B was not necessary and the event is no longer reportable under 10 CFR 50.72(b)(3)(v)(C) and (D) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." Notified the R2DO (McCoy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-03-17
51794 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-03-16 | 2016-03-16 13:11 | 2016-03-16 | TEXAS AGREEMENT STATE REPORT - PACKAGE CONTAINING SOURCES LOST THEN FOUND The following information was obtained from the State of Texas via email: "The Agency [Texas Department of State Health Services] was notified by a manager for a common carrier of radioactive material that a package had fallen out of the transport vehicle. The package was found by a member of the public on a highway [when he] swerved to miss hitting the package. The person collected the package and called the number on the package. The number was to the manufacturer of the source. The radiation safety officer (RSO) for the company met the member of the public to collect the package. The RSO completed a survey of the package and performed leak testing. The container was a type B package containing two Ir-192 sources, SN29629G and 29630G, joint activity of 8,188.8Gbq (>100 curies each) with transport index of 1.2. The package outer shipping box was damaged although the type B container was in good condition and was not leaking. The sources are currently at the manufacturer's location in storage. The sources were enroute to the manufacturer's Baton Rouge location when the container fell out of the transport vehicle onto the freeway. The details of the time frame the member of the public had the package in their possession is being confirmed and details of the time the package was on the freeway is being acquired. Investigation into this event is ongoing and details will be provided in accordance with SA 300 guidelines." Texas Incident No.: I-9387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-03-24
51793 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-03-15 07:25 | 2016-03-15 19:43 | 2016-03-15 | FLORIDA AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following information was obtained from the State of Florida via email: "[A licensee] employee left the shop this morning at 7:25 a.m. [EDT] in a pick up truck. The soil moisture density gauge was locked but not chained and locked to bed of pick up truck. [The] employee drove about one mile to [the] job site and upon arrival realized the gauge was missing. Multiple employees retraced the route to try and find the gauge but could not find it. The RSO [Radiation Safety Officer] notified local law enforcement and fire department. The RSO noted the gauge is an InstroTek 1955 Explorer 3500, sources serial number is CZ6000; 267-14 and estimated current activity is 40 mCi of Am241 and 10 mCi of Cs137. Incident report from RSO to follow." Florida Incident Number: FL16-040 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-03-23
51792 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2016-03-15 06:49 | 2016-03-15 15:14 | 2016-03-15 | IDENTIFIED PRESSURE BOUNDARY LEAKAGE "During a scheduled refueling outage, an inspection of containment components revealed a suspected through wall leak on 1CV-200B, Letdown Orifice 'B' Outlet Control. Non-destructive engineering inspection has been completed and determined that an indication exists. "10 CFR 50.2(2)(i) defines the reactor coolant pressure boundary as being connected to the reactor coolant system, up to and including the outermost containment isolation valve in system piping which penetrates primary reactor containment. 1CV-200B is isolable from the Reactor Coolant System (RCS) by a single motor operated valve, 1RC-427, Reactor Coolant Loop 'B' Leg to CVCS Letdown Isolation valve. 1CV-200B is located inside of containment between 1RC-427 and the two containment isolation valves for the letdown line, 1CV-371 and 1CV-371A. Based on the definition provided in 10 CFR 50.2, the condition is considered pressure boundary leakage and is considered reportable under 10 CFR 50.72(b)(3)(ii). Unit 1 is currently in Mode 6. Repairs for the condition are being determined. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-03-15
51791 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-03-15 | 2016-03-15 10:36 | 2016-03-15 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of Texas via email: "On March 15, 2016, the licensee notified the Agency [Texas Department of State Health Services] that one of its technicians had stopped by an apartment complex on his way to a temporary job site and had left a Troxler model 3430 moisture/density gauge (SN: 63944) secured with 2 chains in the back of the company truck while he went inside an apartment. When he returned to his vehicle, he found that the chains had been cut, the transport case was on the ground near the vehicle, and the gauge had been removed. The licensee's radiation safety officer reported that the insertion rod on the gauge was locked and the technician had the key. The RSO notified local law enforcement and searched the immediate area. They will continue and expand their search for the gauge. The gauge contained a 40 milliCurie americium-241 source and an 8 milliCurie cesium-137 source. An investigation into this event is ongoing. Further information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9386 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-03-23
51790 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-03-12 | 2016-03-14 16:05 | 2016-03-14 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of California via email: "On 03/14/16, RHB [California Department of Public Health - Radiologic Health Branch] was contacted via email by the California Office of Emergency Services (OES) to report a stolen moisture density gauge. This is a Troxler Model 3440, S/N T34436628, gauge containing 9 mCi of Cesium -137 and 44 mCi of Americium - 241. This gauge was stolen from the licensee's storage facility located in Placerville, CA on 03/12/16. [The licensee radiation safety officer] RSO had filed a report with the El Dorado County Sheriff's office. There is no report of damage to the device, however, the whereabouts of the gauge is unknown. RHB will be following up with this investigation." California Report Number: 5010-031416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-03-22
51789 | 0 | GENERAL ELECTRIC OF PLEASANTON |  |  |  | 100 KW NTR (TANK) | 2016-03-10 10:00 | 2016-03-14 14:59 | 2016-03-14 | TECHNICAL SPECIFICATION DEVIATION WHEN OPERATORS MANIPULATED PLANT ON EXPIRED LICENSES On March 10, 2016, it was discovered that two operators at the facility had manipulated the plant with expired NRC licenses. The licenses expired in January, 2016. This constitutes a deviation from the facility's Technical Specification 6.1.3.1 - 'Minimum staffing'. Preliminary investigations have determined that the operators performed licensed activities at least 16 times since the expiration of their licenses. The cause of this event in under investigation. The licensee has notified their NRC Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | RESEARCH AND TEST REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | CA | NPR | [5 empty] | 0 | 2016-03-14
51788 | 0 | ANVIL ENGINEERING PIPE SUPPORT |  |  |  |  | 2015-10-01 | 2016-03-14 14:07 | 2016-04-26 | PART 21 - HYDRAULIC SNUBBER SEAL MATERIAL DEVIATION INTERIM REPORT "Anvil Engineered Pipe Supports (EPS) supplied 14 Fig. 200N Configuration 'A' style hydraulic snubbers to the Exelon owned and operated Peach Bottom Atomic Power Station (PBAPS) in 2013. During the course of routine refueling outage activities in October 2015, it was discovered that 9 of these 14 snubbers had no hydraulic fluid in the reservoir. The cause of the hydraulic fluid loss was premature aging of the reservoir piston seal due to vibration induced frictional heat. Subsequent laboratory testing of both replacement and degraded seal material by Exelon Power Labs suggested that a material substitution had been made from the Anvil approved Ethylene Propylene (EP) compound to a different grade of EP rubber. "On February 17, 2016, Anvil determined that a material substitution was made by the seal vendor. A machined seal that was fabricated by the manufacturer was substituted for a seal molded with the approved Anvil compound. Prior to its installation in Fig. 200N/201N Configuration 'A' hydraulic snubbers, the machined seal compound was not tested to establish a service life for the compound. "Anvil has bounded the extent of condition to 4 specific seal batches of 4" and 5" Fig. 200N/201N Configuration 'A' reservoir piston seals provided after January 1, 2013. Based on its Part 21 investigation, Anvil has yet to determine that a specific defect exists, based on the demonstrated operability of the snubbers at PBAPS despite severe service conditions beyond their published operational limits, and the compatibility of the EP base polymer with Anvil hydraulic fluids. "Anvil is conducting a test campaign to approve and establish a service life for the machined seal compound. This testing will either qualify the machined compound for use at currently published Anvil service conditions (157 degrees F for 25 years with a total lifetime dose not to exceed 2e8 rads), or establish a reduced service life for the snubbers in which a material substitution was made. This testing is being conducted on an assembled reservoir with the substitute machined compound. It will include irradiation of the reservoir to 6.4e7 rads, accelerated temperature aging, and a final radiation exposure to bring the cumulative dose to 2e8 rads. As of 3/14/16, the reservoir specimen had been irradiated to 6.4e7 rads with no effect on the seal. "Anvil expects to have this testing complete by May 1, 2016, with a formal evaluation to follow. PBAPS has been notified of the material substitution, and a full accounting of the affected snubbers by serial number, PO number, site, and utility is being assembled. Anvil will notify affected sites when the testing and equivalency evaluation is complete. "Please feel free to contact me if you have any questions or require any additional information. "Sincerely, Mark R Ward Operations Manager Anvil Engineered Pipe Supports 160 Frenchtown Road North Kingstown, Rl, 02852" * * * UPDATE ON 4/26/2016 AT 12:25 EDT FROM MARK WARD (VIA FAX) TO BETHANY CECERE * * * The following is a summary of information received from Anvil EPS: Anvil performed qualification testing of the machined compound with satisfactory results. The machined compound is now qualified for a service life equivalent to the published service life of the molded compound when used as a reservoir piston seal for the Fig. 200N/201N Configuration "A". Anvil has determined that a specific defect does not exist and no action by licensees is needed. Fifty-nine (59) total snubbers were shipped to NRC licensees (Farley, Peach Bottom, Oconee, ANO, and Diablo Canyon); Anvil will advise sites. Notified R1DO (Dwyer), R2DO (Ehrhardt), R4DO (Groom) and NRR Part 21 Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 1 | RI | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2016-03-14
51787 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-03-14 02:47 | 2016-03-14 04:52 | 2016-03-14 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF OFFSITE EMERGENCY NOTIFICATION SIREN "A South Texas Project, Offsite Emergency Notification Siren, was inadvertently going off. The Matagorda County Sheriff's Office notified Site Security that a siren had actuated for no apparent reason. Station personnel are addressing the issue with the siren. "The Matagorda County Sheriff's Office was the only offsite agency that was contacted during the event." The siren was tested and is considered functional at this time. Additional testing will be completed during daylight hours. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-03-14
51786 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2016-03-11 15:34 | 2016-03-11 19:50 | 2016-03-11 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "A private company reported a soil density meter was damaged and an increase in background radiation was detected due to possible shielding damage. "Event terminated. Gauge has been safely transported back to the manufacturer, Instrotek at 1905 [EST]. Radiation surveys at the scene indicated sources were intact and not leaking. Swipes on the source rod, device and equipment confirmed no contamination at the scene. Scene has been released for general public use. "Radioactive Material Licensee: Froehling & Robertson Incident Location: 1202 Redwood Valley Lane, Knightdale, NC Gauge: Instrotek 3500 Radioactive Material: 10 mCi Cesium 137; 40 mCi Americium 241, Beryllium "Summary: Radiation Protection Staff arrived on site at 1720 [EST]. Gauge housing was found to be damaged along with a bent source rod. When staff approached the gauge, at 5 feet, the readings were 5mR/hr (milliRem per hour) indicating that sources were not properly shielded. When staff surveyed the bottom of the gauge at the shutter, the source rod fell out backwards from the top of the device. All items were moved to survey the area around where the accident occurred to see if the sources had fallen out in the compacted soil. They had not. Readings were background for the area of 25 to 30 uR/hr (microRem per hour) indicating the sources were still in the source rod. Staff put the source rod back in the gauge housing. Readings at the bottom of the device with the source rod in place, showed readings of 150 to 200 mR/hr. This confirmed the sources were in the rod, but indicated the shutter shielding the sources was not functioning properly. The reassembled gauge was placed back in the certified DOT shipping container and properly blocked and braced in the licensee's (Froehling & Robertson) truck. Staff followed the licensee to Instrotek where the device was safely stored until the manufacturer can assess the damage. US Nuclear Regulatory Commission notified via this email Radiation Protection Section will continue its compliance investigation of why this event occurred. Radiation Protection Section will update the National Material Event Database. Pictures to be uploaded into event reporting. No further updates will be given." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2016-03-21
51785 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2016-03-10 08:40 | 2016-03-10 09:44 | 2016-03-10 | SEISMIC ALARM FUNCTION NOT AVAILABLE DURING SEMI-ANNUAL SEISMIC SYSTEM FUNCTIONAL TEST "This notification is being made due to planned maintenance during the Semi-Annual Seismic System Functional Test. This test will result in a major loss of emergency assessment capability for emergency action levels (EAL) HA6 (Natural or destructive phenomena affecting VITAL AREAS), while the control room 0.1g acceleration alarm is non-functional. The emergency preparedness plan requires the 0.1g acceleration alarm indication to declare EAL HA6 during a seismic event > Operating Basis Earthquake (OBE). This condition requires an 8 hour nonemergency immediate reportability to the NRC in accordance with 10 CFR 50.72(b)(3)(xiii), Major Loss of Assessment, Response, or Communication Capability. "At approximately 0840 CST on March 10, 2016 the Semi-Annual Seismic System Functional Test commenced. While this test is in progress, seismic alarm capability is not available for EAL declaration purposes. ANO procedures provide compensatory measures of using offsite sources to obtain seismic data. It should be noted that seismic data will still remain capable of being recorded and only alarm capability is lost. The Semi-Annual Seismic System Functional Test is scheduled to be completed in less than 24 hours." The licensee will inform the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-03-10
51784 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-01-10 02:43 | 2016-03-09 16:53 | 2016-03-09 | INVALID ACTUATION OF THE PRIMARY CONTAINMENT ISOLATION LOGIC "On January 10, 2016, at 0243 CST, with the plant in cold shutdown, the primary containment isolation logic was actuated as the result of an invalid signal. This condition occurred while operators were installing electrical jumpers designed to bypass certain isolation signals for the suction valves in the residual heat removal (RHR) system that comprise the shutdown cooling flow path. These jumpers are installed under procedural guidance for the purposes of increasing the reliability of the shutdown cooling loop by disabling isolation signals that are not required to be operable in certain plant operating modes. Although it could not be proven, it appears that inadvertent contact with an energized circuit occurred during the jumper installation, causing a fuse to blow, de-energizing part of the primary isolation logic. This caused the automatic closure of Division 1 suction and return valves in the shutdown cooling loop, as well as valves connecting the reactor plant sampling systems to the RHR system. The main control room crew implemented recovery procedures to restore shutdown cooling to service at 0401 CST, prior to exceeding any temperature limits. "This event resulted from the failure to maintain corrective actions in place that were develop after a similar event in 1994. Additionally, the operators were not using the type of jumpers required by the procedure, which likely contributed to the blown fuse. "The RHR system operating procedure has been revised to require that the potentially affected valves in the shutdown cooling loop will be de-energized during jumper installation to eliminate the possibility of inadvertent isolation. "This is being reported in accordance with 10 CFR 50.73(a)(1) as an invalid actuation of the primary containment isolation logic." During this event, the RCS temperature increased from approximately 130 to 190 degree F. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-03-09
51783 | 0 | USAF |  |  |  |  | 2016-02-17 09:00 | 2016-03-09 16:36 | 2016-03-09 | LOST AM-241 CHECK SOURCE "Organization Possessing Source(s): 711HPW, USAFSAM/OE. "Specific Location(s): Wright-Patterson AFB, OH Bldg. 20840, Room W329D, OEA Radioactive Material Storage. "What Happened: One (1) each Isotope Product Laboratory, 12.8 nCi Am-241 check source, RP# 0895 was to be shipped, along with three other sources, to Nellis AFB in support of USAFSAM/OEC personnel. The PRSO [Permit Radiation Safety Officer] could not immediately locate RP# 0895. "The PRSO checked the RAM [Radioactive Material] sign-out log to determine if the source had been signed out to other OE personnel. The log did not show evidence of the source having been signed out. The PRSO questioned Radioanalytical Lab, Dosimetry Lab, Calibration Lab, AFRAT, Consulting and Education personnel to determine if anyone was using the source. All of them had a negative reply. All laboratories were thoroughly searched as were the OEC equipment cases used in the Nellis operations. AFRAT equipment cases in WRM were also searched. The source was not located. "The PRSO determined the source had last been accounted for during the RAM inventory dated 17 August 2015. Additional investigation revealed that the prior PRSO had been requested to send the source, along with two other sources, to Nellis AFB in support of OEC personnel in September 2015. These sources were never signed out of the inventory when sent to Nellis AFB. Additionally, no OEC personnel recall using the source during that period. The other two sources requested were received back at USAFSAM on 5 October 2015. DOE personnel working with OEC personnel at Nellis AFB, as well as the Nellis IRSO [Installation Radiation Safety Officer], were contacted to see if they had the source in their possession. All had a negative reply. It cannot be determined if the source was lost at USAFSAM or Nellis AFB. The PRSO contacted the IRSO, at 1531, 17 February 2016 to inform him of the potential lost source. USAF Master Materials License: 42-23539-01AF Docket: 030-28641. Applicable USAF RAM Permit: OH-00563-00/14AFP Docket: 030-00563. Commodity (i.e., compasses, etc.): Isotope Product Laboratory check source. Radioisotope(s) Involved: Am-241 Activity: 12.8 nCi Sealed Source Model/Serial No: K-845/0895 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-03-17
51782 | 0 | PATRIOT ENGINEERING & ENVIRONMENTAL |  |  |  |  | 2016-03-08 | 2016-03-09 15:10 | 2016-03-09 | DAMAGED SIEMENS DENSITY GAUGE The licensee reported that a Siemens C-200 Gauge, model L 640 containing a Ra-226 0.005 Ci source, was run over by a pick up truck and damaged. Damage to the gauge was limited to the electronics package and battery. The source remains properly contained and un-damaged. A survey of the area indicates no leakage and no exposures to personnel. The gauge has been placed in a secure location and will be sent back to the manufacturer for repairs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-03-17
51781 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-03-07 | 2016-03-09 14:11 | 2016-03-09 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The following report was received from the Commonwealth of Pennsylvania via email and facsimile: "Event Type: Loss of licensed material in a quantity greater than or equal to 1000 times the Appendix C quantities in part 20. "Notifications: NRG Energy discovered the event on March 7, 2016, [at their Seward, PA location,] and submitted a report to the Department [Pennsylvania Department of Environmental Protection] on March 9, 2016. This event is reportable as per 10 CFR 20.2201(a)(1)(i). "Event Description: On Monday March 7, 2016, while conducting the six month inventory check of the radioactive sources at the Seward Power Plant, one tritium exit sign was found missing. The exit sign was installed above a door located in Seward's Fuel Barn. The last inventory check was conducted September 11, 2015, and the exit sign was present at that time. The exit sign was manufactured by EMERG-LITE and was an Everlite series sign. The sign contained between 9.5 - 11.5 Ci of tritium gas at the time of manufacture and was to be replaced before February 2023. The sign was last known to be in good condition and not damaged. No cause for the missing sign has been identified and no exposures have been recorded at this time. "Cause of the Event: Unknown at this time. The plant is currently searching the site and conducting interviews with personnel. "Actions: The Department will be following up with the facility for any additional information. The plant is also conducting refresher radiation training to plant personnel. More information will be provided upon receipt." Pennsylvania Event Report ID No: PA160009. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-03-17
51780 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-03-09 03:42 | 2016-03-09 04:01 | 2016-03-09 | UNUSUAL EVENT DECLARED DUE TO A FIRE GREATER THAN 15 MINUTES Watts Bar Unit 2 declared an Unusual Event at 0342 EST based on a fire greater than 15 minutes in the turbine building - 2B Hotwell pump motor. The fire was extinguished by 0401 EST, at the time of notification. Unit 2 is currently shutdown in Mode 5 making preparations for startup. No offsite assistance was requested. All personnel are accounted for and there are no personnel injuries reported. The licensee notified the NRC Resident Inspector. Notified DHS SWO, DOE, FEMA OPS, FEMA National Watch (email), DHS NICC, and Nuclear SSA (email). * * * UPDATE AT 0512 ON 03/09/16 FROM BRIAN McILNAY TO S. SANDIN * * * The licensee terminated the Unusual Event at 0508 EST based on verification that the fire was out and that the fire response team had been secured. The licensee notified the State and local agencies and the NRC Resident Inspector. Notified R2DO (Suggs), NRR EO (Morris) and IRD (Grant). Notified DHS SWO, DOE, FEMA OPS, FEMA National Watch (email), DHS NICC, and Nuclear SSA (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-03-09
51779 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2016-03-06 22:33 | 2016-03-08 15:34 | 2016-03-08 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following report was received from the State of Mississippi via facsimile: "The Licensee notified DRH [Mississippi Department of Radiation Health] on 3/7/2016, that an incident had occurred at 2233 [CST on 3/6/16], at the client's site [in Holly Springs, MS]. The Licensee's two (2) man radiography crew was performing radiography inside a twelve (12) foot, open end vessel, thirty six (36) feet long, and nine (9) foot off the ground. The radiography camera in use was a Sentinel model 880D, serial No. D1120. During one exposure the guide tube became crimped preventing the source from retracting back into the camera. This was due to the camera falling off the scaffolding to the vessel floor while the radiographer was retracting the source. The resulting action caused the guide tube connected to the camera and magnetic stand to become crimped at the camera connection point. The licensee's radiography supervisor was notified and the restricted area boundary was increased by the two (2) radiographers. "Source retrieval was performed by the radiography supervisor with assistance from the radiography crew. A survey was performed using a NDS, ND-2000, SN: 20113, Calibration date: 1/15/2016, at the opposite end of the vessel thirty two (32) feet away from the source revealing a reading of two hundred twenty (220) mR/hr. A decision was made to pull the camera to one opening of the vessel by the camera cranks. The restricted area was then readjusted for two (2) mR/hr. "While the camera was being lowered to the ground with a guide rope out of the vessel opening, the guide tube became straight enough to allow for source retraction. The guide tube and magnetic stand hung at the opening of the vessel causing the guide tube to straighten out from the weight of the camera below the vessel opening. The radiographers made another attempt to retract the source with success when the guide tube was straight. Once the camera was on the ground, the Licensee's survey of 46 mR/hr confirmed the source was retracted back into the camera. "Doses to the radiography crew and supervisor were all below 60 millirems (mR). Instadose radiation badges were used with the highest dose reported of thirty nine (39) mR to both radiographers. Pocket dosimeters were also used with the highest dose reported by the radiography supervisor of fifty five (55) mR. "Licensee's written report was received on 3/7/2016. The camera has been removed from service pending a sealed source and DU wipe test. Implemented corrective actions included adequate lighting at night and tying the camera off when it is used over twelve (12) inches off the ground." The radiography camera contains a 79.9 Ci Ir-192 Source, model A424-9, serial number 28799G. The State of Mississippi instructed the licensee to submit a 30 day written report and considers this case to be closed. Mississippi State Report number: MS-16002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-03-16
51778 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-03-07 | 2016-03-08 09:42 | 2016-03-08 | AGREEMENT STATE REPORT - DENSITY GAUGE STUCK SHUTTER The following was received from Texas via email: "On March 7, 2016, the Agency [Texas Dept. Of State Health Services] was notified by the licensee that while performing routine checks, the shutter on an Ohmart SH-F2 nuclear gauge was stuck in the open position. Open is the normal operation position for the shutter. The gauge contains a 100 millicurie cesium-137 source. The gauge does not create an exposure hazard to the licensee's employees or any member of the general public. The licensee has contacted their service company who will inspect the gauge on March 9, 2016. Additional information will be provided as it is received in accordance with SA-300." Texas incident # I-9384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-03-16
51777 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-03-08 02:32 | 2016-03-08 09:37 | 2016-03-08 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE OUTSIDE SPECIFICATION "On March 8, 2016 at 0232 hours [EST], Secondary Containment Zone 3 (Unit 1&2 Reactor Building) differential pressure lowered to 0.16 inches water gauge when securing Unit 1 Zone 3 HVAC for planned maintenance. Required differential pressure per SR 3.6.4.1.1 could not be maintained in the intended alignment. Zone 3 ventilation was restored to the original alignment and Zone 3 differential pressure recovered to greater than 0.25 inches water gauge at 0335 hours. Zone I (Unit 1 Reactor Building) and Zone II (Unit 2 Reactor Building) ventilation remained in service and stable. Station engineering and maintenance are investigating the Zone 3 HVAC system to determine the cause. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022, Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The NRC Resident Inspector has been notified. | 87 | 100 | 0 | 87 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-03-08
51776 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2016-03-07 16:15 | 2016-03-07 19:17 | 2016-04-13 | ADMINISTRATIVE ITEMS RELIED ON FOR SAFETY (IROFS) NOT PERFORMED "During the afternoon of March 7, 2016, UUSA [Urenco USA] operators moved drums containing uranic material into an IROFS [Items Relied On For Safety] controlled array. This IROFS requires initial and independent operator verification to ensure a subcritical geometry exists prior to adding any new material to the array. The operators moving the drums did not perform the administrative IROFS; that is, neither an initial nor an independent verification were completed prior to adding five additional drums to the array. "UUSA management and nuclear criticality staff have ensured the drums are in a safe and subcritical configuration. "The drums contain clean up materials contaminated with UF6 at unknown levels of enrichment. A nuclear criticality did not occur. The array is in a subcritical geometry. No external events are affecting this event. No emergencies have been, nor will any be declared. "No state or other federal agencies will be notified. No press releases are planned. "Number and types of controls necessary under normal operating conditions: One enhanced sole IROFS. The enhancement is an initial verification and an independent verification of geometry prior to movement of material into the area. "Number and types of controls which functioned properly under upset conditions: Neither the IROFS initial verification, nor the independent verification of geometry were performed before movement occurred. "Number and types of controls necessary to restore a safe situation: A member of operations management passed through during a routine plant tour, questioned the operators, and determined that the drums had been placed in a safe geometry in the array without performing the required IROFS surveillance. "Safety significance of events: Loss of geometry controls preventing criticality. "Safety equipment status: The array is in a subcritical geometry. "Status of corrective actions: Corrective actions to be developed." * * * UPDATE FROM SLAMA TO SHOEMAKER ON 4/13/16 AT 1542 EDT * * * "Isotopic analysis has been conducted for the material in the stored drums; the uranium enrichment is characterized as depleted. As such, criticality was not possible during the operations and the as-found configuration reported in Event Notification 51776 on March 7, 2016. However, the required IROFS was not implemented. The event is hereby being reclassified as a 24-Hour Event Notification in accordance with 10 CFR 70 Appendix A (b)(2). "The previously reported IROFS was available and should have been implemented at the point of storage to ensure safe storage array configuration, thus meeting 10 CFR 70.61 performance requirements. During the ongoing Root Cause Evaluation for this event, it was discovered and documented that an additional IROFS was not implemented during the March 7, 2016 movement evolution. This additional IROFS requires the use of a transfer cart for movement from the point of generation to the point of storage. This cart is to ensure proper spacing between the container and any materials which may be passed during movement. This is a sole administrative IROFS enhanced with initial and independent verifications. "As stated above, analysis has been completed which characterizes the material as depleted UF6. As such, during the movement of the drums, criticality was not possible. The required IROFS was available, however the failure to implement applicable controls resulted in a situation in which no reliable barrier was in place to provide assurance that interaction control would be maintained during movement. The failure to implement this additional IROFS during movement is hereby classified as a 24-Hour report in accordance with 10 CFR 70 Appendix A (b)(2). The information required per 10 CFR 70.50 (c)(1) is same as that contained in the event description [of the original notification]." Notified the R2DO(Bonser) and the NMSS Events Notification Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2016-03-15
51775 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2016-03-07 10:18 | 2016-03-07 17:12 | 2016-03-07 | EMERGENCY DIESEL GENERATORS AUTO-STARTED ON VALID ACTUATION SIGNAL "During Emergency Diesel Generator (EDG) surveillance testing, the normal 480V Bus 3A supply breaker tripped open. All EDGs auto-started as per plant design. During restoration of normal power to the 480V Buses, 23 EDG output breaker opened on overcurrent. All plant systems responded as per design. "There was no loss of core cooling since steam generators were coupled with an operational RCP. No other ESF [Engineered Safety Feature] equipment automatically started. "The 480V Bus 3A normal supply breaker was replaced and the cause of both issues is under investigation. "Indian Point Unit 2 remains in a stable MODE 5 condition with all 480V Buses energized via normal power. The NRC Resident has been informed." The licensee will inform the New York Public Service Commission. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-03-07
51774 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-03-02 | 2016-03-07 14:56 | 2016-03-07 | AGREEMENT STATE REPORT - CONTAMINATION EVENT WITH POSSIBLE SHALLOW DOSE EXCEEDING FEDERAL LIMITS The following report was received from the Commonwealth of Pennsylvania via facsimile: "Notifications: The event occurred on March 2, 2016, the licensee discovered the event on March 3, 2016, and notified the Department [Pennsylvania Department of Environmental Protection] on March 4, 2016, via a phone call. The event is reportable per 10 CFR 30.50(b)(1)(i) and 10 CFR 20.2202(b)(1)(iii). "Event Description: On March 2, 2016, a technologist was injecting a samarium-153 'Quadramet' dose (approximately 81 milliCuries) when there was a problem with the syringe/tubing connection. A 'blowback' occurred and a small amount, believed to be approximately 1-2 mCi, of the dose spilled. The patient was released [and sent] home. The technologist stated that he had gloves on, washed his hands, surveyed the area and called the lead technologist to notify her of the incident. Radiation Safety [at the hospital] was not notified until March 3rd. The technologist was surveyed and found to have contamination on his hands and forearms. An initial calculation indicated a skin dose above 50 rem. Radiation Safety then took smears throughout the department and contamination was found on various surfaces including the floor, other technologist's hands, gloves, shoes, survey meters, chairs, and clothing. Removable contamination was also found in a technologist's vehicle. Radiation Safety has decontaminated most areas. Surfaces and rooms that were not able to be decontaminated were closed off (for decay) or covered with paper to prevent any further spread of contamination. It is believed that after the spill, the technologist attempted to clean up the area. Apparently it was not sufficient, for when housekeeping did their routine cleaning, they may have unknowingly further spread the contamination with floor mopping and other cleaning. No biological effects are expected with any individual. The RSO [Radiation Safety Officer] feels that a 'medical event' did not occur with the patient. The patient returned for a scheduled scan on March 3rd, and that scan appeared normal. The patient did not show any signs of detectable contamination on her skin. "Cause of the Event: Human error. The technologist may not have followed proper procedures, and contributed to the contamination spreading beyond initial spill area. "Actions: A reactive inspection is planned by the Department [Pennsylvania Department of Environmental Protection]. More information will be provided upon receipt." Event Report ID No: PA160008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-03-15
51773 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-03-07 08:37 | 2016-03-07 11:29 | 2016-03-07 | OFFSITE NOTIFICATION DUE TO FATALITY ONSITE "At the Limerick Generating Station, an individual experiencing a non-occupational illness was taken to a local medical facility. The individual was not contaminated. Subsequently, Limerick was informed that the individual has suffered a fatality." The individual was a contract employee and was located in a clean break area, within the protected area, when the individual became ill. The licensee has notified the NRC Resident Inspector and OSHA. | 92 | 100 | 0 | 92 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-03-07
51772 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-03-07 04:00 | 2016-03-07 11:18 | 2016-03-07 | UNANALYZED CONDITION INVOLVING DIESEL DRIVEN AUXILIARY FEEDWATER PUMP AIR INTAKES "The Auxiliary Feedwater (AF) system at Byron automatically supplies feedwater to the Steam Generators (SG) to remove decay heat from the Reactor Coolant System following a loss of normal feedwater supply. The AF System consists of a motor driven pump (A) and a diesel driven pump (B) configured into two trains for each unit. Each pump provides 100% of the required AF capacity to the SGs as assumed in the accident analysis. One pump at full flow is sufficient to remove decay heat and cool the unit to Residual Heat Removal (RHR) entry conditions. The diesel driven AF pump is powered from an independent diesel whose combustion air intake is located in the Seismic Category II (non-seismically qualified) Turbine Building but the diesel and pump are located in the Seismic Category I (seismically qualified) Auxiliary Building. "During the ongoing NRC Component Design Basis Inspection at the sister Braidwood Station, inspectors asked about the acceptability of the diesel combustion air intake being located in the non-seismic Turbine Building. During the review of available documentation related to the AF diesel engine combustion air intake, it was identified that the documentation did not support operation of the diesel with High Energy Line Break (HELB) environmental conditions in the Turbine Building. This has been reviewed and determined to be applicable to Byron Station Units 1 and 2. Specifically, prior evaluations did not account for air displacement by steam release during the event. After running different models for the Turbine Building HELB, diesel driven AF pump operability was supported for all but the Main Feedwater (FW) HELB. For the FW HELB, the best air density obtained failed to remain above the required levels deemed acceptable for engine operation and remained suppressed for extended periods of time. Additional efforts to qualify the FW piping in the Turbine Building for an Operating Basis Earthquake (OBE) to eliminate this piping from HELB considerations were not successful. This condition applies to both Units 1 and 2 but does not affect the motor driven AF pumps. This event does not constitute a loss of safety function at the point of discovery because the Byron opposite train motor driven AF pumps were operable on both Units 1 and 2. This event is reportable per 10 CFR 50.72(b)(3)(ii)(B) for 'any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "The licensee has notified the NRC Resident Inspector." The licensee entered a 72-hour Action Statement and engineering is analyzing the issue. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-03-07
51771 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-03-06 20:00 | 2016-03-07 02:00 | 2016-03-07 | UNANALYZED CONDITION INVOLVING DIESEL DRIVEN AUXILIARY FEEDWATER PUMP AIR INTAKES "The Auxiliary Feedwater (AF) system at Braidwood automatically supplies feedwater to the Steam Generators (SG) to remove decay heat from the Reactor Coolant System following a loss of normal feedwater supply. The AF System consists of a motor driven pump (A) and a diesel driven pump (B) configured into two trains for each unit. Each pump provides 100% of the required AF capacity to the SGs as assumed in the accident analysis. One pump at full flow is sufficient to remove decay heat and cool the unit to Residual Heat Removal (RHR) entry conditions. The diesel driven AF pump is powered from an independent diesel whose combustion air intake is located in the Seismic Category II (non-seismically qualified) Turbine Building but the diesel and pump are located in the Seismic Category I (seismically qualified) Auxiliary Building. "During the ongoing NRC Component Design Basis Inspection at Braidwood Station, Inspectors asked about the acceptability of the diesel combustion air intake being located in the non-seismic Turbine Building. During the review of available documentation related to the AF diesel engine combustion air intake, it was identified that the documentation did not support operation of the diesel with High Energy Line Break (HELB) environmental conditions in the Turbine Building. This has been reviewed and determined to be applicable to Braidwood Station Units 1 and 2. Specifically, prior evaluations did not account for air displacement by steam release during the event. After running different models for the Turbine Building HELB, diesel driven AF pump operability was supported for all but the Main Feedwater (FW) HELB. For the FW HELB, the best air density obtained failed to remain above the required levels deemed acceptable for engine operation and remained suppressed for extended periods of time. Additional efforts to qualify the FW piping in the Turbine Building for an Operating Basis Earthquake (OBE) to eliminate this piping from HELB considerations were not successful. This condition applies to both Units 1 and 2 but does not affect the motor driven AF pumps. This event does not constitute a loss of safety function at the point of discovery because the Braidwood opposite train motor driven AF pumps were operable on both Units 1 and 2. "This event is reportable per 10 CFR 50.72(b)(3)(ii)(B) for 'any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "The licensee has notified the NRC Resident Inspector." The licensee entered a 72-hour Action Statement and is preparing to address the issue with a configuration change. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-03-07
51770 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2016-03-06 15:20 | 2016-03-06 16:09 | 2016-03-06 | EMERGENCY DECLARATION DUE TO FIRE/EXPLOSION IN THE MAIN TRANSFORMER At 1512 EST, a fire/explosion occurred in the Unit 1 Main Transformer which resulted in a reactor trip. At 1520 EST, the licensee declared a Notification of Unusual Event. Offsite assistance was requested. At 1633 EST, smoke and flame were no longer visible. Fire brigade personnel were applying additional foam to prevent a re-flash. No personnel injuries occurred. Offsite assistance was requested with three local fire departments responding. All rods inserted on the trip. Steam generator feed is by the normal path. The plant is in its normal shutdown electrical lineup. The licensee has notified state and local authorities and the NRC Resident Inspector. Notified DHS SWO, FEMA, and DHS NICC. Notified FEMA NWS and Nuclear SSA via email. * * * UPDATE FROM DAVID HALE TO HOWIE CROUCH AT 1711 EST ON 03/06/16 * * * At 1658 EST, the licensee declared an Alert based on EAL Alert A.1. The cause of entry was that the fire damaged an overhead power line that supplies emergency power to all three units at Oconee. Offsite power is still available to all units. At 1708 EST, the fire is declared out. The licensee has notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC, USDA, HHS, DOE, and EPA. Notified FEMA NWS, FDA and Nuclear SSA via email. * * * UPDATE FROM DAVID HALE TO HOWIE CROUCH AT 1805 EST ON 03/06/16 * * * The licensee made notification of the RPS actuation as a result of the transformer fault. The licensee has notified the NRC Resident Inspector. Notified R2DO (Sykes). * * * UPDATE FROM DAVID HALE TO HOWIE CROUCH AT 2026 EST ON 03/06/16 * * * At 2016 EST, the licensee terminated all emergency declarations. The licensee has notified the NRC Resident Inspector. Notified R2DO (Sykes), IRD (Gott), NRR EO (Morris), DHS SWO, FEMA, DHS NICC, USDA, HHS, DOE, and EPA. Notified FEMA NWS, FDA and Nuclear SSA via email. | 0 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | Power Operation | Power Operation | Power Operation | Hot Standby | Power Operation | Power Operation | ALERT | 2 | SC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2016-03-06
51769 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-03-04 12:35 | 2016-03-04 20:02 | 2016-03-04 | EMERGENCY DIESEL GENERATOR DECLARED INOPERABLE "On March 3, 2016, during restoration of power to a Unit 1 electrical bus following planned work, an error in the restoration sequence resulted in an invalid auto-start signal to Emergency Diesel Generators (EDGs) 1, 2, 3 and 4. EDG 1 was out-of-service under clearance to support Unit 1 refueling outage modifications and maintenance and, as such, did not start. EDGs 2 and 4 auto-started as designed. However, EDG 3 failed to auto-start. At 1235 EST on March 4, 2016, EDG 3 was declared inoperable when troubleshooting identified a broken fuse block connection in the EDG 3 auto-start circuitry, which would have prevented a Technical Specification (TS) required auto-start of EDG 3. This condition concurrent with EDG 1 out-of-service would have precluded emergency power supply to emergency busses needed to mitigate the consequences of an accident. "Technical Specification 3.8.1, Required Action D.3, requires declaring the required features supported by the inoperable EDG 3 inoperable when the redundant required features are inoperable. As a result, both required Conventional Service Water (CSW) pumps were declared inoperable at 1635 EST on March 4, 2016. This also required declaring both Control Building Instrument Air Compressors inoperable. As a result, both Control Room Emergency Ventilation (CREV) subsystems and all three Control Building Air Conditioners were declared inoperable at 1635 EST on March 4, 2016. "The above conditions are reportable under 10 CFR 50.72(b)(3)(v)(D), as an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. "This event did not result in any adverse impact to the health and safety of the public. "The risk significance of this event is considered to be low. Both EDG 2 and EDG 4 were available and protected, along with the supplemental diesel generator and offsite electrical sources. Except for the periods of time for repair activities and post-repair testing, EDG 3 remained available via manual start. Actions were taken to protect other redundant safety systems and additional defense-in-depth was provided. "EDG 3 was restored to Operable status March 4, 2016 at 1834 EST and this has restored the safety functions of the above mentioned systems." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-03-04
51768 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-03-03 13:27 | 2016-03-04 13:28 | 2016-03-04 | AGREEMENT STATE REPORT - RADIOACTIVE GAUGE SHUTTER STUCK IN THE OPEN POSITION The following information was summarized from the State of Louisiana via email: "[On 03/03/16, the licensee] RSO e-mailed [Louisiana Department of Environmental Quality (LDEQ)] at approximately 1330 [CST] to report that a gauge installed on a process at the LA Pigment Company facility in Westlake, LA, had a shutter malfunction. The gauge is installed on a routing process for material at the facility. The gauge shutter is stuck in the open position. "The gauge is a Berthold Technologies, Model: Berthold Systems, LB-330 utilizing a 12 mCi Cs-137 source, S/N1768-5-90, Model: Lab. Prof. Dr. Berthold Dwg. #2653.100-001. "On 03/04/2016, a Service Engineer with Berthold Technologies evaluated the situation and stated the source holder/shield will be replaced and the same Cs-137 source will be installed in the new source holder. The cause of the operational failure appears to be corrosion, extended wear and tear and age of the device. The service holder order was placed and anticipated delivery is 4 to 6 weeks. The device will be shipped from Germany. "There are no exposure or health and safety issues involved with this event. The gauge and rod source will remain installed on the functioning process. The areas are posted with 'Do Not Enter or Operate' since the source cannot be locked out for human entry. The resolution of the situation will be directed by the ability to be repaired or if the gauge should be uninstalled and sent for disposal. "The corrective action: The repairs and/or corrective actions were determined on 03/04/2016 by [the Service Engineer] and will be completed when the replacement source holders arrive." LADEQ considers this incident closed. State Event Report ID No.: LA 160004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-03-14
51767 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2016-03-03 21:23 | 2016-03-04 10:26 | 2016-07-25 | CONTAMINATED RADIOACTIVE MATERIAL SHIPMENT "On March 3, 2016, at approximately 1745 [EST], a radioactive material shipment was received at NFS from the Westinghouse Electric Company in Hopkins, South Carolina. Receipt contamination and radiation surveys were completed at approximately 1905. Results indicated removable surface contamination on two of the nine radioactive material packages that exceeded the criteria of the cited regulations. "The radioactive material shipment left the Westinghouse Electric Company facility at 1300 [EST] on March 3, 2016. It was received at the NFS receiving facility at approximately 1745 on March 3, 2016. Surface contamination and radiation surveys were initiated immediately upon receipt. Removable surface contamination in excess of 10 CFR 20.1906(d) limits was verified to be present on the external surface of two of the nine shipping containers in the shipment at 1905. Contamination was controlled at the receiving facility and successfully decontaminated below criteria of 10 CFR 20.1906(d) by approximately 2030 on March 3, 2016." This was an exclusive shipment. The alpha contamination measured 4278 dpm/100 sq. cm. and 6345 dpm/100 sq. cm., respectively. The licensee informed Westinghouse who is conducting an investigation into this incident. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 07/15/16 AT 1243 EDT FROM RANDY SHACKELFORD TO DONG PARK * * * "On 3/4/2016, NFS made an event report to the NRC Operations Center regarding receipt of containers with removable contamination that exceeded the criteria of the cited regulations. Based on a recent determination by NRC that the materials of concern are considered to be low toxicity alpha emitters, the contamination limits for low toxicity alpha emitters were not exceeded. Therefore, NFS is retracting the event report. The licensee notified the NRC Resident Inspector. Notified R2DO (Rich) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 20.1906(d)(1) |  |  |  | 0 | 2016-07-22
51766 | 0 | EUROFINS EATON ANALYTICS, INC. |  |  |  |  | 2016-03-03 14:38 | 2016-03-03 14:39 | 2016-03-03 | LOST ELECTRON CAPTURE DETECTOR SOURCES "Eurofins Eaton Analytical, Inc., (EEA) is reporting two lost ECDs [Electron Capture Detector] serial# B794 and A10856 that were listed under the General License GL-65970 held by Underwriters Laboratories, Inc. "A notice to the NRC was sent on November 25, 2015 stating that the devices under General License GL-65970 were transferred to EEA. On February 4, 2016 it was brought to our attention by NRC Region III's Material Safety Licensing Branch, that ECDs, Serial# B794 and A10856 should be in our possession. After a thorough search of the facility and records we could not locate these ECDs. "(i) Lost device ECD, Serial# B794, Model# 03-917440-00, isotope Ni-63, activity 15 mCi, was manufactured by Varian Associates, Inc. (ii) Lost device ECD, Serial# A10856, Model# 02-0001972-00, isotope Ni-63, activity 15 mCi, was manufactured by Varian Associates, Inc. (iii) Both ECDs were not located in a recent inventory check. (iv) Both ECDs were more than likely returned to Varian for disposal before 2008. (v) No known exposures have been reported from this ECD at this time. (vi) [EEA] performed a thorough search of the facility and in-house records. In addition, [EEA] attempted to contact Varian. In 2010 Varian was sold off to Agilent and Buker Corp. Buker Corp then sold off their portion of Varian Gas Chromatography equipment to Scion in 2014. All three companies were contacted in order to determine who currently holds the Varian ECD records. None of the companies contacted claimed to hold the records. (vii) [EEA] now maintains a list of ECDs showing each ECD location. The list is maintained by the laboratory and monitored by the RSO." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-03-11
51765 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2016-03-02 13:12 | 2016-03-02 18:13 | 2016-03-02 | VALID ACTUATION OF EMERGENCY FEEDWATER "On 3/2/2016, [at] 1312 hours EST, while in the process of a plant cooldown, a valid actuation of the emergency feedwater system (EFW) occurred when B steam generator levels were reduced to 20 [percent]. The lowering level was a result of the unanticipated tripping of the start up feed pump on low condensate storage level while it was the feed source to the steam generators. The start up feed pump was restarted and feed flow had been restored when the actuation took place. The EFW flow was secured per procedure and the start up feed pump remains the feed source to the steam generators. "This is reportable under 50.72(b)(3)(iv)(A). "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-03-02
51764 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-03-02 13:30 | 2016-03-02 17:20 | 2016-03-02 | SECONDARY CONTAINMENT INOPERABLE "On March 2, 2016 at 1330 hrs. [EST], Secondary Containment became inoperable due to failure to meet a Surveillance Requirement (SR 3.6.4.1.3). "The inoperability was caused when Unit 2 Reactor Building Airlock doors were inadvertently opened simultaneously. "Secondary Containment was restored March 2, 2016 at 1331 hrs. when the doors were closed. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022, Rev. 3, section 3.2.7, as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee has notified the NRC Resident Inspector. | 79 | 100 | 0 | 79 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-03-02
51763 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-02-01 16:00 | 2016-03-02 17:06 | 2016-03-02 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE DUE TO CRIMPED TUBE The following information was provided by the State of Louisiana via email: "On February 1, 2016, a crew from NVI [Nondestructive & Visual Inspection, LLC] was performing radiography at a temporary jobsite located at the Loop Clovelly Facility on Highway 1 in Cutoff, LA. The crew was working in an area only accessible by boat. The crew made some exposures and did not notice the 'crank out' cable became wedged between the boat and the vessel support. The crew set [four] boundaries for the duration of the 'shots'/exposures. When the crew tried to retract the source into the shielded position, it would not [retract] because the 'crank out' tube was crimped, but was still connected to the exposure device. The source assembly remained out of the shielded position. When it was determined the source was not retractable, immediately the crew cleared the area and boundaries were established by distance and for unnecessary exposures. "The lead radiographer contacted the RSO and received instructions on how to secure/shield the area from potential/unnecessary exposures. This was after the crew had submerged the source in the water to provide shielding for the source. This was the initial notice and was not received until the source was secured in the shielded position and the event was over. The RSO did the actual retrieval and securing of the source. His direct reading pocket dosimeter reading was 593 mR and the crew's readings were 230 mR and below. "The exposure device and associated equipment ('crank out' control and source guide tube) were SPEC 150 exposure device S/N 1764 and a SPEC G-60, S/N WI1508 source. The source was 42 Ci of Ir-192. The equipment, the exposure device and source assembly were brought to SPEC [Source Production & Equipment Company] in St. Rose, LA and was evaluated and passed the quality assurance requirements. "The radiography crew was suspended from radiography work until they can be reinstructed in the NVIs' Operation Emergency and Safety Manual. The crew was sent to an Occupational Medicine Facility for blood-work. The test results were within normal limits. This is the corrective action. THIS EVENT IS CONSIDERED CLOSED. "NVI, Nondestructive & Visual Inspection, LLC is Departmentally [Louisiana Radiation Protection Division] approved and licensed to perform source retrievals. This is being reported as 10CFR Part 34.101(a)." Louisiana Event Report ID # LA-160002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-03-10
51762 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2016-03-02 02:53 | 2016-03-02 04:27 | 2016-03-02 | TURBINE TRIP CAUSING A REACTOR TRIP "The turbine tripped for an unknown cause followed by a reactor trip. All systems are functioning as designed. Operators have transitioned out of the EOP [Emergency Operating Procedure] network into normal operating procedures. The plant is stable in mode 3." All control rods fully inserted during the trip and no safety or relief valves lifted. The plant is in its normal shutdown electrical lineup. Emergency Feedwater actuation occurred to restore steam generator levels. The plant expects to make a press release. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1043 EST ON 3/2/16 FROM BARRY BRADBURY TO S. SANDIN * * * The licensee will not issue a press release for this event. The licensee will inform the NRC Resident Inspector. Notified R1DO (Cook). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-03-02
51761 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-02-29 | 2016-03-01 13:22 | 2016-04-08 | AGREEMENT STATE - STUCK SHUTTER IN THE NORMALLY OPEN POSITION The following Agreement State Report was received from the State of Texas via email: "On March 1, 2016, the Agency [Texas Department of State Health Services] received notice that on February 29, 2016, the licensee had discovered that a Berthold fixed gauge model MB7442D containing 30 milliCuries of cesium-137 had malfunctioned. The shutter was stuck in the open position. The gauge is normally left in the open position, and no exposure to the public is likely. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9383 * * * UPDATE FROM ART TUCKER TO JOHN SHOEMAKER AT 1746 EDT ON 4/8/16 * * * The following updated report was received from the State of Texas via facsimile: "The following information was provided by the manufacturer: Celanese of Bishop, TX contacted Berthold in early March [2016], to come out and repair a LB 7442 device with a broke shutter. This device was one of many that was sold by BSI until they went out of business in [approximately] 2003. The cause of the broke shutter was corrosion that had built up on the brass shutter shaft making it hard to turn. "When the Berthold service engineer was replacing the shaft he noticed that the source holder did not have a lock washer between the source holder and the source. The missing lock washer was not the cause of the broke shutter but has been an issue in the past with a plant in Wyoming that had some of the older BSI devices. Vibration caused the source to come lose from the source holder, the source dropped down into a position that prevented the shutter mechanism from cutting off the radiation beam when rotated which resulted in continuous high readings. Berthold worked with the NRC and the Wyoming plant to inspect the remaining shields to see if there were others that were missing the lock washer. It was noted that some did in fact have the lock washer in place but some did not. The sources that did not have lock washers on them were disassembled from their source holder and lock washers were added. "[The manufacturer has] not seen any other records of this happening except for the FMC Corp plant in Wyoming in 2010. At Celanese, the Berthold service engineer removed the source from the source holder and added a lock washer before placing it back into the shield. It was noted by the Berthold service engineer that Celanese appeared to have more of the same devices from that era. The issue in Wyoming could have been an isolated incident but definitely worth noting." Notified R4DO (Kellar) and NMSS Events Notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-03-09
51760 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2016-02-26 19:45 | 2016-02-27 09:20 | 2016-02-27 | CONFIRMED POSITIVE TEST FOR ALCOHOL A contract employee supervisor had a confirmed positive for alcohol during follow up FFD testing. The employee's access to all Entergy plants has been terminated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2016-02-27
51759 | 0 | SAINT ALPHONSUS HEALTH SYSTEM |  |  |  |  | 2016-02-26 11:20 | 2016-02-26 18:36 | 2016-03-11 | MEDICAL EVENT - UNDERDOSE TO PATIENT Notification from the licensee's Radiation Safety Officer, of a medical event that occurred on February 26, 2016 at 1120 MST, in which the Y-90 SIR-Sphere dose delivered to the patient's liver was less than the prescribed dose. The intended dose to the patient was 86 mCi, however, most of the dose remained in the catheter and it is estimated the patient received 13 mCi. The patient and attending physician have been informed and there was no harm to the patient. * * * UPDATE ON 3/11/16 AT 1459 EDT FROM ERIC COLAIANNI TO DONG PARK * * * The following was received via email: "Per NRC requirement noted in 10 CFR Subpart M, Section 30.3045 (a)(1) and 30.3045(d), this report is being submitted to provide details of a medical event that occurred on February 26, 2016. This event was previously reported by phone as required in 10 CFR, Subpart M, Section 30.345(c) on February 26, 2016 at 1836 EST to NRC Operations Center. "Patient was to receive 3.1 GBq of Y90 Theraspheres for treatment of right liver lobe hepatocellular carcinoma. Assay dose of 3.2 GBq was prepared via manufacture protocol and brought to the Interventional Radiology Suite and placed into the delivery apparatus. Manufacturer representative was on-site and provided further instruction on apparatus setup of infusion lines. Surefire catheter was deployed in the same location of the initial pre-treatment planning procedure. After angiography confirmed this position, the Theraspheres product was delivered and the entire delivery apparatus was removed from the patient and placed in the appropriate waste jar. After the infusion, and per protocol, post implantation measurements were taken both of the patient and infusion set. It was discovered that the patient's readings were significantly lower than expected along with higher readings than expected within the infusion line. Per protocol the patient was imaged post Y90 implantation which demonstrated activity noted in the target location. The radiologist's interpretation of that exam notes activity within target area with no activity seen in the chest or abdomen, outside the intended target area. Review of final calculations indicates that the patient received .491 GBq which was approximately 15% of the written directive. Imaging of the infusion lines within the waste jar demonstrate activity of the Y90 Theraspheres retained within the infusion lines. "After review with the Surefire catheter representative, it appears the Surefire apparatus may not have been fully extended which would have potentially provided an occlusion and prevented all of the Theraspheres from passing through the device. [The licensee is] continuing to investigate the cause. "The patient was contacted 3 days post procedure to follow up to determine any symptomatic episodes. The patient stated that the patient has not felt any effects from the procedure. The patient was also seen two weeks post procedure for review of any symptoms from the procedure. The patient to date has not reported any unusual symptoms. "[The licensee] ordered a different, and newer, Surefire product to use instead of the Surefire product that has been used for previous Y90 cases. [The licensee] discontinued the use of the Surefire product at issue for this procedure. "The patient was notified immediately post procedure that it appeared that the patient received less than the total intended dosage of the Y90 Theraspheres. The patient has been followed within clinic as set forth above. The patient will continue to be followed as medically appropriate." Notified R4DO (Proulx) and NMSS Events Resource via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-03-07
51758 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2016-02-26 15:47 | 2016-02-26 15:59 | 2016-03-03 | UNCONTROLLED SAFEGUARDS INFORMATION Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measure have not been employed. The license has notified the NRC Resident Inspector. * * * RETRACTION FROM PHILLIP BEABOUT TO HOWIE CROUCH AT 1322 EST ON 3/3/16 * * * Upon further review, the licensee has determined that this event does not meet reportability requirements and is retracted. The event will be logged appropriately in the facility's safeguards log. The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-02-26
51757 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2016-02-25 11:45 | 2016-02-26 12:32 | 2016-02-26 | POTENTIAL COMMON MODE FAILURE OF ITEM RELIED ON FOR SAFETY "While processing liquid effluent, process operators noticed that a set of uranium monitors, IROFS [Item Relied On For Safety] for the process system, registered a negative value. The process operators shut down process flows and contacted maintenance to come and check the uranium monitors. The uranium monitors checked out to be functioning correctly. The process was resumed until the condition repeated. The process operator then contacted maintenance again and shut the process down at 0300 [PST] pending further evaluation. "It appears that an interference material (likely copper or nickel) is masking some of the uranium present in the effluent causing the uranium monitors, which are based on colorimetry, to read low. "At 1145 PST on 2/25/16, AREVA Richland Reliability Engineering and EHS[and]L staff confirmed that this condition had not been anticipated in the ISA [Integrated Safety Analysis] and had the potential to cause a common mode failure of two IROFS. "The waste tank that contains the process effluent is a 30,000 gallon tank and currently contains about 3,000 gallons and based on laboratory analysis of a sample of the tank contents contains about 136 grams of low enriched (<5 wt. [percent] U235) uranium. A total of 2 kg has been processed through the tank since the last NCS [Nuclear Criticality Safety] required emptying and clean out of the tank. "Although the IROFS were degraded, it was determined that the IROFS were available and reliable to perform their function. However, this event meets the criteria in 10CFR70 Appendix A 24 hour reporting item 1, in that this condition had not been anticipated in the ISA and had the potential to cause a common mode failure of IROFS." The NRC Regional Office will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2016-02-26
51756 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-02-21 00:30 | 2016-02-25 16:35 | 2016-03-02 | POWER REDUCTION DUE TO AUTOMATIC OPENING OF A TURBINE BYPASS VALVE "On February 21, 2015, at approximately 0030 EST, with Fermi 2 in Mode 1 operating at 100 percent reactor thermal power, the West Turbine Bypass Valve (TBV) automatically opened in response to the number two High Pressure Turbine Stop Valve (TSV) cycling from full open to closed and then to 22 percent open. Reactor power was subsequently lowered to 91.5 percent reactor thermal power and the bypass valve closed. "Per Technical Specification Bases 3.3.1.1, TBVs must remain shut while reactor thermal power is at or above 29.5 percent to consider the TSV closure and Turbine Control Valve (TCV) fast closure Reactor Protection System (RPS) functions operable. The condition was recognized at the time of the event and the RPS functions were declared inoperable. The Limiting Condition for Operation was exited at 0031 EST following TBV closure. "Since the RPS functions were verified to remain enabled, Fermi 2 did not report this event within 8 hours of occurrence. However, this event was subsequently determined to meet the reporting criterion and is being reported pursuant to 10 CFR 50.72(b)(3)(v)(A). "The licensee informed the NRC Resident Inspector." The cause of the High Pressure Turbine Stop Valve cycling was due to a communication card failure that has since been corrected. This event was determined to be reportable at 1200 EST on 02/24/16. See EN #51755 for a similar event that occurred on 01/06/16. * * * UPDATE FROM JEFF GROFF TO STEVEN VITTO ON 03/02/2016 AT 1530 EST * * * "Upon further review, it was determined that this event also meets the reporting criterion of 10CFR50.72(b)(3)(v)(D) for a condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident. "Although this event was determined to be reportable at 1200 EST on 02/24/16, it met the reporting requirement on the date of the event (02/21/2015). "The licensee informed the NRC Resident Inspector." Notified R3DO (Valos). | 91 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-02-25
51755 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-01-06 15:14 | 2016-02-25 16:35 | 2016-03-02 | POWER REDUCTION DUE TO AUTOMATIC OPENING OF THE TURBINE BYPASS VALVES "On January 6, 2016, at approximately 1514 EST, with Fermi 2 in Mode 1 operating at 100 percent reactor thermal power, the East and West Turbine Bypass Valves (TBVs) automatically opened for 3 minutes and 32 seconds in response to the number one High Pressure Turbine Stop Valve (TSV) drifting from full open to 25 percent open. Reactor power was subsequently lowered to 91.0 percent reactor thermal power and the bypass valves closed. "Per Technical Specification Bases 3.3.1.1, TBVs must remain shut while reactor thermal power is at or above 29.5 percent to consider the TSV closure and Turbine Control Valve (TCV) fast closure Reactor Protection System (RPS) functions operable. The condition was recognized at the time of the event and the RPS functions were not declared inoperable since the functions were verified to remain enabled. "Since the RPS functions were not declared inoperable, Fermi 2 did not report this event within 8 hours of occurrence. However, after further evaluation, it was determined that this event met the reporting criterion. Accordingly, this event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(A). "The licensee informed the NRC Resident Inspector." The cause of the High Pressure Turbine Stop Valve drifting was due to an actuator malfunction that has since been corrected. This event was determined to be reportable at 1200 EST on 02/24/16. See EN #51756 for a similar event that occurred on 02/21/16. * * * UPDATE FROM JEFF GROFF TO STEVEN VITTO ON 03/02/2016 AT 1530 EST * * * "Upon further review, it was determined that this event also meets the reporting criterion of 10CFR50.72(b)(3)(v)(D) for a condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident. "Although this event was determined to be reportable at 1200 EST on 02/24/16, it met the reporting requirement on the date of the event (01/06/2016). "The licensee informed the NRC Resident Inspector." Notified R3DO (Valos). | 91 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-02-25
51754 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-02-24 11:00 | 2016-02-24 18:16 | 2016-02-24 | ELECTRICAL BREAKER ISSUE IDENTIFIED DURING AN ENGINEERING REVIEW "At 1100 CST on February 24, 2016, with the plant in cold shutdown (Mode 4), the shift manager was notified of a condition that could potentially prevent the automatic closure of the circuit breakers powering the emergency ventilation fans in the both the Division 1 and 2 emergency diesel generator rooms. These fans are not in Technical Specifications, however, they provide a support function to the emergency diesel generators, requiring that both diesel generators to be declared inoperable. This inoperability constitutes a condition that could potentially prevent fulfillment of the safety function of onsite AC power sources, and is being reported pursuant to 10 CFR 50.72(b)(3)(v). "Four additional breakers are affected by the same condition. These breakers supply power to Division 1 and 2 containment unit coolers and the Division 1 and 2 auxiliary building 141 ft. elevation general area unit coolers. The auxiliary building unit coolers are not in Technical Specifications, however, they provide a support function to the electrical distribution system. The Technical Specification required action is to declare both trains of the residual heat removal system (shutdown cooling mode) inoperable. This inoperability constitutes a condition that could potentially prevent the fulfillment of the decay heat removal safety function, and is being reported pursuant to 10 CFR 50.72(b)(3)(v). "Division 2 residual heat removal is operating in shutdown cooling, satisfactorily maintaining reactor coolant temperature. The affected breakers can be manually operated to start/stop their associated equipment, if necessary for operation." This condition was identified during an Engineering review. The licensee has compensatory measures in place. Long term corrective actions are under review. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2016-02-24
51753 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-02-22 | 2016-02-24 15:10 | 2016-02-24 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION AT METAL RECYCLING FACILITY The following information was provided by the Commonwealth of Pennsylvania via fax: "Notifications: The non-licensee discovered the event on February 23, 2016 and notified the Ohio Department of Health, who then notified our Department [PA Bureau of Radiation Protection] after normal business hours on the same evening. It is reportable per 10 CFR 30.50(b)(1)(i) and 20.2201(a)(i). "Event Description: On Monday, February 22, 2016, a large orphan radium-226 (Ra-226) source of unknown total activity or origin was shredded at the PSC Metals facility in Beaver Falls, PA. The recycled material was then shipped to two different Ohio facilities where it was discovered during an inbound radiation scan on February 23, 2016. "Cause of the Event: The Pennsylvania facility was [apparently] not performing outbound gamma radiation surveys on recycled materials. "Actions: The contaminated shredder, with gamma radiation levels of over 400 mrem/hr, has been isolated. The locker room, clothes, vehicles and workers have been surveyed and no contamination has been found. The gloves of two workers were found to have contamination. A reactive inspection occurred the evening of the 23rd to survey the entrance/gate area of the Beaver Falls facility, and a full emergency response occurred the morning of February 24, 2016. PA and OH Radiation Control Programs are onsite in their respective states and communicating findings. Surveys of employees, vehicles and equipment are ongoing. The response will continue until isolation and containment of Ra-226 is ensured. A local health physics service provider has also been contracted by PSC to assist with the decontamination operation. More information will be provided upon receipt. "Media Attention: None at this time, but OH may issue a Press Release. "Event Report ID No: PA160007" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-03-03
51752 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-02-23 | 2016-02-24 12:46 | 2016-02-24 | AGREEMENT STATE REPORT - SOURCE DISCONNECT ON FIXED GAUGE The following information was received from the State of Illinois via email: "On February 23, the licensee's radiation safety officer (RSO) called to advise that a sealed source of Cs-137 became separated from its handling rod within a fixed gauge and was now resting at the bottom of a seven foot 'well tube' within a nine foot conical reaction process vessel on their property. The well tube is centered on the vertical axis of the vessel and provides a protected environment for the source holder and rod. Previously the vessel had been emptied for routine maintenance and was being returned to service when the event took place. The current configuration is similar to that of its routine operating configuration other than the gauge is now 'always on' and cannot be returned to its normal shielded position, should the need exist. The plant plans on returning the vessel to service and refilling the vessel with reactants. This material should provide additional shielding such that accessible surface dose rates of the vessel are less than 1 mR/h. "The licensee is making arrangements with the manufacturer to come to the site and recover/dispose of the gauge and the source. Until that time, on site safety personnel and the process operating engineers have been advised of the situation and of the necessary precautions to observe should it become necessary to empty the vessel under emergency conditions. Under no circumstances will individuals be allowed access to the interior of the vessel without otherwise receiving explicit approval for the activity. "Pending recovery of the source by the manufacturer and receipt of the formal written report from the licensee, this matter remains open. No investigation by the Agency [Illinois Emergency Management Agency] is planned at this time." Fixed Gauge Manufacturer: Kay-Ray/Sensall Model Number: 7065 Serial Number: 28219 Source: Cs-137 Activity: 0.027 Ci Illinois Incident #: IL16001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-03-03
51751 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-02-23 17:00 | 2016-02-23 20:45 | 2016-02-27 | UNANALYZED CONDITION INVOLVING NORMALLY OPEN BATTERY ROOM DOORS "At CPNPP [Comanche Peak Nuclear Power Plant], eyewash stations are located just outside of the Class 1E battery rooms. The battery room doors are normally open and if a MELB [Moderate Energy Line Break] occurred on the demineralized water line connected to the eyewash station, the water could potentially spray onto the Class 1E safety related batteries. If this occurred, an electrical short could potentially cause a loss of both the batteries and the associated battery chargers. "This condition has been conservatively determined to be reportable per 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Currently, the demineralized water lines on the battery room eyewash stations for both Units 1 and 2 have been isolated, therefore, all safety related equipment is currently operable. Comanche Peak Engineering is performing a past operability review of this condition. "The NRC Resident Inspector has been notified." * * * RETRACTION AT 1821 EST ON 02/27/2016 FROM DANNY BRADFORD TO JEFF HERRERA * * * "On February 23, 2016 at 2045 [EST], Comanche Peak reported an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B). Specifically, the reported condition involved eyewash stations that are located just outside of the Class 1E battery rooms. The battery room doors are normally open and if a Moderate Energy Line Break (MELB) occurred on the demineralized water line connected to the eyewash station, the water could potentially spray onto the Class 1E safety related batteries. If this occurred, an electrical short could have potentially caused a loss of both the batteries and the associated battery chargers. This condition was conservatively determined to be reportable per 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. The demineralized water lines on the battery room eyewash stations for both Units 1 and 2 were isolated, and Comanche Peak Engineering initiated a past operability evaluation of this condition. "The past operability evaluation has been completed and shows that there are no operability concerns regarding a MELB impact on the Class 1E batteries, DC bus or Class 1E battery chargers. Therefore, Comanche Peak requests that the February 23, 2016, 10 CFR 50.72(b)(3)(ii)(B) reportable event for Units 1 & 2 be retracted." The NRC Resident Inspector has been notified. Notified the R4DO (Whitten). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-02-23
51750 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-02-22 13:45 | 2016-02-22 18:47 | 2016-02-22 | UNIT 1 SECONDARY CONTAINMENT INOPERABLE WHEN PERSONNEL OPENED BOTH ACCESS DOORS SIMULTANEOUSLY "On February 22, 2016 at 1345 [EST]. Secondary Containment became inoperable due to failure to meet a Surveillance Requirement (SR 3.6.4.1.3) on Unit 1. "The inoperability was caused when Unit 1 Reactor Building Airlock doors were inadvertently opened simultaneously. "Secondary Containment was restored February 22, 2016 at 1346 when the doors were closed. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022, Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee informed the NRC Resident Inspector. | 92 | 100 | 0 | 92 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-02-22
51749 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-02-22 13:11 | 2016-02-22 16:19 | 2016-02-22 | SPURIOUS ACTUATION OF ONE EMERGENCY SIREN DURING PLANNED MAINTENANCE Limerick Generating Station Main Control Room was informed that a Limerick Emergency Preparedness Zone (EPZ) siren located in Skippack Township, Montgomery County, Pennsylvania was sounding by an off-site vendor. This notification is being made in accordance with SAF 1.9 due to a spurious actuation of Limerick Emergency Preparedness Zone (EPZ) siren. "The alarm actuated for approximately 90 seconds following preventative maintenance. "No actual plant emergency exists. "All Limerick EPZ sirens remain functional; no other reportability threshold(s) have been met or exceeded." The licensee informed State and local authorities and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-02-22
51748 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-02-18 | 2016-02-22 14:04 | 2016-02-22 | AGREEMENT STATE REPORT - LOST DENSITY GAUGE The following was received from Texas via email: "On February 22, 2016, the Agency [Texas] received notice that while under reciprocity in Louisiana, the licensee had lost a Thermo Fisher model 5192 (sn B8191) with 200 milicuries of Cesium-137 (sn 5854CP). Exposure to the public is unlikely due to the design of the device. It is not known whether the device was lost or stolen. The Louisiana Department of Environmental Quality is conducting the investigation. Addition information will be provided as it is received in accordance with SA-300." The device was lost in Louisiana but reported to Texas by a Texas licensee. The state of Texas notified the state of Louisiana and the NRC. Louisiana will conduct an investigation of the issue. Texas Incident # I-9380 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-03-01
51747 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2016-02-20 03:30 | 2016-02-20 09:12 | 2016-02-20 | DEGRADED CONDITION DISCOVERED ON PRESSURIZER SAFETY RELIEF VALVE WELD "During the CCNPP [Calvert Cliff Nuclear Power Plant] Unit 1 Refueling, [an ultrasonic test] examination of the Unit 1 dissimilar metal weld (DMW) of the pressurizer safety relief valve RV-201 safe end weld found an indication that is approximately 80 percent though-wall, inside diameter connected axial flaw in weld #4-SR-1006-1. "This is an ASME Class 1 component and Unit 1 has entered the requirements of Technical Requirements Manual (TRM) 15.4.3.A. "CCNPP Event #4254." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-02-20
51746 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-02-19 | 2016-02-19 17:06 | 2016-02-19 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following was received via email: "On February 19th, 2016, a patient was prescribed and administered a 1.87 GBq Yttrium-90 [Thera-Sphere] treatment. The patient only received 0.28 GBq. [There are] no details as to the cause of the misadministration. [The Radiation Safety Officer] will provide a detailed report next week." Florida Incident # FL16-033 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-02-29
51745 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-08-27 | 2016-02-19 12:35 | 2016-02-19 | AGREEMENT STATE REPORT - MEDICAL OVERDOSE The following was received via email: "On August 27th 2015, a patient with 21st [Century] Oncology who was prescribed a 67.13 mCi dose of Sm-153 received an 86.9 mCi dose. The resulting over dose was more than 29.5 [percent] of the prescribed dose. The error was discovered through discrepancies in their pharmacies inventory when a new order was created for a new patient. "On Feb 15, 2016, [21st Century Oncology] were preparing an order for Sm-153 for a new patient. The nurse referred to the last administered Samarium case (August 27, 2015) for information on activity, patient weight and pricing. In order to clarify the relation between dosage and patient weight, he asked the physics staff to perform a second check of the records. When the requested check was done the following error was discovered. "Upon re-evaluation of the treatment procedure, the physics staff determined that the dosage of 91 mCi received from the pharmacy was not correctly calculated for the patient weight that was specified on the original order. The pharmacy was then requested to fax back the original order (Form J). The fax which they sent confirmed the correct weight of the patient (148 lbs). For this weight a correct calculation would have indicated an activity of 67.13 mCi. Instead the pharmacy had shipped the (incorrect) activity of 91 mCi. The resulting delivered dosage was 29.5 [percent] more than the prescribed dose. Thus [the staff] concluded that a medical event had occurred. "The Radiation Oncologist notified the referring physician on February 16, 2016. The Radiation Oncologist also will note this communication in the patient's chart." Florida Incident Number: FL 16-029 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-02-29
51744 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2016-02-18 21:27 | 2016-02-19 11:38 | 2016-02-19 | AGREEMENT STATE REPORT - TWO UNUSED PROCESS GAUGES SENT TO SCRAP YARD International Paper performed an inventory of their sources and realized that while performing demolition work at their facility, two unused process gauges were removed from the site. The removal of the gauges was outside the scope of the demolition work. The two process gauges were located on long poles, were removed from the site using a crane, and were sent to a nearby scrap yard. The South Carolina Division of Health and Environmental Control sent an inspector to the scrap yard and he was able to find and recover both gauges. The shutter on one gauge had remained closed and the second gauge shutter was partially open and reading 50 mR/hour on contact. The first gauge was recovered at 1220 EST and the second gauge was recovered at 1315 EST and the shutter was shut. Wipe tests on both gauges were negative. The gauges were returned to International Paper and are locked in a secure location. No personnel exposures were expected from this incident. Gauges: Cs-137 50 mCi each (in 1988) TN Tech Model 5219 Serial Numbers: TNB61 and TNB64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2016-02-29
51743 | -1 | NUCLEAR LOGISTICS INC |  |  |  |  | 2016-02-18 | 2016-02-18 18:29 | 2016-02-26 | PART 21 - CONTACTOR MAKING NOISE The following was received via fax: "Initial notification of a potential 10 CFR Part 21 condition. "Pursuant to the rules of 10 CFR 21.21 this initial notification is being submitted to the NRC to identify a potential reportable condition that is currently under evaluation. "FPL [Florida Power & Light] Turkey Point has identified a contactor that was making a considerable amount of noise that was not expected. The unit was continuing to functionally operate, however the source of the noise is cause for investigation. "The contactors are a non-standard Size 3 and Size 4 Freedom Series Starter/Contactor. These units are currently under evaluation and review by NLI [Nuclear Logistics Inc.] to determine the root cause of the identified condition to determine if the contactor contains a defect. "To date there have been no reported failures of this item to perform the intended safety function. These components were first supplied in September 2002 to Duke Oconee with no reported issues identified. The units reported by FPL Turkey point were supplied in May and December 2011. They have been installed into other facilities including the Duke Shearon Harris plant in December 2013. Although the increased noise is undesirable, it is not presenting a significant condition adverse to quality that could create a substantial safety hazard. Preliminary testing has confirmed that the safety related performance characteristics have not been degraded. However, due to the number of utilities which may have these components in service, this notification is being submitted to identify the condition to the industry. "NLI plans to have the completed report submitted by 3/15/2016." * * * RETRACTION FROM TRACY BOLT TO JOHN SHOEMAKER AT 1847 EST ON 2/26/16 * * * This retraction is a brief summary from a report received from Nuclear Logistics Inc. via email: "This retraction is being submitted to the NRC to provide additional information for the initial notification provided on 2/18/2016. After evaluating the identified condition, it has determined that there is no defect within the contactor that if left uncorrected would create a substantial safety hazard. This issue is not considered reportable per the rules of 10 CFR Part 21." Notified R1DO (Ferdas), R2DO (Shaeffer), R3DO (Stone), R4DO (Whitten), and Part 21/50.55 Reactors via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-02-18
51742 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2016-02-16 06:31 | 2016-02-18 15:48 | 2016-02-18 | WELD OVERLAY FLAW DID NOT MEET ACCEPTANCE CRITERIA "As part of the upgrade to the full structural weld overlays (FSWOL) per NRC-approved ISI [In-service Inspection] Alternative HNP-ISI-ALT-15-01, the surface of the existing weld overlay for the 1E Recirculation weld (1B31-1RC-12BR-E-5) was ground to prepare the surface for receipt of a new Alloy 52M overlay. Upon performance of the subsequent liquid penetrant testing examination, it was discovered that the as-found condition of the flaw did not meet acceptance criteria. It was determined that the flaw constituted a defect in the primary coolant system that could not be found acceptable per ASME Section XI. Therefore, this event notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A). "Evaluation of the flaw found in the weld overlay suggests that the non-satisfactory liquid penetrant surface examination is a result of the propagation of the original flaw that was found on the 1E Recirculation Loop Piping. The flaw is axial in nature and therefore there is no impact on structure integrity degradation. No leakage is currently present or was seen during the previous operating cycle from this flaw. There is also reasonable assurance that there was not a breach in the credited RCS [Reactor Coolant System] boundary during the previous operating cycle. "As part of the corrective action to fix the flaw, the 1E Recirculation weld will be upgraded to full structural weld overlay per the NRC-approved ISI Alternative." The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2016-02-18
51741 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2016-02-17 10:35 | 2016-02-17 17:05 | 2016-02-17 | SECONDARY CONTAINMENT INOPERABLE DUE TO DOOR INTERLOCK MALFUNCTION "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(C), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and 10 CFR 50.72(b)(3)(v)(D), an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. An employee entered a secondary containment interlock and identified that both doors of the interlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the interlock and notified the Main Control Room Supervisor. Both doors in the interlock were open for approximately 5 seconds. With both doors open, TS SR 3.6.4.1.2 was not met. This rendered secondary containment inoperable per TS 3.6.4.1. Reactor Building differential pressure, as observed in the Main Control Room, has remained less than -0.25 inches H20 at all times. Initial investigation determined that a mechanical interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the interlock." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-02-17
51740 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-06-02 | 2016-02-17 12:26 | 2016-02-19 | AGREEMENT STATE REPORT - IRIDIUM 192 SOURCE LOST DURING SHIPMENT The following was received from Florida via email: "On 2 June 2015, an Ir-192 source was shipped via common carrier from Sand Lake Cancer Center in Orlando, Florida to Alpha-Omega Services [AOS] in Vinton, Louisiana. The common carrier states on the travel history that the source was unable to be shipped and was returning to the shipper. There is no date or time for the actual return, and no signature on file (as required). A representative from Elekta reported the 4.7Ci Ir-192 source missing on 17 February 2016 after receiving the information from Sand Lake. Sand Lake and AOS have been in contact between themselves and the common carrier and were unable to locate the source. [The Elekta representative] has already reported this incident to Georgia and is currently trying to get in touch with the common carrier RSO." Florida incident #: FL16-032 * * * UPDATE PROVIDED BY KELLIE ANDERSON TO JEFF ROTTON AT 1136 EST ON 02/19/2016 * * * The following information was provided via email: Alpha-Omega Services reported to the State of Florida that the source has been located and it is in the Alpha-Omega Services offices in Vinton, LA where the source was being shipped to originally. I seems that it was an administrative error that caused the source to be reported as missing. The State of Florida considers incident # FL16-032 to be closed. Notified the R1DO (Dentel), R4DO (Vasquez), and NMSS Events Notification Group via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-02-25
51739 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2016-01-09 09:46 | 2016-02-17 10:36 | 2016-02-17 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATOR "This 60-day optional telephone notification is being made in lieu of an LER submittal, as allowed by 10 CFR 50.73(a)(1). This notification is made pursuant to the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of one of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). "On January 9, 2016, at 0946 Eastern Standard Time (EST), an invalid actuation of EDG 2 occurred. During the performance of procedure 0PT-12.2.1B, 'ECCS D/G #2 Logic Test,' procedure steps were performed out of sequence. As a result, the EDG 2 control logic was not properly defeated to prevent the auto-start prior to testing portions of the Emergency Core Cooling System (ECCS) EDG 2 logic. "EDG 2 responded properly to the auto-start signal. The actuation was complete, in that the EDG started and ran unloaded. EDG 2 was returned to standby status at 1130 EST. Since no actual bus under voltage condition existed which required the EDG to start, and the start was not in response to actual plant conditions satisfying the requirements for initiation, this event has been classified as an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-02-17
51738 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-02-16 08:27 | 2016-02-16 13:44 | 2016-02-16 | AUXILIARY FEEDWATER PUMP AUTO START DUE TO FEED PUMP TRIP "At 0827 [EST], the 21 and 22 Aux Feedwater pumps auto started due to a trip of the running Steam Generator Feed pump (22). The 22 Steam Generator Feed pump tripped while swapping from heating steam to main steam in accordance with normal operating procedures. The cause of the 22 Steam Generator Feed pump trip is being investigated at this time. "The auto start of the Unit 2 Auxiliary Feedwater pumps is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any system listed in Technical Basis 11.3.3 except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.'" The licensee has notified the NRC Resident Inspector and will notify the Lower Alloways Creek Township. | 0 | 4 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-02-16
51737 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2016-02-16 | 2016-02-16 10:32 | 2016-02-16 | AGREEMENT STATE REPORT - DAMAGED FIXED NUCLEAR GAUGE The following report was received from the State of Tennessee via email: "On February 16, 2016 the RSO [Radiation Safety Officer] of Jarden Zinc reported that one of their fixed nuclear gauges (make, model, serial number not reported) had been damaged. Details concerning the cause of the damage were unknown. Surveys of the damaged gauge indicate that the gauge shutter is in the closed position, no radiation beam is emanating from the gauge, and there do not appear to be any exposures to staff. The gauge has been moved into storage until the manufacturer can arrive to inspect the gauge. The RSO indicated that follow-up information to the Tennessee Division of Radiological Health would occur within 24 hours." State Event Report ID NO.: TN-16-021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-02-24
51736 | 0 | DOMINION RESOURCES SERVICES |  |  |  |  | 2016-02-15 | 2016-02-16 10:05 | 2016-02-16 | LOST TRITIUM EXIT SIGNS "Pursuant to Federal Regulation 10 CFR 31.5(a), Dominion Transmission, Inc. is a general licensee of the NRC because it possesses and uses byproduct material in the form of tritium exit signs (TES). Consistent with Federal requirements, Dominion is providing the subject report regarding two (2) lost TES. "Dominion has established a company-wide program to inventory TES. Inventory efforts have identified that the following TES which were present at the previous inventory cannot be located and are presumed lost: "Serial Number: CO563528 Model Number: BX Activity: 20 Curies "Serial Number: CO563530 Model Number: BX Activity: 20 Curies "Dominion conducted this most recent inventory during a recent construction re-modeling project involving the building of a new addition at its Lightburn Station. Dominion has no information that these TES have been transferred. Accordingly, and in addition to physical searches for the TES conducted by Dominion, Dominion interviewed key on-site personnel, contractors and vendors who had worked on the site. Interviewed personnel include the Dominion project manager, site safety personnel and the lead contractor who performed the demolition. None of these interviewees recall disposing of the TES. "Dominion also contacted the local trash removal services (C and D Dumpster) and they have confirmed that a dumpster was removed from the site during the remodeling project. Dominion therefore contacted S and S Landfill. S and S Landfill has no equipment available to monitor for radiation levels and consequently could not provide us with any relevant information as to the possible disposition of these TES. "As a result of these investigative efforts, Dominion concluded that these TES are lost. We have also confirmed that all other TES are currently in place at the Lightburn Station facility." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | WV | MAT | [5 empty] | 0 | 2016-02-24
51735 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-02-15 | 2016-02-15 08:47 | 2016-02-15 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following report was received from the State of Georgia via email: "The following was reported to the State of Georgia on February 15, 2016. "The patient was prepped for the delivery of doses of 18 and 21 Gy to 14 subcentimeter brain metastases with Gamma Knife stereotactic radiosurgery. The frame adapter was placed on the patient's stereotactic head frame by a Gamma Knife trained registered nurse, supervised by Authorized Medical Physicist [AMP], and Authorized User [AU]. After five of the planned 14 lesions were treated, the patient was given a break in order to use the restroom and for additional medication. During this treatment break, the AU and AMP entered the room to release the patient from the restraining device and assist [the patient] to the rest room. It was at that point that it was discovered that the restraining device was locked, but not in the correct position. The displaced distance was measured and determined to be a maximum discrepancy of 2 cm in one plane. The AMP and AU applied the displacement to the treatment plan to determine which areas were treated and which were not. It was determined that a potential misadministration had occurred. "The RSO [Radiation Safety Officer] was notified to discuss the course of action. Following discussions with the AMP, AU, the medical director, the prescribing physician and radiation safety officer, it was decided that there was a potential medical event or misadministration as defined in 391-3-17-.05(115)(a)3 or 391-3-17-.05(115)(b). "The cause of the event is uncertain at this time. The head restraining device should not have been able to be secured unless it was in the proper position. An investigation is ongoing and additional information is being sought. "The patient received an unintended radiation dose to normal brain tissue, however, it was determined by the authorized user in consult with the medical physicist that little clinical effect will be demonstrated due to this inadvertent exposure. The patient, the patient's family and the patient's referring physician were informed of the event. After extensive discussions, it was agreed by all parties that the treatment would be completed to ensure that the correct dose is delivered to the remaining target areas. "This is all the data available at the moment. A reactive inspection is currently underway and updates are soon to follow." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2016-02-23
51734 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-02-14 20:58 | 2016-02-14 23:13 | 2016-02-14 | AUTOMATIC REACTOR TRIP ON MAIN GENERATOR PROTECTION TRIP "This 4-hour and 8-hour notification is being made to report that Salem Unit 2 had an unplanned automatic reactor trip. The trip occurred because the Unit 2 main generator tripped on generator protection with reactor power greater than P-9 (49%). The cause of the generator protection trip that resulted in the reactor trip is unknown at this time. A troubleshooting team is being assembled to determine the exact cause for the generator protection actuation. "All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. The motor driven and steam driven auxiliary feed pumps started as expected on steam generator low level. "Salem Unit 2 is currently in mode 3. Reactor Coolant System pressure is at 2235 psig and temperature is 547 degrees Fahrenheit with decay heat removal via the main steam dumps and auxiliary feedwater systems. Unit 2 has no active technical specification action statement in effect requiring a lower mode of operation. "No safety related equipment or major secondary plant equipment was tagged for maintenance prior to the event. There were no personnel injuries as a result of this event." There was no impact on Salem Unit 1. The licensee informed the NRC Resident Inspector and will inform the Lower Alloways Creek Township (LAC). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-02-14
51733 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2016-02-13 10:00 | 2016-02-13 14:45 | 2016-02-13 | RADWASTE BUILDING NOBLE GAS MONITOR OUT-OF-SERVICE "On 2/10/2016 at 1000 PST, Columbia entered a planned evolution to perform channel functional tests on the RadWaste Building noble gas monitor (WEA-RIS-14). Compensatory measures were implemented per station procedures. The station is experiencing equipment issues and the monitor has not been restored within 72 hours (2/13/2016 at 1000 PST) from the start of the outage. The extended outage of this radiological monitoring instrument is, therefore, being reported as a major loss of radiological assessment capability in accordance with regulation 10 CFR 50.72(b)(3)(xiii). "Compensatory measures will remain in place until the WEA instrument is restored. "The NRC Resident Inspector has been notified. "Note: Reactor Power is 75 percent due to a planned plant downpower for unrelated scheduled work with a planned return to 100 percent at 1900 PST on 2/14/16." | 75 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-02-13
51732 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-02-13 02:06 | 2016-02-13 09:09 | 2016-02-13 | SECONDARY CONTAINMENT INOPERABLE "On 02/13/2016 at 0206 CST, an unexpected trip of a Fuel Building ventilation exhaust fan occurred and secondary containment differential pressure became positive. Secondary containment was declared INOPERABLE when Technical Specification-required differential pressure was not being maintained and entered LCO 3.6.4.1 Action A.1 "At 0256 (CST), the standby gas treatment system was started and secondary containment differential pressure was restored to Technical Specification requirements at 0257 CST. "This loss of secondary containment is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "The cause of the fuel building exhaust fan trip is unknown at this time. The NRC Resident Inspector has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-02-13
51731 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-02-11 | 2016-02-12 13:07 | 2016-02-12 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FOUND IN STUCK OPEN POSITION The following information was provided by the State of Texas via email: "On February 12, 2016, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that on February 11, 2016, while performing a routine inspection of a Berthold model LB 300 l nuclear gauge, they found the source shutter was stuck in the open position. Open is the normal position for the gauge shutter. The gauge contains a one millicurie (original activity, current activity 0.07 mCi.) Cobalt-60 source. The RSO stated the dose rates at and around the gauge are normal. He [the RSO] stated no individuals, including members of the general public, will be exposed to any additional radiation due to the failure. The RSO stated the manufacturer has been contacted and will be at the licensee's facility the week of February 15, 2016 to fix or replace the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-02-22
51730 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2016-02-11 23:05 | 2016-02-12 03:51 | 2016-02-12 | EMERGENCY DIESEL GENERATOR AUTO-STARTED DUE TO THE LOSS OF A STATION SERVICE TRANSFORMER "On 02/11/2016, at 2305 [EST], Ginna Station experienced a loss of Station Service Transformer 12A causing Emergency Diesel Generator 1A to automatically start due to under-voltage signals to safeguards buses 14 and 18. All plant systems responded as designed. Control room operators stabilized the plant per abnormal operating procedures. The plant is currently in a 100/0 electrical lineup [supplied by the 12B Service Station Transformer] on the off site circuit 767 with the 1A Emergency Diesel Generator secured. The loss of the station service transformer is currently under investigation. "This is reportable as a valid system actuation that was not part of a pre-planned sequence during testing. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-02-12
51729 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2016-02-11 15:04 | 2016-02-11 19:38 | 2016-02-11 | AUTOMATIC START OF EMERGENCY DIESEL GENERATOR AND LOSS OF SHUTDOWN COOLING "At 1504 EST on February 11, 2016, with the plant shutdown in a forced outage, the Division 1, 4.16 Kv Safety Bus (EH11) lost power. Division 1 Shutdown Cooling was in service at the time and the Division 1 Shutdown Cooling pump A tripped. The Division 1 Emergency Diesel Generator (EDG) started and loaded EH11 as designed. However, the Emergency Service Water (ESW) A pump, which supplies cooling water to the EDG did not start. Due to the absence of cooling water to the EDG, operators took manual action to secure the Division 1 EDG. Division 2 Shutdown Cooling was operable during this transient and was subsequently started. The Division 1 Shutdown Cooling common suction isolation valve (1E12F0008) had previously been de-energized in the open position to support planned maintenance. The Division 2 Shutdown Cooling isolation valve was not affected by the loss of bus EH11. Shutdown Cooling was re-established at 1544 EST using the Division 2 Shutdown Cooling pump. Reactor coolant temperature rose from approximately 89 degrees Fahrenheit to 115 degrees Fahrenheit during the event. The cause of the loss of EH11 and subsequent failure of ESW A pump to start are currently under investigation. "This event is being reported under 10 CFR 50.72(b)(3)(iv)(A) as a specific system actuation due to the auto start of the Division 1 EDG on a valid signal. "The plant remains shutdown with Division 2 Shutdown Cooling in operation. The plant is in a normal electrical line up with the exception of bus EH11 being de-energized." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-02-11
51728 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-02-11 | 2016-02-11 15:38 | 2016-02-11 | AGREEMENT STATE REPORT - BRACHYTHERAPY DEVICE MALFUNCTION RESULTING IN UNDERDOSE The following information was received from the State of New Jersey via fax: "One of the hospital's authorized medical physicists reported that a patient was due to receive a therapeutic treatment from the center's HDR [High Dose Rate] unit. During administration of the fraction, there was a device malfunction. The source was safely returned to the shielded position, but the patient did not receive the prescribed dose for the fraction. There was an underdose. The patient and the patient's physician have been informed. The unit is a Nucletron MicroSelectron Model 106.990. Additional details will be forthcoming from the hospital." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-02-19
51727 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-06-17 | 2016-02-11 15:43 | 2016-02-11 | AGREEMENT STATE REPORT - EXOTHERMIC REACTION IN SUPERCOMPACTOR ROOM INVOLVING LICENSED MATERIAL The following historical information was received from the State of Tennessee via email: "During a routine inspection, it was discovered through review of Toxco Radiological Occurrence Reports that Toxco had an event on June 17, 2013. In the Building A Supercompactor Room, a 55-gallon drum exploded due to an exothermic reaction. The cause was suspected to be the inadvertent packing of nitro-cellulous filters being placed in a waste drum of 3.7 mCi of I-125 contaminated personal protective equipment from Boston Heart Laboratory. The compactor was secured and no indication of radioactive material was discovered in the vicinity beyond the compaction cell. All personnel passed through a personnel contamination monitor without incident. The licensee performed a root-cause analysis determining that Boston Heart Laboratory had packed the nitro-cellulous filters into the waste containers. The licensee isolated two additional 55-gallon drums for return to Boston Heart Laboratory." State Event ID No.: TN-13-195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-02-19
51726 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2013-02-04 | 2016-02-11 15:43 | 2016-02-11 | AGREEMENT STATE REPORT - MISSING NRD IONIZER DEVICE The following historical information was received from the State of Tennessee via email: "On March 26, 2013, Kilgore Flares Company and the Division of Radiological Health (DRH) discovered that one of Kilgore's NRD Ionizer devices, model P-2035; S/N A2GK795, was lost. The device contained 40 mCi of Po-210. The device was shipped 10/09/08 from NRD, LLC, located in Grand Island, NY. It was taken out of service in October 2009 when Kilgore renewed the lease for the device. Kilgore was under the impression that the ionizer had been sent back to NRD the previous year. Kilgore did not learn until after the inventory list was sent to DRH February 4, 2013, that NRD had not received them. The device was searched for but could not be located. The boxes that contained the devices sat in the shipping department for some time and this is believed to be where the device came up missing. Kilgore reported that they now keep all devices, being sent back, in the Maintenance Planners office until sealed up for shipping. Kilgore provided a report to DRH on 4/2/13." State Event Report ID No.: TN-13-048 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-02-19
51725 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2016-02-10 22:07 | 2016-02-11 01:20 | 2016-02-11 | SECONDARY CONTAINMENT INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and 10CFR50.72(b)(3)(v)(D), event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. LaSalle Station's Unit 1 and Unit 2 were in Mode 1. At 2207 [CST] [on 2/10/16], Secondary Containment Differential Pressure dropped below the Technical Specification (TS) 3.6.4.1 minimum of 0.25 inches water vacuum. The initial indications are a failure of one Unit 1 Reactor Building Exhaust Isolation Damper, which resulted in a trip of the Unit 1 Reactor Building Exhaust Fans. At 2245, Secondary Containment Differential Pressure was restored to within the TS 3.6.4.1 limits by securing and isolating the Unit 1 Reactor Building Ventilation System. Troubleshooting plans are being developed to determine cause of the damper failure and to correct the deficient condition." The licensee has notified the NRC Resident Inspector. | 91 | 100 | 0 | 91 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-02-11
51724 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2016-02-10 09:16 | 2016-02-10 12:20 | 2016-02-10 | OFFSITE NOTIFICATION VIA NEWS RELEASE CONCERNING TRITIUM LEVELS IN GROUNDWATER MONITORING WELLS "This report is being made pursuant to 10 CFR 50.72(b)(2)(xi) for any event or situation related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. On February 10, 2016 at approximately 0916 EST, Entergy provided a news release of updated findings from follow-up groundwater tests at Indian Point that confirm anticipated fluctuations in tritium levels. The most recent samples from on-site groundwater monitoring wells show elevated levels of tritium. The levels of tritium identified including the new readings pose no threat to public health and safety. The tritium levels remain less than one-tenth of one percent of Federal reporting guidelines. Entergy continues to provide voluntary notifications to state agencies and stakeholders. Sampling will continue to be taken regularly from the monitoring wells in accordance with plant procedures." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-02-10
51723 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2016-02-10 02:47 | 2016-02-10 06:29 | 2016-02-10 | INADVERTENT ACTUATION OF ONE EMERGENCY SIREN "At approximately 0354 [EST] on 2/10/2016, the Nine Mile Point Unit 1 Control Room was notified by Exelon Emergency Preparedness of the inadvertent actuation of one Oswego County Notification Siren at approximately 0247 on 2/10/2016. It is unknown at this time why the inadvertent alarm occurred. Siren repair personnel (ANS Services) have been dispatched to isolate the siren and begin repair work. The siren has been silenced. Alternate notification of the public in the area is through Hyper Reach. "The Oswego County Emergency Management Office has issued a news release identifying the inadvertent actuation of the emergency siren." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-02-10
51722 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-02-10 02:47 | 2016-02-10 05:42 | 2016-02-10 | INADVERTENT ACTUATION OF ONE EMERGENCY SIREN "The purpose of this report is to provide a telephone notification under 10 CFR 50.72(b)(2)(xi) to notify the NRC of the inadvertent actuation of one Oswego County notification siren at approximately 0247 [EST] on 02/10/2016. The James A. FitzPatrick Control Room was notified by Oswego County 911 at 0359 on 02/10/2016 of the inadvertent actuation. It is unknown at this time as to why the inadvertent alarm actuated. Siren repair personnel (ANS Services) have been dispatched to isolate the siren and begin repair work. The siren has since been silenced. Alternate notification of the public in the area is through Hyper Reach. "The Oswego County Emergency Management Office issued a News Release identifying the inadvertent actuation of the emergency siren." The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-02-10
51721 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-02-09 21:42 | 2016-02-10 02:17 | 2016-02-10 | SECONDARY CONTAINMENT INOPERABLE "At 2142 [CST] on February 9, 2016, Reactor Building differential pressure did not meet the required 0.25 inches of vacuum water gauge due to failure of the control system. At 2205, the Unit 3 Reactor Building Ventilation System was secured and manually isolated. The Reactor Building differential pressure returned to [greater than or equal to] 0.25 inches of vacuum water gauge at 2207. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.1. As a result, entry into Technical Specifications 3.6.4.1 condition A was made due to Secondary Containment being inoperable. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-02-10
51720 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-02-09 14:15 | 2016-02-09 17:25 | 2016-02-09 | ECCS DISCHARGE TO RCS VIA CHARGING SYSTEM "At 1415 EST on 02/09/2016, Sequoyah Unit 1 was at 0 percent power (mode 3, 526F, 2235 psig) when a low steam line pressure Safety Injection actuated from Loop 2 Steam Generator. Prior to this event, the Loop 2 Main Steam Isolation Valve bypass was opened at 1413 EST for main steam line warm up in preparation for unit startup. Loop 2 Main Steam Isolation Valve bypass closed automatically following low steam line pressure Safety Injection. "Following the Safety Injection, all safety-related equipment operated as designed. "Current Reactor Coolant System temperature and pressure - Unit 1 is currently being maintained in Mode 3 at approximately 517 F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via steam generator atmospheric relief valves. There is no indication of any primary to secondary leakage. The electrical alignment is normal with shutdown power supplied from off-site power. "There is no operational impact to Unit 2. "The cause of the Safety Injection actuation is under investigation. "This event had no impact on the health and/or safety of the public. The NRC Resident Inspector has been notified." Due to RCS pressure, the only system that injected into the RCS was the charging system. The AFW system initiated to feed the steam generators and the Emergency Diesel Generators started but did not load. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-02-09
51719 | 0 | PA DEPT OF ENV PROTECTION |  |  |  |  | 2016-02-03 13:00 | 2016-02-09 12:21 | 2016-02-09 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION The following was received from Pennsylvania via fax: "The licensee discovered the event on February 4, 2016, and notified the Department [PA Dept of Environmental Protection] after normal business hours on Friday, February 5, 2016. It is reportable per 10 CFR 30.50(b)(1)(i). "A 30 year old female patient was treated with 61.4 milliCuries of Iodine-131(I-131) for thyroid cancer and released, with proper discharge instructions, at noon on 02/03/16. The patient then returned to the emergency room (ER) at the same location at [1300 EST]. The patient did not disclose the previous I-131 treatment to ER staff until later that evening. The ER staff immediately contacted radiation safety personnel at 0100 on 02/04/16. The patient was then segregated and all access to the original room was controlled and posted properly. Surveys were taken and all linens and other potentially contaminated materials were collected for proper storage and decay. A radiation survey performed at 0930 on 02/04/16 estimated the potential maximum radiation exposure to staff to be 3 millirem. "Patient failed to follow the discharge instructions given. "A reactive inspection is planned by the Department. More information will be provided upon receipt." Pennsylvania Event Report ID #: PA160006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-02-17
51718 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-02-04 | 2016-02-09 11:47 | 2016-02-09 | AGREEMENT STATE REPORT - LEAKING NI-63 SEALED SOURCE The following information was provided by the State of Washington via email: "Radiation Safety staff at WSU [Washington State University] discovered a GC ECD [Gas Chromatography - Electron Capture Detector] to be leaking during the semi annual sealed source leak test. The sealed source leak test revealed 0.00686 microCuries of removable contamination. The source was removed from the laboratory where it was stored in a box and immediately transferred to radioactive waste, pending disposal. The ECD had been stored in a box and had not been used for several years. Both the source location and the GC were surveyed to ensure contamination was not present. Survey results were well below regulatory limits." The source manufacturer/model number: Hewlett Packard model 5890A, serial number M2044. The sealed source contains 0.015 Ci of Ni-63. WA Incident Number: WA-16-005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-02-17
51717 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-02-09 08:12 | 2016-02-09 09:54 | 2016-02-18 | PLANNED MAINTENANCE OF THE PLANT COMPUTER SYSTEM "Planned maintenance of the Plant Computer System (PCS) will cause a loss of emergency assessment capability. "Beginning February 9, 2016, PCS data will not be available to the following Comanche Peak Nuclear Power Plant (CPNPP) facilities due to planned PCS software modifications: -Emergency Operations Facility [EOF] -Backup EOF -Operations Support Center "The Emergency Response Data System [ERDS] will also be unavailable. "The planned maintenance of the PCS is being reported as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii) because the duration is expected to be more than 72 hours and the data to the Backup EOF is also affected. "CPNPP has compensatory measures in place to ensure timely emergency classification, protective action recommendation and emergency notification, as needed. "The PCS modification is expected to be complete by February 18, 2016. A follow-up ENS [Emergency Notification System] communication will be made when the EOF assessment capability is restored." The Licensee has notified the NRC Resident Inspector. * * * UPDATE FROM RAUL MARTINEZ TO STEVEN VITTO ON 02/18/2016 AT 1541 EST * * * "The planned maintenance of the Comanche Peak Plant Computer System (PCS) that began on February 9, 2016 is complete. "Assessment capability in the following facilities was restored effective 1300 [CST] February 18, 2016: -Emergency Operations Facility (EOF) -Backup EOF -Operations Support Center "The Emergency Response Data System availability has also been restored." The Licensee has notified the NRC Resident Inspector. Notified the R4DO(Werner). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-02-09
51716 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2016-02-08 15:03 | 2016-02-08 17:50 | 2016-02-08 | MANUAL REACTOR SCRAM FOLLOWING SPURIOUS OPENING OF TWO SAFETY RELIEF VALVES "At 1500 EST on February 8, 2016, two safety relief valves (SRV) opened upon a spurious Division 2 initiation signal. This caused suppression pool temperature to increase. At 1503 EST, plant operators took action to manually SCRAM the reactor at 95 degrees Fahrenheit in the suppression pool per plant procedures. The SRVs closed immediately following the scram at 1503 EST. The cause of the SRVs opening is currently under investigation. "During the scram, all rods fully inserted into the core. Reactor Pressure is stable with decay heat being removed via turbine bypass valves to the main condenser. Reactor level control is currently being maintained via feedwater. Main Steam Isolation Valves are open. Cool down and depressurization to Mode 4 to follow. The plant is in a normal post SCRAM electrical line-up." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-02-08
51715 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2016-02-07 13:26 | 2016-02-07 13:46 | 2016-02-07 | MANUAL SCRAM AND ALERT DECLARATION DUE TO ELECTRICAL FAULT RESULTING IN FIRE/EXPLOSION At 1346 EST the licensee reported that at 1326, Brunswick Unit 1 declared an Alert under EAL HA 2.1 due to an explosion/fire in the Balance of Plant 4 kV switchgear bus area. Prior to the Alert declaration, the operators initiated a manual SCRAM due to an unexpected power decrease from 88% to 40%. The licensee has visually verified that there is no ongoing fire and is investigating the initial cause of the event. Offsite power is available to the site, but EDGs 1 and 2 are running and supplying Unit 1 loads. The MSIVs shut and HPCI/RCIC are being used to maintain vessel level. At 1412 EST, NRC decided to remain in Normal Mode. At 1704 EST the licensee reported the following: "At 1313 hours Eastern Standard Time (EST) a manual reactor scram was initiated due to loss of both recirculation system variable speed drives as a result of an electrical fault. At this time, a Startup Auxiliary Transformer (SAT) experienced a lockout fault; interrupting offsite power to emergency buses 1 and 2. Emergency Diesel Generators (EDGs) 1, 2, 3, and 4 automatically started and EDGs 1 and 2 synchronized to emergency buses 1 and 2 per design. The power interruption resulted in closure of the Main Steam Isolation Valves, per design. The manual scram also resulted in closure of Group 2, 6, and 6 Containment Isolation Valves. "The Reactor Core Isolation Cooling (RCIC) system was manually started and is being used to control reactor water level. The High Pressure Coolant Injection (HPCI) system was manually started and is being used for pressure control. "The Plant response to the event was per design. "Unit 2 is not directly affected by the event, however, due to the shared electrical distribution system is in a Technical Specification Action statement due to the Inoperable Unit 1 SAT. "The public health and safety is not impacted by this event." At 1751 EST, the licensee reported that the emergency declaration had been downgraded to an Unusual Event at 1730 because the plant no longer meets the criteria for an Alert, but does meet the criteria for an Unusual Event due to a "loss of all offsite power to Emergency 4 kV buses E1 (E3) and E2 (E4) for greater than or equal to 15 minutes." The NRC Resident Inspector has been notified. The licensee has notified the State and Local governments. Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). * * * UPDATE FROM MARTY IRWIN TO DANIEL MILLS AT 1825 ON 2/07/16 * * * At 1814 EST the emergency declaration was terminated because offsite power was restored. The NRC Resident Inspector has been notified. The licensee has notified the State and Local governments. Notified R2DO (Musser), NRR EO (Morris), IRD MOC (Stapleton), R2RA (Haney), NRR ET (Lubinski), NRR ET (Dean), DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). | 0 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | Power Operation | Power Operation |  | Hot Shutdown | Hot Shutdown |  | ALERT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2016-02-07
51714 | 0 | UTAH DEPT OF ENVIRONMENTAL QUALITY |  |  |  |  | 2016-02-02 | 2016-02-05 17:55 | 2016-02-05 | LOST TRITIUM EXIT SIGN The following was received from Utah via email: "On February 2, 2016, the licensee [University of Utah] was performing a 6-month inventory of the H-3 exit signs, when the individual performing the inventory noticed that one of the licensee's signs was missing. The licensee left a message with the University's facilities management office to see if the sign was removed by them. On February 5, 2016, the licensee was informed by the management group that they had not removed the sign. The licensee then determined that the sign was missing and presumed stolen. The licensee then notified the DWMRC [Utah Department of Environmental Quality, Division of Waste Management and Radiation Control] of the missing sign. The licensee will continue to investigate the incident, and will submit a written report to the DWMRC. The DWMRC will possibly perform an investigation on February 8, 2016. "Manufacturer: unknown (possibly Safety Lite Corporation) "Model: unknown "Serial #: T3478 "Possibly acquired by the licensee in 2003. "Activity: unknown (presumed >20 Ci of H-3)" Utah Event # UT160001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2016-02-15
51713 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-02-04 | 2016-02-05 13:39 | 2016-02-05 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL MISADMINISTRATION The following was received from Florida via email: "Licensee reported a possible medical event on Feb. 4th, while performing a Gamma Knife treatment. The treatment was planned for 11 sites to receive 18 Gy, and 5 sites to receive 11 Gy. After the completion of 15 sites, the treatment was stopped to re-sedate the patient, (at this time the stereotactic frame was still in position). Two minutes after starting the final site with 11 Gy, the patient awoke and started moving significantly. The patient was instructed to stay still for the remainder of the treatment. When the patient was brought out of the device the frame was not in the original position. It is not known if the frame became dislodged during the treatment, or if it occurred when exiting the device. If movement of the frame occurred during treatment: site 16 would have received a 74.5 percent underdose of 2.8 Gy and an approximated cerebellar volume of 0.7cc was treated with 9.3 Gy. Any further investigation will be referred to Licensing and Materials." Florida Incident # FL16-024 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-02-15
51712 | -1 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2016-02-05 01:09 | 2016-02-05 03:49 | 2016-04-04 | EXCESSIVE CONTROL ROOM IN-LEAKAGE IDENTIFIED "On February 5, 2015 at 0109 EST, the Control Room Emergency Ventilation System (CREVS) was declared inoperable due to a higher than allowed identified in-leakage rate for the Control Room Envelope (CRE) when in the Normal Operating Mode. Unit 1 remains at 100 percent power and Unit 2 remains in Mode 3 for an unrelated planned maintenance outage. Unit 1 and Unit 2 share a common CRE. "This in-leakage was detected during additional testing following the event documented in EN #51584. "At the time of discovery, there is a reasonable expectation this condition could prevent the fulfillment of the safety function of a system that is required to mitigate the consequences of an accident, thus satisfying the reporting criteria for 10CFR50.72(b)(3)(v)(D). "Actions to implement mitigating actions were immediately initiated in accordance with Technical Specification 3.7.10. CREVS has been placed in Recirculation Ventilation Mode, isolating the control room from outside air. "The NRC Senior Resident Inspector has been notified of the condition." * * * RETRACTION FROM DAVID HELD TO VINCENT KLCO AT 1411 EDT ON 4/4/16 * * * "Following the 8-hour 10 CFR 50.72 notification made on 02/05/2016 (EN 51712) regarding the Control Room Emergency Ventilation System (CREVS) inoperability, further engineering evaluation has determined the identified in-leakage does not result in exceeding the design criteria for dose to the control room personnel. Therefore the degraded Control Room Emergency Ventilation System remained operable with the identified air in-leakage as determined by the Control Room Envelope Habitability Program. As such, the safety function was never lost and the event notification is being retracted as it is not reportable pursuant to 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident has been notified." Notified the R1DO (Jackson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-02-05
51711 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2016-02-04 15:06 | 2016-02-04 18:50 | 2016-02-04 | NON LICENSED SUPERVISOR IN VIOLATION OF THE FITNESS FOR DUTY POLICY A non-licensed supervisor tested positive for a drugs during a random Fitness for Duty test. The individual's access to the plant has been suspended. The NRC Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.719 |  |  |  | 0 | 2016-02-04
51710 | 0 | KY DEPT FOR PUBLIC HEALTH & SAFETY |  |  |  |  | 2016-02-04 15:00 | 2016-02-04 16:13 | 2016-02-04 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following was received from Kentucky via fax: "KY RHB [Kentucky Radiation Health Branch] was notified via telephone by the radiation oncologist at the facility [Licensee] of a possible medical event. The medical event involved a patient treated for prostate cancer with I-125 [Iodine 125] seeds. The 30 day post-implant dosimetry determined the dose delivered to the target organ based on D90 was less than 80 percent [of prescribed dose]. The state [Kentucky] will continue to keep NRC informed of the status of the investigation." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2016-02-12
51709 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2016-02-04 | 2016-02-04 16:47 | 2016-02-17 | AGREEMENT STATE - LOST SHIPMENT OF CS-131 BRACHYTHERAPY SEEDS The following report was received from the Washington Department of Health, Office of Radiation Protection via email: "[On] 2/4/16, [a common carrier] has lost track of a RAM [radioactive material] Cs-131 brachytherapy seed shipment sent for a patient near Atlanta, GA. The seeds did not reach their destination in time for the implant in a patient at a clinic approximately 1 to 1.5 hrs from Atlanta, so the customer alerted IsoRay. According to IsoRay's Radiation Safety Officer, [the common carrier] is looking for the package. [The common carrier] thinks there is a possibility that the shipment may have been mistakenly transferred from the [common carriers] plane to the US Postal Service at the air field in Atlanta. IsoRay's Radiation Safety Officer called Washington State at [approximately] 9:40 AM [EST] to report the loss. Additional information is forthcoming." Washington Incident Number: WA-16-004 * * * UPDATE FROM ANINE GRUMBLES TO DANIEL MILLS AT 1750 EST ON 2/08/2016 * * * The following was received from Washington via email: "Quantity of seeds in order: 48 "Air kerma strength in micrograys per sq. meter/hr (U) - 2.02 - 2.08 = total 98 U "Total apparent activity= 154 mCi (range from 3.17 - 3.26 mCi/seed) "T1/2 = 9.69 days [half-life]" Notified R4DO (O'Keefe), NMSS_EVENTS_NOTIFICATION (email), and CNSC Canada (email). * * * UPDATE FROM ANINE GRUMBLES TO DANIEL MILLS AT 1640 EST ON 2/17/2016 * * * The following was received from Washington via email: "According to the Radiation Safety Officer at the seed manufacturer/distributor, IsoRay, the US Postal Service delivered the lost package to the intended user at the end of last week. The source had decayed to the point of being useless. The customer is going to send shipment back to IsoRay.'" Notified R4DO (Vasquez), NMSS_EVENTS_NOTIFICATION (email), and CNSC Canada (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2016-02-12
51708 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-02-04 11:21 | 2016-02-04 13:33 | 2016-02-04 | AUTOMATIC REACTOR TRIP DUE TO MAIN TURBINE TRIP "This 4 and 8 hour notification is being made to report that Salem Unit 2 suffered an unplanned automatic reactor trip and subsequent automatic Auxiliary Feedwater system actuation. The trip was initiated due to a Main Turbine trip above P-9 (49% power). The Main Turbine trip was caused by a Main Generator Protection signal. "Salem Unit 2 is currently stable in Mode 3. Reactor Coolant system pressure is 2235 PSIG and Reactor Coolant system temperature is 547 F with decay heat removal via the Main Steam Dump and Auxiliary Feedwater Systems. Unit 2 has no active shutdown tech spec action statements in effect. All control rods inserted on the reactor trip. All ECCS and ESF systems functioned as expected. "No major secondary equipment was tagged for maintenance prior to this event. The 24 Service Water pump is tagged for scheduled preventive maintenance and did not affect post trip plant response. No personnel were injured during this event." The licensee has notified the NRC Resident Inspector and will notify the Lower Alloway Creek Township. | 0 | 0 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-02-04
51707 | 0 | TEXAS A&M UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2016-02-04 07:00 | 2016-02-04 10:50 | 2016-02-04 | DISCOVERED VULNERABILITY IN SECURITY SYSTEM Discovered a vulnerability in a safeguard system that could allow unauthorized or undetected access to a controlled access area for which compensatory measures have not been employed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 0 | TX | NPR |  | 73.71(b)(1) |  |  |  | 1 | 2016-02-04
51706 | 0 | WECTEC LLC (FORMERLY CB&I) |  |  |  |  | 2015-10-09 | 2016-02-03 13:29 | 2016-02-03 | PART 21 REPORT REGARDING DEVIATIONS OF PIPE PENETRATION SLEEVES FOR AP1000 PROJECTS The following information is summarized from notification received by WECTEC LLC via email: "[This report] provides a report in accordance with 10 CFR 21.21 pertaining to deviations of piping penetration sleeves for Vogtle Unit 4 and V. C. Summer Unit 3 AP1000r projects. "During inspection of the listed piping penetration sleeves, corrosion was found. It has been conservatively determined that the penetrations could have failed if they were used in the corroded condition. Therefore, it is conservatively concluded that if left uncorrected this condition could have caused a substantial safety hazard for the V. C. Summer and Vogtle AP1000r projects. "Name and address of the individual or individuals informing the Commission. Deborah A. Gustafson Vice President of Engineering WECTEC LLC 128 S. Tryon St., Suite 1000 Charlotte, NC 28202" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-02-03
51705 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2016-02-01 13:00 | 2016-02-01 15:40 | 2016-02-01 | AGREEMENT STATE REPORT - TROXLER SOURCE SEPARATED FROM SOURCE ROD The following information was obtained from the State of New Jersey via facsimile: "[The New Jersey Department of Environmental Protection] was informed by a portable gauge licensee of a complete failure of their portable gauge source rod resulting in the sealed source (containing 8 mCi of Cs-137) dropping from the rod onto the ground. The incident occurred at Monmouth University this morning [2/1/16] at a construction site there. The loose source is in a concrete container and locked up at their licensed facility awaiting a lead pig sent overnight from Troxler. A survey has been conducted around the storage area to confirm that exposure there is below public dose limit. "The licensee's initial report from the field suspected that the failure of the containment was due to the advanced age of the gauge - reported at 20 years." Event Report ID No.: NJ #16-02-01-1239-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-02-09
51704 | 0 | WECTEC LLC (FORMERLY CB&I) |  |  |  |  | 2016-02-01 | 2016-02-01 12:40 | 2016-02-01 | PART 21 REPORT REGARDING DEVIATIONS OF PIPE SPOOLS FOR AP1000 PROJECTS The following information is summarized from notification received by WECTEC, LLC via email: "The basic components being supplied are piping spools to be used for various safety-related systems for the V. C. Summer and Vogtle AP1000r projects. The pipe spools are classified as ASME Boiler and Pressure Vessel Code Section III. "The specific conditions identified on various piping spools fall into four general categories: (1) Dimensional Length Deviations: These conditions include center-to-end and center-to-center lengths of straight pipe segments that exceed the minimum or maximum tolerances. (2) Bend Angle Deviations: These conditions include spool bend angles that exceed the minimum or maximum tolerances. (3) Minimum Wall Thickness Deviations: These conditions include pipe wall thickness below the applicable tolerance. These conditions typically have been found at some bends in the spools and at some ends of the pipe. (4) Other Conditions: These conditions include weld related attributes, potential carbon contamination, and tools marks." Uninstalled pipe spools are in storage and will be inspected, repaired or replaced prior to installation. Installed products will be identified and issues resolved as appropriate. Name and address of the individual or individuals informing the Commission: David Durham President WECTEC LLC 128 S. Tryon St., Suite 1000 Charlotte, NC 28202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-02-01
51703 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-01-29 | 2016-01-30 13:11 | 2016-01-30 | AGREEMENT STATE REPORT - CONTAMINATION FOUND ON RECEIPT INSPECTION The following report was received from the State of California via email: "Moravek received a package of tritium from Merck and Company (Rahway, New Jersey) on 1/29/16 by [common carrier] delivery (non-exclusive use). Upon performing the receipt radiological survey, Moravek personnel reported finding removable contamination of tritium on the external package surfaces up to 44.75 dpm/square cm. The applicable regulatory limit is 22 dpm/square cm based on wiping a 300 square cm area. Moravek personnel reported they estimate they wiped 100 square cm areas. The results of 5 wipes (approximately 500 square cm) performed by Moravek personnel of the package surfaces yielded an average of 26.4 dpm/square cm. "The contamination regulatory limit is identical for all beta and gamma emitting radionuclides. However, the safety significance of the contamination is nuclide specific, and ranges up to a factor in excess of 10,000 for common beta/gamma emitting radionuclides. Tritium is on the very low end of the safety significance spectrum, with for example, the safety significance of tritium contamination being approximately a factor of 4000 less than the safety significance of a similar contamination level of Cs-137. The dose consequences of the highest wipe concentration of 44.75 dpm/square cm of tritium found on the package is therefore very minor. "The [common carrier] RSO was notified of the contamination wipe results. The New Jersey radiation control program will also be notified." California 5010 Number: 012916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-02-08
51702 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2016-01-30 01:23 | 2016-01-30 07:32 | 2016-01-30 | UNANTICIPATED SFRCS ACTUATION WHILE RESTORING MAIN FEEDWATER TO STEAM GENERATORS "At 0123 EST, with the unit shutdown in Mode 3 (Hot Standby), during the performance of procedure DB-OP-06910, 'Trip Recovery,' while attempting to restore main feedwater to the Steam Generators, Davis-Besse received a Steam Feedwater Rupture Control System (SFRCS) 'reverse delta pressure' signal to the Auxiliary Feedwater System (AFW). The Auxiliary Feedwater System was operating at the time, feeding the Steam Generators. "The SFRCS signal did result in actuation/closure [of] several valves in the Main Steam System, as the SFRCS signal is designed to do. This SFRCS signal/valve actuation was not anticipated. "The unit remained in Mode 3 and is stable. This actuation did not have any negative impact to the AFW system and the ability to feed the steam generators. "The NRC Resident Inspector has been notified of the event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-01-30
51701 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-01-29 15:18 | 2016-01-29 23:00 | 2016-01-29 | SPECIFIED SYSTEM ACTUATION AFTER LOSS OF ONE OFFSITE POWER SOURCE "On January 29, 2016, at 1518 CST, with the plant in cold shutdown, power was lost on reserve station service (RSS) line no. 1. This is one of two sources of offsite power required by Technical Specifications. The power loss de-energized the Division 1 onsite AC safety-related switchgear, causing an automatic start of the Division 1 emergency diesel generator (EDG). The Division 1 reactor protection system (RPS) bus was also de-energized, causing a half-scram signal. Approximately 8 minutes later, a full actuation of the RPS occurred due to a high water level condition in the control rod drive hydraulic system scram discharge volume header. All reactor control rods were already fully inserted. "The loss of Division 1 RPS also caused the actuation of the Division 1 primary containment isolation logic. The Division 1 isolation valves in the balance-of-plant systems closed as designed. Both trains of the standby gas treatment system actuated. "The loss of RSS no. 1 occurred during post-modification testing on relays at the local 230kV switchyard. The exact cause of the event is under investigation. This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). "The unit remains in cold shutdown with 1 source of offsite power and all 3 [EDG] available. "The [NRC] Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-01-29
51700 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2016-01-05 | 2016-01-29 16:56 | 2016-01-29 | PART 21 - IMPROPER ACCESSORY MOUNTING BRACKET PROCESSING "Equipment Affected by this lnformation Notice: Accessory mounting brackets subject to this Fisher Information Notice (FIN) were provided to Sanmen Unit 1 and Haiyang Unit 1 per Change Notice 32 to Westinghouse Electric Company PO 4500280610, and the Fisher Controls International LLC (Fisher) orders noted below. These orders pertain to Westinghouse Electric Company AP1000 units currently under construction in the Peoples' Republic of China. "Fisher Order 004 - B001252772, Sanmen Unit 1, S/N: 19073505 "Fisher Order 004 - B001252773, Haiyang Unit 1, S/N: 19073506 "Purpose: The purpose of this FIN is to alert Westinghouse Electric Company that as of 5 January 2016, Fisher became aware of a situation which may affect the performance of the mounting brackets including their safety-related function. Fisher is informing Westinghouse Electric Company of this circumstance in accordance with Section 21.21 (b) of 10CFR 21. "Applicability: This FlN applies only to the subject mounting brackets supplied by Fisher to Westinghouse Electric Company via the aforementioned orders. "Discussion: Change Notice 32 to Westinghouse Electric Company PO 4500280610 was issued to add commercial grade electronic transmitters to the above referenced serial numbers, which were previously shipped to the Sanmen and Haiyang sites. During the mounting design, it was decided to incorporate the transmitter mounting with an existing switch magnet mounting bracket. Because the transmitter was commercial grade, its mounting parts could also be commercial grade and were processed as such. At that time, Fisher failed to recognize that the existing switch magnet mounting plate was a safety-related item, meaning that the new dual purpose transmitter / magnet mounting bracket should have also been supplied as a safety related item. This resulted in the dual purpose brackets being shipped as a commercial grade item. This oversight was discovered during the processing of other items utilizing the dual purpose bracket for other AP1000 sites. "Action Required: Fisher will provide properly processed safety-related mounting brackets to Sanmen Unit 1 and Haiyang Unit 1. Unshipped AP1000 items having these brackets for Sanmen Unit 2, Haiyang Unit 2, Summer Units 2 & 3 and Vogtle Units 3 & 4 have been identified and will be verified as having the proper safety-related mounting brackets prior to shipping. Corrective Action Request (CAR) 1793 has been opened to identify root causes and corrective actions required to prevent reoccurrence. "10 CFR 21 Implications: Fisher requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR 21. If there are any technical questions or concerns, please contact: Ben Ahrens, Quality Manager Emerson Process Management Fisher Controls International LLC 301 South First Avenue Marshalltown, IA 50158 Phone: (641) 754-2249 Benjamin.ahrens@emerson.com" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-01-29
51699 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2016-01-29 | 2016-01-29 17:06 | 2016-01-29 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR DENSITY GAUGE The following report was received from the State of Nebraska via email: "The Radiation Safety Officer for the Nebraska Radioactive Materials licensee reported that a Humboldt Model 5001, Serial Number 5624 industrial gauge had been damaged today (1/29/2016) at a temporary job site in Falls City, NE. The gauge contains 10 mCi of Cs-137 and 40 mCi of Am-241/Be. The user had left the gauge unattended for a brief time, and upon returning, found that a construction vehicle had run over the gauge. The gauge handle was broken and the case damaged. The source was able to be retracted, however the shutter was damaged and could not be completely closed. Wipe tests verified that there was no leakage from the source. Office of Radiological Health staff were dispatched to the scene." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2016-02-08
51698 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-01-28 17:00 | 2016-01-29 16:42 | 2016-01-29 | AGREEMENT STATE REPORT - LOST/STOLEN NUCLEAR DENSITY GAUGE The following report was received from the State of California via email: "[The licensee] states that the nuclear density gauge was inside a box in company van parked in the public street on the side of the building. It was discovered missing once they needed to use it for a job. [The State] was notified that the item had been missing for approximately 24 hours. "Nuclear Gauge information: Unit: CPN-Campbell Pacific Nuclear MC3 ; Serial # M37107962. Additional information: Substance Type: Cesium -137, Amount: 10 mCi; Americium -241, Amount: 50 mCi." The State of California, Department of Public Health Radiologic Health Branch received notification from the California's Governor's Office of Emergency Services. The licensee has contacted local law enforcement and a search for the gauge is still ongoing. Additional information will be provided when available. California Report No. 012916 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-02-08
51697 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2016-01-29 09:20 | 2016-01-29 17:09 | 2016-02-05 | OFFSITE POWER DECLARED INOPERABLE DUE TO LOWERING GENERATOR VOLTAGE "At 0920 CST on 1/29/16, while performing main generator voltage adjustments at the direction of the transmission operator, Duane Arnold Energy Center (DAEC) switchyard voltage lowered to the calculated point where offsite sources were considered inoperable. During this event, both onsite emergency diesel generators were fully operable and capable of performing their intended safety function. "While no safety concerns arose, Technical Specification (TS) Limiting Condition for Operability (LCO) 3.8.1.a Condition C was entered due to two offsite electric power circuits being inoperable. Immediate actions were taken to adjust main generator voltage to restore switchyard voltage. In less than 10 minutes, both offsite circuits were declared operable and LCO 3.8.1.a Condition C was exited. This resulted in a reportable event pursuant to 10CFR50.72(b)(3)(v)(D). "During the time of reduced grid voltage, no bus low-voltage alarms nor any equipment issues occurred. The cause of this event is under investigation, and there are not any current operability concerns with the offsite power circuits." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM ROBERT MURRELL TO DANIEL MILLS AT 1319 EST ON 02/05/2016 * * * "The purpose of this notification is to retract a previous report made on 1/29/16 at 1709 (EST). NRC notification was initially made as a result of offsite power sources being declared inoperable due to the identification of a low voltage condition by the grid operator. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the offsite power grid conditions were above the required limit and were therefore operable. It was determined that a trip of the DAEC turbine/generator would not have led to fluctuations in voltages in the DAEC switchyard below the trip setpoints for Loss of Power. Based on this, the safety-related buses and loads were fully capable of performing their intended design basis function. The degraded voltage relays setpoint were not reached; therefore, the essential electrical buses remained connected to offsite power. "Therefore, the low voltage condition does not meet the reporting requirements of 10 CFR 50.72 or 10 CFR 50.73 "The Resident Inspector has been notified." Notified R3DO (Kozak). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-01-29
51696 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2016-01-29 13:22 | 2016-01-29 16:43 | 2016-01-29 | AUTOMATIC REACTOR TRIP DUE TO REACTOR PROTECTION SYSTEM ACTUATION "At 1322 EST, with the unit operating at approximately 100% full power, an automatic reactor trip occurred due to actuation of Reactor Protection System (RPS) Channel 4. The cause of the RPS actuation is being investigated at this time. Nuclear Instrumentation calibration for RPS Channel 2 was in progress at the time of the trip, with Channel 2 in bypass and Channel 1 in trip. All control rods fully inserted. Immediately post trip, the Steam Feedwater Rupture Control System actuated due to high Steam Generator 1 level due to unknown causes. The Main Steam Isolation Valves closed and Auxiliary Feedwater started as expected. Secondary side relief valves lifted in response to the trip, with two of the relief valves (one on each header) not properly reseating until operators manually lowered Main Steam Header pressure. The Bayshore 345 kV Offsite Electrical Distribution Circuit automatically isolated at the time of the unit trip. This was unexpected. The remaining offsite circuits remain in service. "The unit is currently in Mode 3 (Hot Standby) and stable, at approximately 550 degrees F and 2155 psig. Steam is being discharged through the Atmospheric Vent Valves for decay heat removal. There is no known primary to secondary leakage, and all safety systems functioned as expected. "Both primary Source Range nuclear instruments automatically energized, however, they were previously declared inoperable due to an administrative issue. Both Source Range instruments are functional and indicating properly. Both alternate Source Range instruments are operable, and all required Technical Specification actions have been completed. "The NRC Resident Inspector has been notified of the event." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-01-29
51695 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2015-12-01 21:19 | 2016-01-29 15:06 | 2016-01-29 | INVALID EMERGENCY FEEDWATER ACTUATION "On December 1, 2015, at 2119 EST, with Unit 1 in power operation mode, during a planned maintenance activity, an invalid Heat Sink Protection System (HSPS) actuation occurred. At the time of the event, electrical maintenance technicians were verifying a HSPS relay contact state using an electrical test meter. The contact was being verified open by recording both voltage and resistance readings across the contact. The technicians first measured voltage. No voltage was found, indicating the relay contact was open, as expected. The technicians then measured for resistance across the open contact. Test meters have lower circuit impedance when measuring resistance as opposed to voltage, which can result in electrically bridging across open contacts. When the meter was installed across the open contact to obtain the resistance reading, the HSPS actuation circuit logic was completed and the inadvertent HSPS actuation occurred. The HSPS actuation resulted in the steam driven Emergency Feedwater (EFW) pump automatically starting and control valves receiving actuation set point signals. There was no emergency feed water injection into the steam generators. At the time of the inadvertent HSPS actuation, steam generator operating levels were above the HSPS actuation setpoint. ''The specific train and system that actuated was the Heat Sink Protection System, Emergency Feedwater System Actuation on Loss of All Reactor Coolant Pumps (RCP) Train A. ''The HSPS Loss of all RCP Train A actuation was complete. ''The EFW valves and EFW steam driven pump started and functioned successfully. "This is reported under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of HSPS Loss of all RCP Train A and in accordance with 10 CFR 50.73(a)(1), this notification of the invalid actuation is provided in lieu of a written LER. "The Licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2016-01-29
51694 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-01-29 08:12 | 2016-01-29 11:02 | 2016-01-29 | OFFSITE NOTIFICATION - SEWAGE TREATMENT PLANT DISCHARGE LIMIT EXCEEDED "On January 29, 2016 James A. FitzPatrick Nuclear Power Plant (JAF) received notification from the site Sewage Treatment Plant (STP) operators that the January 6, 2016 monthly settleable solids result for the STP was 0.2 ml/L/hr [milliliter/liter/hour]. This value exceeds the State Pollutant Discharge Elimination System (SPDES) permit limit of 0.1 ml/L/hr (daily maximum). "The STP operators conduct daily process control tests at the STP and did not identify any system upset issues around the January 6, 2016 sample date, or any time since, that would be symptomatic of the slightly elevated settleable solids result. "The JAF environmental engineer concluded that a notification to the New York State Department of Environmental Conservation (NYSDEC) was not required for this event; however, a courtesy notification for permit noncompliance was made. The NYSDEC has been notified. "Pursuant to 10 CFR 50.72(b)(2)(xi), this condition is being reported as an event or situation for which notification to a government agency has been made. The NRC resident has been notified. "JAF is currently at 0 percent power in Mode 2 following a forced outage resultant of events on January 23, 2016." * * * RETRACTION ON 1/29/16 AT 1630 EST FROM DUSTIN SCURLOCK TO DONG PARK * * * "Based on further review of the NRC reporting guidance relative to this criteria, JAF has concluded that this condition is below the reporting threshold outlined in NUREG-1022 Revision 3. NUREG-1022 states the following (page 54), 'Licensees generally do not have to report media and government interactions unless they are related to the radiological health and safety of the public or onsite personnel, or protection of the environment.' "The condition originally reported in ENS 51694 is considered a minor deviation in sewage process limits, and has no impact on the radiological health and safety of the public or onsite personnel, or protection of the environment. Therefore, JAF is retracting ENS 51694." The NRC Resident Inspector has been notified. Notified R1DO (Bickett). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-01-29
51693 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-01-28 | 2016-01-28 17:30 | 2016-01-28 | AGREEMENT STATE REPORT - STUCK SHUTTER The following report was received from the Texas Department of State Health Services via email: "On January 28, 2015, the licensee notified the Agency [Texas Department of State Health Services] that during routine leak test and shutter checks, it had discovered that the shutters on two Ohmart-Vega SH-F1 gauges were stuck in the open position. Open is the normal operating position for these two level gauges that are mounted on the sides of tanks. Each gauge contains a 120 millicurie cesium-137 source. Due to the location of the gauges, there is no risk of exposure to any individual. The licensee has contacted the manufacturer and is scheduling repairs. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I 9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-02-05
51692 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2016-01-14 | 2016-01-28 13:19 | 2016-01-28 | AGREEMENT STATE REPORT - SHIPMENT EXCEEDED RADIATION LIMIT The following Agreement State Report was received by the State of California via email: "On January 14, 2016, the Southwest Research Institute (SRWI) notified the Texas radiation control program (TxRCP) of the receipt of an exclusive use shipment with package contact dose rates up to 1900 mrem/hr, which exceed the 1000 mrem/hr limit for exclusive use shipments in closed vehicles. The package contained a nominal 8.4 Ci Co-60 source. SWRI personnel verified that the dose rate limits in the cab of the vehicle and at other shipment locations did not exceed regulatory limits. "On 1/27/16 CDPH/RHB [California Department of Public Health/Radiologic Health Branch] was notified by NRC (R. Erickson) by email of the event being investigated by TxRCP inasmuch as a California licensee (JL Shepherd & Associates) had prepared the package for shipment from a Maryland licensee to SWRI. On 1/27/16, TxRCP requested that CDPH/RHB (CaRCP) take the lead in investigation of the event inasmuch as JL Shepherd & Associates had prepared the package for shipment, including performing the radiation surveys. CDPH/RHB agreed to take the investigation lead. At the request of NRC, the TxRCP retracted their event report to NRC HOO, and NRC requested that CDPH/RHB submit an event report to NRC." California 5010 number: 012716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2016-02-05
51691 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-01-21 | 2016-01-28 13:09 | 2016-01-28 | AGREEMENT STATE REPORT - LOST/ABANDONED TRITIUM EXIT SIGN The following Agreement State Report was received by the State of Colorado via email: "[The licensee reported that,] according to the maintenance specialist for the property [located in Steamboat Springs, CO], an inspection of the property was conducted to complete the Radioactive Materials Unit annual report for 2015. They reported on 6/24/15, the exit sign was still in the space. Upon completing an audit of the general license files, contact was made to the current tenant who reported the building had been remodeled. A call was made to the reporting maintenance staff who completed the forms. During the discussion regarding the lost/abandoned exit sign, a request for further information would need to be submitted along with a corrective action should the sign not be found. [The maintenance specialist] conducted a site inspection and found the sign to be missing on 1/21/16. A detailed report was submitted with a corrective action letter received on 1/27/16. "Tritium Exit Sign: Model: SLX 60 Source Serial: #412078 Isotope: H-3, Activity Activity: 7500 mCi Date Shipped from Isolite Corporation: 6-18-2007 "The property management company is reviewing all properties to verify if a Tritium exit signs are still in use and providing the current tenants of regulatory requirements to correct and prevent any future displacement or loss of exit signs containing Tritium." Colorado Event Report ID No.: CO16-I16-02 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-02-05
51690 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2015-09-18 | 2016-01-28 09:33 | 2016-03-18 | AGREEMENT STATE REPORT - FIXED GAUGE OPEN/STUCK SHUTTER The following was received from the State of Mississippi via email: "During Fall shutter checks and inventory, on 9/18/2015, an Ohmart-Vega fixed gauge, DEA-2102, device model no. SHLM-BR1, (housing serial no. 13530993) (source serial no. 8533CN), was discovered to have an open/stuck shutter, the source disconnected, and was unable to be moved into the closed position. The RSO [Radiation Safety Officer] contacted the manufacturer and arrangements for repair are in motion. DRH [Mississippi Division of Radiological Health] was notified on 1/15/2016 and recommended that RSO take surveys with a survey measurement of the source. On 1/22/2016, [the] RSO provided readings that did not exceed 0.02 mR/hr at the surface of the steel drum that encloses the gauge and the source. The gauge and source is sealed in the steel drum and is only accessible by the manufacturer. The source is not in a designated work area, and is not causing exposure limits beyond the limits for radiation control to the general public and occupational workers." Isotope: Cs-137 Activity: 40mCi Mississippi report # MS-16001 * * * UPDATE FROM ROBERT SIMS TO DANIEL MILLS AT 1724 EDT ON 03/18/16 * * * The following was received from the State of Mississippi via email: "DRH [Department of Radiological Health] received vendor's field service update on 3/17/2016, from RSO. Report states that shutter failure was due to fatigue and the harsh environment to the roll pin that holds the two rods together. The source holder was repaired and leak test performed. DRH forwarded updated report to NRC on 3/17/2016. All Updated information on the source repair, the cause of the failure and all corrective action was forwarded the HOO on 3/18/2016. "Violation issued for failure to report event to Mississippi State Department of Radiological Health within 24 hours." Notified R4DO (Haire) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2016-02-05
51689 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2016-01-18 | 2016-01-27 12:36 | 2016-01-27 | AGREEMENT STATE REPORT - LOST I-125 MEDICAL SEED The following report was received from the Commonwealth of Kentucky via email: "[The licensee] reported the loss of a I-125 localization seed (lsoAid Advantage, Model IAI-125A). On 1/19/16, the licensee discovered the number of seeds in storage did not match the number recorded. After the licensee conducted an investigation, they believe the seed was lost when it was transferred from the vial, pathology puts them in, to the Cidex storage/decontamination vial. The seeds in the vial had been placed there between 12/21/15 and 1/18/16. As part of the investigation the licensee verified that all seeds were removed from patients during that time and the hot lab was thoroughly searched. "They [the licensee] believe the I-125 seed was most likely disposed of in the trash and taken to landfill with other waste from the hospital. The licensee reported the missing seed came from one of the three orders, lot #39858, 0.147 mCi as of 1/19/16, lot #39809, 0.128 mCi as of 1/19/16, or lot #39111, 0.075 mCi as of 1/19/16. Corrective actions include retraining Nuclear Medicine Techs in the handling of radioactive breast seeds, including stressing the importance of surveying all material to verify that the seed was placed in the Cidex vial and not lost in the surrounding area. Kentucky Event Report ID No.: KY160001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2016-02-04
51688 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2016-01-27 | 2016-01-27 10:18 | 2016-01-27 | AGREEMENT STATE REPORT: RADIATION OVEREXPOSURE TO EXTERNAL WHOLE BODY The following was received from the State of Florida via email: "Tampa inspection office [State of Florida Bureau of Radiation Control] conducted a routine inspection on January 22, 2016. Searching their records [the inspector] found that [one] employee had exceed the annual limit of 5 Rem per year (not including the month of December). [The employee] had nine high exposure investigative reports recorded in the last year. The report also noted that the RSO [Radiation Safety Officer] failed to take any action to mitigate more exposure to ionizing radiation. "The RSO will be required to submit a report. The BRC [State of Florida Bureau of Radiation Control] will request a safety inspection of the facility paying particular attention to [the employee] daily duties and make recommendations to reduce exposure. The BRC would also suggest additional unannounced inspections to insure improvement to their adherence to regulations. "Isotope: F-18 Activity: 16.5 MeV Cyclotron Material Form: Particle Accelerator External Whole Body exposure Maximum Dose Received: 5.2 Rem/year (excluding December) Florida Incident Number FL16-016." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-02-04
51687 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2016-01-26 23:25 | 2016-01-27 01:44 | 2016-01-27 | MANUAL REACTOR TRIP DUE TO LOSS OF FEEDWATER TO A SINGLE STEAM GENERATOR "At 2325 [CST] on 01/26/2016, Unit 1 was manually tripped due to loss of Feedwater on 'C' S/G [Steam Generator]. The loss of Feedwater was a result of a failure on 'C' S/G Main Feedwater Regulating Valve that caused the valve to travel closed with no Operator action. Auxiliary Feedwater and Feedwater Isolation actuated as designed. All Control and Shutdown Rods fully inserted. Intermediate Range Nl 36 [Nuclear Instrument] failed above P10 and, as a result, Source Range Nuclear Instruments were manually energized. No primary or secondary relief valves opened. There were no electrical problems. Normal operating temperature and pressure (NOT/NOP) is 567 degrees F and 2235 psig. There were no significant TS LCOs entered. "This event was not significant to the health and safety of the public based on all safety systems performed as designed. "Unit 2 was not affected." Decay heat removal is being controlled via Steam Dumps. Offsite power is in the normal electrical lineup. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-01-27
51686 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-01-25 18:15 | 2016-01-26 13:04 | 2016-01-26 | AGREEMENT STATE REPORT - VEHICLE ACCIDENT WHILE TRANSPORTING A TROXLER MOISTURE DENSITY GAUGE The following report was received from the State of Texas via email: "On January 26, 2016, at approximately 1015 CST, the licensee notified the Agency [Texas Department of State Health Services] that at approximately 1815 CST on January 25, 2016, one of its technicians had been involved in a vehicle accident while transporting a Troxler Model 3430 (Serial #24412) moisture/density gauge. The accident occurred near Cumby, Texas. The technician was hospitalized as a result of injuries received in the accident. "The gauge contained a 40 millicurie americium-241 and an 8 millicurie cesium-137 source. The licensee reported that the gauge's insertion rod was locked and the gauge was inside its transport case which had locks on the hasps, the transport case was chained with locks inside a steel box which was bolted to the bed of the pick-up, and there were 2 locks on the steel box. A wrecker service removed the vehicle from the scene and took it to its business location where the vehicle was placed behind a fence with a locked gate. The licensee was notified of the accident after midnight. One of the licensee's employees retrieved the gauge from the vehicle at approximately 0830 this morning. The employee reported the shipping papers were on the seat of the vehicle. The licensee reported that it does not appear anyone was aware of the presence of the gauge until the employee removed it this morning. The gauge was not damaged. More information will be provided as it is obtained in accordance with SA-300." Texas incident #: I 9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [10 empty] | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-02-03
51685 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2016-01-14 | 2016-01-26 11:08 | 2016-01-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from Colorado via email: "An inspection of the property was conducted to report the registration of inventory from the annual mailing received from CDPHE, Radioactive Materials Unit. Six of the eight exit signs registered for the Park Hyatt Beaver Creek were found. Two were not located and are reported as missing. The remaining six signs are being returned to the manufacturer. "The hotel will no longer carry self-luminous exit signs and a policy is in place to purchase LED exit signs only. Should they choose to purchase any Tritium exit signs in the future they will ensure that all devices will be tracked and monitored annually. "Serial numbers for missing exit signs: 12-01538, 12-01539, 12-10540, 12-01541. "Model: SLX60 "Manufacturer: Isolite Corporation "Isotope: H-3 "Activity: 6.2 Ci "An inspection of the property revealed six of eight exit signs. Upon receipt of exit signs staff were unaware the signs contained Tritium and were regulated materials. No tracking or recording of material was kept. Several signs were found still in the original shipping carton and kept in storage. Remaining Tritium exit signs were removed and shipped back to the manufacturer and replaced with LED signs." Colorado Event Report ID No.: C016-116-01 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-02-03
51684 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-25 10:30 | 2016-01-25 15:26 | 2016-01-25 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO DISCOVERED CONDITION "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality due to a loss of cooling of the TSC (Technical Support Center) Ventilation system was discovered on 1/25/2016. At 1030 [EST], maintenance personnel reported the compressor local power breaker was tripped open and that all 3 phases of the compressor indicated grounded. Maintenance will begin repairs as soon as parts are made available. Estimated time to repair is unknown at this time. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable. If relocation of the TSC becomes necessary, the Emergency Coordinator will relocate the TSC staff to an alternate location in accordance with applicable emergency plan implementing procedures. The Emergency Response Organization team will be notified of the condition and the possible need to relocate during an emergency. This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-01-25
51683 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2016-01-25 03:15 | 2016-01-25 05:45 | 2016-01-25 | MANUAL REACTOR TRIP DUE TO ELEVATED CONDENSER SODIUM LEVELS At 0315 EST on 1/25/16, Calvert Cliffs Unit 1 was manually tripped from 10 percent power due to elevated condenser sodium levels. All systems responded per design. Main Feed was secured and auxiliary feed water was initiated. The elevated sodium levels are believed to be due to a condenser tube leak. The reactor is currently shutdown and stable in Mode 3 and will remain in Mode 3 until repairs are effected. Unit 2 was not affected and remains at full power. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-01-25
51682 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2016-01-25 01:47 | 2016-01-25 03:21 | 2016-01-25 | AUTOMATIC REACTOR TRIP DUE TO REACTOR COOLANT PUMP TRIP At 0147 EST on 1/25/16, the 'B' Reactor Coolant Pump (RCP) tripped offline. This caused a reactor trip on low coolant flow. As expected, the Aux Feedwater System (AFW) initiated on the reactor trip. The trip was uncomplicated and the plant is currently shutdown in Mode 3 with a normal electrical lineup and decay heat is being removed via steam dumps to the condenser. The cause of the 'B' RCP trip is under investigation. A containment entry is planned for dayshift on 1/25/16 to inspect and troubleshoot the 'B' RCP. The Licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-01-25
51681 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2016-01-24 03:57 | 2016-01-24 11:23 | 2016-01-24 | AVERAGE POWER RANGE MONITORING SYSTEM INOPERABLE "At 0357 hours [EST] on January 24, 2016, during a shut down required by plant Technical Specifications (see EN#51679), the 3A Feedwater heater isolated while performing a Reactor Recirculation Pump downshift. A consequence of this Feedwater heater isolation was that all 8 of the Average Power Range Monitors (APRM) became inoperable due to a calibration set point being out of tolerance. The APRM's are relied upon for the reactors high neutron flux trips. The inoperable APRM's resulted in a loss of RPS Trip Capability and a loss of safety function. The manual reactor trip function and other RPS functions remained available. RPS Trip capability for the APRM's was restored at 0445 hours on January 24, 2016. This notification is being made under [10 CFR] 50.72(b)(3)(v)(A) for an event or condition that could have prevented the fulfillment of a safety function affecting the ability to shut down the reactor." The licensee has notified the NRC Resident Inspector. | 52 | 0 | 0 | 52 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2016-01-24
51680 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2016-01-23 22:41 | 2016-01-24 01:10 | 2016-01-24 | MANUAL SCRAM DUE TO LOWERING INTAKE LEVEL "At 2241 [EST] on 1/23/2016, James A FitzPatrick inserted a manual scram from 89 percent power due to lowering intake level. Following the successful scram, a residual transfer occurred, resulting in a loss of the non-vital busses, loss of all Circulating Water Pumps, and a manual closure of the Main Steam Isolation Valves (MSIVs). The cause of the residual transfer is unknown. "RPV [Reactor Pressure Vessel] level shrink during the scram resulted in a successful Group 2 isolation. Reactor Vessel [level] and pressure are being maintained with the High Pressure Coolant Injection System which was manually started. A cooldown is in progress." FitzPatrick will proceed to Mode 5 until the cause is identified and corrected. The Emergency Diesel generators auto started as a result of the loss of power to the non-vital busses. Offsite power remained available throughout the event. Operators are controlling pressure manually via the relief valves. FitzPatrick will notify the Public Service Commission of the event. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2016-01-24
51679 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2016-01-23 21:22 | 2016-01-24 00:56 | 2016-01-24 | TS REQUIRED SHUTDOWN DUE TO UNIDENTIFIED LEAKAGE IN DRYWELL "At 2100 hours [EST], on January 23, 2016, the Perry Nuclear Power Plant commenced a reactor shutdown due to unidentified leakage in the drywell. At 2122 hours, drywell unidentified leakage exceeded the Technical Specification 3.4.5.d limit of 'less than or equal to 2 gpm increase in unidentified LEAKAGE within the previous 24 hour period in Mode 1.' The unidentified leakage increased to approximately 3.8 gpm at 2122 hours. Current unidentified leakage is 3.02 gpm. "Technical Specification 3.4.5 actions allow 4 hours to reduce the leakage within limits or be in Mode 3 within 12 hours and Mode 4 within 36 hours. The plant is required to be in Mode 3 by 1322 hours on January 24, 2016 and Mode 4 by 1322 hours on January 25, 2016. "A drywell entry will be made in Mode 3 to identify the leak source. "This notification is being made due to an expected inability to restore the leakage within limits prior to exceeding the LCO action time. "Follow up question from NRC: Event times do not match (2100 versus 2122) - explained downpower was commenced at 2100 with leakage less than TS limit. When Reactor Core flow was reduced, un-identified leakage increased above the TS limit." The Licensee has notified the NRC Resident Inspector. * * * UPDATE FROM MIKE DOTY TO DANIEL MILLS AT 1123 EST ON 1/24/16 * * * "At 1007 hours, on January 24, 2016 with the plant at 8% power during a feedwater shift to place the motor feed pump in service, reactor level rose to the level 8 scram set point and the Reactor Protection System (RPS) initiated, scramming the reactor. During the scram, all rods fully inserted into the core. Decay heat is being removed via turbine bypass valves to the main condenser. Reactor level control is currently being maintained via feedwater. The plant is stable with cool down and depressurization to Mode 4 to follow. The cause of the rise in feedwater level is under investigation. This notification is being made under 50.72(b)(2)(iv)(B) for a RPS initiation while critical." All safety shutdown systems are available. The electric plant is in its normal shutdown alignment being supplied by offsite power. The licensee has notified the NRC Resident Inspector. Notified R3DO (Cameron). NRR (Morris) and IRD (Gott) were notified via email. * * * UPDATE FROM DAVID O'DONNELL TO HOWIE CROUCH AT 1915 EST ON 1/24/16 * * * "Following a shutdown required by plant Technical Specifications a small leak was identified coming from the Reactor Recirculation Loop A Pump Discharge Valve vent line. The Recirculation Loop is part of the reactor coolant system making this reportable under 50.72(b)(3)(ii)(A) as a degraded condition. It was subsequently determined to require a plant cool down in accordance with Technical Specification 3.4.5, Action C which requires the plant to be in MODE 4 within 36 hours. Technical Specification 3.4.5 was previously entered for increased unidentified leakage in the drywell. The plant is required to be in Mode 4 by 1322 hours on January 25, 2016." The licensee has notified the NRC Resident Inspector. Notified R3DO (Cameron). NRR (Morris) and IRD (Gott) were notified via email. | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2016-01-24
51678 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2016-01-23 17:03 | 2016-01-23 19:48 | 2016-01-23 | PARTIAL LOSS OF POWER RESULTS IN EMERGENCY DIESEL GENERATORS STARTING "At 1703 [EST] on 1/23/16, with Unit 1 and Unit 2 operating at 100% power, the North Anna 34.5 kv Bus 3, off-site power feed to the 'C' Reserve Station Service Transformer, was lost which resulted in the loss of power to the Unit 1 'H' Emergency Bus and the Unit 2 'J' Emergency Bus. Loss of 34.5kV Bus 3 resulted from feeder breaker L102 opening. As a result of the power loss, the 1H Emergency Diesel Generator and the 2J Emergency Diesel Generator automatically started as designed and restored power to the associated emergency bus. During this event, the Unit 1 'B' Charging Pump, 1-CH-P-18 automatically started as designed due to the loss of power event. "The valid actuation of these ESF components due to the loss of electrical power is reportable per 10 CFR 50.72 (b)(3)(iv)(A). "The Unit 1 'H' Emergency Bus off-site power source was restored to service and the 1H Emergency Diesel Generator was secured and returned to Automatic. The Unit 2 'J' Emergency Bus power feed continues to be from the 2J Emergency Diesel Generator. Restoration of offsite power to operable status is currently being pursued. The Unit 1 'B' Charging Pump has been secured and returned to automatic. "Both units are in a stable condition. An investigation is underway to determine the cause of the L102 feeder breaker opening resulting in the 34.5 kv Bus 3 loss of power." The licensee notified the NRC Resident Inspector | 100 | 97 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2016-01-23
51677 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-01-23 05:51 | 2016-01-23 08:26 | 2016-01-23 | LOSS OF POWER TO THE SITE EMERGENCY BUILDING "Oyster Creek Generating Station has experienced a loss of power to the Site Emergency Building, which renders the TSC ventilation system non-functional until power is restored. "If an emergency is declared requiring TSC activation during the time TSC ventilation is non-functional, the TSC will be staffed and activated using existing emergency planning procedure unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xii) due to potential loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation." The NRC Resident Inspector has been notified. * * * UPDATE FROM ANDREW KRUKOWSKI TO JEFF HERRERA AT 1121 EST ON 1/23/16 * * * "Due to a loss of power to the Site Emergency Building the Plant Process Computer needed to be secured. Due to the loss of the Plant Process Computer the Emergency Response Data System (ERDS) functions are not available for communications to the NRC. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the loss of úEmergency Response Data System (ERDS) communication capability." The licensee has notified the NRC Resident Inspector. Notified R1DO (Gray). * * * UPDATE FROM ANDREW KRUKOWSKI TO HOWIE CROUCH AT 1446 EST ON 1/23/16 * * * Power was restored to the Site Emergency Building. TSC Ventilation and the ERDS systems were returned to service at 1440 EST. The licensee has notified the NRC Resident Inspector. Notified R1DO (Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-01-23
51676 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2016-01-22 19:35 | 2016-01-23 00:20 | 2016-01-23 | LOW PRESSURE COOLANT INJECTION PUMP ISOLATION VALVE WOULD NOT REOPEN "While performing a Technical Specification surveillance functional test of the Low Pressure Coolant Injection (LPCI) pump and valve surveillance, the Division 1 LPCI outboard Isolation Valve E1150F017A was closed for stroke time testing and would not reopen. Not being able to be open this valve renders the LPCI Loop Select function inoperable. Time of the event was 1935 [EST]. This inoperability of LPCI loop Select results in entry into Technical Specification 3.0.3. "Power reduction activities were briefed at time 2020, however, no power reduction commenced due to resolving the issue with the LPCI outboard Isolation Valve E1150F017A. During the investigation there was a loose screw found preventing the close contactor from fully releasing and allowing the open contactor to engage. No other abnormalities were found during this investigation. This screw was removed and the close contactor functioned normally and the valve was opened. The valve was retested satisfactory and the station exited Technical Specification 3.0.3 at 2145. ''This report is made pursuant to 10 CFR 50.72(b)(3)(v)(D), an event or condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident. "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2016-01-23
51675 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-01-22 | 2016-01-22 16:41 | 2016-01-22 | AGREEMENT STATE REPORT - PACKAGE WITH EXTERNAL CONTAMINATION The following information was received from the State of Oklahoma via email: "[The Oklahoma Department of Environmental Quality (OKDEQ)] has been informed that a package sent from University of Oklahoma Medical Center (OK-21035-01) to the University of Oklahoma Health Sciences Center pharmacy (OK-03176-04MD) was found to have approximately 2.1 X 10^6 DPM of removable contamination when it was received by the pharmacy. The package was empty and the contamination appeared to be confined to an area about 3 cm in diameter on a plastic sleeve which enclosed the shipping label. The nuclide has been identified as Tc-99m. OKDEQ will perform a reactive inspection next week." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-02-01
51674 | 0 | CURTISS WRIGHT NUCLEAR DIVISION |  |  |  |  | 2016-01-21 | 2016-01-22 14:09 | 2016-02-22 | PART 21 NOTIFICATION - POTENTIAL DEFECT IN OKONITE TAPE SPLICES The following information was obtained from Curtiss-Wright Nuclear Division via fax and email: "This letter is issued to provide initial notification of a potential defect in Okonite Tape Splices. The potential defect is inadequate radiation testing performed by Steris/lsomedix. "In response to NRC Information Notice 2015-12: 'Unaccounted for Error Terms Associated with the Irradiation Testing and Environmental Qualification of Important-to-Safety Components,' an investigation was performed to determine if products had radiation testing performed by Steris/lsomedix, and any impact. This investigation commenced on November 25, 2015. "It was determined on January 21, 2016 that the qualification of Okonite Tape Splices is affected by the unaccounted for error terms discussed in Information Notice 2015-12. This product has only been provided to James A. FitzPatrick Nuclear Power Plant. This customer will be notified today. "As a corrective action, Qualification Report PEI-TR-842900-1 will be revised to decrease the Total Integrated Dose (TID) reported by 9.6% based upon the guidance of Information Notice 2015-012. This revision will be provided to James A. FitzPatrick Nuclear Power Plant within 30 days of this notification. Notification will be provided when this corrective action is complete. "If additional information is required, please contact me by the methods provided below or Quality Assurance Manager Tony Gill: 256-426-4558, tgill@curtisswright.com." * * * UPDATE FROM SAMUEL BLEDSOE TO VINCE KLCO VIA FACSIMILE ON 2/22/2016 AT 1434 EDT * * * "February 22, 2016 "To whom it may concern: "On January 22, 2016, Curtiss-Wright Nuclear issued an initial notification letter to the Nuclear Regulatory Commission and customer James A. FitzPatrick Nuclear Power Plant concerning a potential defect in Okonite Tape Splices. The potential defect was inadequate radiation testing performed by Steris/lsomedix. As a corrective action, Qualification Report PEI-TR-842900-1 has been revised to decrease the Total Integrated Dose (TID) reported by 9.6% based upon the guidance of NRC Information Notice 2015-012: 'Unaccounted for Error Terms Associated with the Irradiation Testing and Environmental Qualification of Important-to-Safety Components.' As of this date, Qualification Report PEl-TR-842900-1, Revision C has been provided to James A. FitzPatrick Nuclear Power Plant. This letter provides the final status and closeout of the above referenced 10CFR21 notification. If you require additional details or would like to discuss further, please contact me by the methods provided below or Quality Assurance Manager Tony Gill: 256-426-4558, tgill@curtisswright.com. "Sincerely, Samuel Bledsoe Engineering Manager "Nuclear Division Curtiss-Wright 125 West Park Loop, Huntsville, AL 35806 T: 256.924.74481 M: 256.690.78521 F: 256.722.8533" Notified R1DO (Ferdas) and Part 21 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2016-01-22
51673 | 0 | UNIVERSITY OF MISSOURI |  |  |  |  | 2016-01-19 10:30 | 2016-01-22 12:37 | 2016-01-22 | LEAKING NI-63 SOURCE A 15 mCi Ni-63 source (Sealed Source Device Registry # CA0406S214S), used for research and development, was determined to be leaking greater than the 0.005 microCi limit. The leakage contaminated the desktop where it was being used. No personnel contaminations or overexposures occurred. The source was removed from service and is awaiting proper disposal. Decontamination of the desk, which is in a secure area, is in progress. An investigation into the event is in progress. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2016-02-01
51672 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-12-06 | 2016-01-21 16:23 | 2016-01-21 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE DUE TO DAMAGED GUIDE TUBE The following information was obtained from the State of Tennessee via email: "On December 6, 2015 at approximately 1300 EST, an exposure device D6032, (880 Delta) containing Source S/N SE4869, 50 Ci of Se-75, fell from its position on top of a flange assembly approximately six feet to the finished floor. Upon impact, the guide tube was crimped preventing the source from being able to return to the camera. The source was able to be returned to the collimator reducing the radiation present. Technicians secured a true two mR boundary and notified plant safety personnel and the RSO. The lead technician onsite was source retrieval certified and took charge of the retrieval process. The source was further shielded in a larger diameter pipe and covered with sand bags to reduce radiation levels. Using a pair of pliers, the technician was able to 're-round' the guide tube opening to allow the source to be returned to the camera. The guide tube, camera and control assembly was taken out of service pending inspection. The guide tube was damaged beyond use; the source 'pigtail' and control cable were inspected and tested using a no-go gauge. The guide tube was removed from service and the control assembly will be sent to the manufacturer for further evaluation (ball end connector). Source retrieval technician received a total dose of 150 mR during the event." Tennessee Report No.: TN-16-012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2016-01-29
51671 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-01-21 | 2016-01-21 13:06 | 2016-01-21 | AGREEMENT STATE REPORT - RADIOACTIVE GAUGE SHUTTER FAILURE The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "The roll pin on the shutter handle of a Ronan Engineering gauge broke, most likely due to environmental conditions. The shutter is in the closed position and the gauge is out of service. The licensee plans to contact the manufacturer for repair. No overexposures have occurred. "Manufacturer: Ronan Engineering Model: SA1-F37 Serial #: M7255 Isotope: Cs-137 Activity: 10 mCi "Cause of the Event: The gauge is located in a harsh and dirty environment. In the past, they designed and installed a cover to shield the gauge. When inspecting the gauge after the event, it was noticed that this cover had fallen off. "Actions: A reactive inspection is planned by the Department [Pennsylvania Department of Environmental Protection]. More information will be provided upon receipt." PA Report No.: PA160005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-01-29
51670 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-11-09 | 2016-01-20 18:32 | 2016-01-20 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING HIGH DOSE RATE THERAPY "The Department [Colorado Department of Public Health and Environment (CDPHE)] received a phone report from the Radiation Safety Officer for Saint Joseph Hospital regarding a medical event involving the HDR [high dose rate therapy]. A patient was scheduled to receive three fractions of HDR treatment in November, 2015. It is believed the second fraction caused the medical event on November 9, 2015. In December, the patient reported to their primary care physician, burns to the leg. The authorized user was notified in December by the patient and/or primary care physician. The authorized medical physicist and radiation safety officer were notified of the event on January 19, 2016 and notified CDPHE on January 20, 2016. The intended dose to the treatment site was 6,000 cGy with all of the intended dose being delivered to the patient's leg. The preliminary cause was an error with the transfer tube-applicator interface, but the licensee is still conducting an internal investigation. "The Department is expecting a full report from the licensee within 15 days and preparing for a visit to investigate the event." Colorado Event Report ID No.: CO16-M16-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2016-01-28
51669 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2016-01-20 13:11 | 2016-01-20 18:31 | 2016-01-20 | PRIMARY-SECONDARY CONTAINMENT PRESSURE DIFFERENTIAL EXCEEDED DUE TO CCP EXHAUST FAN TRIP "At 1308 CST on January 20, 2016, the main control room received an alarm that the containment building (VR) ventilation system continuous containment purge (CCP) exhaust fan (1VR07CB) tripped. At 1311 CST, primary-to-secondary containment differential pressure was reported to be +0.411 psid. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.4, Primary Containment Pressure, Action A.1, was entered due to the differential pressure outside the ñ 0.25 psid requirement. At 1327 CST, the CCP B subsystem was restarted and at 1339 CST, primary-to-secondary differential pressure was restored to within the limits of TS 3.6.1.4. The cause of the trip of the 1VR07CB is under investigation. "This event is reportable under 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that could have prevented the fulfillment of the primary containment function due to the differential pressure being outside the primary containment initial conditions to ensure that containment pressures remain within design values during a loss of coolant accident. This event is reportable under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of the primary containment function for the same reason. "The NRC Resident has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2016-01-20
51668 | 0 | SSM HEALTH ST. CLARE HEALTH CENTER |  |  |  |  | 2015-12-22 | 2016-01-20 14:59 | 2016-01-20 | MISSING I-125 CALIBRATION SEED "Licensed material involved: The lost material was a single I-125 sealed source Model 6711 with an apparent activity of 0.359 mCi on 9/14/2015. The specific source missing was the calibration seed ordered along with the implant sources, which are preloaded into needles. "Description of circumstances under which loss occurred: On 12/22/2015, during inventory and collection of seeds (from several prostate seed cases) for shipment back to the vendor for disposal, it was discovered that the calibration seed from one patient's pig was missing. This seed is distinctive due to the black marking on one half of the seed. This seed is only removed from its pig in the hot lab during calibration, so it is hypothesized that it inadvertently flipped out of forceps unnoticed during the calibration process. "A statement of disposition, or probable disposition, of the licensed material involved: The calibrated seed is shipped in a separate pig along with the preloaded needle trays. The calibration seed is only removed from the pig in the hot lab. Therefore, our feeling is that the highest probability of loss was in the hot lab during calibration. While it is difficult to be completely sure of the location of the seed, it is felt that it is still in the hot lab in an inaccessible location. "Exposures of individuals to radiation: Since the seed was not discovered on survey (at the lowest setting of the meter) in the hot lab nor the OR [Operating Room] suite, the best estimate of exposure to personnel is minimal. With the low energy of I-125 and the low activity of 0.359 mCi on the day of the implant (Sept. 24, 2015), it would not take much in the way of attenuating material to mitigate exposure to others. "Actions that have been taken to recover the material: The L-Block shielding and supplies were all dismantled, moved and searched, however the seed was not found. Storage carts and stored supplies around the hot lab were also moved and surveyed, the seed however was still not recovered. Although the OR suite was surveyed at the time of the implant as a part of our policy, we returned to the same OR suite upon discovery of the missing source to survey again. The seed was still not recovered. "Procedures or measures that have been, or will be, adopted to ensure against a recurrence: Several specific actions are warranted to reduce potential loss in the future. The highest likelihood of loss would seem to be when sources are being handled outside of their respective storage location. i.e. During movement of seeds from the pig to ion chamber and consolidation of unused seeds from the extra needles ordered for each implant. First, when the calibration seed is being removed and returned to the pig, use of reverse action forceps will be mandated. Secondly, when the seed is returned to the bottle and the cap replaced, the bottle will be inspected to verify it contains the calibration seed. Third, the practice of 'pushing out' seeds from unused needles into the pig following each case, in the OR suite, will no longer be allowed. Fourth and finally, the calibration source and the pig it is stored in, will remain in the hot lab. An extra pig with an empty bottle will be taken to the OR in the event a seed must be retrieved from a patient and must be stored." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2016-01-28
51667 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-01-18 | 2016-01-20 13:34 | 2016-01-20 | AGREEMENT STATE REPORT - FAILED SHUTTER ASSEMBLY ON LEVEL CONTROL GAUGE The following information was received from the Commonwealth of Pennsylvania via E-mail: "The Department [Pennsylvania Department of Environmental Protection] was notified on January 19, 2016, that during routine activities on January 18, 2016, the weld on the collimator block, which is part of the shutter assembly to the gauge, failed. This event is reportable per 10 CFR 30.50(b)(2). "The weld on the collimator block failed on a Thermo Measure Tech level control gauge. The shutter was closed at the time of the event and no workers received any dose. The licensee notified a service provider who responded and installed a new collimator assembly. Device Information: Manufacturer: Thermo Measure Tech Model: 5204 Device Serial Number: B497 Isotope: Cesium-137 Activity: 4 curies "[The cause is attributed to] equipment failure. "A new shutter assembly was installed and tested. The Department plans a reactive inspection. More information will be provided upon receipt. "Pennsylvania Event Report ID No.: PA160004" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-01-28
51666 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2016-01-19 | 2016-01-20 13:05 | 2016-01-20 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was received from the Commonwealth of Pennsylvania via E-mail: "On January 19, 2016, the Department [Pennsylvania Department of Environmental Protection] was notified that a moisture density gauge became disabled from damage in Berwyn, Pennsylvania. This event is reportable per 10 CFR 30.50(b)(2). "The gauge was run over by a piece of heavy equipment. This damaged the gauge and it became unusable. The source rod was in the retracted position at the time of the incident and instrument readings confirmed no damage to the source occurred. The gauge was taken out of service and transported to the manufacturer for servicing. No exposures occurred. "Manufacturer: lnstroTek "Gauge Model: 3500 Xplorer "Gauge S/N: 000856 "Radioactive Material: Cesium-137: 11 milliCuries, Americium-241: 44 milliCuries "[The cause is attributed to] human error. "The gauge was transported to the manufacturer for repair. A reactive inspection was performed by the Department and verified the validity of the licensee's instrument readings regarding exposure and leaking sources. "Pennsylvania Event Report ID No.: PA160003" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-01-28
51665 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-01-20 | 2016-01-20 14:06 | 2016-01-20 | AGREEMENT STATE REPORT - LOSS OF PROCESS AUTOMATION BETA GAUGE The following information was received from the State of Illinois via email: "The Plant Manager for WINPAK, Inc., in South Chicago Heights, IL, called to report the loss of an ABB Process Automation Model O-2 beta gauge (SN S-1379-T) containing 70 milliCuries of Sr-90. The recent annual general license self inspection revealed some discrepancies in serial numbers and the licensee could not locate this particular device. They believe it to have likely been removed by a local scrap vendor that was on-site. Another possibility is an equipment vendor that was doing some work on site. Both vendors are being contacted as part of the investigation. lEMA [Illinois Emergency Management Agency] staff are at the scrap yard today investigating as well. "The licensee is continuing to pursue possible leads on the location of the source. lEMA has contacted the manufacturer and they have no records of return but have contacted NDC [does service work under contract to ABB] to see if they retrieved it under contract work. This item will remain open for the required time until the source is recovered or declared lost." Illinois Item Number: IL15022 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2016-01-28
51664 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2016-01-20 04:00 | 2016-01-19 18:41 | 2016-01-22 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED PREVENTATIVE MAINTENANCE "At 0400 CST on Wednesday, January 20, 2016, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system will be removed from service for planned maintenance activities. During the maintenance, the TSC Ventilation will be shut down. The TSC air filtration fan and dampers will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed in approximately 43 hours. "Contingency plans are in place so that if an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Planning (EP) procedures and checklists. If radiological or environmental conditions require TSC facility evacuation during ventilation system restoration; the Station Emergency Director will relocate the TSC staff in accordance with station procedures. "The NRC Resident Inspector has been notified." * * * UPDATE AT 0049 EST ON 1/22/16 FROM STEVEN MELL TO JEFF HERRERA * * * "At 2223 CDT on 1/21/16, Dresden TSC Ventilation was restored. The Dresden TSC Ventilation is functional at this time. "The NRC Resident Inspector has been notified." Notified R3DO (Cameron). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-01-19
51663 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-19 16:30 | 2016-01-19 17:42 | 2016-03-10 | UNANALYZED CONDITION DISCOVERED DURING REVIEW OF OUTAGE DATA "On January 19, 2016, while reviewing outage data, plant staff recognized that anomalous data collected in October, 2015, for the 21 Auxiliary Feed Pump time response loop resulted in an unanalyzed condition. Preliminary investigation has revealed that the condition most likely existed since April 20, 2015, when maintenance activities were performed on the auxiliary feedwater pump discharge pressure transmitter. Consequently, there were multiple instances when one of the other auxiliary feedwater pumps was removed from service, thus creating a condition which did not meet the accident analysis assumptions for auxiliary feedwater flow initial response. "This event is being reported under the requirements of 10 CFR 50.72(b)(3)(ii)(B) as 'the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' This condition was corrected on November 20, 2015." The auxiliary feedwater pump discharge pressure transmitter instrument isolation valve was inadvertently left closed after the April 20, 2015 maintenance. The licensee has notified the NRC Resident Inspector and will notify the State of New Jersey, State of Delaware, and the local township. * * * RETRACTED ON 3/10/16 AT 1647 EST FROM JACK OSBORNE TO DONG PARK * * * "This event is being retracted. An engineering review determined that while the auxiliary feedwater flow loop response time test results did not meet the procedural acceptance criteria, the accident analysis assumptions remained valid. The ATWS [Anticipated Transient Without Scram] was the limiting accident, and the loop response time results were still bounded by the existing analyses. The failed loop response time did result in a condition prohibited by TS which will be reported in a Licensee Event Report (LER). This condition has been documented in the licensee's Corrective Action Program." The licensee has notified the NRC Resident Inspector. Notified R1DO (Dimitriadis). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-01-19
51662 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2016-01-18 21:00 | 2016-01-19 15:56 | 2016-01-19 | ACCUMULATION OF URANIUM OXIDE POWDER IN THE DRY SCRAP RECYCLE FURNACE OFF-GAS SYSTEM "It was discovered on 1/18/16, that an accumulation of uranium oxide existed that indicated a degradation of an IROFS [Item Relied On For Safety] in the dry scrap recycle furnace off-gas system. Approximately 42 kg of uranium oxide powder was removed from the favorable geometry off-gas dropout. The degraded IROFS resulted in a failure to meet performance requirements in the event of a fire. The dry scrap recycle operation had been shut down on 1/14/16 and was not in operation at the time. "Additional controls on combustibles, geometry and moderation remained intact and at no time was an unsafe condition present. "Additional corrective actions, extent of condition, and extent of cause are being investigated. "This event is being communicated to meet the reporting requirements of 10CFR70, Appendix A(b)(2)." The licensee will inform State and local agencies and NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2016-01-19
51661 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2016-01-14 | 2016-01-19 09:09 | 2016-01-19 | AGREEMENT STATE REPORT - COMTAMINATION FOUND ON SHIPMENT The following report was received from the Oklahoma Department of Environmental Quality via email: "On January 14, 2016, [the Oklahoma Department of Environmental Quality] was informed that a package containing licensed material shipped from the University of Oklahoma Pharmacy (license OK-03176-04MD) to the University of Oklahoma Medical Center (OK-21035-01) was found to have approximately 17,000 DPM of removable contamination. The contamination appeared to be confined to a plastic sleeve the address label was in. There was no reported damage to the package or contents." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2016-01-27
51660 | -1 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2016-01-17 05:29 | 2016-01-17 07:22 | 2016-01-21 | ALERT DECLARED FOR FIRE NOT EXTINGUISHED WITHIN 15 MINUTES A plant employee discovered a fire in the mechanical factory strap plating room and activated the fire alarm. At 0529 EST, the licensee notified the Richland County Fire Department. The fire was extinguished and the Alert declaration was terminated at 0709 EST. No radioactive materials were involved and no injuries were reported. The licensee notified the State and R2 (Michel). Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). * * * RETRACTION FROM NANCY PARR TO HOWIE CROUCH AT 1726 EST ON 1/21/16 * * * Upon further review and investigation by the licensee, it was determined that the fire was extinguished within 15 minutes. As such, no Alert declaration was required. Based on these facts, the licensee has retracted this event notification. The licensee has notified their R2 Senior PM (Carmen Riviera-Crespo). Notified R2DO (McCoy). Notified NMSS (Erlanger, Moore) and IRD (Stapleton, Gott) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | SC | FUE |  | 70.32(i) |  |  |  | 0 | 2016-01-17
51659 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2016-01-15 20:38 | 2016-01-16 01:42 | 2016-01-16 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "On January 15, 2016 at 2038 CST, an alarm was received indicating Secondary Containment Differential Pressure rose unexpectedly above the Technical Specification Surveillance Requirement, SR 3.6.4.1.1, limit of 0.10 inch of vacuum water gauge. This loss of differential pressure occurred when Operations had entered the 2A Reactor Water Cleanup Pump room. The pump room door was closed and Secondary Containment Differential Pressure returned to Technical Specification limits in approximately 4 minutes. The Standby Gas Treatment System remained in standby and fully operable. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.1. As a result, entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to secondary containment being inoperable. "Given the temporary loss of secondary containment, this event is reportable under 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Senior Resident Inspector has been notified." The licensee also notified the State of Illinois Emergency Management Agency. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-01-16
51658 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-01-14 12:01 | 2016-01-15 17:09 | 2016-01-15 | AGREEMENT STATE REPORT - FIXED GAUGE WITH SHUTTER STUCK IN OPEN POSITION The following Agreement State Report was received from the State of Louisiana via email: "The RSO [Radiation Safety Officer], called to report that a gauge installed on a process at the licensee's Westlake, LA facility, had a shutter malfunction. The gauge is installed on a routing process for material at the facility. The gauge shutter is stuck in the open position. "The Gauge is a Berthold Technologies, Model: Berthold Systems, LB-330 utilizing a 12 mCi Cs-137 source, Model: Lab. Prof. Dr. Berthold Dwg. #2653.100-001. The source and gauge will remain on the process in operation until the Berthold Technician arrives over the weekend service the gauge. This will be either make the necessary repairs to the shutter or remove the gauge from service and perform the disposal. Due to the age of the gauge, if it cannot be repaired, disposal is the resolution. This will be determined by the Berthold personnel performing the repair. The service order request has the repairs scheduled to be made over this weekend. "There are no exposure or health and safety issues involved with this event. The gauge and rod source will remain installed on the functioning process. The resolution of the situation will be directed by the ability to be repaired or if the gauge should be de-installed and sent for disposal. "The corrective action: Will be determined by the ability of the Berthold Technician to repair the shutters on the gauge or if the gauge needs to be de-installed and sent for disposal. The repairs and or corrective actions will be determined by a site visit and assessment by Berthold Technologies." The State of Louisiana considers this event to be closed. State Event Report ID No: LA 160002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-01-25
51657 | 0 | PA DEP BUREAU OF RAD PROTECTION |  |  |  |  | 2016-01-14 | 2016-01-15 08:55 | 2016-01-15 | AGREEMENT STATE REPORT - SHUTTER MALFUNCTION The following was received from Pennsylvania via fax: "On January 14, 2016, the Department [PA DEP Bureau of Radiation Protection] was notified by Universal Well Services that a malfunction of a roll pin on a shutter handle occurred at the Hop Bottom, Pennsylvania temporary job site. It is reportable per 10 CFR 30.50(b)(2). "A roll pin, which holds the shutter handle to the shutter shaft, on an in-line density gauge, became dislodged rendering the gauge unusable. The shutter is in the closed position and out of service awaiting repair from a service provider. No exposures occurred. "Radionuclide: Cs-137 "Manufacturer: Berthold "Model: LB 8010 "Serial Number: 10059 "Activity: 20 mCi "The shutter is in the closed position and the gauge is out of service and secure. There was no other damage to the gauge. A reactive inspection is planned by the Department." PA Event ID # PA160002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-01-25
51656 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-01-14 | 2016-01-14 19:57 | 2016-01-27 | AGREEMENT STATE - RADIATION LEVELS ON PACKAGE GREATER THAN 1 REM/HR LIMIT The following report was received from the Texas Department of State Health Services via email: "On January 14, 2016, the licensee notified the Agency [Texas Department of State Health Services] that it had received an exclusive use shipment of sources in Type A containers that originated in Maryland. The dose rate on one of the containers, which held an 8.4 curie Cobalt-60 source (current activity/decay corrected), exceeded the 1,000 mR/hr limit. The highest dose rate reading on the exterior of the container was 1,900 mR/hr. The licensee surveyed the cab of the truck and measured a dose rate of less than 0.05 mR/hr for the driver. The exterior of the trailer was surveyed and the left side highest measurement was 120 mR/hr and the right side was 50 mR/hr. These dose rates for cab and trailer are below regulatory limits. The licensee reported that none of its workers received any overexposure. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I 9371 * * * EVENT RETRACTION FROM KAREN BLANCHARD TO JOHN SHOEMAKER AT 1326 EST ON 1/27/16 * * * The following event retraction was received from the State of Texas via email: "Texas does not have any regulatory authority for this event. The shipper is licensed by the State of California. Event information has been sent to Robert Greger in California. Headquarters Operations Officer and NMSS Regional Coordinator directed that we [State of Texas] retract our event and for California to report." Notified the R4DO (Farnholtz), NMSS Events Notification, RGN-IV (Erickson), and RGN-IV (Tharakan) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-01-22
51655 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-14 14:43 | 2016-01-14 18:10 | 2016-02-23 | NOTIFICATION OF UNUSUAL EVENT - SECURITY CONDITION THAT DOES NOT INVOLVE HOSTILE ACTION A security condition that does not involve a hostile action was reported by the Diablo Canyon security watch commander. At 1443 PST on 1/14/16, Diablo Canyon declared an Unusual Event, due to an unauthorized person in the Owner Controlled Area. Site Security was dispatched and assistance was requested from the local Sheriff's Department. The individual was apprehended. At 1602 PST on 1/14/16, Diablo Canyon terminated the Unusual Event after the individual was apprehended and placed in custody of local law enforcement. Diablo Canyon remained at 100 percent power for the duration of the event. No radiological release has occurred and all radiation levels are normal on both units. A press release is planned. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified FEDS (DHS SWO, FEMA Ops, DHS NICC, and NuclearSSA via email.) * * * UPDATE AT 1905 EST ON 02/23/16 FROM DOUG EVANS TO S. SANDIN * * * "This Notification is being retracted. "Upon further evaluation, Pacific Gas and Electric has determined that declaration of the Unusual Event was not required. The event did not constitute a threat or compromise to site security, did not involve a threat or risk to site personnel, did not represent a potential degradation to the level of safety of the plant, and did not affect the health and safety of the public. "The licensee has notified the NRC Resident Inspector of the retraction." Notified R4DO (Whitten), IRD (Stapleton) and NRR (Morris). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2016-01-15
51654 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-14 11:33 | 2016-01-14 16:07 | 2016-01-14 | FITNESS FOR DUTY - NON LICENSED SUPERVISORY EMPLOYEE TESTED POSITIVE A non-licensed supervisory employee tested positive for alcohol during a random fitness for duty test. The individual's plant access has been denied. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2016-01-14
51653 | 0 | PA DEP BUREAU OF RAD PROTECTION |  |  |  |  | 2016-01-13 | 2016-01-14 10:31 | 2016-01-14 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received from the State of Pennsylvania via facsimile: "On January 13, 2016, the Department [PA DEP Bureau of Radiation Protection] was notified that a Troxler gauge was damaged while on the job site in Pennsylvania. This event is reportable within 24-hours per 10 CFR 30.50(b)(2). "A Troxler gauge was hit with a truck while on a job site. The source rod became detached from the gauge and rendered the gauge unusable. The area was secured and a local service provider was notified to recover the gauge. The gauge was not found to be leaking and was secured for shipment back to Troxler for repair. There was no exposure to workers or the public. "Gauge Model: 3440 "Test Date: 7/6/2015 "Gauge S/N: 18936 "A local service provider assisted with retrieval of the gauge. A reactive inspection was performed by the Department. More information will be provided upon receipt." PA Event Report ID No: PA160001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-01-22
51652 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2016-01-05 | 2016-01-13 17:40 | 2016-01-13 | AGREEMENT STATE - FIXED NUCLEAR GAUGE REPORTED MISSING The following report was received from the North Carolina Department of Health and Human Services via email: "The RSO [Radiation Safety Officer for International Paper Company], first noticed the missing FNG [fixed nuclear gauge] after the renovation of an older chute and replacement by the new metal chute. The older scrap parts had been taken to Southern Metals in Wilmington, NC scrapyard. The six month inventory was due at the time and the specific date of the inventory check was January 5, 2016. Several rechecks have been made within the storage areas where other gauges are stored and secured and contacts with the metal chute manufacturer, ICBS Group, and the scrapyard have been made, without a trace of the gauge. "Source/Radioactive Material: Cs137, 9 mCi; Thermo Measure Tech, source model 57157C "Device: Thermo Measure Tech, gauge model 5192 SN# B3195 "State inspectors [North Carolina Department of Health and Human Services] will be conducting a reactive on site investigation tomorrow (1/14/2016) to determine causes and if any corrective actions have been implemented. Our Agency [North Carolina Department of Health and Human Services] will also be visiting the scrapyard where old licensee parts were shipped in the event the gauge was sent there by accident. Portal monitors and scrap material will be checked for functionality and presence of heightened radiation, respectively." NC Report ID No.: NC160003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2016-01-21
51651 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2015-12-15 | 2016-01-13 16:24 | 2016-01-15 | MEDICAL EVENT - BRACHYTHERAPY SOURCE NOT PLACED IN INTENDED TREATMENT LOCATION This is a preliminary notification by the State of Maryland, Radiological Health Program of a medical event. During both the first and second of four High Dose Rate brachytherapy treatments to one of the patient's lungs occurring on December 15, 2015 and December 21, 2015, the radioactive source was incorrectly placed between 2 and 3 centimeters away from the intended placement location. The radioactive source being used was Iridium 192. The activity level of the radioactive source is unknown at this time. The placement error was discovered during the third treatment on January 13, 2016. The reason for the placement error involved the use of an incorrect connection between the marker and the catheter. The State of Maryland, Radiological Health Program will conduct an investigation on January 18, 2016. * * * UPDATE FROM ALAN JACOBSON TO JOHN SHOEMAKER AT 1249 EST ON 1/15/16 * * * This updated licensee report was received from the State of Maryland via email: "On January 12, 2016, while treating the third treatment fraction for an HDR patient with exuberant granulation tissue of the right lung lower lobe bronchus, we [the licensee] found out a discrepancy in our simulation imaging procedure which contributed to a geographic miss of approximately 4 cm. The geographic miss occurred for the patient's 1st and 2nd fractions on 12/15/2015 and 12/21/2015, respectively. The activity of the source was 6.9 Curies on 12/15/2015. "In this procedure a dummy marker is normally sent into the catheter and radiographed to mark the dwell source position for treatment. It was found that in previous two treatments the dummy marker was not sent all the way through the catheter because it was used with an adapter piece on. The adapter piece was used with dummy markers in the previous microSelectron afterloader but it is not supposed to be used with the Flexitron afterloader system that we have been upgraded to since August 2014. "The patient was treated correctly on 1/12/2016, however, the Radiation Oncologist is stating that no harm was done to the patient from the geographical miss in last two treatments. Since we reported this case to the State [Maryland Department of the Environment] on Wednesday 1/13/2016, we have found two more patients treated with intrabronchial HDR since the upgrade to Flexitron at this center that may have had a geographic miss. Investigation is still under way for these cases." Notified the R1DO (Gray) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2016-01-21
51650 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2016-01-12 13:40 | 2016-01-12 19:08 | 2016-01-12 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "On January 12, 2016, at 1340 CST, an alarm was received indicating secondary containment differential pressure rose unexpectedly above the Technical Specification Surveillance Requirement, SR 3.6.4.1.1, limit of 0.10 inch of vacuum water gauge. A reactor building supply fan was immediately secured to restore differential pressure below the Technical Specification limit. The secondary containment differential pressure returned to below the Technical Specification limit within one minute. The Standby Gas Treatment System remained in standby, and fully operable. At 1341 CST, the secured reactor building supply fan was restarted to restore the normal ventilation lineup. The secondary containment differential pressure remained below the Technical Specification limit. Troubleshooting is in progress. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.1. As a result, entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to secondary containment being inoperable. "Given the temporary loss of secondary containment, this event is reportable under 50.72(b)(3)(v)(c) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-01-12
51649 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2016-01-12 12:53 | 2016-01-12 18:37 | 2016-01-13 | LOSS OF VENTILATION SYSTEM TO EMERGENCY OFF-SITE FACILITY "On January 12, 2016, during performance of an EOF [Emergency Off-Site Facility] Diesel Operability Test, the EOF Air Conditioning unit and EOF Air Return fan did not run as expected. Per plant procedure, the operators placed the system in filtration mode and then back in normal mode. Again, both units did not run as expected. The EOF was declared non-functional due to the failure of the air conditioning unit and fan. "The EOF is available for emergency response purposes unless the temperature can not be maintained or a release is in progress. The backup EOF is available for use if needed." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAVID LANTZ TO DONALD NORWOOD AT 1517 EST ON 1/13/16 * * * "The Emergency Off-Site Facility (EOF) was restored to functional status at 1223 CST on 01/13/2016." The licensee notified the NRC Resident Inspector. Notified R4DO (Kellar) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-01-12
51648 | 0 | CRITTENTON HOSPITAL MEDICAL CENTER |  |  |  |  | 2016-01-11 | 2016-01-12 15:39 | 2016-01-12 | MEDICAL EVENT - PATIENT RECEIVED DOSE GREATER THAN PRESCRIBED In preparation for lymphoscintigraphy, a patient was injected with 2.4 mCi of unfiltered technetium sulfur colloid (Tc-99) instead of the prescribed dose of 0.5 to 1.0 mCi. The Radiation Safety Officer and Hospital Medical Physicist were notified. The patient's primary physician was also notified. No adverse effects to the patient are expected. This event was caused by the administering technologist's failure to double check the dose given to the patient. The technologist has been counseled. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-01-20
51647 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2016-01-11 22:45 | 2016-01-12 11:31 | 2016-01-12 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE COULD NOT BE RETRACTED TO SHIELDED POSITION The following information was provided by the State of Texas via email: "On January 12, 2016, the Agency [Texas Department of State Health Services] received notice that on January 11, 2016, a radiography source could not be retracted to the shielded position. The camera was an 880D with a 99.8 curie Iridium-192 source. An extension to the guide tube had not been connected, and the drive cable slipped the gears of the crank assembly. The drive cable and crank assembly were reassembled and the source was returned to the shielded position. No overexposures resulted from this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2016-01-20
51646 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2016-01-11 12:00 | 2016-01-12 11:14 | 2016-01-12 | FITNESS FOR DUTY "Event Report per 10 CFR 26.719(b)(2)(ii) "On January 11, 2016, Callaway determined a violation of two provisions of the site Fitness For Duty policy were committed offsite by a non-licensed supervisory employee. Unescorted access for the employee has been denied." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 26.719 |  |  |  | 0 | 2016-01-12
51645 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2016-01-11 03:16 | 2016-01-12 10:56 | 2016-01-12 | AGREEMENT STATE REPORT - QUANTITY OF CONCERN ATTEMPTED THEFT Unauthorized entry and attempted theft of Category 2 material. Licensee informed local law enforcement. Louisiana Event Report ID # LA160001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-01-20
51644 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-01-09 02:37 | 2016-01-09 07:04 | 2016-01-09 | AUTOMATIC REACTOR SCRAM ON MAIN STEAM ISOLATION DUE TO ELECTRICAL FAULT "On 1/9/16 at 0237 [CST], River Bend Station sustained a reactor scram during a lightning storm. An electrical transient occurred resulting in a full main steam isolation [MSIV] (Group 6) and a Division II Balance of Plant isolation signal. During the scram, level 8 occurred immediately which tripped the feed pumps. A level 3 signal occurred also during the scram. Subsequent level 3 was received three times due to isolated vessel level control. The plant was stabilized and all spurious isolation signals reset, then the MSIVs were restored. The plant is now stable in Mode 3 and plant walkdowns are occurring to assess the transient." During the scram, all rods inserted into the core. The plant was initially cooled down using safety relief valves. Offsite power is available and the plant is in its normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2016-01-09
51643 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2015-11-11 | 2016-01-08 16:25 | 2016-03-11 | PART 21 - COMMERCIAL GRADE CAP SCREWS PROVIDED WITH SAFETY RELATED FISHER TYPE 3570 POSITIONERS The following information was provided by the reporting organization via fax: "Pursuant to 10 CFR 21.21(a)(2), Fisher Controls International LLC ('Fisher') is providing required written interim notification of a failure to comply concerning Type 3570 positioners when provided as safety-related equipment. "On November 11, 2015, Fisher became aware of an issue with the dedication of a Type 3570 positioner. When replacement Type 3570 positioners are ordered, the two cap screws (SAE J429 Grade 5 cap screws/size 3/8-16x1.5) used for mounting the positioner to the actuator cylinder are also included. It was not clearly communicated to the end user that these mounting cap screws are included with the positioner. Further, the dedication plan only addresses the 3570 positioner and does not include dedication of the mounting cap screws. "As a result, these cap screws had not been dedicated on any safety-related Type 3570 positioner orders. There is no reason to believe any of the cap screws supplied were defective, only that they were not dedicated and were therefore supplied as commercial grade items. There have been no reported failures of the cap screws in question. "An extent-of-condition investigation is underway to identify all potentially affected bolt-on accessories. Any identified affected products will be reported per the requirements of 10 CFR 21.21 (b). This extent-of-condition review is expected to be completed by January 29, 2016. "Corrective Action 1791 has been opened to document corrective actions taken to prevent reoccurrence. "Should there be any further questions concerning this matter, please contact Benjamin Ahrens, Manager, Quality by email at Benjamin.Ahrens@Emerson.com or via phone at 641-754-2249. Individual informing the NRC: Chad Engle, Director, Nuclear Business Unit, Fisher Controls International LLC, phone (641) 754-3011. * * * UPDATE FROM GEORGE BAITINGER TO HOWIE CROUCH VIA FAX AT 1528 EST ON 2/2/16 * * * The following information is summarized from a fax received from Emerson Process Management (Fisher Controls): On January 22, 2016, Fisher Controls completed their extent-of-condition investigation and determined that seven of their thirty two product series have the potential to include non-dedicated cap screws and mounting studs. The vendor plans to complete their final report within 45 days. Notified R1DO (Rogge), R2DO (Musser), R3DO (Kozak), R4DO (Pick) and the Part 21 group via email. * * * UPDATE FROM LYNN SANDERS TO DONG PARK VIA EMAIL AT 1749 EST ON 3/11/16 * * * The following information is summarized from an email received from Emerson Process Management (Fisher Controls): "The supplied instrument assemblies in question were subjected to the processing requirements of Fisher Controls FMP2K27 (Control of Commercial Grade Items to be Dedicated for Use in Nuclear Safety-Related Applications) and were supplied as safety-related components. However, Fisher supplied various mounting parts (in addition to the requested product) that were not processed under FMP2K27; thus, such parts were supplied as commercial items. "This issue was first discovered in relation to the cap screws used for mounting a 3570 positioner (please see Interim Report dated 01/08/2016). Fisher conducted an extent-of-condition investigation to include all safety-related actuator-mounted accessories. In total, thirty -two (32) actuator-mounted item types were investigated. It is Fisher's opinion the failures to dedicate these mounting accessories do not pose an inherent safety risk. "Additionally, there are no known field issues with respect to the affected equipment and all such non-dedicated equipment passed the required standard testing. "Each affected customer needs to: (i) evaluate the application of each referenced item number for all respective orders; (ii) determine whether the incorrectly processed mounting parts are in violation of regulatory requirements; (iii) contact Fisher or otherwise arrange for the procurement of properly processed mounting parts for use in those applications found to be in violation. In addition, a Corrective Action Request (CAR 1791) has been initiated by Fisher to prevent reoccurrence of this issue." Notified R1DO (Dimitriadis), R2DO (Suggs), R3DO (Riemer), R4DO (Proulx), and the Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2016-01-08
51642 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2016-01-07 19:00 | 2016-01-08 00:03 | 2016-01-08 | UNANALYZED CONDITION - APPENDIX R CREDITED PROCEDURES NOT IN PLACE "Prairie Island's Appendix R calculations credit a procedurally established repair instruction to the Train B Pressurizer Vent valves for a postulated fire in Fire Area 59 (Unit 1) and Fire Area 74 (Unit 2) to obtain Mode 5 during a postulated fire in the affected areas. At 1900 [CST] on 1/7/2016, during a review of corrective actions associated with Prairie Island's NFPA 805 transition, it was identified that the required procedures are not in place to make the analyzed repairs. "It has been determined that this condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "As compensatory measures, hourly fire watches are in place in the affected areas of the Auxiliary Building. The operating crew and Fire Brigade have been briefed on the impact of a fire in the affected area. This brief will continue to future operating shifts via a standing instruction. Fire detection equipment for the affected zones has been protected to ensure availability and operating crews are walking down the affected areas to verify any required transient combustibles in the affected areas are controlled in accordance with plant procedure. These compensatory measures, in addition to automatic fire detection and suppression capability in these fire areas, ensure protection of the potentially affected equipment until corrective actions can be completed. "This condition does not affect the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2016-01-08
51641 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-12-19 | 2016-01-07 16:45 | 2016-01-07 | AGREEMENT STATE REPORT - HUMAN ERROR PREVENTS A RADIOGRAPHY SOURCE FROM RETRACTING The following report was received via e-mail: "On December 19, 2015, a crew from Mistras was working at a temporary jobsite [Donaldsonville, LA] located at CF Industries. The crew set up 2 mR boundaries for the duration of the 'shots'/exposures. The crew cranked out the source and made the exposure. When the crew tried to retract the source into the shielded position, [the source] would not [retract] because the guide tube was improperly connected to the exposure device. The source assembly remained out of the shielded position. When it was determined the source could not be retracted, immediately the area was cleared and the boundaries were reestablished for the 2 mR/hr distance. "The lead radiographer contacted the RSO, and received instructions on how to secure/shield the area from potential/unnecessary exposures. The unshielded source and incident duration was from 1.5 hours to 2 hours. "The initial notice to the Department [LA Department of Environmental Quality] was made at approximately 1257 CST after the source was secured in the shielded position. The RSO did the actual retrieval and securing of the source. His time in the radiation field was approximately 30 to 40 minutes. He used the standards of time, distance and shielding to protect himself. His direct read pocket dosimeter reading was approximately 60 mR. The crew members pocket dosimeter readings were 50 mR and 20 mR. "The exposure device and associated equipment (crank out control and source guide tube) were SPEC 150 exposure device S/N 1106 and a SPEC G-60 source. The source was 61 Ci of Ir-192. The equipment was evaluated and passed the quality assurance requirements. The radiography staff was reinstructed in the Mistras' Operation and Equipment Manual. Specifically the setup and equipment assembly, connecting and cranking out of the source and operating in potentially occupied areas." Louisiana Report: LA-150023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2016-01-15
51640 | 0 | HENRY FORD HOSPITAL |  |  |  |  | 2016-01-06 10:27 | 2016-01-07 15:08 | 2016-01-08 | POTENTIALLY REPORTABLE UNDERDOSE TO PATIENT A patient at the Henry Ford Hospital Interventional Radiology Department received a Y-90 Theraspheres treatment of 120 Gray to a portion of the left lobe of the liver via a written directive from the referring physician. The Interventional Radiologist administered the prescribed dose to the entire left lobe of the liver, and the hospital believes that will result in an underdose to the patient. The exact amount of the underdose has not determined at the time of this report. The referring physician has been notified and the licensee will inform the NRC when the patient has been notified. It is believed that this event will not result in any harm to the patient. The licensee is in the process of determining corrective action to prevent reoccurrence. * * * UPDATE FROM ALAN JACKSON TO JEFF ROTTON AT 1543 EST ON 01/08/2016 * * * The following update information was provided by the licensee via email: "Providing additional materials related to a potential medical event that was reported on January 7, 2016 by Henry Ford Hospital (License 21-04109-16; Docket: 030-02043). Hospital reported an apparent deviation from the written directive of a Y-90 TheraSpheres treatment done on January 6, 2016. The written directive was prepared in tandem by a Radiation Oncologist and a Nuclear Medicine Authorized User physicians for the major portion of the left lobe of the liver, omitting segments 4A and 4B. The entire left lobe of the liver, including segments 4A and 4B, was treated by the Interventional Radiologist. The written directive called for the administration of 2.3 GBq (62.2 mCi) of Y-90. The activity delivered was 2.37 GBq (64 mCi) which properly conformed with the activity specified in the written directive. However, the dose delivered to the liver deviates from the intended dose in two important ways. First, the written directive did not include treating segments 4A and 4B of the left lobe of the liver. Secondly, the dose delivered of 94 Gy (9,400 rad) to the left lobe of the liver was lower (21.5%) than the intended dose of 120 Gy (12,000 rad). The Interventional Radiologist, who is the referring physician for this patient, originally intended to treat the entire left lobe of the liver, including segments 4A and 4B. This Interventional Radiologist, while very experienced in TheraSpheres treatments was new to the institution and proper communication of the intended treatment site did not occur. "It is important to note that all of the physicians involved indicated that no harm resulted to the patient as a result of this deviation. According to the TheraSpheres package insert, the recommended therapeutic dose to the liver is 80 Gy to 150 Gy (8,000 rad to 15,000 rad). Thus the treatment dose of 94 Gy (9,400 rad) is well within the therapeutic range. The referring physician was notified about this case and he notified the patient about the treatment deviation." Notified R3DO (Stoedter) and NMSS Events Notification group via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2016-01-15
51639 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-07 07:59 | 2016-01-07 14:16 | 2016-01-07 | LOSS OF BOTH METEOROLOGICAL TOWERS DUE TO POWER SYSTEM FAILURE "At 0759 CST on 01/07/2016, a partial loss of the 25kV Plant Support Power Distribution System caused an unplanned loss of both primary and backup meteorological towers at Comanche Peak Nuclear Power Plant. Loss of both meteorological towers constitutes a major loss of emergency assessment capabilities in regard to meteorological conditions. During the power loss, the National Weather Service was available to compensate for the on-site data loss. The 25kV system and both meteorological towers were restored at 0923 CST on 01/07/2016. "The 25kV Plant Support Power Distribution System feeds non-safety related equipment and does not affect plant operation, with the exception already described. The fault occurred due to an aged stress cone and faulty lightning arrestor. The fault was isolated and power was restored." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-01-07
51638 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-07 09:00 | 2016-01-07 09:35 | 2016-01-07 | INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA The actual introduction of contraband into a protected area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2016-01-07
51637 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2016-01-05 22:58 | 2016-01-06 09:38 | 2016-01-06 | SECONDARY CONTAINMENT DECLARED INOPERABLE "At [2258] CST, on January 5, 2016, with the plant operating at 100 percent power, the main control room alarm indicating high pressure in the auxiliary building actuated. Operators confirmed that the building pressure, corrected for temperature, indicated slightly positive, whereas the building pressure limit in Technical Specifications is 0.0 - 3.0 inches of water negative pressure. Secondary containment was declared inoperable, and the Division 2 standby gas system was started. This action restored building pressure to the acceptable range, and the building was declared operable at [0027 CST] on January 6. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as an event that caused the secondary containment to be potentially incapable of performing its safety function. The NRC Senior Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2016-01-06
51636 | 0 | NEW JERSEY DEPT OF ENVIR PROTECTION |  |  |  |  | 2016-01-05 | 2016-01-05 16:13 | 2016-01-05 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following was received from New Jersey via fax: "The hospital's Radiation Safety Officer reported that a patient was due to receive a therapeutic treatment of Y-90 SIR-Spheres. The prescribed dose was 10.5 milliCuries to the left lobe of the liver. The dose administered was only 65% of the prescribed dose. Approximately 3.2 milliCuries remained in the vial after the administration was completed. The patient was underdosed and has been informed. Additional details will be forthcoming from the hospital." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2016-01-13
51635 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-05 11:20 | 2016-01-05 16:07 | 2016-01-05 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE "A condition impacting functionality of the TSC [Technical Support Center] ventilation system was discovered on 1/5/2016 at 1120 [EST]. The issue involves a loss of cooling capability of the TSC ventilation system due to a failed compressor. Maintenance will begin repairs as soon as parts are made available. Estimated time to repair is unknown at this time. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable. If relocation of the TSC becomes necessary, the Emergency Coordinator will relocate the TSC staff to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team will be notified of the condition and the possible need to relocate during an emergency. This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2016-01-05
51634 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2016-01-04 06:00 | 2016-01-04 08:14 | 2016-01-04 | OFFSITE NOTIFICATION DUE TO AN EMERGENCY DIESEL ENGINE COOLANT LEAK "The NJ DEP [New Jersey Department of Environmental Protection] was contacted due to a coolant leak from our Emergency Diesel Generator [EDG] that reached the waters of New Jersey. The coolant contains a hazardous substance per NJAC 7:1 E." The EDG has been removed from service for repairs. The Licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-01-04
51633 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2016-01-02 23:40 | 2016-01-03 02:31 | 2016-01-03 | INADVERTANT SIREN ACTUATION "On 01/02/2016 at 2340 [CST], personnel at the Ogle County 9-1-1 call center inadvertently actuated the emergency response sirens associated with Byron Generating Station multiple times. The emergency response sirens were secured at approximately 2350. "This event is being reported under 10CFR50.72(b)(2)(xi) for, 'any event or situation, related to the health and safety of the public or on site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.' "The licensee has notified the State of Illinois and the NRC Resident Inspector." All sirens are operable and available if needed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-01-03
51632 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2016-01-02 23:05 | 2016-01-02 23:56 | 2016-01-03 | OFFSITE NOTIFICATION OF FISH KILL Millstone Unit 3 reported a non spill related environmental fish kill event with greater than 300 fish found in the trash basket. The cause of the fish kill is unknown at this time. The type of fish reported was Atlantic Menhaden. The NRC Resident Inspector has been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2016-01-03
51631 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2016-01-01 16:34 | 2016-01-01 17:19 | 2016-01-01 | UNUSUAL EVENT DECLARED DUE TO UNVERIFIED FIRE ALARM IN CONTAINMENT "Unusual Event declared at BVPS [Beaver Valley Power Station] Unit 1 at 1634 EST due to a fire alarm in Containment [which was] unable to be verified extinguished within 15 minutes. Current Containment parameters do not indicate an actual fire." The licensee notified the NRC Resident Inspector and State and local government agencies. Notified DHS SWO, FEMA Ops Center, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA. * * * UPDATE FROM SAMANTHA BALDWIN TO DONALD NORWOOD AT 2057 EST ON 1/1/2015 * * * "At 1655 the fire alarm was reset. "The Unusual Event has been terminated at 2035 EST after a containment entry and visual inspection determined no fire or indications of fire exist." The licensee notified the NRC Resident Inspector and State and local government agencies. Notified R1DO (McKinley), NRR EO (Morris), and IRD MOC (Gott). Notified DHS SWO, FEMA Ops Center, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2016-01-01
51630 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2015-12-31 06:30 | 2015-12-31 13:15 | 2015-12-31 | HIGH PRESSURE COOLANT INJECTION INOPERABLE "On 12/31/15, at approximately 0630 hours [EST], during shift turnover panel walk-downs, a licensed Unit 3 reactor operator identified that the High Pressure Coolant Injection (HPCI) flow controller output indicated a downscale condition. The controller was in automatic with the set point at 5000 gpm, which would typically indicate a controller output value of 100%. HPCI was not in operation and is a standby system. Operations promptly declared the HPCI system inoperable and entered Technical Specification Condition C for HPCI being inoperable. Other standby systems (Reactor Core Isolation Cooling and low pressure emergency core cooling systems) are OPERABLE. "HPCI is a single train system. Therefore, per NUREG-1022, this condition is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system required to mitigate the consequences of a design event. "This condition has been entered into the Corrective Action program (IR 2606215). Maintenance troubleshooting of the flow controller loop has identified a failed component and repair activities are in progress. "The NRC Resident Inspector has been informed of this notification." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-12-31
51629 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-12-22 | 2015-12-31 10:34 | 2015-12-31 | AGREEMENT STATE REPORT - RECOVERED TROXLER DENSITY GAUGE REPORTED STOLEN IN 1998 The following report was received from the Commonwealth of Pennsylvania via facsimile: "On December 22, 2015, the Department [PA Department of Radiation Protection] was notified by Troxler Electronic Laboratories Inc. that a nuclear density gauge was found at a facility in York, Pennsylvania. [The gauge] was initially reportable per 10 CFR 20.2201 (a)(1)(ii) [EN #34669 - dated 8/27/1998]. "On August 21, 1998, McMinn's Asphalt Co., Inc., NRC License No. 37-19659-01, reported that a Troxler density gauge was stolen from their storage area in Petersburg, PA. Local law enforcement was notified, as well as the NRC (NMED Item Number 980902). Seventeen years later, on December 22, 2015, Zech's Towing from York, Pennsylvania called Troxler informing them that while cleaning out a storage shed a gauge was found. Troxler's RSO [Radiation Safety Officer] called the Department and a follow-up call was made to NRC Region 1. It was learned that McMinn's license was purchased by Pennsy Supply, Inc. (NRC License No. 23-2729496) on March 11, 2008. Pennsy Supply currently has an active Pennsylvania license, PA-1252. Gauge information: "Radionuclide: Cs-137 Manufacturer: Troxler Model: 4640-B Serial Number: 1112 Activity: 8.0 mCi (measure date 10/10/1991) "Two PA [Department] inspectors performed a reactive inspection on December 23, 2015, verifying the details of the gauge. All indications are that the gauge has been isolated in storage since close to the time it was reported stolen. Pennsy Supply took possession of the gauge and will add it to their Pennsylvania license." Pennsylvania Event Report ID No: PA 150038 Previous NRC EN #34669, dated 8/27/1998. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2016-01-08
51628 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-11-06 08:15 | 2015-12-30 13:16 | 2015-12-30 | INVALID ACTUATION OF AN EMERGENCY DIESEL GENERATOR "This 60-day telephone notification is being made per the reporting requirements specified by 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to describe an invalid actuation of the Emergency AC electrical power systems, due to invalid start of an emergency diesel generator (EDG). "On November 6, 2015, at 0815 [CST], EDG A received a fast start signal inadvertently. Maintenance Fix-It-Now (FIN) personnel, working in the vicinity of the relay panel, made incidental contact with one of the relays in the Diesel Generator Logic Relay Panel which initiated the engine start. The engine started and obtained rated speed and voltage in single unit mode. This was not a valid initiation of EDG A. "Operations personnel responded to the EDG actuation by ensuring that the engine was shut down and placed in standby condition in accordance to plant operating instructions. "The plant conditions at the time of the EDG A initiation would not have actuated the EDG; therefore, the actuation of EDG A was invalid. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program (CAP) as Condition Report (CR) 1101730. "The NRC Resident Inspector was notified of this event." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-12-30
51627 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2014-07-01 | 2015-12-29 16:37 | 2015-12-29 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following was received from the State of Nebraska via facsimile: "During the annual inventory certification cycle for Pacific Ethanol Aurora West, the licensee discovered two missing tritium signs. These signs were originally shipped March 3, 2011 with 11.5 curies of material. Current approximate activity calculated as of 12/29/2015 is 8.77 curies. Pacific Ethanol Aurora West shut down for an estimated 18 months between 2012 and 2014. It is assumed these signs went missing at this time." The missing exit signs are Isolite SLX-60 with serial numbers 435489 and 435495. Item number: NE150003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2016-01-06
51626 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-12-29 08:00 | 2015-12-29 13:36 | 2020-09-28 | <br><br>EN Revision Imported Date : 9/29/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following report was received from the State of Florida via email: "At approximately 0800 [EST], a construction 'con-x box' was found with a padlock and chain cut off. The Troxler Gauge Model No. 3440, Ser. No. 70830 was found missing. The incident was immediately reported to [the licensee Radiation Safety Officer], who reported the incident to BRC [Bureau of Radiation Control]. [The licensee Radiation Safety Officer] reported the theft to law enforcement." The gauge contains 8 mCi of Cs-137 and 40 mCi of Am-241/Be. * * * UPDATE ON 09/28/2020 AT 1834 EDT FROM MATTHEW SENISON TO JEFFREY WHITED * * * The following is a summary of an email received from the State of Florida: The Bureau of Radiation Protection (BRP) was notified on September 28, 2020, that the gauge was listed for sale on Ebay on September 23, 2020 from Hialeah, FL, and is still listed. BRP contacted the Hialeah Police Department. Notified R1DO (Arner), NMSS Events Notification, and ILTAB via email. Incident Number: FL15-135 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2016-01-06
51625 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-12-28 16:45 | 2015-12-28 22:57 | 2015-12-28 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO FUNCTIONALITY OF TECHNICAL SUPPORT CENTER VENTILATION "This is a non-emergency eight hour notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality of technical support center [TSC] ventilation system was discovered on December 28, 2015, at 1645 [EST]. The issue could result in higher temperatures than normal for a working environment. "If an emergency is declared requiring TSC activation, the TSC will be staffed and activated using existing emergency planning procedures. Relocation will be considered based upon temperature and radiological conditions. Repairs will be prioritized, but a firm schedule for resolution is not available at this time. "This condition does not affect the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-12-28
51624 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-10-29 11:12 | 2015-12-28 08:38 | 2015-12-28 | INVALID ACTUATION OF UNIT 2 2C SAFEGUARDS EQUIPMENT CABINET "This is to report the Salem Unit 2, 2C Safeguards Equipment Cabinet (SEC) actuation due to an invalid signal. "This report is being made per paragraphs 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to address the invalid actuation of the 2C SEC on October 29, 2015, during performance of maintenance on the Solid State Protection System (SSPS). "Plant conditions: Salem Unit 2 was in Mode 6 at the time of the invalid actuation. "On October 29, 2015, at approximately 1112 [EDT] during performance of maintenance to replace slave relays in the SSPS output test panel 131, the maintenance technician inadvertently made contact with the relay plunger for the 2C SEC. This caused a signal to be sent to the 2C SEC which actuated the equipment associated with it. "The 2C SEC train responded to the signal as required. The equipment associated with the 2C SEC that was not previously removed from service for outage related activities or already in service responded as required. "As a result of the actuation, the 2C Emergency Diesel Generator (EDG) started but did not load (no undervoltage condition existed on the associated vital bus requiring loading), the Unit 2 Emergency Control Air Compressor (ECAC) started. The 22 Charging Pump (CVC) started, and the 22 Safety Injection Pump (SI) started (the Sl pump did not inject as it was isolated and in the process of being tagged out of service at the time of the invalid signal). "The cause of the invalid actuation signal was a human performance error." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-12-28
51623 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2015-12-21 | 2015-12-24 10:37 | 2015-12-24 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL IDENTIFIED AT WASTE RECYCLING FACILITY The following report was received from the State of Arizona via email: "On December 21, 2015, the Agency [Arizona Radiation Regulator Agency] received a telephone call from SA Recycling that they had identified a waste load that contained low levels of radioactive material. The Agency responded on December 22, 2015, and was positively able to identify a pig containing a Cesium 137 waste from the licensee. The average reading on the pig was 5 mR/hr on contact using a Thermo Interceptor. No other sources were identified. The source appears to be an Amdel Model AM213, SN Z-591 contained in an Amdel Model CSA device. The source contains 3.47 mCi of Cesium-137, as of April 1, 1994. "Several issues are under investigation regarding how and when the radioactive material got into the scrap. "The Agency continues to investigate the event." Arizona State First Notice: 15-026 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2016-01-01
51622 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2015-12-23 | 2015-12-23 15:08 | 2015-12-23 | AGREEMENT STATE REPORT - PANORAMIC RESEARCH IRRADIATOR EMERGENCY RETURN CABLE BROKEN The following information was received from the State of Maryland via email: "This afternoon [12/23/15] the emergency return cable for the source rack became crimped and the normal movement of the cable was stopped resulting in most of the emergency cable bunching up in the bottom of the source pool. The source rack was not raised during this occurrence and remains fully shielded at the bottom of the pool. College Park does not intend to use the irradiator until they fix/replace the emergency return cable. "The plan is to wait until after the holidays and put the sources in the storage rack currently located at the bottom of the pool. Once the main rack is empty they will use their established procedures to raise the rack and repair/replace the emergency return cable. It was confirmed that there was no potential for damage to the sources from the emergency return cable hang-up. It was stated that the failure of the emergency return cable could not have resulted in a hung up source rack. It was stated that the repair of the system would not have any potential for additional occupational exposure to employees or would put the sources in any kind of jeopardy. "The licensee will prepare, by next week, a report that will be sent by email to [the State] defining the incident, the methodology of repair ,and ultimately what caused the failure/crimping of the emergency return cable. Note: Due to the previous incident 1.5 years ago, when source rack hung up, the emergency return cable was replaced at that time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2015-12-31
51621 | 0 | HOMEWOOD PRODUCTS CORPORATION |  |  |  |  | 2015-12-21 | 2015-12-23 11:15 | 2015-12-23 | PART 21 REPORT - ERROR IN REPORTING THE VARIABILITY IN THE DOSE DELIVERED ON CERTIFICATE OF PROCESSING The following information was received from Homewood Products Corporation via fax: "Steris Isomedix Services measuring and test equipment used by NTS (Formerly Wyle Laboratories, Inc.) to determine the applied radiation dose did not account for all of the uncertainties involved, and therefore the actual radiation dose applied to components and reported to Homewood Products Corporation by Wyle Laboratories, could be less than the requested service condition dose." The following information was received from Homewood Products Corporation as provided to them by National Technical Services, Inc. (formerly Wyle Laboratories, Inc.): "The defect is an error in reporting the variability in the dose delivered or lack thereof on the lsomedix Certificate of Processing for the Whippany, NJ facility. The U.S. Nuclear Regulatory Commission (NRC) under 10 CFR Part 50, Appendix B issued a Notice of Nonconformance 99901145/2014-201-01 to Steris stating that the measuring and testing equipment used to determine the applied radiation dose reported on the lsomedix Certificate of Processing provided with each gamma irradiation run did not account for all the uncertainties involved (i.e. density of unrelated products in carriers, off-carrier locations within the irradiator, and Cobalt-60 source decay) and therefore the actual radiation dose applied to components could be less than requested as reported on the Certificate of Processing. "Steris lsomedix Services completed an evaluation of the dose rate variability of items processed in off-carrier locations in the irradiator. Steris Isomedix Services Position Paper dated 4/27/15 states the overall variability (uncertainty) associated with gamma radiation exposures at their Whippany, NJ facility." The affected facilities have been notified of the non-conformance. They are: Homewood Products Corporation, Pittsburgh, PA Homewood Energy Services, Pittsburgh, PA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-12-23
51620 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-12-22 13:30 | 2015-12-23 11:43 | 2015-12-23 | FITNESS FOR DUTY REPORT - DISCOVERY OF A PROHIBITED ITEM IN THE PROTECTED AREA The licensee discovered prohibited material inside the protected area. The material has been removed. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2015-12-23
51619 | 0 | MPR ASSOCIATES, INC. |  |  |  |  | 2015-10-08 | 2015-12-23 10:25 | 2015-12-23 | PART 21 REPORT - MPR EMERGENCY DIESEL ENGINE TIMING MODULE FAILURE The following is excerpted from a report submitted by MPR Associates, INC.: "The basic component that contains a defect is an MPR Model 0380-1103 Timing Module. Six modules are in use for the three Emergency Diesel Generators (EDGs) at Plant Hatch Unit 2. Eight modules are at Plant Hatch as spares. The modules use a field programmable gate array (FPGA) to implement a specific pre-programmed load shedding and load sequencing logic associated with the standby power source safety function of the Hatch Unit 2 EDGs. "MPR Timing Module Part Number 0380-1103, Serial Number 16 failed after operating successfully, along with five other installed modules, for more than eight months. The module failure resulted from a capacitor short in the input power circuit. When the capacitor shorted, the module ceased to function and annunciated its failure in the Main Control Room. The other five installed modules have given no indication of failure to date. "MPR identified a replacement capacitor model that is suitable for the application and the application is within the manufacturer's recommendations. MPR is working with Plant Hatch to develop a schedule for rework to restore the expected design life of the timing modules." Contact the following for additional information: Paul Damerell, Principal Officer MPR Associates, Inc. 320 King Street Alexandria, VA 22314 Ph: 703-519-0269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-12-23
51618 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-12-21 | 2015-12-22 19:27 | 2015-12-22 | CALIFORNIA AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was obtained from the State of California via email: "On December 21, 2015, [the] RSO of Standard Soil Geotech, Inc. contacted the Radiologic Health Branch (RHB), Brea Office, to report a gauge (CPN MC-3 S/N M39129253, 10 mCi Cs-137, 50 mCi Am:Be-241) had been run over at the Southern California Edison facility in Porter Ranch in a section that was undergoing construction. The RSO stated that [the] casing of the gauge was damaged by a bulldozer and the Cs-137 source was in the extended position. The RSO confirmed that construction personnel were told to leave the area where the incident occurred. The only path to the incident site was secured by a construction vehicle. The RSO then left his office to assess the scene. After arriving at the scene [at approximately] 7:45 p.m. [PST], the RSO [was] provided photographs that indicated the Am:Be-241 source had detached from the casing and the Cs-137 source appeared to be exposed and not able to be returned to the shielded position. The RSO was asked if he had contacted the fire department and they confirmed that he had not. The RSO was informed that an RHB inspector would go to the scene and assist in removing the radioactive sources from the site. "After the RHB inspector arrived at the site [at approximately] 10:15 p.m., the damage to the gauge was assessed and it was determined that the Am:Be-241 source was not damaged but was detached from the gauge body. The Cs-137 source was also intact, but was still in the extended positon with the opposite end of the source rod broken off at top of the shield, preventing the source from being retracted into the shielded position. After the two parts containing the sources were moved away from the rest of the gauge parts, a survey was performed, using a Victoreen 451B-DE-SI. The dose rate of the remaining parts was found to be background (0.01 mR/hr) and the parts were placed in a plastic bag and removed from the site. The two sources were then placed in the transportation case and a small lead pig was taped to the Cs-137 source to reduce the radiation levels. The box was then closed and locked. A survey of the transport case found the highest dose on contact was 17 mR/hr. The gauge was then secured in [the RSO's] vehicle. Due to the damage to the gauge and the dose rates approaching the maximum allowable for a Type A package, DOT Special Permit 110646, CA-CA-15-99 was issued to allow the RSO to transport the gauge to secure storage at the Standard Soil Geotechnical facility until disposal can be arranged." California Report No.: 5010-122115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-12-30
51617 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2015-12-21 19:55 | 2015-12-21 22:44 | 2015-12-21 | LOSS OF TONE ALERT RADIO SYSTEM TOWER "At 1955 CST on 12/21/2015, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in the event of an emergency condition. This is considered to be a major loss of the public prompt notification system capability and is reportable under 10CFR50.72(b)(3)(xiii). "At 2017 CST, Nemaha, Richardson and Atchison county authorities within the 10 mile EPZ were notified of the condition and the effect on the tone alert radios and will utilize local route notification (backup notification method) making this condition reportable under 10CFR50.72(b)(2)(xi) for notification of other government agencies. "Estimated return to service time is unknown. The cause of the failure is a loss of communication with the tower. "The NRC Senior Resident Inspector has been notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2015-12-21
51616 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-12-21 16:25 | 2015-12-21 22:12 | 2016-01-14 | UNANALYZED CONDITION DUE TO NON-COMPLIANT FIRE PROTECTION MANUAL OPERATOR ACTIONS "As part of the License Amendment development to transition to NFPA 805, PINGP [Prairie Island Nuclear Generating Plant] Calculation ENG-ME-353, Mechanical MOV [Motor Operated Valve] Analysis to support IN-92-18 Response, revision 1, issued in 1998, was reviewed for applicability for the transition to NFPA 805. Recent consultation with an MOV engineer regarding the scope of the revision indicated ENG-ME-353 is out of date. "On 12/21/2015, during technical review for a new weak link calculation, several MOVs were identified from the list of MOVs that are credited to be manually operated from outside the control room in the event of a fire in the control room or relay room per PINGP Procedure F5 Appendix B, Control Room Evacuation (Fire), that could be damaged if hot shorts were to bypass the torque and limit switches. There are also four other motor valves associated with the Gland Steam system of both Unit 1 and Unit 2 that were added to the procedure F5 Appendix B, Control Room Evacuation (Fire), that have not been analyzed for a weak link. This unanalyzed condition could impact the ability of plant operators to implement procedure F5 Appendix B, Control Room Evacuation (Fire). "New hourly fire watch impairments were created for Fire Area 13 (Control Room) and Fire Area 18 (Relay and Cable Spreading Room) as compensatory measures. "Therefore, this is an unanalyzed condition reportable under 10 CFR 50.72(b)(3)(ii)(B). "The public health and safety is not impacted. "The NRC Resident Inspector has been notified." * * * UPDATE AT 0107 EST ON 01/14/16 FROM NATHAN BIBUS TO DANIEL MILLS * * * "Reviews of the list of MOVs susceptible to hot shorts bypassing the torque and limit switches credited to be manually operated from outside the control room in the event of a fire have continued. Additional valves have been noted to be affected by this failure mechanism in areas outside of the Control Room or Relay Room. The additional MOVs affected by this unanalyzed condition could impact the ability of plant operators to implement PINGP Procedure F5 Appendix D, Impact of Fire Outside Control/Relay Room. "As a compensatory measure, additional hourly fire watch impairments were created for the following fire areas: Fire Area 031 ( A Train Hot Shutdown Panel & Air Compressor/Aux 695 Feedwater Room) Fire Area 032 ( B Train Hot Shutdown Panel & Air Compressor/Aux 695 Feedwater Room) Fire Area 058 (Aux Building Ground Floor Unit 1) Fire Area 073 (Auxiliary Building Ground Floor Unit 2) "The public health and safety is not impacted. "The [NRC] Resident Inspector has been notified." Notified R3DO (Duncan). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-12-21
51615 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-12-21 15:33 | 2015-12-21 18:06 | 2015-12-21 | MANUAL REACTOR TRIP DUE TO FEEDWATER ISOLATION "At 1519 [CST], the Main Turbine was tripped due to an Oscillating Governor Valve 2 (cause not known). At 1533, Unit 1 was manually tripped due to a feedwater isolation P-14 [caused by steam generator swell induced high steam generator level, resulting in] steam generator low level [after the isolation]. Aux feedwater actuated as designed. "All Control and Shutdown Rods fully inserted. "Intermediate Range NI 36 failed above P-10 so SR-Nis [source range nuclear instruments] were manually energized. "No primary relief valves lifted. "All Steam Generator PORVs [power operated relief valves] opened. "There were no electrical bus problems. "Normal operating temperature and pressure (NOT/NOP) is 567F and 2235 psig. "There were no significant TS LCOs [Technical Specification limiting conditions for operations] entered. "This event was not significant to the health and safety of the public based on all safety systems performed as designed." Unit 2 was not affected and continues to operate at 100% power. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 48 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-12-21
51614 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-12-19 07:02 | 2015-12-19 10:38 | 2015-12-19 | AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "At 0702 EST on 12/19/2015, the Unit 2 reactor automatically scrammed on a valid reactor low level signal (12.5 inches). The reactor low level signal was caused by the trip of the in-service 2A Reactor Feedwater Pump, causing reactor level to lower, exceeding the low reactor level setpoint of 12.5 inches. "The shutdown was normal. The plant is stable in Hot Shutdown with normal reactor level, pressure control via the Main Steam Bypass Valves to the Main Condenser and normal level control using the Condensate System. "High level trip of the 2A Reactor Feedwater Pump was caused by high reactor level of +54 inches following opening of bypass valves during reactor start-up and pressurization. The cause is still being investigated." All systems functioned as expected following the reactor scram. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 6 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-12-19
51613 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-12-18 17:22 | 2015-12-19 00:44 | 2015-12-19 | BOTH TRAINS OF CONTAINMENT ATMOSPHERE DILUTION SYSTEM INOPERABLE "On December 18, 2015 at 1722 EST, with James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100 percent power, JAF received a notification pursuit to 10 CFR 21.21(d)(3)(ii) related to Moore Industries RTD temperature transmitters. Specifically, wire insulation in T2 transformer was damaged during assembly which reduced the insulation resistance and dielectric breakdown between the windings of the transformer. This equipment is in both redundant trains (A and B) of the Containment Atmosphere Dilution (CAD) System. "Preliminary review by Operations and Engineering, which was completed on 12/18/15 at 2100 EST, determined the Part 21 results in both trains of CAD being inoperable and the applicable Technical Specification (TS) for both redundant trains of CAD being inoperable was entered. "Per TS 3.6.3.2 Condition B, this places the unit in a 7-day shutdown LCO, provided the hydrogen control function is maintained. Per the TS Bases, the alternate hydrogen control capabilities are provided by the Primary Containment lnerting System, which is unaffected. "The event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(D), as an event or condition that could prevent fulfillment of a safety function." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-12-19
51612 | 0 | NUTHERM INTERNATIONAL, INC |  |  |  |  | 2015-12-18 | 2015-12-18 16:41 | 2015-12-18 | POTENTIAL PART 21 INVOLVING RTD TRANSMITTER The following is excerpted from a report submitted by Nutherm International, Inc.: "The wire insulation in T2 transformer on the Moores Industry RTD transmitter, Part Number: RBT/3W20-40/4-20MA/117AC/-EZ84.06-LNP-VTD [EX] was damaged during assembly. This damage reduced the insulation resistance and dielectric breakdown between the windings of the transformer. This resulted in early, catastrophic failure of the RTD transmitter. "It has been determined that no visual inspection of the transformer or testing after the transformer is installed will discover this defect. This defect can only be found by performing testing on the transformer prior to installation." Two of these transmitters were sent to Entergy Operations - Fitzpatrick. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-12-18
51611 | 0 | QUALTECH NP |  |  |  |  | 2015-10-06 | 2015-12-18 15:50 | 2019-02-08 | POTENTIAL PART 21 INVOLVING A200 SERIES STARTERS The following is excerpted from a report submitted by QualTech NP, Nuclear Division, Curtiss-Wright Corporation: "Pacific Gas and Electric (PG&E) reported to QTNP [QualTech NP] that they have had eight Cutler Hammer A200 series starter failures since September 15, 2008. The failures would remain in the operated/energized contact state with power removed for some period of time. All starters impacted with this failure were continuously energized. The concern was that if tripped, that the main contacts would not open to protect the motor. "Testing was performed by Eaton Industrial Controls Division after receiving defective samples from PG&E. The test report from Eaton was received by QTNP for further review and evaluation. On October 6, 2015 QTNP determined that the Cutler Hammer A200 series starter failures may be reportable and an extent of condition review needed to be done. "The root cause was a silicon based mold release that remained on the molded parts and would come between the moving (magnet) & fixed armatures. When heated for an extended period of time, this material would become sticky causing anywhere from a minor delay in opening, up to a frozen closed condition. "Cutler Hammer has determined that the silicone mold release was first introduced into the manufacturing facility in May, 2008, due to a shortage of the Zinc Stearate Mold release that was traditionally used. The silicon based mold release was periodically used until October 2012. According to Cutler Hammer, anything made after January 1, 2013 should definitely be silicon mold release free. "Thus any starters/contactors of the CH A200 series manufactured between May 2008 & December 31 , 2012 could have this concern. This failure has only been reported for continuously energized applications. The end user should evaluate their applications for this potential failure mechanism." QTNP has notified North Anna, H. B. Robinson, Diablo Canyon, and Hatch. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-12-18
51610 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-12-17 15:15 | 2015-12-18 13:23 | 2015-12-18 | AGREEMENT STATE REPORT - LEAKING RADIOGRAPHY SOURCE The following report was received from the State of Louisiana via email: "The RSO and crew were performing routine maintenance and leak test on industrial radiography equipment on 12/11/2015. The leak test wipes were delivered to their service company NDT Repair (LA-6631-L01) for analysis on 12/14/2015. On 12/17/2015, the RSO received a call from NDT Repair to inform him one of the leak tests came back with slightly elevated results of 0.006 microCi Ir-192. Acceptable limit is 0.005 microCi. "The source is being transferred for disposal to SPEC [Source Production & Equipment Company], LA-2966-L01, Mfg. & Service Company in St. Rose, LA (New Orleans, LA). Also, the exposure device and associated equipment are being evaluated for breakthrough and removable contamination before re-sourcing and putting them back into service. "Exposure Device SPEC 150, s/n 991 and the 'leaking source' a SPEC Model G-60, s/n WD 2405 with approximately 19 Ci Ir-192." State Event Report ID No.: LA 150022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-12-28
51609 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-12-17 13:18 | 2015-12-17 14:33 | 2015-12-17 | UNUSUAL EVENT DECLARED DUE TO FIRE ALARM IN CONTAINMENT NOT VERIFIED WITHIN 15 MINUTES "Unusual Event HU2.1 declared at 1318 [CST]. A fire alarm was received in unit 2 containment at 1307 [CST]. Due to the location of the alarm, personnel were unable to verify the status within 15 minutes. At 1343 [CST], the fire alarm in containment cleared. This alarm came in shortly after a unit 2 reactor trip. The reactor trip was due to a turbine trip. Decay heat removal is via forced circulation with aux feed and steam dumps providing secondary cooling. Offsite power remains available." The reactor trip was uncomplicated and all control rods inserted. 25B feedwater heater relief valve lifted and has reseated. No offsite assistance was requested. The licensee has notified the NRC Resident Inspector. State and local authorities were notified. * * * UPDATE ON 12/17/2015 AT 1734 EST FROM TOM HOLT TO DONG PARK * * * "The licensee terminated the NOUE [Notification of Unusual Event] at 1450 CST. The basis for the termination was determination that there was no smoke or fire in the Unit 2 containment observed during containment entry. "NRC Resident Inspectors were notified. State and local governments were notified. The health and safety of the public was not at risk." Notified the R3DO (Valos), NRR EO (Morris), IRD (Grant), DHS SWO, FEMA Ops enter, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2015-12-17
51608 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-12-11 17:38 | 2015-12-15 17:16 | 2015-12-15 | AGREEMENT STATE REPORT - UNATTENDED RADIOGRAPHIC EXPOSURE DEVICE The following report was received from the State of Ohio via email: "On 12-11-2015, at 1738 EST, a radiographic exposure device was left unattended by licensee personnel and found by a customer's employee. "Licensee's investigation indicated that their crew had performed 2 exposures at 2 minutes and 30 seconds on each exposure. Customer operations wanted to get their nuclear gauges back online as soon as possible so when the last exposure was complete the radiographer sent the assistant to let [the Customer] operations know they were complete. The radiographer then broke down everything and picked up the assistant [radiographer] at the ops building. They then drove back to the trailer where the radiographer went to the smoking area and the assistant went to the restroom. When the assistant came out they both went to back of the vehicle to grab film and they realized that the source was not in the vehicle. They immediately drove back to the area. "While enroute back to the location of the radiography work they received a phone call from the customer's project manager that an employee had located an unattended exposure device. When the crew arrived, they determined the device was in the same place where they left it and the device was locked. Estimated time that the device was unsecured was 15 minutes. They surveyed the device, secured the device in the vehicle, and went back to the trailer. The licensee left a voice mail at ODH [Ohio Department of Health] at 1819 EST describing the situation. "There was an immediate safety stand down put in place and no further exposures were to be made. On Saturday morning, 12/15/15, there was a conference call made at 0706 EST to the licensee's crews that were working. The crew that was involved in the incident were suspended from any radiographic work until a full investigation was made. "On 12-14-2015, the [licensee's] RSO [Radiation Safety Officer] conducted a site visit and there was another safety meeting held with all crews on site. "The exposure device was an 880 Delta made by QSA, the device contained 33.2 curies of IR-192, the source was made by QSA, model number 424-9. "A more detailed report is expected from the licensee." Ohio State NMED Report: OH150013 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-12-23
51607 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2015-12-15 05:44 | 2015-12-15 10:24 | 2015-12-15 | MANUAL REACTOR TRIP DUE TO LOSS OF FEED TO ONE STEAM GENERATOR "This is a 4-hour Non-Emergency 10 CFR 50.72(b)(2)(iv)(B) notification due to a Reactor Protection System (RPS) actuation. Arkansas Nuclear One, Unit 1, was manually tripped from 43 percent power at 0544 CST. The reactor was manually tripped due to operator judgement during control issues with the Integrated Control System (ICS) during a planned downpower for Electro-Hydraulic Control (EHC) system maintenance. CV-2672 B, low load control valve, failed to close. Subsequently, CV-2674 B, low load block valve, began to close and caused a loss of feed to E-24B Steam Generator. "No additional equipment issues were noted. All control rods fully inserted. Emergency Feedwater (EFW) actuated and was utilized to maintain Steam Generator (SG) levels. This [EFW actuation] meets the 8 hour Non-Emergency Immediate Notification Criteria [(10CFR50.72(b)(3)(iv)(A)]. No Primary safety valves lifted. Main Steam Safety Valves (MSSVs) did lift initially after the trip. "The NRC Resident [Inspector] has been notified." Decay heat is being removed via the steam dump valves to the main condenser. Unit 1 is in a normal shutdown electrical lineup. Unit 2 was not affected by the transient on Unit 1. The licensee notified the State of Arkansas. | 0 | 0 | 0 | 43 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2015-12-15
51606 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-12-14 19:06 | 2015-12-14 19:49 | 2015-12-14 | AUTOMATIC REACTOR TRIP DUE TO MAIN GENERATOR LOCKOUT "At 1906 [EST] on 12/14/2015, Indian Point Unit 3 received a Main Generator Lockout trip signal, and the reactor automatically tripped. Site personnel reported seeing arcing on a 345kV output transmission line tower. At the time of the trip, there was moderate rain and fog in the area. The site fire brigade leader investigated the reports of arcing and found no evidence of fire; fire brigade response was not required. "All automatic systems functioned as designed and all control rods inserted automatically. Auxiliary Feedwater Pumps started automatically due to expected low steam generator levels following a reactor trip from 100% power. Unit 3 is being maintained in Mode 3 with decay heat removal via steam dumps to the condenser. Offsite power remains available and in service from 138kV to the 480V safeguards buses. The cause of the Main Generator Lockout signal is being investigated. "Unit 2 was not impacted and continues to operate at 100% power. "The NRC Resident Inspector has been notified." After the trip, operators observed high vibrations on the 33 reactor coolant pump which eventually returned to normal range. The licensee will be notifying the New York Public Service Commission and their local Independent System Operator. A press release will be issued by the Communications Department. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-12-14
51605 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-12-14 | 2015-12-14 15:14 | 2015-12-14 | AGREEMENT STATE REPORT - FIXED GAUGE WITH SHUTTER STUCK IN THE OPEN POSITION The following report was received from the State of Texas via email: "On December 14, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer [RSO] that while performing routine test of gauge shutters they found a gauge where the shutter failed to operate. The gauge is located on a polyurethane tank/vessel. The gauge is an Ohmart Vega model SHF2 containing source serial number 9754GK of 200 millicurie cesium - 137. The shutter was left in the normal operating, unshielded position [open]. The source does not pose any additional risk of exposure to the workers or members of the general public. The RSO stated they have called TechStar to repair the gauge within the next few days." Texas Report #: I 9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-12-22
51604 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2015-10-21 00:29 | 2015-12-14 14:32 | 2015-12-14 | DIESEL GENERATOR START DUE TO INVALID SIGNAL "This report is being made per paragraphs 50.73(a)(1) and 50.73(a)(2)(iv)(A) to address an actuation of Emergency Diesel Generator 'A' on October 21, 2015, during the performance of a Diesel Generator Load and Safeguard Sequence Test. The Emergency AC Electrical Power system, including Diesel Generators is a system named in 50.73(a)(2)(iv)(B). "During the performance of the Diesel Generator Load and Safeguard Sequence Test restoration steps a human performance error, while taking resistance readings on a relay, resulted in the unintentional start of the 'A' Emergency Diesel Generator. The testing was aborted and the affected Diesel Generator was restored to standby service in accordance with plant procedures. This is defined as an 'invalid signal' in that the 'A' Diesel Generator did not start as the result of an actual initiating condition. "The start signal is considered an INVALID signal with respect to 50.73(a)(2)(iv)(A), however the system was not fully removed from service. The 'B' train was not affected by this event. The actuation signal was considered complete since all necessary components responded as would have been expected if there had been a valid signal. "The NRC Resident Inspector was notified." The licensee has determined that shorter test probe tips, when taking resistance readings, are necessary to prevent reoccurrence of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-12-14
51603 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2015-12-14 09:04 | 2015-12-14 13:10 | 2015-12-14 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR TESTED POSITIVE DURING FOR CAUSE TESTING A non-licensed supervisor tested positive for alcohol during a for-cause fitness-for-duty test. The individual's access to the facility has been denied. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2015-12-14
51602 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-12-14 10:11 | 2015-12-14 12:30 | 2015-12-14 | FITNESS FOR DUTY REPORT - NON-LICENSED SUPERVISOR TEST POSITIVE FOR ILLEGAL SUBSTANCES A non-licensed supervisor tested positive for drugs on a random fitness-for-duty test. The individual's access to the facility has been terminated. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2015-12-14
51601 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-12-13 03:07 | 2015-12-13 10:41 | 2015-12-14 | ESSENTIAL SERVICES CHILLED WATER SYSTEM INOPERABLE "This is a non-emergency eight hour notification for a condition that could have prevented fulfillment of a safety function in a system needed to remove decay heat and to mitigate the consequences of an accident. "At approximately 0307 EST on December 13, 2015, the 'A' and 'B' trains of the essential services chilled water (ESCW) system were inoperable for a time period of 23 minutes. The 'B' train of the ESCW system was being tested at the time that the 'A' train of the ESCW system became inoperable. The 'B' train of the ESCW system was returned to operable status at approximately 0330 EST and remains operable. "The ESCW system provides cooling support functions to remove decay heat and mitigate the consequences of an accident. There were no safety system actuations during this time period and the plant is stable. "This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." The 'A' ESCW pump tripped on low lube oil pressure. * * * RETRACTION FROM JOHN CAVES TO JOHN SHOEMAKER AT 1756 EST ON 12/14/15 * * * "Upon further review of the condition, it was determined that the 'A' train of the ESCW system was capable of performing its safety function throughout the time period previously reported, and the 'A' train of the ESCW system was operable. Therefore, there was no loss of safety function. Event notification 51601 is retracted. The NRC Resident Inspector has been informed of this notification retraction." Notified the R2DO (Guthrie). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-12-13
51600 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-12-11 04:16 | 2015-12-11 11:28 | 2015-12-11 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "At 0416 [CST] on 12-11-2015, River Bend Station declared the High Pressure Core Spray system INOPERABLE in accordance with Technical Specification 3.8.9, Condition E (Declare High Pressure Core Spray System and Standby Service Water System Pump 2C inoperable immediately) due to Division 2 Control Room Air Conditioning System HVK-CHL1D tripping off because of high inboard bearing temperature of 180 deg F. "Actions taken to exit LCO: Alternated divisions of Control Room Air Conditioning System to Division 1 HVK-CHL1C in service and Division 2 HVK-CHL1B in standby and exited LCO at 0439." The licensee has notified the NRC Resident Inspector. | 83 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-12-11
51599 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-08-03 15:30 | 2015-12-11 02:30 | 2015-12-11 | OFFSITE NOTIFICATION FOR CONDENSATE SPILL IN THE TURBINE BUILDING "On August 1, 2015, during tagging activities to support planned maintenance on a condensate demineralizer, operators incorrectly positioned certain air-operated components which, combined with apparent leakage past a solenoid valve, resulted in a drain opening on a demineralizer that was in service. Flow through the drain line caused a turbine building sump to overflow to the floor of the 67 foot elevation of the Turbine Building. Immediate actions were taken to stop the leak. "The spill volume was approximately 60,000 gallons of condensate. The tritium activity of the water is estimated at 1.32E-2 microCi/ml. Gamma activity was from noble gases only in a concentration of approximately 2.30E-6 microCi/ml. The spill was confined to the Turbine Building. The affected area contains degraded floor seals which might allow the spill to reach groundwater. "The reason for this notification is that industry and governmental officials were notified of this event on August 3, 2015. The NRC Senior Resident Inspector was notified and informal notification was made to the NRC Region IV office, the Louisiana Department of Environmental Quality, and West Feliciana Parish government authorities. The Nuclear Energy Institute was informed as specified in their ground water protection initiative. "Plant cleanup activities arising from the spill are complete." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-12-11
51598 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-12-10 08:30 | 2015-12-10 19:43 | 2015-12-10 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the State of Utah via email: "The licensee stopped and parked their truck in Cottonwood Heights, Utah. Licensee personnel stepped away from the truck but left it unlocked and running. An unknown man ran up to the vehicle and stole the truck and its contents. At the time the truck was stolen, a Troxler Moisture Density Gauge containing licensed material was secured in the bed of the licensee's truck in its transportation case with the source rod locked (gauge and source information listed below). The licensee notified the police and has begun actions to recover the gauge (Cottonwood Police Department, Case Number 15x7206). "Troxler Moisture Density Gauge: Gauge Serial Number: 12386 Source Information: CS-137 (8.7 mCi) S/N: 50-0529 Source Information: Am241: BE (40.0 mCi) S/N: 47-7684 "This incident is still being investigated [by the State of Utah]." Utah Event Report ID No.: UT150009 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-12-18
51597 | 0 | TERRACON CONSULTANTS, INC |  |  |  |  | 2015-12-10 12:40 | 2015-12-10 17:40 | 2015-12-10 | DAMAGED MOISTURE DENSITY GAUGE While in use at a remote job site, a Troxler moisture density gauge (Model 3440, Serial Number 37384) was damaged when it was struck by a bulldozer. The source rod was out at the time of the incident but the source was able to be retracted into the shielded position. The licensee surveyed the meter and found no abnormal radiation readings. The gauge was transported back to the licensee facility for storage awaiting results of the swipe test. Once the swipe test results are returned, the licensee intends to ship the gauge to the vendor for repair or replacement. The licensee will provide the model and source information for the gauge once is it obtained. No personnel overexposures occurred during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-12-18
51596 | 0 | DEPARTMENT OF THE ARMY |  |  |  |  | 2015-11-17 | 2015-12-10 11:48 | 2015-12-10 | LOST IODINE-125 SEED "One 180 microCi I-125 seed for breast radioactive seed localization (I-125 RSL) was lost at Brooke Army Medical Center (BAMC) on 17 November 2015. "Loss of the I-125 seed occurred in BAMC Pathology on 17 November 2015 due to lack of training and supervision of new Residents during the removal of the seed while grossing the specimen. Health Physics Service (HPS) was notified and responded to Anatomic Pathology/Histology at approximately 1130 on 20 November. "According to events leading up to the loss, the I-125 seed was not removed from the specimen prior to being submitted for sectioning. Typically, RSL seeds are tracked on a BAMC I-125 Seed Tracking Form, which indicates when the seed is removed from the specimen. In this case, the tracking form was completed only to the point of Pathology receiving the specimen with the seed still within. A radiograph illustrating the seed within the specimen was taken on 16 November 2015 in Mammography and delivered with the specimen to Pathology. Due to a lack of supervision and training, [the Pathology Resident] did not verify on the tracking form that the seed had been removed. The I-125 Seed Tracking Form was found incomplete on 20 November 2015 by the RSO [Radiation Safety Officer], who then contacted [the Pathology Resident] and informed the Health Physics personnel. Health Physics personnel immediately responded and performed a survey of the entire Histology suite focusing on all work stations and processing equipment used in the preparation of this specimen; the seed was not located within the Histology suite. According to [the Pathology Resident], the step to verify seed removal was overlooked, and confirmation of the seed's absence with a radiation probe was skipped. Furthermore, the tissue was grossed and submitted entirely for sectioning. Most likely, the seed stuck to the grid and was disposed of as biohazard waste. The biohazard disposal route from Pathology on the 4th floor to the hospital exit passes through radiation monitors located on the fourth floor and in basement utility rooms and the biohazard waste room, but due to the low activity of one I-125 seed in biohazard bag with unknown amount of material the monitors would not alarm. "Initial activity of the I-125 RSL seed was 300 microCi on 7 October 2015, and had decayed to 180 microCi on 20 November 2015. Assuming no shielding, an exposure rate of 0.03 mR/hr at 1 meter is to be expected. Personnel are not likely to handle the waste for an extended period of time and the waste was likely incinerated at Stericycle. "Steps have been taken since the incident to prevent recurrence. A. Procedure: The grossing staff pathologist will ensure seed disposal via inspection of appropriate paperwork and scanning with appropriate probe rather than verbal assurance. B. Additional training sessions on the use of the NeoProbe and I-125 RSL seed procedure. "Based on accounts above, the I-125 seed was left with the specimen during grossing and was then submitted to sectioning and the seed was lost. In addition to ensuring the proper training and SOPs [Standard Operating Procedures] are in place and followed, we will continue to have radiation monitors in place on each floor and the back loading docks of the facility to make certain there is full accountability of the I-125 seeds." The licensee notified NRC Region 4 (Torres). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-12-18
51595 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-12-09 14:43 | 2015-12-09 22:28 | 2016-01-29 | REACTOR RECIRCULATION LOOP FLOW TRANSMITTERS OUT OF TOLERANCE "During surveillance testing, 2 reactor recirculation loop flow transmitters, which input to the Average Power Range Neutron Monitors (APRM's) associated with the 'A' Reactor Protection Trip System (RPS), were found out of tolerance in the non-conservative direction. "Non-conservative reactor recirculation flow setpoints for all 'A' side APRM's results in a loss of safety function for the APRM Neutron Flux High (Flow Biased) trip function of RPS. "All instruments were adjusted back to within tolerance as allowed by the procedure, restoring the RPS safety function. Extent of condition and instrument drift issues are under evaluation via the corrective action process. "This is an 8 hour reportable event under 10CFR50.72(b)(3)(v)(A) - Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shutdown the reactor and maintain it in a safe shutdown condition. "The NRC Senior Resident Inspector has been notified." * * * RETRACTION ON 1/29/16 AT 1414 EST FROM DUSTIN SCURLOCK TO DONG PARK * * * "On the basis of a subsequent engineering evaluation, which reviewed the uncertainties considered within the setpoint calculations and the sequencing of the transmitter calibrations, it was determined that the APRM channels and Control Rod Block Monitor instrumentation associated with the Neutron Flux High (Flow Biased) function were unaffected by the out of calibration condition. "Technical Specification (TS) Table 3.3.1.1 FUNCTION 2.b requires two (2) APRM Neutron Flux High (Flow Biased) channels per RPS trip system. TS Table 3.3.2.1 FUNCTION 1.a requires two (2) Rod Block Monitor [RBM] Upscale channels. These TS requirements were met upon discovery of this condition. The past-operability of the RPS and RBM instrumentation was unaffected by this condition. In addition, the engineering analysis confirmed that the Neutron Flux High (Flow Biased) allowable values in the Core Operating Limits Report (COLR) and the TRM were not exceeded. "Therefore, there was no loss of safety function, and this condition was not reportable pursuant to 10 CFR 50.72(b)(3)(v)(A), as an event or condition that could have prevented fulfillment of a safety function. FitzPatrick is retracting ENS 51595. "The degraded flow transmitters have been replaced, and the operability determination for the condition has been revised. All RPS and RBM instrumentation remain operable." The NRC Resident Inspector has been notified. Notified R1DO (Bickett). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2015-12-09
51594 | 0 | NASA GODDARD |  |  |  |  | 2015-12-08 12:00 | 2015-12-09 09:05 | 2015-12-09 | IRRADIATOR EQUIPMENT FAILURE "At approximately noon on December 8, 2015, the source located inside the right side of the J. L. Shepherd Model 81-24Q Beam Irradiator didn't move upward from its normal down shielded position to the normal operational position when the operator pressed the button on the operation console. A second attempt was made to have the source be raised to its normal operational position, but the source remained at its normal down shielded position. An emergency shutter built into the system was deployed just as a precaution. Facility Manager notified the Radiation Safety Officer in the Radiation Protection Office (RPO). "Upon entering the room, it was noted that the source position indicator found on the operating tower mounted on the top of the irradiator showed that the source was located at its normal down shielded position in the irradiator. RPO staff conducted a radiation survey surrounding the irradiator and found that all readings were similar to levels noted in previous surveys conducted when the sources in the irradiator were in their shielding position and the highest reading was noted as 1 mR/hr on contact with the irradiator. "Contact was made to J. L. Shepherd and arrangements are being made to have a representative come onsite to conduct an evaluation of the system. Arrangements are being made to have that evaluation be conducted during the week of December 14th and the Radiation Safety Officer has given direction for the irritator to not be used until this evaluation by the manufacture can be conducted." No personnel exposures were reported. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-12-17
51593 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2015-12-07 16:00 | 2015-12-08 15:08 | 2015-12-08 | CRANE ITEM RELIED UPON FOR SAFETY NEVER INSTALLED "During unrelated maintenance, it was discovered that the UUSA UBC crane was missing components that are within the IROFS27e, QL1 boundary. These components have been missing since the crane went into operation in early 2015. The IROFS [Item relied upon for safety] has been declared degraded and is currently inoperable, and in a location where it cannot impact licensed material. "This IROFS is designed to mitigate the consequences of UF6 release, to meet 10 CFR 70.61 performance requirements. No accident occurred, no release occurred. "During the period in which the crane was operating in a degraded state, no design basis accidents occurred, thus there are no actual consequences. The crane had been moved to a safe position in order to perform other repairs (away from licensed material), and it locked in a place, thereby removing applicability of the IROFS. Thus, there is currently no potential for consequences. "During unrelated repair activities, it was discovered that the URENCO USA UBC Crane has been in operations since March of 2015 while in a degraded condition. A component within the IROFS QL1 boundary was never installed. "This is a sole IROFS to mitigate consequences. There are no other IROFS in place to support this function. Currently there is no analysis available to support the ability of the degraded IROFS to perform its safety function. "There were no design basis external events during operation of the crane, nor do any currently exist. "The UBC Crane was already locked out for ongoing corrective maintenance, The lockout remains active, and the IROFS is now declared inoperable. The condition was entered into the USA's Correcting Action Program for Evaluation and Corrective Actions. "The degraded IROFS has been declared inoperable. No accident sequences occurred. "The plant did not enter an emergency classification, nor is one planned. "There are no planned notifications other that this event notification to the NRC Operations Center." The NRC Regional Inspector (Munson) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2015-12-08
51592 | 0 | HOWDEN NORTH AMERICA, INC. |  |  |  |  | 2015-10-16 | 2015-12-08 14:31 | 2015-12-08 | PART 21 REPORT - 2 MOTORS WERE NOT PROPERLY PREPARED BEFORE SMALL STEEL SHOT BLASTING The following information is an excerpt from an Howden North America email: "It was discovered that two motors being prepared for steel shot blasting prior to application of the coating system may not have been properly sealed allowing a small amount of small steel shot blast to enter into the motor." The two motors have been repaired and returned to FPL (Florida Power and Light Company), no further action is required. Customer: Florida Power and Light Company Location/Site: Turkey Point Motor Serial Numbers: GG153620115 and GG153620116 For questions and additional information, contact: J. Todd Gunvalson Director, Quality Howden North America 7909 Parklane Road Columbia, SC 29223 Phone 803-741-2716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-12-08
51591 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-12-04 | 2015-12-07 15:08 | 2015-12-07 | AGREEMENT STATE - TWO GAUGE SHUTTERS FAILED TO CLOSE The following report was provided by the Pennsylvania Department of Environmental Protection via facsimile: "Two separate shutter issues occurred during gauge standardization procedures on December 4, 2015. The shutters failed to close completely. All proper lock out procedures were followed and leak tests and survey data revealed no elevated radiation levels. A service provider has been contacted for repairs. "Gauge #1 Radionuclide: Am-241 Manufacturer: Accu-Ray Source Model#: S-16 Source SN#: AM-109 Device Model: U-3 Device SN#: 6631901 Activity: 1 Ci "Gauge #2 Radionuclide: Am-241 Manufacturer: IRMS Source Model#: S-16 Source SN#: AM-1149 Device Model: TG-2 Device SN#: OOM0397 -15 Activity: 3 Ci "A reactive inspection is planned by the Pennsylvania Department of Environmental Protection. More information will be provided upon receipt." Pennsylvania Event Report ID No: PA150033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-12-15
51590 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-12-04 | 2015-12-07 14:39 | 2015-12-07 | AGREEMENT STATE REPORT - DELIVERED DOSE OF YTTRIUM-90 LESS THAN PRESCRIBED DOSE The following report was received from the Pennsylvania Department of Environmental Protection via facsimile: "On 12/4/2015, a patient was scheduled for a yttrium-90 (Y-90) Sirsphere procedure. The prescribed dose on the written directive was 10 mCi. The ion chamber measurements indicated a delivered dose of 7.72 mCi (-22.8% of prescribed dose). Both the patient and referring physician were notified. No harm is expected to the patient. "A reactive inspection is planned by the Pennsylvania Department of Environmental Protection." Pennsylvania Event Report ID No: PA150032 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-12-15
51589 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-12-07 08:25 | 2015-12-07 14:02 | 2015-12-07 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "On December 07, 2015, at 0825 hours (CST), the Control Room Emergency Ventilation (CREV) system was declared inoperable due to the Air Handling Unit (AHU) tripping upon attempting to swap from the non-safety related CR HVAC. Swapping was being performed to allow maintenance on the non-safety related system. "Technical Specification 3.7.4, Condition A, was entered which requires the CREV system to be restored to an operable status in seven (7) days. Additionally, Technical Specification 3.7.5, Condition A, was entered which requires CREV AC to be restored to an operable status in 30 days. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function,' because the CREV system is a single train system required to mitigate the consequences of an accident." The NRC Resident Inspector was notified. The Licensee notified the Illinois Emergency Management Association. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-12-07
51588 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-12-06 05:46 | 2015-12-06 09:58 | 2015-12-06 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE DUE TO EXHAUST FAN TRIP "On December 06, 2015 at 0546 [EST], Reactor Building Zone 1 Secondary Containment differential pressure lowered to less than 0.25 inch Water Column (WC) [degrading vacuum] when the running Reactor Building Zone 1 exhaust fan tripped. This required a TS 3.6.4.1 entry for failure to meet SR 3.6.4.1.1 on Unit 1 and Unit 2. "The standby fan automatically started, restoring of Reactor Building Zone 1 Secondary Containment differential pressure to greater than -0.25 inch WC. Field operators confirmed proper system response at 0553 [EST] December 06, 2015. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. " The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-12-06
51587 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-12-06 03:50 | 2015-12-06 05:28 | 2015-12-06 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE DUE TO ICING OF INTAKE SUPPLY PLENUM SCREENS "On December 06, 2015 at 0350 [EST], Reactor Building Zone 1 Secondary Containment differential pressure lowered to less than 0.25 inch Water Column (WC) [degrading vacuum] when the intake supply plenum screens were found to be iced over. This required a TS 3.6.4.1 entry for failure to meet SR 3.6.4.1.1 on Unit 1 and Unit 2. "Snow melt heaters were manually started to melt the ice allowing restoration of Reactor Building Zone 1 Secondary Containment differential pressure to greater than 0.25 inch WC at 0434 on December 06, 2015. "This event is being reported under 10 CFR 50.72 (b)(3)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-12-06
51586 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2015-12-05 17:31 | 2015-12-05 18:48 | 2015-12-05 | MANUAL REACTOR TRIP INITIATED DUE TO MULTIPLE DROPPED CONTROL RODS "At 1731 [EST] on December 5, 2015, Indian Point Unit 2 Control Room operators initiated a Manual Reactor Trip due to indications of multiple dropped Control Rods. The initiating event was a smoldering Motor Control Center (MCC) cubicle in the Turbine Building that supplies power to the Rod Control System. The unit is stable in Mode 3 with heat sink provided by Auxiliary Feedwater and decay heat removal is via the steam dumps to the condenser. Offsite Power remains in service. "The smoldering MCC cubicle had power removed from it when 24 MCC breaker tripped on overcurrent. The affected cubicle has ceased smoldering and is being monitored by on-site Fire Brigade trained personnel. The trip of 24 MCC removed power to 22 Battery Charger, 22 DC Bus remained powered from the 22 Battery without interruption, and 22 Battery Charger was subsequently repowered." The cause of the smoldering MCC is being investigated and a post reactor trip evaluation is being conducted by the licensee. There was no impact on Unit 3, which continues to operate at 100% power. The licensee has notified the NRC Resident Inspector and appropriate State and Local authorities. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-12-05
51584 | -1 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-12-03 21:07 | 2015-12-04 01:33 | 2016-01-07 | EXCESSIVE CONTROL ROOM IN-LEAKAGE IDENTIFIED "On December 3, 2015 at 2107 [EST], the Control Room Emergency Ventilation System (CREVS) was declared inoperable due to a higher than allowed identified in-leakage rate for the Control Room Envelope (CRE) when in the Normal Operating Mode. Both Unit 1 & Unit 2 remain at 100 percent power and they share a common CRE. "At the time of discovery, there is a reasonable expectation this condition could prevent the fulfillment of the safety function of a system that is required to mitigate the consequences of an accident, thus satisfying the reporting criteria for 10CFR50.72(b)(3)(v)(D). "Actions to implement mitigating actions were immediately initiated in accordance with Technical Specification 3.7.10. CREVS has been placed in Recirculation Ventilation Mode, isolating the control room from outside air. "The NRC Senior Resident Inspector has been notified of the condition." * * * RETRACTION ON 1/7/16 AT 1110 EST FROM SHAWN SNOOK TO DONG PARK * * * "Following the 8-hour 10CFR50.72 notification made on 12/4/2015 (EN 51584) regarding the Control Room Emergency Ventilation System (CREVS) inoperability, an engineering evaluation determined inleakage did not exceed limits described in the Beaver Valley licensing basis. Therefore, the degraded Control Room Emergency Ventilation System remained Operable with the identified air inleakage as determined by the Control Room Envelope Habitability Program. As such, the safety function was never lost and the event notification is being retracted as it is not reportable pursuant to 10CFR50.72(b)(3)(v)(D). FENOC is planning to repair the degraded components of the system. "The NRC Resident [Inspector] has been notified." Notified R1DO (Dimitriadis). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-12-04
51577 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2015-12-01 18:20 | 2015-12-01 20:25 | 2015-12-01 | MANUAL REACTOR TRIP AFTER STEAM GENERATOR FEED PUMP TRIP "On 12/01/2015 at 1820 EST, the Main Control Room received a 22 Steam Generator Feed Pump trip. The 22 Steam Generator Feed Pump was not able to be reset and the Main Control Room manually tripped the Unit 2 Reactor. The licensee entered Emergency Operating Procedure (EOP)-0, 'Post Trip Immediate Actions' and all safety functions were met. "At 1833, Unit 2 transitioned into EOP-1, 'Uncomplicated Reactor Trip.' At 1841, Unit 2 transitioned into Operating Procedure #4 , 'Plant Shutdown from Power to Hot Stand-by.' "The plant is stable in Mode 3." All control rods inserted fully on the reactor trip. No primary or secondary safety relief valves lifted. The steam generators are being fed by the 21 steam generator feed pump and decay heat is being dumped to the condenser via the steam dumps. The electric plant is in a normal shutdown electrical lineup and there was no impact on Unit 1. Unit 1 continues to operate at 100 percent power. The cause of the 22 steam generator feed pump trip is still under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-12-01
51576 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-12-01 12:45 | 2015-12-01 16:07 | 2015-12-01 | SECONDARY CONTAINMENT INOPERABLE DUE TO REACTOR BUILDING AIRLOCK DOORS BEING OPENED SIMULTANEOUSLY "On December 1, 2015 at 1245 EST, Secondary Containment became inoperable due to the failure to meet a Surveillance Requirement (SR 3.6.4.1.3) on Unit 2. "The inoperability was caused when RB [Reactor Building] airlock doors were inadvertently opened simultaneously. "Secondary Containment was restored December 1, 2015 at 1246 EST when the doors were closed. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022, Rev 3, section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-12-01
51575 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-12-01 12:15 | 2015-12-01 15:35 | 2015-12-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was provided by the State of Colorado via email: "Event date and time: 12-1-2015, 12:15 MST. The exit sign is considered to be lost material and it is unknown what date the sign was removed or abandoned. "Event location: 9351 Willow Court, Henderson, CO "Event type: Lost Exit Sign Model # SLX 60, Serial Number 11-13624, 6.2 Ci, H-3, Shipped from Isolite Corporation on 4/26/2011. "Event description: The onsite manager completed an inspection of the property. No Tritium exit sign was discovered. The exit sign is considered to be lost. The company representative will provide a written policy and procedure to resolve this from happening in the future." Event Report ID No.: CO15-I15-35 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-12-09
51574 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2015-10-12 | 2015-12-01 14:53 | 2015-12-01 | PART 21 REPORT - IMPROPER SILVER PLATING DURING REFUBISHMENT OF AK-25 TYPE CIRCUIT BREAKERS The following information is a synopsis of information received via E-mail: During refurbishment of General Electric AK-25 type circuit breakers (P/N's: AK-2A-25-1, AK-3A-25-1, and AK-7A-25-1) by United Controls International (UCI), non-current carrying/non-copper based components of the upper stud assembly were silver plated. Bubbling of the silver plating was later noted which is an indication that the plating material was not adhering to the base metal. Flaking of the silver plating material may occur and may introduce conductive foreign material into the host circuit breaker. Introduction of this conductive material could create the possibility of a short circuit of the current sensor terminal board for circuit breakers configured with RMS-9 trip units and subsequent failure of the circuit breaker. Fort Calhoun Nuclear Station is the only known recipient of affected breakers. Fort Calhoun received 18 breakers that contained improperly silver plated components. 14 of these 18 circuit breakers have been returned to UCI. Four of the 18 circuit breakers have been installed at Fort Calhoun and UCI is currently awaiting the return of these four circuit breakers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-12-01
51573 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-11-17 | 2015-12-01 10:17 | 2015-12-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received from the State of Colorado via email: "Event Date and Time: 11/17/15. Time is unknown as the current owner took possession of the property after a business had remodeled the interior of the structure. This report is for an exit sign that was disposed of between 2007 to 2012. "Event Type: Lost Exit Sign "Event Description: An exit sign was purchased during the renovation of a church to an office. By Design Homes purchased the property in 2007 and used the property for their offices until the renovation was completed and resold as private residence in 2012. The disposition of the exit [sign] is unknown. By Design Homes was unaware of the exit sign containing Tritium. "Detail: During an audit of the records, a contact was made with one of the investors who worked with By Design Homes. During the discussion, we [Colorado Department of Public Health and Environment (CDPHE)] discovered the transition [of] the property from a church to By Design Homes. They renovated the property [into] a private residence. It is unknown what happened with the exit sign. Speculation is the sign was taken down and disposed of in a dumpster during the renovation from the business to a residence. "The current owner does not have any record of an exit sign being in the home when purchased in 2012. "Our [CDPHE] office made contact with By Design Homes, leaving emails with the investor to relay the incident and to obtain a corrective action report. No further communication has been received at this date." Colorado Event Report ID No.: CO15-I15-34 * * * UPDATE FROM LINDA BARTISH TO DONALD NORWOOD AT 1211 EST ON 12/1/2015 * * * The following information was received via E-mail: "Additional information regarding the exit sign: Model Number is 1091, Serial Number is U1796, Activity is 7.5 Ci of H-3, Manufacturer is Safety Light, Shipped on 7/25/2007." Notified R4DO (Gepford). E-mailed ILTAB (Johnson) and NMSS Events Notification group. * * * UPDATE FROM LINDA BARTISH TO DONALD NORWOOD AT 1438 EST ON 12/1/2015 * * * The following information was received via E-mail: "Correction, the Model Number is 101." Notified R4DO (Gepford). E-mailed ILTAB (Johnson) and NMSS Events Notification group. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-12-09
51572 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-11-30 19:51 | 2015-11-30 23:31 | 2015-12-08 | UNACCOUNTED FOR SPECIAL NUCLEAR MATERIAL "Unable to locate Traversing Incore Probe (TIP) detector that was removed from service. "At 1951 PST on 11/30/2015, it was concluded that an irradiated TIP containing an estimated 0.001 grams of Uranium-235 was unaccounted for. The TIP was previously located in a locked high rad storage area on the 437 foot elevation of the radwaste building. Efforts to locate the TIP are ongoing. There is no reasonable basis that exposure could result to persons in unrestricted areas. Furthermore, there is no evidence of theft or diversion. This event is being reported in accordance with 10CFR74.11." The licensee notified the NRC Resident Inspector * * * RETRACTION FROM NICHOLAS RULLMAN TO JOHN SHOEMAKER AT 1856 EST ON 12/8/15 * * * "Subsequent to the initial report and following a thorough investigation, Energy Northwest has reasonable assurance that the TIP detector was placed in open-top liner 13-068 which was shipped to US Ecology on March 11, 2015. Therefore, this notification is being retracted. "The NRC Senior Resident Inspector has been notified." Notified the R4DO (Hagar) and ILTAB (Grose), IRD MOC (Gott), NRR EO (Morris), NMSS (McIntosh), and NMSS Events Notification via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 74.11(a) |  |  |  | 1 | 2015-12-08
51571 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-11-29 16:00 | 2015-11-29 20:40 | 2015-11-29 | OFFSITE NOTIFICATION DUE TO SMALL OIL SPILL "On November 29, 2015 at approximately 1600 Central Standard Time, it was reported that the oil catch device in place around the Temporary Diesel Generators (TDG) had overflowed due to a combination of accumulated rainwater and failure of one wall of the catch device to float. There is a small oil leak from the TDG. Less than one gallon of oil is estimated to have been spilled. The oil spill has reached the BFN [Brown Ferry Nuclear] forebay (waters of the US) via the station's storm drainage as evidenced by an oil sheen on the water of the forebay. The source of leakage has been contained. "This oil spill is reportable to the EPA (National Response Center) under 40CFR112. Notification to the National Response Center has been made. "Additional notification has been made to Alabama Emergency Management." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-11-29
51570 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2015-11-28 19:12 | 2015-11-28 23:54 | 2015-11-29 | AUTOMATIC REACTOR TRIP DUE TO GENERATOR LOCKOUT AFTER VOLTAGE REGULATOR MALFUNCTION "Unit 1 automatic reactor trip actuated due to an automatic voltage regulator (AVR) malfunction which caused a generator lockout and turbine trip. The cause of the AVR malfunction is unknown at this time. "All control rods fully inserted. The RCS is being cooled by forced flow (reactor coolant pumps). Secondary heat sink is being provided by the condenser steam dumps utilizing the main feed water system. The auxiliary feed water system actuated based on low steam generator level, but since has been secured. Off-site power remains available. No release is occurring and emergency core cooling systems did not actuate. Emergency plan entry was not required." The plant is in its normal shutdown electrical lineup at normal operating temperature and pressure. Unit 2 was not affected by the Unit 1 transient. The licensee has notified the NRC Resident Inspector | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-11-29
51569 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-11-26 21:00 | 2015-11-27 19:33 | 2015-11-27 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE UNABLE TO BE FULLY RETRACTED The following information was provided by the State of Utah via email: "At approximately 2100 MST on November 26, 2015, two radiographers, working for QTI [Quality Testing and Inspection], were completing radiography operations [at a job site in Provo, UT for Dragon Manufacturing]. When the exposure was completed, the source was withdrawn to the camera but was not fully retracted into the shielded position when the locking mechanism was engaged. The radiographers could not move the source or cable. The source was secured, personnel exited the affected area and the radiographers notified the Radiation Safety Officer (RSO). Temporary lead shielding was placed over the affected camera. Licensee personnel waited in low dose areas until the RSO arrived at the site. Licensee personnel maintained visual control of the affected area. "After performing radiation surveys of the camera, the RSO withdrew and inserted the source into the source changer. The RSO locked the source inside the source changer and transported the radiography equipment to the Licensee's facility. "The source changer, camera and associated cables were removed from service and transported to the licensee shop. Radiation exposures (from self-reading dosimetry) to the licensee personnel were approximately 10 mRem. The RSO's dosimeters indicated an exposure of approximately 40 mRem. More information will be provided in coming days." The licensee notified the State of Utah at 1200 MST on 11/27/2015. The camera was a model IR 100, serial number -4122, which contained a 93 curie Ir-192 source, serial number - Z825. UT Event Report ID No.: UT 150006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-12-07
51568 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-11-27 04:31 | 2015-11-27 09:23 | 2015-11-27 | AUTOMATIC REACTOR SCRAM FOLLOWING PARTIAL LOSS OF OFFSITE POWER "At 0431 CST on November 27, 2015, an automatic reactor scram occurred following the trip of the main generator. The generator trip was apparently caused by a partial loss of offsite power, which resulted from a differential ground on the north bus of the local 230 kV switchyard. The ground signal caused the reserve station service line no. 1 to de-energize, which tripped the Division 1 offsite power source to station, as well as the main generator. The plant responded as designed as follows: The Division 1 emergency diesel generator started and tied to the bus restoring Division 1 emergency power. The Division 3 emergency diesel generator started and tied to the bus, restoring power on the Division 3 switchgear. The reactor protection system tripped as designed. Reactor water level was controlled normally with condensate and feed water. A level 3 reactor water level scram signal occurred as expected, and RPV [Reactor Pressure Vessel] water level was restored to normal level band. Reactor pressure was controlled by the bypass valve system, and a normal cool down was initiated. The reactor is being taken to cold shutdown pending an investigation of the event. The loss of power also resulted in a partial loss of normal service water cooling to the plant, and emergency service water cooling automatically initiated per design. At the time of event, the reactor protection system was aligned to the backup power supply, which was momentarily lost. This resulted in multiple system isolations including reactor water clean up, and outboard balance of plant isolations. These isolations were initiated due to loss of offsite power, and all responded as designed. The isolation resulted in a loss of the running decay heat removal pump for the spent fuel pool. The standby pump is available for service and being aligned for service. The plant is currently stable in hot shutdown. Transmission and distribution personnel are currently investigating the ground in the 230 kV switchyard." All control rods inserted. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-11-27
51567 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-11-20 | 2015-11-25 11:34 | 2015-11-25 | AGREEMENT STATE REPORT - LOST RADIOACTIVE SEED The following was received from the Commonwealth of Pennsylvania via email: "The licensee discovered the event on November 23, 2015 and notified the Department [Commonwealth of Pennsylvania] on November 25, 2015. It is reportable as per 10 CFR 20.2201(a)(1)(ii). "An iodine-125 (I-125) seed was used for radioactive seed localization of a breast lesion. After surgical excision of the breast tissue at an outpatient surgical center, the specimen was placed in a plastic bag and imaged radiographically to confirm the presence of the seed. The seed was noted to be at the edge of the specimen. The specimen was then transferred to a plastic container for transport to the main hospital pathology department. When the specimen was received at pathology, a survey indicated that there was no seed present. "Radionuclide: I-125 Seed "Manufacturer: Best Medical "Model No.: 2301 "Activity: 113 microCi "The licensee assumes the seed became separated from the specimen and remained in the plastic bag which was disposed as biohazardous waste. A survey of the surgical center was performed, but the seed was not able to be located. "A reactive inspection is planned by the Department. More information will be provided upon receipt." Event Report ID No: PA150030 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-12-03
51566 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-11-24 12:53 | 2015-11-24 17:02 | 2015-11-24 | OFFSITE NOTIFICATION FOR A DISCHARGE CANAL TEMPERATURE CHANGE CAUSING A FISH KILL "At 1253 CST on 11/24/2015, XCEL Energy Environmental Services made a report to the Minnesota Pollution Control Agency (MPCA) and the Minnesota Department of Natural Resources (DNR) due to the recorded total fish loss (59) as a result of the Monticello Plant's discharge canal temperature change following the reactor scram on 11/23/2015. This notification is being made under 10 CFR 50.72(b)(2)(xi) based on a notification to another government agency. "This issue has no safety significance and no impact on the health and safety of the general public. "NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-11-24
51565 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-07-24 | 2015-11-24 15:00 | 2015-11-24 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following report was received via e-mail: "The licensee performed a prostate Iodine-125 (I-125) seed implant on July 24, 2014. The prescribed dose of 144 Gray (Gy) to 90 percent of the prostate gland (D90) was not within 20 percent of prescribed dose [144 Gy prescribed, 86.1 Gy administered]. The post plan performed on August 12, 2014, demonstrated that the prostate D90 was 59.79 percent, not within 20 percent limit of the prescribed dose. The licensee did not notify the Ohio Department of Health of this occurrence as a medical event. The medical event was discovered as a result of an inspection conducted on 10/28/15. "A Notice of Violation for the medical event and failure to report the medical event has been issued to the licensee. The investigation is ongoing." Ohio Report: OH150012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-12-02
51564 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-11-24 05:34 | 2015-11-24 14:19 | 2015-11-24 | RESIDUAL HEAT REMOVAL PUMP TRIPPED DURING INITIATION OF SHUTDOWN COOLING "On 11/24/2015 at 0534 hours [CST] the plant was in MODE 3 [hot standby] for a forced outage. While initially placing Shutdown Cooling (SDC) in service, the 12 Residual Heat Removal (RHR) pump tripped approximately 8-10 seconds after start due to the closure of the RHR SDC suction isolation valves. This was determined to be from an invalid signal on the Reactor Pressure Vessel (RPV) suction interlock. This is being reported under 10 CFR 50.72 (b)(3)(v)(B) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. This event did not challenge the ability to maintain safe shutdown conditions, remove residual heat, control the release of radioactive material, or mitigate the consequences of an accident as other methods of decay heat removal were being utilized successfully to establish plant conditions. "The NRC Resident Inspector has been notified." This incident places the RHR system in a 24-hour technical specification limiting condition for operations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2015-11-24
51563 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-11-23 21:48 | 2015-11-23 22:41 | 2015-11-24 | UNUSUAL EVENT DECLARED DUE TO REACTOR COOLANT SYSTEM LEAKAGE "At 2148 EST on November 23, 2015, Salem Unit 2 declared an Unusual Event due to reactor coolant system leakage greater than 10 gallons per minute. While performing troubleshooting to determine the source of leakage from the Emergency Core Cooling System high head safety injection piping, a motor operated valve was opened and the high head piping relief valve lifted. Indications in the control room calculated the leak rate at 16 gallons per minute based on the change in Pressurizer level. The leak was terminated when the motor operated valve was closed and the relief valve reseated. The time [duration] of the leak was about one minute." The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA. * * * UPDATE AT 0105 EST ON 11/24/15 FROM BILLY MOWER TO JEFF HERRERA * * * The licensee terminated the Unusual Event at 0100 EST on 11/24/15. The licensee will be cooling down and depressurizing to mode 5 in order to replace the affected valve. The licensee will be notifying the NRC Resident Inspector as well as the New Jersey State police, Delaware State Police and local emergency dispatch. Notified the R1DO (Dwyer), NRR EO (Morris), IRD MOC (Stapleton), DHS SWO, FEMA Ops enter, and NICC Watch Officer. E-mailed FEMA NWC and Nuclear SSA. * * * UPDATE FROM JOHN OSBORNE TO JOHN SHOEMAKER AT 0341 EST ON 11/24/15 * * * "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D). 'Any event of condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident,' due to inoperability of both trains of the Emergency Core Cooling System high head safety injection systems. "The unusual event was exited at 0100 [EST] on November 24th, 2015, when the Emergency Core Cooling System high head safety injection piping inlet valves were closed, ensuring isolation of the relief valve. The criteria for exit was leakage rate was below the 10 GPM rate. The plant is in mode 3 cooling down to mode 5. "The licensee notified the states of New Jersey and Delaware, Lower Alloways Township, and the NRC Resident Inspector." Notified the R1DO (Dwyer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | ACCIDENT MITIGATION |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-11-23
51562 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-11-24 13:30 | 2015-11-23 17:50 | 2015-11-23 | OFFSITE NOTIFICATION OF FUEL DEFECTS "At approximately 1100 PST, Columbia Generating Station (CGS) planned to make a non-required notification to Energy Facility Site Evaluation Council (EFSEC) regarding indications of two fuel defects. This condition has not affected full power operation at CGS, and there is no impact to the health and safety of the public or to the environment. CGS plans on making this notification to EFSEC on November 24, 2015 at 1330 PST. "This condition is being reported pursuant to 10 CFR 50.72 (b)(2)(xi). "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-11-23
51561 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-11-23 09:30 | 2015-11-23 17:00 | 2015-11-23 | POSITIVE FITNESS-FOR-DUTY TEST A non-licensed contract supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2015-11-23
51560 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-11-23 10:40 | 2015-11-23 15:03 | 2015-11-23 | REACTOR SCRAM DUE TO A REACTOR RECIRCULATION PUMP LOCKOUT "At 1040 CST, with the plant at 100% power, a lockout of the 11 recirculation pump occurred. Following the 11 recirculation pump lockout, at 1041 CST, a reactor scram and a Group 1 isolation occurred. All Main Steam Isolation Valves closed as a result of the Group 1 isolation signal. HPCI [High Pressure Core Injection] has been placed in service to control RPV [Reactor Pressure Vessel] pressure. HPCI did not inject into the RPV and was not needed to control RPV level. "At 1104 CST, a Group 2 containment isolation signal was received due to RPV level less than +9 inches. The Group 2 isolation signal has been reset. "The cause(s) of the 11 recirculation pump lockout, the reactor scram, and the Group 1 isolation are currently not known and are under investigation. "This event is being reported under 50.72(b)(2)(iv)(B) due to the actuation of the Reactor Protection System when the reactor is critical. "For the following reasons, this event is also being reported under 50.72(b)(3)(iv)(A): 1) This event resulted in a valid Group 2 containment isolation signal, 2) Since the cause of the Reactor Protection System actuation is not known, the event is being reported as a valid actuation of the Reactor Protection System, and 3) Since the cause of the Group 1 isolation is not known, the event is being reported as a valid primary containment isolation signal affecting multiple Main Steam Isolation Valves. "All systems have responded as expected, all control rods fully inserted following the Reactor Protection System actuation. The plant is currently shutdown in mode 3, RPV pressure and RPV level are stable. This event did not result in any radiological release from the plant. This event did not challenge the health and safety of the public. "The NRC Resident Inspector has been notified." The plant is in its normal shutdown electrical lineup. HPCI is in pressure suppression mode with RHR cooling the suppression pool. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-11-23
51559 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-11-23 08:44 | 2015-11-23 11:52 | 2015-11-23 | MANUAL REACTOR TRIP AFTER PARTIAL MSIV CLOSURE "At 0820 EST on 11/23/2015, Sequoyah Unit 1 was at 100% power when operators identified the Loop #3 Main Steam Isolation Valve (MSIV) came off its full open seat. This was evidenced by no OPEN indication on the main control board, dual indication on the post accident monitoring panel, and a change in both Tavg and steam pressure. Operators were dispatched locally to the MSIV and to the battery board room to investigate if a cause could be identified for the MSIV movement. The field investigation identified no issues. The operating crew manually tripped the reactor at 0844 EST due to an increasing Tavg-Tref mismatch. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the feedwater isolation signal. "Unit 1 is currently being maintained in Mode 3 at normal operating temperature and pressure, approximately 547 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. "There is no indication of any primary to secondary leakage. All control rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. There is no operational impact to Unit 2 as it continues through the refueling outage with the core off-loaded. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector." All control rods fully inserted during the reactor trip. The atmospheric steam dumps did operate during the transient and then shut. After the trip, the MSIV re-opened. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-11-23
51558 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2015-11-20 18:08 | 2015-11-20 21:49 | 2015-11-20 | METEOROLOGICAL TOWER OUT OF SERVICE "On [11/20/2015 at 1808] CST it was noted that the MET tower (both primary and backup) was offline and not communicating with the Plant Management Information System(PMIS). This results in a major loss of emergency assessment capabilities with respect to meteorological conditions and is reportable under 10CFR50.72(b)(3)(xiii). Communications technicians responded to the plant and the MET Tower communications were restored to PMIS on [11/20/2015 at 1937]." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-20
51557 | -1 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2015-11-20 08:23 | 2015-11-20 15:34 | 2016-01-11 | INOPERABLE VENT STACK RADIATION MONITOR "At 0823 EST on 11/17/2015, the Unit 1 'A' Vent Stack radiation monitor, 1-VG-RI-179, was declared non-functional due to a faulty heat trace circuit. Compensatory measure to perform grab samples every 6 hours was implemented. At 0823 EST on 11/20/2015, the Unit 1 'A' Vent Stack radiation monitor, 1-VG-RI-179, had been out-of-service for 72 hours. The loss of 1-VG-RI-179 is being reported per 10 CFR 50.72(b)(3)(xiii) as a loss of emergency assessment capability. Corrective actions continue to be pursued to restore 1-VG-Ri-179 to functional status. "The NRC Senior Resident Inspector has been notified by the licensee." * * * UPDATE FROM PATRICK FRENCH TO JOHN SHOEMAKER AT 0931 EST ON 11/22/15 * * * The Unit 1 'A' Vent Stack radiation monitor, 1-VG-RI-179, was returned to service at 1440 EST on 11/21/15. The licensee has notified the NRC Resident Inspector. Notified R2DO (Ernstes). * * * RETRACTION FROM MICHAEL WHALEN TO DONALD NORWOOD AT 1509 EST ON 1/11/2016 * * * "The purpose of this report is to retract the event notification report made in accordance with 10 CFR 50.72(b)(3)(xiii) on November 20, 2015 at 1534 EST (EN# 51557). After further review it has been determined that the performance of grab samples is an approved back-up method for radiological assessment capabilities as described in the North Anna Emergency Plan implementing procedure EPIP-4.24 Gaseous Effluent Sampling During Emergency. During non-emergencies, VPAP-2103N Offsite Dose Calculation Manual governs grab sampling and is tracked by Operations using 1-LOG-14 Non-Routine Surveillance Log. As such, a loss of radiological assessment capability did not exist and the ability to assess EAL RU1.4 was not affected. This is consistent with NUREG 1022, Rev.3, Supplement 1 and NEI 13-01, Rev. 0. The action was cleared at 1440 hours on 11/21/15 and the Unit 1 'A' Vent Stack radiation monitor, 1-VG-RI-179, was returned to functional status. "The NRC Senior Resident lnspector has been informed of this event notification retraction." Notified R2DO (Masters). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-20
51556 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2015-11-20 11:00 | 2015-11-20 14:56 | 2015-11-20 | AGREEMENT STATE REPORT - STOLEN MOISTURE-DENSITY GAUGE The following information was received from the State of Arizona by facsimile: "At approximately [0800 MST], November 20, 2015, the Agency [Arizona Radiation Regulatory Agency] was informed that the Licensee had a Campbell-Pacific Model MC-3, Serial Number MC310700331, portable moisture- density gauge stolen from a truck at an apartment parking lot. The theft occurred before [0500 MST], November 20, 2015. The gauge was the only thing stolen from the truck which had expensive tools in it. The sources were Cs-137, 10 millicuries and Am-241:Be, 50 millicuries. "The Agency continues to investigate the event. "The AZ Governor's Office, U.S. NRC, the States of CA, CO, NV, and NM are being notified of this event [by the Agency]." Arizona First Notice: 15-025 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2015-11-30
51555 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2014-02-17 | 2015-11-20 11:19 | 2015-11-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received from the State of Colorado via email: "Detail: After no response from initial mailing to Fort Collins South Sanitation District [from the Colorado Department of Public Health and Environment (CDPHE)] , a call was made to verify information from SRB Technologies quarterly report on 10-21-2015. The superintendent of the facility was unaware of the order for the exit signs and had not received the annual mailing from our office. He was emailed a copy of the manufactures report and annual forms to be completed and asked to verify if the exit signs had been installed at the location reported. The superintendent stated a project was being constructed during the time the signs were ordered however, he would have to contact the companies involved with the project. He contacted the local distributor, CED, 2405 W 15th Avenue, Denver, CO 80204. CED stated they delivered the signs to the electrical contractor on 2-7-14. The superintendent then contacted the electrical contractor Master Electrical Contractors Inc. [MECI] for further information. The superintendent emailed our [CDPHE] office on 11-18-15 regarding the tracking events for the exit signs and provided a report from MECI. The lost exit sign is model number BX-20-WH, serial number is C107403, with activity of 20 Ci of Tritium H-3 shipped from SRB Technologies on 1-24-14 for installation at 2560 East County Road 32, Fort Collins, CO 80528. "Event description: During construction of the dewatering and headworks improvement project, one of the five tritium exit signs was lost. The signs were in the possession of Master Electrical Contractors at the site. It is not certain at what point during the project or what caused the one sign to be lost or where it ended up. Therefore, the General Contractors of the project, Filanc Construction and Master Electrical Contractors, shall be responsible for the lost sign." Colorado Event Report ID No.: CO15-I15-32 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-11-30
51554 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2015-11-19 13:00 | 2015-11-19 19:10 | 2015-11-19 | UNANALYZED CONDITION DUE TO SPENT FUEL POOL TEMPERATURE OUTSIDE LIMITS "A review of operations log data revealed the Unit 2 Spent Fuel Pool temperature was allowed to drift approximately two degrees below the accepted analyzed temperature of 68 degrees F. The Extent of Condition is under review and the number of instances has not been fully determined. It is possible Unit 3 may have also been affected. "As described in the San Onofre UFSAR, Section 9.1.2.3 'Design Basis for Fuel Storage and Handling,' one of the conditions assumed in meeting the design basis, is as follows: the most adverse delta-k (reactivity change) was analyzed for a pool temperature range from 68 degree F to 160 degree F. Although the temperature decrease is considered unlikely to have a significant impact on the results of the analysis, it is being reported under 10 CFR 50.72(b)(2) as an unanalyzed condition because there is at this time no analysis of record for the reduced temperature condition. "There were and continue to be no observed, abnormal effects from the temperature drop below 68 degrees F, and no impact on the health or safety of plant personnel of the public. Re-analysis is in progress and is expected to demonstrate that the criticality acceptance criteria of 10CFR50.68 were met at all times." The licensee notified the Regional NRC Contact. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-11-19
51553 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-11-19 05:30 | 2015-11-19 18:05 | 2015-11-20 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MISSING A radiographer for the licensee was in contact with other PetroChem personnel at approximately 0530 CST on 11/19/2015. As of the time of this report, the radiographer has not been heard from and is unaccounted for. The radiographer is considered a Trustworthy and Reliable employee by the licensee. Searches have been and continue to be conducted of routes that the radiographer could have taken to travel to his work location in Corpus Christi, Texas. The licensee has also contacted family members, interviewed co-workers, and checked the job site, all with negative results. The radiographer was traveling in a 2015 Ford F250 diesel 4x4 truck, white in color, with Texas license number GDY-6331. A QSA 880 Delta source projector (serial number 5187) containing a 74 curie IR-192 source was in the truck and is now considered unaccounted for. The Corpus Christi police department has been contacted by the licensee for assistance. Texas Report Number: I-9359. Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC Watch Officer and EPA. Notified via E-mail only FDA, Nuclear SSA, FEMA National Watch Center, and DNDO-JAC. Notified Mexico via facsimile. * * * UPDATE FROM ART TUCKER TO JOHN SHOEMAKER AT 0701 EST ON 11/20/15 * * * "The Agency [Texas Department of State Health Services] contacted the [licensee's] radiation safety officer [RSO] at 0655 [CST] and [the RSO] stated they recovered the camera and the truck at 0000 [CST on 11/20/15]. The investigation into this event is on going. Additional information will be provided as it is received in accordance with SA 300." Notified R4DO (Warnick), NMSS (McIntosh), ILTAB (Bunch), IRD (Stapleton), NMSS Event Notification via email, DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC Watch Officer and EPA. Notified via E-mail only FDA, Nuclear SSA, FEMA National Watch Center, and DNDO-JAC. Notified Mexico via facsimile. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-11-27
51552 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-11-19 07:24 | 2015-11-19 11:51 | 2015-11-19 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "At 0724 [CST] on 11-19-2015, River Bend Station declared the High Pressure Core Spray System inoperable in accordance with Technical Specification 3.8.9, Condition E (Declare High Pressure Core Spray System and Standby Service Water System Pump 2C inoperable immediately) due to Division 2 Control Room Air Conditioning System Chiller HVK-CHL1D being inoperable due to a significant lube oil leak. HVK-CHL1D tripped on Low Lube Oil Differential Pressure. Division 1 Control Building Air Conditioning System Standby Chiller HVK-CHL1A automatically started as expected. "Actions taken to exit LCO [Limiting Condition of Operation]: Operators alternated to HVK-CHL1B in standby." The licensee notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-11-19
51551 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2015-11-18 23:33 | 2015-11-19 00:56 | 2015-11-19 | AFTER-THE-FACT NOTIFICATION OF UNUSUAL EVENT "Unit 3 experienced Loss of Offsite Power due to lockout on Unit 3 Startup transformer. The 3B EDG auto started and loaded on the 3B 4KV Bus. The 3A Sequencer was out of service and prevented the 3A EDG from auto starting and supplying 3A 4KV busses. With only 3B 4KV bus powered from an EDG and no offsite power to Unit 3, Unit 3 entered an Unusual Event. "Core cooling was restored with 3B RHR pump at 2343 EST. At 2350 EST, 3A 4KV Bus was manually loaded onto 3A EDG and conditions for Unusual Event were terminated. "Additionally this is a non-emergency eight hour notification in accordance with 10CFR50.72(b)(3)(iv)(A), for a valid automatic actuation of the 3B Emergency Diesel Generator." While core cooling was lost, the core experienced a 3 degree heat up. Spent fuel pit cooling has also been restored. The cause of the transformer lockout is under investigation. Unit 4 was unaffected and continues to operate at 100% power. The licensee has notified state and local authorities about this event. The licensee has also notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2015-11-19
51550 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2015-11-18 18:00 | 2015-11-18 18:40 | 2015-11-18 | TRUCK CONTAINING LOW LEVEL WASTE RADIOACTIVE MATERIAL OVERTURNED At approximately 1800 EST on 11/18/2015, the Maryland State Police responded to an overturned truck on route I-81 in Washington County, MD. The truck departed Three Mile Island Nuclear Generating Station en route to Oak Ridge, TN. Maryland Department of Environment responded to the site with radiation detectors and the hazmat team. The radioactive material was classified as low level waste and contained within the vehicle. The radiation levels on contact were very low, and at 1 meter, radiation levels were at background levels. The State Police closed the road for accident reconstruction. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2015-11-27
51549 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-11-18 10:53 | 2015-11-18 18:30 | 2015-11-18 | FITNESS FOR DUTY - UNOPENED CAN OF ALCOHOLIC BEVERAGE FOUND IN THE PROTECTED AREA "An 8 oz. can of alcohol 'Mike's Harder Lemonade' (8% by volume) was discovered inside the protected area. The can was unopened. Site security took possession of the can and removed it from the protected area. This report is being made under 10CFR26.719(b)(1) as a 24 hour telephone notification. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2015-11-18
51548 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2014-02-06 | 2015-11-18 15:13 | 2015-11-18 | AGREEMENT STATE REPORT - STOLEN GAS CHROMATOGRAPH The following information was received from the State of New York via email: "On October 19, 2015, the New York State Department of Health was informed by a representative from Zebra Environmental Corp., that between 2/5/2014 and 2/6/2014 a Hewlett Packard model 5890 Gas Chromatograph [GC] containing an electron capture detector with a 15 mCi Ni-63 source was stolen by forced entry. Several items, including the gas chromatograph, were stolen at a temporary job site [in] Asheville, North Carolina. The GC was stored in a locked trailer which was within a locked fenced in area. The local county police were notified and a report was submitted. The licensee failed to notify the New York State Department of Health at the time of the theft. The Department only learned of the incident on October 19, 2015 as part of the license renewal process. New York State Department of Health specifically licenses companies that use gas chromatographs at temporary job sites. A violation letter will be issued to the company for a number of code violations including failure to notify the Department immediately of the theft of licensed material." NY Event Report ID No. NYDOH-15-10 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-11-26
51547 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2015-11-18 03:26 | 2015-11-18 09:53 | 2016-01-19 | INVALID ACTUATION OF 3A EMERGENCY DIESEL GENERATOR (EDG) "This is a non-emergency eight hour notification in accordance with 10 CFR 50.72(b)(3)(iv)(A), for an automatic actuation of the 3A Emergency Diesel Generator (EDG). "On 11/18/15 at approximately 0326 [EST] a loss of power was experienced on the 3A 4KV Bus. The redundant 3B 4KV bus did not experience a loss of power. All systems operated as expected following the loss of power with the 3A EDG automatically sequencing onto the 3A 4KV bus and the load sequencer loading as designed. At the time of the actuation, Unit 3 was in a refueling outage in MODE 5. Investigation into the cause of the loss of power is in progress. There was no impact on Unit 4 operation during this time." The NRC Resident Inspector has been informed. * * * UPDATE AT 2100 EST ON 01/19/16 FROM JIM SPEICHER TO S. SANDIN * * * The licensee is retracting the original notification of a valid actuation and has re-categorized this as a 60-day optional report based on the following: "This 60-day telephone notification is being made under the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of the 3A EDG. The 3A EDG start resulted from an unexpected actuation of the 3A load sequencer during setup activities for the 3A Engineered Safeguards Integrated Test (ESIT) loss of offsite power (LOOP) sequence. "On November 18, 2015, at approximately 0330 EST with Unit 3 in Mode 5 during a refueling outage, an unexpected LOOP occurred on the 3A 4160 V bus. At the time, an Instrument and Control (I&C) specialist was working in sequencer cabinet 3C23A verifying proper placement of flags in preparation for the installation of a local test switch that would be used to initiate the 3A ESIT LOOP signal. The 3A EDG started and functioned as designed. Initial troubleshooting determined that there were no actual plant conditions or parameters (e.g., undervoltage, degraded voltage, manual initiation) involved in the actuation. "The root cause investigation revealed that individuals working in the room near the open cabinet did not have their mobile phones in airplane mode as required and two computer tablets being used adjacent to the sequencer cabinet were not in airplane mode as required prior to entering the 3A sequencer room. The cause of the actuation was determined to be an unintended human interaction in the form of electromagnetic or radio frequency interference at the proximity of the 3C23A cabinet. "The licensee notified the NRC Resident Inspector." Notified R2DO (McCoy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-11-18
51546 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-11-04 | 2015-11-18 09:45 | 2015-11-18 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING YTTRIUM-90 The following information was received from the State of Ohio via email: "A medical event occurred at The Ohio State University Wexner Medical Center on Wednesday, November 04, 2015 involving the medical use of TheraSphere Yttrium-90 (Y-90) glass microsphere therapy. Upon completion of the post procedure measurements, it was noted that a high residual activity was found during the post-procedure exposure measurements. Based on the pre and post-procedure exposure measurements, it was calculated that a total of 74% of the prescribed dose was delivered to the patient. No adverse effects to patient are anticipated and the prescribing physician determined that a therapeutic dose had been received." Intended dosage was 20.1 mCi (120 Gy) Received dosage was 15 mCi (89 Gy) OH Report No. 2015-017 NMED Report No. OH150011 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-11-26
51545 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-11-17 23:55 | 2015-11-18 08:45 | 2015-11-18 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "At 2355 (CST) on 11/17/2015, River Bend Station declared the High Pressure Core Spray [HPCS] system inoperable in accordance with Technical Specification 3.8.9, Condition E (Declare HPCS system and Standby Service Water System Pump 2C inoperable immediately) due to Division 1 Control Room Air Conditioning System HVK-CHL1C being inoperable because of a significant Freon leak on SWP-PVY32C. "Actions taken to exit LCO: Alternated divisions of Control Room Air Conditioning System to Division 2 HVK-CHL1D in service and Division 1 HVK-CHL1A in standby." The basis for declaring High Pressure Core Spray inoperable was that the control room chiller also chills the switchgear room that supplies power to the HPCS. HPCS was out of service for less than one hour while the chillers were swapped from Division 1 to Division 2. The licensee has notified the NRC Resident Inspector. | 71 | 0 | 0 | 71 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-11-18
51544 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2015-10-27 | 2015-11-17 16:18 | 2015-11-17 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the Commonwealth of Virginia via email: "On October 27th, the VRMP [Virginia Radioactive Materials Program] received a letter from CJCLDS [The Church of Jesus Christ of Latter Day Saints] stating that 25 exit signs each containing approximately 3 curies of H-3 were lost. The letter stated that a contractor was hired in July to replace the H-3 signs with new electric signs and place the H-3 signs in a closet so that CJCLDS staff could properly dispose of them by packaging and returning them. The letter stated the signs were not in the designated location. "The contractor was contacted by the VRMP who stated that an electrical sub-contractor was hired to perform this work. That company was contacted and VRMP was able to speak to the electrician and his supervisor. The electrician stated verbally and in writing that he removed the H-3 exit signs and placed them in the designated location. "A search was performed by CJCLDS staff and church members were contacted to see if they had seen the signs. It has been concluded that the signs were discarded by accident and can't be found or recovered at this time. "This location and the serial numbers of the H-3 signs could not be found in our GL database. The NRC was contacted to search their GL database for the serial numbers to no avail." Virginia Event Report ID No: VA-15-9 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2015-11-25
51543 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2015-11-17 11:11 | 2015-11-17 12:11 | 2015-11-18 | PLANNED MAINTENANCE ON SEISMIC SYSTEM FUNCTIONAL TEST "This notification is being made due to planned maintenance during the Semi-Annual Seismic System Functional Test. This test will result in a major loss of emergency assessment capability for emergency action level (EAL) HA6 (natural or destructive phenomena affecting VITAL AREAS), while the control room 0.1g acceleration alarm is non-functional. The emergency preparedness plan requires the 0.1g acceleration alarm indication to declare EAL HA6 during a seismic event greater than the Operating Basis Earthquake (OBE). This condition requires an 8 hour non-emergency immediate reportability to the NRC in accordance with 10 CFR 50.72(b)(3)(xiii), Major Loss of Assessment, Response, or Communication Capability. "At approximately 1200 CST on November 17, 2015, the Semi-Annual Seismic System Functional Test will commence. While this test is in progress, seismic alarm capability is not available for EAL declaration purposes. ANO procedures provide compensatory measures of using offsite sources to obtain seismic data. It should be noted that seismic data will still remain capable of being recorded and only alarm capability is lost. The Semi-Annual Seismic System Functional Test will occur intermittently over the next four days." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM STEVE KIRSCHBERGER TO VINCE KLCO ON 11/18/15 AT 1940 EST * * * The licensee returned the Seismic System to service at 1347 CST on 11/18/15. The licensee notified NRC Resident Inspector. Notified the R4DO (Warnick). | 100 | 68 | 0 | 100 | 68 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-17
51542 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2015-11-15 23:54 | 2015-11-16 16:56 | 2015-11-16 | AGREEMENT STATE REPORT - LOST DENSITY MOISTURE GAUGE The following was received from the State of North Dakota via email: "Taney Engineering, Inc. (Taney) reported the loss of a moisture/density gauge (Troxler Model No. 3430, Serial No. 30530) that contained a 1.48GBq (40mCi) Am-241:Be source (Serial No. 47-27626) and a 0.3 GBq (8 mCi) Cs-137 source (Serial No. 77-13400) currently licensed under North Dakota Department of Health License No. 33-53306-01. This event was initially reported to the Minot, North Dakota Police Department at 11:54 P.M. on Sunday, 11/15/2015. At that time, the field inspector noticed the Troxler nuclear density gauge designated above to be missing from the bed of his truck at the end of the day. The field inspector stated the nuclear density gauge was in the yellow transport box secured in the bed of his truck with chains and locks to both side handles and locks on the transport case when he stopped at Wal-Mart located at 3900 S Broadway St., Minot, ND 58701. When he returned from the store, the equipment was still secure in the bed of his truck. He drove to Buffalo Wild Wings in the adjoining parking lot located at 3820 S Broadway St., Minot, ND 58701 at approximately 11:35 P.M. He placed an order for take-out and waited for food inside. He arrived home in Minot, ND 58701 before 11:50 P.M. to drop off groceries before checking in the nuclear gauge and discovered company equipment, including the gauge, missing from the back of his truck. He immediately notified the Minot Police Department, filed incident report No. 2015-00036173. He then notified Troxler Electronic Laboratories at 877-876-9537. He than notified Taney." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2015-11-24
51541 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-11-16 11:15 | 2015-11-16 15:53 | 2015-11-16 | AGREEMENT STATE REPORT - DAMAGED DENSITY MOISTURE GAUGE The following was received from the State of Tennessee via email: "On November 16, 2015, a neutron soil density and moisture gauge belonging to Terracon Consultants, Inc. was run over by a dump truck. The source was fully retracted at the time of the incident. Initial surveys have indicated that the source remained in the shielded position after the incident. A leak test has been taken and sent off for evaluation. The device was a CPN MCIDR (SN# MD40407363) with 50 mCi of Am-241 Be (Source #7363) and 10 mCi of Cs-137 (Source #7363). The licensee placed the device 'out of service'. On November 16, 2015, the device will remain in shielded storage until Terracon Consultants, Inc. decides what they are going to do with it. A follow-up report will be submitted upon receipt of further information." Tennessee State Event Report ID No: TN-15-168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-11-24
51540 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-11-16 09:20 | 2015-11-16 15:53 | 2015-11-16 | AGREEMENT STATE REPORT - FIRE IN AN OFF GAS DUST COLLECTOR The following was received from the State of Tennessee via email: "A fire occurred in an off gas dust collector and particulate filtration system used for ventilation from a process providing oxidation of metal depleted uranium chips. Alarm engaged and fire suppression system engaged. The local fire department responded and reinforced suppression. The fire department departed by 11:20 AM. Initial indications indicate no releases to the environment based on visual indications and stack monitoring systems not alarming. Negative pressure to the building was maintained. Smears taken outside of the building and radiologically controlled area does not indicate any elevated activity outside of the building. Air samples are being pulled and analyzed for workplace and air effluent stacks. Bioassays were being conducted to assess worker and firemen. A follow-up report will be submitted upon receipt of further information." Tennessee State Event Report ID No: TN-15-167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-11-24
51539 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-10-22 11:00 | 2015-11-16 12:59 | 2015-11-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA FAILED TO FUNCTION PROPERLY The following was received from the State of Tennessee via email: "On October 22, 2015, a radiography device belonging to TUV Rheinland Industrial Solutions failed to function properly due to a jammed selector ring; this occurred when the operator attempted to rotate from the connect to the lock position. The source was fully retracted at the time of the incident. The device was a Sentinel 880D (SN# D2620) with 29.4 Ci of Se-75 (Source #SE4627). The licensee placed the device 'out of service'. On October 26, 2015, the device was shipped back to QSA Global for repair. A follow-up report will be submitted upon receipt of further information." Tennessee State Event Report ID No: TN-15-166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-11-24
51538 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2015-11-13 17:45 | 2015-11-14 00:22 | 2015-11-14 | DEGRADED CONDITION OF LEAKAGE FROM PUMP LOWER SEAL WELD "On 11/13/15 at 1745 EST, Unit 1 drywell entry was performed during an unplanned Unit 1 outage. The licensee identified leakage from a weld on the 3/4 inch lower seal vent piping connected to the 1B reactor recirculation pump lower seal area. The location is within the reactor recirculation loop isolation valves, therefore isolable from the reactor vessel. The piping is ASME Class 2 and is a reactor coolant pressure boundary. The reactor was in mode 3 at the time of discovery. Control Room determined at 2110 EST on 11/13/15, that requirements for 10CFR50.72(b)(3)(ii)(A) were not met. "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii)(A)." The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-11-14
51537 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-11-11 | 2015-11-13 17:29 | 2015-11-13 | AGREEMENT STATE REPORT - RADIOGRAPHER OVERDOSE The following report was received via e-mail: "On November 13, 2015, a licensee notified the Agency that one its radiographers had an overexposure. The licensee stated the radiographer cranked out the source and waited the time for the shot, then thought he cranked the source back into the camera. When he went to retrieve the film, the radiographer noticed his survey metered was pegged off scale. He immediately went back to the truck and checked his pocket dosimeter and it was off scale also. He picked up the crank and retracted the source. He checked the area with the survey meter and the radiation level had dropped. He informed his supervisor that night and the corporate radiation safety officer had the radiographers monitoring badge sent off for processing. The badge reading was DDE [Deep Dose Equivalent] of 11,453 mRem and LDE [Lens of the eye Dose Equivalent] 11,494 mRem. The radiographer is being interviewed of the details of the incident and a detailed report will be provided. The radiographer has not had any health effects at this time nor are any expected." This incident occurred on 11/11/2015 at a job site in Pecos, TX. Texas Incident: I-9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-11-23
51536 | -1 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-11-13 06:39 | 2015-11-13 08:21 | 2015-12-08 | NOTIFICATION OF UNUSUAL EVENT DUE TO UNIDENTIFIED RCS LEAKAGE GREATER THAN 10 GPM While in Mode 3, South Texas Project Unit 1 declared an Unusual Event at 0639 CST on 11/13/15, due to SU7 of EAL1- Unidentified RCS or Pressure Boundary leakage greater than 10 gpm. The excessive leakage to the WHT (waste holding tank) occurred when a letdown system demineralizer was placed in service. Operators bypassed the demineralizer and the RCS leakage was stopped. The excess leakage lasted for approximately 8 minutes and the maximum leakage was estimated to be 12-15 gpm. There was no impact on South Texas Unit 2 which continues to operate at 100% power. South Texas Project Unit 1 exited the Unusual Event at 0802 CST on 11/13/15, after verifying Unidentified RCS leakage less than 1 gpm. The demineralizer drain valve was partially open and was the cause of the excess leakage. The drain valve has been closed. The licensee has notified the NRC Resident Inspectors. Notified DHS SWO, FEMA Ops Center, FEMA NWC, NICC Watch Officer, and NuclearSSA via email * * * UPDATE AT 1414 EST ON 11/13/2015 FROM JASON BERRIO TO MARK ABRAMOVITZ * * * "Due to entering the STP [South Texas Project] Emergency Plan (Unusual Event), STP has officially determined to make a planned press release. Per 10 CFR 50.72(b)(2)(xi), STP is making a notification to the NRC via the emergency notification system (ENS). "The NRC Resident Inspector has been notified of the press release. "The planned press release shares the following information: "On November 13, 2015, STP Nuclear Operating Station, Unit 1, declared an Unusual Event at 0639 CST. Plant operators identified increasing reactor coolant system leakage in Unit 1. Plant Operators took immediate actions to verify the source and safely isolate and stop the leakage. Upon identifying the source of the leakage, the Unusual Event was exited at 0802 CST on November 13, 2015. "The leakage was captured and maintained within an on-site storage tank and there was no radioactive release to the environment. STP Unit 1 is preparing for restart following a scheduled refueling and maintenance outage." Notified the R4DO (Gaddy). * * * RETRACTION AT 1221 EST ON 12/08/15 FROM MARC HILL TO JEFF HERRERA * * * "The purpose of this report is to retract the ENS report made in accordance with 10 CFR 50.72 (a)(1)(i) on November 13, 2015, at 08:21 EST (ENS # 51536). STP Nuclear Operating Company declared an Unusual Event at 0639 CDT on November 13, 2015, based on Initiating Condition for Reactor Coolant System (RCS) Leakage Emergency Action Level (EAL) SU7. The event was reported to the NRC under EN # 51536 and the event was subsequently terminated on November 13, 2015 at 0802 CST. After further review, the emergency declaration is being retracted because the source of the leakage was from the Chemical and Volume Control System (CVCS) and not from the RCS." The NRC Resident Inspector will be notified. Notified the R4DO (Hagar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2015-11-13
51535 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-11-12 15:00 | 2015-11-12 18:59 | 2015-11-12 | PORTABLE CHEMICAL TOILET SPILL TO THE ENVIRONMENT "On 11/12/2015 at approximately 1500 EST, a spill to the environment was determined to be reportable to the state environmental and local health agencies. A press release is planned. "The spill occurred when a portable chemical toilet tipped over and was identified at approximately 1440 EST. The contents and exact quantity of the spill are unknown but the toilet has a capacity of 60 gallons. The spill contacted the ground but did not reach any waterways. Cleanup efforts are in progress. "The NRC Senior Resident Inspector has been notified." The licensee notified the Michigan Department of Environmental Quality. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-11-12
51534 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2015-11-12 | 2015-11-12 18:36 | 2015-11-12 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE A Troxler moisture density gauge owned by the South Carolina Department of Transportation was run over and damaged. The Am-241 and Cs-137 sources were retracted at the time of the accident. Surveys by the Radiation Safety Officer were normal. The damaged gauge will be sent to the manufacturer for refurbishment or disposal. Sources: Am-241: 40 mCi Cs-137: 8 mCi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2015-11-20
51533 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-11-12 11:32 | 2015-11-12 17:47 | 2015-11-12 | SECONDARY CONTAINMENT INOPERABLE "On November 12, 2015 at 1132 hrs. [EST], Secondary Containment became inoperable due to failure to meet SR 3.6.4.1.1 requirements on Unit 2. "The inoperability was caused when RB [Reactor Building] Zone II differential pressure [D/P] oscillated between 0.23 and 0.43 inches WG [water gauge] (less than SR 3.6.4.1.1 requirement of greater than or equal to 0.25 inches WG). The oscillations subsided at 1501 [EST] and RB Zone II D/P continues to be maintained at approximately 0.35 inches WG. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-11-12
51532 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2015-11-12 11:32 | 2015-11-12 15:15 | 2015-11-12 | AUTOMATIC REACTOR SCRAM "At 1132 hours [EST] on November 12, 2015, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to one Main Steam Isolation Valve (MSIV) unanticipated closure causing a High Pressure RPS [Reactor Protection System] trip. "All control rods inserted and both reactor recirculation pumps tripped due to reactor water level 2. Reactor water level lowered to -37 inches causing Level 3 (+13 inches) and level 2 (-38 inches) (Division 2 only) isolations. RCIC [Reactor Core Isolation Cooling] automatically initiated and was overridden by control room operators after RPV [Reactor Pressure Vessel] water level was restored to the normal band with feedwater. All isolations and initiations occurred as expected. No main steam relief valves opened. Pressure was controlled via main turbine bypass valve operation. All safety systems operated as expected. "The Unit 1 reactor is currently stable in Mode 3. Investigation into the cause of the MSIV closure is underway. "Unit 2 was unaffected and continues power operation. "The NRC Resident Inspector has been notified. A voluntary notification to PEMA [Pennsylvania Emergency Management Agency] and press release will occur." The plant is in its normal shutdown electrical lineup. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-11-12
51531 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-10-22 | 2015-11-12 13:51 | 2015-11-12 | AGREEMENT STATE REPORT - LEAKING NI-63 SOURCES The following report was received via e-mail: "On 10/27/15, the RSO [Radiation Safety Officer] contacted RHB [California Radiation Health Branch] via an email to report two Ni-63 leaking sources. On 10/22/15, Thomas Gray and Associates, the vendor contracted to run the leak test analysis had informed the licensee that two of their Ni-63 sources were leaking above the prescribed limit of 0.005 microCuries. These sources were manufactured by New England Nuclear and had an initial activity of 10 mCi as of July 1966. They do not have a S/N, but were assigned internal tag numbers of 55 and 56. Both sources have not been used in any experiments for many years and have remained in storage. As of 10/27/15, both sources had an activity of 7.11 mCi each. They were not found to be leaking or damaged in previous leak tests. [The] RSO further stated that these sources were not removed from its safe or from its container anytime in the last year. As a result, no contamination was spread through the buildings. "[The] RSO is working with Thomas Gray and Associates to schedule a waste pick up in early 2016 to dispose of these sources." California Event 5010-102715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-11-20
51530 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-11-11 13:44 | 2015-11-11 19:40 | 2015-11-11 | SEISMIC MONITOR INOPERABLE "At 1344 CST on 11/11/15, the seismic monitor was found inoperable. The seismic monitor was inoperable such that emergency classification at the ALERT level could not be obtained with site instrumentation. "The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). "[The NRC] Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-11
51529 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-11-11 10:00 | 2015-11-11 16:04 | 2015-11-11 | DAMAGED TROXLER GAUGE The following was received via email: "At approximately 1000 [EST], a Troxler Gauge was run over by a road construction roller resulting in a cracked housing of the gauge. The instrument's source probe was not extended. Initial survey results indicated 0.5 mR/hr at 12 inches (background was less than 0.1 mR/hr). An ERCIT inspector was dispatched to investigate. [The inspector's] survey indicated 15 mR/hr on contact; his report is forthcoming." The gauge contains Cesium-137 and Americium/Beryllium sources. The gauge was transferred to the licensee's radwaste facility. Florida Incident Report Number: FL-15-116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-11-19
51528 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-11-11 08:26 | 2015-11-11 11:48 | 2015-11-12 | SHIELD BUILDING VENT GAS RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE "At 0826 CST on 11/11/2015, 1R-22, Shield Building Vent Gas Radiation Monitor, was removed from service for planned maintenance. This monitor has no compensatory measure that will allow timely classification of two Emergency Action Levels (EALs) - NUE (Notification of Unusual Event) and Alert classifications - when out of service. It is also used for offsite dose projection calculations. This results in a Loss of Emergency Assessment Capability while 1R-22 is out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "Unit 1 Shield Building Ventilation Stack is also monitored by high range monitor, 1R-50, which is used for the same purpose in Site Area or General Emergency classifications. 1R-50 is being monitored and is indicating normal values. There are no radioactive leaks that will impact the Shield Building as evidenced by normal readings on 1R-22 prior to its removal from service. The duration of this maintenance is scheduled for 24 hours and will continue until the monitor is returned to service. Maintenance will not result in the unplanned release of radioactivity to the environment and will not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." * * * UPDATE AT 1547 EST ON 11/12/15 FROM PAUL FINHOLM TO JEFF HERRERA * * * The licensee indicated that the duration of maintenance was extended for approximately 24 hours to allow continued repair of the monitor. The NRC Resident Inspector was notified. Notified the R3DO (Kozak). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-11
51527 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-11-10 15:02 | 2015-11-10 20:13 | 2015-11-10 | UNANALYZED CONDITION DUE TO DEBRIS DROPPED INTO REACTOR CAVITY EQUIPMENT PIT "On 11/10/2015 at 1502 [EST], Unit 2 MCR [main control room] was notified by workers in containment that 2 ice suits had been dropped into the Unit 2 Containment Reactor Cavity Equipment Pit. Based upon size and location of the dropped suits, Unit 2 entered LCO 3.6.15 (Containment Recirculation Drains) Condition B and LCO 3.0.3 for refueling canal drains being inoperable. The two refueling canal drains and the ice condenser drains function with the ice bed, Containment Spray System and ECCS to limit the pressure and temperature that could be expected following a DBA [Design Basis Accident]. Following performance of a Safety Function Determination it was determined that, during the short duration when both coats were in the process of being retrieved, they could have potentially clogged the drains and prevented the fulfillment of safety functions if there was a DBA. Both suits were retrieved from the equipment pit by 1556 [EST] and all LCO conditions were exited." The licensee notified the NRC Resident Inspector. | 0 | 81 | 0 | 0 | 81 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION | UNANALYZED CONDITION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 50.72(b)(3)(ii)(B) |  | 0 | 2015-11-10
51526 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-11-09 20:40 | 2015-11-10 04:15 | 2015-11-10 | REACTOR BUILDING VACUUM LESS THAN TECHNICAL SPECIFICATIONS REQUIREMENT "At 2040 PST on 11/9/2015, Reactor Building (Secondary Containment) pressure increased to above the Technical Specification Surveillance requirement of 0.25 inches vacuum water gauge for approximately seven minutes. Operators took action to manually start Standby Gas Treatment System to restore Reactor Building pressure. This event is reportable as an event that could have prevented fulfillment of a safety function needed to control the release of radiation and mitigate the consequences of an accident. The cause of the event is under investigation. "There were no radiological releases associated with the event. "No safety system actuations or isolations occurred. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-11-10
51525 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-10-20 | 2015-11-09 17:14 | 2015-11-09 | LOST STATIC ELIMINATOR SOURCE The following was received from the State of California via email: "On 10/30/15, the RSO at Lockheed Martin reported the following to RHB [California] via an email: "On 10/20/15, the RSO had declared a missing Po-210 static eliminator source from their inventory. The device model is Nuclecel P-2035 static eliminator, S/N A2KB502. The sealed source contained 10 mCi as of 10/15/14. As of 10/29/15, the source would have remaining activity of 1.5 mCi. The lab using the static eliminator had recently relocated operations between buildings within the Sunnyvale campus and the licensee suspects that it was lost during this process. "RHB [California] will be following up with this incident." California 5010 Number: 103015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-11-17
51524 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2015-11-08 | 2015-11-09 14:33 | 2015-11-09 | FIXED GAUGE STUCK SHUTTER The following was received from the State of Wisconsin via email: "On Sunday November 8, 2015, the Wisconsin Radiation Protection Section received a phone call from the mill Radiation Safety Officer (RSO) for the Wisconsin Rapids facility that the licensee had a fixed gauge with a shutter stuck open. An alarm light on the panel indicated that the shutter was not closed. The operator notified the mill RSO who then contacted the corporate RSO. The RSO had Voith Paper, who is authorized for non-routine maintenance to come in to fix the shutter. He pulled the scanner offline around 2230 [CST] with the shutter stuck open. The manufacturer's representative was able to fix the shutter. The scanner went back online around 0030, Monday, November 09, 2015." Wisconsin Event Report ID No.: WI150020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2015-11-17
51523 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-11-09 08:00 | 2015-11-09 09:10 | 2015-11-09 | TECHNICAL SUPPORT CENTER UNAVAILABLE DUE TO PLANNED MAINTENANCE "On Monday, November 9, 2015 at 0800 [EST], planned routine maintenance was initiated on the Technical Support Center/Operations Support Center (TSC/OSC) ventilation system. The planned maintenance is to replace the charcoal filters and test the HVAC trains. All other TSC/OSC functions remain available. "Under certain accident conditions the TSC/OSC may become unavailable as a result of the ventilation system not being available. Existing Emergency Procedures direct the responsible Emergency Plant Manager to relocate the TSC/OSC staff to the designated alternate location. The affected Emergency Response Organization facility leads have been informed. "The licensee has notified the NRC Senior Resident Inspector. "The Commonwealth of Massachusetts will be notified. "This notification to the USNRC Operations Center is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the potential loss of an Emergency Response Facility (ERF)." * * * UPDATE ON 11/9/15 AT 1750 EST FROM KENNETH GRACIA TO DONG PARK * * * "At 1730 EST on Monday, November 9, 2015, the TSC/OSC ventilation system was restored to service." The licensee will notify the NRC Resident Inspector. Notified R1DO (Arner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-09
51522 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2015-11-09 05:47 | 2015-11-09 08:40 | 2015-11-09 | UNUSUAL EVENT DECLARED DUE TO CONTAINMENT FIRE ALARM "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "During Palo Verde Nuclear Generating Station Unit 2 containment pressurization for integrated leak rate testing in Mode 5, a containment fire alarm in Fire Zone 63B (Steam Generator 2 all elevations of containment) was received. Containment temperature and pressure at time of event were 72 degrees F and 13 PSIG. "Due to the inability to access containment to validate the fire alarm, an Unusual Event (HU2.1) was declared at 0547 [MST] for a Fire in containment which was unable to be validated within 15 minutes of receipt. No safety functions have been impacted due to the fire alarm. No automatic or manual RPS or ESF actuations occurred and none were required. "Actions are being taken to depressurize containment to enter and validate the fire alarm. "The NRC Resident Inspector has been notified." There has been no effect on U-1 or U-3 due to this fire alarm. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer and via E-mail only FEMA NWC and Nuclear SSA. * * * UPDATE FROM ROB WARNER TO DONALD NORWOOD AT 1125 EST ON 11/9/2015 * * * "Containment was entered following depressurization. Operations and Fire Protection personnel inspection of containment and Fire Zone 63B identified no indication of fire or smoke and the fire alarm was determined to be invalid. No other impacts to plant equipment were identified. The Unusual Event was terminated on 11/9/2015 at 0901 MST. "The NRC Resident Inspector has been notified." Notified R4DO (Proulx), NRR EO (Morris), and IRD (Grant). Notified DHS SWO, FEMA Ops Center, NICC Watch Officer and via E-mail only FEMA NWC and Nuclear SSA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-11-09
51521 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-11-08 02:30 | 2015-11-08 02:55 | 2015-11-08 | MANUAL REACTOR TRIP DUE TO REACTOR COOLANT PUMP OIL LEAK During power ascension following refueling outage, a decreasing oil level in the 'C' Reactor Coolant Pump was noted. When the oil level reached 69 percent, with the reactor at approximately 56 percent rated thermal power, per plant procedure, a rapid downpower was initiated which brought the plant to approximately 15 percent power and a manual reactor trip was initiated at that point. The reactor trip was uncomplicated and all plant equipment responded as expected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-11-08
51520 | -1 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-11-05 | 2015-11-06 20:24 | 2016-01-26 | AGREEMENT STATE REPORT - UNDERDOSE TO PATIENT The following report was received from the State of Utah via email: "On 11/5/15, a 66 year-old male patient was scheduled to receive a TheraSphere infusion. The patient required a TheraSphere vial dose of 1.94 GBq Y-90 (order was for 5.5 GBq dose calibrated on 11/1/15 to deliver 1.94 GBq on 11/5/15) to treat the left hepatic lobe of the liver to a dose of 125 Gy for hepatocellular carcinoma. "It was not until the Nuclear Medicine technologist returned to the In-Patient 'hot lab' to finish her calculations and make her final measurements after the procedure that she determined that the patient received a TheraSphere vial dose of 1.502 GBq instead of the prescribed vial dose of 1.94 GBq. (22.5 percent of the dose remained in the administration system.) "The Nuclear Medicine Coordinator notified the Radiation Safety Officer and the authorized user. The Authorized User notified the patient. Also, the manufacturer's representative was notified. This incident is currently under investigation." Utah Event Report No.: UT150005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * EVENT RETRACTION FROM GYWN CALLOWAY TO JOHN SHOEMAKER AT 1919 EST ON 1/26/16 * * * The State of Utah (Division of Waste Management) has received additional information, from the licensee, indicating that the actual underdose to the patient was < 5% and does not meet the reportability criteria. Therefore, this event is being retracted. Notified the R4DO (Farnholtz) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-11-16
51519 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-11-04 14:30 | 2015-11-06 17:14 | 2015-11-06 | AGREEMENT STATE REPORT - HAIRLINE CRACK FOUND IN HOUSING OF A BERTHOLD LEVEL DENSITY GAUGE The following report was received from the State of Louisiana via email: "On 11/04/2015, the ARSO [Assistant Radiation Safety Officer] for [the licensee] called the LA DEQ [Louisiana Department of Environment Quality] about a hairline crack on the housing of a Berthold level density gauge. The crack was noticed when the annual operational inspections were being performed. The level gauges are required to be inspected by Condition Number 6 of the licensee's radioactive material license. "The [gauge is located] in Geismar, LA within the secure boundary the licensee's chemical plant. "The fixed gauge is installed on a hopper/drum, but the gauge has not been used as a qc/qa [quality control/quality assurance] device since March 21, 2003, when the device was locked-out. The crack or hairline crack was not detected or documented before the November 2015 annual inspections. The notification to LA DEQ is required by Condition Number 6 of the license. The gauge remained installed on the hopper since 2003, but was not functioning as a gauge during that time. "LA DEQ was notified on November 4, 2015, at approximately 1430 CST, that during [the licensee's] annual operational inspections, they detected a hairline crack in the housing of an installed locked-out density measuring device (gauge). The device was a Berthold gauge Model LB 7440D loaded with approximately 60 mCi of Cs-137. "On 11/04/2015, the licensee's ARSO called LA DEQ to make a preliminary report about a hairline crack found in a gauge housing/source holder. The crack was at the union of the gauge shielding and the mounting plate of the device. "[A contract company] has been contacted to provide services at [the licensee' facility], for packaging the source to be shipped and for the source disposal. This will be the 'corrective action' and it was speculated the crack possibly happened due to the vibration of the hopper. The source or device is not leaking. The source is not exposed or removed from the shielded position. This appears to be reportable under 10 CFR 31.5(c)(5). The source was not being used/operational when the crack was detected. "There is no possible exposure to the plant workers because the gauge is still installed on an elevated process. Surveys were taken of the source/gauge housing and they were in the same range as before noticing the crack. The exposure level is approximately 150 mR/hr. The gauge has been locked-out since March 20, 2003. The shutter remains closed and the gauge does not cause a safety hazard to the plant personnel. The gauge operated in the open direction without a problem. [The ARSO] called and reported the incident to comply with Condition Number 6 of [licensee's] Radioactive Material License. The gauge is a Berthold, model #LB-7440D [originally] loaded with approximately 100 mCi of Cs-137 and received and installed in 1992. The SN for the source is 3029-9-90. The corrective action will be disposal by [the contractor]. The Department [LA DEQ] considers this item OPEN until the disposal. The records will be reviewed during a site visit and the next inspection." Louisiana Event Report ID No.: LA 15-0020, T167164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-11-16
51518 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-11-06 11:38 | 2015-11-06 14:08 | 2015-11-06 | OFFSITE NOTIFICATION DUE TO DECEASED AMERICAN CROCODILE "This 4-hour Non-Emergency notification to the NRC is being made based on notifications to other government agencies per 10 CFR 50.72(b)(2)(xi). "On November 6, 2015, at approximately 1138 EST, notification of a deceased American Crocodile discovered in the Owner Controlled Area was made to state and federal agencies. The crocodile's death was not caused by facility operations. The U.S. Fish and Wildlife Service, and the Florida Fish and Wildlife Conservation Commission were notified. "The licensee notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-11-06
51517 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-09-02 | 2015-11-05 12:53 | 2015-11-05 | AGREEMENT STATE REPORT - MISSING EXIT SIGNS The following was received from the State of Colorado via email: "After no response from the annual mailing to register active general licensee's in our radioactive materials unit, a public record search was conducted to discover the owner of the property. Research disclosed from county records the homeowner's name and contact address. He was mailed a letter on 9/2/15. The exit signs were from the manufacturer Isolite Corporation. Isolite provided Glasco Electric, 700 W Mississippi Avenue Denver, CO 80223, the exit signs that were designated to be used at 5744 N 71st Street, Longmont, CO 80223. The two (2) exit signs were model # 2040-50G-20WH, activity 11.5 Ci, serial numbers were not recorded on the manufacturers quarterly report dated 10/1/2001 to 12/31/2001. "A response was received from the home owner. He provided the following information: The Association for Community Living occupied 5744 N 71st Street, in Longmont, CO 80503 at the time the exit signs were shipped. According to the historical information, the building was used as a school for the developmentally disabled. The school closed and the property was sold in 2013. The new owner began renovation of the property and removed the exit signs. The owner reported local city codes requires all deconstruction materials to be recycled. He took the exit signs to The Center for Resource Conservation located in Boulder, CO during the calendar year of 2014. The home owner was unaware of any regulations pertaining to the use or disposal of Tritium exit signs. "The Center for Resource Conservation was contacted 11/4/15 to inquire about the exit signs possibly being at the location 6400 Arapahoe Road, Boulder, CO 80303. Management explained upon materials being dropped off the donor is given a receipt for the donation showing items donated. When large boxes are inspected smaller items may not get noticed and slip through the donation lane. Items are separated and maybe placed in a recycling roll off to be picked up by Evraz located in Denver, CO. It is unknown when they would have accepted the exit signs in 2014. It is unknown if the exit signs were resold or scrapped. No further information is available." Event Report ID No.: CO15-I15-29 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-11-13
51516 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-11-05 10:00 | 2015-11-05 10:32 | 2015-11-05 | INTEGRATED PLANT COMPUTER SYSTEM REMOVED FROM SERVICE "On November 5, 2015 at approximately 1000 EST, the Fermi 2 Integrated Plant Computer System (IPCS) was removed from service for planned maintenance on the Uninterruptible Power Supply (UPS) vital bus power supply. The Safety Parameter Display System (SPDS) resides on the IPCS platform and will be out of service and unavailable to Emergency Response Facilities (ERFs) during the time that IPCS is removed from service. The duration of work is expected to be approximately 48 hours. During this time dose assessment (Raddose) capability will only be available in the manual data input mode. The majority of the Control Room indications remain available to the plant staff and will be used for emergency response, if needed. Information will be communicated to the NRC using other available communication systems as needed. A follow-up notification will be submitted when the IPCS is completely restored, including SPDS to the Operational Support Center, the Technical Support Center, and alternate facilities. The plant is currently in Mode 5, and will remain in Mode 5, for the duration of the IPCS and SPDS unavailability. This 8-hour non-emergency notification is being made per the requirements of 10 CFR 50.72(b)(3)(xiii), as an event that results in a major loss of emergency assessment capability, as described in NEI 13-01. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-05
51515 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-11-04 21:12 | 2015-11-05 00:49 | 2015-11-05 | INFORMATION ONLY - UNIT 4 TECHNICAL SPECIFICATION ENTRY DUE TO LOSS OF UNIT 3 STARTUP TRANSFORMER DURING UNIT 3 OUTAGE "This is a non-emergency, information only notification to the NRCOC. Plant conditions are as follows: Unit 3 is de-fueled and Unit 4 is in Mode 1 [At 100 percent power]. The Unit 3 Startup transformer is INOPERABLE due to preplanned maintenance. The 3B Emergency Diesel Generator (EDG) became INOPERABLE due to loss of all 480V vital AC load centers on Unit 3. "With Unit 4 in Mode 1, Technical Specification [TS] 3.8.1.1.c requires a 4-hour report to the NRC due to inoperability of 1 of 3 required EDGs onsite, concurrent with inoperability of a required Startup transformer. This report is for informational purposes only and is not required by 10CFR50.72/73. "Spent Fuel Pool Cooling at Unit 3 remains available via 3B SFP Cooling Pump which is powered from Unit 4." The loss of the Unit 3 480V AC load centers is still under investigation. TS 3.8.1.1.c requires Unit 4 to exit the TS action statement in 2 hours or shutdown. To exit this TS, no two battery chargers may be powered from the same motor control center. The 480V vital AC load centers for Unit 3 must be restored since Unit 4 requires at least one train from Unit 3 480V AC load centers. The licensee is in the process of performing those actions. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2015-11-05
51514 | 0 | ZION |  |  |  | ISFSI | 2015-11-04 16:20 | 2015-11-04 18:28 | 2015-11-04 | OFFSITE NOTIFICATION MADE DUE TO TRANSFORMER LEAK "Discovery of a PCB [Polychlorinated Biphenyls] leak on a 440 gallon deenergized transformer. Leak was approximately 0.5 gallons (3-5 lbs of PCB). [The leak was] contained onsite within unit 2, 617 turbine building. Contractor clean-up [is] enroute. No personnel injury or exposure. No offsite release. "[The licensee] contacted IEMA [Illinois Emergency Management Agency], National Response Center, and the local emergency planning center." The licensee has notified the NRC Inspector. Notified FEMA, USDA, HHS, DOE, and EPA EOC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OFFSITE NOTIFICATION | [9 empty] | NON EMERGENCY | 3 | IL | ISF |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-11-04
51513 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-11-04 11:33 | 2015-11-04 11:56 | 2015-11-04 | FIRE ON THE 'A' EMERGENCY DIESEL GENERATOR At 1133 EST on 11/4/15, an Alert was declared due to a fire in the 'A' Emergency Diesel Generator (EDG) enclosure. Fire caused damage to the safety related EDG and was declared inoperable. The fire is out, and off-site assistance was not necessary. A fire watch has been stationed, and no personnel injuries were reported. The licensee has notified the NRC Resident Inspector. Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). * * * UPDATE ON 11/4/15 AT 1449 EST FROM HERB SEARLE TO DONG PARK * * * At 1446 EST on 11/4/15, Millstone Unit 3 terminated the Alert declaration following satisfactory atmospheric samples at the site boundary and notifying the State of Connecticut. The licensee will notify the NRC Resident Inspector. Notified R1DO (Rogge), NRR EO (Morris), and IRD (Grant). Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Power Operation; FMode3: Power Operation | ALERT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-11-04
51512 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-09-22 16:09 | 2015-11-03 16:19 | 2015-11-03 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE EXCEEDED TECHNICAL SPECIFICATION ALLOWED VALUE "On September 22, 2015, with James A. Fitzpatrick Nuclear Power Plant operating at 100 percent power, the Emergency and Plant Information Computer (EPIC) indicated a spike in Secondary Containment differential pressure during performance of a surveillance test associated with automatic initiation of the Standby Gas Treatment System. Plant data systems recorded Secondary Containment differential pressure exceeding the Technical Specification allowed value. The Secondary Containment differential pressure was at or above zero inches of water for approximately ten (10) seconds, and then immediately trended negative following auto-start of one of the trains of Standby Gas Treatment. An operator was subsequently dispatched to the ventilation control panel, and verified that Secondary Containment differential pressure was more negative than the Technical Specification allowed value. "This condition was entered into the Corrective Action Program, and subsequently, it was determined that the approximate ten second duration that Secondary Containment differential pressure was greater than the Technical Specification allowed value was reportable pursuant to 10 CFR 50.72(b)(3)(v)(C), as an event or condition that could have prevented fulfillment of a safety function. Secondary Containment was Operable following reestablishment of greater than or equal to 0.25 inches of water vacuum, and remains Operable." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-11-03
51511 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-10-30 | 2015-11-02 10:34 | 2015-11-02 | UNDERDOSE DUE TO MALFUNCTION OF THE DOSE DELIVERY SYSTEM The following was received via email: "During the administration of an yttrium-90 SIR Spheresr procedure, a portion of the dose began to leak out of the top of the vial containing the activity. To prevent contamination of the interventional radiographic suite, the medical physicist and authorized user aborted the administration. It is estimated that only 10 - 20% of the dose noted on the written directive was actually delivered to the patient. The patient and radiation safety officer were notified immediately following the cancellation of the administration and the patient has agreed to be treated again in the near future. Knowing the exact administered activity is nearly impossible given the characteristics of the procedure and radiopharmaceutical. No harm is expected to the patient. "The event seems to be due to a malfunction of the dose delivery system. It appeared to the interventional radiologist that the leak was located at the top of the dose vial and likely at the original puncture site of the radiopharmacy upon preparation of the dose for administration." Event Report # PA150028 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-11-10
51510 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2015-11-02 09:20 | 2015-11-02 09:20 | 2016-01-08 | LOSS OF RADIATION MONITORING EQUIPMENT DUE TO PLANNED MAINTENANCE "A planned modification at Calvert Cliffs Nuclear Power Plant will remove the Spent Fuel Pool Area Radiation Monitoring system from service. The planned out of service window is expected to be 7 weeks, beginning 11/02/15 and ending 12/18/2015. During this time portable radiation monitors will be installed as compensatory measures to monitor and support timely and accurate EAL declarations. Affected Emergency Response Organization personnel have been made aware of the compensatory measures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to a planned event that affects Emergency Preparedness Assessment Capability for greater than 72 hours. An update will be provided once the Spent Fuel Pool Area Radiation Monitoring system is restored to normal operation." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1616 EST ON 12/18/2015 FROM BRIAN HAYDEN TO MARK ABRAMOVITZ * * * "This is concerning the planned modification to Calvert Cliffs Nuclear Power Plant Spent Fuel Area Radiation Monitoring System. The modification window is extended to January 8, 2016. Compensatory measures that were put in place on November 2, 2015 will continue to be in effect until the completion of the modification testing and the new equipment is fully in service." The licensee notified the NRC Resident Inspector. Notified R1DO (Ferdas). * * * UPDATE FROM TIM HUBER TO JEFF ROTTON AT 1547 EST ON 01/08/2016 * * * "This is concerning the planned modification to Calvert Cliffs Nuclear Power Plant Spent Fuel Area Radiation Monitoring System. The modification window was originally extended to January 8, 2016 as updated on December 18, 2015. Based on field equipment issues during the installation process, the modification window has been extended to February 12, 2016. Compensatory measures that were put in place on November 2, 2015 will continue to be in effect until the completion of the modification testing and the new equipment is fully in service." The licensee notified the NRC Resident Inspector. Notified R1DO (Dimitriadis). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-11-02
51509 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-10-30 14:29 | 2015-10-30 17:38 | 2015-10-30 | OFFSITE NOTIFICATION DUE TO LOSS OF LIFT STATION POWER "At 1429 CDT, Dresden Nuclear Power Station (DNPS) notified the Illinois Environmental Protection Agency (IEPA) of an upset condition involving the loss of power to the DNPS lift station. The lift station power was lost at approximately 1350 CDT, and in response, DNPS entered abnormal operating procedures to limit hot canal levels. Power was restored to the lift station at approximately 1500 CDT. There was no impact to the health and safety of the public or to the environment. "The NRC Resident Inspector has been notified." | 0 | 89 | 100 | 0 | 89 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-10-30
51508 | 0 | TEXAS A&M UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2015-10-30 12:42 | 2015-10-30 13:53 | 2015-10-30 | NOTIFICATION OF UNUSUAL EVENT DUE TO A TORNADO WARNING ON TEXAS A&M CAMPUS At 1250 CDT, a Notification of Unusual Event was declared at the Texas A&M Nuclear Science Center due to a tornado warning on the Texas A&M Campus. The reactor was secured and Science Center staff were evacuated to their designated tornado shelter in the facility. There is no risk to public health and safety. The tornado warning is in effect until 1345 CDT. * * * UPDATE FROM JERRY NEWHOUSE TO HOWIE CROUCH AT 1735 EDT ON 10/30/15 * * * At 1342 CDT, the tornado warning was terminated. The licensee conducted a facility walkdown and did not observe any damage to the facility. At 1400 CDT, the Notification of Unusual Event was terminated. The licensee notified their NRC Project Manager (Hardesty). Notified NRR (Reed), NRR EO (Howe), IRD (Gott), DHS SWO, FEMA Ops, DHS NICC, Nuclear SSA (email) and FEMA Watch Center (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 0 | TX | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-10-30
51507 | 0 | CB&I |  |  |  |  | 2015-05-05 | 2015-10-29 15:33 | 2015-10-29 | PART 21 REPORT - DEFECT ASSOCIATED WITH PRESSURIZER INSTRUMENTATION PIPING PENETRATION IN MODULE FOR VOGTLE UNIT 3 The following information was excerpted from an email received from CB&I: "This letter provides a report in accordance with 10 CFR 21.21 pertaining to the identification of a defect associated with a structural module piping penetration for the Vogtle Unit 3 AP1000 project. The defect is associated with a Pressurizer instrumentation piping penetration in structural module CA01 for Vogtle Unit 3. "This condition was previously identified by interim report letters dated July 1, 2015, and September 2, 2015. "The discovery date of these deviations is based on the date of the associated CB&I Power Inspection Report (IR). That IR was initiated on May 5, 2015. Interim Part 21 reports dated July 1, 2015, and September 2, 2015, were submitted to the NRC that state the evaluation of this condition was expected to be completed by October 30, 2015. The interim reports were identified as Accession Nos. ML15254A043 and ML15201A130, and Log Nos. 2015-50-01 and 2015-50-00, on the NRC 'Part 21 Reports' website. "Name and address of the individual or individuals informing the Commission: Don DePierro CB&I Power 128 S. Tryon St., Suite 1000 Charlotte, NC 28202" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-10-29
51506 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-10-29 03:48 | 2015-10-29 10:38 | 2015-10-29 | ACTUATION OF THE AUXILIARY FEEDWATER SYSTEM DUE TO MAIN TRANSFORMER LOCKOUT "At 0348 CDT, while Point Beach Unit 2 was performing outage activities, it experienced a Main Power Transformer lockout and associated loss of busses (2A-01, 2A-02, 2B-01 and 2B-02). The loss of the two non-vital 4160 V buses resulted in actuation of the Unit 2 undervoltage logic which resulted in actuation of the Auxiliary Feedwater System. The Auxiliary Feedwater System functioned normally upon actuation. "This condition was determined to be reportable per 10CFR50.72(b)(3)(iv)(A)(6), PWR auxiliary or emergency feedwater system actuation. "This event did not affect the operating Unit 1. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-10-29
51505 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2015-09-09 21:03 | 2015-10-28 13:26 | 2015-10-28 | INVALID ACTUATION OF A GENERAL CONTAINMENT ISOLATION SIGNAL AFFECTING MORE THAN ONE SYSTEM "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe invalid actuation containment isolation signals affecting containment isolation valves in more than one system. "On September 9, 2015 at 2103 hours Eastern Daylight Time (EDT), Unit 1 experienced a loss of electrical power to motor control center 1CB when the substation E6 feeder breaker tripped. The loss of power resulted in closure of primary containment isolation valves (PCIVs) in Unit 1 Primary Containment Isolation System (PCIS) Group 2 (i.e. Drywell Equipment and Floor Drains, Residual Heat Removal (RHR) Discharge to Radwaste, RHR Process Sample, and Traversing lncore Probe), Group 3 (i.e., Reactor Water Cleanup), and Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems). It has been determined that affected PCIVs appropriately closed. However, the limit switch within the motor operator of the inboard RWCU PCIV (i.e. 1-G31-F001) malfunctioned; resulting in an inaccurate remote position indication. Testing has confirmed that 1-G31-F001 properly closed and can perform its intended safety function. "These PCIV isolations were the result of a substation E6 feeder breaker trip to motor control center 1CB and not in response to actual plant conditions (i.e., to mitigate the consequences of an event) and, therefore, were invalid. "This event did not result in any adverse impact to the health and safety of the public." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-10-28
51504 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-10-28 06:28 | 2015-10-28 13:26 | 2015-10-28 | BOTH TRAINS OF CONTROL ROOM EMERGENCY AIR CONDITIONING SYSTEM INOPERABLE "At 0628 [EDT] on 10/28/15, the Salem Unit 1 Control Room Emergency Air Conditioning System (CREACS) train was declared inoperable due to the results of charcoal filter testing not meeting the surveillance requirement. Prior to declaring the Unit 1 train inoperable, the system was operating in the single train filtration operation mode due to refueling outage activities being performed on Unit 2 with the Unit 2 CREACS train inoperable. This resulted in both units' CREACS trains being inoperable. "Prior to the event on 10/28/15, Salem Unit 1 was operating in Mode 1 at 100% power and Unit 2 was in Mode 6 with fuel movement in progress. "At 0628, Unit 1 entered Technical Specification 3.0.3, and Unit 2 suspended fuel movement to comply with Technical Specification 3.7.6 (Modes 5 and 6, or during movement of irradiated fuel assemblies), action c. The Unit 2 train was placed in service at 0755, allowing Unit 1 to exit Technical Specification 3.0.3. Operators continued to align the Unit 2 CREACS to single train filtration operation to comply with Unit 1 Technical Specification Action Statement 3.7.6.1, Action a. Actions to place the Unit 2 CREACS in single train filtration operation were completed at 0950. "This 8 hour notification is being made pursuant to the requirements of 10 CFR 50.72(b)(3)(v) for 'any condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to : (D) Mitigate the consequences of an accident.'" The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-10-28
51503 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-10-27 15:57 | 2015-10-27 19:48 | 2015-10-27 | SAFEGUARDS REPORT - UNAUTHORIZED ACCESS Discovered vulnerability in a safeguards system that allowed unauthorized access to the protected area and vital area for which compensatory measures have not been employed. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-10-27
51502 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-10-27 10:30 | 2015-10-27 17:50 | 2015-10-29 | TSC AIR FILTRATION SYSTEM DEGRADED "A planned surveillance was started on the Quad Cities Station Technical Support Center (TSC) ventilation air filtration system. The surveillance measures the flow rate through the air filtration unit and verifies the TSC is pressurized to ensure habitability requirements. The flow rate obtained was high, outside of acceptance criteria, and the surveillance was stopped pending resolution. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing procedures. If TSC evacuation is warranted due to radiological conditions, the facility will be relocated in accordance with existing procedures. "This event is reportable per 10CFR50.72(b)(3)(xiii) since the air filtration unit affects an emergency response facility. "The NRC Resident Inspector has been notified." * * * UPDATE FROM CLIFFORD STEINER TO HOWIE CROUCH AT 1315 EDT ON 10/29/15 * * * "The TSC Air Filtration system was successfully tested on 10/27/15 at 2100 CDT." The licensee notified the NRC Resident Inspector. Notified R3DO (Stoedter). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-10-27
51501 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-10-26 09:29 | 2015-10-27 13:46 | 2015-10-27 | AGREEMENT STATE REPORT - POTENTIAL SECURITY INCIDENT - SUSPICIOUS EMAIL The following information was received via email: "TDEC [Tennessee Department of Environment and Conservation] was notified on 10/27/15 by the Radiation Safety Officer at St. Jude Children's Research Hospital of a suspicious e-mail received concerning the purchase of an irradiator. The sender did work with St. Jude Immunology department until July 2015. However, identity could not be verified since the e-mail appears to originate from China. The originator's e-mail address does not show any organizational affiliation nor did the individual have a history of working with irradiators at St. Jude." The FBI Field Office in Memphis, TN was notified. State Event Report ID Number: TN-15-154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 1 | 2015-11-04
51500 | 0 | ACUREN INSPECTION - WIT PIPELINE |  |  |  |  | 2015-06-18 23:30 | 2015-10-27 07:07 | 2015-10-27 | ATTEMPTED FORCED ENTRY TO RADIOGRAPHY DARKROOM TRUCK "On June 18th 2015 at approximately 1130 EDT while parked at a Hawthorn Suites in Meriden, Ct., an attempted breech of a darkroom containing a Sentinel Delta 880 Device Serial # D3582, with a model A424-9 Ir-192 source serial #17586G (100 curies). Operator 1 and Operator 2 were sitting on the back patio of the hotel when they heard the alarm chirp twice on a darkroom unit. Operator 1 ran to the unit to make sure everything was okay. When he got to the side of the darkroom he looked around the back and saw a black male standing on the bumper of unit # 1620 [truck] trying to break in with a screw driver. Operator 1 yelled for Operator 2 that someone was trying to break into the darkroom. The burglar was scared off, then the burglar came back to retrieve his budget rental van and he sped off. The Meriden Police Department was immediately contacted and dispatched to the scene, Officer took all statements and the police report # 15-004841 was filed. Unit was checked to make sure that security of all locks and that the alarm system was still operable. "(RSO) was made aware of this attempted breech on 10/26/2015 at 5:03 pm by NRC auditor." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | ACT/ATTEMPT THEFT CAT 1/2 RAD MATL | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 37.57(a) |  |  |  | 0 | 2015-11-04
51499 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-10-26 | 2015-10-26 19:38 | 2015-10-26 | NUCLEAR DENSITY GAUGE POTENTIALLY DAMAGED DURING SHIPMENT The following report was provided by the Louisiana Department of Environmental Quality via email: "On 10/26/2015, [The] RSO [Radiation Safety Officer] / Technical Service Manager for QSA Global notified the LDEQ [Louisiana Department of Environmental Quality] about an incident where a [common carrier] delivered a device containing radioactive material to their facility on Langley Dr., Baton Rouge, LA. When the receipt surveys were being performed, they noticed at one point on the surface they had a reading of 2 R/hr at the surface. It appears that one or more of the pull ties used to secure the shutters on the device broke causing a shift in the shielding. Part of the bracing material minimized the shielding shift. "The device in question is a Texas Nuclear level/density gauge, Model # 5210, SN B1110, loaded with [approximately] 733 mCi of Co-60 sealed source. The origin of the shipment was Puerto Ordaz, EDO Bolivar, Venezuela. It came stateside via [common carrier] to Houston, TX and then to the QSA Global facility in Baton Rouge, LA by [common carrier]. The shipment arrived [at approximately] 1145 [CDT] on 10/26/2015. The activity is below Cat 2 quantities at [approximately] 733 mCi of Co-60. "The device was surveyed and moved to a bunker on the QSA Global site. Re-enactments and calculations will be conducted on 10/27/2015 AM when [the RSO] is present. The LDEQ personnel will be on site for the measurements, calculations and follow-up information [dissemination]. "This is a preliminary notification of an incident reported to LDEQ [at approximately] 1530 [CDT]. After the source was secure, safe and locked in a bunker at the QSA Global Baton Rouge, LA facility. Possible exposure calculations will be determined from the reconstruction of events. "The Baton Rouge facility is compliant for the IC [Increased controls] principles and Radiation Safety procedures/aspects for the receipt activities. The Department, LDEQ personnel will be on site for the corrective actions and calculations. The NRC, Region IV, was made aware of this situation on 10/26/2015. Follow-up information will be [disseminated] when available. "This is being reported as a preventive and protection action under 10 CFR Part 30.50(a). "Information will be updated when available. LDEQ considers this incident still open." Event Report ID No.: LA-150019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-11-03
51498 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-10-26 07:03 | 2015-10-26 15:20 | 2015-11-30 | UNANALYZED CONDITION ASSOCIATED WITH A HIGH ENERGY LINE BREAK "At 0703 CDT on 10/26/2015, Prairie Island Nuclear Generating Plant (PINGP) identified Door 62, '11/21 Auxiliary Feedwater Pump (AFW) Room to 12/22 AFW Pump Room' to be in a closed position. Door 62 functions as a fire door, and closes in the event of a fire in either A or B Train AFW Pump Rooms. When Unit 1 or Unit 2 is in modes 1-4, Door 62 is required to remain open in the event of an internal flood in AFW Pump Room or a Turbine Building High Energy Line Break (HELB) Flood into the AFW Pump. Currently, Unit 2 is in MODE 6, so only the Unit 1 Turbine Building HELB applies. Door 62 is normally open with a fusible link to allow closure during a fire. "Door 62 was closed during maintenance. With the door closed the Unit 1 side of the Auxiliary Feedwater Pump Room lost its ability to adequately drain water in a Unit 1 HELB event and was in an unanalyzed condition. Upon discovery, Door 62 was immediately repositioned to be open per the analyzed condition and a fire watch established per plant procedure. "This notification is being conducted in accordance with 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition. "The plant remains safe, and this condition does not pose any additional risk to the public. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION FROM NATHAN BIBUS TO DONALD NORWOOD AT 1703 EST ON 11/30/2015 * * * "Prairie Island Nuclear Generating Plant is retracting this event notification, EN# 51498. "Further analysis determined that the closure of Door 62 would not have prevented the structures, systems and components (SSC) located in the AFW Pump rooms, or SSCs powered from Motor Control Centers (MCCs) located in the AFW Pump rooms, from performing their safety functions. This is because the door closure would not have caused water level to rise above the maximum tolerable water height during any design basis flooding event. The acceptance criteria of the area flooding calculations were still met with Door 62 closed. "Therefore, the Unit 1 side of the AFW Pump room did not lose its ability to adequately drain water in a Unit 1 HELB event, this event was not an 8-hour notification for an Unanalyzed Condition that significantly degrades plant safety, under 10CFR50.72(b)(3)(ii). "The licensee has notified the NRC Resident Inspector." Notified R3DO (Lipa). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-10-26
51497 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-10-24 06:57 | 2015-10-24 11:45 | 2015-10-26 | OFFSITE NOTIFICATION FOR ONSITE INCIDENT OF LOCAL INTEREST Prairie Island Nuclear Generating Plant (PINGP) notified Local Law Enforcement Agency and the Prairie Island Community Tribal Council due to an incident onsite of local interest. "This notification is being conducted in accordance with 10 CFR 50.72(b)(2)(xi) for notification to an outside government agency. "The plant remains safe, and this condition does not pose any additional risk to the public. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-10-26
51496 | 0 | CRANE NUCLEAR, INC. |  |  |  |  | 2015-08-26 | 2015-10-23 18:28 | 2015-10-23 | PART 21 REPORT - PRESSURE SEAL VALVE NONCOMPLIANCE The following is a summary of a submitted facsimile: "Pressure Seal Valve orders may potentially have misclassified material and non-destructive examination requirements for segment ring designs. "Crane Nuclear 'Classification of Valve Parts', Procedure 03-107, provides guidance for appropriate material and NDE [Non Destructive Test] requirements for processing valve and valve part orders. The procedure is based on the ASME Code Case N-62, which is ASME B&PV Section Ill, 2015 Edition, Non-Mandatory Appendix HH 'Rules for Valve Internal and External Items'. "A pressure seal valve segment ring requires the material to be purchased Safety Related, ASME B&PV Section II, Part D materials, and required NDE (reference Category 3 valve items per N-62). A segment ring may have been processed to material requirements not as pressure retaining material per NX-2000 of the Code resulting in the incorrect material specification and non-destructive examination specified. "Limited to (1) CNI [Crane Nuclear, INC.] SO# 069000408, Dominion, Millstone. P.O. 954282 and Purchase Req. No. N90136-01- Quantity shipped = 1, Crane, 8'', Fig. 55009-12CF8M-WE, Class 900, ASME Class 1, 1986 Ed. "Should you have any questions regarding this matter, please contact Jason Klein, Engineering Manager at (630) 226-4953 or Rosalie Nava, Director of Safety and Quality at (630) 226-4940" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-10-23
51495 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2015-08-26 | 2015-10-23 17:00 | 2015-10-23 | PART 21 REPORT - SPEED SWITCH CAPACITOR FAILURE The following is a summary of a submitted facsimile: "Engine Systems Inc. (ESI) began a 10 CFR 21 evaluation on August 26, 2015 upon notification by Harris Nuclear Plant of a ground fault condition after installing two speed switches, P/N ESI50267B, supplied by ESI. Subsequent investigation revealed the condition was due to a failed capacitor installed across the relay output to ground within each speed switch. The evaluation was concluded on October 22, 2015 and it was determined that this issue is a reportable defect as defined by 10 CFR Part 21 . The speed switch output contacts are utilized in the engine's start circuitry and failure of the contacts to function properly could adversely affect the safety-related operation of the emergency diesel generator set. "This issue only affects one part number (qty 6) supplied on one customer purchase order: ESI Sales Order: 3013958 Part Number: ESI50267B Customer: Duke Energy Progress - Harris Nuclear Plant Customer P.O.: 00763117 ESI Serial Numbers: 3013598-1.1-1, 3013598-1.1-2, 3013598-1.1-3, 3013598-1.1-4, 3013598-1.1-5, 3013598-1.1-6 C of C Date: April 10, 2015 "Point of Contact: Tom Horner, Quality Assurance Manager, Engine Systems, Inc., phone (252) 977-2720" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-10-23
51494 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2015-09-02 | 2015-10-23 16:53 | 2015-11-05 | PART-21 REPORT - CLOSED SWITCH NOT ACTUATING WHEN VALVE IS FULLY CLOSED The following is a summary of a submitted facsimile: "Items subject to this Fisher Information Notice (FIN) were provided to Catawba Nuclear Station (CNS) per CNS Order 00178457 (Fisher Order Number 033-D800306145). Specifically, Fisher supplied an 8 inch Design A11 Butterfly Valve with a Type 1052 Actuator and TopWorx Switches, serial number F000458892 ('Equipment'). The issue is with the closed switch not actuating when the valve is fully closed. "The purpose of this FIN is to alert CNS that as of 2 September 2015, Fisher Controls International LLC (Fisher) became aware of a situation which may affect the performance of the Equipment, including its safety-related function. "If there are any technical questions or concerns, please contact: Ben Ahrens, Quality Manager, Emerson Process Management, Fisher Controls International LLC, 301 South 1st Avenue, Marshalltown, La 50158, Phone: (641) 754-2249, benjamin.ahrens@emerson.com" * * * UPDATE ON 11/5/15 AT 1731 EST FROM CHAD ENGLE TO DONG PARK * * * The following is a summary of a submitted facsimile: "The purpose of this document is to correct an erroneous serial number on FIN 2015-03, dated 22 October 2015." Serial number F000458892 should read F000503836. Notified R2DO (Desai) and PART 21/50.55 REACTORS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | CONSTRUCT DEFICIENCY | [8 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) | 50.55(e) |  |  | 0 | 2015-10-23
51493 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-10-16 12:00 | 2015-10-23 13:06 | 2015-10-23 | AGREEMENT STATE REPORT - PATIENT DOSED WITH WRONG ORGAN UPTAKE TAG The following information was received from the state of Louisiana via email: "On October 19, 2015, the Radiology/Nuclear Medicine Manager, reported that on October 16, 2015 at 1200 hours, a PRN Licensed Nuclear Medicine Tech inadvertently dosed a patient with 25 mCi of Tc-99-MDP. The error was detected shortly after administration. The patient had physician's orders to have a cardiac scan utilizing 25 mCi of Tc-99-Tetrofosmin. The isotope activity was correct. However, the organ uptake tag was incorrect. "The error resulted from the Nuclear Medicine Tech not using the patient two identifiers before administering the unit dose. The activity was correct for the unit dose, but the organ uptake tag was different. "The facility employees were off and a PRN Tech was filling-in on that Friday. This Tech is used at the facility frequently when an essential employee is absent. He is no stranger to the work environment of the Facility/Licensee. "The source was a 25 mCi Tc-99 unit dose. He performed the receipt procedures, unit dose assay, and utilized procedures to administer the isotope, but did not cross-reference the name on the unit dose with the individual who received the injection. "This site is a Medical Institution. The unit doses are kept in a locked 'HOT' lab in the Nuclear Medicine Department. KLS Physics Consultants was called in the help with the reporting requirements. "The Tech was counselled and retrained in the facility's procedures for patient identification and administration of radioactive materials for human in vivo imaging. "The patient will receive the correct unit dose and scan, 25 mCi Tc-99-Tetrofosmin, for a cardiac scan at a later date." Event Report ID No.: LA-150018, T166800 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-11-02
51492 | 0 | WATERFORD | 3 |  |  | [3] CE | 2015-10-23 | 2015-10-23 12:04 | 2015-10-23 | PART 21 - WESTINGHOUSE TYPE KIR-60 CURRENT TRANSFORMER The following is excerpted from LER 2015-007 submitted by the licensee (see related EN #51348): "On October 9, 2015, Waterford 3 received information from the external evaluation concerning the Generator Differential Current Transformer. The evaluation concluded that a manufacturing defect internal to the current transformer was the cause of the failure. On October 22, 2015, engineering evaluation determined the manufacturing defect could create a substantial safety hazard, as defined in 10 CFR 21, and provided the site vice president information of the defect the same day. Additional information identified in the report is as follows: "Constructor - Westinghouse Type KIR-60 current transformer, style 7524A01G16, serial number 28218571; Defect and safety hazard - There were voids found in the insulation, and the thickness of the insulation material around the fault area appeared reduced when compared to the other areas of the current transformer. There is only one transformer of this type remaining installed in the plant. Scheduled replacement is no later than November 15, 2015." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2015-10-23
51491 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2015-10-23 05:23 | 2015-10-23 06:21 | 2015-10-23 | CONTRABAND FOUND DURING SEARCH AT PLANT ENTRANCE Attempted introduction of contraband into the protected area. The licensee will be notifying the NRC Resident Inspector. * * * RETRACTION AT 1044 EDT ON 10/23/2015 FROM DON CRISP TO MARK ABRAMOVITZ * * * The contraband was found during the search process and did not enter the protected area. There was no malevolent intent. Notified the R1DO (Gray), ILTAB (Whitney) and Part 73.71 Safeguards group. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-10-23
51490 | -1 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2015-10-22 18:25 | 2015-10-22 19:20 | 2015-10-22 | SAFEGUARDS SYSTEM DEGRADATION Attempted introduction of contraband into protected area. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 10/22/15 AT 2133 EDT FROM MICHAEL MOORE TO DONG PARK * * * The event notification was retracted after an investigation determined no malevolent intent. The licensee has notified the NRC Resident Inspector. Notified R2DO (Blamey), ILTAB (Whitney), and IRD (Stapleton). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-10-22
51489 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-10-22 09:58 | 2015-10-22 10:37 | 2015-10-22 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to monitoring and detection of protected area boundary. Compensatory actions taken. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-10-22
51488 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-10-22 08:45 | 2015-10-22 09:04 | 2015-10-22 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to monitoring and detection of protected area boundary. Compensatory actions taken. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-10-22
51487 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2015-10-21 13:50 | 2015-10-21 18:33 | 2015-10-21 | UNANALYZED CONDITION DUE TO PRESSURIZER HEATER BANK POTENTIAL CIRCUIT FAILURE VULNERABILITY "The isolation function when transferring control from the Main Control Room to the Alternate Shutdown Panel (AI-185) for Pressurizer Heater Bank No. 4 (including Groups No. 10, No. 11, and No. 12) has been identified as a potential circuit failure. "Identification of the potential circuit failure vulnerability is for Pressurizer Heater Bank No. 4 when isolated from Alternate Shutdown Panel (AI-185) and operated locally from Motor Control Center (MCC-4C1) for Alternate Shutdown Fire Areas 41 (Cable Spreading Room) and 42 (Main Control Room). "The vulnerability involves an external hot short affecting the conductor connecting to the control room switch which may keep the 94/10 relay energized and defeat MCC control of the heaters. In a postulated event, a fire in the control room could prevent the heaters from energizing when demanded, or cause the heaters to unintentionally energize. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Per National Fire Protection Association (NFPA) 805, fire watch is an adequate compensatory measure. Therefore, this vulnerability has been added to the existing NFPA 805 Fire Protection compensatory measure for Fire Area 41. For Fire Area 42, the Main Control Room is continuously staffed, which has been credited as the compensatory measure. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-10-21
51486 | 0 | EVONIK CORPORATION |  |  |  |  | 2015-10-11 | 2015-10-21 13:08 | 2015-10-21 | LOST TRITIUM EXIT SIGN A tritium exit sign was mistakenly placed in general waste by an employee who was replacing the sign on 10/11/15. The employee reported the mistake on 10/13/15 and the licensee initiated attempts to locate the sign. The sign was determined to have been placed in a general waste container which had already been collected. The manufacture date of the sign was 2/2009 and at the time of the disposal the source was intact. The lost source material (0.426 TBq of Tritium as of 2/2009) is considered unrecoverable. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-10-29
51485 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2015-10-20 14:14 | 2015-10-21 10:03 | 2015-10-21 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2015-10-21
51484 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-10-20 18:00 | 2015-10-20 23:55 | 2015-10-21 | DIESEL GENERATORS STARTED AFTER TRANSMISSION LINE LIGHTNING STRIKES "This report is being made under 10CFR50.72(b)(3)(iv)(A) 'any event or condition that results in a valid actuation of any system listed in paragraph (b)(3)(iv)(B) of this section' due to the automatic start of 'A' and 'B' Standby Diesel Generators. "The automatic start of the Standby Diesel Generators occurred on a valid bus under-voltage condition caused by severe weather (lightning strikes) in the DAEC [Duane Arnold Energy Center] area. The Standby Diesel Generator output breakers did not close onto their respective essential buses. Essential electrical buses remained powered from off-site circuits through their normal power supply transformer, 1X3 Startup Transformer, during and after the event. "The Standby Diesel Generators have been returned to the standby readiness condition. Both credited off-site power circuits were available before the event and remain available after the event." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-10-21
51483 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2015-10-20 20:24 | 2015-10-20 21:06 | 2015-10-20 | UNUSUAL EVENT DUE TO SUSPICIOUS VEHICLE IN OWNER CONTROLLED AREA "Security condition in the Owner Controlled Area outside of the Protected Area. [There is] an unknown vehicle located on the South side of the Intake Canal. The vehicle is locked, the engine is not running, and the parking lights are on. Security is performing an inspection of the vehicle for explosives or other contraband in conjunction with local law enforcement." The Unusual Event was declared based on EAL HU-1. The licensee notified the NRC Resident Inspector. The licensee notified State and local government agencies. Notified (via phone and E-mail): DHS SWO, FEMA Ops Center, and NICC Watch Officer. Notified (via E-mail): FEMA NWC and NuclearSSA. * * * UPDATE FROM WILLIAM RAYBURN TO DONALD NORWOOD AT 2255 EDT ON 10/20/15 * * * "At 2229 EDT, the Unusual Event for a Security Condition at Davis-Besse Nuclear Power Station was terminated. "An inspection of the vehicle in question was performed and it was determined that no threat existed to the site at any time." The licensee notified the NRC Resident Inspector. The licensee notified State and local government agencies. Notified R3DO (Daley), IRD (Stapleton), NRR (Morris) and ILTAB (Tucker). Notified (via phone and E-mail): DHS SWO, FEMA Ops Center, and NICC Watch Officer. Notified (via E-mail): FEMA NWC and NuclearSSA. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-10-20
51482 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-10-20 07:00 | 2015-10-20 16:40 | 2015-10-20 | UTAH AGREEMENT STATE REPORT - SUSPICIOUS ACTIVITY INVOLVING PHYSICAL SECURITY SYSTEM The RSO of MET-CHEM Testing Labs, Inc. contacted the State of Utah, Division of Radiation Control to report an incident involving the installed security system. All radioactive material has been accounted for by the RSO. The State of Utah is sending investigators to the company facility today. * * * UPDATE PROVIDED BY GWYN GALLOWAY TO JEFF ROTTON VIA EMAIL AT 2142 EDT ON 10/20/2015 * * * The following information was provided by the State of Utah via email: "The State of Utah inspectors determined that the activity contained in all of the cameras (in aggregate) stored behind one barrier was less than the quantity found in Table 1 of 10 CFR 37. Therefore, the additional security measures were not required to be implemented. All sources are accounted for and will be secured in accordance with requirements tonight." Notified R4DO (Werner), ILTAB (Tucker) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-10-28
51481 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-10-19 | 2015-10-20 10:24 | 2015-10-20 | TEXAS AGREEMENT STATE REPORT - BROKEN SOURCE OPERATING CABLE The following information was received from the state of Texas via email: "On October 19, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee that the operating cable on a 150 milliCurie Cesium - 137 source used in a Berthold model 21357 nuclear gauge broke during routine operation of the source. The licensee stated the source is stored in the fully shielded position. The licensee stated the source does not create an exposure risk to its personnel or any member of the general public. The licensee has contacted the manufacturer for assistance in repairing the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-10-28
51480 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-08-23 12:42 | 2015-10-19 08:19 | 2015-10-19 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID PRIMARY CONTAINMENT ISOLATION SIGNAL "On 8/23/2015 at 1242 [EDT], with the reactor at 100% power, an invalid RPS MG [Reactor Protection System Motor-Generator] set 'A' trip resulting in a loss of RPS bus 'A'; this occurred during testing of the RPS instrument channels. All equipment operated as designed as a result of the loss of power to the 'A' RPS bus. The invalid trip was determined to be a result of the overvoltage relay being set too low. "The above event meets the reporting criteria of 10CFR50.73(a)(2)(iv)(A) since the loss of RPS bus resulted in primary containment isolation signals affecting containment valves in more than one system. The following systems isolated as a result of the loss of 'A' RPS bus: Reactor Water Cleanup, Reactor Building ventilation, 'A' Containment Atmosphere Dilution, Torus Vent and Purge, Drywell Equipment and Floor Drain Sumps, 'A' Drywell Containment Atmospheric Monitors, Recirculation System Sample Line, Main Steam Line Drains and Residual Heat Removal drain valve to radwaste. 'A' Standby Gas Treatment System started as designed. This notification is being made in accordance with 10CFR50.73(a)(2)(iv)(A) to provide information pertaining to an invalid 'A' Reactor Protection System actuation. "Completed actions were the replacement of overvoltage relay and voltage setpoint change, completed on 9/11/2015. "In accordance with 10CFR50.73(a)(i) a telephone notification is being made instead of submitting a written Licensee Event Report." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-10-19
51479 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2015-10-17 16:13 | 2015-10-17 19:30 | 2015-10-17 | OFFSITE NOTIFICATIONS MADE FOR HAZARDOUS CHEMICAL LEAK "At 1230 EDT, it was discovered that sodium hypochlorite had leaked into the ground soil at the bottom of a leak sensing pit, which is located near the BVPS-1 Cooling Tower Pump House, at the Beaver Valley Power Station Unit Number 1 (BVPS-1). The source of the sodium hypochlorite, is suspected to be from a piping leak, and has been terminated. The cause of the leak has not yet been conclusively determined, and there is no evidence that the sodium hypochlorite reached the surface water of the Ohio River. "At 1613 EDT on October 17, 2015, it was determined that there was CERCLA (Comprehensive Environmental Response Compensation & Liability Act) reportable leak of a minimum 294 gallons of sodium hypochlorite to ground soil, and the following offsite notifications were made starting at 1625 EDT: "National Response Center (Incident Report #1131084); Pennsylvania (PA) Department of Environmental Protection; Beaver County Emergency Management; PA Emergency Management Agency. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-10-17
51478 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-10-16 12:45 | 2015-10-16 15:41 | 2015-10-16 | OFFSITE NOTIFICATION MADE FOR HAZARDOUS CHEMICAL SPILL "At 1115 EDT there was a non-oil chemical spill at the main intake structure during delivery of corrosion inhibitor. The spill occurred due to a failed tank-fill connection. Approximately 10 gallons of the inhibitor reached the Ohio River. The spill has been stopped and contained, and recovery is in progress. This is not a CERCLA (Comprehensive Environmental Response Compensation and Liability Act), Reportable Quantity for the Environmental Protection Agency. However, at 1245 EDT, it was determined to be reportable to the Pennsylvania Department of Environmental Protection (PADEP), in accordance with the Pennsylvania Clean Streams Law and NPDS (National Pollutant Discharge Elimination), permit; thus, a notification was made, to the PADEP, at 1250 hours EDT . "This condition is being reported pursuant to 10 CFR 50.72 (b)(2)(xi). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-10-16
51477 | 0 | US EPA |  |  |  |  | 1983-12-31 | 2015-10-16 14:18 | 2015-10-16 | MISSING TWO GENERAL LICENSE KR-85 AEROSOL NEUTRALIZERS Two TSI Model 3054 Aerosol Neutralizers containing 10 mCi Kr-85 each as of 1977, delivered to the Andrew W. Breidenbach Environmental Research Center (AWBERC or US EPA Cincinnati) facility in Cincinnati, OH can not be accounted for in available US EPA Cincinnati inventory records. The devices were delivered to their facility on 4/21/1977. The device serial numbers are 290T and 291T. The licensee began their investigation after receiving a letter from the U.S. NRC on 8/5/15 which identified that these devices should be in their possession. Members of the US EPA Cincinnati staff completed an exhaustive search of all available records and located radioactive inventories dating back to 1983, but could not locate any records prior to 1983. The 1983 inventory did not list the devices in question. As part of their investigation, the licensee contacted the manufacturer who has no record that the devices were returned. In addition, the US EPA facility in Research Triangle Park was contacted and requested to review their records. That location has no record of ever possessing these devices. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-10-26
51476 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-10-02 15:00 | 2015-10-16 14:19 | 2015-10-16 | LOUISIANA AGREEMENT STATE REPORT - RADIATION WORKERS CONTAMINATED WHILE WORKING IN HOT CELL The following information was received from the State of Louisiana via email: "On October 02, 2015, around 1500 CDT, Source Production & Equipment Company [SPEC] was manufacturing a 30 Curie sealed Co-60 source within Hot Cell Number 2. During the welding process of double encapsulating the sealed source the welder malfunctioned. Two radiation workers within Hot Cell Number 2, behind the room divider, attempted to grind off the ruined outer encapsulation. "The result was two workers inhaled Co-60 material. Nasal swipes indicated 11,743 cpm on the highest wipe. It was initially calculated internal exposure of around 200 mRem. "The event was basically contained to Hot Cell Number 2 except for some footprints outside the cell which were remediated. The Hot Cell is currently restricted because of contamination. "The workers have had two whole body scans on 10/07/15 and 10/12/15 with a third scan planned for 10/19/15. "Currently internal exposure from inhalation has been calculated to be 373 mRem from 2.3 microCi of Co-60. The other worker's calculated exposure was 80 mRem from 0.42 microCi of Co-60. "SPEC has enacted a policy in regards to this event to no longer allow reworking a ruined source during manufacturing by grinding on it. They will just retire/dispose of that source and get a new source to work with." The licensee is also collecting bioassay samples from both workers for analysis. LA Event Report ID NO.: LA150017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-10-26
51475 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2015-10-15 | 2015-10-16 12:12 | 2016-03-07 | ILLINOIS AGREEMENT STATE REPORT - LOST AMERICIUM/BERYLLIUM SOURCE The following information was provided by the State of Illinois via email: "The Radiation Safety Officer of Wayne County Well Surveys contacted the Agency [Illinois Emergency Management Agency] on Friday morning, October 16, 2015, to report the loss of a 3 Ci Am-241/Be source. A description of the container which holds the source was provided as well as anticipated radiation levels, markings and the route along which was followed when the container was most likely lost. The licensee had conducted visual surveys along this route with no success. The Agency dispatched teams with appropriate radiation detection instrumentation to traverse the route. The search is currently underway. Local law enforcement and emergency managers have also been advised of the matter." The RSO last verified possession of the source on June 2, 2015 during a leak test. The search is being concentrated on several rural roads between Fairfield and Decatur, IL. The loss is believed to have happened sometime in the middle of September. Source information: QSA Global; model number AMNK8208; serial number 82989B IL Report Number: IL15020 * * * UPDATE FROM DAREN PERRERO TO HOWIE CROUCH AT 1528 EST ON 4/7/16 * * * On March 4, 2016, the State was informed that the source was returned, intact, by a citizen to the licensee. The source was still locked in its transport case and was not tampered with. The licensee swiped the source with negative results. The State of Illinois considers this event closed. Notified R3DO (Riemer) and NMSS Events resource (email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2015-10-26
51474 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-10-07 06:55 | 2015-10-15 22:18 | 2015-10-15 | UNPLANNED AFW ACTUATION DURING REFUELING OUTAGE TESTING "On October 7, 2015, with McGuire Nuclear Station Unit 2 in Mode 4, operators were testing the main turbine and main feedwater pump turbines, 2A safety injection (SI) train trip functions. At the time of the test, the 2A and 2B Auxiliary Feedwater (AFW) pumps were in operation to provide make-up to the steam generators. The main feedwater system was not in service. During realignment activities from the 2A Sl test, the 2A AFW train actuation signal was unblocked when the '2A AFW auto start defeat' switch was returned to 'reset.' This caused the 2A AFW train control valves to fully open, and the associated steam generator sampling and blowdown valves to close. The actuation occurred as designed and there was no adverse impact to the Unit. Public health and safety were not impacted by this event. "Based on a review of the Event Reporting Guidelines and the plant licensing basis, this event was initially determined to be an invalid actuation. However, after further review and discussions with the NRC, Duke Energy concluded the event should be reported as an 8-hour non-emergency in accordance with 10 CFR 50.72 (b)(3)(iv)(A) as a valid actuation of the Auxiliary Feedwater System. A Nuclear Condition Report was initiated for the late notification. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-10-15
51473 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-10-14 12:20 | 2015-10-15 22:02 | 2015-10-15 | TWO CONTAINMENT ISOLATION VALVES NOT PROPERLY TESTED PER TECHNICAL SPECIFICATIONS "At 1220 CDT on October 14, 2015, GGNS identified that in June 2013, testing of two containment isolation valves in a penetration were not tested in accordance with Technical Specification Surveillance Requirement 3.6.1.3.9. Specifically, the pressure used to demonstrate operability of the penetration did not meet the post-Extended Power Uprate expected highest Containment pressure during an accident. "The valves were declared inoperable and isolated in accordance with Technical Specification 3.6.1.3, Primary Containment Isolation Valves (PCIVs) . Even though a reasonable assurance that the safety function could be met existed based on previous analysis and testing, the containment penetration was declared inoperable until appropriate testing could be completed to demonstrate operability. Testing of the penetration was completed at 1101 CDT on October 15, 2015 and demonstrated that both penetration valves were operable at the higher test pressure for the entire time period between June 2013 and October 15, 2015. "In accordance with NUREG-1022, Event Reporting Guidelines 10 CFR 50.72 and 50.73, Section 3.2.7, Event or Condition that Could Have Prevented Fulfillment of a Safety Function, requires that when a signal train system is declared inoperable the condition must be reported under 10CFR 50.72(b)(3)(v)(C)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-10-15
51472 | -1 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-10-15 15:54 | 2015-10-15 20:54 | 2015-11-12 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO DISCOVERED CONDITION "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality of the TSC Ventilation system was discovered on October 15, 2015 at 1554 EDT. The issue involved a loss of heating capability of the TSC Ventilation system due to failed ventilation system components. The review of the impact of this equipment failure on the habitability of the TSC over the 30 day mission time determined that this condition was reportable as a loss of emergency assessment capability. The repair of the equipment failure is currently being planned. "If an emergency is declared requiring TSC activation during the non-functional period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. This condition does not affect the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 11/12/2015 AT 1453 EST FROM JOHN CAVES TO MARK ABRAMOVITZ * * * "Subsequent calculations determined that the loss of heating capability of the TSC Ventilation system did not affect the TSC functionality at the time of discovery or during the 30 day mission time period. Therefore, the TSC remained functional throughout the time in question. "The initial 10 CFR 50.72(b)(3)(xiii) report is being retracted. The NRC Resident Inspector has been informed of this notification retraction." Notified the R2DO (Ehrhardt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-10-15
51471 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-10-15 08:30 | 2015-10-15 15:26 | 2015-10-15 | ALCOHOL DISCOVERED INSIDE THE PROTECTED AREA On October 15, 2015 at approximately 0830 EDT, BWXT NOG-L Security management determined alcohol had been introduced into the Protected Area. The item in question was a single bottle of beer which was identified amongst the personal items on display in a contracted employee's office. BWXT Security Management contacted the Fitness for Duty Coordinator, who escorted the bottle of beer out of the Protected Area. BWXT NOG-L Management will conduct an evaluation of the incident to include root cause analysis and corrective actions to prevent recurrence. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2015-10-15
51470 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-10-14 14:30 | 2015-10-15 13:55 | 2015-10-15 | COLORADO AGREEMENT STATE REPORT - PATIENT RECEIVED 40 PERCENT LESS THAN PRESCRIBED DOSE The following information was provided by the State of Colorado via email: "The [licensee] RSO reported that a patient received 40 percent less than the prescribed dose during a TheraSphere (Y-90) treatment on 10/14/2015. The exact cause is still under investigation. "Initial written direction was for 120 Gy. However, due to unavailability of this dose the written directive was amended to 140 Gy and the dose was ordered. "The AU [Authorized User] reported that stasis was not reached and it was believed the patient received the entire dose. The associated survey meter was reading 0 and the AU flushed the system 3 times - the meter continued to read 0. The procedure ended around 1430 MDT. "After the procedure the AMP [Authorized Medical Physicist] reviewed the paperwork, took waste measurements and performed calculations. At this point 40 Gy was found in the waste. The RSO was notified at 1545 MDT." At this time, it is not known if the patient has been notified. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-10-23
51469 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-10-15 10:30 | 2015-10-15 12:01 | 2015-10-16 | OKLAHOMA AGREEMENT STATE REPORT - PACKAGE RECEIVED WITH EXTERNAL CONTAMINATION The following information was received via email from the State of Oklahoma: "The State of Oklahoma Department of Environmental Quality [DEQ] was notified by Saint Francis Health System (OK-07163-01) that they have received a package with removable contamination on the exterior. The dose rate when surveyed is reported at 70 mR/hr, the wipe count was 400,000 cpm. The package contained an unknown amount of Sirtex Y-90 SirSpheres. The microsphere container is reported to be intact, and it appears that the contamination was spilled on the package after it was closed. The licensee is analyzing the wipe on an MCA [multi channel analyzer] to determine if the contamination is Y-90 or another nuclide." The carrier who delivered the package is unknown at this time. * * * UPDATE PROVIDED BY KEVIN SAMPSON TO JEFF ROTTON AT 1632 EDT ON 10/16/2015 * * * The following information was received via email from the State of Oklahoma: "The contamination on the package has been identified as Tc-99m, not Y-90. The contamination was limited to a [common carrier shipping] label applied to the package at the [common carrier] facility in Boston, MA. The package was transported from Boston to Dallas, TX by [common carrier airline], then by truck from Dallas to Saint Francis. The trucking company was contacted by the licensee and the truck driver was scanned at a local hospital in Dallas yesterday; results were negative. Wipe tests of the interior of the package confirm no contamination. The package was surveyed today by DEQ inspectors and the dose rate was 2 Mr/hr. The package is being held for decay in storage at the licensee facility." Notified R4DO (Miller) and NMSS Events Notification group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-10-23
51468 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-10-13 13:00 | 2015-10-14 09:09 | 2015-10-14 | AGREEMENT STATE - STUCK OPEN SHUTTER ON VESSEL LEVEL GAUGE The following report was received from the Texas Department of State Health Services via email: "On October 13, 2015, the licensee [BASF Corporation] reported to the Agency [Texas Department of State Health Services] that during routine gauge inspection and shutter checks, its [BASF Corporation] staff found the shutter on one of its Ronan SA-1 gauges, containing a 10 milliCurie cesium-137 source, was stuck in the open position. The gauge normally operates with the gauge in the open position and due to its location on the side of a vessel there is no risk of exposure. The licensee has contacted the manufacturer to schedule repairs. An investigation into this event is ongoing. Further information will be provided as it is obtained in accordance with SA-300. "Gauge/source Information: Gauge: Ronan model SA-1 -- (no unique serial number for the source holder) "Source: 10 mCi cesium-137 -- SN: 6727GK" Texas Incident Number: I-9347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-10-22
51467 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2015-10-13 18:15 | 2015-10-13 21:20 | 2015-10-13 | REACTOR TRIP AFTER A TURBINE TRIP "Surry Unit 1 Reactor automatically tripped at 1815 hours [EDT] on 10/13/2015 due to a Generator Differential Lockout Turbine trip. The cause of the Generator Differential Lockout is under investigation at this time. Reactor Coolant System is currently being maintained at 548 degrees F on the Steam Generator PORVs due to closing Main Steam Trip Valves manually. All three Auxiliary Feedwater Pumps started automatically as designed on Low-Low Steam Generator Water Level following the trip. Auxiliary Feedwater Pumps have since been secured and Main Feedwater is in use. All systems operated as required. Off-site power remains available. There is no impact on Surry Unit 2. "This notification is being made pursuant to 10CFR50.72(b)(2)(iv)(B) for 4 hour notification of Reactor Protection System activation and 10CFR50.72(b)(3)(iv)(A) for 8 hour notification of automatic actuation of Auxiliary Feedwater. The NRC Resident Inspector has been notified and is on site. "There were no radiation releases, personnel injuries, or contamination events due to this event." All control rods fully inserted during the reactor trip. The Main Steam Trip Valves were shut due to excessive cooldown. The plant is in its normal shutdown electrical lineup. There is no steam generator tube leakage. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2015-10-13
51466 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2015-06-25 | 2015-10-13 11:03 | 2015-10-13 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE "A prostate brachytherapy implant using I-125 performed at Fauquier Hospital on 6/25/2015, resulted in a dose distribution having a D90 percent of 97Gy as measured on post implant CT done on 8/12/15. The written directive prescribed a D90 percent of 145Gy. The implanted dose of 97 Gy is 66.9 percent of the intended 145 Gy. The patient was notified and is being monitored to determine if additional treatment is required. "The final determination was not made until 10/8/15 and Fauquier notified VRMP [Virginia Radioactive Materials Program] by email on 10/8/15. A telephone conversation was held on 10/13/15 regarding the 15 day written report. VRMP will review the report and determine whether an inspection will be performed." Virginia Report ID: VA-15-14 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2015-10-21
51465 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2015-10-10 08:30 | 2015-10-12 10:55 | 2015-10-12 | AGREEMENT STATE REPORT - DAMAGED DENSITY GAUGE The following information was received from the state of Kansas via email: "At 0843 [CDT] hours, on 10/10/15, a call was received by the State of Kansas Staff Duty Officer (SDO), to the SDO line regarding a radiological 'accident'. The caller, [the licensee technician], stated that he had an accident involving a density gauge, and that the radiation sources had been compromised from their cases (Cs-137 less than 9 mCi, Am/Be less than 44 mCi.) [The State] asked him if this involved radiation which had contaminated the highway, and he stated that it had not. [The licensee] further explained that he had isolated the source rods in a cooler. [The licensee technician] stated that he was wearing his nuclear badge, and had not detected a change in the level of radiation. "In response to this, [the State] made a phone notification to the KDEM [Kansas Department of Environmental Management] Response and Recovery Branch Director, KDHE [Kansas Department of Health and Environment] Radiation Control staff, and Johnson County Emergency Management. [The State] then called [the licensee] back to confirm details regarding the accident. According to [the licensee], he started the equipment, and placed it on his truck to let it 'warm up'. [The licensee technician] stated he then forgot the machine, and drove away. When this happened, the machine fell from the truck, and was broken when it hit the ground. [The licensee technician] stated he had not called any first responders about the incident. [The licensee technician] stated he picked up the pieces, and isolated the sources in the cooler. [The licensee technician] stated he would wait for personnel to respond, if needed. [The State] informed [the licensee] that KDHE was requesting that he make notification to them as well. [The licensee technician] was given the contact information, and stated he would do so. "Local Response: Johnson County Emergency Management indicated they were planning to coordinate a local response to the scene, to ensure no further action would be needed. "At 1038 [CDT], the Kansas Radiation Program Director dispatched two KDHE Radiation Control staff, with instrumentation to the scene with an ETA of 1145. Company [licensee] RSO could not be reached . [The licensee technician's] supervisor arrived on scene. [The licensee technician] was advised by [Kansas Radiation Program Director] to fill the cooler with dirt and/or sand to aid in shielding. "1148, [the licensee technician] reported that Johnson County HazMat surveys were not showing any radiation exposure rate readings above background. As soon as KDHE staff confirm the readings, [the licensee] will transport the device back to their business where it will be stored in a secure location. The licensee already in communication and coordination with Troxler to return the damaged gauge to them. KDHE staff arrived on site. "1202, KDHE staff verified that radiation sources were secured. Swipes taken and analyzed by KDHE staff showed no contamination on container with surveys confirming Johnson County readings. [The licensee technician] was able to contact the [licensee] RSO. Instructions were provided and arrangements made for storing the device in a secure location at [licensee] headquarters. Licensee transported RAM to their headquarters with a follow up report forthcoming." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2015-10-20
51464 | 0 | WATERFORD | 3 |  |  | [3] CE | 2015-10-09 18:00 | 2015-10-09 21:59 | 2015-10-09 | INADVERTENT SIREN ACTIVATION DURING TESTING "At 1800 [CDT] on October 9, 2015 a polling test was initiated in Saint Johns Parish to test the circuitry of the installed sirens. During the polling test no sirens are expected to sound as it is only a circuitry test. Siren number SJ39 inadvertently sounded for 15 to 20 minutes, and no others. Saint Johns Parish notified the parish residents that the sounding of the siren was inadvertent via a Parish wide cable television channel and a press release. A contract vendor has disabled the siren and will troubleshoot and repair starting on October 12, 2015. All remaining sirens within Saint Johns Parish remain operational and capable of being activated when required. 0% of the population is affected by the loss of this siren due to siren overlap. "Time to repair and restore siren SJ39 to service is still being investigated. "This event is reportable pursuant to 10CFR 50.72 (b)(2)(xi), News Release or Notification of Other Government Agency. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-10-09
51463 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-10-09 | 2015-10-09 18:20 | 2015-10-09 | AGREEMENT STATE REPORT - STUCK MOISTURE/DENSITY GAUGE SHUTTER The following information was received via email: "On October 9, 2015, the Agency [Texas Department of State Health Services, Radiation Branch] was notified by the licensee that during an Agency inspection at their Corpus Christi site it was discovered that the shutter on a Troxler model 3430 moisture/density gauge was stuck open. The gauge was in its transport case and the 8 milliCurie cesium-137 source was fully retracted into the gauge. The licensee stated they inspected the shutter and found debris around it. The licensee cleaned the area of the shutter and the shutter closed properly. The licensee stated the gauge had been used the day before by a technician working in a field near ponds. The licensee does not believe any significant exposure was received by the operator or any member of the general public. The gauge has been removed from service until further inspections can be completed. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-10-19
51462 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-10-09 10:02 | 2015-10-09 14:04 | 2015-10-09 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-SUPERVISORY LICENSED EMPLOYEE A non-supervisory, licensed employee had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2015-10-09
51461 | 0 | DEPARTMENT OF THE ARMY ABERDEEN |  |  |  |  | 2015-10-08 | 2015-10-09 09:32 | 2015-11-10 | SOURCE LOST DURING SHIPPING A 1.2 mCi Californium-252 sealed source was shipped from Aberdeen Proving Ground, MD to Fort Irwin, CA via common carrier. The source did not arrive as expected and the common carrier has initiated a trace. Licensee will notify NRC Region 1. * * * UPDATE FROM SCOTT DAVIDSON TO DANIEL MILLS AT 1328 EST ON 11/10/15 * * * The following was received via email: "The package did not arrive at its destination (Fort Irwin, CA) but was delivered to Dugway Proving Ground, UT (DPG). We [Department of the Army] were notified on 3 NOV 15 that the package was at DPG with a photo of the package showing the same serial number as the package that was shipped. The package [was held] at DPG awaiting coordinating instructions to have it returned to the unit responsible for shipping the package." The package has since been received and will be repackaged for shipment to its original destination. Notified R1DO (Arner), R3DO (Kozak), R4DO (Gaddy), ILTAB (Wray), NMSS Events Notification (email), CNSNS (Mexico - via fax) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-10-19
51460 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2015-10-07 21:47 | 2015-10-08 18:23 | 2015-10-08 | HIGH ENERGY LINE BREAK DOOR FOUND UNLATCHED "At approximately 2147 EDT on October 7, 2015, a high energy line break (HELB) door between the Turbine Building (TB) and the safety related Emergency Switchgear Room (ESGR) was determined to be unlatched. The door was immediately closed (latched). Investigation determined the door was unlatched for approximately 47 minutes. At 1617 EDT on October 8, 2015, it was determined the Unit 2 ESGR was outside of the design analysis for a Unit 1 HELB. A high energy line break in the TB with the door open could result in equipment in the Unit 2 ESGR experiencing high temperature, pressure, or humidity beyond conditions analyzed for equipment qualification which has the potential to render redundant safety-related equipment inoperable. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition and in accordance with 10 CFR 50.72(b)(3)(v)(A) & (B) & (D) as a condition that could have prevented the fulfillment of safety functions to shutdown the reactor and maintain it in a safe shutdown condition, remove residual heat, and mitigate the consequences of an accident. "The NRC Senior Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2015-10-08
51459 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-10-07 19:30 | 2015-10-07 22:47 | 2015-10-07 | SECONDARY CONTAINMENT RENDERED INOPERABLE "At 1930 [CDT] on 10-7-2015, GGNS [Grand Gulf Nuclear Station] identified that on October 1, 2015, Secondary Containment was inoperable between 0324 and 0440 and therefore could have prevented fulfillment of its safety function. That event is being reported under 10 CFR 50.72(b)(3)(v)(c), as any event or condition that, at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. "During the Standby Gas Treatment drawdown surveillance performed October 1, 2015, Secondary Containment failed technical specification required average enclosure building pressure of less than or equal to -0.311 water gauge at 0324 [CDT] (LCO-1-TS-15-0360 entered). "Secondary Containment has two boundaries that can be separately credited for meeting the Tech Spec requirements of TS 3.6.4.1. "Two inner doors are required to be open during the surveillance in order to test the outer door. While open, those inner doors were attended by Security personnel provided with communications capability. "Following completion of the surveillance, Secondary Containment was returned to operable status at 0440 on 10/1/15 by closing the inner doors and maintaining them closed. "A subsequent Standby Gas Treatment drawdown surveillance test on October 6, 2015, was performed satisfactorily." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-10-07
51458 | 0 | DRESDEN |  |  |  |  | 2015-10-05 12:00 | 2015-10-06 22:06 | 2015-10-06 | PART 21 REPORT - ELECTROMATIC RELIEF VALVE (EMRV) CUTOUT SWITCH "Following the return of the actuator that failed bench testing to GEH, on 6/12/15 at 1804 [CDT], General Electric Hitachi (GEH) notified Dresden Station of a potential parts quality Potential Failure of the EMRV Cutout Switch. It has been determined the notification is applicable to DNPS [Dresden Nuclear Power Station], Units 2 and 3. "The GEH investigation concluded that the EMRV actuator assemblies failed to change state because of the failure of the cutout switch to fully close and provide the appropriate current path. Multiple contributing factors were discovered which could have led to the presence of the gaps in the cutout switch. The most significant of these factors is a change in lever arm positioning causing increased forces in the tension spring which prevent proper closure of the cutout switch. Design changes to reduce wear caused by vibration on the actuators changed lever arm position and also allowed for additional dimensional tolerance which tended to increase force in the tension spring. "Identification of Facility and Component: DNPS / EMRV Actuator, GEH Part Number 352B2632G001 "Safety Significance (e.g., substantial hazard that is or could be created): Identified condition is a Potential Substantial Safety Hazard since it could cause affected EMRVs to fail to operate as designed, which could result in a loss of safety function. Potential to affect the Minimum Critical Power Ratio (MCPR), Reactor Coolant System (RCS), Automatic Depressurization System (ADS), and Low Set Relief Function "Plants with similar GEH cutout switches: Quad Cities Nuclear Power Station." Part 21 Reference: EN #51386 The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-10-06
51457 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-10-06 13:30 | 2015-10-06 17:56 | 2015-10-06 | INADVERTENT EMERGENCY SIREN ACTUATION "At 1333 [CDT] on 10-6-2015, GGNS [Grand Gulf Nuclear Station] was notified by Claiborne County Civil Defense that the Public Notification System (ANS) Sirens in Claiborne County had been inadvertently initiated by Claiborne County at 1330 today. "In response, GGNS informed Claiborne County, MS, State of Mississippi, Tensas Parish, LA, the State of Louisiana and other government agencies of a spurious actuation of the emergency response sirens in Claiborne County. The duration of the siren actuation was approximately 2 minutes. Upon cancellation of the siren activation command at 1332, the Claiborne County Emergency Director issued a 'NO EMERGENCY' message via CODE RED and Tone Alert Radio. "At approximately 1342, Claiborne County Emergency Management Agency also faxed a 'NO EMERGENCY' Emergency Alert System message transmission request to the following television stations: WJMI, WLBT, and WJTV." The licensee stated Claiborne County technicians believed this was caused by human error. The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-10-06
51456 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-10-05 17:25 | 2015-10-05 21:48 | 2015-10-05 | SAFE SHUTDOWN ANALYSIS FOR FIRE EVENT - OPEN ITEM WITH POTENTIAL TO IMPACT CAPABILITY TO OPERATE MOTOR OPERATED VALVES "At 1725 [EDT] on Monday, October 5, 2015, while updating the site fire safe shutdown analysis report, Pilgrim Nuclear Power Station (PNPS) identified vulnerabilities in two (2) specific fire areas that required a compensatory fire watch. The compensatory fire watches have already been established. "The specific concern involves the unlikely scenario that fire forces evacuation of the control room. In addition, it is postulated that motor operated valves cannot be operated from their alternate control location due to spurious operation caused by hot shorts in control wiring. The specific failure mode is described in NRC Information Notice (IN) 92-18. "Engineering modifications are under development and scheduled for implementation to address this specific IN 92-18 concern. "Based on the above, the condition is reportable to the NRC as an unanalyzed condition that significantly degrades plant safety. As such the condition is reportable under 50.72(b)(3)(ii)(B), and requires an 8 hour notification. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-10-05
51455 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2015-10-05 21:15 | 2015-10-05 21:47 | 2015-10-06 | ALERT DECLARATION DUE TO FIRE IN THE AUXILIARY BUILDING "At 2115 [EDT] on 10/05/15, an Alert was declared due to a fire in the Auxiliary building affecting DC-P-1A [Decay closed cooling pump 1A] and A-Train safety equipment. The fire is out." The licensee reported the fire was extinguished at approximately 2201 EDT. The fire did not hamper operations personnel responding to the fire. Offsite fire assistance was requested. The NRC Resident Inspector will be notified. The licensee notified the York Haven Power Station, PEMA (Pennsylvania Emergency Management Agency), and the counties of Cumberland, Lebanon, Lancaster, York, and Dauphin. Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). * * * UPDATE AT 0015 EDT ON 10/06/15 FROM JAMES CREIGHTON TO S. SANDIN * * * The licensee is terminating the Alert at 0009 EDT on 10/06/15 based on the following: "At 2115 [EDT] on 10/05/15, an Alert (HA3) was declared due to a fire in the Decay Closed Cooling Water Pump '1A' motor and breaker. The fire was extinguished at 2201 [EDT]. "Following inspection by electrical maintenance the 'P' 480V bus was re-energized at 2305 [EDT] and restoration of previously running loads is in progress. "Station (TMI) is in a 72-hour LCO for repairs to the Decay Closed Cooling Water Pump '1A' (DC-P-1A). "TMI (Three Mile Island) is terminating the event based upon the above information." The licensee notified the York Haven Power Station, PEMA (Pennsylvania Emergency Management Agency), and the counties of Cumberland, Lebanon, Lancaster, York, and Dauphin. The licensee will issue a press release. The licensee informed the NRC Resident Inspector. Notified R1DO (Bickett), NRR (Howe) and IRD (Gott). Notified DHS, FEMA, USDA, HHS, DOE, DHS NICC, EPA EOC, FEMA NWC (via email), FDA EOC (via email) and Nuclear SSA (via email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-10-05
51454 | 0 | AZZ/NUCLEAR LOGISTICS INC |  |  |  |  | 2015-10-05 | 2015-10-05 17:47 | 2015-10-05 | PART 21 - ELECTRONIC POSITION CONTROLLER FAILED INTERNAL COMPONENT The following was excerpted from a fax received from the licensee: "NLI manufactured the reverse engineered units to replace the existing obsolete electronic position controller NLI Model: NLI-10A-LM-P. "The failed component within the controller was sized based on the original published ratings of the original components installed. The unit had an internal component that was subjected to a current value that was higher than the rating for the component. The actual applied current value was not originally provided to NLI when the units were being designed. NLI and the affected plant has been in communication regarding the component condition since the first reported failure. "Three of units that initially failed in the plant have already been returned to NLI for failure analysis and design modifications. These units were modified by installing a larger bridge rectifier and wire wound resistor onto the revision 0 circuit board. The modified versions, quantity of three, S/N: NLI-10A-LM-P-1003- 0, NLI-10A-LM-P-1004-0 and NLI-10A-LM-P-1006-0 have been returned to Calloway under purchase orders 689233 SR and 694253 SR and have been accepted and installed into the plant and are working with no reported issues. The model number NLI-10A-LM-P, has been redesigned with a larger bridge rectifier of a higher rating and wire wound resistor that will withstand the applied current in the intended application. The parent circuit board has also been revised to revision 1 to accept the larger bridge rectifier without impacting other components on the board. The remaining unmodified revision 0 units that were originally supplied have not yet been returned to NLI for incorporation of the design modification. NLI recommends that at the plant's earliest convenience, the remaining units be returned to NLI to be retrofitted with the latest design configuration (revision 1 circuit board)." The affected plant is Callaway. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-10-05
51453 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-10-05 08:15 | 2015-10-05 15:01 | 2015-10-22 | TWO REACTOR VESSEL HEAD PENETRATIONS COULD NOT BE DISPOSITIONED AS ACCEPTABLE "On 10/5/2015, during the Beaver Valley Power Station Unit No. 2 (BVPS-2) refueling outage, while performing planned ultrasonic examinations (UT) on the 66 reactor vessel head penetrations, it was determined, that two penetrations could not be dispositioned as acceptable per ASME [American Society of Mechanical Engineers] Code Section XI in a Reactor Coolant System pressure boundary. The indications of a degraded condition, on these two penetrations, are not through wall, as no leak path was identified. The examinations are being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D), and ASME Code Case N-729-1, to find potential flaws/indications well before they grow to a size that could potentially jeopardize the structural integrity of the reactor vessel head pressure boundary. All 66 reactor vessel head penetrations are scheduled to be examined during the current refueling outage. "The plant is currently shutdown and in Mode 6. The reactor vessel head is not currently installed. Repairs are currently being planned and will be completed prior to startup. "This is reportable, pursuant to 10 CFR 50.72(b)(3)(ii)(A) since the as found indications did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM DAN SCHWER TO STEVEN VITTO ON 10/22/2015 AT 1039 EDT * * * "The Beaver Valley Power Station Unit 2, FirstEnergy Nuclear Operating Company (FENOC) is retracting the 8-hour non-emergency notification made on 10/05/2015 (EN 51453). This retraction is based on additional examinations and subsequent engineering assessments completed that concluded the penetrations meet the requirements of ASME Code Case N-729-1 as amended by 10CFR50.55a(g)(6)(ii)(D) and no repairs are required. "The two reactor head penetration indications, are therefore not reportable, pursuant to 10CFR50.72(b)(3)(ii)(A). "The NRC Resident Inspector has been notified." R1DO(Gray) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-10-05
51452 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-08-21 | 2015-10-05 09:58 | 2015-10-24 | AGREEMENT STATE REPORT - DOSE TO IMPROPER TREATMENT SITE The following information was received by the State of Ohio via facsimile: "A patient had a prostate volume study done on 7/24/15 at Mount Carmel St. Ann's (MCSA). The mass that was observed on the ultrasound is in the location of a typical prostate and takes the shape of a typical prostate. Implant (I-125) procedure was performed on 8/21/15. During the implant, ultrasound guidance was used when placing the seeds and the images that were seen matched what was taken at the time of the volume study on 7/24/15. "A CT [Computerized Axial Tomography] scan was taken on 9/23/15 for post implant study to verify the seed placement and target coverage. The post implant study was performed on 10/1/15 and revealed that the prostate that is visible by CT is not adequately covered by the seeds, and that the seeds may be in the rectum. The images were reviewed further and there is a mass located between the rectum and the prostate. This is what is believed to have been visualized on the ultrasound, and what was treated in the OR [Operating Room]. "The licensee is still investigating to determine whether this tissue is part of the prostate, possibly rectum, or something else altogether. The patient has been scheduled for an MRI [Magnetic Resonance Imaging] to better visualize the tissues in this area. What is known at this time is that a large part of the prostate was not treated, the coverage to the intended target organ is below 80%, and this is being treated as a medical event. The licensee will submit a complete report when the analyses are finalized. "ODH [Ohio Department of Health] intends to send an investigator to the licensee for follow-up. This NMED record will be updated as more information becomes available." Ohio Incident: OH150010 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-10-24
51451 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-08-07 19:19 | 2015-10-05 10:00 | 2015-10-05 | 60-DAY OPTIONAL TELEPHONE NOTIFICATION FOR AN INVALID CONTAINMENT ISOLATION ACTIVATION "This 60-day telephone notification is being submitted in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to report an invalid actuation of the Unit 2, Train B Containment Ventilation Isolation (CVI) at Sequoyah Nuclear Plant. "At 1919 EDT on August 7, 2015, during planned performance of a Unit 2 containment vent, the Train B CVI actuated due to an invalid Hi Rad signal from 2-RM-90-131, Containment Vent Radiation Monitor. In addition to the Train B CVI alarm, unexpected alarms were received for 2-RM-90-106, Lower Containment Radiation Monitor and 2-RM-90-112, Upper Containment Radiation Monitor instrument malfunctions as they isolated for the CVI and 2-RM-90-131 Hi Rad alarm. Prior to the invalid Hi Rad alarm, all radiation monitors were stable at their normal values. All required automatic actuations occurred as designed. Upon investigation, the cause of the invalid Hi Rad alarm was due to an exposed shield wire at the 2-RM-90-131 detector. Preventative maintenance had been performed the week prior to the CVI and it is believed the damage occurred at that time. "Control Room Operators performed Annunciator Response actions and verified by diverse indications that the subject condition was an invalid Hi Rad signal. There were no indications of degraded reactor coolant system parameters or fuel failure. Applicable Technical Specification (TS) Limiting Condition for Operations (LCOs) were entered and the radiation monitors declared inoperable. No Emergency Response criteria were applicable with the subject radiation monitors inoperable. Radiological surveys performed in the vicinity of 2-RM-90-131 verified no abnormal radiological conditions. "Radiation Monitor 2-RM-90-131 was removed from service, the shield wire was repaired and returned to service with no issues. Radiation Monitors 2-RM-90-106 and 2-RM-90-112 were tested and returned to service. The applicable TS LCOs were exited. At the time of the event, plant conditions for a Hi Rad alarm did not exist; therefore, the CVI was invalid. "The NRC Resident Inspector was notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-10-05
51450 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-10-05 01:05 | 2015-10-05 08:41 | 2015-10-05 | SPECIFIED SYSTEM ACTUATIONS "Braidwood Unit 2 was performing a planned plant shutdown for refueling outage A2R18. In accordance with plant shutdown procedures while in Mode 1 (Power Operations) at approximately 15% power, operators attempted to start the Start Up Feedwater (SFWP) pump and the pump immediately tripped on Phase A Overcurrent. The 2A Motor Driven Feedwater pump (MDFWP) was manually started to maintain Steam Generator Water Level during the shutdown and subsequent plant cooldown. While in Mode 3 (Hot Standby) at [550 Degree-F], the 2A MDFWP was manually secured due to pump inboard journal bearing temperature exceeding its [200 Degree-F] operating limit. At 0105 [CDT] an anticipated automatic Auxiliary Feedwater actuation signal was generated on low Steam Generator level (36.3%) and both the 2A and 2B Auxiliary Feedwater pumps (AFP) auto-started. Also at 0105 [CDT] a Reactor Protection System (RPS) Reactor trip signal was received due to low Steam Generator level (36.3%) with the reactor not critical. Both Auxiliary Feedwater trains operated as designed with the Main Steam Dumps in service and the Main Condenser providing the heat sink. "All systems operated as designed with the exception of the SFWP and the MDFWP described above. "The plant is currently stable in Mode 5 with both AFPs secured. "This report is being made per 10 CFR 50.72(b)(3)(iv)(A) for automatic actuation of the (1) RPS Reactor Trip with the reactor not critical and (6) Auxiliary Feedwater System, 8 hour notification." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-10-05
51449 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-10-04 09:56 | 2015-10-04 14:16 | 2015-10-04 | SECONDARY CONTAINMENT INOPERABLE WITH THE POTENTIAL TO DRAIN THE REACTOR VESSEL "On October 4th, at approximately 0956 EDT, 'Operations with the Potential to Drain the Reactor Pressure Vessel' (OPDRV) was unintentionally initiated without secondary containment operable. Operators promptly identified the condition and immediately initiated actions to identify and suspend the source of the drain path. At approximately 1120 EDT the source of the OPDRV was isolated. Reactor cavity water level and spent fuel pool level remained constant throughout the event. An investigation is in progress. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-10-04
51448 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-10-04 09:32 | 2015-10-04 10:03 | 2015-10-04 | UNUSUAL EVENT DECLARED DUE TO IDENTIFIED RCS LEAKAGE > 25 GPM At 0932 EDT on 10/4/15, the licensee declared an Unusual Event for identified RCS [Reactor Coolant System] leakage exceeding 25 gallons per minute [GPM], per EAL BU2, due to a relief valve leaking on the Shutdown Cooling System common header. The RCS leakage was within the capacity of the Charging System. At 0954 EDT the RCS leakage was terminated by isolating the Shutdown Cooling System. The cause of the relief valve failure is unknown and under investigation. The RCS cooldown was terminated and both RCS loops were restored to service for decay heat removal using both Steam Generators and the Main Condenser. Current RCS temperature is 248 degrees F with RCS pressure at 248 psig. All offsite power and EDGs [Emergency Diesel Generators] are available. The licensee intends to repair the relief valve to resume the RCS cooldown using the shutdown cooling system.. The licensee informed State and local agencies and the NRC Resident Inspector. Notified DHS SWO, DHS NICC, FEMA, and Nuclear SSA via email. * * * UPDATE AT 1115 EDT ON 10/04/15 FROM FRED PERKINS TO S. SANDIN * * * The licensee terminated the Unusual Event at 1100 EDT, based on verification that the RCS leakage was stopped. The licensee informed State and local agencies and the NRC Resident Inspector. Notified R1DO (Bower), NRR EO (Morris), and IRD (Gott). Notified DHS SWO, DHS NICC, FEMA, and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-10-04
51447 | 0 | WATERFORD | 3 |  |  | [3] CE | 2015-10-03 23:07 | 2015-10-04 03:51 | 2015-10-04 | AUTOMATIC REACTOR TRIP "At 2307 CDT Waterford 3 experienced an automatic reactor trip and all Control Element Assemblies (CEAs) inserted into the core. The cause of the automatic reactor trip is currently under investigation. "The plant is currently in Mode 3 [Hot Standby] and stable with Main Feedwater feeding and maintaining both Steam Generators. Main Feedwater Pump 'A' tripped subsequent to the reactor trip. Emergency Feedwater actuated following the plant trip as expected, but was not required to maintain Steam Generator level. "The plant entered the Emergency Operating Procedure for an uncomplicated reactor trip and has now transitioned to the normal operating shutdown procedure." Unit 3 is in a normal post trip electrical lineup. The Main Condenser is in-service removing decay heat.. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-10-04
51446 | 0 | PALISADES | 1 |  |  | [1] CE | 2015-10-03 22:35 | 2015-10-03 23:27 | 2015-10-03 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to monitoring and detection of a vital area. Compensatory actions taken. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-10-03
51445 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2015-10-03 10:25 | 2015-10-03 14:46 | 2015-10-03 | FITNESS FOR DUTY - CONFIRMED POSITIVE FFD TEST A non-licensed supervisory employee had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been restricted. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2015-10-03
51444 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-10-03 10:00 | 2015-10-03 12:02 | 2015-10-05 | MANUAL REACTOR TRIP DURING SHUTDOWN FOR A REFUELING OUTAGE "During the scheduled Unit 2 down power to start 2RF15, Steam Generator 3 Feed Control Valve failed to control in Automatic or Manual resulting in excessive feedwater flow. Control Room Operators manually tripped the reactor and aligned Auxiliary Feedwater. No automatic RPS or ESF actuations occurred. Plant conditions are stable." All control rods fully inserted on the trip and no safety or relief valves lifted. The plant is supplying water to the steam generators with auxiliary feedwater and removing decay heat through the main condenser. The unit is in its normal shutdown electrical lineup. There was no effect on unit-1. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1848 EDT ON 10/05/15 FROM JOHN RASMUSSEN TO JEFF HERRERA * * * The licensee added 10 CFR 50.72(b)(3)(iv)(A) to the 10 CFR codes reporting section. No other text was modified. Notified the R4DO (Taylor). | 0 | 0 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-10-03
51443 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2015-10-02 09:05 | 2015-10-02 10:27 | 2015-10-03 | SECURITY REPORT Potential introduction of contraband into the Protected Area (PA). Immediate compensatory actions taken upon discovery. See EN #51439. The licensee notified State and local agencies and the NRC Resident Inspector. * * * UPDATE FROM LAUREL KETCHAM TO DANIEL MILLS AT 1214 EDT ON 10/02/15 * * * The suspicious package was determined to not be contraband. The licensee notified State and local agencies and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-10-03
51442 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2015-10-02 | 2015-10-02 17:59 | 2015-10-02 | AGREEMENT STATE REPORT - GAMMA KNIFE TREATMENT TO INCORRECT LOCATION The following report was received via e-mail: "A Gamma Knife patient with trigeminal neuralgia was treated to the incorrect side. The intended side was the patient's right, however, the left side was treated. The prescription was 85 Gy @ 100%. The intended volume was approximately only 33.5 cubic mm which corresponds to the 80% isodose (68 Gy). The incorrect treatment location was determined as the patient completed treatment at approximately 1000 EDT. Once the situation was reviewed, discussed and confirmed by those involved with this treatment, the Radiation Safety Officer (RSO) was notified via phone call at approximately 1100 EDT. The RSO stated that he would contact the State to report the event. The patient has already been informed regarding what happened by the attending neurosurgeon, and after a short break, the patient was then treated to the correct side. The correct treatment was completed at approximately 1230 EDT. The attending radiation oncologist notified the referring physician practice at approximately 1400 EDT. Licensee will provide a required report within 15 days. They are still determining corrective actions to prevent reoccurrence. A state inspector will be on-site doing a follow up investigation Monday, 10/5/2015. "The treatment isocenter was positioned incorrectly due to human error. More details to be gathered during site visit and investigation by Agency [North Carolina Division of Health and Human Services] scheduled for 1000 EDT, Monday, October 5, 2015. Corrective actions are being discussed by licensee. "Note: Licensee radiation team and referring physician do not believe patient will suffer any acute deleterious effects at this time." North Carolina NMED #NC150026 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-10-12
51441 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-10-01 | 2015-10-02 16:54 | 2015-10-02 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER STUCK OPEN The following report was received via fax: "An OHMART gauge was discovered with the shutters malfunctioning on a level gauge installed on processes. The shutters were stuck in the open position due to the buildup of grime and corrosive material from the operational environment. This device does not pose a radiation exposure hazard or a threat the work force or the general public. The device will remain in operation on the processes until the repair or replacement. "The detected malfunction was discovered during the annual inventory/operational checks. These checks are required by condition # 7 of the radioactive material license, LA-2316-L01. The repairs will be made and documentation will be reviewed during the next inspection. "The gauge detected was an OHMART Corp. gauge, Model Number SHF-2. The gauge/device S/N unknown is loaded with approximately 671 mCi of Cs-137 with source S/N 5895GK. BBP Sales was contacted to fix the problem by repairing the gauge or replacing the device." Louisiana Event: LA-150016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-10-12
51440 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2015-10-02 08:25 | 2015-10-02 14:50 | 2015-11-20 | LOOSE SAFETY RELIEF VALVE DISCHARGE FLANGE BOLTS "On October 2nd, at approximately 0825 EDT, maintenance technicians were performing as-found torque checks on the discharge flange of the 'B' Safety Relief Valve (SRV). 12 of the 16 bolts were not adequately torqued. The 'B' Safety Relief Valve is credited for Remote Shutdown. The as-found condition of inadequate torque potentially impacts the seismic qualification of the 'B' SRV. "An investigation and extent of condition review is ongoing. The NRC Resident Inspector has been notified." Before the outage, there were no abnormal indications of leakage as indicated by a rise in drywell temperature or pressure. The SRVs had been cycled under pressure with no abnormal indications. The four bolts that were tight were in a diagonal pattern. The looses bolts were described as "finger tight." The licensee is determining the actions to take regarding the remaining 14 SRVs. * * * RETRACTION FROM STEVE WARD TO DONALD NORWOOD AT 1552 EST ON 11/20/2015 * * * "As part of the event investigation and extent of condition review, the as-found torque values of the inlet and outlet Safety Relief Valve (SRV) flange connections were measured and an engineering evaluation of the as-found condition was performed. The evaluation confirmed that all 15 SRVs would have remained operable during a design basis earthquake. Any potential discharge flange connection leakage during SRV operation would be bounded by the design basis Loss of Coolant Accident analysis described in the UFSAR. "Subsequent investigation activities of the as-found condition of SRV 'B' determined that the four tight bolts were not oriented in a diagonal pattern across the discharge flange as originally reported. This information is provided only to clarify previously reported information and does not affect the original basis for reporting or the current basis for retraction." The licensee notified the NRC Resident Inspector. Notified R3DO (McCraw). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2015-10-02
51439 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2015-10-02 09:05 | 2015-10-02 10:27 | 2015-10-03 | NOTIFICATION OF UNUSUAL EVENT At 0905 CDT on 10/02/15, Ft. Calhoun Station declared a Notification of Unusual Event based on criteria in the site security plan. The licensee notified State and local agencies and the NRC Resident Inspector. Notified DHS SWO, DHS NICC, FEMA, and Nuclear SSA via email. * * * UPDATE FROM LAUREL KETCHAM TO DANIEL MILLS AT 1214 EDT ON 10/02/15 * * * At 1136 CDT, the Unusual Event was terminated based on the fact that criteria for entry into the site security plan no longer exists. The licensee notified State and local agencies and the NRC Resident Inspector. Notified R4DO (Taylor), R4RA (Dapas), NRR ET (Dean), NSIR ET (Holian), NSIR (Lewis, Stapleton), ILTAB (Johnson), IRD MOC (Gott). Notified DHS SWO, DHS NICC, FEMA, and Nuclear SSA via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-10-03
51438 | 0 | LANTHEUS MEDICAL IMAGING |  |  |  |  | 2015-10-01 | 2015-10-01 17:18 | 2015-10-01 | RADIATION WORKER OVER EXPOSURE Lantheus Medical Imaging received notification that the dosimeter of an employed radiation worker indicated a whole body over exposure for the month of August 2015. The indicated dose is 7929 mRem for August and the 2015 total is 8500 mRem. The employee is a technician in charge of operating the cyclotron and has been removed from radiation work. The licensee has notified the employee and is conducting an investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2015-10-09
51437 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-10-01 09:30 | 2015-10-01 15:26 | 2015-10-01 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SOURCE DISCONNECTED The following report was received via e-mail: "On October 1, 2015 the Agency was notified by the licensee's radiation safety officer that a source was disconnected and dropped into a vessel. [This was caused by] a shutter malfunction which occurred on October 1, 2015 at 0930 [CDT] on a nuclear gauge. The source is an Ohmart Model MDTS, Serial Number 8480GK, Cesium 137, 9.5 mCi source. The shutter malfunction occurred during a routine check of the shutter operation. This particular device utilizes a tape which is connected to the source. The tape allows the source to be lowered and raised inside a well within the vessel. During the routine shutter checks, the tape disconnected from the source. At this time, the source is located inside the well near its normal operational position. A radiation survey was conducted at areas which would contain general employee access. All radiation readings were at background level. This event did not cause any additional radiation exposure than normal day to day operations. The gauge manufacturer has been notified and will be on-site October 7, 2015 to repair the device. Updates will be provided in accordance with SA-300 guidelines." Texas Incident: I-9342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-10-09
51436 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-10-01 09:06 | 2015-10-01 14:38 | 2015-10-01 | MODE CHANGE WITH TURBINE TRIP LEADS LIFTED "At 0906 [CDT], it was determined that U1 [Unit 1] was in a condition that could have prevented fulfillment of the turbine trip safety function and TS [Tech Spec] 3.0.3 was entered. Leads had been lifted to disable the turbine trip function on both SSPS [Solid State Protection System] trains while U1 was in Mode 4 (which is outside the mode of applicability). However, at 0059 [CDT], U1 entered Mode 3 with these leads still lifted. In Mode 3, both trains of the turbine trip function are required to be operable per TS 3.3.2. The turbine was subsequently tripped at 0932 [EDT] and the leads were re-landed enabling the turbine trip function at 0946 [CDT], TS 3.0.3 was subsequently exited. This condition is being reported in accordance with 10 CFR 50.72 (b)(3)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function to mitigate the consequences of an accident. "The Byron NRC site Resident Inspector has been notified of this condition." The licensee has notified the State of Illinois. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-10-01
51435 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2015-09-29 | 2015-10-01 10:23 | 2015-10-01 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING AN UNDERDOSE TO THE PATIENT The following report was received from the State of Kansas via email: "Yesterday afternoon [the State of Kansas] was contacted by [the licensee's], RSO [Radiation Safety Officer] for KU Hospital Authority lic# 18-C801, to report a medical event. On the morning of 9/29/15, a Thera-spheres Y-90 therapy procedure was found to have underdosed the patient by 36%. The details are as follows: "A RADose RAD 60R personal electronic dosimeter is attached to the plexiglass 'box' which holds the vial containing the Y-90 Thera-spheres during the procedure. This dosimeter is the only method of detection to ensure that all of the Y-90 material is placed within the patient. In comparison, the Sir-sphere, similar material and procedure, utilizes a contrast to better ensure material is where it's supposed to be. "Prior to the procedure, the dosimeter was checked for current calibration and source checked and found to be satisfactory including low battery indicator not active. During this pre-procedure check, the dosimeter exhibited fluctuating readings. A backup dosimeter of the same make and model was searched for but could not be located. The dosimeter was then re-checked and the fluctuations could not be duplicated, thus it was decided to utilize the dosimeter for the procedure. The Y-90 procedure was then completed, with the dosimeter reading at levels that indicated the required Y-90 had been placed within the patient. At this point, the 'waste' from the procedure i.e. vials, tubing, pads is taken back to the hot lab and surveyed to calculate the remaining Y-90. It was discovered that 36% still remained and that the patient did not receive the entire prescribed dose. It was determined that enough of the Y-90 had been administered to the patient to receive a satisfactory therapeutic dose thus another procedure would not be necessary. "Exposure to staff was also determined to be negligible due to the nature of the material/shielding/remaining concentration. The RSO stated that the dosimeter was again rechecked and the low battery indicator was active during the check. The RSO made the preliminary assessment that the dosimeter was possibly functioning just above the 'cutoff' point of low battery. "The licensee stated that a detailed report is in process and will be submitted within the required time parameters." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2015-10-09
51434 | 0 | U.S. ARMY |  |  |  |  | 2015-09-30 | 2015-09-30 15:59 | 2015-10-01 | MISSING TROXLER MOISTURE DENSITY GAUGE The U.S. Army contracted with [common carrier] to pick up two Troxler moisture density gauges from their Life Cycle Management center in Warren, Michigan and deliver them to an Army National Guard (ANG) center in Methuen, Massachusetts. On 9/28/15, [common carrier] tracking indicated that only one of the gauges was delivered. The ANG center didn't receive the gauge until 9/29/15. The RSO at U.S. Army TACOM contacted [common carrier] about the status of the second gauge. On 9/30/15, [common carrier] informed the RSO that the gauge was "misplaced" and an investigation and search was underway. The missing gauge is a Troxler Model 3440+, serial number 68419, containing 8 mCi of Cs-137 and 40 mCi of Am-241. The U.S. Army will update this report as appropriate. * * * UPDATE FROM KAREN MCGUIRE TO JOHN SHOEMAKER AT 1140 ON 10/01/15 * * * The common carrier located and delivered the remaining gauge to the proper location. Notified R1DO (Bower), R3DO (Orth), and NMSS Events Notifications via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-10-08
51433 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2015-09-23 | 2015-09-29 16:49 | 2015-09-29 | NEW MEXICO AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING Y-90 SIRSPHERES On 9/23/15, a patient underwent Y-90 SirSphere treatment on their liver. Post-treatment scans indicated the patient had SirSpheres present in their stomach and liver. The calculated dose to the patient's stomach was 54 Rem. The state of New Mexico will be sending an inspector to investigate the cause of the event. New Mexico Report No.: NM150004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2015-10-07
51432 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2015-09-29 10:30 | 2015-09-29 14:56 | 2015-09-29 | BOTH TRAINS OF THE STANDBY GAS TREATMENT SYSTEM DECLARED INOPERABLE "On 9/29/15 at 1020 EDT, the 'B' train of Standby Gas Treatment System was declared inoperable for planned testing. On 9/29/15 at 1030 EDT, during performance of a surveillance on Unit 1 Reactor Pressure Vessel water level instrumentation, one channel was found to not meet acceptance criteria. The failed level channel is part of the initiation logic for the 'A' train of Standby Gas Treatment. This resulted in a loss of safety function for the Standby Gas Treatment System. On 9/29/15 at 1145 EDT, the 'B' train of Standby Gas Treatment was restored to operable by restoring from the planned testing. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-09-29
51431 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2015-07-30 | 2015-09-29 14:42 | 2015-09-29 | NEW YORK AGREEMENT STATE REPORT - LOST STRONTIUM-90 CALIBRATOR SOURCE The following information was received from the state of New York via facsimile: "A routine inspection by the NYS Department of Health resulted in a finding that a Thermo Fisher Scientific Model 885326 Ser. No. B7131 point level gauge calibrator source had not been used since 2011. Licensee efforts to locate the device following the inspection were not successful. The source was officially deemed missing July 30, 2015. The device contained a 2 microCurie Strontium 90 source. The licensee states that at some time between the original installation in 2001 and 2003, the board on which the Sr-90 source was installed, failed and was replaced by a new electronic test board that did not require a radioactive source. Thermo Fisher did the installation. Neither the facility nor Thermo Fisher have any documentation showing the disposition of the Sr-90 source." NYS Event Report ID No.: NYDOH-15-09 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-10-07
51430 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2015-09-28 20:46 | 2015-09-28 22:49 | 2015-09-28 | AUTOMATIC REACTOR SCRAM FOLLOWING TRIP OF BOTH REACTOR RECIRCULATION PUMPS "On September 28, 2015 at 2046 EDT, the Hope Creek reactor scrammed following a trip of both reactor recirculation pumps. "All control rods fully inserted into the core. All safety systems responded as designed and expected. There was no radiological release. The unit is stable in Mode 3 with decay heat being removed via the turbine bypass valves rejecting steam to the main condenser. Normal feedwater level control is providing makeup to the reactor vessel. "No personnel injuries resulted from the event. "The Outage Control Center has been staffed to determine the cause of the reactor scram. "The Hope Creek NRC Resident Inspector has been notified." The licensee notified Lower Alloways Creek township of the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-09-28
51429 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2015-09-28 13:27 | 2015-09-28 21:54 | 2015-11-04 | BOTH UNIT 1 EMERGENCY DIESEL GENERATORS INOPERABLE AT THE SAME TIME "At approximately 1327 CDT on September 28, 2015, both D1 and D2 Diesel Generators (EDG) were inoperable simultaneously until corrected at 1345 CDT. The D2 Diesel Generator had been declared inoperable for the planned performance of SP1307, D2 Diesel Generator 6 Month Fast Start Test. Tech Spec LCO 3.8.1 Condition B had been entered for D2 Diesel Generator. Subsequently, D1 Diesel Generator was determined to be inoperable but available due to Train A Cooling Water Header being inoperable during post maintenance testing of SV-33133, Backwash Water Supply to the 121 Safeguards Traveling Screen. Tech Spec LCO 3.7.8 Condition B was entered for the Cooling Water Header inoperability, which forced a cascade to Tech Spec 3.8.1 Condition B for D1 Diesel Generator. With both Emergency Diesel Generators inoperable, Tech Spec 3.8.1 Condition E was entered, which required the restoration of one Emergency Diesel Generator to operable status within 2 hours. D2 was returned to operable status through completion of SP 1307, and Tech Spec 3.8.1 Condition E was exited at 1345 CDT. "With both Emergency Diesel Generators inoperable, this condition is reportable under 10 CFR 50.72 (b)(3)(v)(D), Event or Condition that Could Have Prevented Fulfillment of a Safety Function. "The plant remains safe, and this condition does not pose any additional risk to the public. Additionally, our defense in depth strategies are relied upon to take actions to protect the health and safety of the public. D2 Diesel Generator remained available with full cooling water flow during this time. The safety significance of this event is low, as engineering hydraulic analysis has demonstrated that with the safeguards traveling screen backwash water supply valve fully opened, the Cooling Water System would have continued to provide full cooling flow to the D1 Diesel Generator. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION ON 11/4/15 AT 1510 EST FROM NATHAN BIBUS TO DONG PARK * * * "An evaluation has been performed and it has been determined that SV-33133 and SV-33134 do not have an active close safety function. The Cooling Water System analysis of record, calculation ENG-ME-820, Rev 0B shows that the Cooling Water System continues to have flow margin with screen wash control valves SV-33133 and SV-33134 open. "Therefore, there is no need for the valves to close to ensure the Cooling Water System's safety function. Because the valves do not have a safety function to close, this event was not an event or condition which could have prevented the fulfillment of a safety function of an SSC [structures, systems and components] required to mitigate the consequences of an accident and, therefore, did not require an 8 hour notification in accordance with 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function (i.e., accident mitigation) under 10 CFR 50.72(b)(3)(v)(D). The notification is hereby retracted. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Orlikowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-09-28
51428 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-09-28 14:44 | 2015-09-28 20:28 | 2015-09-28 | INVALID SEISMIC EVENT ALARM "At 1444 CDT on September 28, 2015, the station's seismic instrumentation generated a seismic event alarm that was determined to be invalid based upon no seismic activity being felt on site, and no activity detected in the area by either the National Earthquake Information Center, or nearby nuclear plants. The instrumentation that actuated recorded steady values of -0.3 to -0.4g on three axes of one instrument, which is greater than the +/- 0.02g threshold value in the Emergency Action Level in the station's emergency procedures; however, no other instrument channel or axis indicated a valid event exceeding the 0.02g threshold. Since the event alarm was determined to be invalid as described above, no EAL thresholds were met. "The seismic instrumentation was declared non-functional since it would not generate a seismic event alarm during an actual event until the invalid event was reset. The alarm was reset through the alarm reset process. The seismic instrumentation alarm capability was restored and returned to service at 1746. The Seismic Instrumentation remains non-functional pending troubleshooting. "This resulted in a Loss of Emergency Assessment Capability while the seismic instrumentation was out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." This is a recurring event. See EN #51263 and EN #51282. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-09-28
51427 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2015-09-24 | 2015-09-28 17:29 | 2015-09-28 | AGREEMENT STATE REPORT - EIGHT MISSING TRITIUM EXIT SIGNS The following is a summary of information received from the State of North Carolina via email: Eight new Tritium exit signs were reported missing to the State of North Carolina by the licensee. The new signs were placed in a temporary storage location during building renovations. They were discovered missing when the licensee was preparing to return old signs back to the manufacturer for disposal. The licensee believes the new signs were inadvertently discarded as trash. All eight signs were manufactured by Isolite Corporation and each contained approximately 6.22 Curies of Tritium. The serial numbers of the missing signs are: 1203962, 1203964, 1203966, 1203961, 1203900, 1203963, 1203902, and 1203897. North Carolina will be citing the licensee for loss of radioactive material. NC Item Number: NC 150025 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-10-06
51426 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-09-28 06:35 | 2015-09-28 07:42 | 2015-09-28 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures were not employed. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-09-28
51425 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2015-09-25 04:30 | 2015-09-25 12:09 | 2015-09-25 | OFFSITE NOTIFICATION DUE TO EMPLOYEES INJURED BY NON-RADIOACTIVE HIGH TEMPERATURE WATER AND STEAM "On September 25, 2015 at roughly 0430 EDT, four employees were in the work area when high temperature water and steam released from a wash operation in the Final Assembly Area. The cause of the water/steam release is unknown at this time, and a comprehensive investigation is underway. The area is in a safe, shutdown state, and is roped off to preserve the scene. The event did not involve any special nuclear material or contamination and is classified as an industrial safety incident. "Three of the four employees were affected by the high temperature water/steam and were transported by ambulance to the hospital for treatment. "This concurrent report is being made under Paragraph c of 10 CFR 70, Appendix A because in-patient hospitalization requires a 24 hour report to the South Carolina Department of Labor." The licensee will notify NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2015-09-25
51424 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-09-23 | 2015-09-25 09:14 | 2015-09-25 | AGREEMENT STATE REPORT - STOLEN GENERAL LICENSED MATERIAL The following information was provided by the State of Ohio via email: "Sometime between 2330 EDT pm on 9/22/15 and 0430 EDT on 9/23/15, a vehicle maintained by a staff member of the ODH [Ohio Department of Health] Public Health Lead Investigation Program was broken into at their residence in Chillicothe, Ohio. A NITON X-Ray Fluorescence (XRF) lead-based analyzer (SN 92956) containing a Cadmium-109 radioactive source with a maximum activity of 50 mCi [was stolen]. The XRF device was in a locked pelican case in the locked trunk of the vehicle. The theft was reported to local law enforcement and to the Ohio State Highway Patrol. The device has not been recovered as of the date of this report (9/25/15)." OH Reference Number: 2015-014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-10-05
51423 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2015-09-17 12:22 | 2015-09-24 16:34 | 2015-09-24 | VALID ACTUATION OF UV RELAYS FOLLOWING LOSS OF UNIT 2 STARTUP TRANSFORMER "On September 17, 2015, at 1222 hours, with Unit 2 in Mode 5 at the beginning of a refueling outage, an electrical fault on the 2A 6.9 kV bus resulted in the loss of the 2A startup transformer and its associated non-safety related 2A2 and safety related 2A3 busses. At the time of the event, the 2A Emergency Diesel Generator (EDG) had been properly removed from service for scheduled maintenance. The loss of the 2A start up transformer initiated the under voltage relays, which resulted in a valid actuation signal that would have started the 2A EDG. "Additionally, the 2A train of shutdown cooling (SDC) was de-energized; the 2B (protected) train of SDC was not affected by the event and remained in service to remove decay heat. The 2A shutdown cooling train was restored and made available on September 19, 2015 at 0030. The 2B EDG and 2B startup transformer remained operable. "St. Lucie did not report this event within 8 hours of occurrence, however, this event was subsequently determined to be reportable pursuant to 10CFR50.72(b )(3)(iv)(A). "During this event, Unit 1 experienced a loss of the 1A startup transformer. There was no effect on Unit 1 operation, as its associated non-safety and safety-related busses remained powered by the auxiliary transformer. The 1A startup transformer returned to service on September 18, 2015 at 2103." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-09-24
51422 | -1 | ROBINSON | 2 |  |  | [2] W-3-LP | 2015-09-24 14:54 | 2015-09-24 15:38 | 2015-11-23 | UNAUTHORIZED STORAGE DEVICE USED FOR SAFEGUARDS INFORMATION Safeguards information was found on an unauthorized storage device. Compensatory measures were taken upon discovery. The NRC Resident Inspector has been briefed. * * * RETRACTION FROM LAURA BASTA TO DONALD NORWOOD AT 1222 EST ON 11/23/2015 * * * "An evaluation has determined that there is no evidence that safeguards information stored on the subject unauthorized storage device was compromised. Therefore, the threshold for reporting the issue as compromised safeguards information has not been met." The licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes) and CAT (Pezeshki). E-mailed 73.71 Safeguards Group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-09-24
51421 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-09-23 21:00 | 2015-09-24 05:52 | 2015-09-24 | HIGH PRESSURE COOLANT INJECTION INOPERABLE DUE TO MGU FAILURE "During surveillance testing of the U2 HPCI [High Pressure Coolant Injection] system, the HPCI motor gear unit [MGU] was positioned from 100 percent to 75 percent demand to satisfy operability testing. The motor gear unit did not respond as system demand was returned to 100 percent. This indicated a failure of the MGU which requires declaration of inoperability of the HPCI System. This is a 14 day LCO. HPCI is a single train system and reportable under SAF 1.8 'Event or condition that could have prevented fulfillment of a safety function.'" The licensee will be notifying the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-09-24
51420 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2015-09-02 | 2015-09-23 15:59 | 2015-09-24 | AGREEMENT STATE REPORT - LOST PORTABLE MOISTURE/DENSITY GAUGE The following report was received from the Commonwealth of Virginia via email: "On September 22nd at 1749 EDT. [The Commonwealth of Virginia Department of Health] received a call from the Virginia Emergency Operations Center, stating that the RSO [Radiation Safety Officer] from WRA [the licensee, Whitman, Requardt & Associates] was calling to report a missing gauge. [Virginia Department of Health] contacted the [licensee's] RSO who then informed [Virginia Department of Health] that one of their gauges was lost in shipment. [Virginia Department of Health] requested the RSO send an email detailing the event. "On August 12th, WRA shipped a Troxler 3411B gauge (S/N: 5374), containing 9 mCi of Cs-137 and 44 mCi of Am-241, to Northeast Technical Services (NETS) for calibration. On September 1st, WRA was contacted by NETS that the calibration was completed and the gauge was being shipped back. On September 15th, WRA contacted NETS to say they had not received the gauge. On September 22nd, NETS contacted WRA to inform them that [the common shipper] was unable to locate the gauge and considered it to be unlikely recovered. "NETS supplied [Virginia Department of Health] with the tracking number which indicated the gauge was picked up on September 1st, sent to the York, PA facility, then the Greencastle, PA facility. The results then say on September 2nd, the gauge was sent to the Winchester, VA facility and unloaded. "On September 23rd, [Virginia Department of Health] contacted the [common shipper's] facility in Winchester, VA and spoke with the site manager. The manager stated that the gauge was not on the truck when it arrived at this facility on September 2nd, and that an 'All Points Bulletin' (APB) was submitted. [Virginia Department of Health] then contacted the Greencastle, PA facility and spoke to the OS&D/Customer Service Representative regarding the loss of this gauge. [Virginia Department of Health] discussed what actions had been taken to locate the gauge and supplied them with an email containing pictures of the transportation case and the gauge. "At 1458 EDT on September 23rd, an APB from the Greencastle, PA facility was created and submitted to [the common shipper's] staff. They have checked the truck that was used on September 1st, and the gauge was not found in the truck. They are speaking with the driver of this truck and showing him pictures of the gauge and case. "Currently, [the common shipper] is looking through the Greencastle, PA facility and contacting the Pittsburgh, PA facility regarding the gauge. The Greencastle OS&D/Customer Service Representative stated they will provide daily updates regarding the search. "The Pennsylvania RMP [Radioactive Materials Program] has been notified and made aware of this event. "The Virginia RMP will provide updates as they become available. "There is no public health or safety impact at this time." Commonwealth of Virginia Event Report ID No.: VA-15-11 * * * UPDATE FROM MIKE WELLING TO CHARLES TEAL ON 9/24/15 AT 1156 EDT * * * "On September 24th, it was discovered that the portable gauge was delivered to another Virginia licensee who also had sent a portable gauge to NETS for service. The gauge was returned to [common carrier] who is shipping it back to NETS to inspect. The gauge will then be sent to WRA. "The investigation at [Common Carrier] is on-going with regards to how it was delivered to the wrong licensee." Notified R1DO (Welling). Notified ILTAB (Johnson) and NMSS_Events_Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2015-10-01
51419 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-09-21 16:37 | 2015-09-23 15:26 | 2015-09-23 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received from the State of Tennessee via email: "On September 21, 2015, a moisture density gauge, belonging to Professional Services Industries, was run over at the Memphis International Airport. No contamination was reported by the licensee. The rods were still attached and shutter was in the closed position. The gauge was a Troxler Model 3430 (S/N # 31540) containing an 8 mCi Cs-137 sealed source and a 40 mCi Am-241 source in the base of the gauge. The licensee is making arrangements with manufacturer to package and ship the device. A follow-up report will be submitted upon receipt of further information." Tennessee State Event Report ID NO: TN-15-144. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-10-01
51418 | -1 | UNIV OF VT MEDICAL CENTER |  |  |  |  | 2015-09-23 10:00 | 2015-09-23 12:09 | 2015-09-29 | MEDICAL UNDERDOSE DURING SIRSPHERE ADMINISTRATION "SirSphere administration to [the patient] on Wednesday Sept 23, 2015. "[The patient] was prescribed, with appropriate written directives, 0.27 GBq and 0.29 GBq to segments in the posterior and anterior right lobe of the liver. Paperwork for determination of the activities and volumes are available. "The SirSpheres were received on Sept 22, 2015, calibrated for 1800 [EDT] on Sept 23, 2015. The two doses were prepared between 0900 and 0930 AM on Wed Sept 23, 2015. The procedure used is attached as are the worksheets for verification of activity. No unusual behavior was observed (e.g. clumping or unusual settling of the spheres). "The posterior right lobe treatment was given first. The system was set up with D5W for the agitating solution and contrast in a three way set up for the contrast flush. The interventional radiologist administered in the method that has been used for all prior, successful, administrations. [The radiologist] reports that he did not encounter any difference in resistance in the syringe, nor did [medical center staff] note any difference in the appearance of the solution flowing through the three way stopcock. The administration was completed and the residual immediately checked using the method of pre vs post assay of delivery vial then delivery vial and associated tubing. The post reading was initially higher than the pre. The vial and tubing was carefully put onto a plastic backed pad and it was determined that there were higher readings from the vicinity of the three way stopcock. "This patient was scheduled for two infusions due to their vasculature, and after much discussion it was decided, based on our prior success with treatments, to proceed with the second but pay very close attention to whether there were some spheres that were backed up at the three way. In the past, [medical center staff] have been able to dislodge such an occurrence by gentle knocking of the three way prior to the clearing of the vial with air. A new administration set was installed and the administration proceeded. Frustratingly, it was immediately apparent that some of the spheres were clumping at the three way but that some had passed through and were then in the patient. With gentle knocking of the stopcock, it was possible to dislodge many of the spheres. However, the after reading again showed that there was a measurable amount of activity that had stuck somewhere in the delivery tubing. "Because the pre and post readings are so dependent on the presence of the plastic for both stopping the electrons and production of Bremmstrahlung, it was not possible to get any type of accurate assessment of the activity remaining. However, it was possible to evaluate the last three Sirsphere post Brem SPECT scans, determine a counts/administered activity, and evaluate that number. For the three patients the values were acceptably comparable, that this calibration value was then used to determine the activity present for the after study Brem scan on today's patient. This gave an estimate of approximately 70% of the written directive. "Please note that this report is a preliminary report and an updated will be forwarded as this is reviewed by all concerned and also further evaluations performed." The licensee will contact the manufacturer to troubleshoot the issue, and will notify the patient, prescribing physician, and NRC Region 1. * * * RETRACTION FROM MARLEEN MOORE TO HOWIE CROUCH AT 1613 EDT ON 9/29/15 * * * Based on re-analysis of the data, and with concurrence of USNRC Region I DNMS Inspector (Nguyen), it was determined that the patient received between 82% and 90% of the prescribed dose. Based on this information, this event no longer meets the reporting criteria and is being retracted by the licensee. Notified R1DO (Bower) and NMSS Events Resource (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-10-01
51417 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-09-22 | 2015-09-22 17:22 | 2015-09-22 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION EVENT The following report was received from the State of Colorado via email: "On September 22, 2015, during a routine inspection at Colorado licensee St. Thomas More Hospital and Progressive Care (license CO 397-01), [Colorado State] inspectors noted multiple areas with contamination. Upon further investigation, the inspectors learned a patient earlier in the day was undergoing a diagnostic test involving nebulized Tc-99m DTPA for a lung scan. The patient began coughing and pulled off the mask during administration and coughed, spreading the contamination in the diagnostic area. The patient began to require elevated levels of medical care and nursing staff and nuclear medicine staff may have been contaminated while caring for the patient. Arrangements were made to transfer the patient to a different medical facility via helicopter. The second facility was notified and nuclear medicine technologists surveyed the helicopter and patient upon arrival with no contamination found. "Reporting requirement: 10 CFR 30.50(b)(3); Colorado Part 4, Section 4.52.2.4 "Cause and corrective action: patient intervention. St. Thomas More has closed the affected areas to allow for decay. Surveys will be performed in affected areas prior to re-opening for additional patients. "A full report of investigation and evaluations will follow within the next 30 days. "Incident identification: CO15-I15-27" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-09-30
51416 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-09-21 | 2015-09-22 15:03 | 2015-09-23 | AGREEMENT STATE REPORT - DAMAGED SOURCE HOUSING The following report was received from the State of California via email: "On Sept. 21, 2015, [the] RSO [Radiation Safety Officer for] ExxonMobil contacted Los Angeles County Radiation Management regarding an equipment malfunction to one of the two sources in Vessel #5C31, found during routine maintenance. [Source information]; cesium-137, Model 7063 K-ray; SN: 29456B; 500 milliCuries. Per [the RSO], the source housing was damaged and was left in its normal operating position. Using a Ludlum Model 3, 44-6 beta gamma probe, the background radiation was measured at approx. 0.02 mR/hr and the radiation rate at 1 meter from the source is 0.06 mR/hr. The service company has been contacted and repair/replacement will be performed as soon as possible." California Report 5010#: 092115 * * * UPDATE FROM JOSEPHINE ORTEGA TO JOHN SHOEMAKER AT 1437 EDT ON 9/23/15 * * * The following information was excerpted from a updated report received from the State of California via email: "The shutter was stuck in the open position as used during its normal operating position. Using a Ludlum Model 3, 44-6 beta gamma probe, the background radiation was measured at approx. 0.02 mR/hr and the dose rate at 1 meter in areas outside of the vessel that could be occupied is approx. 0.06 mR/hr. The dose rate obtained in the path of the beam after passing thru two vessel walls is approx. 0.6 mR/hr. The vessel walls are 1 inch thick steel and the vessel diameter is approximately 8 feet." Notified R4DO (Pick) and NMSS_Events_Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-09-30
51415 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-09-22 06:32 | 2015-09-22 07:19 | 2015-09-22 | SECURITY REPORT INVOLVING DEGRADATION IN SAFEGUARDS SYSTEM Degradation in safeguards system that could allow unauthorized access to controlled access area. Compensatory measures taken upon discovery. The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-09-22
51414 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2015-09-20 20:19 | 2015-09-20 22:05 | 2015-09-20 | ALERT DECLARED DUE A FIRE GREATER THAN 15 MINUTES OUTSIDE OF THE FACILITY At 2019 CDT, the licensee declared an Alert due to a truck fire, outside of the protected area, that lasted greater than 15 minutes. The truck was awaiting entry to the plant to deliver materials when the truck driver noticed smoke emanating from the dash. He attempted to put out the fire using a handheld extinguisher but was unsuccessful so he left the vehicle and notified licensee employees. The licensee contacted the Massac County and Metropolis Fire Departments who responded to the site and put out the fire. The cab of the truck is considered a total loss but the trailer was not affected by the fire and remains intact. The licensee is awaiting clearance from the fire department to enable them to take swipes of the trailer to verify no contamination exists. At 2055 CDT, once they determined the fire was out, the licensee downgraded the Alert to a plant emergency. The licensee notified local authorities and the Illinois Emergency Management Agency of the event. Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer and the EPA EOC. * * * UPDATE FROM SEAN PATTERSON TO HOWIE CROUCH AT 2329 EDT ON 09/20/15 * * * At 2216 CDT, the licensee declared all clear for the event when the swipes taken on the trailer did not indicate a spread of contamination. Notified IRD (Gott), NMSS EO (Gonzalez) and R2DO (Sykes) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | IL | FUE |  | 40.35(f) |  |  |  | 0 | 2015-09-24
51413 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-09-19 | 2015-09-20 15:21 | 2015-09-20 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE TO THE SHIELDED POSITION The following information was obtained from the state of Texas via email: "On September 19, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee that one of its radiography crews was unable to return a 63 curie Iridium-192 source to the fully shielded position in an IR-100 exposure device. The licensee stated the radiographer had made several attempts using the crank-outs to return the source to the shielded position, but surveys indicated the source was not fully shielded in the camera. The radiographer isolated the area and contacted the licensee's radiation safety officer (RSO). The RSO contacted a service contractor who is qualified to recover sources who then responded to the location. The retrieval team arrived at the location at 2030 hours [CDT]. The service provider moved the camera to the ground and then straightened source tube. The service provider stated it was apparent that the source would move, but was unable to return the source completely into the camera. The service provider then realized that the key on the camera was locked and that the source indicator was up in the locked position instead of down as it should be when the source is out. The radiographer informed the service provider that the indicator had popped up and that he had removed the key and realized the source was in the exposed position so [he] put the key back in the lock and attempted to crank the source back in. The service provider made several attempts to return the source into the exposure device, but was not able. The service provider had a new set of crank-outs and an empty exposure device delivered to the location. The service provider cranked the source into the [collimator] and placed additional shielding over the source. The guide tube was removed from the original device and the source were disconnected from the drive cable. The drive cable from a different crank-out device was inserted through the new exposure device then connected to the source. The source was then retracted to the fully shielded position in the new device. "The dosimetry of all involved was reviewed periodically during the event. The radiographer trainer's self-reading dosimeter was noted off scale when the service provider arrived at the scene. He was removed from the work area. The service provider believes his exposure was approximately 300 millirem for that day. No other individual received an exposure that exceeded any limit. "The dosimetry for the two radiographers involved in the event will be sent to the processor for reading on September 21, 2015. No member of the general public received exposure from this event. All equipment used in at the site when the failure occurred will be sent to the manufacture for inspection. The cause for the inability to retract the source into the initial exposure device is not currently known. The licensee will investigate the event and provide its findings to this Agency. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-09-28
51412 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-09-17 00:30 | 2015-09-20 02:53 | 2015-09-20 | CONTROL ROOM AREA RADIATION MONITORS NOT ABLE TO PROVIDE RADIATION LEVEL INFORMATION "On 9/17/2015 at 0030 [CDT], during the Byron Station Unit 1 refueling outage, Main Control Room area radiation monitors were removed from service to support an electrical bus outage. During this time, the Main Control Room area radiation monitors were not able to generate Main Control Room annunciation or provide area radiation level information necessary for Emergency Action Level (EAL) threshold determination until the area radiation monitor is restored which is scheduled for 9/20/15. "This event is being reported under 10 CFR 50.72(b)(3)(xiii) for 'Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability.' "The licensee has notified the NRC Resident Inspector." The licensee discovered this issue at 2145 CDT on 9/19/15. The licensee established compensatory measures upon discovery of the issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-09-20
51411 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-09-18 13:00 | 2015-09-19 12:56 | 2015-09-24 | POTENTIALLY EXCEEDING GLOVEBOX MODERATOR MASS LIMITS "EVENT DESCRIPTION Certain operations for development of Advanced Gas Reactor (AGR) fuel are conducted in gloveboxes in BWXT NOG-L's Specialty Fuel Facility (SFF). The amount of U-235 mass and the amount of moderator in the gloveboxes is controlled to prevent an inadvertent nuclear criticality. A 3-tier limit for control of U-235 mass and moderator mass is utilized for the gloveboxes. As the U-235 mass in the box increases, the allowed mass of moderator decreases. Mass/moderator logs are used by the operators to track the amounts of both materials in the gloveboxes. Anomalies with one of these logs were identified during a routine Nuclear Criticality Safety (NCS) audit. During the follow-up investigation it was determined at 1300 [EDT] on September 18th, 2015, the log entries may not have been bookkeeping errors. The Limiting Condition for Operation (LCO) for moderator mass may have been exceeded for four entries on the log. The operators involved stated their understanding at the time of the log entries (July 13 and July 14, 2015) was they needed to adhere to the mass limit or the moderation limit, but not both. In addition, the log contained two entries noted as 'Box Correction' in which no material entered or was removed from the glovebox, but the total amounts of U-235 mass and moderator were adjusted. At this time the reason for the corrections cannot be determined within the required time period for reporting; the investigation is ongoing. Therefore, BWXT conservatively assumes that the material was previously in the box and the log updated to reflect the box's contents. "EVALUATION OF THE EVENT The accident sequence documented in the ISA [Integrated Safety Analysis] for an excessive amount of moderator in this operation credits two IROFS [Items Required Relied on for Safety], operator control of U-235 mass and operator control of moderator mass. Considering the values documented in the mass/moderator log and the operators' understanding of the limits, the U-235 mass in the glovebox was controlled, but the moderator mass may not have been controlled. This IROFS (operator control of mass of moderator) appears to be lost. Under these circumstances the scenario documented in the ISA for a moderator upset does not demonstrate that the performance requirements of 10 CFR 70.61 were maintained. The mass/moderator limits assume the U-235 in the glovebox is 100% enriched in the form of a sphere. The moderating material is assumed to be homogenously mixed with the U-235. The material in the glovebox is actually LEU in [less than or equal to] 2.5 liter containers or other geometrically favorable equipment. The as-found condition presented no immediate safety concern. There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. "NOTIFICATION REQUIREMENTS BWXT is continuing to investigate this event. As stated in FCSS Interim Staff Guidance-12, Revision 1, 10 CFR Part 70, Appendix A - Reportable Safety Events, 'The twenty-four hour time period for reportable events is intended to allow licensees sufficient time to make this determination. However, if the determination cannot be completed within this time frame then the event must be reported to the NRC Operations Center within twenty four hours of discovery.' Due to the timeliness of reporting requirements, BWXT is making a 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(2) - Loss or degradation of items relied on for safety that results in failure to meet the performance requirement of 10 CFR 70.61. "STATUS OF CORRECTIVE ACTIONS SFF glovebox operations utilizing mass moderators logs have been shutdown pending further investigation. Other BWXT NOG-L operations working to the tiered limits have been shutdown pending review of current mass/moderator logs and verification of the operators' understanding of the limits. An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ROB JOHNSON TO STEVE SANDIN AT 1311 EDT ON 9/24/15 * * * "I. EVENT DESCRIPTION "On September 19th, 2015 BWXT NOG-L notified the NRC of a potentially failed IROFS that resulted in a failure to meet the performance requirements of 10 CFR 70.61 (refer to Event Report # 51411). At that time it had been determined that anomalies on a mass/moderator log used to track the amount of U-235 mass and moderator mass in a Specialty Fuel Facility (SFF) glovebox were in error. The glovebox operations in SFF utilizing mass/moderators logs were shutdown pending further investigation. An Extent of Condition Review of other SFF mass/moderator logs was initiated. During this review a similar condition was identified at 4:00 pm on September 23, 2015 for another SFF glovebox. "II. EVALUATION OF THE EVENT "The mass/moderator log in question was used to track materials in another SFF glovebox that worked to similar tiered NCS limits. The entries occurred on 7/6/15 and involved some of the same operators. Based on the log entries the Limiting Condition for Operation (LCO) for moderator mass was apparently exceeded three successive times. "The glovebox had been previously shutdown except for operations required to maintain regulatory compliance for materials accountability. These limited operations are conducted under the oversight of area management and an NCS engineer. The glovebox was in compliance with the NCS posted limits at the time of the discovery of the mass/moderator log anomalies entered in July. There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event "Ill. NOTIFICATION REQUIREMENTS "BWXT is revising Event Report # 51411 dated September 19, 2015. A similar condition was identified during the Extent of Condition Review that indicates the IROFS of operator control of mass of moderator for another SFF glovebox has failed. The condition is still under investigation. The performance requirements of  70.61 have not been maintained. Due the timeliness of the reporting requirement, BWXT is making this 24 hr. report in accordance with 10 CFR 70, Appendix A, (b)(2) - Loss or degradation of items relied on for safety that results in failure to meet the performance requirement of  70.61. "IV. STATUS OF CORRECTIVE ACTIONS "An investigation of the root causes of this event is still ongoing. Corrective actions will be determined as a result of the investigation. Glovebox operations in SFF will remain shutdown pending the results of the investigation and the implementation of corrective actions." The licensee has notified the NRC Resident Inspector and Region 2 (Michel, Munson). Notified R2DO (Sandal) and NMSS EO (McCartin). Notified Fuels Group OUO and NMSS_Events_Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 1 | 2015-09-28
51410 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-09-18 20:00 | 2015-09-19 00:11 | 2015-09-19 | REACTOR VESSEL HEAD PENETRATION REPAIR DID NOT MEET ACCEPTANCE CRITERIA "On 9/18/2015 at 20:00 [CDT], during the Byron Station Unit 1 refueling outage, it was determined that the results of a planned Liquid Penetrant (PT) examination performed on a previous overlay repair of the reactor vessel head did not meet applicable acceptance criteria. The penetration requires repairs prior to returning the vessel head to service. These indications are not in the reactor coolant pressure boundary; however they are very near the previously repaired J-groove weld. The examination was being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1, to ensure the structural integrity of the reactor vessel head pressure boundary. No ultrasonic indications have been identified at this time. Repairs are currently being planned in accordance with the ASME Code of Record. The repairs will be completed prior to returning the vessel head to service. "This event is being reported under 10 CFR 50.72(b)(3)(ii)(A) for 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' "The licensee has notified the NRC Resident Inspector. "Per regulatory commitment, Exelon Generation Company, LLC (EGC) is notifying NRC staff of the Division of Component Integrity or its successor, of changes in indication(s) or findings of new indication(s) in the penetration nozzle or J-groove weld beneath a seal weld repair, or new linear indications in the seal weld repair, prior to commencing repair activities. "The original indications that led to the overlay repairs were discovered during ultrasonic testing and were reported to the NRC and assigned EN46686 and EN48311." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-09-19
51409 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-09-18 14:08 | 2015-09-18 18:01 | 2015-09-18 | EQUIPMENT FAILURE RESULTS IN INOPERABLE SECONDARY CONTAINMENT "At 1408 EDT on 9/18/2015, Secondary Containment Refuel Floor exhaust flow degraded due to an equipment malfunction in the running Refuel Floor exhaust train. The degraded exhaust flow caused Secondary Containment differential pressure to go positive for approximately three minutes, resulting in Secondary Containment being declared inoperable. Corrective action to start the Stand-by Gas Treatment System and the alternate Refuel Floor exhaust train restored Secondary Containment operable by re-establishing its required negative differential pressure. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG-1022, Rev. 3, 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The Duty Team has been activated to develop a repair plan. "The NRC Resident Inspector has been notified." | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-09-18
51408 | 0 | KNAUFF INSULATION |  |  |  |  | 2015-09-01 | 2015-09-18 15:34 | 2015-09-18 | LOST GAS CHROMATOGRAPH SOURCE When requested by the NRC, the licensee was unable to locate a 15 mCi Ni-63 source. The source was used in a Perkin-Elmer gas chromatograph electron capture detector. The licensee noted that the device may have been decommissioned, but a fire at their facility effectively destroyed all records that could be used to located the source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-09-28
51407 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-09-17 12:30 | 2015-09-18 11:59 | 2015-09-18 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was received from the State of Texas via email: "On September 18, 2015, the Agency [Texas Department of State Health Services] was informed by the licensee's radiation safety officer (RSO) that a radiography crew had experienced a source disconnect at a temporary field site [Galveston, Texas]. The RSO stated the crew was working inside a vessel using a QSA 880D exposure device containing a 52.9 curie Iridium-192 source. The device fell from a distance of 30 feet and hit the floor of the vessel. The source was in the fully shielded position when the device fell. The radiographers noted the guide tube had a small kink in it and replaced the guide tube. The radiographers tested the source by cranking the source out, but when they attempted to retract the source, the drive cable did not stop at the rear outlet of the camera. The radiographers contacted their supervisor and performed a dose rate survey at their barrier. The dose rate was 1 millirem per hour. An individual qualified in source recovery was able to remove the source from the guide tube and place it in a source changer for storage. The RSO stated their inspection of the source drive cable found the connecter on the drive cable had separated from the drive cable. The RSO stated all equipment involved in the event will be returned to the manufacturer for inspection. No individual received an over exposure as a result of this event. No member of the general public received an exposure due to this event. The licensee is conducting an investigation into the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: I-9339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-09-28
51406 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-09-17 16:10 | 2015-09-17 21:32 | 2015-09-17 | MINIATURE ALCOHOL BOTTLE DISCOVERED INSIDE THE PROTECTED AREA "A miniature alcohol bottle, containing trace amounts of liquid, was discovered inside the protected area. Site security took possession of the bottle and removed it from the protected area." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2015-09-17
51405 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-09-17 12:20 | 2015-09-17 16:24 | 2015-09-17 | BRIEF LOSS OF SECONDARY CONTAINMENT DUE TO BOTH AIRLOCK DOORS OPEN SIMULTANEOUSLY "At 1220 (EDT) on 9/17/2015, both doors of a Secondary Containment airlock were reported to be simultaneously open for approximately five seconds during the normal passage of personnel. The brief time that the doors were simultaneously open constitutes an inoperable condition of Secondary Containment. Secondary Containment differential pressure was maintained throughout the time period that the doors were open. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG-1022, Rev. 3, 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-09-17
51404 | 0 | JANX |  |  |  |  | 2015-09-16 12:15 | 2015-09-17 11:36 | 2015-09-17 | RADIOGRAPHY CAMERA SOURCE DISCONNECT While the licensee was performing radiography work in Twilight, West Virginia, a radiography camera (SPEC-150; Ir-192; 72 Ci; S/N: WH0603) source became disconnected and did not return to the shielded position. The West Virginia site called the corporate RSO at 0200 on 9/17/2015, who then called a qualified Pennsylvania RSO in order to supervise source retraction. The qualified RSO verified boundaries at the 2mR level. The source was retrieved and placed in the shielded position. The camera was secured and is out of service. There was no indication of excessive dose. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-09-25
51403 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2015-09-16 23:01 | 2015-09-17 02:53 | 2015-09-17 | NOTIFICATION OF UNUSUAL EVENT DUE TO RAPID COMBUSTION OF A LOAD CENTER BREAKER "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event, or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "Non Class Load Center Breaker, 2ENGN-L04 failed, resulting an a visible observation of rapid combustion and resultant charring (burned area) of the breaker enclosure and housing. No physical deformation to the breaker housing or surrounding area has been identified. The rapid combustion self-extinguished immediately following the audible and visible combustion event. As a result, an Emergency Classification of HU2.2, EXPLOSION was declared due to the Load Center breaker failure and noise and visible indication observed in the field. "The plant was, and continues to operate at 100% full power operations on normal power alignment. The 2ENGN-L04 Non-Class Load Center breaker supplies power to non-essential service loads and has no immediate impact to plant operation or safety mitigating systems. The plant remains stable and the event did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified." Notified DHS SWO, DHS NICC, FEMA, and Nuclear SSA via email. * * * UPDATE FROM ROBERT PIERCE TO HOWIE CROUCH AT 0702 EDT ON 9/17/15 * * * "PVNGS Unit 2 terminated the Unusual Event HU2.2 on 9/17/15 at 04:04 MST. Non-Class load center 2ENGN-L04 has been isolated and de-energized. There was no reflash or fire at the breaker and no hazard to plant personnel exists. Damage appears to be limited to the NGN-L04D3 breaker cubicle and a spare breaker cubicle below NGN-L04D3. There was no damage to any safety related equipment." The licensee will be notifying the state of Arizona, Maricopa County authorities and the NRC Resident Inspector. Notified R4DO (Farnholtz), NRR EO (Morris), IRD MOC (Gott), DHS SWO, FEMA Ops, DHS NICC and NuclearSSA (email). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-09-17
51402 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-09-16 20:14 | 2015-09-17 00:36 | 2015-09-17 | AUTOMATIC START AND LOADING OF THE #2 EMERGENCY DIESEL GENERATOR "While performing degraded voltage/under voltage Instrumentation & Control testing with both Units at 100%, the Unit 2 'H' Emergency Bus was lost when an inadvertent under voltage matrix was satisfied. The #2 Emergency Diesel Generator auto-started and assumed the 2H Emergency Bus as designed. The cause of the under voltage matrix coincidence is currently being investigated by station personnel. All testing activities have been terminated and recovery efforts are in progress in accordance with station procedures. Current status is both Units stable at 100% with the #2 Emergency Diesel Generator carrying the 2H Emergency Bus." The loss of the bus places the Unit in a 7-day action statement for the loss of offsite power to the 2H bus and a 14-day action statement for the auxiliary feed cross tie to Unit 1. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-09-17
51401 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-09-16 22:00 | 2015-09-16 21:17 | 2015-09-16 | LOSS OF SEISMIC MONITORING INSTRUMENTATION DURING PLANNED MAINTENANCE "At 2200 CDT on September 16, 2015, Byron Station's Seismic Instrumentation will be removed from service to support an electrical bus outage. During this time, the seismic instrumentation will not be able to generate Main Control Room annunciation or provide ground acceleration information necessary for Emergency Action Level (EAL) threshold determination until the seismic instrumentation is restored, which is scheduled for 1700 CDT on September 19, 2015. Since the duration of maintenance activity may last greater than 72 hours, with viable compensatory measures in place and communicated to applicable Emergency Response Decision Makers, this condition will result in a Loss of Emergency Assessment Capability while the Seismic Instrumentation is out of service and results in a reportable condition in accordance with 10 CFR 50.72(b)(xiii). "The Licensee has notified the NRC Resident Inspector and informed the State of Illinois Resident Engineer ." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-09-16
51400 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-09-16 | 2015-09-16 14:34 | 2015-09-16 | FLORIDA AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE WITH STUCK OPEN SHUTTER The following information was received from the State of Florida via email: "The RSO [Radiation Safety Officer] at Georgia Pacific Corporation in Palatka, Florida called to report [to the State of Florida that] a fixed Cesium-137 source installed on the top half of a tank has the shutter stuck open. Device originally had 2,000 mCi, but now is estimated to have 892 mCi of Cs-137. This same equipment was reported with the same defect on April 9, 2015 (FL15-025). There is no report of any over exposure of personnel and no leaks (confirmed by leak test). The location of the device prohibits the access of personnel and the shutter is only closed when maintenance or repair is performed. The RSO has put in a work order for repair and will provide a copy of a report confirming the equipment was serviced/repaired back in April. Initial NRC Event Notification #50971." The fixed gauge manufacturer is Kay-Ray, Model number - 7063P, serial number 10682F. FL Incident Number: FL 15-094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-09-24
51399 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2015-03-10 | 2015-09-16 11:38 | 2015-09-16 | KENTUCKY AGREEMENT STATE REPORT - STUCK SHUTTER MECHANISM The following information was obtained from the Commonwealth of Kentucky via facsimile: "[This failure was] not previously reported by licensee to RHB [KY Radiation Health Branch], but recent inspection of facility [performed on 8/4/2015] showed that the defect was noted on 3/10/15 during the routine 6 month inventory and shutter check updates. "Equipment failure: On-Off shutter mechanism on KAYRAY/Sensall 7062BP (Cs-137, 100 mCi; Serial No. 2975) fixed gamma gauge has broken spring. Shutter is kept in open position by makeshift wire fastener. No release of radioactivity. (Sealed Source capsule model 7700Y). Last leak test on 3/19/15 showed MDA (<5 nCi)." Event Report ID No.: KY 150006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2015-09-24
51398 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-09-16 02:00 | 2015-09-16 10:10 | 2015-09-16 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE DUE TO VALVE STEM PACKING STEAM LEAK "At 0200 CDT on 9/16/2015, the High Pressure Coolant Injection (HPCI) System was manually isolated to stop a steam leak from the stem packing of the HPCI Steam Supply Valve 2-FCV-073-0016. The leak occurred following performance of 2-SR-3.6.1.3.5 (HPCI) HPCI System Motor Operated Valve Operability, which cycled 2-FCV-073-0016. No Area Radiation Monitoring (ARM) or PCIS Area High Temperature alarms were received and no automatic isolation setpoints were reached. HPCI was declared inoperable per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.1 Emergency Core Cooling Systems (ECCS)- Operating, Condition C. "This constitutes an unplanned HPCI system inoperability and requires an 8-hour ENS notification in accordance with 10 CFR 50.72(b)(3)(v)(D), due to the failure of a single train system affecting accident mitigation, and a 60-day written report in accordance with 10 CFR 50.73(a)(2)(v)(D). "The NRC resident inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-09-16
51397 | 0 | PALISADES | 1 |  |  | [1] CE | 2015-09-16 01:17 | 2015-09-16 03:59 | 2015-09-16 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0117 [EDT] on 9/16/2015 a reactor trip occurred (4-hr non-emergency). The plant was at approximately 85% power performing a coastdown in preparation for a refueling outage when a Digital Electro-Hydraulic (DEH) alarm was received in the control room. Shortly following receipt of the alarm the turbine tripped. This resulted in an RPS actuation and a reactor trip on Loss of Load. The crew entered EOP-1 Standard Post Trip Actions and completed all required actions. The crew subsequently entered EOP-2 Reactor Trip Recovery. "All full-length control rods inserted fully. Auxiliary Feedwater System actuated in response to low steam generator water levels (8-hr non-emergency). Steam generator water levels are in progress of being returned to normal operating levels. No known primary to secondary leakage. Atmospheric Steam Dump Valves lifted after the trip and subsequently reseated. "The plant is currently stable in Mode 3 at NOP/NOT being maintained by the Turbine Bypass Valve. "Initial investigation into the cause of the turbine trip appears to be from a DEH power supply failure. "The NRC Resident Inspector was notified of the reactor trip at 0139 on 9/16/2015." | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-09-16
51396 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2015-09-14 | 2015-09-15 15:52 | 2015-09-15 | SOUTH CAROLINA AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE WITH A STUCK SHUTTER The following information was provided by the State of South Carolina via email: "The licensee provided notification of a stuck shutter, on a Berthold Model LB7440D fixed gauging device, discovered while performing a semi-annual shutter check. The gauging device contains 30 mCi of Cs-137. The device remains mounted to the process piping with no gap available to permit personnel exposure to the radiation beam. A licensed contractor has been contacted and will proceed with corrective maintenance on the shutter mechanism within the next 30 days." State Event Report ID No.: SC-04-2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2015-09-23
51395 | 0 | WESTINGHOUSE |  |  |  |  | 2015-09-15 | 2015-09-15 09:14 | 2015-09-15 | PART 21 REPORT - POTENTIALLY AFFECTED COILS USED IN FREEDOM SIZE 1 AND SIZE 2 STARTERS AND CONTACTORS The following information was excepted from a facsimile: "The Basic component that contains the potential defect is manufactured by Eaton Corporation and commercially dedicated by Westinghouse. The coil (part number 9-3285-19) is used in Freedom Size 1 and Size 2 starters and contactors. Westinghouse has delivered potentially affected parts to the LaSalle generating station. "These coils are to be manufactured using high temperature wire as dictated in the Westinghouse qualification program and per Eaton's manufacturing documentation. After the in-service failure at the plant, a sample was taken and subjected to Fourier Transform Infrared Spectroscopy to verify the correct wire was used during manufacturing. This analysis resulted in the finding that the coil windings were not manufactured using the required high temperature wire and were manufactured from a lower temperature class of wire that was not qualified for use in full voltage non-reversing (FVNR) applications. These coils are manufactured by Eaton at their Haina, Dominican Republic facility. "The lower temperature wire is acceptable in full voltage reversing (FVR) applications, but not in FVNR applications as dictated by the Westinghouse qualification The safety concern is if these coils were used in redundant safety related applications and were to fail, that safety function may not be available. The failure is due to heat and would not likely occur simultaneously, but more likely would occur at random times. Due to the limited data available on these coil failures, the possibility of simultaneous failures cannot be eliminated. "Forty-three potentially affected coils were delivered to LaSalle. Forty one were supplied as spare parts and were never installed in the plant. One coil was supplied and installed at the plant and failed after 6 weeks of service. An alarm was annunciated in the control room and the part was replaced. One additional coil was supplied and installed at the plant. This was removed from service and the coil was sent for testing. The coil in this starter was made from the correct material. "Eaton has confirmed to Westinghouse that this issue may affect coils made between May 29, 2014 and November 3, 2014. Westinghouse has informed its customer and identified the potentially affected coils to them. The customer has identified the affected parts and has returned them to Westinghouse for replacement. Westinghouse has purchased a lot of new coils and sent samples to have the coil wire verified (destructive testing). Future deliveries will be supplied from these dedicated coils. There are currently no potentially affected parts in service." For additional information, contact Mr. James A. Gresham, Regulatory Compliance, Westinghouse Electric Company, 1000 Westinghouse Drive, Suite 310, Cranberry Township, Pennsylvania 16066. Phone number: (412) 374-4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-09-15
51394 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2015-07-16 | 2015-09-15 07:12 | 2015-10-30 | INTERIM PART 21 REPORT - ACTUATOR FAIL MODE DEVIATION AND POTENTIAL NON-CONSERVATIVE ACTUATOR SIZING The following information was received via fax: "Pursuant to 10 CFR 21.21(a)(2), Fisher Controls International LLC ('Fisher') is providing required written interim notification of a deviation or failure to comply in product shipped to the Krsko Nuclear Station ('Krsko') located in Slovenia. "On July 16, 2015, Fisher became aware of an issue with an actuator fail mode for an 8 [inch] 2052- Control Disc valve, Serial Number 19443837. The affected valve was supplied in a 'Fail Closed' configuration rather than the desired 'Fail Open' configuration. Fisher has corrected the configuration and retested the affected valve at the Krsko site. Krsko has since accepted the valve for installation. "During the investigation, it was also noted there was an increase in one of the sizing factors for the valve that may have led to a non-conservative actuator sizing for this and other valves provided to this Krsko site. Fisher is currently performing an extent-of-condition review of safety-related rotary orders in order to confirm that correct orientations and actuator sizing were provided. Any identified deficiencies will be reported per the requirements of 10 CFR21.21(b). This review is expected to be completed by October 23, 2015. Additionally, all current safety related rotary orders in-house are being reviewed prior to shipment. This notice affects only rotary valves with Fisher factory mounted actuators. "Corrective Action CAR 1756 has been opened to document corrective actions taken to prevent reoccurrence. "Should there be any further questions concerning this matter, please contact Benjamin Ahrens, Manager, Quality by email at Benjamin.Ahrens@Emerson.com or via phone at 641-754-2249." * * * UPDATE FROM GEORGE BAILINGER (VIA FAX) AT 1634 EDT ON 10/30/15 * * * As excerpted from the fax: "Extent of condition investigations into both issues have determined that no additional valve configurations have shipped with these deficiencies." Fisher issued Fisher Information Notice 2015-02 pertaining to the particulars of this event. Notified R1DO (Cahill), R2DO (Bonser), R3DO (Duncan) and R4DO (Okeefe). NRR/NRO Part 21 group was notified via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2015-09-15
51393 | 0 | NOAA MARINE LABORATORY |  |  |  |  | 2014-04-01 | 2015-09-14 14:07 | 2015-09-14 | LOST HEWLETT-PACKARD GAS CHROMATOGRAPH "The NOAA Atlantic Oceanographic and Meteorological Laboratory (AOML) reported a lost Ni-63 source. The licensed device is an [generally licensed, Hewlett Packard/Agilent Technologies Gas Chromatograph, [Model 5890A, Serial Number M1827, containing a 15 mCi Ni-63 source]. [It was discovered that the chromatograph was missing after an April 2014 inventory.] According to several end users of the device, the item was disposed of prior to the annual 2014 inventory. To the best of NOAA's knowledge, the device was disposed of through UNICOR and the Federal Bureau of Prisons (FBP) by a previous property custodian, who has since retired from the agency. Documentation does not exist for this transfer. Another previous property custodian, requested that this item be removed from AOML inventory on 8/4/2014, based on the verbal report from the previous property custodian. Between July 28 and August 19th, 2014, the current property custodian unsuccessfully attempted to contact UNICOR, to confirm that this device did get transferred to UNICOR." It cannot be confirmed the device was been disposed of via UNICOR and is therefore considered lost. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | FL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-09-22
51392 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-09-14 04:26 | 2015-09-14 08:12 | 2015-09-14 | MANUAL REACTOR TRIP DUE TO LOSS OF POWER TO VITAL INSTRUMENT BOARD "At 0426 EDT on 9/14/2015, Sequoyah Unit 1 was at 100% power when the Vital Instrument Power Board (VIPB) 1-II deenergized. A manual reactor trip was initiated in accordance with the Abnormal Operating Procedure for the loss of VIPB 1-II. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP [Normal Operating Temperature/Normal Operating Pressure], approximately 547 degrees F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. "Current Temperature and Pressure - Reactor Coolant System (RCS) temperature is 547 degrees F and stable and RCS pressure is 2235 psig and stable. There is no indication of any primary to secondary leakage. All rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100 [percent]. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector. " | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2015-09-14
51391 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-09-13 23:05 | 2015-09-14 02:46 | 2016-02-27 | MANUAL SCRAM DUE TO LOSS OF TURBINE BUILDING CLOSED COOLING WATER "At 2305 EDT on September 13, 2015, a manual scram was initiated in response to a loss of all Turbine Building Closed Cooling Water (TBCCW). All control rods fully inserted. The lowest Reactor Water Level (RWL) reached was 137 inches. All isolations and actuations for RWL 3 occurred as expected. Decay heat was initially being removed through the Main Turbine Bypass System to the Main Condenser, however, as a result of the loss of TBCCW, the Main Feed Pumps lost cooling and had to be secured. At 2310, Standby Feedwater was initiated and Main Feedwater was secured. "The loss of TBCCW also caused all Station Air Compressors (SACs) to trip on loss of cooling. The loss of SACs caused the Instrument Air header pressure to degrade to the point at which the Secondary Containment isolation dampers drifted closed. This resulted in the Reactor Building vacuum exceeding the Technical Specification limit. At 2325, operators started the Standby Gas Treatment system and manually initiated a Secondary Containment isolation signal. Secondary Containment vacuum was promptly restored to within Technical Specification limits. Additionally, Operators were monitoring for expected MSIV drift due to the degraded Instrument Air header pressure. When outboard MSIVs were observed to be drifting, Operators closed the outboard and inboard MSIVs at 2345. At 2352, Safety Relief Valves (SRVs) reached the Low-Low Setpoint and began cycling to control reactor pressure. "RWL is currently being maintained in the normal level band with the Standby Feedwater and Control Rod Drive systems. Reactor Pressure is being controlled with Safety Relief Valves. Operators are currently in the Emergency Operating Procedure for Reactor Pressure Vessel control. Investigation into the loss of TBCCW continues. "No safety-related equipment was out of service at the time of the event. All offsite power sources were adequate and available throughout the duration of the event. "The NRC resident inspector has been notified." * * * UPDATE AT 0555 EDT AT 09/14/15 FROM CHRIS ROBINSON TO JEFF HERRERA * * * "At 0409 EDT the Reactor Core Isolation Cooling (RCIC) system was placed in service due to identification of an unisolable leak in the Standby Feedwater System. Reactor water level and pressure is now being controlled though the RCIC system and Safety Relief Valves. This event update is reportable as a valid manual initiation of a specified safety system under 10CFR50.72(b)(3)(iv)(A). "The NRC resident inspector has been notified." The leak rate was reported as approximately 5-10 gallons per minute from a weld on the standby feedwater pump header drain valve F326. The licensee reported the leak stopped once RCIC was placed into service. The licensee is still investigating the issue. Notified the R3DO (Pelke), IRD Manager (Grant), NRR EO (Morris). * * * UPDATE PROVIDED BY CHRIS ROBINSON TO JEFF ROTTON AT 2135 EDT ON 09/14/2015 * * * "At 1847 EDT on September 14, 2015, a valid automatic Reactor Protection System (RPS) actuation occurred due to Reactor Water Level 3 while shutdown in MODE 3. Operators were manually controlling Reactor Pressure Vessel (RPV) level and pressure with Reactor Core Isolation Cooling (RCIC) and Safety Relief Valves (SRV). While operators were cycling SRVs, the RPV level went below the Level 3 setpoint. Operators promptly restored RPV level by manual operation of RCIC. The Level 3 actuation and associated isolations were verified to operate properly. "The scram signal has been reset. Fermi 2 remains in MODE 3 controlling RPV Level and Pressure through manual operation of RCIC and SRVs. "This is the second occurrence of a valid specified safety system actuation reportable under 10CFR50.72(b)(3)(iv)(A) for this ongoing event. "The NRC Resident Inspector has been notified." Notified R3DO (Riemer), IRD Manager (Grant), and NRR EO (Morris) * * * UPDATE FROM BRETT JEBBIA TO JOHN SHOEMAKER AT 1446 EST ON 2/27/16 * * * "This update provides clarification of the applicable reporting criteria for this Event associated with primary containment isolation actuations. "Upon the manual reactor scram at 2305 EDT on September 13, 2015, Reactor Protection System (RPS) Level 3 actuated and Primary Containment Isolation System (PCIS) Groups 4, 13 and 15 actuated as expected. The applicable reporting criterion for these actuations is 10 CFR 50.72(b)(3)(iv)(A). "The applicable reporting criterion for the manual closure of the inboard and outboard main steam isolation valves at 2345 EDT on September 13, 2015, is also 10 CFR 50.72(b)(3)(iv)(A). In addition, the manual closures of all MSIV lead to a loss of condenser vacuum which resulted in the actuation of PCIS Group 1 at 0001 EDT on September 14, 2015, as expected. The applicable reporting criterion for this actuation is also 10 CFR 50.72(b)(3)(iv)(A). "Upon reaching Level 3 at 1847 EDT on September 14, 2015, PCIS Groups 4, 13 and 15 actuated as expected. The applicable reporting criterion for this actuation is 10 CFR 50.72(b)(3)(iv)(A). "The licensee informed the NRC Resident Inspector." Notified the R3DO (Stone). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | POT UNCNTRL RAD REL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(iv)(A) |  | 0 | 2015-09-14
51390 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2015-09-10 | 2015-09-11 16:41 | 2015-09-11 | AGREEMENT STATE REPORT - MEDICAL TREATMENT DOSE LOWER THAN PRESCRIBED The following was received from the State of New York via fax: "A New York State licensee informed the Department [New York State Department of Rad Health] of a patient receiving HDR therapy being delivered a fractionated dose that differed from the prescribed fractionated dose by more than 50 percent. The written directive called for a vaginal treatment consisting of three fractions of 1050 cGy per fraction. The second of the three fractions was scheduled on September 10, 2015. Treatment began as planned with both the AU and the AMP at the console. After successful extension and retraction of the dummy source, it was noticed that treatment countdown time was increasing instead of decreasing. The source extension was in contradiction to the console, which indicated 'treatment terminated' although the source extension warning light was also activated near the console. Two AMPs engaged the Emergency-Stop, terminating the treatment and retracting the source to the shielded position. Surveys of the patient and the HDR unit verified that the source was returned to the shielded position. The HDR console indicated that 41.8 seconds had elapsed with source extended. The Patient received an estimated dose of 105 cGy. The patient was informed of the event and no further patients were treated that day. "Electa was contacted and a service engineer arrived that same afternoon. He was unable to reproduce the fault condition. Electa is currently investigating the internal performance log of the unit. The physicist performed a complete QC and no aberrations were noted. The HDR unit seems to be performing properly. The last source exchange was on August 14, 2015. Source activity on 9/10/15 was approximately 8 curies." New York event # NY-15-08 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-09-21
51389 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-09-10 17:45 | 2015-09-11 16:07 | 2015-09-11 | AGREEMENT STATE REPORT - INDUSTRIAL RADIOGRAPHY CAMERA SOURCE DISCONNECT The following report was received from the State of Colorado via email: "Event description: The Department [Colorado Department of Public Health and Environment] received a phone report from [licensee] on 09/11/15, at 0906 [MST]. It was reported that a source disconnect occurred on 09/10/15, at about 1745. At that time, the licensee RSO [Radiation Safety Officer], went out and retrieved the source according to procedures for source retrieval. The source was successfully retrieved, and no over exposure was reported. "The Department [Colorado Department of Public Health and Environment] is preparing for a visit to investigate the event and is expecting a full report from the licensee within 30 days. No reported over exposure from this event." No additional information on the Radiography Camera or source strength is available at this time. Event Report ID No.: CO15-I15-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-09-21
51388 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-08-26 | 2015-09-11 15:42 | 2015-09-11 | AGREEMENT STATE REPORT - LOST RADIOACTIVE MATERIAL The following information was received from the State of California via email: "On August 26, 2015, [Nordion] shipped three packages containing approximately 200 mCi of Yttrium-90 to Hoag Hospital by [a commercial shipping company]. One of the three packages did not arrive at Hoag Hospital. The Radiation Safety Officer (RSO) reported that [Nordion] was contacted on 8/27/15, to report that one of the three packages had not arrived. [Nordion] told the RSO that they reported this event to the Canadian authority and that [the commercial shipping company] was the responsible party since [Nordion] had turned the packages over to [the commercial shipping company] for shipping. The [commercial shipping company] health physics consultant contacted [California Department of Public Health/Radiologic Health Branch] CDPH/RHB on 9/11/15, (this was the first CDPH/RHB learned of this event) to report that a [commercial shipping company] investigation had identified that the missing package had fallen off of a conveyor belt in the [the commercial shipping company's] Costa Mesa, CA sorting facility and landed in a waste container. This information was identified by [the commercial shipping company] personnel review of video within their facilities. The package was not noticed to have fallen into the waste container, and the waste container was subsequently emptied into a larger trash receptacle by a cleaning crew. The larger trash receptacle was picked up for disposal at a local landfill. The half life of the Y-90 is 64 hours." California report #091015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-09-21
51386 | 0 | GE-HITACHI NUCLEAR ENERGY |  |  |  |  | 2015-04-16 | 2015-09-10 15:50 | 2015-09-10 | PART 21 REPORT - POTENTIAL FAILURE OF ELECTROMATIC RELIEF VALVE CUTOUT SWITCHES The following information was excerpted from an Interim Part 21 Report, received from GE-Hitachi (GEH) via email: "[This GEH Report #MFN-15-042 R2, is a closure of a Part 21 60-Day Interim Report Notification, containing] information concerning an evaluation of the failure during bench testing of Electromatic Relief Valve Actuators (ERV - GEH Part number 352B2632G001) caused by the failure of a cutout switch to determine applicability to components previously supplied to and accepted by licensees. GEH has performed component testing but has been unable to complete the evaluation to determine if a Reportable Condition, in accordance with 10 CFR 21.21 exists. "Testing was unable to model plant conditions with sufficient accuracy to draw conclusions based on the results. As such, in accordance with discussions with the sites previously identified as potentially applicable to this concern, GEH will close this 10 CFR Part 21 evaluation with a 10 CFR 21.21(b) Transfer of Information to the Dresden 2 and 3 and Quad Cities 1 and 2 sites." References 1. 60-Day Interim Report Notification, Titled: Potential Failure of Electromatic Relief Valve Cutout Switch, Numbered: MFN 15-042 R0, Dated: June 12, 2015. 2. 60-Day Interim Report Notification, Titled: Potential Failure of Electromatic Relief Valve Cutout Switch, Numbered: MFN 15-042 R1, Dated: June 22, 2015. The original notification was reported on June 12, 2015. Because there was a proprietary information disclaimer at the top of that page, GEH revised the original report and submitted that revised letter on June 17, 2015. The revision 1 letter was posted in ADAMS with the following accession numbers as the original report. - ML15169A007 - Part 21 60-Day Interim Report Notification: Potential Failure of Electromatic Relief Valve Cutout Switch. (2 page(s), 6/17/2015) - ML15169A008 - Attachment 1 - US Plants Potentially Affected. (1 page(s), 6/18/2015) - ML15169A009 - Attachment 2 - 60-Day Interim Report Notification Information per 21.21(a)(2). (2 page(s), 6/18/2015) - ML15169A010 - Enclosure 1 - MFN 15-042 R0 - Description of Evaluation. (6 page(s), 6/18/2015) If you have any questions, please call; Dale E. Porter Safety Evaluation Program Manager GE-Hitachi Nuclear Energy Americas LLC Ph: (910) 819-4491. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-09-10
51385 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-09-10 08:31 | 2015-09-10 11:35 | 2015-09-10 | CONTRACT SUPERVISOR TESTED POSITIVE FOR ALCOHOL "A contract supervisory employee had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. "The licensee has notified the NRC Resident Inspector." | 100 | 94 | 0 | 100 | 94 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2015-09-10
51384 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2015-09-08 | 2015-09-10 10:40 | 2015-09-10 | AGREEMENT STATE REPORT - ORPHAN Ra-226 SOURCE The following report was received via e-mail: "KY RHB [Kentucky Radiation Health Branch] was notified on 9/8/2015 via the request and issuance of DOT Special Permit No. 10656 KY-KY-15-018 of a rail car emitting ionizing radiation above normal background levels. Personnel at the facility performed exposure rate surveys on the exterior of the rail car. Highest reading was reported as 20 mR/hr with a background reading of 0.005mR/hr. The rail car was returned to the point of origin on 9/8/2015. On 9/9/2015 RHB dispatched a team of inspectors to the origin facility in order to better determine the source of the ionizing radiation. The team discovered 1 Ra-226 static eliminator bar most likely registered under SS&D certificate number NR-654-D-829-U. The team further discovered additional pieces of what appear to be at least one more static eliminator bar in the vicinity of the facility's metal shredding equipment. At this time no removable contamination has been found and there are no indications of personnel overexposures. A decommissioning, decontamination contractor has been contacted by the facility. RHB continues to monitor the situation with onsite inspectors. RHB will update the Commission as more information becomes available. RHB is tracking this event as KY-15-0006." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2015-09-18
51382 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2015-09-09 11:02 | 2015-09-09 18:42 | 2015-09-29 | POTENTIALLY CONTAMINATED EMPLOYEE TRANSPORTED OFFSITE FOR MEDICAL ASSISTANCE "On Wednesday, September 9, 2015 at 1102 PDT, while trouble shooting process equipment in the ceramic area, an instrument technician got his right thumb caught between two pieces of equipment and severed the nail and part of the end of his thumb. The individual received first aid in the health and safety technician (HST) office and was surveyed for radioactive contamination and was found clean (the injured gloved hand was bandaged and was not surveyed). The injured individual, accompanied by an HST and survey instruments, was transported to a medical facility for treatment. "After the injured individual was unbandaged by medical personnel, the HST surveyed the injured individual and portions of the medical facility and confirmed that no radioactive contamination was on the injured individual's hand nor had any spread to the facility. The bandage and damaged glove was returned to the plant and laboratory instrumentation was used to confirm that it was also free from contamination. "This report is being made under 10 CFR 70, Appendix A, Section C, 'concurrent reporting,' because the severed thumb requires a 24 hour report to Washington State Division of Occupational Safety & Health per Washington Administrative Code (WAC) 296-27-031. It is also conservatively being reported under 10 CFR 70.50 (b)(3), 'treatment of an individual with radioactive contamination,' because a small portion of the individual had not been surveyed and confirmed to not have any contamination prior to transporting the individual to a medical facility." The Licensee will notify NRC Region 4 during business hours on 9/10/15. * * * UPDATE FROM CALVIN MANNING TO HOWIE CROUCH AT 1822 EDT ON 9/29/15 * * * "On September 9, 2015, the AREVA Inc. Richland facility reported per the requirements of 10 CFR 70 Appendix A, section C, that an employee doing maintenance work severed the nail and part of the end of their thumb which required reporting to the Washington State Division of Occupational Safety & Health per Washington Administrative Code (WAC) 296-27-031. "AREVA also conservatively reported, under 10 CFR 70.50(b)(3), treatment of an individual with radioactive contamination, because although the employee was surveyed for radioactive contamination and found to be free from such contamination prior to transport to a medical facility, a small portion of the individual had not been surveyed due to bandages on the injured hand. A Radiation Technician porting a radiation detection instrument accompanied the individual to the medical facility and when the bandage was removed confirmed that the hand, the bandage material and the medical facility room were all free from radioactive contamination. Based on this finding, AREVA retracts the portion of the report dealing pertaining to 10 CFR 70.50(b)(3). "It is noted that a 60-day follow-up report is not required by 10 CFR 70 Appendix A for concurrent reporting (section C), therefore AREVA does not anticipate further correspondence with the NRC regarding this matter." Notified R4DO (Vasquez), R2DO (Ayres), NMSS EO (Guttman), NMSS Events Resource (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2015-09-09
51381 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-09-02 | 2015-09-09 15:50 | 2015-09-09 | LOUISIANA AGREEMENT STATE REPORT - DELIVERY OF CATEGORY 3 SOURCE TO WRONG ADDRESS The following information was provided State of Louisiana via email: "On 09/02/2015, the RSO for A&O [Alpha-Omega Services, Inc.] called in a mis-delivery/wrong delivery of 11.6 Ci Ir-192 source intended for the Radiation Oncology Center at Sibley Memorial Hospital (SMH) in Washington, DC. SMH is a client/customer of A&O in association with ELEKTA. SMH purchased and attempted to possess the radioactive source under a license NRC 08-07398-03. A&O packaged the Ir-192 source and addressed it to SMH, Dept. of Radiation Oncology, 5255 Loughboro Road NW, Washington, DC 20016. The source was shipped from the [A&O] Vinton, LA address to SMH on August 31, 2015. However, [common carrier] delivered the source to Howard University Hospital, Cancer Center, 2041 Georgia Avenue NW, Washington, DC 20060 [on September 2, 2015]." Common carrier was notified of the delivery error and took possession of the source on September 3, 2015 and delivered to the proper address [SMH] that day. The source shielding and shipping container was intact during the incident. It was not damaged nor was the container opened until it reached the final destination. Source information: Elekta Model 105.002 source: 11.6 Ci Ir-192, Serial Number - D36F5755 LA Event Report ID No.: LA-150015; T165946 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-09-17
51380 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-07-08 | 2015-07-08 16:02 | 2015-09-09 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE The following information was provided by the State of California on 07/08/2015 via email: "On July 8, 2015, RHB [CA Radiation Health Branch] was notified that a SUV containing a CPN MC-1 DR # MD60608339 portable soil gauge containing 50 mCi of Am-241/Be and 10 mCi of Cs-137 was stolen in San Clemente. An authorized gauge user parked his SUV, with the gauge secured in the rear of the vehicle, in the driveway of his house. The vehicle containing the gauge was stolen during the night. The vehicle and its contents were reported stolen to the police (Orange County Sheriff / San Clemente Station). RHB will continue to work with the licensee regarding this ongoing investigation." CA 5010 Number - 070815 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-09-17
51379 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-09-08 13:26 | 2015-09-08 18:15 | 2015-09-08 | POSITIVE RANDOM FITNESS-FOR-DUTY TEST RESULT A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the site has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2015-09-08
51378 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-09-04 14:45 | 2015-09-08 17:59 | 2015-09-14 | AGREEMENT STATE REPORT - DAMAGED PORTABLE DENSITY GUAGE The following information was received via facsimile: "The RSO of the Utah Department of Transportation (UDOT), called [the State of Utah, Department of Environmental Quality, Division of Waste Management and Radiation Control] to report an incident involving one of their thin lift, Troxler 4640 gauges containing a 9 mCi Cs-137 source. The incident occurred at about 1400 MDT on Friday, September 4, 2015, at a construction site on eastbound I-215 at Redwood Road. A survey vehicle entered the construction zone at freeway speeds and ran over the gauge while the operator was making a measurement. The gauge was 'destroyed,' but the sealed source remained intact. However, the gauge's shielding for the source was demolished. "The licensee performed surveys of the accident site and of the vehicle involved. No contamination was found. The licensee transported the damaged gauge and source back to the licensee's gauge storage room. The licensee has ordered a replacement base for the gauge to provide shielding for the source so that the source can be safely shipped back to the gauge manufacturer. "The licensee has a report from the gauge operator, reports from eyewitnesses to the incident, and a report from the Highway Patrol. It will take the licensee about a week to compile all of the information into a written report to send to the Division [of Waste Management and Radiation Control]." Utah Event Report ID No.: UT150004 * * * UPDATE PROVIDED BY PHILIP GRIFFIN TO JEFF ROTTON AT 1347 EDT ON 09/14/2015 * * * The following information was provided by the State of Utah via email: The event took place at 1445 MDT on September 4, 2015 versus 1400 initially reported. The gauge contains 8 mCi Cs-137 versus the 9 mCi that was originally reported and the gauge serial number is 65867. A black 4 door car entered the construction zone and ran over the gauge followed by two other vehicles. The manufactured is sending an appropriate shipping container for the licensee to use when returning the source to the manufacturer. "The licensee is authorized to remove portable gauge source rods from their gauges to perform non-routine maintenance on their gauges. Because of this, the licensee has a source rod shield that will be used (per the manufacturer's instructions) to shield the source rod taken from the damaged gauge during transport to the manufacturer." Notified R4DO (Farnholtz) and NMSS Events Notification group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-09-16
51377 | 0 | UNIVERSITY OF NOTRE DAME |  |  |  |  | 2015-09-08 09:35 | 2015-09-08 16:52 | 2015-09-09 | LEAKING NI-63 SOURCE While preparing a Varian Ni-63 source for shipment, the Radiation Safety Specialist was performing wipes for a leak test. After multiple attempts, the leak test kept returning the same results, which were 0.012 milliCi and the limit is 0.005 milliCi. The source is part of a Hewlett-Packard gas chromatograph, model number 0201972-00. The source is a Varian Ni-63 15 milliCi source with a current activity of 14.1 milliCi. The source serial number is A-15296. The source has been wrapped and stored in a sealed bag and placed in the facilities waste building. * * * UPDATE ON 9/9/15 AT 0823 EDT FROM ANDREW WELDING TO DONG PARK * * * The leak test results were 0.012 microCi and the limit is 0.005 microCi; not 0.012 milliCi and 0.005 milliCi. Notified the R3DO (Pelke) and NMSS Events Resource via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-09-16
51376 | 0 | KAKIVIK ASSET MANAGEMENT, LLC |  |  |  |  | 2015-09-07 12:05 | 2015-09-08 16:41 | 2015-09-08 | FAILURE OF CAMERA SOURCE LOCK SLIDE TO LOCK The following event occurred at the Kuparuk Oil Field on the North Slope of Alaska: After performing a routine exposure with a QSA model 880D camera containing a 65.8 curie Iridium-192 source, the source was cranked back into the camera. The radiographer noted that the lock slide did not lock the source as it should have. While using a survey meter, the radiographer then approached the camera. After noting that the source was fully shielded, the radiographer was able to manually lock the slide into the locked position. Supervision was then called. The camera was taken out-of-service. The camera locking mechanism was cleaned and tested. After determining that the locking mechanism was operating properly, the camera was returned to service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-09-16
51375 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-09-07 09:25 | 2015-09-07 11:32 | 2015-09-07 | OFFSITE NOTIFICATION "This report is made due to notification from Susquehanna to Pennsylvania Department of Environmental Protection (DEP) regarding a bypass of the sewage treatment plant at the plant property. The notification was approved at 0925 [EDT] and completed at 0940 [EDT] hours on 09/07/15. "The sewage treatment plant operator reported excessive influent which led to an unanticipated bypass of the sewage treatment plant. The influent was returned to normal values by isolating the domestic water filter backwash line. No bypass leakage is occurring at this time." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-09-07
51374 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-09-05 10:10 | 2015-09-05 17:24 | 2015-09-05 | SECONDARY CONTAINMENT INOPERABLE DUE TO LOSS OF VACUUM FROM OPEN INSPECTION HATCH "At 1010 [CDT] on September 5, 2015, Reactor Building differential pressure did not meet the required 0.25 inches of vacuum due to an open inspection hatch. At 1018 [CDT], an inspection hatch was found to have fallen open and [was] subsequently closed [manually] on the Reactor Building exhaust fan damper access hatch. The damper is outside of the Reactor Building secondary containment isolation boundary. Following closure of the hatch, Reactor Building differential pressure returned to greater than or equal to 0.25 inches of vacuum water gauge. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.1. As a result, entry into Technical Specifications 3.6.4.1 condition A was made due to Secondary Containment being inoperable. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(c) as a condition that could have prevented the fulfillment of a safety function. "The NRC Senior Resident Inspector has been notified." | 0 | 100 | 80 | 0 | 100 | 80 | 0 | -1 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-09-05
51373 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-09-04 | 2015-09-04 22:46 | 2015-09-04 | COLORADO AGREEMENT STATE REPORT - BROKEN DRIVE CABLE ON RADIOGRAPHY CAMERA The following information was provided by the State of Colorado via email: "A radiography source stuck outside the shielded position on Friday, September 4, 2015 [at a temporary job site near Rangely, CO]. The source did not return to the shielded position after an exposure and was quickly discovered by the radiographer. Neither the radiographer nor assistant approached the source. [Both individuals] set up a 2 mR/hr boundary and ensured no person entered the area; then called the RSO for support at approximately 1400 MDT. The RSO arrived on scene and notified the State around 1700 MDT. The licensee is authorized for retrieval and verbally verified all necessary emergency equipment was available and there were no elevated exposures suspected at the time. The licensee began retrieval and contacted the State at 2000 MDT to verify the source was successfully returned to the shielded position. A full report on the cause and recovery efforts to follow. "Cause and corrective action: broken drive cable, corrected by replacing drive cable and returning [source] to the shielded position. "Camera/device information: QSA Global Delta 880; SN D8543 Source information: QSA Global A424-9; SN 20273G; current activity 97.7 Ci assayed 8/26/2015 - 106.3 Ci - leak tested by manufacturer at that time "Doses from pocket dosimeters: RSO - 110 mRem; Radiographer - 21 mRem; assistant - 4 mRem (this was the total from previous exposures during the day, he did not assist with retrieval but was tasked with maintaining surveillance of the boundaries)" Incident identification: CO15-I15-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-09-14
51372 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-09-03 13:20 | 2015-09-04 15:06 | 2015-09-04 | TENNESSEE AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR The following information was provided by the State of Tennessee via email: "A General Licensed (GL) facility called Choo Choo Customs Group possessed a Po-210 static eliminator GL device with approximately 10 mCi of activity. [Choo Choo Customs Group] has been inactive or dissolved. The [State of Tennessee - Division of Radiological Health] has been trying for a number of years to get them to reply. The [Division] has had our field office staff go by the last known and suspected addresses this year (2015) to run them down but to no avail. The collections company for the [Tennessee Department of Environment and Conservation - Division of Fiscal Services] has also had no success. This would be a lost source that the [Division] would report but were hoping to get some resolution or locate the individuals who had owned the company. The [Division] has now exhausted all our leads and are proceeding with reporting it as a lost source/device." Manufacturer: AEA Technology/USA Inc. Static Eliminator Model: PDV1420 (PDM.1002Hn series) Serial#: 8139KB Isotope: Po-210 (10 mCi) Shipped date: 6/25/1999 State Event Report ID NO.: TN-15-132 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-09-14
51371 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-09-04 08:10 | 2015-09-04 14:36 | 2015-09-04 | SECONDARY CONTAINMENT INOPERABLE DUE TO BOTH AIRLOCK DOORS BEING OPEN SIMULTANEOUSLY "At 0810 [CDT] on September 4, 2015, two Secondary Containment doors in one access opening, were opened simultaneously. The interlock mechanism preventing both doors from operating simultaneously at the Unit 2 570 foot elevation Turbine to Reactor Building interlock did not operate as expected. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2. As a result, entry into Technical Specifications 3.6.4.1 condition A was made due to Secondary Containment being inoperable. Secondary Containment differential pressure was maintained within specification. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "The NRC Senior Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-09-04
51370 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2015-08-31 13:00 | 2015-09-04 13:00 | 2015-09-04 | NORTH CAROLINA AGREEMENT STATE REPORT - NUCLEAR GAUGE WITH STUCK CLOSED SHUTTER The following information was provided by the State on North Carolina via email: "On 8/31/15, at approximately 1300 EDT, a NASCO worker operating the #4 Protos cigarette making machine noticed that the nuclear gauge seemed to be malfunctioning. The worker immediately reported this observation to the NASCO RSO. The RSO performed a shutter test and determined that the shutter would not open. [RSO] then turned #4 Protos off and established a no-entry cordoned area around the gauge, the radius of the restricted area was and still is about 20 feet. The RSO next contacted Little Creek Electronics, a North Carolina licensee, for assistance in repairing the shutter. "The RSO of Little Creek contacted a health physicist inspector with the NC Radiation Protection Section, on 9/2/15 to ask whether they are authorized to perform this repair. This is how the Agency [North Carolina Radiation Protection Section] learned of this incident. [Little Creek] was not authorized and instructions were given not to perform work on the gauge; the Agency decided to investigate first thing in the morning on 9/3/2015 to get the details straight from NASCO. "State inspector visited site on 9/3/15 to perform a health and safety assessment. State inspector determined that licensee had confirmed that shutter is closed and that the associated machinery had been deactivated. Furthermore, the licensee had established a cordoned, do-not-enter area of approximately twenty feet in radius around the affected gauge. The inspector's surveys were consistent with the surveys during the last regular inspection (8/6/15) of this license. "NASCO arranged with Automated Control Technologies (ACT), a reciprocal license which handles manufacturing and repair of fixed nuclear gauges. [ACT] should be in to the facility before close of this week." The licensee address and location of the event is 321 Farmington Road, Mocksville, NC 27028. Nuclear gauge is a Accuray TG-5 fixed gauge, model number: S-18, serial number S-4086-H containing a Sr-90 25 milliCi source (assay date 04/2001), and last leak test on 4/23/15 was negative. Report identification number: NMED NC150024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-09-14
51369 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2015-09-04 09:16 | 2015-09-04 12:58 | 2015-09-04 | UNPLANNED AUTOMATIC SCRAM AND SPECIFIED SYSTEM ACTUATIONS DUE TO MSIV CLOSURE "On September 4, 2015, at 0916 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram following Main Steam Isolation Valve [MSIV] closure and isolation of both main steam lines. The cause of the MSIV closure is not known at this time. All control rods fully inserted. Following the scram, pressure was momentarily controlled through the use of the Emergency Condenser system. At 0950, pressure control was established through the main steam lines to the condenser through Main Steam Isolation Valves (MSIVs) 01-02 and 01-04. MSIV 01-03 would not reopen. All other plant systems responded per design following the scram. The reactor scram is a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B)." "The following systems automatically actuated after the scram as expected. These system actuations are an 8-hour report per 10 CFR 50.72(b)(3)(iv)(A). "1. The High Pressure Coolant Injection (HPCI) system. HPCI initiated at 0916 and reset at 0917 when RPV level was restored above the HPCI system low level actuation set point. HPCI initiated and was reset a second time at 0922. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. "2. The Core Spray system actuated, but did not discharge to the Reactor Coolant system. The Core Spray system was secured at 1033. "3. The Emergency Condenser (EC) system actuated to control pressure. EC-11 was secured at 0917. EC-12 was secured at 0921 . The maximum shell temperature of EC system was 193 degrees Fahrenheit. "4. Containment Isolation actuation. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. Since the scram, there have been no anomalies observed with feedwater system operation. Decay heat is being removed via steam to the main condenser using the turbine bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect." The Reactor is being supplied by the normal feedwater system and there was indication of a partial lift/reset on one Electromatic Relief Valve (ERV). The licensee notified the NRC Resident Inspector and the State of New York Public Service Commission. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-09-04
51368 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-09-03 19:01 | 2015-09-03 22:04 | 2015-09-03 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE "At 1901 EDT on 9/3/2015, the Unit 2 HPCI system inboard steam supply valve isolated due to a high steam flow instrument failure. The inboard steam supply valve closed and isolated as expected. There were no indications of a steam leak. Drywell parameters and affected Reactor Enclosure rooms and piping areas were inspected with no indications of a steam leak. In addition, the steam leak detection system did not indicate any rising temperatures for any of the affected areas. The issue has caused Unit 2 HPCI to be declared inoperable and unavailable. Unit 2 has entered into a 14 day [Technical Specification] Limited Condition of Operation per T.S. 3.5.1." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-09-03
51367 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2015-09-03 11:45 | 2015-09-03 16:09 | 2015-09-03 | NEW JERSEY AGREEMENT STATE REPORT - LOSS OF CS-137 DOSE CALIBRATOR VIAL SOURCE The following information was provided by the State of New Jersey via email: "At approximately 1145 [EDT] on Thursday, September 3, 2015, the licensee's Administrator/Radiation Safety Officer was contacted [by the State of New Jersey] to discuss several issues related to the re-location of their office. One of the issues raised was the location of several dose calibrator vial sources and gamma-camera flood sources that were last known to be in the possession of the licensee. The licensee had not provided confirmation that the sources had been moved during their office re-location or had been disposed of properly. The licensee stated that their consulting physicist was taking care of the sources. When informed that the consultant had been contacted and did not know the location of the sources, the licensee stated then they did not know where they were either. As such, the sources are considered lost. "Of the sources unaccounted for, only the above listed Cs-137 vial source was of sufficient activity to warrant a report. The vial source in question is a North American Scientific, Inc., model MED 3550, serial # 28809, 205.6 microCi as calibrated on 10/1/02." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2015-09-11
51366 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-09-03 08:20 | 2015-09-03 15:29 | 2015-09-03 | TEXAS AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE RETRACTION FAILURE The following information was received from the State of Texas via email: "On September 3, 2015, the Agency [Texas Department of State Health Services] received a report from the licensee that a radiography source retraction failure occurred at a temporary field site in Borger, Texas. A mount fell on the guide tube, crimping the tube. The source was retrieved according to license conditions and the damaged equipment was removed from service. The camera was a SPEC-150 and the source was 78 curies of Iridium-192. No exposure to the public occurred. Further information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-09-11
51365 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-09-02 | 2015-09-03 08:05 | 2015-09-09 | AGREEMENT STATE REPORT - TWO RADIOACTIVE ZIRCONIUM METAL CYLINDERS DISCOVERED AT METAL RECYLING CENTER The following report was received from the California Department of Public Health Radiologic Health Branch via email: "On November 11, 2014, an individual associated with the Orange County Science Education Center obtained two small metal cylinders that had caught his eye that were on a shelf at a metal recycling center (DBW Metals Recycling, Anaheim, CA). The metal recycler's analysis of a cylinder showed 96.76% Zirconium with 2% Nb and some Mo, Cr, Pd, Mn, BI, FE, Ni, & Cd. "On August 14, 2015, the member of the public donated one of the Zirconium metal cylinders to the Geology Department at the California Institute of Technology. The location of the second Zirconium metal cylinder is unknown at this time. On August 21, 2015, the California Institute of Technology determined the zirconium metal cylinder was radioactive. The cylindrical metal item measured 3.3 cm D x 5 cm L and weighed 290 gm. "The [State of California] Radiation Safety Office subsequently analyzed the item using a Germanium detector and determined it contained approximately 20 gm of U-238 and 8 gm of U-235 (28.6% enrichment). No fission products were detected, and only minor surface contamination was found (removable surface contamination <30 DPM over entire item. GM [Geiger Muller] meter survey results are as follows: 48,000 cpm on contact (mostly beta); 1 mrem/hr on contact; and 0.03 mR/hr at 1 foot (background of 0.02 mR/h). The Radiation Safety office believes the item is a portion of an unirradiated uranium fuel element. "The Brea Office [State of California Radiation Health Branch] will follow-up under this 5010 to investigate the current location of the 2nd similar item and to ensure it is properly possessed, and will also investigate from whom the metal recycler received the two SNM [special nuclear material] items (what licensee apparently lost control of these SNM items). "LA County also has a 5010 (090215) associated with this event to ensure that CalTech properly possesses the SNM and makes required reports." California 5010 Number: 090315 * * * UPDATE PROVIDED VIA EMAIL FROM ROBERT GREGER TO JEFF ROTTON AT 1919 EDT ON 09/03/2015 * * * The following information was provided by the State of California via email: "After a discussion with the private party who received the SNM item from the local metal recycling facility, it appears that there is no second similar item. Rather the second item had significantly different visual characteristics. The individual indicated he no longer has the second item. [State of California] will attempt to verify the metal composition of the 2nd item with the metal recycling facility. "The private party who received the SNM item from the recycling facility is associated with the Science Education Center of California, not the Orange County Science Education Center. "The SNM item is not clad in zirconium or anything else, rather the SNM item is a mixture of zirconium and enriched uranium, with some other metals in significantly smaller amounts, and perhaps additional non-metals. "The Caltech RSO indicated that he had not performed as good of an analysis as he would have liked to have done, and emphasized that the values he provided for the U-238 and U-235 weights were both approximate values, leaving the U-235 enrichment better represented as between 21-28 percent." Notified the R4DO (Warnick), ILTAB (English) and NMSS Events Notification group via email. * * * UPDATE PROVIDED BY ROBERT GREGER TO JEFF ROTTON AT 1544 EDT ON 09/09/2015 * * * The following information was provided by the State of California via email: "Personnel from Los Alamos National Laboratory (LANL) were contacted to assist in evaluation of the apparent SNM item recovered from a metal recycler. The LANL personnel determined that the item did not contain SNM. Rather the item contained approximately 30-35 grams of unenriched processed uranium. Notified the R4DO (Drake), ILTAB (English), CNSNS (Mexico) and NMSS Events Notification group via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-09-11
51364 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-09-02 21:00 | 2015-09-02 22:11 | 2015-09-03 | PLANNED TECHNICAL SUPPORT CENTER (TSC) MAINTENANCE "Planned maintenance activities will commence today (September 2, 2015) on the Quad Cities Station TSC. The activity involves inspection and replacement of the TSC charcoal absorber trays and canisters on the filtration portion of the Air Handling Unit (AHU). Work on the charcoal absorbers affects habitability of the TSC during a declared emergency when radiological conditions require activation of the filtration portion of the AHU. The duration of maintenance is currently planned to begin on September 2, 2015 at 2100 hours [CDT] and is estimated to be completed by September 3, 2015 at 1100 hours [CDT], depending on any conditions discovered during the inspections. Since restoration from this maintenance activity is expected to take longer than the required activation time of the TSC, this notification is being made. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Station Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This event is reportable per 10CFR50.72(b)(3)(xiii) since the maintenance activity affects an emergency response facility. "The NRC Resident Inspector has been notified [and the Illinois Emergency Management Agency]." * * * UPDATE PROVIDED BY ALAN MEURS TO JEFF ROTTON AT 1625 EDT ON 09/03/2015 * * * "At 1430 CDT on September 3, 2015, the maintenance activity was completed and the TSC ventilation was restored." The licensee notified the NRC Resident Inspector and the Illinois Emergency Management Agency. Notified R3DO (Skokowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-09-02
51363 | 0 | SOR MEASUREMENT AND CONTROL |  |  |  |  | 2015-09-02 | 2015-09-02 15:31 | 2015-09-21 | PART-21 REPORT - NUTHERM IRRADIATION CERTIFICATION WITH INSUFFICIENT MARGIN The following report was received via fax: "SOR Inc. was notified by Nutherm International, Inc. that irradiation certification performed by Steris Isomedix did not meet the additional 10 percent margin to meet the requirements of IEEE 323 due to measuring and test equipment uncertainties. "This issue was originally identified by STERIS lsomedix Services, Whippany, New Jersey as part of NRC Inspection Report No. 99901445/2014-201. Nutherm International, Inc. has completed their evaluation of work performed for SOR, Inc. and has identified a potential impact to the conclusions of equipment qualification testing under SOR Inc. purchase order number 166984. Nutherm International, Inc. has reported this potential issue and forwarded an update to the NRC per Event Notification Report Number 50359. "SOR Inc. is conducting an evaluation of projects to determine whether a defect or failure to comply exists as defined by 10 CFR Part 21. At the conclusion of the evaluation, any customer impacted by this issue will be notified and the U.S Nuclear Regulatory Commission will be notified in accordance with 10 CFR Part 21.21. "If you have any questions regarding this issue, please contact Mike Bequette, Vice President of-Engineering at (913) 888ú2630 or email mbequette@sorinc.com." * * * UPDATE FROM MELANIE DIRKS TO JOHN SHOEMAKER AT 1729 EST ON 9/21/15 * * * The following updated information was excerpted from a SOR, Inc. report received via email: "As a result, corrections were made to test report SOR-12043R revision 1, approved 9/8/2015. The uncertainty calculations by the radiation lab used for the qualification program reduced the qualification level from 35 Mrad to 33.8 Mrad. "SOR found that there were three switches potentially affected as shown [on table I provided with this report]. While these switches were shipped before completion of the of test report SOR-12043R, revision 0, it has been established that there was a contractual agreement between SOR and Xcel Energy-Monticello Nuclear Generating Plant that these switches would be equivalent to those to be qualified in the new test report. Also listed are recipients of the original test report SOR-12043R revision 0 [on table II provided with this report]. "In either Case, SOR does not have the capability to perform further evaluations to determine if a safety hazard exists as the specific customer application and end use is not known by SOR. Since the release of revision 0 of the test report, SOR has not provided certificate of conformance to any 141 series product shipped citing the 12043R test report other than qualification units for Excel Energy - Monticello Nuclear Generating Plant. Recipients, Customer, Utility Names: - Xcel Energy - Monticello Nuclear - Progress Energy - Brunswick - Entergy Corporation - Pilgrim "In accordance with the requirements of 10 CFR Part 21.21, the customers listed have been notified regarding this issue to allow them to evaluate this deviation or failure to comply and its potential safety hazard." lf you have any questions regarding this matter, please contact; For technical issues; Joe Modig SOR Inc. 14685 W. 105th Street Lenexa, KS 66215-2003 Ph: (913) 956-3046 jmodig@sorjnc.com And for any other questions; Melanie Dirks Director of Quality Assurance SOR Inc. 14685 W. 105th Street Lenexa, KS 66215-2003 Ph: (913) 956-3160 Email: mdirks@sorinc.com Notified R1DO (Welling), R2DO (Sykes), R3DO (Dickson), R4DO (Pick), and Part 21 Reactors and Part 21 Materials via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | KS | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-09-02
51362 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2011-05-06 | 2015-09-02 15:17 | 2015-09-02 | AGREEMENT STATE REPORT - GAUGE SHUTTER BROKEN AND TAPED SHUT "On September 2, 2015, inspectors from the Nashville Field Office [Tennessee Division of Radiological Health] went to Letica-Maui Cup Division in Clarksville, Tennessee to inspect their generally licensed devices. It was discovered during the inspection that one of their gauges was broken. On May 6, 2011, the shutter on the NDC model 102X (serial number 12571) broke off. The shutter was taped back into the closed position at that time and the gauge was removed from the manufacturing line. No notification was made to the Division. The gauge contains an 80 mCi Americium 241 source." Tennessee Event: TN-15-129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-09-10
51361 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-08-11 | 2015-09-01 13:16 | 2015-09-01 | AGREEMENT STATE REPORT - RADIOACTIVE SOURCE SENT TO A WASTE RECYCLING FACILITY AND RETURNED The following report was received via e-mail: "On August 18, 2015, Mitsubishi Rayon Carbon Fiber and Composites (Mitsubishi) contacted the California Office of Emergency Services to report a missing source. The source, a Honeywell Measurex (now Vega Americas Corporation) BAL-55 source holder , S/N K0-003 with a Generally Licensed Kr-85 source (300 milliCuries as of 10/20/97). The source was determined to be missing on August 11, 2015. Upon learning that the machinery that the source holder was attached was sent to SA Recycling, Anaheim, [Mitsubishi] went to the facility and was informed that the unit had already been shredded and that there was no source found. [Mitsubishi] then contacted the manufacturer, who also provides services for their fixed gauges. When [Mitsubishi] finally was in contact with a service technician for Vega Americas, they were informed that the missing source was to be reported to RHB [California Radiologic Health Branch]. When [Mitsubishi] could not get in touch with RHB personnel after contacting the RHB Brea and Los Angeles County Radiation Management offices, he contacted the Office of Emergency Management. "After the OES [Office of Emergency Services] report was forwarded to the ICE RAM [Inspection, Compliance, and Enforcement Radioactive Materials] South office, [Mitsubishi] was contacted by an RHB Inspector and informed that the source had been found by SA Recycling safety personnel and was currently being stored at their secure radioactive material storage area. [Mitsubishi] was informed that a written report was required to be submitted to RHB within 30 days. "On August 19, 2015, an RHB Inspector arrived at SA Recycling to determine integrity of the device to ensure that the source was not damaged. Using a Ludlum 19, the dose rate was greater than 5 mR/hr on contact, 5 mR/hr at one inch, and 0.8 mR/hr at one foot (background was 7 microR/hr), which was consistent with the dose rate found by SA Recycling personnel (greater than 5 mR/hr on contact, 5mR/hr at 3.5 inches, 1.5 mR/hr at one foot and 0.21 mR/hr at three foot with a background of 9 microR/hr. The meter was a Ludlum 3 with a sodium iodide probe). Since the source is a noble gas, a significant amount would likely have released to the atmosphere within a weeks time if the source had been damaged. The consistent dose rate indicated that the source was most likely intact and not leaking. Since the source was most likely to be intact, the [RHB] inspector took possession of the source and returned it to Mitsubishi for storage in an isolated and secure area until disposal can be arranged with the manufacturer. Mitsubishi had been in the process of securing proper disposal when the source was improperly disposed as scrap metal. Upon arriving at the Mitsubishi facility, the [RHB] inspector was informed that the funds for the fees associated with the disposal were approved on August 19, 2015 and the disposal will be scheduled after the proper shipping package arrives at the Mitsubishi facility." California Event: 081815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-09-09
51360 | -1 | FORT SAINT VRAIN |  |  |  | ISFSI | 2015-08-31 14:45 | 2015-08-31 17:15 | 2015-09-02 | 73.71 REPORT - PHYSICAL PROTECTION PLAN Reported as a failure to implement compensatory measures in the physical protection plan. * * * RETRACTION PROVIDED BY STEVE AHRENDTS TO JEFF ROTTON AT 1647 EDT ON 09/02/2015 * * * It was determined that the previously reported failure does not meet the 1 hour reporting criteria of 10CFR73.71, Appendix G. An appropriate entry will be made into their Safeguards Log concerning the failure. Licensee will be notifying NRC Region IV Physical Security Branch personnel. Notified R4DO (Warnick), NMSS Events Notification group, and 73.71 Safeguards group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | CO | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2015-08-31
51359 | -1 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-08-21 15:50 | 2015-08-31 16:40 | 2015-09-03 | AGREEMENT STATE REPORT - LOW LEVEL ALPHA RADIATION ON A SHIPPING CONTAINER The following information was received via e-mail: "On 8/21/2015 at 1550 [MDT] an incident involving radioactive material was reported to the Utah Department of Environmental Quality's 24 hr. hotline. The caller reported low level alpha radiation activity on an empty shipping container and roll-off box that exceeds DOT standards. The container arrived at their facility the morning of 8/21/2015 from a Utah (NRC Agreement State) regulated facility near Blanding. It was the belief of the caller that it is very unlikely there was any dosage to humans or the environment. "The container was shipped from Blanding, Utah to Douglas, Wyoming through Grand Junction. The caller has notified the NRC [National Response Center], Incident #1126333. They have also contacted Colorado and Wyoming DOT." Utah Event: UT15-0003 * * * UPDATE AT 1825 EDT ON 9/1/2015 FROM RYAN JOHNSON TO MARK ABRAMOVITZ * * * The source of the alpha radiation was natural uranium. The container was decontaminated. A radiation survey of the container was conducted before decontamination with the following results: Direct alpha readings of 2437, 7616, and 6092 dpm per 100 square cm Removable alpha readings of 191, 200, and 786 dpm per 100 square cm. These results are below the DOT 49CFR173.443(a) reporting requirements Notified the R4DO (Warnick) and NMSS Events Resource (via e-mail). * * * RETRACTION PROVIDED BY RYAN JOHNSON TO JEFF ROTTON VIA EMAIL AT 1514 EDT ON 09/03/2015 * * * The following information was received from the State of Utah via email: "After further investigation into this incident, the DWMRC [Division of Waste Management and Radiation Control] has concluded that the reported incident was in error and that DOT standards were not exceeded. The DOT alpha contamination limits found in 49 CFR 173.443(a) are for removable (non-fixed) contamination. The incident was reported on an incoming survey results for direct alpha measurements and not on removable alpha measurements. The removable alpha measurements from the same incoming survey were below the DOT alpha contamination limits. Therefore, the State of Utah is requesting to retract this incident (EN#51359)." Notified R4DO (Warnick) and NMSS Events Notification group via email. THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-09-08
51358 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-08-19 | 2015-08-31 13:20 | 2015-08-31 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER STUCK CLOSED The following was received via e-mail: "The Tennessee Division of Radiological Health was notified on August 19, 2015 of an inoperable fixed nuclear gauge at the Jarden Zinc facility in Greeneville, TN. The gauge shutter was stuck in the closed position due to a defective solenoid in the gauge. The gauge was a LFE Model SS3A containing a 1 curie Americium 241 source." Tennessee Event: TN-15-126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-09-08
51357 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-08-27 11:30 | 2015-08-28 17:12 | 2015-08-28 | AGREEMENT STATE REPORT - LOST CS-137 CALIBRATOR CHECK SOURCE The following information was obtained from the State of Louisiana via email: "Event date and time: On August 27, 2015, [a licensee employee] reported a lost QC/QA check source utilized to perform the daily constancy on the dose calibrator. He did the daily test at approximately 6:00 a.m. [CDT] with the source. He noticed the source was missing at approximately 1130. His administrator and he used survey meters and searched every possible place where the source could be, but have not located the missing source. [He] reported the source missing to LADEQ Radiation Assessment at 1538 on August 27, 2015. "The source is an Atomic Labs 102 microCurie Cs-137 check source. The model number given was #11010170 and the serial number was 356013-0001. The source was last leak tested on April 29, 2015, with no leakage detected. "This site is a medical institution. The source was kept in a locked hot lab in the Nuclear Medicine Department. They surveyed the Nuclear Medicine Dept., the Radiology Department and the waste disposal location. KLS Physics Consultants was called in to help with the search and the reporting requirements. "Event Location: Ville Platte Medical Center/dba Acadian Medical Center, 3501 Hwy 190, Eunice, LA 70535. The last known location within the facility was during the daily dose calibrator constancy check." Louisiana Event Report ID No.: LA-150014, T165187 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-09-07
51356 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2014-12-12 | 2015-08-28 11:29 | 2015-08-28 | AGREEMENT STATE REPORT - GENERALLY LICENSED SOURCE MISSING, LATER RECOVERED The following information was received via facsimile: "On 12/12/14, the Department of Health (DOH) became aware of this incident. A liquid scintillation counter [LSC] (25 years old and containing 10 microCuries of Radium 226) had been stored for three years. It could not be located on 12/12/14. An attorney in Estee Lauder's legal department was asked to contact the DOH to report that the LSC could not be located. "DOH received a phone call from Estee Lauder's legal department to say that they had found where the missing LSC was shipped. Keith Machinery Corporation had purchased the LSC and then sold it. "On 6/15/15, a letter was sent to Estee Lauder [from DOH] requesting a copy of the Keith Machinery Corporation Equipment Trade-In Credit Memo. "On 6/17/15, DOH received a letter from Estee Lauder's RSO which had an attachment from Keith Machinery Corporation stating that they had received the Perkin Elmer LSC, Model 1217 Rackbeta. Keith Machinery Corporation stated by phone, on 6/29/15, that the LSC was to be shipped to Romania and he will send DOH a confirmatory letter that it was received in Romania if he can. If not, he will send a letter that it was shipped to Romania. "On 8/18/15, [DOH was notified that] Keith Machinery Corporation had located the Perkin Elmer LSC, Model 1217 Rackbeta, which was awaiting shipment to Romania. Items are not shipped immediately and individually to places like Romania, but are accumulated until a large shipment is acquired, which is more efficient and cost effective. Keith Machinery Corporation was able to locate the LSC and return it to Estee Lauder. Estee Lauder shipped it to Radiac Research Corporation for disposal on 7/28/15. DOH received a copy of Radiac Research Corporation receipt. The Estee Lauder General License Registration can now be terminated according to their request." NY State Event Report ID No.: NY-15-07 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-09-07
51355 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-08-27 13:47 | 2015-08-27 20:39 | 2015-10-22 | BRIEF LOSS OF SECONDARY CONTAINMENT DUE TO BOTH AIRLOCK DOORS OPEN SIMULTANEOUSLY "On 8/27/2015 at 1347 [EDT], a cart and personnel were being traversed through an airlock in the Unit 2 reactor building and both airlock doors were inadvertently opened at the same time for a brief period of time (approximately one minute). "Secondary Containment differential pressure was maintained throughout the time period that the doors were opened. The doors serve as a Secondary Containment boundary and at least one in series is required to be closed at all times for Secondary Containment Operability. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee notified the NRC Resident Inspector. * * * RETRACTED ON 10/22/15 AT 1645 EDT FROM ALEX MCLELLAN TO DONG PARK * * * "NUREG-1022, Revision 3, Section 3.2.7, 'Event or Condition that Could Have Prevented Fulfillment of a Safety Function,' states, in part, that 'events covered in paragraph (b)(3)(v) of this section may include one or more procedural errors, equipment failures, and/or discovery of design, analysis, fabrication, construction, and/or procedural inadequacies.' "The level of judgment for reporting an event or condition under this criterion is a reasonable expectation of preventing fulfillment of a safety function. A SSC [System, Structure, and/or Component] that has been declared inoperable is one in which the SSC capability has been degraded to the point where it cannot perform with reasonable expectation or reliability. For SSCs within the scope of this criterion, a report is required when: - There is a determination that the SSC is inoperable in a required mode or other specified condition in the TS [Technical Specification] applicability, -The inoperability is due to one of more personnel errors, including procedure violations; equipment failures; inadequate maintenance; or design, analysis, fabrication, equipment qualification, construction, or procedural deficiencies, and -No redundant equipment in the same system was operable. "Subsequent to the reporting of this condition, Susquehanna Nuclear, LLC performed an investigation of the event. Below are the results. "When the airlock doors were opened at the same time, they were being operated as designed. Each individual had a 'green' light, which allowed them to open each door. Based on the investigation, the doors were open at the same time for approximately one second. In summary, the inoperability of Secondary Containment was not due to personnel error or a procedure violation. "At the time of the event, both airlock doors were operable. No equipment failures, inadequate maintenance, or design, analysis, fabrication, equipment qualification, construction, or procedural deficiencies were identified. "In summary, based on the above, the identified condition is not reportable in accordance with 10 CFR 50.72(b)(3)(v), for an event or condition, that at the time of discovery, could have prevented the fulfillment of a safety function. As such, this 8-hour event notification is being retracted." The licensee has notified the NRC Resident Inspector. Notified R1DO (Gray). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-08-27
51354 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-08-27 17:00 | 2015-08-27 18:33 | 2015-08-27 | TEXAS AGREEMENT STATE REPORT - COBALT-57 SOURCE LOST DURING SHIPMENT The following information was received from the State of Texas via email: "On August 27, 2015, the licensee notified the Agency [Texas Department of State Health Services] that a 100 milliCurie cobalt-57 source had been ordered by one of its investigators and shipped to the proper address for the licensee, but the source had not been received. The licensee's radiation safety officer (RSO) reported that the investigator had checked around noon on the status of the order with the radiation safety office. The radiation safety staff learned that the investigator had ordered it without following procedure and going through their office, so they had not been aware that the source was supposed to be coming. The RSO reported that upon checking with the common carrier handling the package, the carrier showed the package had been delivered on August 21, 2015, 'in College Station' (no other information documented by the driver), and the carrier provided the name of the person who signed for receipt. The carrier opened an investigation. The RSO contacted the company from whom the source was purchased and verified the shipping address was correct. A search was conducted of the building it should have been delivered to, staff was questioned if they had seen/received it or knew the person who signed for it, and the RSO searched staff and student directories and checked through the university's police department for the signer's name with negative results. At approximately 1630 [CDT], the RSO made the determination the package was missing and reported to the Agency. The RSO stated that a team will begin canvasing other buildings in the morning and efforts will continue to locate the package and identify the signer. Further information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9335 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-09-04
51353 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-08-27 07:52 | 2015-08-27 14:10 | 2015-08-27 | SECONDARY CONTAINMENT INOPERABLE "At 0752 CDT on 8/27/2015, both doors of a Secondary Containment Airlock were reported to be open simultaneously for a period of approximately five seconds. The brief time that the doors were simultaneously open constituted an inoperable condition of Secondary Containment. The airlock interlock was verified to operate correctly, and Secondary Containment has been restored to an operable status." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-08-27
51352 | 0 | OAKWOOD HOSPITAL |  |  |  |  | 2015-08-25 15:00 | 2015-08-27 13:26 | 2015-08-27 | LOST I-125 SEED "Late on 8/25/15, the [Chief Physicist] was informed that the I-125 seed count in storage does not reconcile with the Written Directives and the pathology log. The storage vial is one seed short. Instead of 30 seeds, there are only 29 seeds. Also there is a non-radioactive marker/clip in the storage container along with 29 Iodine-125 seeds. All seeds are of nominal activity of 0.3 mCi. The lead container housing the sources was brought down to Radiation Oncology source storage room on 8/26/2015. "So far our findings are as follows: Radiation survey of the pathology lab was performed by the pathology lab supervisor. Survey revealed no presence of radioactivity. Radiation survey of the stored tissue specimens for these cases revealed no radioactivity. [Licensee staff] reviewed the radiographs of each tissue specimen and the count was 30 seeds. It would seem that the pathology assistant mistook the marker/clip to be an iodine seed and put it in storage container and the actual seed somehow got discarded as hazardous waste, in spite of the documented procedure to survey everything which comes in contact with specimen to be surveyed with Geiger counter. By reviewing the radiographs of each specimen we have ruled out the possibility that a source was left in the patient. On 8/26/2015, another independent radiation survey of the Pathology Lab was performed by Nuclear Medicine using a scintillation detector and once again no seed was found." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-09-04
51351 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-08-26 19:20 | 2015-08-26 21:44 | 2015-08-26 | TREE BRANCH FELL ON AMTRAK POWER LINE AND CAUSED BRUSH FIRE "A small brush fire occurred adjacent to an AMTRAK railroad right of way that passes through the Millstone Power Station owner controlled area, due to a downed tree branch that knocked down an AMTRAK electrified power line. The fire is outside the protected area of the site, and poses no public hazard or threat to building or structures. Outside assistance has been requested. Waterford Fire Department and AMTRAK have responded, and have eliminated the source and extinguished the fire. This report is being made pursuant of 10CFR50.72(b)(2)(xi). There is no radioactive release associated with this event. Dominion may respond to public inquiry, but no press release is planned." The NRC Resident Inspector has been notified. The Connecticut State Department of Energy and Environmental Protection and Waterford Dispatch were notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-08-26
51350 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-08-25 | 2015-08-26 17:23 | 2015-08-28 | AGREEMENT STATE REPORT - CONTAMINATION IN AN UNCONTROLLED AREA The State of Oklahoma reported that contamination from a leaking Ba-137 generator was discovered in a 'shed' at the University of Tulsa. It is estimated that approximately 1 milliCurie of Cs-137, used in the generator, was leaked. The licensee, Tracerco, licensed by the State of Texas, was using the generator for tracer studies on University of Tulsa equipment under a reciprocity agreement with the State of Oklahoma. The contamination occurred between October and November of 2014. Tracerco discovered the generator leakage at their Texas facility in May, 2015 but only recently informed the University of Tulsa. The Radiation Safety Officer at the University of Tulsa surveyed the area on 8/25/15 and obtained count rates as high as 100,000 cpm inside the shed. Contamination was also found outside of the shed's location. According to Tracerco, it is estimated that approximately 1 milliCurie of Cs-137 was leaked at the University of Tulsa. The University of Tulsa reported that approximately eight individuals work in the area at least some of the time, however, the University is working on obtaining occupancy information at the contaminated location. The shed has been quarantined. The Ba-137 generator, which contained 50 milliCuries of Cs-137, was manufactured by the China Institute of Atomic Energy. The State of Oklahoma will be investigating the event and will be determining the amount of exposure to the individuals. Tracerco is continuing evaluating the event. The State of Texas reported the leaking generator under NRC EN #51102 * * * UPDATE FROM KEVIN SAMPSON TO DONALD NORWOOD AT 1640 EDT ON 8/28/2015 * * * The following information was received via facsimile: "On August 27, 2015 the Oklahoma Environmental Agency Radiation Management Section performed a reactive inspection of this facility. The facility consists of a closed flow-loop pipeline which water or petroleum was pumped through. A port was used to inject radioactive tracers into the material to study its behavior in the flow-loop. Normally the crew from Tracerco would set up the generator at the injection port which was located on a platform about 12 feet above grade. However for some reason, possibly bad weather, the crew that performed the work last year decided to set up in an enclosed pump house immediately adjacent to the pipeline. At some point during the procedure an estimated 0.1 mCi of Cs-137 (not 1 mCi as previously reported) was released in the interior of the structure. The material was in the form of small resin spheres, about the size of a poppy seed, with the Cesium coating the surface. Sometime around May of this year, after Tracerco discovered that the generator was leaking and their own facility was contaminated, they sent staff back to the University to survey for contamination. However, they were unaware that the previous crew had used the pump house, and only surveyed around the injection port where they found no contamination. No further action was taken until August 24 when Tracerco employees again visited the site and surveyed the pump house. After finding the contamination they decontaminated the area using adhesive tape to pick up the material. Two office chairs and a floor mat were also found to be contaminated and removed to an area the university uses for radioactive storage. None of the University employees who worked at the facility were badged. "During our inspection we noted that the background radiation level was elevated in the vicinity of the pump house and flow-loop (approx. 100 microR/hr as measured with a Victoreen 450P, this was about 10 X background off the facility). It should be noted the University has it's own license and uses or stores about 25 fixed gauges, with a total possession limit of 15 Ci., either on or near the flow-loop. Surveys inside the pump house showed isolated areas of contamination with radiation levels as high as 500 micro-R/hr. Multiple areas (usually concrete joints or gravel at the edge of the concrete) around the exterior of the pump house were also found to be contaminated with dose rates around 200 microR/hr. One trailer adjacent to the pump house was found to have a small spot of contamination in the carpet just inside the door. This was surveyed at 260 micro-R/hr. This trailer was used for office space for two persons, one of whom is a member of the public. 14 samples were collected at various points and will be counted next week. The University has restricted access to the contaminated areas but has continued to allow essential radiation workers to enter when necessary to operate the flow-loop. They were instructed to require anyone entering to wear disposable gloves and shoe covers. "Tracerco has arranged for Chase Environmental to characterize and remediate the facility. This will begin on August 31 and is expected to take 5 to 7 days. Tracerco has also arranged for any university staff who desire to be scanned at a full-body counter in Houston." Notified R4DO (Campbell) and via E-mail the NMSS Events Notification group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-09-03
51349 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-08-26 12:15 | 2015-08-26 16:30 | 2015-08-26 | UNANALYZED CONDITION DUE TO APPENDIX R POSTULATED FIRE "On 8/26/2015 at 1215 [EDT], a review of the Salem Appendix R Safe Shutdown Analysis in response to the Byron Event Notification #51334 and Braidwood Event Notification #51335, identified a fire scenario that could cause spurious operation of the pressurizer power operated relief valves (PORVs) (PR1 and PR2) and also prevent the ability to close the PORV block valves (PR6 and PR7) until AC power is restored to close the block valves. This scenario would result in the loss of reactor coolant system (RCS) inventory and pressure control that is not accounted for in safe shutdown analysis. The above fire scenario is applicable to a fire in the Control Room and Relay Room fire areas. "Hourly fire watches of the Relay Room have been implemented. In addition, the Control Room is continuously staffed by the Operating Shift. In addition, the Relay Room is equipped with automatic detection and suppression. "This event is being reported under 10CFR50.72(b)(3)(ii)(B), for 'any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.'" The NRC Resident Inspector has been notified. The licensee will be notifying the Lower Alloways Township, the State of New Jersey and the State of Delaware. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-08-26
51348 | 0 | WATERFORD | 3 |  |  | [3] CE | 2015-08-26 07:40 | 2015-08-26 15:47 | 2015-08-31 | BOTH EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE "This is a non-emergency notification from Waterford 3. On August 26, 2015, at 0111 CDT, Emergency Diesel Generator (EDG) 'A' was declared inoperable following a trip of EDG 'A' on Generator Differential. Technical Specification (TS) 3.8.1.1 actions b. and d. were entered. EDG 'A' was being routinely run in accordance with OP-903-115, 'Train A Integrated Emergency Diesel Generator/Engineering Safety Features Test', Section 7.4, '24 hr EDG A Run with Subsequent Diesel Start' to satisfy Technical Specification Surveillance Requirement 4.8.1.1.2 6. EDG 'B' was subsequently started per TS 3.8.1.1 action b. (1). At 0740 CDT, EDG 'B' was declared inoperable and TS 3.8.1.1 f. was entered due to the exhaust fan not starting when the diesel engine was started. "Troubleshooting determined that the EDG B exhaust fan did not start due to HVR-501B (EG B ROOM OUTSIDE AIR INTAKE DAMPER) not opening. Action was taken to isolate air and fail HVR-501B to its open safety position. At 1001 CDT, EDG 'B' was declared operable and TS 3.8.1.1.f. was exited following verification of proper operation of the EDG 'B' exhaust fan. "Waterford 3 is currently in TS 3.8.1.1 actions b. and d. Actions to verify a temporary EDG is available and restore EDG 'A' to operable status are in progress. "This event is reportable pursuant to 10 CFR 50.72(b)(3)(v) (A) and 10 CFR 50.72 (b)(3)(v) (D), 'event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to (A) shut down the reactor and maintain it in a safe shutdown condition' and (D) 'mitigate the consequences of an accident due to both emergency diesel generators being inoperable.'" "The NRC Resident Inspector has been notified." * * * UPDATE FROM SCOTT MEIKLEJOHN TO DONALD NORWOOD AT 1328 EDT ON 8/31/2015 * * * "The following is a correction to a non-emergency event notification from Waterford 3 originally made on 8/26/2015: "On August 26, 2015, at 0111 CDT, Emergency Diesel Generator (EDG) 'A' was declared inoperable following a trip of EDG 'A' on Generator Differential. Technical Specification (TS) 3.8.1.1 actions b and d were entered. EDG 'A' was being routinely run in accordance with OP-903-115, 'Train A Integrated Emergency Diesel Generator/Engineering Safety Features Test,' Section 7.4, '24 hr EDG A Run with Subsequent Diesel Start' to satisfy Technical Specification Surveillance Requirement 4.8.1.1.2(e)6. EDG 'B' was subsequently started per TS 3.8.1.1 action b.(1). At 0740 CDT, EDG 'B' was declared inoperable and TS 3.8.1.1 f was entered due to the room exhaust fan not starting when the diesel engine was started. "Troubleshooting determined that the EDG B room exhaust fan did not start due to HVR-501B (EDG B ROOM OUTSIDE AIR INTAKE DAMPER) not opening. Action was taken to isolate air and fail HVR-501B to its open safety position. At 1001 CDT, EDG 'B' was declared operable and TS 3.8.1.1.f was exited following verification of proper operation of the EDG 'B' room exhaust fan. "Waterford 3 is currently in TS 3.8.1.1 actions b and d. Actions to verify a temporary EDG is available and restore EDG 'A' to operable status are in progress. "This event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D), Event or Condition that Could Have Prevented Fulfillment of a Safety Function of structures or systems that are needed to (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident due to both emergency diesel generators being inoperable. "The NRC Resident Inspector has been notified." Notified R4DO (Warnick) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-08-26
51347 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2015-08-26 08:50 | 2015-08-26 13:20 | 2015-08-26 | OFFSITE NOTIFICATION REGARDING MATERIAL BEING RELEASED AND RECOVERED "On 8/26/2015, it was determined that a report to the NRC under 10 CFR 50.72(b)(2)(xi) may have been missed. The station is making this report due to the station making a courtesy call to a State agency regarding release of radioactive waste from the site as non-radioactive material. "The original event involved a release of 14 bags of debris from the Administration Building roof prior to survey results being obtained. The bags were recovered from the local landfill and a determination was made that the amount of material temporarily removed from the Protected Area was below NRC reporting limits per 10 CFR 20.2201 'Reports of theft or loss of licensed material.' "On 5/29/13 a courtesy phone call was made to the Nebraska Department of Health and Human Services (Radiation Control Program) informing the authority of the event. There were no state notification requirements based on the low level of licensed material released (and then recovered) from the site. "This is a four hour report made in accordance with 10 CFR 50.72(b)(2)(xi) as 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of environment, for which a news release is planned or notification to other government agencies has been or will be made.' "There was no overexposure to a member of the public. "The NRC Resident and State of Nebraska have been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-08-26
51346 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2015-08-25 | 2015-08-26 10:08 | 2015-08-26 | ABANDONED GAUGE FOUND IN SCRAP METAL The following report was received from the State of Alabama Department of Public Health Office of Radiation Control via fax: "On August 25, 2015, Sam Price, Environmental Health & Safety for Nucor Steel, Birmingham, Alabama notified the Office of Radiation Control that a load of scrap received from Covington, Georgia had set off radiation monitors and was reading 11.0 mR/hr and had been identified as Cs-137. "Representatives from the Office of Radiation Control investigated the load and confirmed all measurements that were previously taken. The load was segregated and a single fixed type gauge was discovered in the load. The gauge contained only an unreadable general license label which was still attached. No other labels or markings were identified. The shutter appeared intact, but partially open. "The gauge has been secured in place and is awaiting pick-up by an appropriate driver being provided by the scrap metal dealer in Covington, Georgia. "The State of Georgia has been notified of the incident. "As of today [August 26, 2015], 8:45 a.m. CDT, the gauge remains secure in place at Nucor Steel, Birmingham, Alabama." Alabama Incident 15-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2015-09-03
51345 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-08-26 05:48 | 2015-08-26 09:45 | 2015-08-26 | SPURIOUS INTERMITTENT ACTUATION OF AN EMERGENCY NOTIFICATION SYSTEM SIREN "At 05:48 [EDT] BVPS [Beaver Valley Power Station] received notification that siren #6, Potter Township Municipal Building, was sounding intermittently. The fire department activation cable to the siren was severed by a motor vehicle. The ENS activation function remains functional. "This event is reportable as a 4-hour Non-Emergency Notification 10 CFR 50.72(b)(2)(xi) as 'a News Release or Notification of Other Government Agency.' "The Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-08-26
51344 | 0 | FURMANITE |  |  |  |  | 2015-08-25 | 2015-08-25 18:31 | 2016-07-13 | PART 21 FURMANITE NUCLEAR GRADE LEAK SEAL MATERIAL FSC-N-1B "Furmanite FSC-N-1B Batch #1026 was discovered (post-delivery) to have Chloride levels above acceptable limits. As Discovered: 2400 ppm Chloride. Furmanite Specification: 100 ppm Chloride. "Part Name: Nuclear Grade Leak Seal Material FSC-N-1B. "Specification: Furmanite Material Specification 1220.1 R2. "Furmanite Notice Number: 25.08.2015 "Potential affected customers: America Electric Power - DC Cook Arizona Public Service - Palo Verde DTE Energy - Fermi Power Plant 2 Duke - Catawba Nuclear Station Duke - McGuire Nuclear Station Exelon Nuclear - Limerick Generating Station Florida Power & Light Co. - St. Lucie Nuclear Plant Florida Power & Light Co. - Turkey Point Nuclear Plant" * * * UPDATE AT 1629 EDT ON 7/13/16 FROM EDWARD RICH TO JEFF HERRERA * * * The following update was received via email: "This is an update to part 21 report 2015-63-00. Event # ML15243A174 "The remaining in process items 4 and 5 of the attached report have been completed. "4. Team Furmanite has contacted all affected customers and has accounted for all boxes of batch # 26 that were manufactured. No material was installed and the boxes were either returned or destroyed by the plant. "5. Root cause and corrective actions are complete and are listed below. "Root cause: "Inadequate controls during manufacturing process. Testing of concentration levels only at one time during process and it was determined this was not adequate to detect contamination. "Corrective action: "New procedure PRG.000284.022 was developed with concentration levels being checked at raw material stage and after final packaging. Compound is placed in a hold area before being shipped until third party test results have shown the batch to be acceptable." Contact information for additional questions: Edward Rich Director of Quality - Team Furmanite Phone: (281) 388-5567 Notified the R1DO (Ferdas), R2DO (Rich), R3DO (Kunowski), R4DO (Gaddy), Part 21 Reactors group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-08-25
51343 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-08-25 12:52 | 2015-08-25 16:01 | 2015-08-25 | UNPLANNED LOSS OF PRIMARY AND BACKUP METEOROLOGICAL INSTRUMENTATION "On August 25, 2015, at approximately 12:52 EDT, an unplanned loss of power to the Vogtle Meteorological Towers occurred. The loss of power was the result of an electrical disturbance in the Plant Wilson switchyard. Power was restored 14:45 EDT. The electrical disturbance impacted meteorological instrumentation only and did not impact operation of either Unit 1 or Unit 2. "The TSC and EOF remained functional and compensatory measures existed within emergency plan implementing procedures to obtain meteorological tower data locally and with the National Weather Service. Meteorological information could have been provided via the emergency notification system to the NRC Operations Center. "This event is reportable per 10 CFR 50. 72(b)(3)(xiii) for 'any event that results in a major loss of emergency assessment capability.' The Emergency Response Organization was notified and necessary compensatory actions were established. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-08-25
51342 | -1 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-08-19 | 2015-08-25 10:52 | 2015-08-27 | OHIO AGREEMENT STATE REPORT - PROSTATE TREATMENT UNDERDOSE The following information was provided by the State of Ohio via email: On 8/20/2015, the Ohio Department of Health (ODH) was notified by voice mail regarding a prostate seed implant to a patient performed on 07/16/2015. This implant consisted of [60] seeds (each seed - 23.6 milliCi of I-125). On 8/18/2015, a post seed implant CT scan was done to verify dose distribution. It was discovered that the D90 "dose" delivered [an under dose] that varied by 34 percent of the prescribed D90 dose for a prostate seed implant. The Referring physician and patient have been notified. Ohio Item Number: OH150008 * * * RETRACTION PROVIDED FROM STEPHEN JAMES TO JEFF ROTTON VIA EMAIL AT 1454 ON 08/27/2015 * * * The following information was provided by the State of Ohio via email: "After additional reporting by the licensee and investigation by ODH, it was determined that the patient did NOT receive the under dose as initially reported and DOES NOT qualify as a medical event. This report is RETRACTED, as of 8/27/15." Notified R3DO (Skokowski) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-09-02
51341 | 0 | MCLAREN MCCOMB |  |  |  |  | 2015-08-18 10:35 | 2015-08-19 13:31 | 2015-08-24 | FLEXITRON SOURCE LODGED IN CHECK RULER On August 18, 2015, at 1035 EDT as a part of acceptance of a new Flexitron mHDR Unit, [Mt. Clemens Regional Medical Center d/b/a McLaren McComb] tested the source position accuracy using a position check ruler. Licensee programmed the source so that it would go to certain positions. The positions were initialized at 1034 EDT. The source was being watched with the room monitor camera and the camera was zoomed in on the position and not the entire ruler. The source was viewed moving out and passing the positions. The source was supposed to dwell two seconds in each position. After 10 seconds, the cable was seen retracting. At 1035 an error message was received from the machine. The camera was zoomed out and noticed the cable was stuck in the ruler and the source was lodged somewhere between the faceplate and the groove in the ruler. At this point the service engineer from Elekta was there and he looked at the situation and the door had been decided to be opened so the source could be retracted to resolve the situation. With the door open, the room monitor was showing radiation present so we closed the door. At this point, the service engineer engaged the emergency switch and tried to add additional force to the source to retract. This was unsuccessful. Contacted the Elekta Radiation Safety Officer (RSO) for advice. The Elekta RSO suggested to go into the room and retract the source manually. The service Engineer and the Director for Radiation Services then entered the room to secure the ruler with the source in it inside the lead pig sitting right next to the mHDR unit. The plan for securing the source and ruler was discussed and approved with the Elekta RSO. The event was planned and timed. It took 11 seconds from opening the door to securing the source inside the pig. The source cable was secured to the pig. The pig was secured inside a cabinet and the room was secured to prevent unauthorized entry. The exposure around the container was 50 mR/hr at the surface and 18 mR/hr at one meter away. Lead bricks were placed around the cabinet to reduce the exposure and the dose was measured at <1mR/hr at the lead bricks where the door is located. The Device is an Elekta Nucletron Flexitron Serial Number: 00225 Source: Ir-192, 12.21 Ci on 7/30/2015 Serial Number: D363E-0477 Model Number: 136.147 This event was also reported by the device manufacturer, ELEKTA, at 0948 EDT on 08/19/2015 NRC License No. 10-35096-01- SEE EN # 51330 * * * UPDATE PROVIDED BY MARK YUDELEV TO JEFF HERRERA AT 1519 EDT ON 08/24/2015 * * * The following additional information summary was excerpted from a detailed time line provided by licensee via email: "McLaren Macomb was in the middle of a project to replace a microSelectron v2 HDR unit with a Flexitron unit. The installation was scheduled to be completed on Friday, August 14, 2015, with training and commissioning to begin immediately. However, the dedicated camera for source position verification was pending shipment and installation by the vendor. In light of this missing camera, a Source Position Ruler was borrowed from our sister facility at Karmanos Cancer Institute in Detroit, MI to check the source position accuracy with Gafchromic film as part of acceptance procedures. "On August 18, 2015, the source position check ruler was connected to the Flexitron channel five using matching transfer tubes. The plan was created for the source to dwell at positions 360 (most proximal), 370, 380, 390, 395, and 400mm (most distal) within the ruler for two seconds each. In the absence of dedicated Elekta camera, the CCTV camera for in-room patient monitoring was used. The camera was zoomed on the part of the ruler where the source was expected to dwell. The plan was executed successfully with the source position check ruler two times. On the third attempt, the source got wedged inside the ruler and could not be retracted into the HDR safe. No patient was involved in this incidence and the event did not result in any unplanned exposure to any personnel." "[During source retrieval] , the total time from entering the room until the source was secured inside the emergency container was 11.16 seconds, which would result in total exposure of 140 mRem to the whole body. The survey around the lead container showed an exposure rate of 8 mR/hr at the top, 48 mR/hr at the side and 18 mR/hr 3 feet away. The background radiation recorded by the meter was 0.002 mR/hr. The power to the unit was removed. The radiation survey meter recorded background radiation at the console area and patient access hall about 20 feet away from HDR door. "The door to the HDR room was secured. The automatic door switch to the HDR room was disabled, and the door knob inside the room turned so that the keypad to unlock the door was deactivated. The electrical door opener was also disengaged from inside the room. As such, one could only enter the room using a dedicated key. There are only two copies of the key which are in the possession of the Authorized Medical Physicists[AMP]. A 'Do Not Enter' sign, along with the AMPs name and mobile phone number, was placed on the door. "The emergency container was placed inside the HDR cabinet into the back corner and the cabinet locked. The survey meter showed an exposure rate of 5 mR/hr at the cabinet door. A wall was built around the emergency container using 8 inch x 5 inch x 2inch steel bricks. This reduced the exposure rate at the cabinet door to about 1 mR/hr." Notified R1DO(DeFrancisco), R3DO(Skokowski) and NMSS Events Notification (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-08-27
51340 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2015-08-24 10:20 | 2015-08-24 11:36 | 2015-08-24 | LOSS OF SEISMIC ALARM CAPABILITY DURING CONDUCT OF FUNCTIONAL TEST "This notification is being made in accordance with 10 CFR 50 72(b)(3)(xiii) as an event that will result in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g. a significant portion of control room indication, Emergency Notification System or offsite notification system.) "The emergency preparedness plan requires seismic monitoring instruments to diagnose an earthquake for emergency actions levels (EAL) HU6 (Natural or destructive phenomena affecting protected area) and HA6 (Natural or destructive phenomena affecting vital areas). "At 1020 CDT on August 24, 2015 the Semi-Annual Seismic System Functional Test commenced. While this test is in progress, seismic alarm capability is not available for EAL declaration purposes. ANO procedures provide compensatory measures of using offsite sources to obtain seismic data. It should be noted that seismic data will still remain capable of being recorded, only alarm capability is lost." The licensee notified the NRC Resident Inspector. | 100 | 96 | 0 | 100 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-08-24
51339 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-08-23 13:00 | 2015-08-23 17:37 | 2015-08-23 | GRASS FIRE IN OWNER CONTROLLED AREA "A fire was reported to the unit 2 control room at 1300 central time [CDT]. The fire was reported to be in the owner controlled area 3/4 of a mile west of the protected area and switchyard. The local fire department was dispatched to fight the fire. The fire burned approximately 1.5 acres. The fire was reported to be out at 1417 central time. No plant equipment was damaged and the operation of the plant was not affected. Region 12 (Houston) of the Texas Commission of Environmental Quality (TCEQ) was notified of the event at 1509 for visible emissions resulting from the grass fire. No further actions are required by the TCEQ at this time and no press release is planned." The fire was caused by a downed 12.5 kV power line which powers outlying plant areas. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-08-23
51338 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-08-22 16:28 | 2015-08-22 20:14 | 2015-08-22 | REACTOR SCRAM DUE TO A SINGLE MSIV CLOSURE "On Saturday, August 22, 2015, at 1628 [EDT], with the reactor at 100% core thermal power (CTP) the Pilgrim Nuclear Power Station (PNPS) experienced an automatic reactor scram signal due to the rapid closure of one main steam isolation valve (MSIV). Other than the MSIV all other plant systems responded as designed. Plant cooldown is in progress using steam bypass to the main condenser. "The plant is in hot shutdown. The cause of the MSIV closure is still under investigation. This event has no impact on the health and safety of the public. The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'Any event that results in actuation of the reactor protection system (RPS) when the reactor is critical'. "Subsequent to the reactor scram the plant experienced the following isolation signals: - Group 2 Isolation: Miscellaneous containment isolation valves - Group 6 Isolation: Reactor Water Clean-up - Reactor Building Isolation Actuation "This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).'" Plant response was considered normal and the plant is in a stable shutdown / cooldown condition. The license will be notifying the Commonwealth of Massachusetts. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-08-22
51337 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2015-08-22 08:30 | 2015-08-22 09:27 | 2015-08-22 | SUSPECTED TAMPERING OF PLANT EQUIPMENT Interruption of normal operation due to tampering with security equipment. Immediate compensatory actions were implemented. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-08-22
51336 | 0 | DEPARTMENT OF THE NAVY |  |  |  |  | 2015-07-31 | 2015-08-21 13:29 | 2015-08-21 | LOST/MISSING AIRCRAFT ICE DETECTOR "On 31 July 2015, Fleet Readiness Center East (FRC East) Radiation Safety Officer (RSO) was notified that an H-53E ice detector probe was missing. The ice detector probe contains a solid 50 microcurie source of Strontium 90 (Sr-90) sealed within a metal casing. The RSO was notified about the missing probe by the H-53 Task Manager. The last known date and location of the ice detector probe was 4 November 2014 in the Aircraft Line Fiberglass Repair Shop. It is believed the probe has departed FRC East and MCAS [Marine Corps Air Station] Cherry Point as scrap/trash. "To prevent future recurrence, the following actions will occur: a. The aircraft line will include a mandatory task line to remove the ice detector probe from the duct any time the duct is removed from the aircraft. B. A training course will be established to distribute throughout the facility for proper identification, handling, and disposal instructions of all radioactive components. Prior to this incident, training was tailored to specific shops which process these parts. A need for broader training has been recognized and will now include those areas which would not normally receive a radioactive component." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-08-31
51335 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-08-20 17:55 | 2015-08-20 23:08 | 2015-09-02 | CONDITION THAT COULD PREVENT PRESSURIZER PORV BLOCK VALVES FROM OPERATING "On 8/20/2015 at 1755 [CDT], a design flaw was discovered with the pressurizer power operated relief valve (PZR PORV) block valve control circuitry. Specifically, the circuit deficiency for which a design basis fire in the Main Control Room (MCR) or cable spreading room could prevent the PZR PORV block valves from being closed from the local control switch at their associated motor control center (MCC). Engineering has reviewed this issue and determined that a potential fire induced ground in the MCR or cable spreading room could clear the associated control power fuses which would prevent the block valves from operating at the local control switch. "These valves are considered to form a High/Low pressure interface which requires postulating a proper polarity DC cable to cable fault. Engineering has reviewed the circuit design and cable routing associated with PORVs 1(2)RY455A and 1(2)RY456 and determined that their associated cables are routed with other DC circuit cables in the MCR control board and cable spreading room raceways, such that this postulated fault could potentially cause spurious opening of one of the PORVs even after the control power fuses have been removed as directed by the station abnormal operating procedures for control room inaccessibility. "This identified block valve circuit deficiency prevents the credited safe shutdown action of locally closing the block valves to mitigate the spurious operation of a PORV. "Hourly fire watches of the affected MCR and cable spreading room fire zones have been implemented. In addition, the MCR is continuously staffed and the affected cable spreading room fire zones are equipped with detection and automatic suppression. "This event is being reported under 10CFR50.72(b)(3)(ii)(B) for 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "The licensee has notified the NRC Resident Inspector." * * * UPDATE AT 1816 EDT ON 9/2/2015 FROM BRIAN LEWIN TO MARK ABRAMOVITZ * * * "During the extent of condition review, an additional design deficiency was identified with respect to the PZR PORV and PZR PORV Block valves control circuitry. Specifically, the current mitigating strategy for removing PZR PORV control power fuses does not adequately prevent a PZR PORV from spuriously opening due to fire induced hot short. Furthermore, local actions to close the associated PZR PORV block valve at the motor control center (MCC) may not be effective because the MCC may not have electrical power during the design basis fire. Therefore, the credited safe shutdown action to remove the PZR PORV control power fuses does not prevent the PZR PORV from spuriously opening during design basis fires in some of the upper and lower cable spreading room fire zones. "The affected Fire Zones are the same upper and lower spreading rooms previously identified and fire watches of the affected areas remain in place. "The NRC Resident Inspector has been notified." Notified the R3DO (Skokowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-08-20
51334 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-08-20 17:10 | 2015-08-20 22:28 | 2015-09-02 | CONDITION THAT COULD PREVENT PRESSURIZER PORV BLOCK VALVES FROM OPERATING "On 8/20/2015 at 1710 CDT, a design flaw was discovered with the pressurizer power operated relief valve (PZR PORV) block valve control circuitry. Specifically, the circuit deficiency for which a design basis fire in the Main Control Room (MCR) or cable spreading room could prevent the PZR PORV block valves from being closed from the local control switch at their associated motor control center (MCC). Engineering has reviewed this issue and determined that a potential fire induced ground in the MCR or cable spreading room could clear the associated control power fuses which would prevent the block valves from operating at the local control switch. "These valves are considered to form a High/Low pressure interface which requires postulating a proper polarity DC cable to cable fault. Engineering has reviewed the circuit design and cable routing associated with PORVs 1(2)RY455A and 1(2)RY456 and determined that their associated cables are routed with other DC circuit cables in the MCR control board and cable spreading room raceways, such that this postulated fault could potentially cause spurious opening of one of the PORVs even after the control power fuses have been removed as directed by the station abnormal operating procedures for control room inaccessibility. "This identified block valve circuit deficiency prevents the credited safe shutdown action of locally closing the block valves to mitigate the spurious operation of a PORV. "Hourly fire watches of the affected MCR and cable spreading room fire zones have been implemented. In addition, the MCR is continuously staffed and the affected cable spreading room fire zones are equipped with detection and automatic suppression. "This event is being reported under 10CFR50.72(b)(3)(ii)(B) for 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "The licensee has notified the NRC Resident Inspector." * * * UPDATE PROVIDED BY ROB SHERMAN TO JEFF ROTTON AT 1845 EDT ON 09/02/2015 * * * "During the extent of condition review, an additional design deficiency was identified with respect to the PZR PORV and PZR PORV Block valves. Specifically, the current mitigating strategy for removing PZR PORV control power fuses does not adequately prevent a PZR PORV from spuriously opening due to fire induced hot short. Furthermore, local actions to close the associated PZR PORV block valve at the motor control center (MCC) may not be effective because the MCC may not have electrical power during the design basis fire. Therefore, the credited safe shutdown action to remove the PZR PORV control power fuses does not prevent the PZR PORV from spuriously opening during design basis fires in some of the upper and lower cable spreading room fire zones. "The affected Fire Zones are the same upper and lower spreading rooms previously identified and fire watches of the affected areas remain in place. "The NRC Resident Inspector has been notified." Notified the R3DO (Skokowski) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-08-20
51333 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-08-20 10:32 | 2015-08-20 18:51 | 2015-08-20 | AUTOMATIC START OF AN EMERGENCY DIESEL GENERATOR ON LOW BUS VOLTAGE "On August 20, 2015, at approximately 1032 CDT, during the Residual Heat Removal flow rate test, the 3ED 4kV Shutdown Board received a degraded voltage signal, which automatically started the 3D Emergency Diesel Generator (EDG). The EDG performed its safety function by automatically supplying power to the Shutdown Board. Troubleshooting on the degraded voltage signal is in progress. The remaining 4kV Shutdown Boards and EDGs were unaffected and remain operable. "This constitutes an automatic actuation of the EDG and requires an 8-hour ENS notification in accordance with 10 CFR 50.72(b)(3)(iv)(A), due to the valid actuation of the EDG, and a 60-day report in accordance with 10 CFR 50.73(a)(2)(iv)(A). "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-08-20
51332 | 0 | U.S. ARMY |  |  |  |  | 2015-08-19 15:52 | 2015-08-20 15:05 | 2015-08-20 | LOST/STOLEN U.S. ARMY RADIOACTIVE CHEMICAL ALARMS FOR SALE OR SOLD ON EBAY The U.S. Army TACOM Radiation Safety Program Manager in Warren, MI was notified via email of what appeared to be U.S. Army material containing radioactive sources were for sale on eBay. The program manager was not able to find the listing but the information received indicated that the material was already sold or the listing expired. When the program manager contacted eBay about the material and the seller, eBay was uncooperative, citing privacy of the individuals selling/buying the material. The program manager contacted the U.S. Army Criminal Investigative Command in Troy, MI and provided them with all the information pertaining to the material. Since the material was not recovered, the U.S. Army considers the material lost/stolen. The materials are two M8A1 Chemical Agent Alarms each containing nominally 300 microcuries of Am-241. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-08-28
51331 | 0 | INTERNATIONAL ISOTOPES |  |  |  |  | 2015-08-20 09:00 | 2015-08-20 13:04 | 2015-09-08 | PERSONNEL OVEREXPOSURE "At about 0900 MDT on Thursday August 20, 2015, [the CEO of International Isotopes] was informed by our area manager that one of our technicians had been exposed to a 'flash' of radiation while handling a Co-60 source drawer. They reported his electronic dosimeter was reading 5.62 Rem. [The CEO of International Isotopes] immediately went to the work area and verified the Co-60 source (approximately 4000 Curies of Co-60) was in a secure shielded position and interviewed the technicians involved. All of the other technicians in the area reported their pocket or electronic dosimeters were reading normally (e.g. doses in the range of 1 to 5 mRem). The initial investigation indicates there was only one technician performing the work and in the immediate vicinity of the cask and source drawer at the time of the exposure. "The technicians were preparing to transfer the Co-60 source drawer into another shielded container (a therapy head). A special handling tool had been bolted to the end of the source drawer for positioning the source drawer within a therapy head. This special handling tool needed to be removed from the source drawer in order to transfer the source back into the therapy head. The technician attempted to move the source drawer just enough to expose the bolts on the special handling tool so it could be removed. The technician stated that the drawer was sticking and when he pulled harder on the drawer it slid out of the cask about 9 inches, bringing the source to within an estimated 2 inches of the cask external surface. The technician immediately pushed the source drawer back into the cask into a fully shielded position. The technician then noted that his electronic dosimeter was reading 5.62 [Rem] and he left the work area." The electronic Dosimeter reading was at 26 inches from the source. The TLD was approximately 15 inches from the source and a dose calculation resulted in a whole body dose of 16.9 Rem. Dose calculations for the hand (extremity) is 237 to 950 Rem depending on various assumptions. The technician was not wearing any finger rings. His dosimetry is being sent off for emergency reading. The technician is being restricted from work on radioactive materials. * * * UPDATE FROM STEVE LAFLIN TO JOHN SHOEMAKER AT 1135 EDT ON 8/22/15 * * * "The follow-up investigation continues at INIS. We have completed several simulated walk-throughs of the event and compared to personnel statements and descriptions of the event. "We have been able to retrieve security camera footage of the event as well from two different angles. The security video footage reveals that the technician did, in fact, momentarily completely remove the source drawer containing the cobalt source from the shield. This video is being used to carefully model estimated exposures to both the individuals extremity and whole body. "Dosimetry results were obtained from Landauer and indicated whole body readings of 201.875 Rem. Blood sampling from the individual does not support this high of an exposure and a review of the security video indicates the individuals TLD (on a lanyard around his neck) swung out away from his body, very near the source drawer, and was not in a position to accurately represent whole body exposure. Additional modeling using the security camera footage and additional data obtained from the electronic dosimeter will be used to estimate a more accurate whole body dose to the individual. "The exposed individual has been providing blood samples at the local hospital per the sampling protocol prescribed by the DOE Radiation Emergency Assistance and Training Center. All blood samples are normal with no indication of radiation exposure. This sampling will continue through today (August 22) until a 48 hour period of testing from the event has been completed. "Closer modeling to more accurately determine the individuals extremity dose are still in progress. This modeling is using both security camera footage as well as video footage from the mock-up of the event. While this modeling is not complete it appears that extremity dose may be closer to 50 Rem or less rather than the 250 - 950 Rem initially estimated. "Daily photographs are being taken of the individuals hands and lower extremities to monitor for the development of any edema or signs of radiation damage to tissues. At this time there are no indications of radiation effects to any extremity. "Additional data was extracted from the electronic dosimeter worn by the individual. This dosimeter was the device that initially read 5.62 Rem after the event. Analysis of the dosimeter data indicates it was exposed to a peak dose rate of about 3,739 R/hr. This is significantly less than the 10,166 R/hr initially estimated to have caused the 5.62 Rem ED reading at an estimated 2 seconds of exposure time. Using dose and dose rate information from this ED it appears the actual exposure time was about 5.4 seconds and this correlates with the security camera video time stamp. "Additional information will be reported as it becomes available." Notified R4DO (Hay), NMSS EO (Habighorst), and NMSS (McIntosh), NSIR (Milligan), and NMSS_Events_Notification via email. * * * UPDATE FROM STEVE LAFLIN TO JOHN SHOEMAKER AT 2129 EDT ON 8/22/15 * * * The following update was received from International Isotopes via email: "Blood testing for the technician involved in the exposure event has been completed and all results are normal. Complete documentation is to be provided to the company by the medical provider on Monday and an additional follow-up discussion will be held directly between the company and the physicians at REAC/TS [National Nuclear Security Administration - Radiation Emergency Assistance / Training Site] on Monday, 8/24 to see what additional, if any, testing is recommended." Notified R4DO (Hay), NMSS EO (Habighorst), and NMSS (McIntosh), NSIR (Milligan), and NMSS_Events_Notification via email. * * * UPDATE AT 1309 EDT ON 8/23/15 FROM STEVE LAFLIN TO MARK ABRAMOVITZ * * * "Dose modeling of the technician's extremity (left hand) and whole body exposures have been completed. These models estimate 49.1 Rem to the left hand. The whole body dose has been calculated to be 7.245 Rem. Both models were completed using micro shield and based upon a 3664 curie source in a 5.5 second exposure period. The whole body model assumed 3 worker positions and all times and distances are based upon our observations of the security video and supplemented by the mock-up of the event. Additional modeling will be performed of the lower extremities to confirm whether the left hand was likely to have been the most exposed extremity. The whole body model will also be validated by repeating the calculations and assumptions used against the known position of the electronic dosimeter and comparing calculated results of this modeling to the 5.62 Rem indicated on that dosimeter after the event. Over the coming weeks the company plans to acquire an expert in this type of dose reconstruction and have them independently verify the company's models and exposure calculations. "The completed report of all lab work on the exposed technician is expected to be obtained on Monday, August 23. The company also plans to contact DOE's REAC/TS on Monday and confer with them on all blood test results and discuss whether any additional precautionary sampling or testing is advised. "Visual examination of the exposed technicians hands and lower extremities will continue to be performed daily at least through August 28 unless REAC/TS recommends a longer monitoring period. At this time there are still no indications of radiation effects to any extremity of the exposed technician." Notified the R4DO (Hay), NMSS EO (Habighorst), IAEA Contact (Milligan & McIntosh via e-mail), and NMSS Events Resource (via e-mail). * * * UPDATE AT 1220 EDT ON 08/24/15 FROM STEVE LAFLIN TO JEFF HERRERA * * * "REAC/TS has been contacted to discuss and review the results of laboratory work of the exposed technician. [The] Associate Director, Radiation Emergency Assistance Center/Training Site confirms that all blood work appears normal. [The Associate Director REACTS/TS] recommended that we continue CBC once daily through Friday this week and continue to forward them the results. She also agreed with our plan for continued daily examination of extremities through 8-28 but recommended further that we continue this examination every other day for up to 3 weeks post event (Sept. 10). "The company has contracted with [the] Associate Dean for Idaho State University, to perform an independent dose assessment of the event. This work is expected to begin this week with a goal of including this report with the formal 30 day report on this event." Notified the R4DO (Campbell), NMSS EO (Habighorst), IAEA Contact (Milligan & McIntosh via e-mail) and NMSS Events Resource (via email). * * * UPDATE AT 1353 EDT ON 9/8/2015 FROM STEVE LAFLIN TO MARK ABRAMOVITZ * * * The following report was received via e-mail: International Isotopes received the cytogenetic biodosimetry analysis for this event. "The results are dated September 2, 2015 but were just made available through the ordering physician and the individual to the Company today. The result of 0.504 Gy (50.4 Rad) is much higher than our previous whole body dose estimates but does not change the Company's current course of action and corrective actions. REAC/TS was contacted to discuss the results and does not recommend any re-testing to validate the results. REAC/TS still confirms they do not consider this a 'clinically significant dose.'" Notified the R4DO (Drake), IAEA (Milligan and McIntosh), NMSS EO (Silva), and NMSS Events Resource via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2015-08-28
51330 | 0 | ELEKTA, INC. |  |  |  |  | 2015-08-18 10:18 | 2015-08-19 09:48 | 2015-08-24 | FLEXITRON SOURCE LODGED IN CHECK RULER "On the morning of August 18, 2015, the Elekta Field Service Engineer (FSE) was called to the [Customer's facility, McLaren Cancer Institute Macomb, in Mt. Clemens, MI] to investigate an obstruction error involving a 10.2 Ci Ir-192 source and a Flexitron HDR. The facility was using a microSelectron source position check ruler to check the source positioning of the Flexitron source. The source became lodged in the check ruler. The system E-stop was unable to retract the source. "The FSE placed the check ruler and stuck source assembly into the customer's microSelectron HDR (mHDR) Emergency Service container (ESC) in order to secure the radioactive material in a shielded container. He then tried to manually retract the source back into the Flexitron unit which was also unsuccessful. "Elekta RSO [Radiation Safety Officer] and FSE engaged the assistance from Senior Technical Support in Veenendaal [Netherlands]. After several troubleshooting attempts, the final decision was to remove the source tail in its entirety from the Flexitron unit. During the whole process, the source cable, check ruler and transfer tube remained secured in the emergency service container. "Currently, the customer's mHDR ESC, which contains the source cable assembly, is secured and being bunkered inside the facility's 'dog house.' The survey readings of the ESC obtained by the customer physics staff were 50 mR/hr at the surface hot spot and 18 mR/hr at 1 meter. "The FSE has checked the mechanical condition of the Flexitron unit and has loaded a dummy source. The unit is functioning properly. "Elekta has reached out to their source manufacturer for assistance in transporting the source assembly in its entirety out of the facility. "Elekta has escalated this case to the complaint handling department at Elekta/Nucletron B.V. for investigation. Further information will be forwarded upon receipt." There were no over exposures or contamination involved with this event. * * * UPDATE AT 1331 EDT ON 08/19/15 FROM PRAVEEN DALMIA OF MT. CLEMENS REGIONAL MEDICAL CENTER TO JEFF HERRERA * * * This event was reported by Mt. Clemens Regional Medical Center d/b/a McLaren McComb, Mt. Clemens, MI. NRC License No. 21-04080-01 - See EN # 51341 Notified R1DO (DeFrancisco), R3DO (Riemer) and NMSS Events Notification Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-08-27
51329 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2015-08-18 13:31 | 2015-08-18 19:38 | 2015-08-18 | RESIDUAL HEAT REMOVAL HEAT EXCHANGER OUTLET VALVES UNANALYZED CONDITION At 1331 hours [EDT] on August 18, 2015 with the plant in mode 1, IP2 entered TS [Technical Specification] 3.0.3 upon determination by the Shift Manager that MOV-746 and 747 at the outlet of the Residual Heat Removal (RHR) Heat Exchangers may not (fully) open on an Sl [Safety Injection] signal if there was a degraded grid voltage (where the voltage at the 480V Safeguards Buses is below the minimum drop-out value of 415V and above the loss-of-voltage value of 206.6V). The MOV 746 and 747 valves are normally closed so the Sl signal with degraded voltage present could cause the fuses to fail. The time when the fuses would fail and the extent to which the MOVs open has not yet been analyzed. Immediate corrective actions was taken to replace the fuses with fuses that would not fail. The RHR trains were restored to an operable condition at 1419 and 1431 hours. This event is potentially reportable under 10 CFR 50. 72(b)(3)(ii) and 10 CFR 50.72(b)(3)(v) since the condition has not yet been fully analyzed but has been corrected. "The plant remained at 100% power during the time of this event. All technical specification requirements were followed." The licensee will notify the NRC Resident Inspector and the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | UNANALYZED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2015-08-18
51328 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-07-21 00:11 | 2015-08-18 17:52 | 2015-08-18 | AGREEMENT STATE REPORT - IRRADIATOR SOURCE RACKS FAILED SAFE The following report was received via e-mail: " On 07/21/15, Sterigenics Corporate RSO [Radiation Safety Officer] contacted RHB-Sacramento office [California Radiation Health Branch] via an email and telephone to report the following event in accordance with 36.83(a)(4). His email stated the following: "Last night [7/21/15] at approximately 12:11 AM PDT at the Sterigenics Hayward Facility (Radioactive materials License 6268-1), the pneumatic cylinder used to raise one of the two source racks (Hoist #1) failed to function as designed. The failure did NOT cause a 'stuck source' nor was there any risk of exposure to any individual as a result of this failure. The source did return to the 'down' position in the pool as designed, however, the pneumatic cylinder experienced a failure and a broken flange and is not operable. "We [Sterigenics} will review in detail the cause of this failure and implement appropriate corrective action including any necessary changes in maintenance and equipment and report these changes to you [California] in writing within 30 days as required by 10CFR36.83 (b). "In the interim, the facility will not commence operations until repairs are completed to the hoist and approval to commence operations is granted by the Corporate RSO and Corporate Engineering. "[Sterigenics] further stated that there is no emergency or current issue. A corporate engineer will arrive in San Francisco by 2:00 on 7/21/15 to work on the irradiator. Facility is staffed 24/7 and will notify RHB before resuming any operations. "[California] RHB will be following up with the licensee." California Event 072115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-08-26
51327 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2015-08-15 | 2015-08-18 12:15 | 2015-10-15 | AGREEMENT STATE REPORT - ORPHAN SOURCE FOUND IN A GARBAGE TRUCK "A garbage truck containing a radioactive source was reported by local police in Union City, NJ. NJ State police preliminarily identified Ra-226, which was confirmed by NJDEP Radiation Program staff who responded to the event. Exposure rate was measured as 60 mR/hr on contact on the truck. Based on measurements, activity was estimated to be 10 mCi. The US DOT was contacted, and approved issuance of a DOT Special Permit 11406 even though readings exceeded 50 mR/hr. Truck was moved to truck owner's (Galaxy Sanitation) location in Jersey City, NJ., where the hired contractor sorted the load and found a small radium source. No identifying information was on the source. It has been adequately shielded and secured at the site pending disposal. "NJDEP will continue to monitor the situation and provide updates as necessary." The garbage truck made a pickup in Union City, New Jersey and was stopped by the police because the truck was leaking liquid. As the officer approached the truck, his paging radiac alarmed. New Jersey Incident: C569188 * * * UPDATE PROVIDED BY JAMES MCCULLOUGH TO JEFF ROTTON AT 1607 EDT ON 10/15/2015 * * * The following information was provided by the State of New Jersey via email: Consultant was able to reduce the surface exposure rate below 50 Mr/hr so that the DOT Special Permit 11406 could be issued. The item was removed from the site by a licensed waste broker on 8/25/2015. Notified R1DO (Jackson) and NMSS Events Notification group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2015-08-26
51326 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-08-05 12:45 | 2015-08-17 15:10 | 2015-08-17 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE RETRIEVAL "The crew [for H&H X-Ray Services] was x-raying pipe at a temporary job site in Elm Grove, LA. Due to the configuration, the camera was above the guide tube and the source and guide tube were on a surface below. The camera slipped and fell approximately 18 inches and landed on the guide tube and crimped the guide tube not allowing the source to be returned to the shielded position. A survey indicated the source was still in the guide tube. The boundaries were maintained until the RSO and his assistant arrived to perform the retrieval. Following the source retrieval procedure, the source was placed into a shielded source changer, QSA Global 650L, and returned to the company's West Monroe, LA storage location. Except for the guide tube, none of the equipment was damaged. Exposures to the crew and the retrieval crew were minimal. "Reported to the LA Department of Environmental Quality 08/13/2015 at 1533 CDT. "Exposure Device AEA/QSA Model 880 Delta, SR D2767, Source: 58 Ci Ir-192, Model A424-9, SN 18108G" State Event Report ID No.: LA 150013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-08-25
51325 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-08-16 | 2015-08-17 15:05 | 2015-08-17 | AGREEMENT STATE REPORT - RADIOGRAPHY TRUCK DARKROOM ATTEMPTED BREAK-IN "On Sunday August 16, 2015, the Colorado Department of Public Health and Environment, Radioactive Materials Unit, received a phone call on the after-hours emergency response line. The Corporate RSO for Desert NDT, CO 902-01, reported an attempted break-in on a radiography truck. The attempt occurred while the vehicle was parked overnight at the Cotton Wood Suites, 12095 Mariposa Street, Westminster, CO 80234. The radiographer's reported that the door to the darkroom had been tampered with, the door was not breached, therefore the alarm never activated. Evidence of the attempted break-in was identified the following morning, Sunday, August 16, 2015. All radioactive materials were accounted for by Desert, NDT, no theft occurred. "The approximate time of break-in occurred between the hours of 1755 MDT, Saturday, August 15, 2015 and 0815 MDT, Sunday, August 16, 2015. The radioactive material involved in this incident was 39 Ci of Ir-192, Source SN: Y560, Model: Industrial Nuclear Company Model 7. The source was inside a QSA Delta 880 camera. The Westminster Police were called and a police report was filed. The police report number is: 2015-14914." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-08-25
51324 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-08-17 05:05 | 2015-08-17 13:01 | 2015-08-17 | LOSS OF ASSESSMENT CAPABILITY DUE TO PLANNED MAINTENANCE ON SEISMIC INSTRUMENTATION "At 0505 CDT on August 17, 2015, Clinton Power Station's Seismic Instrumentation system was removed from service to support scheduled maintenance. During this time, the seismic instrumentation will not be able to generate Main Control Room annunciation or provide ground acceleration information necessary for Emergency Action Level (EAL) threshold determination until the seismic instrumentation is restored. Since the duration of the maintenance activity is expected to last greater than 24 hours, with no viable compensatory measure specified in the EAL's, this condition will result in a loss of emergency assessment capability while the Seismic Instrumentation is out of service and results in a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector and the licensee has informed the State of Illinois Resident Engineer." The licensee also notified the State of Illinois Emergency Management Agency. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-08-17
51323 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-08-17 10:30 | 2015-08-17 12:59 | 2015-08-17 | OFFSITE NOTIFICATION DUE TO OIL SPILL "At 0837 EDT on August 17, 2015, it was determined that Beaver Valley Unit 2 had experienced a small oil leak of approximately 1 liter from equipment located inside the Alternate Intake structure, some of which progressed to the Ohio River. Subsequent to confirmation of this discovery, notification was made to the following offsite agencies starting at 1030 EDT: "National Response Center (Incident Report# 1125865), Pennsylvania (PA) Department of Environmental Protection, Beaver County Emergency Management, PA Emergency Management Agency, and downstream water authorities (Midland Water Authority, Allegheny Ludlum, East Liverpool Water Co.) "This notification is a required 4-hour report per 10 CFR 50.72 (b)(2)(xi). "The source of the oil leak has been stopped. Absorbent material has been placed to contain the oil that had leaked. No press release is planned. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-08-17
51322 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-08-11 | 2015-08-17 11:10 | 2015-08-24 | AGREEMENT STATE REPORT - ORPHANED SOURCE DISCOVERED / POSSIBLE OVEREXPOSURE INVOLVED "[The Oklahoma Environmental Agency, Radiation Management Section] has been informed [on 8/17/2015] that a member of the public was cleaning out a warehouse belonging to Northern Oklahoma College in Enid, Oklahoma on August 15, 2015 when they came across an unusually heavy box. When opened, they found what was apparently a lead pig and about 10 glass vials. The pig was not secured and when tipped over a metal rod approximately 1.25 inches by 3 inches fell out. A piece of masking tape on the rod was labeled 'HOT' and '4 Radium tubes 1 broken.' One of the workers picked up the tube and handled it for a few minutes before they noticed the Radioactive label on the box. At this point, they returned the contents to the box and notified the University. The University does not possess a radioactive materials license. The person who handled the rod is now seeking medical attention complaining of nausea, dizziness, pain like arthritis in his hands, and blistering on his feet. [The Oklahoma Environmental Agency, Radiation Management Section] will be sending an inspector to the University, probably today. More information [will be provided] as it becomes available." * * * UPDATE AT 1013 EDT ON 8/24/15 FROM KEVIN SAMPSON TO JEFF ROTTON * * * The following update was received from the Oklahoma Department of Environmental Quality via email: The original report documented that the material was discovered on 8/15/2015 while cleaning out a warehouse. This update revised this report to document that the discovery of the radioactive material occurred on 8/11/2015. The individual that handled the material with his hands was wearing leather work gloves when handling the radioactive material, but they were discarded with the other trash. On 8/14/15 the [member of the public] who handled the object reported feeling ill and on 8/17 went to a doctor complaining of nausea, dizziness, pain in his hands, and blisters on his feet. "On 8/17/15 [The Oklahoma Department of Environmental Quality, Radiation Management Section] conducted a reactive inspection of the facility. Surveys of the facility using a microR meter and survey meter with GM detector did not find any contamination. Wipe tests of various objects and areas were collected and are being counted. The pig was as described in the original report and surveys of it produced readings from 1.5 to 3.5 mR/hr on the exterior and approx. 70 mR/hr directly above the open mouth. A variety of other sealed and unsealed sources were also found, many dating from the late 1950s. The college has secured these and will arrange for their disposal as soon as possible. "On 8/18/15 [The Oklahoma Department of Environmental Quality, Radiation Management Section] again spoke with one of the workers who stated that the man who handled the source had been diagnosed with a reaction to mold exposure and given a cortisone injection. He was reportedly much better and had returned to work." Notified the R4DO (Campbell), NMSS Events (via email) and NMSS Mgr. (Henderson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-08-25
51321 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-08-03 09:00 | 2015-08-14 18:09 | 2015-09-23 | LOSS OF SIRENS DUE TO LOSS OF POWER "On August 14, 2015, the Grand Gulf Nuclear Station (GGNS) determined that less than 75% of the population in the ten mile EPZ could have been notified using the alert notification system (sirens). This condition existed between the time period starting sometime after 1800 [CDT] on Friday, July 31, 2015 until 1630 [CDT] on Monday August 3, 2015. "The completion of this notification was delayed because at the time of discovery the available information and built in system redundancy supported a conclusion that greater than 75% of the population could have been notified using the siren system. The diversity of the systems required repairs and testing to be coordinated with local officials in both Mississippi and Louisiana. "At 1000 CDT hours on August 3, 2015, GGNS was informed that the Claiborne County Emergency Operations Center (EOC) siren activation equipment had lost power over the weekend. Investigations and repairs were initiated by Claiborne County Emergency management upon discovery. The system was repaired and functional at 1630 hours on August 3, 2015." The licensee reported that 30 of 42 sirens lost power. The NRC Resident Inspector has been notified. * * * UPDATE FROM DAVID BURRUS TO JOHN SHOEMAKER AT 1243 EDT ON 9/23/15 * * * "Based on a detailed investigation (an apparent cause evaluation performed by the Grand Gulf Nuclear Station) into the events surrounding the power interruption at the Claiborne County EOC, Entergy has determined that the emergency power source for the Claiborne County EOC was available and would have been manually established by the Claiborne County EOC Emergency Director if the facility was activated. "Upon discovery of the problem, maintenance was immediately performed on the system to reestablish the normal source of power to the Claiborne County EOC. This maintenance required approximately 8 hours to complete. This maintenance activity required the lock-out tag-out of all power (normal and back-up) to the facility. "During the time period that all power was removed from the facility, the pre-established and pre-approved back-up notification system was available and would have been utilized to complete the required public notifications. "Supplement 1 to Revision 3 of NUREG-1022, Event Reporting Guidelines, 10CFR50.72(b)(3)(xiii), states in part the following: NEI 13-01 proposes that for extended unplanned losses of the primary public alerting system, a report would not be required if the FEMA approved backup alerting method was available and the primary public alerting system was returned to service within 24 hours This 24-hour cap is put into place to limit reliance on a less capable backup alerting method. However, because some backup capability exists, NRC action or awareness is not likely warranted in such scenarios for which the loss of the primary capability is limited in duration. As a result, a report would not be required "Therefore, Entergy is updating the above notification based on the developed information that the Claiborne County EOC Emergency Director understood how and would have manually established electrical power to the alert notification system if required and because the maintenance period was less than the 24 hour allowable period established in Supplement 1 to Revision 3 of NUREG-1022." The licensee has notified the NRC Resident Inspector. Notified R4DO (Pick). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-08-14
51320 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-08-13 | 2015-08-14 17:14 | 2015-08-14 | AGREEMENT STATE - EXTERNAL RADIATION LEVELS ON SHIPPING PACKAGE ABOVE LIMITS The following report was received from the Pennsylvania Department of Environmental Protection via facsimile: "NOTIFICATIONS: On August 13, 2015, Avid Radiopharmaceuticals (a PA licensee) informed the Department [Pennsylvania Department of Environmental Protection Bureau of Radiation Protection] of a shipment of fluorine-18 (F-18) from IBA Molecular Inc. (a New Jersey radiopharmaceutical licensee) with a maximum surface reading of 210 mR/hr. The event is immediately reportable per 10 CFR 20.1906 and 10 CFR 71.47. "EVENT DESCRIPTION: The licensee informed the Department that upon inspection of the package, the following was determined: 1. The area along the gap between the lid and the body of the shipping package gave the highest dose rates (180-230 mR/hr). 2. The licensee opened the package to [examine] the interior for any damage, but instead determined that the lid of the secondary shield was not present. 3. The licensee removed the 'Biodex pig' containing the F-18 activity in a vial to determine damage or contamination. It was observed that the screw top of the 'pig' was not secured properly (the thread of the lid and the body did not align), therefore there was a gap in the shielding. "The licensee determined that there was no observable damage to the activity, vial and an absence of removable contamination from the surface of the shipper. The F-18 is in the custody of the licensee. "CAUSE OF THE EVENT: Possible human error. "ACTIONS: The Department notified New Jersey's Department of Environmental Protection Radiation Control Program. Pennsylvania will follow-up during the next routine inspection of Avid." Event Report ID No: PA150023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-08-24
51319 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-08-14 08:50 | 2015-08-14 09:32 | 2015-08-14 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-08-14
51318 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-08-13 09:38 | 2015-08-13 16:52 | 2015-08-13 | FITNESS-FOR-DUTY REPORT INVOLVING A LICENSED EMPLOYEE "A licensed, non-supervisory employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated." The licensee notified the NRC Resident Inspector as well as the NRC Region 3 Office Safeguards Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Startup |  | Power Operation | Startup |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2015-08-13
51317 | 0 | MIDDLESEX HOSPITAL |  |  |  |  | 2015-08-11 12:00 | 2015-08-13 12:03 | 2015-08-25 | MEDICAL EVENT - PATIENT RECEIVED UNDERDOSE OF YTTRIUM 90 During a treatment of the left lobe of the liver, the dose delivered to the patient was discovered to differ greater than 20 percent than the intended dose. 120 Gray was prescribed by the physician and 72 Gray was delivered. During the procedure the Rados meter did not appear to be operating properly. Subsequent investigation determined that there was some radioactivity that remained in the vial. The technologist called the manufacturer who advised to perform several flushes and the Rados meter still did not change. The procedure was ended at that point. After ending the procedure when the survey was performed on the waste jar, it was discovered that only 60% of the dose was delivered. The activity appeared to be concentrated in the plunger attached to the vial. A new Rados detector will be obtained prior to the next procedure. The patient will be informed of the issue by the physician. Source Material: Yttrium 90, 7.03 GBq. * * * UPDATE AT 1718 EDT ON 08/25/15 FROM JOAN MERTON TO JEFF HERRERA * * * "On 8/11/15, a left lobe liver Y-90 embolization was performed in the interventional radiology room at Middlesex Hospital. The Y-90 therasphere activity was 7.04 GBq on 8/2/15 at [12:00 EDT] and 0.696 GBq on 8/11/15 at 10:00 am. Prior to placing the vial containing the Y-90 into the dose calibrator, the nuclear medicine technologist turned and tapped the lead pot 90 [degrees] three times. The Y-90 was infused at 12:11 pm on 8/11/15. The prescribed dose to the target volume was 120 Gray. The device and assembly were set up according to the checklist provided by the manufacturer. The authorized user turned the lead pot containing the vial 90 degrees three times and then tapped it on the table twice. The Rados meter read 1.0 mR/hr when the seal was removed from the Y-90 vial and before the commencement of the embolization. After the first flush with saline (20 ml/min) the rados meter still displayed a reading of 1.0 mR/hr. Two further flushes failed to reduce the reading of 1.0 mR/hr. The authorized user requested that the company (BTG/Nordion) representative be contacted. The lead technologist was advised by phone by the BTG representative to have the physician repeat the massaging of the tubing where the Roberts clamp had been released and perform two (2) additional saline flushes. After performing the representative's suggestions the reading was still 1.0 mR/hr. Per the lead NM [Nuclear Medicine] technologist, the BTG representative had no further recommendations. The authorized user then lifted the plexiglass cover of the apparatus and tapped on the green plunger three times and replaced the cover and flushed one more time. The rados meter reading was still 1.0 mR/hr. The procedure was ended. Following post procedure measurements on the waste jar, the calculations showed that 60% (72 Gray) of the dose was delivered to the left lobe of the liver. "Theraspheres may have been stuck in the vial and plunger. On 8/12/15, the Middlesex Hospital RSO/physicist measured the exposure levels from the separated out items in the waste jar. The highest reading was from the vial and plunger. The plunger was still attached to the vial. "There is no anticipated adverse effect on the patient despite the fact that a lower dose (72 Gy) was delivered to the left lobe. Most of the patient's tumor burden is localized to the right lobe. Therefore, no additional Y-90 administration is necessary. "Actions taken or planned: 1. BTG was notified. 2. The BTG RSO is working with the Middlesex Hospital RSO to determine the cause of the event. 3. In approximately 30 days, the Y-90 waste container will be sent to BTG for their investigation "On 8/13/15, the patient and the referring physician were notified of the medical event." Notified the R1DO (Krohn) and NMSS Events (via email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-08-21
51316 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-08-06 | 2015-08-12 20:20 | 2015-08-12 | AGREEMENT STATE REPORT - LOST TRITIUM TARGET SIGHTS The following report was received by the State of California via email: "On August 12, 2015, [the licensee's], Alternate Radiation Safety Officer, contacted the [State of California Radiologic Health Branch] Brea Radioactive Materials office to report lost Tritium [target sight] sources. After receipt at the [licensee] facility, 18 sources were no longer accountable in the inventory process. [The licensee] noted that, sometime between August 6 and August 10, the loss was discovered by one of the [licensee's] authorized users while performing an inventory of sources in the shipment to ensure that the proper number of sources were received. The lost sources were SRB Technologies, Inc. model AR Tritium [target sights] generally licensed sealed sources (these sources do not have serial numbers) with 0.8 Curies of tritium, for a total of 14.4 Curies. "After the missing sources were discovered, SRB Technologies was contacted to determine the number of sources that were supposed to be contained in the package. When SRB Technologies personnel notified [licensee] that the package contained 36 sources, as listed in the included packing slip, [licensee] personnel conducted a search of the facility to find the sources. When the search did not find the missing sources, it was determined that the missing sources were likely to have been thrown away with the packaging in their trash bin, which had already been emptied on the morning of August 7, 2015. The Irvine facility of Waste Management was contacted to determine if it was possible to search the trash bin, but they were told that was not possible and the trash was most likely to have been dumped in a landfill. Once the investigation into the loss of sources was completed on August 12, 2015, the licensee determined the sources to be lost, most likely in a landfill. After the determination that the source were lost was made, [the licensee] then contacted the [State of California] Brea Office to make the official report." California 5010 Number: 081215 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-08-20
51315 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-07-13 09:45 | 2015-08-12 17:14 | 2015-08-12 | AGREEMENT STATE REPORT - NDC GAUGE RECOVERED FROM LANDFILL "On July 13, 2015, a load of residential waste set off the radiation alarm at Middlepoint Landfill, in Murfreesboro, TN. The load, originally thought to be personnel medical waste, was set aside to decay. [Tennessee Radiological Health] Division staff returned on July 16, 2015, with a Canberra Inspector 1000 [detector], for identification and to obtain a spectrum for analysis. After review, the material was determined to be Am-241. [Tennessee Radiological Health] Division staff returned to landfill on July 17, to search for item. Separated from residential waste, the item was found to be a NDC Model 100 series backscatter gauge, SN #11755. The activity on the label was 0.93 GBq (25 mCi). The gauge was transported to the [Tennessee Radiological Health] Division field office in a probe down position surrounded by lead bricks; this resulted in dose rate readings to nearest occupant at approximately background levels. The [Tennessee Radiological Health] Division staff monitored the gauge in route to the field office. Upon arrival, the gauge was surrounded by lead bricks and stored in an isolated area with a pre-arrival background level of 6 microR/hr dose rate. The post-arrival dose rate readings were 8 microR/hr. "Under reciprocity, NDC Technologies personnel are scheduled to pack and remove the gauge on 8/13/2015, for return to the manufacturer." Tennessee State Event Report ID NO: TN-15-102 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-08-20
51314 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2015-08-11 13:00 | 2015-08-12 16:30 | 2016-03-08 | AGREEMENT STATE REPORT - DAMAGED KAY-RAY FIXED GAUGES REPAIRED WITH SHUTTER OPEN The following report was received from the State of Arkansas via email: "[The licensee] discovered two fixed gauges, manufactured by Kay-Ray, model #GRP-6082, serial #6124 (digester 2) and #6125 (digester 3) with a 5 Curie Cs-137 source were damaged sometime in May 2014. "The Department [Arkansas Department of Health] became aware of the repair during a routine inspection of the plant. According to the field service report, repairs were performed on June 5, 2014. The repairs were to the lead shielding around source holders which was separated from the original fabrication and needed to be refastened. The field service report indicated the shutter was not closed during the repairs. "Basic evaluations at the time of inspection, by [licensee] Radiation Control Health Physicists, indicated there were no public exposure levels above the regulatory requirement. The gauges are mounted on a steel metal box. The gauges are located on the 3rd floor 10 feet above the floor. Gauges are in cages inaccessible without a ladder. It is believed a small field of radiation was present but there were no significant exposures to the public. "The State is awaiting a written report from the licensee and will continue to investigate this event. The State will update this event as more information becomes available. "Louisiana Department of Environmental Quality office was notified." Arkansas Event Number: ARK-2015-011 * * * UPDATE FROM SUSAN ELLIOTT TO STEVEN VITTO ON 03/08/2016 AT 0943 EST * * * The following was received via email: "The written report dated March 3, 2016, from Clearwater Paper Corporation, detailed corrective actions to ensure repairs to the lead shielding around source holders were sufficient to prevent radiation exposure. A licensed contractor inspected all sources for physical integrity and validated their findings. There was no radiation leakage from any of the fixed gauges to include the two in question. The licensee confirms no exposure to the public. "The State considers this event closed." Notified R4DO (Proulx) and NMSS_EVENTS_NOTIFICATION via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-08-20
51313 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-08-12 10:07 | 2015-08-12 13:31 | 2015-08-13 | SECONDARY CONTAINMENT TECHNICAL SPECIFICATIONS NOT MET "At 1007 [EDT] on August 12, 2015, while restoring Reactor Building (RB) HVAC (RBHVAC) after surveillance testing, an equipment malfunction resulted in improper damper alignment resulting in Secondary Containment Technical Specifications (TS) to not be met. "The plant TS require Secondary Containment pressure be maintained greater than or equal to -0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1). This specification was not maintained for five seconds and the highest pressure observed was -0.095 inches of vacuum water gauge. This value was observed on only one of two installed recorders, of the Secondary Containment pressure recorders. The highest observed pressure on the other recorder was -0.14 inches of vacuum water gauge. Secondary Containment was restored by the Standby Gas Treatment System (SGTS) already in operation and shutting down the affected train of RBHVAC. "The technical specification requirement is to maintain secondary containment at -0.125 inches of vacuum water gauge for secondary containment operability. Declaring secondary containment inoperable is reportable under 10 CFR50.72(b)(3)(v)(c) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1159 EDT ON 08/13/15 FROM BRETT JEBBIA TO S. SANDIN * * * The licensee is updating this report to delete the minus sign for all references to inches of vacuum water gauge. "FOLLOW UP - CORRECTED INFORMATION: At 1007 [EDT] on August 12, 2015, while restoring Reactor Building (RB) HVAC (RBHVAC) after surveillance testing, an equipment malfunction resulted in improper damper alignment resulting in Secondary Containment Technical Specifications (TS) to not be met. "The plant TS require Secondary Containment pressure be maintained greater than or equal to .125 inches of vacuum water gauge (TS SR 3.6.4.1.1). This specification was not maintained for five seconds and the highest pressure observed was .095 inches of vacuum water gauge. This value was observed on only one, of two installed recorders, of the Secondary Containment pressure recorders. The highest observed pressure on the other recorder was .14 inches of vacuum water gauge. Secondary Containment was restored by the Standby Gas Treatment System (SGTS) already in operation and shutting down the affected train of RBHV AC. "The technical specification requirement is to maintain secondary containment greater than or equal to .125 inches of vacuum water gauge for secondary containment operability. Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)c as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material." the licensee informed the NRC Resident Inspector. Notified R1DO (Powell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-08-12
51312 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2015-08-05 | 2015-08-12 09:09 | 2015-08-12 | AGREEMENT STATE REPORT - Sr-90 SOURCE FOUND AT RECYCLING FACILITY The following report was received via fax: "On August 5, 2015, while investigating a collection of naturally occurring radioactive material (NORM) at Newell Recycling Southeast facility in Phenix City, AL, representatives from the Alabama Office of Radiation Control identified what appeared to be a very old gauge containing radioactive material. Initial field analysis measurements identified the isotope as Sr-90. "A follow-up visit on August 7, 2015 by Alabama Office of Radiation Control personnel confirmed the source of radiation to be a very old device containing a sealed Sr-90 source. Maximum radiation levels of 1500 mR/hr (beta + gamma) and 300 mR/hr (gamma only) at the port opening were measured. The device was secured and placed in storage at the facility. A leak test was performed and the results are pending. "The origin of the device is unknown. There are no identifying marks on the device. The Alabama Office of Radiation Control continues to investigate to determine the make, model and serial number. It is assumed that the device is a very old, generally licensed device that was abandoned, lost or stolen in the past." Alabama Incident 15-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2015-08-20
51311 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-08-11 | 2015-08-12 08:43 | 2015-08-12 | AGREEMENT STATE REPORT - DAMAGED PORTABLE INLINE DENSITY GAUGE The following report was received via e-mail: "On August 11, 2015, the licensee notified the Agency [Texas Department of State Health Services] that during a routine inspection of one of its Berthold model 8010 portable inline density gauges (SN: 10182), that contained a 20 millicurie Cesium-137 source, it found that the shutter handle was bent and the shutter could not be fully operated. The shutter was in the closed position. The gauge was secured at the licensee's facility. The licensee's radiation safety officer (RSO) is investigating the cause of the damage. The RSO has contacted the gauge manufacturer and arrangements are being made for repairs. There have been no exposures to any individual as a result of this event. Further information will be provided as it is obtained in accordance with SA-300." Texas Incident #I-9333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-08-20
51310 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2011-01-01 | 2015-08-11 15:16 | 2015-08-11 | AGREEMENT STATE REPORT - STOLEN THERMO ELECTRON XRF ANALYZER The following report was received from the Commonwealth of Kentucky via fax: "On 8/7/15, [the licensee] reported that [sometime] in 2011, a Thermo Electron XRF Analyzer Model XLp818 (serial number 17620) was stolen from their facility in Louisville, KY. The device contained a QSA Global AMCL Am-241 source (serial number 5588CW) that was 30 mCi on 3/13/2007. The KY RHB [Kentucky Radiation Health Branch] has requested additional information." KY Report: KY150004. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2015-08-19
51309 | 0 | ROTORK CONTROLS |  |  |  |  | 2015-07-28 | 2015-08-11 09:55 | 2015-09-10 | PART-21 NOTIFICATION - MICRO SWITCH INTERMITTENT VARIATION IN RESISTANCE The following report was received via fax: "On June 4, 2015, Rotork Controls Inc. opened a formal Part 21 [10 CFR 21.21] investigation into a self-identified anomaly relating to a basic micro switch - Pt No N69-921, description 'V12'. The anomaly is intermittent variation in electrical contact resistance and was first observed during the factory acceptance test of a Rotork safety related NA Range Electric Actuator; also referred to as an electric Valve Operator. "Rotork and the switch manufacturer are currently characterizing switch population contact resistance to establish whether an unsafe condition could exist as defined under 10 CFR 21." * * * UPDATE AT 0958 EDT ON 9/10/2015 FROM PATRICK SHAW TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "Rotork has concluded the investigation and based on test data determine an unsafe condition can exist as defined under 10CFR21. Testing has established that a small percentage of the switches supplied against Rotork purchase order P0116932 may exhibit an open circuit condition when operated. A slightly larger percentage of the population may exhibit high contact resistance ranging from 0.5 Ohm to open circuit. The anomaly affects the normally open and normally closed contacts equally. Contact resistance anomalies are random, not permanent, and appear to be unaffected by accumulated cycles. Additionally when a switch is operated its electrical state remains constant until the next operation. "Probabilities have been established by resistance measurements and by dynamic testing using voltages representative of customer applications. The dynamic evaluation predicts an open circuit probability of 0.0008% per operation. To date, no switch failures have been reported from any customer sites. Below are listed all orders provided to customers containing V12 switches from the defect batch. Report ER791 provides full details of Rotork's technical investigation." Notified the R1DO (Gray), R2DO (Shaeffer), R3DO (Pelke), R4DO (Drake), and Part-21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-08-11
51308 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2015-08-11 01:39 | 2015-08-11 05:19 | 2015-08-11 | AUTOMATIC REACTOR TRIP AFTER AN OFFSITE ELECTRICAL FAULT "Reactor trip caused by turbine trip. Turbine tripped immediately following the trip of one of four 345KV offsite lines. The reason for protective relaying not preventing the grid disturbance from tripping the turbine generator is not known at this time. All normal offsite and onsite power sources are available. "Auxiliary Feedwater actuated as expected on low steam generator level following the trip from 100% power. All systems functioned as expected in response to the trip. "The NRC Senior Resident Inspector has been notified." An electrical fault on a 345 kV line 2 miles from the site caused the bus to strip and reclose, which cleared the fault. All control rods fully inserted and the plant is in its normal shutdown electrical lineup. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-08-11
51307 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2015-08-10 23:32 | 2015-08-11 02:01 | 2015-08-11 | INADVERTENT SIREN ACTIVATION "At approximately 2332 EDT on August 10, 2015, the Ginna Control Room was notified of an inadvertent siren activation by the Monroe County Emergency Center. It is unclear at this time why the siren inadvertently activated. Company personnel are addressing the issue with the siren. "The licensee notified the NRC Resident Inspector." The siren activated for approximately 1 minute. The licensee will remove the siren from service until the cause of the inadvertent actuation can be corrected. The licensee has a sufficient number of sirens to allow this siren to be removed from service. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-08-11
51306 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-08-10 15:35 | 2015-08-10 19:49 | 2015-08-10 | INADVERTENT ACTIVATION OF A SINGLE EMERGENCY SIREN "On August 10, 2015, at approximately 1555 CDT, the licensee was notified that emergency siren S-07 in Sherburne County, MN had inadvertently activated from approximately 1525-1538 CDT. The cause of the activation is under investigation. The siren vendor (NELCOM) was also contacted and made the notification to the licensee. As a result, this issue is being reported under 10CFR50.72(b)(2)(xi) for notifications to other offsite government agencies as the licensee was notified by the Sherburne County Sherriff's Office. The source of the activation signal has not been determined. The vendor is investigating. The siren is no longer actuating. There was no impact to the health and safety of the public as a result of this event as the offsite response capabilities remain functional with a failure of only 1 out of 106 total sirens. The site is operating normally with no emergency present. "[The] NRC Resident Inspector has been notified." The licensee will notify the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-08-10
51305 | 0 | WEAVER CONSULTANTS GROUP |  |  |  |  | 2015-08-10 | 2015-08-10 16:46 | 2015-08-10 | DAMAGED TROXLER MOISTURE DENSITY GAUGE "After completing 17 moisture density gauge readings on the southern half of the West Slope of Clinton County landfill, the Troxler (Model: 3440, Serial # 39264) portable nuclear density gauge owned by [the licensee] was placed on the ground behind a Ford F150 pick up truck owned by [the licensee]. [The gauge operator] sat at the back of the truck reviewing the field sheets of moisture density readings and preparing for the next group of readings. When it was clear that additional blank forms were needed, [the gauge operator] went to the cab of the truck to look for the additional forms. No forms were available so the truck was started and backed up to go to the field office to retrieve the forms. "After backing and going forward a few feet, [the gauge operator] remembered the moisture density gauge behind the truck. The truck was backed up beside its original location and the damaged gauge was observed. [The gauge operator], got out of the truck to see the plastic casing of the gauge broken in several pieces. The source rod was still in the shielding but the guide rod was broken. "[The gauge operator] was the only person on that portion of the jobsite at the time of the incident and received no exposure from the source as it was still contained in the shielding. The closest other person to the area was more than a thousand feet away at the time of the incident. "The gauge and broken plastic housing was placed into its transportation box after confirmation of intact sources. The area of the incident was cordoned with orange paint for containment purposes. The licensee's radiation safety officer [RSO], was notified of the incident and the gauge was photographed and photos were sent to him. "The RSO mobilized to the site with a SE International radiation meter to survey the cordoned area of the incident as well to verify that sources were intact in the portable nuclear density gauge. Survey results indicated that both sources, Cs-137 and Am-241:Be were intact and undamaged." The gauge is a Model 3440 Troxler Moisture Density gauge, serial #39264, with Cs-137 8 mCi, serial #77-6741 and Am/Be 241 40 mCi sources, serial #78-4049. The licensee has temporarily stored the gauge in a secure location and will transport the gauge back to the company office, in Michigan, for repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-08-18
51304 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-08-10 | 2015-08-10 14:51 | 2015-08-10 | TEXAS AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECT The following information was received via email from the State of Texas: "On August 10, 2015, the licensee's radiation safety officer [RSO] reported to our Agency [State of Texas Department of State Health Services] that a source was not able to retract into a radiography camera [at a temporary job site in Houston]. The RSO responded to the job site and checked the equipment. The RSO found the drive cable had broken. The RSO replaced the crank out control mechanism and retracted the source. The new crank mechanism was checked and the source was easily extended and retracted as normal. The camera was placed back into service. The RSO will be providing a detailed report on the cause of the break. Camera specifics were QSA model: Delta 880, serial number: D8509 with source serial 17604G, model A424-9, Ir-192 at 44 curies. Updates to be provided in accordance with SA300." Texas Incident #: I-9331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-08-18
51303 | 0 | ATC-NUCLEAR |  |  |  |  | 2015-06-11 | 2015-08-10 13:50 | 2015-10-09 | PART 21 INTERIM REPORT - POTENTIAL DEFECT ON P/N 535-601 MOORE INDUSTRIES MILLIAMP MODULES The following information is a summary that was excerpted from a facsimile received from ATC-Nuclear: "The basic component which is the subject of this notification is identified as Moore Industries Milliamp Module with part number (P/N) 535-601 (alternate P/N: 535-601-SSTRV) which has been provided individually and/or contained within a STS 535 Single Loop Process Controller. "On December 22, 2014, ATC Nuclear received a 535 controller from Detroit Edison (DTE) with a failed Milliamp Module (P/N 535-601). The customer requested ATC Nuclear to perform a failure analysis to determine the cause of no output (0 Ma) on output 2 of the 535 controller. ATC Nuclear initiated a failure analysis in January 2015 that was broken down into several stages to determine the cause of the Milliamp Module failure. ATC Nuclear is continuing to evaluate the cause of the Milliamp Module failure and has preliminarily identified workmanship issues with a surface-mount fuse that is installed in the Milliamp Modules. ATC Nuclear has provided the results of the analysis to Moore Industries and Littelfuse to support or refute the workmanship concerns. "Preliminary information provided by Littelfuse on June 11, 2015, was sufficient evidence to identify the existence of a deviation potentially associated with a substantial safety hazard (i.e., discovery as defined in 10 CFR Part 21). This information was documented as part of CAR 15T-24. Evaluation of reportability in accordance with 10 CFR Part 21 was not able to be completed within the 60 day evaluation period. "The discovery date of the deviation requiring evaluation under 10 CFR Part 21 is June 11, 2015. "ATC Nuclear has preliminarily identified a total of 285 Milliamp Modules with P/N 535-601 that have been supplied to customers by ATC Nuclear since 2010. However, there is not sufficient evidence to establish that all Milliamp Modules supplied to customers have defective Littelfuse surface-mount fuses (P/N 0448.100MR) installed. ATC Nuclear will continue to work with Moore Industries and Littelfuse to define the population of Milliamp Modules that potentially have a defective surface-mount fuse installed. This information will become available once our 10 CFR Part 21 evaluation is completed. "ATC Nuclear is reviewing customer purchase orders for Milliamp Modules to identify the population of Milliamp Modules that potentially have a defective surface-mount fuse installed. Additionally, ATC Nuclear is working with Moore Industries to purge its stock of potentially defective fuses. Additional time is needed to evaluate the condition of new surface-mount fuses and it is expected that this evaluation will be completed no later than October 9, 2015. "Littelfuse identified a very low failure rate (< 0.001 %) in a preliminary report issued June 2015 spanning approximately an eighteen month period commencing January 2014. There were 356,250 fuses manufactured during this period. Littelfuse is conducting a more thorough review of this failure mechanism. There is no additional advice at this time." For additional information, contact the following; Ray Chalifoux Vice President QA, ATC-Nuclear 777 Emory Valley Road, Oak Ridge, TN 37830 (865) 384-0124 * * * UPDATE FROM RAY CHALIFOUX TO DONALD NORWOOD AT 1602 EDT ON 10/9/2015 * * * The following information is a synopsis of information received via facsimile: ATC Nuclear has concluded that the identified deviation could be considered a defect on the surface-mount fuses supplied by Littelfuse. However, ATC Nuclear determined that it does not have the capability to complete a 10 CFR Part 21 evaluation to determine if a substantial safety hazard exists. A total of 285 Milliamp Modules with P/N 535-601 have been supplied to customers by ATC Nuclear since 2010. However, there is not sufficient evidence to establish that all Milliamp Modules supplied to customers have defective Littelfuse surface-mount fuses installed. ATC Nuclear identified Milliamp Modules supplied in the January 2013 - June 18, 2015 timeframe as potentially having defective Littelfuse surface-mount fuses. Nuclear plants that received Milliamp Modules which potentially have a defective surface-mount fuse were as follows: LaSalle, Fermi 2, Limerick, and Clinton. ATC Nuclear has developed a Technical Bulletin to direct the purchasers and/or affected licensees for inspections to determined if the manufacturing defect could be present in their applications. Notified R1DO (Bickett), R3DO (Stone), and via E-mail Part 21 Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-08-10
51302 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2015-08-09 22:15 | 2015-08-10 00:23 | 2015-08-10 | AUTOMATIC REACTOR TRIP DURING TESTING "On August 9, 2015, during the performance of Reactor Protection System Logic Matrix Testing, a reactor trip occurred. All CEA's [control rods] fully inserted into the core. Decay Heat removal is from Main Feedwater and Steam Bypass to the Main Condenser. All equipment operated as expected. Currently maintaining pressurizer pressure at 2250 psia, temperature maintaining at 532 degrees F. "Unit 2 was unaffected and remains in Mode 1 at 100% power. "This event is reportable pursuant to 10CFR 50.72(b)(2)(iv)(B) for the Reactor Trip and 10CFR 50.72(b)(3)(iv)(A) for the Specified System Actuation." The plant is in its normal shutdown electrical lineup. No safety or relief valves lifted during this event. The cause of the trip is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-08-10
51301 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-08-09 16:27 | 2015-08-09 20:15 | 2015-08-09 | SALT SERVICE WATER SYSTEM DECLARED INOPERABLE "On Sunday, August 9, 2015 at 1627 [EDT], with the reactor at 90 percent core thermal power (CTP), the Pilgrim Nuclear Power Station (PNPS) entered a 24-hour shutdown Limiting Condition for Operation Action Statement (LCO-AS) for Salt Service Water (SSW) inlet temperature exceeding the Technical Specification (TS) limit in TS 3.5.B.4. The LCO-AS was subsequently exited at 1653 when the temperature of SSW trended to below the TS limit. "Under certain accident conditions, the SSW system is required to provide cooling water to various heat exchangers such as the Reactor Building Closed Cooling Water (RBCCW) and Turbine Building Closed Cooling Water (RBCCW) systems. When the inlet temperature to these supplied loads exceeds the 75 degrees F limit established in the TS, the SSW system is conservatively declared inoperable until the temperature trends below this value. This condition existed for approximately 1/2 hour. When the SSW system was declared operable, the LCO-AS was exited. "The SSW temperature is being closely monitored and trended on a continuous basis. "This event has no impact on the health and safety of the public. "The licensee has notified the NRC Senior Resident Inspector. "This notification is being made in accordance with 10 CFR 50.72 (b) (3) (v) (D) due to an event or condition that could have prevented fulfillment of a safety function." The licensee will be notifying the Commonwealth of Massachusetts Emergency Management Agency. The licensee returned the unit to 100 percent power at approximately 2000 EDT. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-08-09
51300 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2015-08-07 13:40 | 2015-08-07 19:58 | 2015-08-07 | DEGRADED CONDITION DUE TO PRESSURE BOUNDARY LEAKAGE ON VENT LINE WELDED JOINT "This notification is being provided in accordance with 10 CFR 50.72(b)(3)(ii)A, Degraded Condition. "At 1340 CDT on 8/7/15, on LaSalle Unit 2, a through-wall (welded joint) leak was identified on a 3/4 inch vent line off of the bonnet of the 2B33-F067B, 2B Reactor Recirculation Pump Discharge Valve. This condition qualifies as pressure boundary leakage, which requires entry into Technical Specification 3.4.5, Reactor Coolant System Operational Leakage, Required Action C, to be in Mode 4, Cold Shutdown, by 0140 on 8/9/15. This leakage is significantly less than 10 gpm [leak rate is 0.2 gpm] and therefore, does not meet the threshold for entry into the Emergency Action Plan. At the time of discovery, Unit 2 was in Mode 3 - Hot Shutdown, heading into Cold Shutdown for a planned maintenance outage." This event does not affect Unit 1. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-08-07
51299 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2015-08-05 | 2015-08-07 15:58 | 2015-08-11 | GEORGIA AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO OVEREXPOSURE The following information was provided by the State of Georgia via email: "The [Georgia] Radioactive Materials Program received a call on Aug 7, 2015 that a medical event occurred in the radiation oncology department at Wellstar Kennestone Hospital on August 5, 2015. The event was found out 2 days later when the physicist was reviewing the patient's records on Aug 7, 2015. "Patient was being treated for cervical cancer (T&O implant) using the HDR (Ir-192, 5 Ci) . The authorized user had prescribed a treatment plan and then changed it to a reduced dose by 1/3 for 3 fractions. The first 2 fractions the patient received the reduced dose. On the third fraction, the 1st plan was delivered. The total dose delivered exceed the prescribed dose by [greater than] 20 percent and the fractionated dose delivered differs from the prescribed dose by more than 50 percent. The authorized user determined no harm came to the patient. The authorized user will be informing the patient on August 7, 2015. "The dose delivered on the 3rd fraction was 900 cGy and for the T&O implant, the total dose received for all 3 fractions was 1500 cGy." * * * UPDATE AT 0808 EDT ON 8/11/2015 FROM TRAVIS CARTOSKI TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "First fraction delivered was 300 cGy Second faction delivered was 300 cGy Third fraction delivered was 900 cGy, should have been 300 cGy Total dosed received 1500 cGy "On August 4, 2015, the patient received the first fraction. The physicist confirmed with the AU [Authorized User] that the plan was 900 cGy , 3 fractions and began the treatment. The dwell time for each fraction for the first plan was 1128.4 sec. After realizing how much dose was being delivered to the patient, the AU ordered to stop the treatment 219 sec into the treatment. A new written directive was prepared for 300 cGy per fraction, 900 cGy total. The first fraction continued to be delivered with the second plan. The total volume treated with the first plan was subtracted out from the seconded plan. The first two fractions the patient received the correct amount (300 cGy). "On August 7, 2015, the patient was scheduled to receive her third fraction. When the patient's chart is pulled up on the computer console, both plans are displayed, the first plan and the second plan. The first plan auto defaults as the current plan being used. The physicist accidently used the initial plan (900 cGy/fraction) for the third fraction. It wasn't until August 7, 2015 when the physicist was reviewing the patients chart when she realized the first plan was delivered on the third fraction. The dwell time for each fraction should have been 350 sec. However, the dwell time for the third fraction was 1128 sec. "The authorized user determined no harm came to the patient. The authorized user will be informing the patient on August 8, 2015." Notified the R1DO (Powell) and NMSS Events Resource (via e-mail). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2015-08-17
51298 | 0 | SEQUOYAH |  |  |  |  | 2013-10-23 12:00 | 2015-08-07 15:48 | 2015-08-07 | PART 21 - DAMAGED SURVEILLANCE CAPSULES "In April 2015, during Sequoyah Nuclear Plant Unit 1 end of cycle 20 refueling outage, the Tennessee Valley Authority (TVA) identified that there was unanticipated damage to the 'S' and 'W' surveillance capsules that were located within the reactor pressure vessel. Inspections determined that the surveillance capsules were not contained within the intact designated baskets. TVA conducted an extensive foreign object search and recovery initiative to recover the specimen capsule contents prior to concluding the refueling outage. "During the October 2013 Sequoyah Unit 1 refueling outage, the Westinghouse Electric Company (WEC) relocated the above referenced surveillance capsules in accordance with Westinghouse procedure MRS-SPP-2970. The procedure specified the requirements for performing specimen capsule relocations. WEC created a deviation when an inadequate procedure referenced in the applicable purchase order, which did not ensure proper seating of the sample capsule, was used at Sequoyah Nuclear Plant Unit 1. "TVA considers the above condition to be reportable pursuant to 10 CFR 21.21 as a defect associated with a condition that, if uncorrected, could have created a substantial safety hazard." "The NRC Resident Inspector and the vendor were notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-08-07
51297 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-08-06 17:39 | 2015-08-06 20:53 | 2015-08-17 | TECHNICAL SUPPORT CENTER NON-FUNCTIONAL "Technical Support Center (TSC) Air Conditioning [AC] unit is out of service. Due to expected high temperatures in the upcoming days, there exists the potential for the TSC to become nonfunctional. This could result in a reduction in Emergency Plan Response Capability. The Alternate TSC is available for use in the event of an emergency and would be staffed and activated using existing EP (Emergency Preparedness) procedures and checklists." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM P.C. MOORE TO STEVEN VITTO ON 08/17/2015 AT 1010 [EDT] * * * "As of 0700 [CDT], 8/17/15, the TSC is fully functional, the HVAC system has been restored to 100 percent capacity. "NRC Resident Inspector has been notified." R4DO (HAGAR) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-08-06
51296 | 0 | CRANE NUCLEAR, INC |  |  |  |  | 2015-02-20 | 2015-08-06 20:00 | 2015-08-06 | PART 21 - CRANE NUCLEAR PRESSURE SEAL VALVE WITH RETAINING RINGS The following summary was excerpted from a facsimile received from Crane Nuclear: "This letter provides interim notification of Crane Nuclear's investigation into ASME Boiler and Pressure Vessel Section Ill Code design Pressure Seal Valve orders for yokes with integral hubs acting as retaining rings. "The information required for this notification is provided below: "Name and address of the individual or individuals informing the Commission: Jason Klein, Sustaining Engineering Manager and Rosalie Nava, Director Safety and Quality, Crane Nuclear, 860 Remington Blvd., Bolingbrook, IL 60440 "Identification of the basic component supplied for such facility or such activity within the United States which may fail to comply or contains a potential defect: Pressure Seal Valve orders may potentially have misclassified material and non-destructive examination requirements for Yokes with integral hub retaining ring designs. "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply: Crane Nuclear 'Classification of Valve Parts', Procedure 03-107, provides guidance for appropriate material and NDE requirements for processing valve and valve part orders. The procedure is based on the ASME Code Case N-62, which is ASME B&PV Section III, 2015 Edition, Non-Mandatory Appendix HH 'Rules for Valve Internal and External Items'. A yoke incorporating a threaded hub should be treated in the same manner as a threaded retaining ring requiring the material to be purchased Safety Related, ASME B&PV Section II, Part D materials, and required NDE (reference Category 3 valve items per N-62). However, yokes with integral hubs acting as retaining rings may have been processed to material requirements for a yoke per Procedure 03-107 and not a threaded retaining ring resulting in the incorrect material specification and non-destructive examination specified. "Crane Nuclear has completed the sales orders search of the ASME Section III Code Pressure Seal Valve designs with retaining rings from 1992 to present. We identified a total of 112 orders that required review. Of these orders, three orders were supplied with non-compliant retaining ring material for the valve assemblies. The three orders are as follows: "CNI SO# 24237-011, TVA, Browns Ferry, P.O. 00031943 - Quantity shipped = 1, Chapman, 8 inch, Figure L953, Class 900, ASME Class 2, 95 Ed., 96 Add., no N stamp "CNI SO# 39501-01, Georgia Power, Hatch, P.O. SNG10016537 - Quantity shipped = 3, Crane, 3 inch, Figure 776U, Class 600, ASME Class 3, 71 Ed., W71 Add. "CNI SO# 39745-01, Southern California Edison, San Onofre, P.O. 4500456451 - Quantity shipped = 1, Aloyco, 4 inch, Figure N5247PSB, Class 900, ASME Class 3, 71 Ed., S73 Add. "Crane Nuclear is currently investigating sales orders from 1968 to 1992. We require an additional 30-60 days to complete our review. "Corrective action being taken by Crane Nuclear is to review documentation of the supplied material on the affected orders to determine if the yokes can be recertified as currently supplied, amend Crane Nuclear Procedure 03-107 to add figures reflecting configurations and clarify classifications, and train Engineering personnel by August 24, 2015. "Crane Nuclear has notified the respective customers for the [three] orders that have been identified to date. Crane will notify the respective customers for any additional orders that are identified. "Should you have any questions regarding this matter, please contact Jason Klein, Sustaining Engineering Manager at (630) 226-4953 or Rosalie Nava, Director of Safety and Quality at (630) 226-4940." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-08-06
51295 | 0 | WATERFORD | 3 |  |  | [3] CE | 2015-08-06 12:00 | 2015-08-06 18:47 | 2015-08-06 | NON-FUNCTIONAL EMERGENCY SIRENS "At 1200 CDT, on August 6th, 2015, during the monthly test of Emergency Plan sirens in Saint Charles Parish (county), all sirens failed to actuate when required. There are a total 73 sirens of which 37 sirens are in Saint Charles Parish, which covers approximately 49 percent of the total population within the Waterford 3 10-mile emergency planning zone. The siren vendor is currently investigating to repair the issue. "Waterford 3 still maintains 100 percent backup notification capabilities. "The Saint John the Baptist Parish Sirens remain fully operational. "The Saint Charles Parish Emergency Manager has been notified. "This event did not result in any adverse impact to the health and safety of the public. The Waterford 3 and Saint Charles Parish Emergency Response Plans include back-up processes to provide warning to affected areas, if required, in the event of the loss of sirens." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-08-06
51294 | 0 | XCEL ENERGY |  |  |  |  | 2015-06-16 | 2015-08-06 17:47 | 2015-08-06 | PART 21 REPORT - ABB 50H INSTANTANEOUS OVER CURRENT PROTECTION RELAY FAILURE The following information was excerpted from a facsimile received from the Xcel Energy: "Pursuant to 10 CFR 21.21(d)(3)(i) Northern States Power Company, a Minnesota corporation, doing business as Xcel Energy, submits the attached initial notification of failure to comply or existence of a defect. "If there is any question or if additional information is needed, please contact Dr. Glenn A. Carlson, P.E., at (651) 267-1755. "Name and address of the individual or individuals informing the Commission: Scott M. Sharp, Site Operations Director, Prairie Island Nuclear Generating Plant (PINGP), Northern States Power Company - Minnesota, 1717 Wakonade Drive East, Welch, MN 55089 "Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: ABB Power T&D Company Inc., Relay, Overload, Overcurrent, 58/125VDC, Type: 50H, Cat.: 468S0475, 1.B.: 7.2.1.7-3 "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply: During bench testing to calibrate the relay, 125 VDC was applied to the relay with no noticeable effect. This was shop work on a spare relay and was not a plant installed piece of equipment. The relay protects against an instantaneous over current condition, which if undetected would cause substantial damage to the motor. This type of relay is installed in many locations; the failed relay was reserved to replace an existing relay protecting a Residual Heat Removal System pump motor. If the relay had been installed and required actuation during an accident, it would have resulted in major degradation in safety related equipment. "The ABB 50H relays are installed in ten locations at PINGP. All of the 50H relays are installed on the Unit 2 safety-related buses. The equipment protected is 21 Aux Feedwater Pump, 21 Component Cooling Pump, 21 Residual Heat Removal Pump, 21 Safety Injection Pump, 21 Containment Spray Pump, 22 Safety Injection Pump, 22 Residual Heat Removal Pump, 22 Component Cooling Pump, 22 Containment Spray Pump, and 121 Cooling Water Pump. The failed relay was reserved to replace an existing relay protecting a Residual Heat Removal pump motor. "PINGP Material Management has custody of the failed relay pending further investigation and notified the supplier of this notification by email on 8/6/2015. "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: Continue bench testing relays prior to installation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-08-06
51293 | 0 | ABB INC. (MEDIUM VOLTAGE SERVICE) |  |  |  |  | 2015-08-06 | 2015-08-06 14:23 | 2015-08-06 | PART 21 REPORT - NOTIFICATION OF DEVIATION REGARDING HK CIRCUIT BREAKER PIVOT PIN The following summary was excerpted from a facsimile received from ABB: "This letter provides notification of a failure to comply with specifications associated with a pivot pin, part number 193610B00, used in HK circuit breakers. This pin is used as the pivot point for the arcing contacts. Information is provided as specified in 10CFR21 paragraph 21.21(d)(4). "Notifying individual: Jay Lavrinc, Vice President & General Manager, ABB (Medium Voltage Service), 2300 Mechanicsville Road, Florence, SC 29501, phone number: (843) 413-4727 "Identification of the Subject component: ABB part number 193610B00 pivot pin. This pivot in is used on new legacy HK circuit breakers and during HK breaker refurbishments. The pivot pin is also available as a component item, as part of HK breaker refurbishment kits, and as part of upper terminal contact assemblies. "Nature of the deviation: During a breaker refurbishment at the ABB Florence facility, it was noted that a pivot pin cracked at the threads during installation. The peening operation performed on the threaded end of the pivot pin caused cracking due to brittle failure. Laboratory testing revealed that this particular pivot pin was made from an incorrect material. This pivot pin was purchased in April of 2015 and parts from this batch were used between 14 April and 28 May of 2015. There have been no field failures reported at this time. "Corrective actions include: a. Removed all remaining pivot pins from stock. (Action complete) b. Contact primary vendor to investigate cause and correct on future orders. (Action Complete) c. Added material verification to our Critical Characteristic cards for future orders. (Action Complete) d. Upgrade of ABB's spectrometer to analyze this silicon bronze material on all future shipments. (Action Complete) e. Obtained and tested, via qualified laboratory, a batch of pivot pins to supply to customers. (Action Complete) f. Notification of the potential existence of this deviation to affected customers (Action to be completed the week of 10 August 2015) "Affected Customers: Dominion (Surry Power Station); DTE Energy (Enrico Fermi Power Plant 2); Exelon Corporation (Limerick Generating Station); TVA (Sequoyah Nuclear Plant) "Recommendations: If the part was installed in a breaker or assembly and the threaded end did not show signs of failure or fracture at installation, it is not considered to be part of the suspect population. ABB recommends that these pivot pins be visually inspected at the next convenient maintenance cycle. If the pivot pin is in their inventory as a component item or in a kit and was shipped in the time interval of the suspect material, it should be returned to ABB for replacement." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-08-06
51292 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2015-08-05 | 2015-08-06 12:22 | 2015-08-06 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO ADMINISTRATION OF HIGHER DOSE THAN PRESCRIBED The following information was provided by the State of North Carolina via email: "Pitt County Memorial Hospital, Inc. dba Vidant Medical Center (License No. 074-1457-1) had a medical event occur yesterday afternoon [08/05/2015]. In brief, a patient with a low GFR [Glomerular Filtration Rate] was being treated for thyroid carcinoma. The original plan was to give the patient 50 mCi of I-131, which was received, assayed and ready for the Radiologist's approval. "The Radiologist on site was not the original Radiologist who planned the treatment for this patient. The physician onsite felt that with the low GFR (score to indicate kidney function) a lower dose, 35 mCi, would be prudent and a second order was placed with the radiopharmacy. "Around 1200 EDT, the dose was received, assayed and ready for administration. The Radiation Safety Representative identified the patient as required and discussed the home-going instructions with the patient prior to the administration. After the patient acknowledged the instructions, the Radiation Safety Representative went to the hot lab, confirmed the written directive, identified an assayed dose with the patient's name on it (of which there were two), failed to confirm the activity on the pig and slip, and administered the dose. "The error was not identified until the hot lab nuclear medicine technologist noted that the 35 mCi dose was still in the hot lab. The Radiologist and Radiation Safety Office was notified immediately. As of 1420 EDT, the referring physician was notified and patient was to be notified by the end of the day. At this time, it is not probable that there will be any health impact from the discrepancy. "A NC Health Physicist will be doing a reactive inspection before the end of this week. The radiation safety team is conducting an investigation and will be filing a formal report (15-day report) by August 20, 2015." NC NMED Report Identification number: NC150023 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-08-14
51291 | 0 | ALPHA-OMEGA SERVICES, INC |  |  |  |  | 2015-08-04 | 2015-08-05 19:02 | 2016-03-16 | PART 21 - POTENTIAL RADIOACTIVE MATERIAL TRANSPORT PACKAGING SHIELDING FAILING TO COMPLY WITH 10CFR71.47 AND/OR 10CFR71.51 The following information is a summary that was excerpted from a facsimile received from Alpha-Omega Services, Inc.: "Pursuant to 10CFR 21.21 (d)(3)(ii) Alpha-Omega Services, Inc. [AOS] is providing the USNRC with written notification of the identification of a potential failure to comply. The following information is required per 10CFR 21.21 (d)(4): "Name and Address of the individual or individuals informing the Commission. Troy Hedger, President, Alpha-Omega Services, Inc., 9156 Rose Street, Bellflower, CA 90706 "Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. AOS Document Number FM9054, Rev. H, Radioactive Material Transport Packaging System Safety Analysis Report for Model AOS-025, AOS-050, and AOS-100 Transport Packages (Revision H, December 30, 2012; Docket No. 71-9136) Model AOS-100A Package, USA/9316/B(U)-96 (Certificate of Compliance #9316) "Nature of the defect of failure to comply and the safety hazard which is created or could be created by such defect of failure to comply. There is a potential issue that shielding fails to comply with 10CFR 71.47 and/or 10CFR 71.51 (a)(2). This is not a 'defect' of the package, but rather an un-analyzed condition that could lead, if credible, to a safety hazard. DAHER-TLI Engineering Services notified AOS via telephone conversation on July 28, 2015 that there is a possible discrepancy in the original SAR shielding calculations originally performed. The potential discrepancy was discovered in conjunction with the independent preparation of a DAHER-TLI symposium paper that they are working on for presentation for future use of the AOS Cask family products. Specifically, DAHER-TLI observed that the AOS SAR does not analyze the radiation levels on the exterior of the package when a point source is located in a corner of the cask cavity. "In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. Currently, four (4) AOS-100A packages have been fabricated and three (3) were certified for use prior to August 4, 2015; one (1) is currently not in service. There are two (2) AOS-050 packages which are on hold for completion of fabrication activities. The following are the locations of the active units: AOS - Bellflower, CA, Serial no. AOS-100A-0001 (not currently in service); Elekta - Nordion Ottawa, Canada, Serial no: AOS-100A-0002; AOS - GE Vallecitos Sunol, CA, Serial no: AOS-100A-0003; Elekta - Nordion Ottawa, Canada, Serial no: AOS-100A-0004" * * * UPDATE FROM TROY HEDGER TO JOHN SHOEMAKER AT 0954 EDT ON 8/7/15 * * * The following update information is a summary that was excerpted from a facsimile received from Alpha-Omega Services, Inc.: "As of August 6, 2015, responsible personnel for the owner/users of the AOS Packages have been notified in writing, as follows: Elekta AB GE-Hitachi International Isotopes, Inc. Nordion Source Production and Equipment Co., Inc. "Based on our initial evaluation, AOS has initiated CAPA No. FM9016.1-082015-001 for providing corrective action relating to the above-identified subject. A 10 CFR Part 21 Applicability Form (re. FM9015.2-082015-001) has also been prepared and is currently under evaluation. The CAPA identifies the issue and begins the internal investigation process to determine the cause and to identify corrective action(s); this investigation is currently in progress. 1. AOS has initiated a Part 21 evaluation to determine applicability. 2. In parallel, AOS has contacted the NRC to inform the project manager of the concern; and to seek guidance/advice as to the direction that this evaluation needs to proceed. 3. Assuming that all of the activity is condensed in a point source in the corner of the cavity is a very conservative assumption. 4. In reality there may not be a problem due to self-shielding and distributed activity; i.e., it is very unlikely to have all of our activity in a single source and if we did, we would constrain it to the center of the cavity. "In parallel to this notification, AOS is notifying the owners and users of the AOS-100 package of this potential failure to comply." For additional information, contact the following; Troy Hedger, President Alpha-Omega Services, Inc. 9156 Rose Street Bellflower, CA 90706 Notified R4DO (Azua) and Part 21 Materials Group via email. * * * UPDATE FROM TROY HEDGER (VIA FAX) TO HOWIE CROUCH AT 1315 EDT ON 3/16/16 * * * The analysis and corrective actions stated in previous updates have been completed therefore the vendor considers this Part 21 notification completed. Notified R4DO (Warnick) and Part 21 Materials group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-08-05
51290 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-08-05 15:38 | 2015-08-05 18:51 | 2015-08-05 | AUTOMATIC REACTOR TRIP ON LOW REACTOR COOLANT FLOW "This 4-hour and 8-hour notification is being made to report that Salem Unit 2 had an unplanned automatic reactor trip. The trip occurred because the 2H 4kV infeed breaker tripped on over current protection which deenergized the 2H 4kV group bus resulting in a reactor trip on reactor coolant flow due to the loss of the 21 reactor coolant pump [RCP]. The 21 RCP remains unavailable. The cause of the over current protection trip on the 2H 4kV infeed breaker is unknown at this time. "All control rods inserted on the reactor trip. All ECCS [emergency core cooling systems] and ESF [engineered safety feature] systems functioned as expected. The auxiliary feed pumps started as expected. "Salem Unit 2 is currently in Mode 3. Reactor coolant system pressure is at 2235 psig and temperature is 547 degrees Fahrenheit with decay heat removal via the main steam dumps and auxiliary feedwater systems. Unit 2 has no active technical specification action statements in effect requiring a lower mode of operation due to the transient. "The 22 auxiliary building supply fan was tagged for maintenance prior to this event and has no adverse impact of the post trip plant response or stabilization. There was no major secondary equipment tagged for maintenance prior to the event. There were no personnel injuries as a result of this event. "There is no physical evidence of damage to the 2H 4kV bus based on visual observations and thermography." Normal offsite power is available to the site. There is no effect on Unit 1. The licensee has notified the NRC Resident Inspector and will notify the Lower Alloways Creek Township Police Department. | 0 | 0 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-08-05
51289 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2015-08-05 12:52 | 2015-08-05 16:22 | 2015-08-05 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "Nine Mile Point Unit 1 (NMP1) experienced a momentary loss of Secondary Containment due to both Reactor Building (RB) airlock doors being opened at the same time. "At 1252 [EDT] on 08/05/15, both RB airlock doors were opened simultaneously for less than 5 seconds. This resulted in Secondary Containment being declared inoperable (TS 3.4.3). Secondary Containment was restored to operable when the doors were closed. "The event is reportable in accordance with 10 CFR 50.72(b)(3)(v)(c), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the NRC Resident Inspector has been notified." The licensee also notified the State of New York Public Service Commission. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-08-05
51288 | 0 | ADVANCE TESTING COMPANY, INC |  |  |  |  | 2015-08-05 | 2015-08-05 10:02 | 2015-08-07 | DAMAGED PORTABLE MOISTURE DENSITY GAUGE The licensee reported that a portable moisture density gauge was damaged, by a dump truck, during a road paving project in Glastonbury, CT. The gauge case and keypad were damaged however, the sources are in the stored/safe position. There is no indication of leakage and no radiation exposures have occurred. The licensee has stored the gauge in their secure location pending further evaluation. The gauge is an Instrotek Model 3500 gauge containing 11mCi Cs-137 and 44 mCi Am/Be sources. * * * UPDATE PROVIDED BY MARK CLARK TO JEFF ROTTON AT 1258 EDT ON 08/07/2015 * * * Licensee called to correct initial report. The damaged gauge was actually a Troxler 3440, Serial number 18428 and not an Instrotek model 3500. Reported activity of sources remains the same. Notified R1DO (Burritt) and NMSS Events Notification Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | NY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-08-13
51287 | 0 | SANFORD HEALTH |  |  |  |  | 2015-07-30 12:00 | 2015-08-04 18:09 | 2015-08-04 | MEDICAL EVENT RESULTING FROM ACTUAL TREATMENT DOSE 30 PERCENT GREATER THAN PRESCRIBED On 7/31/2015, a patient was undergoing a single treatment for liver cancer using Y-90 microspheres (SIR-Spheres) with a prescribed dose from the physicians written directive of 29.43 milliCi. On 8/4/2015, it was discovered that the patient actually received 38.2 milliCi dose due a calculation error based on the physician's initial written directive when the physician had decided on a final dose reduction prior to treatment. The physician has been notified and believes that there will be no adverse effects to the patient. The patient will be notified on 8/5/2015. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-08-12
51286 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2013-07-20 | 2015-08-04 14:06 | 2015-08-04 | CALIFORNIA AGREEMENT STATE REPORT - HISTORICAL MEDICAL EVENTS DISCOVERED DURING STATE INVESTIGATION The following information was provided by the State of California via email: "RHB [ California Radiation Heath Branch] personnel noted irregularities in the way brachytherapy was being performed by an authorized user and investigated all facilities where he is authorized to perform brachytherapy. "On August 3, 2015, after reviewing files and consulting with the RSO of the facility, it was determined that there had been two medical events that had gone unreported. Both events were prostate Pd-103 implants performed in 2013 and 2014. One treatment resulted in a dose of only 37.6 percent of the target dose to the prostate (139.5 mCi Pd-103) and the second resulted in a dose of 66.9 percent of the target dose to the prostate (189.1 mCi Pd-103). The licensee will submit a follow up report within 15 days." CA 5010 (Date Notified): 072015 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-08-12
51285 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2015-06-05 | 2015-08-04 10:29 | 2015-08-04 | PART 21 REPORT - FERRAZ SHAWMUT/MERSEN FUSES P/N: AJT25 AND AJT60 The following information was excerpted from the email provided by the reporting organization: "On April 2015, United Controls International (UCI) performed dedication testing on time delay fuses AJT25 and AJT60 for First Energy - Perry Nuclear Power Plant under purchase orders 45469886 and 45469450, respectively. The subject fuses were being tested per United Controls Standard dedication testing which excludes seismic and environmental testing requirements. Both fuses, AJT25 and AJT60 opened during their current clearing tests at times that are within their respective clearing time tolerance ranges but their Smartspot labels did not change color, as required, to indicate the fuses cleared. "For fuse AJT25, eight fuses have been tested, including one (1) fuse from the first lot which comprises 30 fuses (with manufacture date 09/15 [9th week of 2015]) and seven (7) fuses from the second lot which comprises 32 fuses (with manufacture date 10/15). Five (5) fuses were tested for current clearing at 135% of the fuse rated current, two (2) fuses were tested for current clearing at 200% of the fuse rated current and one (1) fuse was tested for current clearing at 500% of the fuse rated current. "For fuse AJT60 with manufacture date 06/15, only one (1) fuse was tested from the received lot of fuses which comprises 24 fuses for current clearing time at 135% of the fuse rated current. Further testing of the AJT60 fuses was not performed since a trend was already observed in regard to the fuses AJT25 failure. "UCI has returned all received fuses in the three (3) received lots. Mersen [Ferraz/Shawmut/Mersen] has then performed evaluation on the 30 AJT25 fuses with manufacture date of 9/15 (9th week of 2015), confirmed that the seven (7) fuses that UCI has tested were open and conducted testing on six (6) among the remaining 23 fuses. Testing by Mersen revealed that only two out of the six fuses had their Smartspot indicator that went off to indicate that the fuses cleared. Upon further examination by Mersen; it is believed that over tightening of the crimping jars during installation and crimping of the ferrule endcaps is the cause of the Smartspot indicator's malfunction. "The fuses are Ferraz Shawmut/Mersen part numbers AJT25 and AJT60. UCI recommends the purchaser to include a requirement for suppliers to provide fuse with manufacture date after 6/30/15 where the manufacturer has performed corrective action to prevent this issue from recurring." Point of Contact: Divya Paidy, Engineering Manager, dpaidy@unitedcontrols.com, (770) 496-1406, ext. 106, | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-08-04
51284 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-08-03 | 2015-08-03 17:35 | 2015-08-03 | TEXAS AGREEMENT STATE REPORT - DAMAGED HUMBOLDT MOISTURE DENSITY GAUGE The following information was received from the State of Texas via email: "On August 3, 2015, the licensee reported to the Agency [Texas Department of State Health Services] that one of its technicians had run over and damaged a Humboldt 5001 EZ moisture/density gauge at a temporary job site in Belton, Texas. The gauge contained a 10 millicurie cesium-137 source and a 40 millicurie americium-241/beryllium source. The technician had started the test and the cesium source was extended four inches into the ground. The technician decided to move his pickup and while doing so he backed over the gauge and then pulled forward over it again. The source rod handle broke completely off of the gauge. A boundary around the gauge was marked and the licensee's radiation safety officer called a licensed service company. The service company responded and reported that the source was inside the gauge and not down in the hole, that it had apparently been pulled back into the gauge when it was run over. The service technician performed surveys and found no contamination. No member of the public received any exposure as a result of this event. No elevated exposures are anticipated for the technicians. An investigation into this event is ongoing. More information will be provided as it is obtain in accordance with SA-300." Texas Incident #: I-9329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-08-11
51283 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2015-08-01 17:55 | 2015-08-01 20:09 | 2015-08-02 | ALERT DECLARED DUE TO AN URANIUM HEXAFLUORIDE (UF6) RELEASE At 1755 CDT on 08/01/15, Honeywell declared an ALERT and activated their Emergency Response Team (ERT) based on an on-going UF6 release. The source of the leak is from a tell-tale valve installed during maintenance activities for Condenser #4 in the Feed Materials Building (FMB) 6th floor. The licensee employed a mitigating strategy using CO2 inside the FMB and spray towers external to the FMB. A Protective Action Recommendation (PAR) order was issued for local residents to shelter in-place although there was no indication of an offsite release. At 2035 CDT the licensee reported that the leak was isolated by installing a pipe plug into the threaded tell-tale line. The PAR was lifted at 1948 CDT. There are no worker injuries with all personnel accounted for. The licensee plans to issue a press release. Notified other FEDS (DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and FDA EOC, FEMA NWC and NuclearSSA via email) * * * UPDATE AT 2240 EDT ON 08/01/15 FROM MARK WOLF TO REGION 2 INCIDENT RESPONSE CENTER * * * At 2032 CDT on 08/01/15, the ALERT was downgraded to a Plant Emergency based on mitigation status and visual observation of the affected area. * * * UPDATE AT 0032 EDT ON 08/02/15 FROM MARK WOLF TO REGION 2 INCIDENT RESPONSE CENTER * * * The licensee will be remaining in the plant emergency mode while monitoring the vessel under vacuum conditions. The decision to replace the flange will be made by the licensee in the morning following monitoring of the vacuum conditions. Notified the R2DO (Hopper). Notified other FEDS (DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, and FDA EOC, FEMA NWC and NuclearSSA via email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | IL | FUE |  | 40.35(f) |  |  |  | 0 | 2015-08-01
51282 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-08-01 12:05 | 2015-08-01 15:28 | 2015-08-01 | INVALID SEISMIC EVENT ALARM "At 1205 CDT on August 01, 2015, the station's Seismic Instrumentation generated a seismic event alarm that was determined to be invalid, based upon no seismic activity being felt on site and no activity detected in the area by either the National Earthquake Information Center or nearby nuclear plants. The instrumentation that actuated, recorded a value of 0.07 g on a single axis of one instrument, which is greater than the 0.02 g threshold value in the Emergency Action Level in the station's emergency procedures; however, no other instrument channel or axis indicated a valid event exceeding the 0.02 g threshold. Since the event alarm was determined to be invalid as described above, no EAL thresholds were met. "The seismic instrumentation was declared non-functional since it would not generate a seismic event alarm during an actual event until the invalid event was reset. The alarm was reset through the alarm reset process. The seismic instrumentation alarm capability was restored and returned to service at 1250 CDT. "This resulted in a Loss of Emergency Assessment Capability while the Seismic Instrumentation was out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." The licensee performed a channel calibration in response to the previous Seismic Instrumentation malfunction (see EN # 51263) and plans to perform more extensive troubleshooting in response to the latest malfunction. The licensee will notify the State of Illinois plant inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-08-01
51281 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-07-31 | 2015-07-31 17:02 | 2015-07-31 | AGREEMENT STATE REPORT - INABILITY TO RETRACT A RADIOGRAPHY SOURCE The following information was received from the Commonwealth of Pennsylvania: "On July 31, 2015, the licensee reported a disconnected radiography source at a work site in New Milford Township, Pennsylvania. A secure and restricted area around the source has been established, limiting potential public radiation exposure to below the 2 millirem in any one hour 'unrestricted area' limit. "Source: lridium-192 (lr-192) "Activity: 68 curies "The license has informed the Department [PA DEP Bureau of Radiation Protection] they will keep the source secure and shielded until the radiography device manufacturer arrives. They are expected be onsite at approximately 0300 [EDT] on August 1st. A full report is expected within 15 days. A Southeast Regional Office Radiation Protection staff radiological health physicist has already been onsite to perform a reactive inspection and validate the licensee's actions. More information will be provided as received. "Event Report ID No.: PA150021" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-08-10
51280 | 0 | NAMCO CONTROLS |  |  |  |  | 2015-05-19 | 2015-07-31 14:27 | 2015-07-31 | PART 21 REPORT INVOLVING LIMIT SWITCHES EA180 AND EA170 MANUFACTURED IN A SPECIFIC DATE RANGE The following information is an excerpt from a Namco Controls fax: "Subject: Notification of Product Anomaly Namco Controls Division of Dynapar Corp EA180 & EA170 Limit Switches Manufactured March 25th 2014 through December 30th 2014. "Dear Sir(s) / Madam(s), "The purpose of this letter is to notify you of our resolution for the subject anomaly that was brought to our attention by the Nebraska Public Power District, Cooper Nuclear Station in Brownville, NE via our rep network (Mr. Curt Duphill) on May 19th 2015. On May 30th our senior engineer, Mr. Troy Kloss, visited the plant site during a plant shutdown to investigate the issue and determined that a Part 21 investigation was warranted. Dynapar's Namco Controls business sent out an early indication notice to customers as part of the investigation on 6/3/15 which included switches of date codes 1214 and 1314 (week-year). As a result of this initial notice, a second reported potential anomaly was identified by Salem Nuclear Power in Hancocks Bridge, NJ. However these switches at Salem were replaced previously and no root cause analysis was performed prior to the switches being discarded. "Because of this anomaly the nuclear limit switch may not reliably state the condition of the device (in this case a main steam isolation valve) that the switch is measuring and could be a potential safety hazard depending on the nuclear power plant control logic. "As a result of our internal investigation, we isolated the switch performance degradation to a compression spring in the limit switch assembly. We have validated lot control traceability of the compression spring in question, which contained 1100 suspect springs, to shipments within the subject date range and have determined 417 Namco limit switches were shipped to US customers with this potential anomaly. We are notifying the affected customers- see included list. In addition, Namco Controls has changed our inspection criteria as of 07/31/2015 for this item in order to prevent future occurrences. "At this time, we have generated a Technical Bulletin (TB1501) summarizing the conclusions and recommendations. We will notify all customers, both domestic and foreign, by August 7th 2015. "If you have any questions or concerns, please direct them to Quincy Hill, Quality Manager at qhill@dancon.com. "Thank you. "Kevin Sutherby "Vice President & General Manager "Namco Controls Division of Dynapar Corporation "ksutherby@dancon.com "910.862.5411 (office) "2100 West Broad Street, Elizabethtown, NC 28337" The part numbers impacted are: EA170-11302,-12302,-21302,-31302,-32302,-41302,-42302-,51302, and EA180-11302,-11307,-11309,-11402,-12302,-12307,-12309,-12402,-21302,-21309,-21402,-22302,-22309,-31302,-31309,-31402,-32302,-32309,-32402 at the following facilities: Farley Nuclear Plant, Callaway Energy Center, Palo Verde Nuclear Generation Station, Fermi 2 Nuclear Power Plant, Millstone Nuclear Power Station, North Anna Power Station, Catawba Nuclear Station, McGuire Nuclear Station, Robinson Nuclear Plant, Harris Nuclear Plant, Columbia Generation Station , Arkansas Nuclear One, River Bend Nuclear Station, Waterford 3 Nuclear, Clinton Nuclear Station, LaSalle County Generating Station, Braidwood Generating Station, Limerick Generating Station, Byron Generating Station, Quad Cities Generating Station, Perry Nuclear Plant, Plant Hatch, Cook Nuclear Plant, Cooper Nuclear Station, Seabrook Station, Duane Arnold Energy Center, Salem/Hope Creek Nuclear Generation Station, South Texas Nuclear Project Electric Generating Station, Watts Bar Nuclear Plant, Wolf Creek Nuclear Operating Corporation, Prairie Island Nuclear. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-07-31
51279 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-07-31 10:42 | 2015-07-31 14:11 | 2015-07-31 | FITNESS FOR DUTY REPORT INVOLVING A SUPERVISOR "A supervisory employee failed a pre-access Fitness-for-Duty (FFD) test required for reinstatement of site access. The employee did not have unescorted access to the site at the time of the test. The employee has been assigned a mandated EAP referral, and his site access has been revoked pending review by the medical review officer. "The NRC Resident Inspector has been informed. "Reportable per 10 CFR 26.719 and Entergy Procedure EN-NS-102, Fitness for Duty Program." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.719 |  |  |  | 0 | 2015-07-31
51278 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2015-07-30 | 2015-07-30 18:18 | 2015-07-30 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the State of Washington via email: "A Troxler 3440 gauge used by Kleinfelder, Inc., license number WN-I0475, fell from the back of a truck onto the middle of the runway at Seatac airport. The only sign of damage was to the circuit board. The source rod was undamaged and still works. Reporting requirement WAC 246-221-250(2)(f)(ii) - Damage affects the integrity of the radioactive material or its container." The gauge contains 10 mCi of Cs-137 and 50 mCi of Am-241/Be. The damage is attributed to a failure to block and brace equipment. Washington Incident Number WA-15-026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2015-08-07
51277 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2015-07-29 09:00 | 2015-07-30 17:26 | 2015-09-04 | AGREEMENT STATE REPORT - RADIOACTIVE SHIPMENT DELIVERED TO WRONG ADDRESS The following information was received from the State of Arkansas via email: "The Arkansas Radiation Control Program is making this immediate notification under 10 CFR 20.2201(a)(1)(i) and Arkansas Regulations RH-1501.c.1.A. "On July 30, 2015, at 1349 [CDT], NEA Baptist Memorial Hospital, in Jonesboro, Arkansas Radioactive Material License Number ARK-0504-02120, reported that an Iridium-192 sealed source, approximately 10 Curies had been delivered to the wrong address. The source was in an unsecured location for approximately 23.5 hours. The source had been delivered by [common carrier] at 0900 [CDT] on July 29, 2015, to a clinic of a similar name as the hospital but at the wrong address. The source was delivered to the therapy department through the Hospital's receiving department this morning at 0830 [CDT]. "This concludes the available information at this time. The Licensee is investigating this event. The Arkansas Radiation Control Program continues to investigate this event under Arkansas Event Number AR-2015-010." * * * UPDATE PROVIDED BY STEVE MACK TO JEFF ROTTON AT 1458 ON 09/04/2015 * * * The following information was provided by the State of Arkansas via email: "The Program [Arkansas Radiation Control Program] received a written report from the licensee on September 3, 2015, outlining actions taken to inform staff should a package containing radioactive material be delivered to the wrong area. These actions included: reviewing procedures, photos of packages containing radioactive material and retraining on the receipt procedures. The Department [Arkansas Department of Health] considers this event to be closed." Notified R4DO (Warnick) and NMSS Events Notifications group via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-08-07
51276 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-07-30 08:30 | 2015-07-30 09:48 | 2015-07-30 | AGREEMENT STATE REPORT - RADIOGRAPHY TRUCK (WITH CAMERA) STOLEN AND RECOVERED The following report was received from the State of Oklahoma via e-mail: "At about 0830 [CDT] American Piping Inspection, Inc., [license] OK-27438-02 (Tulsa, OK) reported to [the State of Oklahoma] that one of their radiography trucks was stolen and that there was a radiography camera on board. The truck has GPS and the company had tracked the truck to North Garnett Street in Tulsa, OK and the police were enroute. [At approximately 0930 CDT], "the radiography camera was recovered by the company [American Piping Inspection, Inc]." The thieves were in the truck when the police arrived. The thieves departed the scene on foot and were not apprehended. There was no apparent damage to the truck or the camera. Device Model Number: Spec. G-60, containing 100 curies of IR-192. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-08-07
51275 | 0 | CHEVRON USA, INC |  |  |  |  | 2015-07-21 | 2015-07-29 20:14 | 2015-09-02 | FIXED GAUGE SHUTTER STUCK IN THE OPEN POSITION A fixed gauge shutter was determined to be stuck in the open position on 7/21/15. The device manufacturer was called and arrived on location on 7/24/15, and determined that the device "dip tube" is bent and the device will have to be removed for repair. The device is a Tracerco Profiler Series Fixed Density Profiler (Serial # 101020) with either 49 or 62 30mCi Am-241 sources (1470 mCi or 1860 mCi Am-241 aggregate). The device is located inside a process vessel on an offshore platform. Radiation measurements taken outside the process vessel indicate no detectable radiation. The have been no radiation exposures. The manufacturer will remove the device and repair it. * * * UPDATE FROM RUSTY GRIMSLEY TO DANIEL MILLS AT 1852 EDT ON 7/30/15 * * * The following was received from the licensee via email: "In accordance with 10 CFR 30.50(b)(2), Chevron submitted a verbal notification to the NRC Operations Center at 2014 hrs. EDT on July 29, 2015. We [Chevron USA, Inc.] are submitting this written report to verify the information conveyed in the verbal report. "Test separator MBD1010 on Chevron's Jack/St. Malo oil and gas production platform is equipped with a Tracerco Profiler Series Model T-240 fixed density profiler, serial number T240-FM-1-324. On July 21, 2015, it was discovered that this profiler's shutter was in the open position and would not close. Tracerco, the manufacturer of the device, was immediately notified. Tracerco inspected the profiler on July 24, 2015 and confirmed that the shutter would not close. Tracerco's initial investigation indicated that the density profiler source and detector tubes were bent, prohibiting the movement of the shutter. "The Jack/St. Malo platform is located in Walker Ridge Block 718, OCS-G 32703, approximately 190 miles offshore Louisiana in the Outer Continental Shelf. The test separator is located on the Production Module lower deck. The shielded source housing and shutter mechanism are located on the Production Module mezzanine deck, which sits immediately above the separator. "The profiler source tube contains 62 Americium 241 sources, 30 milliCuries per source, for a total of 1,860 milliCuries. "Tracerco, the manufacturer of the profiler, is onsite and is developing a plan for disassembly and removal of the device from the separator using appropriate shielding and other protective measures to minimize potential exposures. If entry into the separator with the sources still in place is deemed necessary, Tracerco will implement appropriate radiation safety measures to minimize exposures. The device and sources will be stored in appropriate containers during shipment to Tracerco; turnover of the sources to Tracerco will be documented. As any repairs to the device or vessel entry would not constitute routine maintenance, Chevron personnel will not be involved in repairing or removing the profiler. "There has been no exposure of platform personnel. Although the shutter remains in the open position, no one has entered the separator, and no radiation is detectable at the exterior of the separator. The separator is coated in insulation, covering the manways that provide access to the interior of the separator. "Tracerco has been working on the Production Module mezzanine deck and has partially removed the profiler from the separator to assess its condition. Tracerco has established a barricade around the work area to prevent unauthorized access. Their monitoring indicates no exposures beyond five feet from the sources. Tracerco reports that the radiation detected appears to be lower than expected for fully unshielded sources. Tracerco has conducted wipe tests and has found no leakage from the sources." Notified R4DO (Warnick) and NMSS Events Notification via email. * * * UPDATE AT 1641 EDT ON 9/2/2015 FROM J. GRIMSLEY TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "The incident investigation indicated a deflector plate inside the test separator became disconnected and struck the profiler. Under the supervision of Tracerco, entry was made into the vessel and the damaged profiler removed and returned to Tracerco's Pasadena, Texas facility for repairs. The deflector plate was reinstalled in the separator per manufacturer's specifications. The profiler was not re-installed. "Tracerco reported the results of the wipe test taken at the time of the removal of the profiler showed no contamination." Notified the R4DO (Warnick) and NMSS Events Resource (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-08-06
51274 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2015-07-28 13:58 | 2015-07-28 18:55 | 2015-08-12 | DISCOVERED ONE INCH DIAMETER HOLE BETWEEN REACTOR BUILDING AND AUXILIARY BUILDING "At 1358 [EDT] on July 28, 2015, a 1 inch diameter hole was discovered in the secondary containment wall, between the Reactor Building and the Auxiliary Building, causing the Secondary Containment to become inoperable under Technical Specification 3.6.5.1. Reactor Building pressure was maintained at a negative pressure as required by Technical Specification 3.6.5.1 with the Reactor Building ventilation system in service before and after discovery of the hole. In addition, the Filtration, Recirculation and Ventilation system remained fully operable and remained in standby. The hole was sealed at 1600 and technical specification 3.6.5.1 was exited. Plant operation was not impacted by the event and was operating at 100% power. No personnel injuries resulted from this event." The hole was discovered by plant personnel that were walking past the wall. Due to the discovery of the hole, the plant is performing an extent of condition inspection. The licensee notified the NRC Resident Inspector and the Lower Alloways Creek Dispatch. * * * * RETRACTION FROM MARIAZ DAVIS TO STEVEN VITTO AT 1232 EDT ON 08/ 12/15 * * * * "This event is being retracted. "Hope Creek Generating Station Unit 1, is retracting the 8-hour non-emergency notification (EN# 51274) made on July 28, 2015, at 1855 EDT. The notification on July 28, 2015, reported that secondary containment was declared inoperable when a 1 inch hole was discovered in the secondary containment wall, between the Reactor Building and the Auxiliary Building. Secondary containment was declared inoperable based on the initial interpretation of the definition of secondary containment. The hole did not impact the ability to maintain the Tech Spec required negative pressure. Subsequent evaluation determined that secondary containment was always operable. Based on the engineering evaluation, the condition reported in EN# 51274 did not result in an inoperability of the secondary containment. Therefore, there is no reportable condition and this event report is being retracted. "The NRC Resident Inspector has been briefed on the evaluation results and informed of this retraction." The licensee also notified the Lower Alloways Creek Dispatch. Notified R1DO (Powell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-07-28
51273 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2015-07-22 | 2015-07-28 16:59 | 2015-07-28 | AGREEMENT STATE REPORT - FIXED GAUGE WITH SHUTTER STUCK CLOSED The following report was received from the State of North Carolina (NC) via email: The licensee was performing routine maintenance and leak testing checks on a Berthold fixed nuclear density gauge when they discovered its shutter was stuck in the closed position. This maintenance record was dated for 7/22/2015 and listed that the device needed cleaning, showed signs of mild to moderate corrosion, the shutter failed to open, and replacement was necessary. The closed shutter was verified by a survey meter and its detector response. The [North Carolina] State was notified the following week, on 7/27/2015. The gauge manufacturer, Berthold, had already been contracted to dispose of the source and device. No exposures or radiation safety concerns have resulted from this failed shutter at this time and none are expected. The Berthold Fixed Nuclear Gauge is serial #6625, model# LB7440 with a Berthold source serial #1329, model #D7547, 20 mCi Cs-137 source (as of 5/98). The last leak test performed March 28, 2013, that passed according to Thermofisher (3 year leak test requirement). Berthold will perform another leak test before transporting off site. The cause of the stuck shutter is dirt and corrosion products that appear to be the leading cause of the shutter failing in the closed position. NC will follow up with the licensee to determine if dirt accumulation and corrosion occurred by operating in environmental conditions outside of the manufacturer's intentions. NC State report: NC NMED #150022. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-08-05
51272 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-07-27 17:30 | 2015-07-28 01:08 | 2015-07-28 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "On July 27, 2015, at 1730 hours [CDT], the Control Room Emergency Ventilation (CREV) system was declared inoperable due to the 'B' Air Filtration Unit (AFU) Booster Fan discharge damper stuck open in mid-position. In this condition, the CREV system cannot be guaranteed to achieve required design flow rate. As a result, Technical Specification 3.7.4, Condition A, was entered. "The CREV system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions as well as protection of the operators from a high dose environment assumed during a design basis accident. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV system could impact the plant's ability to mitigate the consequences of an accident as stated in Chapter 6 of the UFSAR [Updated Final Safety Analysis Report]. This event is also reportable under 10 CFR 50.72(b)(3)(xiii) since this condition also impacts the control room as an Emergency Response Facility. "The NRC Resident Inspector has been notified." Both units are in a seven day technical specification for troubleshooting and repairs. If the control room became uninhabitable, procedure "Complete Loss of Control Room HVAC" would be entered. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(xiii) |  |  | 0 | 2015-07-28
51271 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-07-27 17:00 | 2015-07-27 18:27 | 2015-07-27 | SECURITY EVENT INVOLVING UNACCOUNTED FOR EQUIPMENT "This report is being made in accordance with 10CFR 73.71(b)(l). Security notified the Shift Manager of unaccounted for security related equipment within the protected area. "The Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-07-27
51270 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2015-07-22 13:30 | 2015-07-27 18:01 | 2015-07-27 | DEGRADED CONDITION DUE TO REACTOR COOLANT SYSTEM LEAK "On July 8, 2015, Fort Calhoun Station was in Mode 1, 100% when personnel identified an increase in the Reactor Coolant System unidentified leakage rate. As a result, personnel performed a containment entry and identified the source coming from the Reactor Coolant Pump 3A seal area. Based on this observation, a monitoring plan was established and on July 20, 2015 the leak rate exceeded the pre-establish leak limit and operators manually shutdown the reactor. On July 22, 2015, at approximately 1330 CDT, personnel identified the source of the seal leak as a crack on the middle seal inlet line, which is part of the reactor coolant system boundary. Maintenance personnel have since repaired the seal line and it has passed post-maintenance testing. "The 8-hour verbal report is being made post event due to additional review of the leakage condition identifying the leakage constituted a degraded condition due to be material defects in the primary coolant system." The leak rate was between 1 and 2 gpm. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-07-27
51269 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-07-27 11:18 | 2015-07-27 17:50 | 2015-07-27 | LOSS OF SECONDARY CONTAINMENT DUE TO OPENING SINGLE DOOR WITHOUT PROPER AUTHORIZATION "On July 27, 2015 at 1118 [EDT], Secondary Containment became inoperable requiring a Technical Specification 3.6.4.1 entry for failure to meet SR [Surveillance Requirement] 3.6.4.1.1 on Unit 1 and Unit 2. "The inoperability was caused by Zone 2 differential pressure lowering to less than 0.25 inches WC when a secondary containment door was opened without appropriate authorization. "The secondary containment door was closed at 1149 and secondary containment D/P verified greater than 0.25 inches WC at 1205. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev. 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The loss of secondary containment occurred due to multiple openings of Door 104R which provides access to area of the building that provides alternate access to the building roof, but this door is not the normal access to the building roof The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-07-27
51268 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2015-07-27 09:56 | 2015-07-27 16:31 | 2015-07-27 | VALID ACTUATION OF UNIT 2 EMERGENCY FEEDWATER SYSTEM DURING STARTUP "At approximately 0956 EDT on July 27, 2015, Oconee Nuclear Station Unit 2 experienced a valid actuation of the Emergency Feedwater System [EFW]. At the time of the event, Unit 2 was in Mode 1 at approximately 17% power and increasing with preparations in progress for placing the main turbine on line during a unit startup. The [EFW] actuation was due to a low level on the 2B steam generator, which resulted from failure of 2B Main Feedwater Block Valve 2FDW-40 to automatically open upon demand. All systems operated as expected with no problems observed. Unit 2 is currently stable at approximately 16% power while troubleshooting valve 2FDW-40 [and the 2B Steam Generator level stable at the normal operating level]. Units 1 and 3 were unaffected and remain on line and stable at 100% power. Public health and safety were not impacted by this event. "This event is being reported as an 8 hour non-emergency in accordance with 10 CPR 50.72(b)(3)(iv) for a valid actuation of the Emergency Feedwater System. "The NRC Resident Inspector has been notified. "Corrective Action: Troubleshooting of valve 2FDW-40 is on-going." | 0 | 16 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-07-27
51267 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-07-27 12:29 | 2015-07-27 16:05 | 2015-07-27 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED EMPLOYEE "A licensed employee violated the site Fitness-for-Duty (FFD) policy. The employee's plant access has been denied. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.719 |  |  |  | 0 | 2015-07-27
51266 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-07-27 09:02 | 2015-07-27 14:28 | 2015-07-27 | PLANNED OUTAGE FOR PLANT COMPUTER SYSTEMS "On July 27, 2015 at 0902 [CDT], [the site commenced] a planned outage of the Emergency Response Data System (ERDS) and Safety Parameter Display System (SPDS), referred to as 'plant computer'. The unavailability of ERDS and SPDS could significantly affect the site's ability to respond to an emergency if one were to occur. During this time, Operations will be utilizing the site's procedures 1C1.5 and 2C1.5, 'OPERATION WITHOUT COMPUTER', which requires additional operators for monitoring of equipment affected by the loss of the plant computer. Additionally, as this is a planned outage, the work week schedule has been modified to ensure limited interactions required by Operations during this time frame. The site expects ERDS and SPDS to be operational 1200 July 28, 2015. "This event is reportable under 10 CFR 50.72(b)(3)(xiii), Any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of Control Room indication, Emergency Notification System (ENS), or Offsite Notification System). The ENS and Offsite Notification System are not affected by this planned outage. "The health and safety of the public are not impacted by this planned outage. "The NRC Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-27
51265 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-07-27 10:43 | 2015-07-27 13:44 | 2015-07-27 | AUTOMATIC REACTOR/TURBINE TRIP "At 1043 EDT on 7/27/2015, Sequoyah Unit 1 was at 82% power and continuing to perform a startup when the reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3, at NOT/NOP [normal operating temperature and normal operating pressure], approximately 545 F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. "The immediate cause of the trip was an electrically-induced turbine trip. Due to fluctuating voltage the main generator voltage regulator was taken to manual; immediately after this the unit tripped. "Current Temperature and Pressure - Reactor Coolant System (RCS) temperature is 545 degrees F and stable and RCS pressure is 2235 psig and stable. There is no indication of any primary/secondary leakage. All rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-07-27
51264 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-07-26 20:25 | 2015-07-26 22:08 | 2015-07-26 | UNIT 2 SITE STACK RADIATION MONITOR FAILURE "The Millstone Site Rad Monitor, RM-8169, has failed and was declared NOT FUNCTIONAL at 2025 [EDT] on July 26, 2015. "This is reportable pursuant to 10CFR50.72(b)(3)(xiii), as any event that results in a major loss of emergency assessment capability, off-site response capability, or off-site communication capability. "I&C [Instrumentation and Control] is developing a troubleshooting and repair plan." The licensee notified the NRC Resident Inspector, the State of Connecticut Department of Energy and Environmental Protection, and the City of Waterford Dispatch. The loss of this radiation monitor is considered a major loss of assessment capability since it is used in Emergency Action Level (EAL) classification and there is no compensatory measure available. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-26
51263 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-07-26 04:49 | 2015-07-26 11:50 | 2015-07-26 | INVALID SEISMIC EVENT ALARM "At 0449 CDT on July 26, 2015, the station's Seismic Instrumentation generated a seismic event alarm that was determined to be invalid based upon no seismic activity being felt on site, and no activity detected in the area by either the National Earthquake Information Center, or nearby Exelon plants. The instrumentation that actuated recorded a value of 0.0449 g on a single axis of one instrument, which is greater than the 0.02 g threshold value in the Emergency Action Level in the station's emergency procedures; however, no other instrument channel or axis indicated a valid event exceeding the 0.02 g threshold. Since the event alarm was determined to be invalid as described above, no EAL thresholds were met. "The seismic instrumentation was declared non-functional since it would not generate a seismic event alarm during an actual event until the invalid event was reset. The alarm was reset through the alarm reset process. The seismic instrumentation was declared functional and returned to service at 0520. "This resulted in a Loss of Emergency Assessment Capability while the Seismic Instrumentation was out of service. This is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "The licensee has notified the NRC Resident Inspector." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-26
51262 | 0 | FLOWSERVE CORPORATION |  |  |  |  | 2015-07-24 | 2015-07-24 17:05 | 2015-07-24 | PART 21 - MOUNTING BRACKET SEISMIC QUALIFICATION The following information was excerpted from a facsimile from FLOWSERVE: "In accordance with the provisions of 10CFR Part 21, [Flowserve] has identified a potential issue and is submitting our evaluation of the event. "DESCRIPTION: Entergy Design Specification, SPEC-09-0001-P, paragraph 3.1.1 a, requires that position indicators remain operable during a seismic event. The seismic analysis performed [for installation at Pilgrim Station] did not include mounting brackets for the position indicators. Later review of these brackets found them to be inadequate for the application. "SCOPE: The engineering evaluation searched all instances of the use of safety related Topworx C7 position indicators, base part number 04126889, by the Flowserve, Raleigh facility. "PROPOSED ACTION: Flowserve will provide seismically analyzed replacement mounting brackets to Entergy Pilgrim Station at no charge. To prevent reoccurrence of this situation, additional training on the use of nuclear order checklists will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-07-24
51261 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2015-07-12 | 2015-07-24 17:24 | 2015-07-24 | ARIZONA AGREEMENT STATE REPORT - MISSING TRITIUM LIGHT SOURCE The following information was received from the State of Arizona via email: "On July 22, 2015, the licensee reported that they lost one gaseous tritium light source on approximately July 12, 2015. The licensee was removing each source from its subsequent device in order to make disposal more efficient. The lost source was part of a TLS Model 42000 drogue light. The model 42000 drogue light consists of two 450 millicuries (November 1988 assay date) mb-Microtec Model T4376-1 gaseous tritium light sources mounted in a stainless steel assembly. The sources are held in place with silicone. To remove the sources from the drogue light, the silicone (containing two sources) is removed from the stainless steel housing. The silicone is then placed in solvent to soften it. Once the silicone is soft, the sources are removed with little effort and with little or no silicone adhering to the source. "The sources were placed in the solvent on July 12, 2015 and the nonradioactive components of the assemblies, including the silicone, were discarded as regular trash on that date. The source removal and consolidation was completed for all legacy sources on July 22, 2015, at which time, a complete inventory was performed and one source was discovered to be missing. The missing tritium source has a current activity of 100 millicuries. "The Agency [Arizona Radiation Regulatory Agency is continuing to investigate the event." Arizona First Notice: 15-017 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2015-08-03
51260 | 0 | FLOWSERVE CORPORATION |  |  |  |  | 2015-07-24 | 2015-07-24 04:55 | 2015-07-24 | PART 21 - ACTUATOR SHAFT DID NOT MEET DIMENSIONAL REQUIREMENTS The following information was excerpted from a facsimile provided by Flowserve: "In accordance with the provisions of 10CFR Part 21, [Flowserve] has identified a potential issue and is submitting our evaluation of the event. "DESCRIPTION: Energy Northwest - Columbia Station reported a replacement actuator shaft for 6-900 Anchor/Darling swing check was different than the one removed and could not be installed. After consultation with Flowserve, it was determined the actuator shaft did not meet the dimensional requirements of the manufacturing drawing. The shaft includes an off-set lug that engages the hinge and allows testing or exercising the valve disc. The shaft diameter opposite the lug was too large but must be equal to or less than the basic diameter adjacent to the lug in order to allow free disc swing. "SCOPE: Replacement actuator shafts supplied by Flowserve using manufacturing drawings that do not definitively specify the radius/diameter at the lug. Applies to Anchor/Darling swing check valves with levers or actuators. "PROPOSED ACTION: Flowserve will revise actuator shaft drawing to clearly define the radius/diameter at the lug. Flowserve will notify the customers of the attached evaluation of the defect and will request that the actuator shafts be returned to Flowserve for evaluation and/or replacement at no charge. "SUBJECT: Actuator Shaft supplied for 6-900 Exercisable Swing Check Valve, Drawing No. 3489-3 manufactured by Anchor/Darling Valve Co. and installed at Energy Northwest (ENW) - Columbia Station. "ROOT CAUSE: The actuator shaft was machined by a Flowserve subvendor which incorrectly interpreted the machining drawing and produced the shaft with a large, out of tolerance radius around the lug. The drawing was not clear to the subvendor. Flowserve inspection did not discover the discrepancy during subsequent dimensional inspection. "POTENTIAL EFFECT: An excessively large diameter at the lug will not allow installation of a replacement actuator shaft. A shaft with a diameter opposite the lug that is greater than design but still small enough to allow installation could retard or prevent free disc swing and adversely affect check valve function. "EVALUATION: Swing check valves normally operate automatically reacting to fluid flow and do not include external operating mechanisms. Some valves include external mechanisms to confirm valve operation using an external lever or actuator to cycle the disc. Normally these check valves are allowed to swing freely and the external mechanism is not engaged. The external mechanism is only engaged for testing or exercising. The engagement is accomplished by a lug on the actuator shaft that rides in a cut out in the hub of the hinge. The hinge rotates on the actuator shaft during normal, free operation therefore the clearance between the hinge hub bore and shaft is a critical design feature and can affect operation. Proper operation of valve assemblies are verified during production testing therefore are not within the scope of this evaluation. "CONCLUSION: Although the ENW actuator shaft could not be installed due to the excess material, inadequate removal to allow installation could affect the function. In addition shafts manufactured to similar manufacturing drawings supplied as replacement parts could be capable of installation but not allow complete free disc / hinge swing." Affected plants include Exelon - Limerick, Exelon - Quad Cities, and Energy Northwest - Columbia. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-07-24
51259 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-07-24 13:51 | 2015-07-24 17:04 | 2015-07-24 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON MAIN GENERATOR LOCKOUT "At 1351 EDT on 7/24/2015, Sequoyah Unit 1 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 548 F and 2235 psig, with auxiliary feedwater supplying the steam generators and decay heat removal via the condenser steam dumps. The immediate cause of the trip was an electrically-induced turbine trip. There was no associated work in progress related to this and all systems were normally aligned. "There is no indication of any primary/secondary leakage. All rods fully inserted on the reactor trip and remain inserted. The electrical alignment is normal with shutdown power supplied from off-site power. The 2B-B Emergency Diesel Generator is currently in service for the performance of an unrelated surveillance. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector." The cause of the main generator lockout is under investigation. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-07-24
51258 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-07-24 | 2015-07-24 11:50 | 2015-07-24 | TEXAS AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of Texas via email: "On July 24, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that one of his crews was unable to retract a 39 curie Iridium-192 source into QSA 880 D camera. The RSO stated the radiographers had completed their first shot of the day in a shooting bay and noted the lock on the camera did not trip when the source was retracted. The RSO stated the radiographers noted the dose rate where they were standing was 30 millirem per hour after they attempted to retract the source. The radiographers notified the RSO of the event. The RSO responded to their location. The RSO is authorized to recover disconnected sources. "The RSO stated he recovered the source by disconnecting the source guide tube and shaking the source out of the guide tube and into a shield they have designed for this purpose. The RSO was able to connect the source pig tail to the drive cable and retract the source into the camera. The RSO stated he received 15 millirem during the source retrieval. No member of the general public received a dose as a result of this event. The RSO stated they cycled the source in and out of the camera several times without incident. The RSO stated he remained at the work site and monitored the radiographers for several shots and did not note any issues. The RSO is not sure at this time if a source disconnect or misconnect occurred. The RSO is continuing to investigate the event. "Additional information will be provided as it is received in accordance with SA-300." The event location was Wedge Measurements Systems located in Joshua, TX. Texas Incident #: 1-9327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-08-03
51257 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2015-07-23 13:57 | 2015-07-23 19:39 | 2015-07-23 | AUXILIARY FEEDWATER MANUAL START DUE TO LOSS OF MAIN FEEDWATER PUMP DURING PLANT COOLDOWN "During plant cooldown in response to conditions reported to the NRC in Event Notification 51253, Callaway was in Mode 3 (Hot Standby) and on the way to Mode 5 (Cold Shutdown). In accordance with cooldown procedures, Callaway was operating with one Main Feedwater Pump when the pump speed unexpectedly lowered to 0 RPM. The pump was manually tripped in response to the condition. This led to a decrease in water level in the steam generators. In response, operators manually activated the Auxiliary Feedwater System. All systems and components functioned normally in response to the event, and plant operators are currently continuing the controlled shutdown from Mode 3 to Mode 5. Safety related buses are receiving normal off-site power and the grid is currently stable." "The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-07-23
51256 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-07-23 13:05 | 2015-07-23 15:52 | 2015-07-23 | OFFSITE NOTIFICATION DUE TO SODIUM HYPOCHLORITE SPILL "At 1120 EDT on 07/23/2015, while performing Chemistry rounds, a Chemistry Technician discovered an underground leak near the Plant Service Water bleach moat. The Plant Service Water bleach injection pumps were secured at 1130 EDT on 07/23/2015. The leak was later confirmed to be bleach. Approximately 200-300 gallons of 12.5% sodium hypochlorite are estimated to have leaked out of a broken underground pipe. This amount exceeded the reportable limit [100 lbs. or 80 gallons] as specified by the National Response Center. The bleach leaked into the surrounding soil and into a Plant Hatch storm drain where it pooled before reaching the Altamaha river. No bleach discharged into the river. "Cleanup began immediately by neutralizing the bleach with sodium bisulfite and is still on-going. "Plant Management authorized Southern Nuclear Company Environmental Affairs to report to the US Coast Guard National Response Center at 1305 EDT on 07/23/2015 in accordance with corporate procedures. The event was reported to the National Response Center at 1316 EDT. The Georgia Environmental Protection Division was also contacted. "This event is reportable under 10 CFR 50.72(b)(2)(xi) as an event or situation related to the protection of the environment for which a notification to other government agencies have been made. "NRC Resident Inspector was notified at 1530 at 07/23/2015. "CR [Condition Report] 10099779" | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-07-23
51255 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-07-23 | 2015-07-23 14:55 | 2015-07-23 | OKLAHOMA AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED AT CONSTRUCTION SITE The following information was received from the State of Oklahoma via email: "A Troxler Model 4640 gauge has been struck by a vehicle at a road construction site about 5 miles south of Guymon, OK. We will provide more information as it becomes available." The status of the source or damage to the gauge was unknown at the time of the report. A Troxler 4640 gauge typically contains 8 milliCi of Cs-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-07-31
51254 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2015-07-22 | 2015-07-23 14:53 | 2015-07-23 | NEW JERSEY AGREEMENT STATE REPORT - FIXED GAUGE WITH STUCK OPEN SHUTTER The following information was provided by the State of New Jersey via email: "On 7/22/2015, an inspection was conducted of an Ohio fixed gauge service provider working in NJ under reciprocity for a NJ specific licensee. The inspector was made aware that a fixed gauge had failed to shutter when attempted by the licensee. At this time, it is not known when the shutter failed. The gauge was in otherwise normal condition and no members of the public had access to the gauge due to engineering controls. The service provider replaced the air actuator and rotor during the inspection and the shutter was then functioning normally. The licensee was contacted by NJ and committed to providing the report required by 10 CFR 30.50(c). "Location: Phillips 66 Bayway Refinery, Linden, NJ "License No.: 506897-RAD150001 "Device: Vega SH-F1A (with air actuator) serial number 0317 CG, containing 50 mCi (Assay date 1/2001) [Cs-137 contained in gauge] "Follow-up information will be provided when it is known." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2015-07-31
51253 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2015-07-23 01:15 | 2015-07-23 04:21 | 2015-07-26 | INITIATION OF PLANT SHUTDOWN DUE TO RCS LEAKAGE "On July 23, 2015 at 0115 [CDT], Callaway Plant initiated a shutdown required by Technical Specifications (TS). At 2139 [CDT] on July 22, 2015, TS 3.4.13 Condition A was entered due to unidentified RCS leakage being in excess of the 1 gpm TS limit. The leak was indicated by an increase in containment radiation readings, increasing sump levels, and decreasing levels in the Volume Control tank (VCT). "A containment entry identified a steam plume; due to personnel safety the exact location of the leak inside the containment building could not be determined. "At this time radiation levels inside [the] containment are stable and slightly above normal. There have been no releases from the plant above normal levels. "The [NRC] Senior Resident Inspector was notified." * * * UPDATE PROVIDED BY ROB STOUGH TO JEFF ROTTON AT 1757 EDT ON 07/23/2015 * * * "Callaway entered TS 3.4.13 Condition B at 0053 [CDT on July 23, 2015] for the subject leakage since reactor coolant pressure boundary leakage could not be ruled out by visual inspection. The estimated leak rate when the decision was made to shut down the plant was approximately 1.8 gpm. The plant entered Mode 3 at 0600 CDT. "Additionally, at approximately 1315, it was determined that the duration of the required outage would be greater than three days, thus requiring notification to the Missouri Public Service Commission. This offsite notification is reportable to the NRC [per 10CFR50.72(b)(2)(xi)], and the above table has been updated to reflect this reporting requirement." The licensee notified the NRC Resident Inspector. Notified R4DO (Gepford). * * * UPDATE FROM RICHARD HUGHEY TO VINCE KLCO AT 0728 EDT ON 7/26/2015 * * * "Clarification to the initial event notification: the term 'RCS' used above means 'Reactor Coolant System.' Therefore the second sentence from the initial notification is clarified to read, 'At 2139 [CDT] on July 22, 2015, TS 3.4.13 Condition A was entered due to unidentified Reactor Coolant System (RCS) leakage being in excess of the 1 gallon per minute (gpm) TS limit.'" The licensee notified the NRC Resident Inspector. Notified the R4DO (Gepford). | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(xi) |  |  | 0 | 2015-07-23
51252 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2015-07-01 | 2015-07-22 15:20 | 2015-07-22 | AGREEMENT STATE REPORT - VAGINAL CATHETER SLIPPED DURING TREATMENT The following report was received via e-mail: "An incident has come to light at [the licensee's] Conyers clinic. A patient was treated with a vaginal cylinder at the beginning of July, 2015. The treatment was delivered in 3 fractions. On a recent follow-up exam, the patient presented with a single mark on the skin of the upper inner thigh on both legs. The radiation oncologist felt these marks were consistent with radiation dermatitis. A review of the patient's treatment plan and treatment records showed no errors had occurred. "[The licensee's] current thinking is that the only plausible explanation is that the catheter which contains the source wire was not securely locked inside the vaginal cylinder and partially slipped out during treatment.. If this occurred, the most proximal dwell position could have fallen on the skin of the upper thigh. "[The Georgia Radioactive Materials Program] is continuing to investigate." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2015-07-30
51251 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2015-07-17 | 2015-07-22 15:20 | 2015-07-22 | AGREEMENT STATE REPORT - MEDICAL OVERDOSE FOR SKIN CANCER The following report was received via e-mail: "1. A patient received an [Ir-192] HDR treatment using a skin applicator on the nose. This treatment is used to treat skin cancer. "2. The physician's written directive specified a dose to the tumor volume, and a maximum tumor dose of 130 percent of the prescribed dose. The total dose was delivered in 8 fractions. "3. The patient's course of treatment proceeded to conclusion. On recent follow-up exam, the patient's skin reaction was more than usual for this type of treatment, so the physician asked physics to review the plan. "4. This review indicated the tumor volume maximum dose exceeded the prescribed 130 percent by more than 50 percent." The date, time, and dose prescribed/received were not given in the report. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2015-07-30
51250 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-07-22 04:45 | 2015-07-22 12:38 | 2015-07-22 | HPCI DECLARED INOPERABLE "During the performance of the Unit 1 quarterly surveillance 1-SR-3.6.1.3.5 (HPCI), HPCI [High Pressure Coolant Injection] System Motor Operated Valve Operability, the inboard steam isolation valve failed to close within the required time. The valve was subsequently declared inoperable and Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.3 (Primary Containment Isolation Valves (PCIVs)) was entered which required the HPCI steam line to be closed and de-activated. To comply with TS LCO 3.6.1.3 Condition A, the outboard steam isolation valve was closed and breaker opened. Due to the steam line being isolated, TS 3.5.1, ECCS Operating, Condition C was entered on July 22, 2015 at 0445 CDT as a result of the inoperable HPCI system. Troubleshooting and repair is in progress and during this inoperability, other systems are available to provide the required safety functions. "This constitutes an unplanned HPCI system inoperability and requires an 8-hour ENS notification in accordance with 10 CFR 50.72(b)(3)(v)(D), due to the failure of a single train system affecting accident mitigation, and a 60-day written report in accordance with 10 CFR 50.73(a)(2)(v)(D). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-07-22
51249 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-07-21 | 2015-07-22 11:21 | 2015-07-22 | AGREEMENT STATE REPORT - DAMAGED TROXLER The following was received from the State of California via Email: "A CPN thin layer density gauge, serial #1228, was run over by a dump truck that was spreading sand at a paving project on Highway 12 at Terminous Road in San Joaquin County, CA. The source was not breached and remained intact. The gauge was taken to Pacific Nuclear and a leak test disclosed no removable contamination. The California Code of Regulations, Title 17, Section 30350.3 states that the licensee shall immediately notify the Department by telephone and subsequently, within 30 days, by confirmation letter if the licensee knows or has reason to believe that a sealed source has been ruptured. This incident is being reported to the NRC as information only." California 5010 number: 072115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-07-30
51248 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2015-06-05 | 2015-07-22 11:22 | 2015-07-22 | AGREEMENT STATE REPORT - LOSS OF I-125 SEED The following report was provided by the Maine Radiation Control Program via email: "Maine Medical Center (MMC) reported the loss of an I-125 localization seed (39209B-5-12) that contained an activity of 3.4 MBq (92 æCi). The seed was discovered lost during an inventory performed on 6/5/2015. The seed was still in the inventory log, but was not physically present. A nuclear medicine technologist searched the hot laboratory, mammography, and ultrasound areas, but the seed was not found. MMC continued to search for the seed for several weeks. There is no evidence that the seed was implanted into a patient. MMC believes that the seed was inadvertently placed into the trash in the hot laboratory. Corrective actions included providing additional training to personnel." Maine Event Report: ME150003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2015-07-30
51247 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-07-22 00:13 | 2015-07-22 07:08 | 2015-07-22 | SEISMIC MONITOR INOPERABLE "[At] 0013 CDT, [on] 7/22/15, the seismic monitor was found inoperable. The seismic monitor was inoperable such that emergency classification at the ALERT level could not be obtained with site instrumentation. "The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). "[The NRC] Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-22
51246 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-07-21 14:53 | 2015-07-21 21:22 | 2015-07-21 | SINGLE EMERGENCY SIREN INADVERTENT ACTUATION "On 7/21/2015, at approximately 1453 Pacific Daylight Time (PDT), while performing quiet testing of the early warning system, a Pacific Gas and Electric (PG&E) Telecommunications Technician identified that a single emergency response siren was making a full sound output when it should not have been. PG&E Technicians took action and deactivated the single siren. The siren sounded for approximately 1 minute. As a result, this issue is being reported under 10 CFR 50.72(b)(2)(xi) for notifications to other offsite government agencies as the licensee notified the County of San Luis Obispo of the siren deactivation. The San Luis Obispo County Sheriff Watch Commander has been notified of the need to implement alternate means of alert and notification for the areas affected by the deactivation of the single siren. This was accounted for in pre-planning efforts and neither the utility nor 911 received any calls [from the public] related to this matter. The source of the activation signal has not been determined and is being investigated. "There was no impact to the health and safety of the public as a result of this event as the offsite response capabilities remain functional with a single siren failure. The site is operating normally with no emergency conditions present. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-07-21
51245 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-07-21 00:11 | 2015-07-21 20:06 | 2015-07-21 | AGREEMENT STATE REPORT - SOURCE RACK PNEUMATIC CYLINDER FAILURE The following report was received from the State of California via email: "On 07/21/15, the Sterigenics Corporate RSO [Radiation Safety Officer] contacted [California - Radiologic Health Branch] RHB-Sacramento office, via an email and telephone, to report the following event in accordance with [10CFR]36.83(a)(4). [The licensee's] email stated the following: "Last night, at approximately [0011] PDT, at the Sterigenics Hayward Facility (Radioactive materials License 6268-1), the pneumatic cylinder used to raise one of the two source racks (Hoist #1) failed to function as designed. The failure did not cause a stuck source, nor was there any risk of exposure to any individual as a result of this failure. The source did return to the down position in the pool as designed, however, the pneumatic cylinder experienced a failure and a broken flange and is not operable. "[The licensee] will review, in detail, the cause of this failure and implement appropriate corrective action including any necessary changes in maintenance and equipment and report these changes to [the State of California] in writing, within 30 days, as required by 10CFR36.83(b). "In the interim, the facility will not commence operations until repairs are completed to the hoist and approval to commence operations is granted by the Corporate RSO and Corporate Engineering. "[The licensee RSO] further stated that there is no emergency or current issue. A corporate engineer will arrive in San Francisco by [1400 PDT] on 7/21/15, to work on the irradiator. The facility is staffed 24/7 and will notify RHB before resuming any operations. "[California] RHB will be following up with the licensee." The irradiator is in safe mode and the licensee will be investigating the reason for the failure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-07-29
51244 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-07-21 05:04 | 2015-07-21 07:40 | 2015-07-21 | SURRY UNIT 2 TRIP DURING REACTOR STARTUP "Unit 2 Reactor automatically tripped during Unit start up following a maintenance outage. The first indication of the reactor trip was the annunciator Reactor Trip by Turbine Trip. There were no complications following the trip and Unit 2 is stable at Hot Shut Down. Decay Heat Removal is being maintained by dumping steam to the Main Condenser. Steam Generator water level is being maintained by the Main Feedwater system. "At the time of the Reactor Trip, Overspeed Protection Circuitry (OPC) Test was being performed on the Unit 2 Main Turbine. The SOV Turbine Trip annunciator was received. The cause of the reactor trip is under investigation. "This notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for 4-hour notification of Reactor Protection System activation. The Plant responded as expected for the trip. The NRC resident has been notified of the event. "There was no radiation release due to this event, nor were there any personnel injuries or contamination events." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 5 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-07-21
51243 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2015-06-03 | 2015-07-20 16:48 | 2015-07-20 | POTENTIAL PART 21 - ALLEN BRADLEY FAILURE TO DOCUMENT DESIGN CHANGE The following information is excerpted from an email received from United Controls International: "[In] August 2014, United Controls supplied four (4) time delay relays to Omaha Public Power-Fort Calhoun Station. The subject relay was qualified in accordance with IEEE 323-74/83, IEEE 344-1975/1987 and IEEE C37.98-1987, for use in mild environment safety related applications. "Per NRC Part 21 notifications, UCI was informed that the Allen Bradley relays base model 700RTC contain a Complex Programmable Logic Device (CPLD) which was unpublished. This design change could not be noticed since the external appearance of the relay and the relay part number remained the same. Hence, UCI has qualified the subject relay as solid state relay whereas the presence of the CPLD device elects the item as a digital device which can be affected by EMI/RFI noises. "At this time, UCI has no sufficient information to determine whether this design change would create a Substantial Safety Hazard as it relates to the plant applications for the subject relay. "Per the Nutherm Part 21 ML 1516IA230, Allen Bradley has indicated that a rolling change occurred from mid-2009 with no specific manufacturing date to distinguish between the old and the new configuration. Hence, all units manufactured during 2009 and later are suspect. "If you have any questions or wish to discuss this matter or this report, please contact: "Jim Garrison "Engineering Manager "jgarrison@unitedcontrols.com "770-496-1406 x 103" Affected facility: Omaha Public Power-Fort Calhoun Station Part Number: 700-RTC-11200U1 Quantity: 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-07-20
51242 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-07-20 07:40 | 2015-07-20 14:27 | 2015-07-20 | TEMPORARY LOSS OF DIFFERENTIAL PRESSURE IN SECONDARY CONTAINMENT "On the morning of July 20, 2015 at 0740 EDT, with James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100 percent power, the Secondary Containment differential pressure decreased below the JAF Technical Specification (TS) Surveillance Requirement (SR-3.6.4.1.1) value of greater than or equal to 0.25 inch of vacuum water gauge. Both trains of the Standby Gas Treatment System were placed in service and the Reactor Building was isolated. The decrease in Secondary Containment differential pressure was caused by Reactor Building roof maintenance creating multiple openings. Maintenance workers were immediately ordered to stop work and address the condition. Secondary Containment differential pressure was restored to within the TS SR value at 0915 EDT, and remains greater than 0.25 inch of vacuum water gauge. "The secondary containment is a structure that surrounds the primary containment and is designed to provide secondary containment for postulated loss-of-coolant accidents inside the primary containment. To prevent exfiltration the secondary containment requires the control volume pressure at less than the external pressure. The differential pressure requirement of TS SR-3.6.4.1.1 ensures that the secondary containment boundary is sufficiently leak tight to preclude exfiltration. During this period there were no unmonitored radioactive releases; however, this event could have prevented the fulfillment of a safety function to control the release of radioactive material and it is reported pursuant to 10 CFR 50.72(b)(3)(v)(C)." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-07-20
51241 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-07-20 08:55 | 2015-07-20 13:37 | 2015-07-20 | OFFSITE NOTIFICATION DUE TO SPURIOUS ACTUATION OF EMERGENCY SIREN "On 7/20/2015 at approximately 0931 CDT, the Monticello nuclear generating plant was notified by Wright County Sheriffs Office of a spurious actuation of one emergency response siren in the city of Monticello that occurred at approximately 0855 CDT (lasted for approximately three minutes). This actuation was confirmed by vendor system monitoring. As a result, this issue is being reported under 10 CFR 50.72(b)(2)(xi) for notifications to other offsite government agencies as the licensee was notified by the Wright County Sheriffs Office. The source of the activation signal has not been determined. The vendor is investigating. The siren is no longer actuating. There was no impact to the health and safety of the public as a result of this event as the offsite response capabilities remain functional with a single siren failure. The site is operating normally with no emergency conditions present. The NRC Resident Inspector has been notified." The State of Minnesota will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-07-20
51240 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2015-07-18 12:14 | 2015-07-18 18:39 | 2015-08-18 | STANDBY GAS TREATMENT SYSTEM DECLARED INOPERABLE DUE TO INOPERABLE SUMP PUMPS "At 1214 CDT on 7/18/2015, during normal surveillance testing of Z sump, Z2 sump pump run time was found to exceed its upper Augmented IST limit, rendering it non-functional. Operators continued with the surveillance, opening the power supply breaker to Z1 sump pump, rendering it non-functional also. When this was identified, station personnel backed out of testing and restored power to Z1 sump pump. Z sump functions to limit condensation buildup in the common Standby Gas Treatment System (SGT) discharge line to support SGT operability. One sump pump is required to be functional to support SGT operability. With both Z sump pumps non-functional, operability of both trains of SGT is not assured. Loss of both trains of SGT constitutes a loss of safety function for control of rad release and accident mitigation per 10 CFR 50.72(b)(3)(v) functions (C) and (D). "The breaker for Z1 sump pump was reclosed at 1225 CDT, restoring functionality to Z1 sump pump and operability to both trains of SGT. Both Z sump pumps were considered non-functional and unable to support SGT operability for a period of 11 minutes." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 8/18/2015 AT 1347 EDT FROM DAVID VAN DER KAMP TO MARK ABRAMOVITZ * * * "Cooper Nuclear Station (CNS) is retracting the 8-hour non-emergency notification made on July 18, 2015 at 1839 EDT (EN# 51240). "The notification on July 18, 2015 reported a condition where the two Z Sump Pumps were considered non-functional and unable to support the operability of the Standby Gas Treatment System (SGT). "Subsequent evaluation concluded that Z2 Sump Pump was functional with the run time identified and would have supported the operability of SGT during the time the Z1 Sump Pump breaker was open for surveillance testing. A loss of safety function did not exist. A modification had been previously installed at CNS that prevents the buildup of significant amounts of water in a hold-up line. This volume of water was the basis for the original Z Sump Pump IST [in-service-testing] run times. With the buildup of water previously resolved, the calculated Z Sump Pump IST run times are much longer than measured on July 18, 2015." Notified the R4DO (Hagar). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-07-18
51239 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-06-22 | 2015-07-16 17:40 | 2015-07-16 | AGREEMENT STATE REPORT - BRACHYTHERAPY SEED IMPLANT RESULTS IN UNDERDOSE The following was received by the State of California via email: "During the investigation of the licensee's brachytherapy program, the RHB [Radiation Health Branch] personnel discovered a possible medical event. After further review, the RHB personnel determined on 7/14/15 that a medical event had occurred on 6/22/15 which resulted in an underdose of 27 percent to a patient than the dose called for in the written directive. The licensee is in agreement with the RHB that this is a medical event. The investigation is ongoing and there may be additional medical events discovered as documentation is reviewed." State 5010 Number: 070115 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-07-24
51238 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2015-07-16 01:00 | 2015-07-16 15:16 | 2015-07-16 | AGREEMENT STATE REPORT - DAMAGED TROXLER The following was received from the Kansas Department of Health and Environment via email: "A nuclear density gauge was struck at approximately 0100 [CDT], Thursday, July 16, 2015. At 0132 [CDT], [Kansas Division of Emergency Management] KDEM on duty staff officer, received a call from the Kansas Highway Patrol that a nuclear density gauge had been struck in Wichita. [Kansas Department of Transportation] KDOT was on scene. [KDOT] said the gauge was in use at the time by Cornejo and Sons. The supervisor from Cornejo was on the scene. He said the gauge was completely destroyed. He could see the source plate containing the neutron source and said the source rod was stuck in the car that hit the gauge. [KDEM] had similar incidents in the past and could put the source in 5 gallon bucket of dirt for shielding and transport both sources back to their shop, place in a secure area, and contact Troxler for further instructions. KDOT had a radiation survey instrument on scene and did not detect any unusual readings. "At that time emergency response personnel at the scene were not letting anyone approach the debris and the source rod. [Personnel at the scene] confirmed that the Cs-137 source was still intact and that Cornejo could transport both sources back to their shop. [The licensee] recovered the sources and were transporting them back to their shop. On the afternoon of July 16, 2015, [Kansas Department of Health and Environment] confirmed that Cornejo had the source rods secured. [The licensee RSO] stated that they contacted Troxler to begin the source return process i.e. pictures of the source rods as well as leak tests." Kansas Item Number: KS150008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2015-07-24
51237 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-07-15 | 2015-07-16 14:09 | 2015-07-16 | AGREEMENT STATE REPORT - OVERDOSE TO PATIENT DURING PROSTATE SEED IMPLANT The following information was received via facsimile: "On July 16, 2015 the licensee informed the Department's [Pennsylvania Department of Environmental Protection Bureau of Radiation Protection] Central Office of a medical event. The event is reportable within 24-hours per 10 CFR 35.3045(a)(1)(i). Both the patient and referring physician were notified. "On July 15, 2015, a patient was scheduled to receive a partial iodine-125 (I-125) prostate seed implant of 107 Gy, to be followed by a course of external beam radiation therapy of 45 Gy. During the procedure, the physician made an error and administered a full I-125 implant of 160 Gy. This resulted in a 49.5 percent overdose. No harm is expected to the patient. "Cause of the event: Human error. "The licensee plans to compensate for the overdose by eliminating the follow-up external beam therapy. A full report is expected within 15 days. The Southcentral Regional Office plans to perform a reactive inspection. More information will be provided as received." Pennsylvania Event Report ID No.: PA150020 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-07-24
51236 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2015-07-15 23:32 | 2015-07-16 04:41 | 2015-07-16 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO METEOROLOGICAL TOWER SOFTWARE FAILURE "This notification is being made due to a loss of emergency assessment capability in accordance with 10CFR 50.72(b)(3)(xiii). At 2332 [CDT], on 07/15/2015, the meteorological tower computer system software failed which resulted in a loss of meteorological data to the plant. Proceduralized compensatory measures for dose assessment include use of National Weather Service followed by historically determined default values. Information Technology personnel reported to the plant and successfully reset the software. Meteorological data to the plant was restored at 0216 [CDT] on 07/16/2015. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-16
51235 | 0 | UNITED STATES AIR FORCE |  |  |  |  | 2015-07-15 15:15 | 2015-07-15 15:52 | 2015-07-15 | LOST Am-241 SOURCES The following was received via email: "The Installation Radiation Safety Officer of the Wright- Patterson AFB telephoned at 1515 [EDT] stating that they lost two sources which have 10 microcuries of Am-241 each. IAW 10 CFR 20.2201, [the licensee has] reported the loss of sources to the NRC Operation Center." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-07-23
51234 | 0 | CB&I AREVA MOX SERVICES, LLC |  |  |  |  | 2015-02-24 | 2015-07-15 12:25 | 2015-07-15 | INADEQUATE WELDS AFFECTING STRUCTURAL CAPACITY OF EMBED PLATES MOX [Mixed Oxide] Services has determined that the fillet welds connecting the ledger angle to the embed plate did not comply with the minimum size required by AWS D1.1-98 and the design requirements. The embed plates containing defects were supplied to MOX Services as a basic component by Specialty Maintenance and Construction, Inc. (SMCI) Division of MetalTek International. The undersize fillet welds connecting the ledger angle to the embed plates were determined to be inadequate. Inadequate welds would adversely affect the load bearing and structural capacity of these components. CB&I Part 21 interim report, dated January 20, 2015, indicates that Vogtle Units 3 and 4 have been supplied with basic components by SMCI. These weld defects related to the SMCI embed plates were initially identified by nonconformance report on February 24, 2015. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-07-15
51233 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-07-14 10:30 | 2015-07-15 10:50 | 2015-07-15 | AGREEMENT STATE REPORT - DOSE TO IMPROPER TREATMENT SITE The following information was received by the State of Ohio via email: "On July 14, 2015, the licensee reported that the intended delivery of Y-90 SirSpheres went to the small bowel instead of the right lobe of the liver during a procedure that morning. The intervention physician felt that the dose delivery was not going where it should be going and discontinued the treatment. Scanning the patient identified that the Y-90 microspheres were delivered to the small bowel. The original prescribed dose to the right lobe of the liver was 78 Gy with 20.5 mCi. The delivered dose of 36 Gy with 7.79 mCi went to the small bowel instead of the liver right lobe. The patient was notified at the time of the event. The interventional physician was the referring physician and AU [Authorized User]." Ohio Report: OH150007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-07-23
51232 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-07-15 00:04 | 2015-07-15 01:04 | 2015-07-17 | TECHNICAL SUPPORT CENTER OUT OF SERVICE DUE TO PLANNED MAINTENANCE "At 0004 [CDT] on Wednesday, July 15, 2015, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system will be removed from service for planned maintenance activities. During the maintenance, the TSC Ventilation will be shut down. The TSC air filtration fan and dampers will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed in approximately 24 hours. "Contingency plans are in place so that if an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Planning (EP) procedures and checklists. If radiological or environmental conditions require TSC facility evacuation during ventilation system restoration; the Station Emergency Director will relocate the TSC staff in accordance with station procedures." "The NRC Resident Inspector has been notified." * * * UPDATE FROM TRAVIS PRELLWITZ TO DONALD NORWOOD AT 1733 EDT ON 7/17/2015 * * * "At 1347 CDT on July 17, 2015, Dresden TSC Ventilation was restored. The Dresden TSC Ventilation is Functional at this time. "The NRC Resident Inspector has been notified." Notified R3DO (Orth). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-15
51231 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-07-14 17:15 | 2015-07-14 22:59 | 2015-07-14 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 1810 (Central Daylight Time) on July 14, 2015, Browns Ferry Units 1, 2, and 3 initiated actions to commence a reactor shutdown to comply with TS [Technical Specifications] LCO 3.0.3. TS LCO 3.0.3 was entered at 1715 (Central Daylight Time) due to concurrent losses of the A and B Control Bay Chillers. This resulted in a loss of cooling to the U1 and U2 4kV Shutdown Board Rooms. Required actions for the loss of cooling to the U1 and U2 4kV Shutdown Board Rooms are to declare the electrical equipment in the 4kV Shutdown Board Rooms inoperable. The declaration of inoperability of the equipment supported by the U1 and U2 4kV Shutdown Boards resulted in TS LCO 3.0.3 for Units 1, 2, and 3. TS LCO 3.0.3 requires actions to be initiated within one hour to place the affected units in MODE 2 within 10 hours; MODE 3 within 13 hours; and MODE 4 within 37 hours. "This event requires a 4-hour report in accordance with 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications.' "The NRC Resident Inspector has been notified. "Condition Report #1056829 has been initiated in the Corrective Action Program." The 4kV shutdown electrical boards are required in all modes of operation. | 99 | 99 | 99 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2015-07-14
51230 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-06-09 | 2015-07-14 15:20 | 2015-07-14 | AGREEMENT STATE REPORT - LOST CD-109 SOURCE The following report was received from the California Radiation Health Branch via email: "Stanford University RSO [Radiation Safety Officer] informed RHB [California Radiation Health Branch] that a 0.285 mCi Cd-109 source had been lost." The licensee has implemented corrective actions to bolster inventory accountability. California 5010 Number: 062515 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-07-22
51229 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2015-07-09 | 2015-07-14 14:20 | 2015-07-14 | AGREEMENT STATE REPORT - IMPLANT BRACHYTHERAPY OVERDOSE The following report was received from the North Carolina Department of Health and Human Services via email: "Narrative event description: I-125 Prostate seed implant medical event occurred when physicist ordered the incorrect activity and number of seeds. The patient plan had the correct planned activity, but when the order was placed with air kerma, the wrong activity was ordered and subsequently implanted to the patient. "Event date and notification date: Implanted 7/9/15. Identified and reported the medical event 7/13/15. "Phone Call received from Physicist to NC RAM [North Carolina Radioactive Materials] Branch at 1246 [EDT] on 7/13/15. "Cause and corrective actions: Incorrect calculations and human error in conversion from air kerma to activity; [The licensee] ordered and implanted [the] wrong activity. "Notifications: NC RAM Branch notified 7/13/2015 "Indicate if there are any generic implications: Lack of attention to units and procurement procedures for seeds. "Source/Radioactive Material: Iodine 125 brachytherapy seeds from Theragenics Corporation "Procedure administered; dose intended and actual dose administered; isotope and activity administered; target organ: Prostate Seed Implant, Intended Dose 144 Gray or 23.48 mCi (71 seeds), Implanted Dose of 31.299 mCi (75 Seeds), ~33% overdose based on activity alone (physicist reported 28%), I-125 seeds and 31.299 mCi administered, prostate was target organ. "[The] patient and Referring Physician were notified 7/13/15. "Report identification number: NC150017" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-07-22
51228 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-07-13 23:39 | 2015-07-14 05:37 | 2015-08-25 | SECONDARY CONTAINMENT PRESSURE INCREASE ABOVE TECHNICAL SPECIFICATION LIMIT "Reactor Building (Secondary Containment) pressure increased to above the Technical Specification Surveillance requirement of 0.25 inches vacuum water gauge for approximately 2 minutes during a planned surveillance test due to a subsequent failure of REA-FN-1A [Exhaust Fan] to manually start during restoration from the surveillance test. This event is reportable as an event that could have prevented fulfillment of a safety function needed to control the release of radiation and mitigate the consequences of an accident. "Prior to taking test data the surveillance test directs declaring Secondary Containment inoperable in anticipation of potentially exceeding 0.25 inches vacuum water gauge reactor building pressure during the conduct of the surveillance. Consequently Technical Specification LCO 3.6.4.1.A was entered with a 4 hour completion time to restore Secondary Containment to an operable state. "Upon failure of REA-FN-1A to start immediate actions were taken to close reactor building ventilation dampers and secure ROA-FN-1A [Supply Fan]. Following closure of ventilation dampers and stopping ROA-FN-1A reactor building pressure was quickly restored to less than 0.25 inches vacuum water gauge with Standby Gas Treatment that was already in operation as part of the surveillance test. "There were no radiological releases associated with the event. "No safety system actuations or isolations occurred. "The licensee notified the NRC Resident Inspector." Maximum Secondary Containment pressure noted was 0.1 inches positive water gage. * * * RETRACTION AT 1351 EDT ON 8/25/2015 FROM MATT HUMMER TO MARK ABRAMOVITZ * * * "Subsequent to the initial report, Columbia has since determined that per NUREG-1022 3.2.7 the event was not reportable as Secondary Containment was 'declared inoperable as a part of a planned evolution ... in accordance with an approved procedure and [Columbia's] TS [Technical Specifications].' No condition has been discovered that would have resulted in the system being declared inoperable prior to the surveillance. "Therefore, this event is not considered to be a condition that could have prevented fulfillment of a safety function or a condition prohibited by TS and is not reportable to the NRC as a Licensee Event Report (LEA) per 10 CFR 50.73. "The NRC Senior Resident Inspector will be notified." Notified the R4DO (Campbell). | 64 | 0 | 0 | 64 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-07-14
51227 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-07-13 16:00 | 2015-07-13 19:17 | 2015-07-13 | AGREEMENT STATE REPORT - LOST/STOLEN TROXLER DENSITY GAUGE At approximately 1745 EDT the State of Florida was contacted by the Radiation Safety Officer for MC Squared, Inc. The RSO reported a probable stolen Troxler gauge. Model number 3411B Serial Number: 13563. The company vehicle was parked at a contractor's site at the intersection of Anderson and West Waters Avenue in Tampa, FL. The gauge and packaging were chained and locked to the bed of the truck and was also strapped down. When the technician came out around 1600 EDT he noticed it was missing. They were only parked in that area between 30 minutes to an hour and the lock is also missing. The Hillsboro County Sherriff's office was notified. A report was filed by the Hillsboro County Deputy, Report Number: 15-441038. When the report is completed it will be available to the State of Florida. The Troxler gauge sources are 40 mCi of Am/Be, and 8 mCi of Cs-137. State of Florida Incident Number: FL15-068. The State of Florida is continuing to investigate this event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-07-21
51226 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-07-12 21:05 | 2015-07-13 17:24 | 2015-07-13 | AGREEMENT STATE REPORT- POTENTIAL RAD WORKER OVEREXPOSURE The following report was provided by the Tennessee Division of Radiological Health via email: "At approximately 2105 [EDT] on the night of July 12th, using our local access control program (i.e., Canberra HIS20) and a DMC 3000 series electronic dosimeter, an Erwin Resin Solutions employee was exiting the Radiological Controlled Area when he received a message stating that he had exceeded his TEDE [Total Effective Dose Equivalent] limit. According to the access control program, a dose of 10002.2 mrem was received. The employee was immediately removed from the area and follow up surveys were conducted. Surveys indicated that general area dose rates were 2-15 mr/hr and that the highest individual package dose rate was 45 mr/hr. The individual had been in the area for approximately 0.47 hours and he recalls at one point looking down at his dosimeter to see a display of 2.4 mrem. The employee's TLD has been pulled and sent off to Mirion for an emergency read, results are expected within 24-48 hrs. The individual will remain out of the RCA until the investigation has concluded. "Access records have been pulled from the HIS20 program and the doses given were not reflective of a normal entry. A START READ of 0 mrem was given and an END READ of 0 mrem was also given. A GAMMA COMPONENT READ of 10002.2 mrem was given but should have been the same as the END READ which was 0 mrem. All indicators lead to a faulty electronic dosimeter, the dosimeter in question is being sent to our instrument department for further evaluation. "Tennessee Event Report ID No.: TN-15-101" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-07-21
51225 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2015-07-13 12:10 | 2015-07-13 15:45 | 2015-07-13 | INADVERTENT ACTIVATION OF EMERGENCY SIREN BY VENDOR "At approximately 1210 [EDT] on July 13, 2015 during conduct of vendor maintenance, a contract maintenance worker inadvertently activated siren 71. "The licensee was notified of the siren activation by the vendor at 1211 [EDT]. "Wayne County was notified of the siren activation by the vendor at 1212 [EDT]. "One of the 96 sirens in the 10-mile Emergency Planning Zone (EPZ) were activated for less than one minute. "No press release is planned by Exelon. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-07-13
51224 | 0 | PALISADES | 1 |  |  | [1] CE | 2015-07-13 08:38 | 2015-07-13 13:33 | 2015-07-13 | OFFSITE NOTIFICATION DUE TO SPILL OF PORTABLE CHEMICAL TOILET TO THE ENVIRONMENT "On 7/13/15 at 1000 EDT, a spill to the environment was determined to be reportable to the state environmental and local health agencies. "The spill occurred when a portable chemical toilet tipped over and was identified at approximately 0838 EDT. The contents and exact quantity of the spill are unknown, but the toilet has a capacity of 60 gallons. The discharge flowed to a storm drain which ultimately discharges to the beach of Lake Michigan. Rainfall was present when the spill was identified. Cleanup efforts are in progress. "The State of Michigan, via the Pollution Emergency Alert System (PEAS), was notified as required by the Site Spill Plan by the Site Environmental Coordinator at 1024 [EDT]. The Local government (Van Buren County) was notified at 1045 [EDT] via 911. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-07-13
51223 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-07-13 08:30 | 2015-07-13 07:50 | 2015-07-18 | PRIMARY AND BACKUP METEOROLOGICAL TOWERS TO BE REMOVED FROM SERVICE FOR UPGRADE "On July 13, 2015, planned activities will be performed to upgrade the Vogtle Electric Generating Plant Meteorological Towers and its communication equipment. The emergency response data system will be affected. The work will be completed within approximately 5 days. This activity requires the meteorological tower to be out of service greater than 72 hours rendering equipment used for emergency assessment non-functional. "The TSC and EOF remain functional during the outage. Compensatory measures exist within emergency plan implementing procedures to obtain meteorological tower data via Savannah River Site and with the National Weather Service. Meteorological information will be relayed via the emergency notification system to the NRC Operations Center. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) for 'any event that results in a major loss of emergency assessment capability.' The Emergency Response Organization has been notified of the upgrade and necessary compensatory actions. "The NRC Resident Inspector has been notified." * * * UPDATE FROM DANIEL MONAHON TO DONALD NORWOOD AT 2013 EDT ON 7/18/2015 * * * Vogtle primary and backup Meteorological Towers have been returned to service and functionality of equipment has been restored. The NRC Resident Inspector will be notified. Notified R2DO (King). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-13
51222 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-07-11 18:22 | 2015-07-11 18:46 | 2015-07-11 | UNUSUAL EVENT FOR A CO2 RELEASE AFFECTING NORMAL PLANT OPERATIONS "At 1810 [EDT], the Salem unit 1 control room received an alarm that a CO2 discharge occurred in the Diesel Fuel Oil Transfer Pump Rooms on the 84 foot elevation in the Auxiliary Building. The control room referred to the OHA [Overhead Annunciator] response procedure S1.OP-AR.ZZ.0001 for OHA A-8, 'Fire Prot CO2/Halon Disch.' The ARP [Alarm Response Procedure] directed implementation of the S1.OP-AB.Fire-0001 procedure and control room ventilation was shifted to the 'fire outside' mode of operation. The on site fire protection team responded to the area and confirmed the CO2 discharge. The [on site] fire department determined that there was no fire and no smoke in the area of the discharge. The Fire Brigade Liaison inspected the equipment and determined that there was no adverse impact to any equipment located in the vicinity of the discharge and no operational impact on the plant. "All systems responded as expected. "There were no personnel injuries as a result of the discharge. "Atmosphere in the area of the discharge has been verified normal and no restrictions to the area are in place." The cause of the discharge was determined to be a faulty detector. No off site response was requested and an hourly firewatch will be initiated until the detector is repaired. The licensee will notify the NRC Resident Inspector and has notified the states of Delaware and New Jersey. Notified DHS, FEMA Operations Center, and NICC and e-mailed Nuclear SSA and FEMA National Watch Center. * * * UPDATE AT 2206 ON 7/11/15 FROM MARK FIOCCO TO MARK ABRAMOVITZ * * * The Unusual Event was terminated at 2154 EDT. The licensee notified the NRC Resident Inspector and the states of Delaware and New Jersey. Notified IRD (Stapleton), R1DO (Cahill), NRR (Morris), DHS, FEMA Operations Center, and NICC and e-mailed Nuclear SSA and FEMA National Watch Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-07-11
51221 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-07-10 07:00 | 2015-07-10 14:57 | 2015-07-10 | EMERGENCY SIREN OUT OF SERVICE "At 0710 CDT on July 10, 2015, Exelon was notified by the siren vendor that siren CL27 experienced a communications failure during the daily test. Siren CL27 affects 33.9% of the Clinton EPZ population. The loss of communications represents more than 25% of the EPZ population and is therefore reportable under 10 CFR 50.72(b)(3)(xiii). "The siren vendor is currently investigating to repair the issue. "The DeWitt County Emergency Manager has been notified. DeWitt County has implemented the backup means of notification called 'Route Alerting' in lieu of siren communications. Route Alerting consists of vehicles and public address systems. "The NRC Senior Resident has been notified. "1300 - Siren returned to service." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-10
51220 | 0 | OAKWOOD HOSPITAL |  |  |  |  | 2015-07-01 | 2015-07-10 13:18 | 2015-07-10 | SEALED I-125 SOURCE DAMAGED DURING PATHOLOGY EXAMINATION A breast implant of an I-125 seed had been performed followed by a lumpectomy. The lump with the implanted seed was sent to the pathology lab for analysis. During the analysis, the Pathology assistant cut through the I-125 seed. No contamination was noted on the counter top and a thyroid scan of the Pathology assistant was negative. "1) The source was placed in the leaded container which would not allow any I-125 to escape and release any radioactivity any longer. "2) There was no radioactive material left on the countertop which was further verified by a wipe test. "3) A thyroid bioassay was performed on the Pathology assistant working on the specimen and the results were negative. "4) On 7/9/15 a wipe test of the source revealed that the source integrity was compromised indicated by elevated counts on the wipe compared to the background (4900 dpm vs 120, indicating an activity of approximately 1.5 micro Curie). This indicates that surface of the solid source is contaminated. "5) [The licensee] will also contact the vendor to find out if the source can be returned to them (since the source is in a sealed shielded container)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-07-20
51219 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-07-09 17:32 | 2015-07-09 18:05 | 2015-07-09 | NOTIFICATION OF UNUSUAL EVENT - FIRE IN CONTAINMENT The Vogtle Unit-1 control room received a fire alarm from inside the containment building. Per plant requirements, verification of the fire was not obtained within 15 minutes and an Unusual Event was declared. Plant personnel were able to enter containment and verify that there was no fire present. The reactor remained at 100% power throughout the event. Unusual Event entered: 1732 EDT Unusual Event exited: 1848 EDT The licensee notified the NRC Resident Inspector, State, and local governments. Notified DHS, FEMA, and NICC. NuclearSSA (email) and FEMA NWC (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-07-09
51218 | 0 | TTL ASSOCIATES, INC. |  |  |  |  | 2015-07-09 14:00 | 2015-07-09 15:10 | 2015-07-09 | TROXLER MOISTURE DENSITY GAUGE DAMAGED BY BULLDOZER At a temporary construction site in Yale, MI, a Troxler Model 3440, s/n 26515, was run over by a bulldozer. The gauge user was injured and taken to a local hospital. TTL Associates, a materials testing lab located in Plymouth, MI, is responding to the scene to recover the damaged gauge and perform radiation surveys. Local HAZMAT was also contacted. The gauge was in a wheel barrow and not in use at the time it was struck. The licensee is contacting Troxler for instructions to return the gauge. The Troxler Model 3440 contains two sources; Cs-137 and Am:Be-241 of 8 mCi and 40 mCi, respectively [typical values]. * * * UPDATE AT 1731 EDT ON 07/09/15 FROM JEFF ELLIOTT TO DANIEL MILLS * * * The gauge was recovered from the construction site with the source still in the locked and stored position and is enroute to TTL Associates for evaluation prior to return to Troxler Labs. A survey of the affected area found no contamination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-07-17
51217 | 0 | U.S. ARMY |  |  |  |  | 2015-07-08 12:00 | 2015-07-09 11:49 | 2015-07-09 | ARMY CHEMICAL ALARM DEVICE RETRIEVED FROM EBAY "The report is being made per 10 CFR 20.2201(a) (Report of Theft) on July 9, 2015, possibly under NRC License 21-32838-01 (Amendment 7). "On May 11, 2015, an agent from the US Army Criminal Investigation Command (CID) at Joint Base Lewis-McChord (JBLM), Ft. Lewis, WA contacted the [Radiation Safety Officer (RSO)] to indicate the possession of a M8A1 chemical alarm which is a licensed item under NRC license 21-32838-01. The item containing 250 uCi of Am-241. The item was sold on line (eBay) and the CID was able to retrieve it. The serial numbers identifying the individual item was scratched off as reported to [the RSO]. The CID was looking to identify who owned the item and for disposition. "Due to the CID criminal investigation, access to the item was not possible until May 21, 2015 and access was limited after the indicated date with little information obtained. It was during this limited access, that we were able to determine that the item was not a M8A1, but a M22 ACADA, which is also under the same Army license. The M22 ACADA contains two drift tube modules of 15 mCi Nickel - 63 for a total of 30 mCi. There are some M22 ACADAs indicated with a total of 20 mCi. Also, the initial thought was that the M22 ACADA was a training dummy device without radioactive sources, because of it being marked 'TNG'. "On June 29, 2015, the item was released from the CID to go to Pine Bluff Arsenal (PBA), Arkansas for further investigation. On July 1, 2015, the M22 ACADA was received at PBA and on July 8, 2015, information was received to indicate that the item may have had the nickel radioactive sources. The M22 ACADA was opened up to find components to include the drift tube modules with the nickel sources missing and the wire that would have led to it was cut. PBA indicated that it appeared gutted. PBA indicated that the plate with the serial numbers and identifying information was removed from the M22 ACADA and of course the source modules had serial numbers in which the source modules are missing. "PBA performed a Radiac survey of the M22 ACADA and did not note any radioactive material. "The Army is trying to figure out who the owner is, but without identifying information this may not happen. The suspect in the event is not providing any information. We are looking into the bar code and other identifications from the manufacturer to see if there is a way to identify the owner, but this is considered a long shot for identifying the owner. It is an assumption that the M22 ACADA is under TACOM LCMC's license due to the Army green color, but there are other licensees out there with similar devices." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 1 | 2015-07-10
51216 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-07-02 19:30 | 2015-07-09 09:16 | 2015-07-09 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following was received form the State of Louisiana via fax: "LA DEQ [Louisiana Department of Environmental Quality] Radiation Section was notified on Thursday July 2, 2015, 2155 [CDT], by a representative from Toulong-Wong Engineers, Inc., of the theft of a Troxler MD [Moisture Density] Portable Gauge. The gauge and transport case was stolen from the bed of a Toyota Tundra pickup [Dark Gray newer Toyota Tundra pickup] parked in the front of the operator's residence. It was secured to the truck by two end cables, the case was locked and the gauge itself was locked. The end cables were cut and the transport container and gauge were stolen. The Gauge was a Troxler, Model 3430, s/n 25042, loaded with Cs-137 9 mCi, s/n 75-7211 and Am-241 44 mCi, s/n 47-21246. "The LA [DEQ] has inspectors involved and will continue to keep NRC informed of the status of our investigation. "LA Department of Environmental Quality, Radiation Section. The call came into the 24 hour emergency hotline. The Baton Rouge City Police [Department] was notified and a theft report was filed. "[A] press release has been issued, with contact information, photos, and a reward for recovery." Louisiana Incident # LA 150012 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-07-17
51215 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2015-07-08 09:48 | 2015-07-09 10:29 | 2015-07-09 | CONTAMINATED EMPLOYEE WITH MEDICAL CONDITION TRANSPORTED OFFSITE "On July 08, 2015 a Honeywell employee experienced a non-work related medical condition that required off site medical support. The incident occurred at approximately 0948 [CDT] in the Feed Materials Building Control Room at the Metropolis facility. Due to the nature of the employee's condition, the individual was transported to a local medical facility. Honeywell Health Physics staff accompanied the injured employee and provided guidance to Emergency Room personnel and controlled the facilities prior to decontamination. A whole body survey of the employee and plant clothing was performed; the maximum amount of contamination present was on the employee's work boots, 86,000 dpm/100 sq. cm [employees work coveralls also contaminated]. All contaminated clothing was removed from the employee and an additional whole body survey was performed; no contamination above background levels was detected. Following medical evaluation, hospital facilities were decontaminated and found to be free of contamination prior to release for unrestricted use. All contaminated materials from the hospital and injured employee were returned to the Metropolis facility." The licensee notified NRC Region 2 (Hartland) and the Metropolis Emergency Coordinator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2015-07-09
51214 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-07-08 | 2015-07-09 08:17 | 2015-07-09 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER FOUND STUCK The following information was received from the State of Texas via email: "On July 8, 2015, the Agency was notified by the licensee's radiation safety officer (RSO) of a stuck shutter on an Ohmart Vega SH-F2 nuclear gauge containing a 500 millicurie Cesium - 137 source. The stuck shutter was found during a routine six month inspection. The RSO determined the source shutter would not operate due to internal corrosion seizing it in the open position. The RSO verified the radiation levels in the area of the gauge had not changed. The RSO stated the source normally operates in the open position and there are no safety issues. The RSO stated he had contacted a service provider to make repairs to the gauge. The RSO stated a replacement internal shutter mechanism equipped with a gasket will also be ordered for installation to prevent future water intrusion and corrosion. The gauge does not pose an exposure risk to the licensee's workers or to members of the general public. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-07-17
51213 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-07-08 18:37 | 2015-07-08 21:53 | 2015-07-11 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE "This telephone notification is provided in accordance with Exelon Reportability manual SAF 1.10, 'Major Loss of Emergency Preparedness Capabilities', and 10CFR50.72(b)(3)(xiii). "On July 8th 2015 at 1837 [CDT], it was determined that the onsite Technical Support Center (TSC) Ventilation System Supply Fan belts had failed, resulting in loss of ventilation for the facility. Repairs were not completed within the time required had the TSC needed to be staffed. There is currently no emergency event in progress requiring TSC staffing. If an emergency is declared and the TSC ERO [Emergency Response Organization] activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable site procedures. "The licensee has notified the [NRC] Senior Resident Inspector of the issue." * * * UPDATE FROM TODD CASAGRANDE TO DANIEL MILLS AT 1510 EDT ON 7/11/15 * * * "After repairs were completed, the TSC Ventilation was restarted on 7/9/15 at 0625 EDT for a maintenance run, the TSC Ventilation was restored to operable status at 1500 EDT on 07/11/2015. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Stone). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-08
51212 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-07-07 11:05 | 2015-07-08 17:43 | 2015-08-27 | TECHNICAL SUPPORT CENTER VENTILATION OUT OF SERVICE "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality of the TSC Ventilation system was discovered on July 7, 2015 at 11:05 EDT. The issue involved a loss of cooling capability of the TSC Ventilation system due to failed ventilation system components. Maintenance started repairs immediately following the discovery of the component failures and completed repairs to restore functionality of the TSC Ventilation system on July 8, 2015 at 17:07 EDT. On July 8, 2015, at approximately 15:30 EDT, further review of the impact of this equipment failure determined that this condition was reportable as a loss of emergency assessment capability. "If an emergency were declared requiring TSC activation during the non-functional period, the TSC would have been staffed and activated using existing emergency planning procedures unless the TSC became uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC became necessary, the Emergency Director would have relocated the TSC staff to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team was notified of the maintenance and the possible need to relocate during an emergency. This condition did not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." * * * UPDATE ON 8/27/15 AT 1445 EDT FROM INGRID NORDBY AND JOHN CAVES TO HOWIE CROUCH * * * "An extent of condition review revealed three additional instances of loss of cooling capability of the Technical Support Center due to failed ventilation system components: January 7, 2015; June 20, 2015; and June 30, 2015. Functionality was restored after these conditions were identified. Each of these instances was determined to be reportable in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident Inspectors have been notified." Notified R2DO (Rose). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-08
51211 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-07-08 14:25 | 2015-07-08 15:37 | 2015-07-08 | MANUAL REACTOR TRIP DUE TO LOWERING STEAM GENERATOR WATER LEVELS "Indian Point Unit 3 was manually tripped at 1427 EDT due to lowering steam generator water levels. At 1425 EDT, #31 condensate pump tripped, causing the lowering water levels. There were no immediate complications on the trip and the unit is stable in Mode 3. Auxiliary feedwater actuated as expected and is in service. All rods inserted and decay heat is being rejected to the condensers. Offsite electrical power is in service. Unit 2 is stable at 100% power." The licensee plans on issuing a press release. The licensee notified the NRC Resident Inspector and New York Public Service Commission. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-07-08
51210 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-06-18 | 2015-07-08 15:31 | 2015-07-08 | AGREEMENT STATE REPORT- LOST MOISTURE/DENSITY GAUGE The following report was received from the State of California via e-mail: "On 6/18/15 an RHB [Radiologic Health Branch] inspector discovered one the licensee's gauge cases was empty and the licensee stated they did not know where the gauge was and would do an investigation. The licensee stated they were not able to determine where the gauge was (Troxler, 3441B, #5803 with 8 mCi Cs-137 and 40 mCi Am-241:Be). The last time the gauge was seen was when it was brought to Maurer Technical Services (the CPN representative) for repair on July 23, 2014. The licensee was going to review additional paperwork to see if he could figure out what happened to the gauge, but at this point he has not gotten back to us [RHB] with any additional information. Maurer Technical Services has done a complete search of their facility and said they do not have the gauge. Maurer Technical [Services] does not have a record of which individual picked up the gauge from their facility. The licensee states they do not remember who picked up the gauge and could not find any paperwork to show gauge #5803 had been used after July 23, 2014. The licensee states there had been no break ins at their facility nor had the locked storage cabinet been tampered with. The Department [California Department of Environmental Health] also interviewed all of the current employees and no one can remember who last used the gauge or picked up the gauge from the repair facility. The Department contacted several of the major companies that perform leak test analysis and this gauge had not been leak tested since prior to July 23, 2014. The Department also researched whether the gauge (serial #5803) was listed in the NMED system as having been 'found', but it was not found in any of the reports. The gauge remains missing." 5010 Number: 070615 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-07-16
51209 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-07-08 | 2015-07-08 15:30 | 2015-07-08 | AGREEMENT STATE - TWO GAUGE SOURCES COULD NOT BE FULLY RETRACTED The following report was received from the State of Texas via e-mail: "On July 8, 2015 the Agency [Texas Department of State Health] was notified by the licensee's radiation safety officer that while performing routine test of gauge shutters, they found two gauges where the source could not be fully retracted. Both gauges are Ohmart Vega model SHLMBR-4 gauges containing a 5,000 millicurie cesium-137 source. The gauges are mounted on the side of poly resin tanks. The sources were left in the normal operating, unshielded position. The sources do not pose any additional risk of exposure to the workers or members of the general public. The RSO stated they have not decided how they were going to resolve the problem yet, but will notify the Agency [Texas Department of State Health] once a decision has been made. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # I-9325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-07-16
51208 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-05-11 01:19 | 2015-07-08 13:23 | 2015-07-08 | INVALID ACTUATION OF THE DIVISION 2 EMERGENCY DIESEL GENERATOR "The following information is provided as 60-day telephone notification to the NRC in accordance with 10 CFR 50.73(a)(1) reported under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of the Division 2 emergency diesel generator (DG). The event occurred on May 11, 2015, at 0119 CDT. As allowed by 10 CFR 50.73(a)(1), the notification is being made via telephone. "(a) The specific train(s) and system(s) that actuated were: "During the restoration from surveillance test procedure CPS 9080.25, 'DG 1B Test Mode Override, Load Reject Operability and Idle Speed Override,' the Division 2 DG automatically started. The Division 2 DG started when the maintenance technicians improperly removed a temporary toggle switch installed for simulation of a Loss of Coolant Accident (LOCA) signal. "(b) Whether each train actuation was complete or partial: "Upon receiving the simulated LOCA signal, the Division 2 DG started as expected. No additional actuations occurred. "(c) Whether or not the system started and functioned successfully: "Upon receiving the simulated LOCA signal, the Division 2 DG started and was verified to have properly started in response to a start signal. "The NRC resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-07-08
51207 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-07-08 08:20 | 2015-07-08 11:13 | 2015-07-08 | OFFSITE NOTIFICATION DUE TO WORKER FATALITY NOT RELATED TO PLANT OPERATION "This notification is being reported to the NRC in accordance with 10 CFR 50.72(b)(2)(xi) for notification of a fatality of an employee. Station personnel intend to notify OSHA of the individual fatality. "At approximately 0629 [EDT] on July 8th, 2015, Control Room personnel received an emergency call requiring station medical first responders. The individual was transported offsite via ambulance. The site has been notified of the individual fatality. The fatality was due to an apparent personal medical issue and not work related. The individual was not contaminated. "A press release is not planned at this time. The NRC Resident Inspector has been notified." The individual was inside the Protected Area but not within a Radioactive Control Area. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-07-08
51206 | 0 | CRANE NUCLEAR, INC. |  |  |  |  | 2015-07-07 | 2015-07-08 07:49 | 2015-08-10 | PART 21 INTERIM REPORT - NOTIFICATION OF PRESSURE SEAL VALVE YOKE MATERIAL COMPLIANCE The following information was received via fax: "This letter provides interim notification of Crane Nuclear's investigation into ASME Boiler and Pressure Vessel [B&PV] Section Ill Code design Pressure Seal Valve orders for yokes with integral hubs acting as retaining rings. The information required for this notification is provided below: "(i) Name and address of the individual or individuals informing the Commission. Jason Klein Sustaining Engineering Manager Rosalie Nava Director Safety and Quality Crane Nuclear 860 Remington Blvd Bolingbrook, IL 60440 "(ii) Identification of the basic component supplied for such facility or such activity within the United States which may fail to comply or contains a potential defect This is an interim report. Crane Nuclear is currently investigating Pressure Seal Valve orders potentially having misclassified material and non-destructive examination requirements for Yokes with integral hub retaining ring designs. The material requirements are specified per Crane Procedure 03-107 which utilizes ASME B&PV Code Case N-62-7 as guidance for material classification. "(iii) Identification of the firm supplying the basic component which fails to comply or contains a defect. Crane Nuclear 860 Remington Blvd Bolingbrook, IL 60440 "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. Crane Nuclear 'Classification of Valve Parts', Procedure 03-107, is guidance for appropriate material and NDE requirements for processing valve and valve part orders. The procedure is based on the ASME Code Case N-62-7. A yoke incorporating a threaded hub should be treated in the same manner as a threaded retaining ring requiring the material to be purchased Safety Related, ASME B&PV Section II, Part D materials, and required NDE (reference Category 3 valve items per N-62-7). Yokes with integral hubs acting as retaining rings may have been processed to material requirements without required CNI Classification per Procedure 03-107. "(v) The date on which the information of such defect or failure to comply was obtained. Crane Nuclear Engineering initiated investigation correspondence to Crane Nuclear Director of Safety and Quality via email correspondence dated Feb 20th, 2015. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. Crane has yet to determine the extent of Pressure Seal Valve designs sales order numbers (SO#) affected prior to 2001; the following Utility and Sites were supplied non-compliant CNI Procedure 03-107 Classification yokes for the following valve assemblies: 1. CNI SO# 24237-01, TVA, Browns Ferry, P.O. 00031943 - Quantity shipped = 1, Chapman, 8 [inch], Figure L953, Class 900, ASME Class 2, 95 Ed., 96 Add., no N stamp 2. CNI SO# 39501ú01, Georgia Power, Hatch, P.O. SNG10016537 - Quantity shipped = 3, Crane, 3 [inch], Figure 776U, Class 600, ASME Class 3, 71 Ed., W71 Add. 3. CNI SO# 39745-01, Southern California Edison, San Onofre, P .0. 4500456451 - Quantity Shipped = 1, Aloyco, 4 [inch], Figure N5247PSB, Class 900, ASME Class 3, 71 Ed., S73 Add. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. Crane Nuclear has completed sales orders search of Pressure Seal Valve designs with integral retaining ring hubs from 2001 to present identifying a total of 25 orders where three orders are impacted, as identified in part iv of this report (see above). Crane Nuclear is currently investigating sales orders previous to 2001, which will require an additional 30 days to complete (estimated completion date, August 6th, 2015). Corrective action by Crane Nuclear is to review documentation of supplied material to determine if yokes can be recertified as currently supplied. A revision to Crane Nuclear Procedure 03-107 to add figures reflecting configurations, and clarify classifications with applicable training, is in-process. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. Crane Nuclear is notifying sites affected and are developing a plan to address the valve items. "(ix) In the case of an early site permit, the entities to whom an early site permit was transferred. Not applicable. "Should you have any questions regarding this matter, please contact Jason Klein, Sustaining Engineering Manager at (630) 226-4953 or Rosalie Nava, Director of Safety and Quality at (630) 226-4940." * * * UPDATE FROM JASON KLEIN TO JOHN SHOEMAKER AT 1802 EDT ON 8/10/15 * * * The following excerpted information was received via fax: "Crane Nuclear has completed the sales orders search of the ASME Section Ill Code Pressure Seal Valve designs with retaining rings from 1992 to present. Crane Nuclear identified a total of 112 orders that required review. Of these orders, two orders were supplied with non-compliant retaining ring material for the valve assemblies. The orders are as follows: 1. Walworth's Supplied Order #PP37653, Dominion, Millstone. 2. CNI SO# 32634-01, Dominion, Millstone. "Corrective action being taken by Crane Nuclear is training held for engineers involved in classification of components, completed 8/10/15. Revise Procedure 03-107 to add figures reflecting configurations and clarify classifications 8/24/15. Revise assembly drawings to correct item identification as pressure retaining material, recertify ASTM material as ASME, and provide corrected documentation 8/28/15. "Should you have any questions regarding this matter, please contact Jason Klein, Sustaining Engineering Manager at (630) 226-4953 or Rosalie Nava, Director of Safety and Quality at (630) 226-4940." Notified R1DO (Powell), R2DO (Masters), R3DO (Orlikowski), R4DO (Hagar), and PART 21/50.55 REACTORS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-07-08
51205 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-07-08 01:30 | 2015-07-08 07:04 | 2015-07-08 | SEISMIC MONITOR INOPERABLE "At 0130 [CDT] on 7/8/15, the seismic monitor was found inoperable. The seismic monitor was inoperable such that emergency classification at the Alert level could not be obtained with site instrumentation. The seismic monitor was restored to operable status within 11 minutes. "The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-07-08
51204 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2015-07-03 16:30 | 2015-07-07 17:01 | 2015-07-07 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was received from the State of Mississippi by email: "Location of Incident: Brandon, Mississippi, I-20 exit ramp 56 construction. "Description of Incident: July 3, 2015 at approximately [1630 CDT], a Humboldt Model 5001 portable nuclear moisture density gauge, Serial Number 3339, was run over by a heavy equipment truck while on a jobsite. The gauge was severely damaged, but the sources remained intact and in shielded position. DRH [Mississippi Division of Radiological Health] was notified and provided with a survey measurement of 8mR/hr at the surface of the damaged gauge. The RSO was able to safely load the fragmented gauge back into its approved transport case and return it to the MDOT [Mississippi Department of Transportation] storage facility. DRH personnel visited the MDOT storage facility and observed an 8mR/hr surface survey reading with an NDS ND-2000 survey meter, serial number 24562, calibration date 7-1-2015. Leak test wipes were taken from both sources and sent for analysis by the licensee. The measured activity was well below the regulatory upper limit of .005 microcuries. Wipe analysis was received 7-7-2015. Gauge is being returned to the manufacturer for disposal." Radioisotopes: Cs-137(11 mCi); Am-241/Be(44 mCi). Radiation measurements taken by the Mississippi Division of Radiological Health: 8 mR/hr at surface; Less than 1 mR/hr at 1 meter. Mississippi Event: MS-15001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2015-07-15
51203 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-07-06 | 2015-07-07 16:20 | 2015-07-07 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER The following information was received from the State of Texas by email: "On July 7, 2015, the Agency [Texas Department of State Health Services-Radiation Branch] was notified by the licensee's radiation safety officer (RSO) that the shutter on a Ronan GS-400 level gauge containing a 50 millicurie cesium - 137 source was stuck in the open position. The stuck shutter was discovered during the start up of a system component. Open is the normal position for the shutter. The gauge does not possess an exposure risk to any individuals. The manufacturer has been contacted and will replace the gauge. Additional information on this event will be provided as it is received in accordance with SA-300." Texas Incident: I-9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-07-15
51202 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-07-07 14:35 | 2015-07-07 16:07 | 2015-07-07 | SECONDARY CONTAINMENT PRESSURE BOUNDARY VACUUM NOT MAINTAINED WITHIN SPECIFICATIONS "On 7/7/2015 at approximately 1435 EDT, the Technical Specification for Secondary Containment Pressure Boundary was not met when vacuum could not be maintained greater than or equal to -0.125 inches of water gauge for approximately 41 seconds. As part of post-maintenance testing for the non-safety related Reactor Building HVAC Center Exhaust Fan, the fan was started while the safety-related Standby Gas Treatment system was also in operation. Shortly after the fan was started, operators observed degrading vacuum in secondary containment and subsequently secured the center exhaust and supply fans. Vacuum continued to degrade momentarily after the fans were secured, and then returned to a Technical Specification allowable value. "Subsequent inspections discovered that the affected fan was operating in the reverse direction. This is believed to have caused Secondary Containment pressure to increase. "Since vacuum could not be maintained with the safety-related Standby Gas Treatment system operating, the plant operated in an unanalyzed condition. "The cause of the reverse rotation is under investigation. There were no radiological releases associated with this event. "The NRC Senior Resident Inspector has been notified." * * * UPDATE FROM CHRIS ROBINSON TO VINCE KLCO ON 7/7/2015 AT 2153 EDT* * * "Based on plant configuration at the time of the event and further review of the Fermi 2 UFSAR, the plant did not operate in an unanalyzed condition. The Reactor Building HVAC fans would have tripped, as designed, upon receipt of a safety-related Standby Gas Treatment actuation signal during the time of the event. Therefore, the fans' pressurizing effect on secondary containment would have ceased within the time limits assumed in the existing accident analysis. "The reporting criteria of 10CFR50.72(b)(3)(v)(C) remains valid." The licensee notified the NRC Resident Inspector. Notified the R3DO (Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-07-07
51201 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-07-06 14:20 | 2015-07-06 20:41 | 2015-07-06 | POSTULATED MULTIPLE SPURIOUS OPERATIONS SCENARIO THAT COULD ADVERSELY IMPACT POST-FIRE SAFE SHUTDOWN "A recent review of Fire Protection and Post Fire Safe Shutdown (PFSS) Programs at Columbia Generating Station (CGS) identified a potential unanalyzed condition with Multiple Spurious Operation (MSO) Scenario 2x. "Review of the circuit design for High Pressure Core Spray (HPCS) HPCS-V-10, HPCS-V-11 and HPCS-V-15 identified that fire-induced circuit failure (hot shorts) on the OPEN function control circuits for each valve would create the flow path to potentially drain inventory from the suppression pool (SP). The normal operation of HPCS-P-3 (keep-fill pump) would allow additional inventory from the SP to be transferred to the CSTs [Condensate Storage Tank]. If a fourth hot short is postulated, HPCS-P-1 would transfer inventory from the SP to the CST at a much faster rate. "HPCS-V-11 was deactivated on 6/12/2015 due to a maintenance repair issue and will be left in the fully closed position. This plant alignment resolves current concern for MSO scenario 2x as fire-induced circuit damage cannot cause spurious opening of HPCS-V-11. However, with an incomplete analysis for MSO scenario 2x, compliance with PFSS MSO requirements would have been challenged from the completion of the MSO project (October 2012) up to June 2015. "CGS is reporting this event as an unanalyzed condition in conformance with 10 CFR 50.72(b)(3)(ii)(B). Further analyses are being implemented to confirm the condition and to develop appropriate remedial actions." The licensee will notify the NRC Resident Inspector. | 64 | 0 | 0 | 64 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-07-06
51200 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2013-06-14 | 2015-07-06 15:52 | 2015-07-06 | AGREEMENT STATE REPORT - BRACHYTHERAPY TONGUE LOW DOSE RATE IMPLANT RESULTED IN OVERDOSE TO SKIN The following report was received from the Kentucky Department of Health via facsimile: "Brachytherapy LDR [low dose rate] tongue implant was loaded with thirty 1.12 mCi lr-192 sources on 6/13/13 by attending radiation oncologist. On 6/14/13 at [0730] [CDT] another physician rounded on the patient and all catheters and sources were in the proper position. At [1000] nursing on 6 East changed bedding of patient. At [1230] attending radiation oncologist rounded on patient and discovered one of the strands of sources (5 sources total) was no longer in the catheter. Physician removed nursing personnel and himself from the room and notified Physics. A Geiger counter was used to survey the room and a hot area was found in the linen basket. The linens were surveyed individually and the source was found. At [1245] the sources were reinserted into the proper catheter. Dosimetry was done to compare the plans and the deviation was well below the 20% reportable levels and almost indiscernible on the DVH [Dose Volume Histogram]. "During an inspection of the medical broad scope license, RHB [Kentucky Radiation Health Branch] reviewed the above procedure and inquired as to the dose potentially received by healthy tissues, namely the skin, assuming worst the case scenario. Specifically, the lr-192 strand displaced from the catheter actually lay against the patient's skin in one location for the whole 2 hours and 15 minutes between the time the physician last saw the strand in place and the time the patient's bed linen were changed. Based on this unrecognized worst case scenario, the RSO performed a dose calculation to the patient's skin and determined the patient may have potentially received a dose of 51.75 rem to the skin at a location which was not anticipated to receive any appreciable dose had the strands remained in place. A dose of 51.75 rem exceeds the limit requiring the report and notification of the Medical Event. A dose to the skin or an organ or tissue other than the treatment site that exceeds by five-tenths (0.5) Sv (fifty (50) rem) to an organ or tissue and fifty (50) percent or more of the dose expected from the administration defined in the written directive. The RSO at U of L [University of Louisville] e-mailed RHB a copy of the Medical Event report on July 6, 2015 at [1446]. Upon receipt of an email to the Radiation office the required 24 hour notification is made to the NRC Headquarters Operations Officer. "The physician was notified of this potential medical event at the time of the inspection. The patient had follow up visits during and after the course of 6/14/13 treatment and was not found to be necessary to notify them of this potential event since no effects to the patient were noted." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2015-07-14
51199 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2015-07-02 13:30 | 2015-07-03 14:04 | 2015-07-03 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following report was received from the New York State Department of Health via facsimile: "On 7/2/15, at 1330 EDT, the Radiation Safety Officer (RSO) of Applus RTD USA Inc., called the New York State Department of Health to report that they had a source disconnect of an industrial radiography camera at a temporary jobsite in Wellsville, New York. They were taking images of a pipeline using an QSA Global Model: 880 Delta with an 80 curie Iridium source. The radiography team secured the area by extending the barricades and keeping 100% visual surveillance of the area. Applus RTD is not approved per the license to perform source retrieval. Applus contracted with another NYS licensee authorized to perform the source retrieval. Applus's RSO and the retrieval personnel arrived on site at 1715 EDT and the source was secured at 1815 EDT. "According to the RSO, no person of the general public was ever in danger of receiving a dose above the legal limits." New York State Event Report ID No.: NYDOH-15-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-07-13
51198 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2015-07-02 08:30 | 2015-07-02 10:54 | 2015-07-02 | INADVERTENT EMERGENCY SIREN ACTUATION "This event is being reported in accordance with 10CFR50.72(b)(2)(xi). "On July 2, 2015, at approximately 0830 EDT, an inadvertent actuation of the Perry Nuclear Power Plant's (PNPP) alert notification system occurred. Seventy-six of seventy-six sirens sounded for three minutes affecting the emergency planning zone in Ashtabula, Geauga, and Lake Counties. Following the actuation, county agencies received calls from members of the public. "PNPP's capability to notify the public in an emergency was not affected. The siren actuation was not related to any condition or event at the PNPP. An investigation is in progress to determine the cause of the inadvertent actuation. Preliminarily, it appears that the wrong test was initiated from a county agency; an audible test was initiated instead of a silent test. "At the time of the event, the plant was in Mode 1 at 100 percent rated thermal power. The public was informed of the inadvertent actuation by way of the Emergency Alert System (EAS). Additionally, social media was used to respond to social media inquiries. "The NRC Resident Inspector has been notified." The licensee notified the Ohio Emergency Management Branch Chief, and the County Emergency Managers of Ashtabula, Geauga, and Lake Counties. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-07-02
51197 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2015-06-24 08:00 | 2015-07-01 17:05 | 2015-07-02 | AGREEMENT STATE REPORT - TWO POTENTIALLY LOST IODINE-125 SEEDS The following information was obtained from the State of Arizona via email: "At approximately 0800 [MST] on July 1, 2015, the licensee reported that two (2) 0.256 millicurie Iodine-125 seeds were potentially lost on June 24, 2015. The licensee stated that while implanting 84 I-125 seeds into a patient in the operating room, the doctor realized that one of the syringes, which was supposed to have two (2) I-125 seeds in it, was empty. The licensee surveyed the entire operating room and hot lab but did not locate the seeds. The manufacturer was also contacted in an attempt to see if the syringe was shipped to the licensee without the seeds in it. "The Agency [Arizona Radiation Regulatory Agency] is investigating the event. "The Governor's Office is being notified of this event." Arizona First Notice: 15-012 * * * UPDATE ON 7/2/15 AT 1741 EDT FROM BRIAN GORETZKI TO JEFF HERRERA * * * The following update was provided by the Arizona Radiation Regulatory Agency via email: "On July 2, 2015, the two lost seeds were discovered to be actually implanted into the patient. After a review of the new CT scan, the licensee was able to identify that all 84 seeds were in the patient." Notified the R4DO (Okeefe) and NMSS Events (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2015-07-09
51196 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-06-01 | 2015-07-01 16:43 | 2015-07-01 | COLORADO AGREEMENT STATE REPORT - RADIUM-226 DISCOVERED AT SCRAP YARD The following information was obtained from the State of Colorado via email: "The Colorado Radiation Program [CRP] is investigating an incident at 711 S. 6th Ave. in Grand Junction, CO. A number of weeks ago, we [CRP] were asked to investigate a crushed car that was rejected at a scrap yard because it set off the radiation detector. Yesterday, [CRP] found in the car, a metal plate approximately 1.5 ft. long, 5 inches wide and less than a half an inch thick that contains Radium-226. The readings on contact with this piece of metal are higher than what our instrument could read which means it's an unknown amount, over 200 mr/hr. Last night, the item was placed in a locked room in a warehouse on the property with no one around it and [CRP] instructed the property owner to not let anyone near it. "Today, the Colorado Civil Support Team is responding to the site to verify the isotope and try to determine the dose rate and activity. Additionally, they will help secure the source on site." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-07-09
51195 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2015-05-04 20:27 | 2015-07-01 10:39 | 2015-07-01 | INVALID AUXILIARY FEEDWATER ACTUATION SYSTEM PARTIAL ACTUATION "On May 4, 2015 with Unit 1 in Mode 1 at 100 percent power, during performance of the 'A' channel Auxiliary Feedwater Actuation System (AFAS) monthly functional test, an invalid 'A' channel AFAS actuation occurred. The monthly functional test resulted with AFAS-1 in a half trip condition. Due to a poor contact on a manual actuation switch, a pathway was dropped out causing the partial AFAS actuation to occur. The faulty mechanical switch was replaced and the post maintenance testing was satisfactory. "The partial AFAS actuation resulted in the successful start of 'A' AFW electric driven pump and the opening of its motor control valve, feeding the 'A' steam generator. The system responded to the invalid actuation as designed. "In accordance with 10 CFR 50.73(a)(1), this notification of the invalid actuation is provided in lieu of a written LER." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-07-01
51194 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-06-30 16:35 | 2015-06-30 20:05 | 2015-06-30 | OFFSITE NOTIFICATION DUE TO AN INJURED EMPLOYEE TRANSPORTED TO HOSPITAL "This notification is being made in accordance with NUREG-1022, Event Report Guidelines 10 CFR 50.72 and 50.73 Section 3.2.12, News Release or Notification of Other Government Agency. "On June 30, 2015 at 1256 [CDT] an employee was injured while conducting a work activity and a non-contaminated hospital transport was completed. "29 CFR 1904.39(a) requires a report to the Occupational Safety and Health Administration (OSHA), US Department of Labor within twenty four (24) hours after the in-patient hospitalization of one or more employees as a result of a work-related incident. At 1635 CDT, it was determined that this is a 24-hour OSHA reportable occurrence." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-06-30
51193 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2015-06-30 14:00 | 2015-06-30 16:41 | 2015-06-30 | AGREEMENT STATE REPORT - PORTABLE MOISTURE/DENSITY GAUGE DAMAGED The following information was received from the Commonwealth of Virginia via email: "On June 30, 2015 at about 1400 EDT, the Virginia Radioactive Material Program (VRMP) received a telephone report from the Radiation Safety Officer (RSO) that a moisture/density gauge was damaged. While performing testing at a temporary jobsite in Manassas, the moisture/density gauge (CPN, Model: MC1, Serial # MD90104762, Cs-137 (9 mCi), Am-241 (44 mCi)), was hit by the subcontractor's equipment at the project site and resulted in damage to the control rod. The RSO stated that the sources were in the shielded position and the shielding integrity was not damaged. A survey of the gauge was performed by the licensee and reading observed was 2 mrem/hr on contact. The gauge was packaged and returned to the office where a wipe test was taken and the analysis will be performed by the manufacturer/distributor. There was no public health and safety threat from this incident. VRMP will review the licensee's report for corrective actions. "Event Report ID No.: VA-15-10" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2015-07-08
51192 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2015-06-29 | 2015-06-30 12:17 | 2015-07-07 | AGREEMENT STATE REPORT - MISSING RADIOACTIVE MATERIAL IN TRANSIT The following information was received from the Commonwealth of Massachusetts via email: "Worcester Polytechnic Institute reported on 6/30/15 that a shipment of one Selenium-75 (1 curie) and two Ytterbium-169 (1.76 curies together) brachytherapy sealed sources arrived as an empty package (no radioactive material was within the package). The received Yellow-II labeled cardboard package was visibly damaged and resealed with clear shipping tape. Survey of the received package determined background radiation readings. Carrier, shipper and various government agencies have been contacted. Search for missing items is ongoing. Radiation from the unshielded sources expected to be approximately 1 R/hr at one meter distance. Agency [MA Radiation Control Program] to perform on-site investigation in Worcester today ." HOO NOTE: Also reported by the common carrier to the National Response Center on 6/29/15 [Incident Report # 1121358] and by the State of Louisiana [EN # 51191]. * * * UPDATE ON 7/2/15 AT 1149 EDT FROM ANTHONY CARPENITO TO JEFF HERRERA * * * The following update was received from the Massachusetts Radiation Control Program via email: "Agency [Massachusetts Department of Public Health - Radiation Control Program] (MADPH-RCP) conducted investigation at receiving licensee facility on 6/30/15. Agency also conducted radiation surveys on 7/1/15 at the three carrier facilities in Massachusetts through which the package passed. No sources were identified and all radiation readings were at background levels. The three sources have been described by shipper as titanium capsules approximately 5 mm long and 1 mm diameter. Each source may still be individually contained within an approximate 1.5 inch tall glass vial with teal-colored plastic screw-on cap, each vial with white label taped to outside of vial describing the contents. The receiving licensee ordered a 0.2 curie Se-75 source (same physical description) and it is unknown at this time which Se-75 activity amount (0.2 or 1 curie) was shipped." Notified the R1DO (Dimitriadis), ILTAB (Johnson) and NMSS Events (via Email) * * * UPDATE ON 7/7/15 AT 1616 EDT FROM JOSHUA E. DAEHLER TO JEFF HERRERA * * * The following update from the Massachusetts Radiation Control Program was sent via email: "The shipper (i.e. SPEC) provided clarification that, contrary to the activities identified in shipping papers, one Yb-169 source was actually approximately 1.74 curies, another Yb-169 source was actually approximately 1.77 curies and the third source, Se-75 was approximately 207 millicuries. The sources continue to be missing." Notified the R1DO (Cahill), ILTAB (Johnson) and NMSS Events (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-07-08
51191 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-06-29 15:04 | 2015-06-30 11:41 | 2015-07-07 | AGREEMENT STATE REPORT - MISSING SHIPPED SOURCES The following information was received from the State of Louisiana via email: "On June 25, 2015, Source Production & Equipment Company shipped [using a common carrier] three sources to Worcester Polytechnic Institute (WPI), . . . , [in] Worcester, MA 01609. The three sources were two Yb-169 for total activity of 65 Gbq (1.75 Ci) and one Se-75 37 Gbq (1 Ci). The package arrived at WPI damaged. The lead pig container did not have the three sources. There are no source serial numbers. The State of Massachusetts and [the common carrier] have been notified. State of Massachusetts stated that they have contacted the FBI. "Event Report ID No.: LA150011" HOO NOTE: Also reported by the common carrier to the National Response Center on 6/29/15 [Incident Report # 1121358] and by the Commonwealth of Massachusetts [EN # 51192]. * * * UPDATE FROM JAMES PATE TO JEFFREY HERRERA ON 7/7/2015 AT 1400 EDT * * * After discussion between Louisiana and Massachusetts, The State of Louisiana considers their event (LA150011) to be closed out. The Commonwealth of Massachusetts (NRC Event Number #51192) is continuing their investigation. Notified R4DO (Haire), ILTAB (Johnson) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-07-08
51190 | 0 | ABB, INC. |  |  |  |  | 2015-06-29 | 2015-06-29 17:16 | 2015-06-29 | PART 21 NOTIFICATION OF DEVIATION REGARDING COM-5 PROTECTIVE RELAY DEFECTIVE FRAME ASSEMBLY The following information was provided by ABB via fax: "This letter provides notification of a deviation for Class IE COM-5 (Long Time Overcurrent Relays) styles 1326D81A01, 1326D81A02, and 326D81A09. "On April 30, 2015, ABB received a customer complaint regarding a COM-5 relay received with a bracket (ABB Part Number #3518A17H01) detached from the relay frame assembly (ABB Part Number #1456C92G01). "ABB's investigation determined that the bracket, which is spot-welded to the frame, can be detached from the frame using a relatively small amount of force. If the weld fails, the Indicating Contactor Switch (ICS) unit held by the bracket could inadvertently close, causing a false trip. The affected frame assemblies were manufactured by ABB on 9/25/2014 (Lot#: 45001414115) by an operator who incorrectly followed the inspection procedure required to verify the integrity of the resistance spot welds. "ABB records show a total of 11 suspect relays were provided to two customers as detailed in attachment 1 [BELOW]. "ABB does not have the capability to perform the evaluation to determine if a defect exists, thus we are notifying the purchasers or affected licensees of this determination so that they may evaluate the deviation, pursuant to 10 CFR 21.21(b). "ABB recommends that the affected licensees evaluate their specific application and determine whether the deviation described in this notice affects their design basis. If it is determined that it does, the licensees should contact ABB to determine appropriate corrective action. ABB is conducting the following actions: - ABB has improved existing inspection processes used to verify resistance spot welds. - ABB has performed an extent of condition evaluation and determined that this issue is limited to this process. "If you have any questions regarding this notice, please contact ABB Technical Support at +1-954-752-6700 or+ 1-800-222-1946 "Very truly yours, "Dennis Batovsky - Managing Director "ATTACHMENT 1 "Customer List for 1326D81A01, 1326D81A02 and 1326D81A09 COM-5 Relays "Exelon Business Services Corporation, Chicago, IL - Clinton Nuclear Station "ORDER / CUSTOMER PO / DATE / STYLE / SERIAL NO. / QTY "ENW0716 / 00531032 Rev 001 / 9-26-2014 / 1326D81A01 / 12910-12912 / 3 "ENW0742 / 00541813 Rev 002 / 3-3-2015 / 1326D81A01 / 12938, 12939 / 2 "Westinghouse Electric Corporation, New Stanton, PA "ORDER / CUSTOMER PO / DATE / STYLE / SERIAL NO. / QTY "VEP10980 / 4500653421 Rev 1 / 12-8-2014 / 1326D81A02 / 12928, 12929 / 2 "VEP10976 / 4500653398 Rev 1 / 12-8-2014/1326D81A02 / 12925-12927 / 3 "VEP11168 / 4500657304 rev 1 / 1-20-2015 / 1326D81A09 / 12919 / 1" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-06-29
51189 | 0 | MALLINCKRODT PHARMACEUTICALS |  |  |  |  | 2015-06-19 | 2015-06-29 14:45 | 2015-06-29 | LOST SHIPMENT OF I-123 On 06/8/15, a shipment of I-123, 1.4 mCi, used for diagnostic imaging, was shipped from the Mallinckrodt Maryland Heights, MO facility for overnight delivery via highway carrier to a company located in Baltimore, MD. The material was not received in Maryland as scheduled. The shipper, carrier and customer performed searches. The shipper concluded that the material was missing as of 6/19/15. The half-life of I-123 is 13.3 hours. The licensee will submit a written report within the 30 day requirement. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-07-07
51188 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2015-05-15 | 2015-06-29 12:56 | 2015-06-29 | AGREEMENT STATE REPORT - MISSING STATIC ELIMINATOR The following information was received from the State of Illinois via email: "By letter received on June 23, 2015, the registrant [Lakeland Plastics] advised [the Illinois Emergency Management Agency] that a static eliminator provided to them under general license is missing although believed to be still at their facility. The device was received on May 22, 2014 for use with special projects to control dust. When the lease for the device came up for renewal a year after its initial receipt, it was discovered to be missing. It was last used in March of this year. Efforts have been underway since June 11, 2015, to locate the device. The registrant indicates that a new and more rigorous check out procedure has been developed to prevent future recurrence of this event for its other static eliminator. The current activity of the missing item is 1.4 milliCi. Given the age, form, and design of the static eliminator, no exposure to employees or the public is suspected. This item will remain open for the required time until the source is declared as lost or is recovered. "Radionuclide: Po-210 "Activity: 0.0014 Ci [1.4 milliCi] or 0.0518 GBq "Manufacturer: NRD, Inc. "Model Number: P-001 "Serial Number: A2JX845 "IL Report ID: IL15014" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2015-07-07
51187 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-06-28 09:00 | 2015-06-28 11:24 | 2015-07-08 | CONTROL ROOM ENVIRONMENTAL BOUNDARY DOOR FOUND UNLATCHED "During Security checks of Control Room doors, a boundary door was found not latched. This door is capable of being manually closed and latched. The door was in this condition for 4 hours and 25 minutes. The door is currently closed and latched. This is being reported as it could have prevented the fulfillment of a safety function to mitigate the consequences of an accident per 10 CFR 50.72(b)(3)(v)(D)." The NRC Resident Inspector has been notified. A condition report has been written and the door is posted to require manual checks to ensure it is latched until the door closing mechanism is repaired. * * * RETRACTION FROM THOMAS CLEARY TO VINCE KLCO ON 7/8/2015 AT 1314 EDT * * * "Event Report number 51187 describes a condition at Millstone Power Station Unit 2 (MPS2) in which a control room environmental boundary door was found unlatched. This was reported in accordance with 10CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function to mitigate the consequences of an accident. "Upon further review, MPS2 has concluded that there was no loss of safety function, because even with the control room boundary door unlatched, the control room emergency ventilation system would have been able to perform its safety function during accident conditions. The MPS2 control room is pressure neutral and the hydraulic door closure mechanism was verified adequate to ensure the door would close and remain closed during accident conditions (even though it was not latching). Therefore, this condition is not reportable and NRC Event Number 51187 is being retracted. "The basis for this conclusion will be provided to the NRC Resident Inspector." Notified the R1DO (Cahill). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-06-28
51186 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-06-27 11:00 | 2015-06-27 13:19 | 2015-06-27 | OFFSITE NOTIFICATION MADE AFTER PORTABLE TOILET TIPPED OVER "On 6/27/2015 at 1100 EDT, a spill to the environment was determined to be reportable to the state environmental and local health agencies. A press release is planned. "The spill occurred when a portable chemical toilet tipped over and was identified at approximately 0925 EDT. The contents and exact quantity of the spill are unknown, but the toilet has a capacity of 60 gallons. The spill flowed to nearby gravel and two storm drains, one of which discharges to navigable state waters. Rainfall was present when the spill was identified. Cleanup efforts are in progress. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-06-27
51185 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2015-06-26 23:35 | 2015-06-27 07:16 | 2015-06-27 | BOTH AUX FEEDWATER TRAINS DECLARED INOPERABLE "On June 26, 2015 at 2335 [EDT], with Auxiliary Feedwater (AFW) train 1 declared inoperable for scheduled surveillance testing, AFW train 2 was declared inoperable as a result of the supply breaker for SW1395, Service Water Loop 2 secondaries isolation valve, being found open, i.e. out of its required position. Limiting Condition for Operation (LCO) 3.7.5 Condition D was entered for two Emergency Feedwater trains inoperable. AFW train 1 and the non-safety related motor driven AFW pump were available to provide emergency feedwater if required. "The breaker was verified to be functioning as required and then closed, restoring the safety function. All associated LCOs were exited by 0133 [EDT] on June 27, 2015." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2015-06-27
51184 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2015-06-26 21:49 | 2015-06-27 06:40 | 2015-06-28 | SEISMIC MONITOR DECLARED NON FUNCTIONAL "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) as an event that will result in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g. significant portion of control room indication, Emergency Notification System or offsite notification system.) "The emergency preparedness plan requires seismic monitoring instruments to diagnose an earthquake for emergency action levels (EAL) HU6 (Natural or destructive phenomena affecting Protected Area) and HA6 (Natural and destructive phenomena affecting Vital Areas). "At 2149 CST on June 26, 2015, [the] ACS-8003 seismic monitor was declared non-functional due to having a fault light indicated on the C529 seismic cabinet. [The] ACS-8001 seismic monitor had previously been declared non-functional due to the same condition. With these 2 monitors out of service the seismic alarm capability is not available. ANO procedures provide compensatory measures of using offsite sources to obtain seismic data." The NRC Resident Inspector has been notified. * * * UPDATE ON 6/28/15 AT 1552 EDT FROM KENYON MCNEAILL TO DONG PARK * * * "On 6/28/15 at 1232 CDT, batteries have been replaced in ACS-8001 and ACS-8003 seismic monitors. Both monitors have been restored to a fully functional status. Seismic alarm capability is restored and Emergency Assessment Capability has been restored." The licensee will notify the NRC Resident Inspector. Notified R4DO (Campbell). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-27
51183 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-12-31 | 2015-06-26 10:28 | 2015-07-27 | AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following was received from the State of Nebraska via email: "On June 26, 2015, Gregg Young Chevrolet (GL0488) reported a loss of 10 exit signs containing tritium (Evenlite 201) via letter. Each sign originally contained 10.5 curies and current approximate activity is 3.852 curies. Our records show that the registrant possessed these signs in 2013 (latest inventory) however, the registrant assumes these signs were removed from their facility by a tenant sometime in 2008." * * * UPDATE FROM HOWARD SHUMAN TO VINCE KLCO ON 7/27/2015 AT 0916 * * * The following information was received from the State of Nebraska via email: "No additional information has been submitted. The NMED event is closed." Notified the R4DO (Warnick), ILTAB (Johnson) and NMSS Events Notification via email. NE Item Number: NE150002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2015-07-06
51182 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-06-25 22:00 | 2015-06-26 04:38 | 2015-06-26 | TWO REACTOR VESSEL LEVEL CHANNELS FAILED HIGH "At 2200 PDT during startup from refueling outage 22, it was discovered that both level instruments used in reactor protection system (RPS) trip system 'A' for initiation of a reactor scram on low reactor pressure vessel (RPV) level were observed to have failed high. This resulted in the inability to generate a full reactor scram on low level (+13 inches). All remaining RPV level indications demonstrated that level was being maintained within normal operating bands. This constitutes a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor. "The RPS trip logic at Columbia consists of two trip systems, RPS trip system 'A' and RPS trip system 'B'. There are two level instrument channels in each trip system. Columbia utilizes a 'one-out-of-two taken-twice' trip logic to generate a full scram signal. At least one channel in both trip systems must actuate to generate a full scram signal. With both level instruments in RPS system 'A' failed high, the RPS trip logic was unable to generate a full scram. "At 2246 [PDT] and in accordance with TS LCO 3.3.1.1 Condition C, a half scram was generated on RPS trip system 'A' to restore full scram capability. The cause of the failure of the two level instruments associated with RPS Trip system 'A' is under investigation." The level channels are being calibrated prior to changing to mode 1 (power operations). The licensee will notify the NRC Resident Inspector. | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2015-06-26
51181 | 0 | ELECTRIC POWER RESEARCH INSTITUTE |  |  |  |  | 2015-05-01 | 2015-06-25 15:40 | 2015-07-24 | PART 21 REPORT - DEVIATION IN NOZZLE MODELING INTERNAL REPORTS The following was received via facsimile: "[This report pertains] to a deviation in a basic product (EPRI nozzle modeling internal reports) supplied by EPRI (Electric Power Research Institute) regarding Westinghouse Pressurizer Head Nozzle Inner Corner Region Ultrasonic Inspections. EPRI will complete all evaluation efforts and provide a determination of reportability in accordance with 10 CFR Part 21 no later than July 24, 2015. "EPRI has conducted an evaluation to the basic product's actual use and determined that the ASME examination volume coverage for at least one of the pressurizer nozzles has changed and is now 90 percent or less. A 90 percent threshold is required by ASME Boiler & Pressure Vessel Code, Section XI. "Design inputs used in EPRI modeling for ultrasonic scanning coverage for nuclear safety related component nozzles may have been inaccurate. In some cases, the upper and lower heads of Westinghouse pressurizers can be offset from the center of each nozzle (spray, safety, relief, surge). This offset results in a change in the thickness of the pressurizer head as compared to an on-axis pressurizer head with the same radial dimensions. Some of the computer models EPRI used to describe these pressurizer heads did not account for an increase in the thickness due to these offsets. As a result, in some cases the ultrasonic inspection parameters produced by these computer models may have produced inaccuracies in the examination volume coverage calculations. "In the case of a basic component which contains a defect or falls to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. Utility Name/Plant Name Exelon Corporation / Ginna First Energy Nuclear Operating / Beaver Valley 1 Entergy / Indian Point 2 Entergy / Indian Point 3 Pacific Gas & Electric Co. / Diablo Canyon Unit 2 Dominion Generation / North Anna "EPRI has reviewed the pressurizer upper and lower head drawings for the nozzles that it has modeled and determined if these offsets are present. For those cases that are potentially affected EPRI has recalculate the new examination volume coverage for the nozzle inspection detection techniques and provided this information to the corresponding licensees. "EPRI staff shall develop a matrix or table to better define the necessary design inputs for computer modeling of nozzles. This should also include a question to the utility regarding any obstructions or thickness changes which would impact the ultrasonic inspection parameters. EPRI staff shall improve its documentation for review and approval of design inputs for computer modeling. Consideration shall also be given to including a review of design inputs by the member along with an acknowledgement from the member that the design inputs are appropriate for use. EPRI staff shall consider methods of including additional conservatism to the modeling results to better accommodate changes which may be observed in the field. The project quality plan and quality project instruction shall be updated as necessary to accommodate or clarify these improvements. Completion commitment date - 10/27/2015. "The coverage calculations indicated in the notification letters would likely increase if the EPRI modeled scan plans are exceeded and or if additional inspection angles were implemented. Conversely, these coverage calculations would likely decrease if physical field limitations prevented the ultrasonic probe from executing the EPRI modeled scan pattern. It is on this basis that recipients of this letter must evaluate the condition pursuant to 10 CFR Part 21.21 to determine if it could represent a substantial safety hazard reportable under 10 CFR Part 21." Potentially affected US plants include Ginna, Beaver Valley Unit 1, Indian Point Units 2 and 3, Diablo Canyon Unit 2, and North Anna. * * * UPDATE AT 0938 EDT ON 07/24/15 FROM NEIL WILMSHURST TO JEFF HERRERA VIA FACSIMILE * * * "As part of the evaluation, EPRI [Electric Power Research Institute] performed an 'extent of condition' review. During the course of the review, EPRI found that the above described deviation also affected EPRI nozzle modeling internal reports supplied by EPRI (Electric Power Research Institute) regarding Westinghouse Steam Generator Primary Nozzles. "After conducting the 'extent of condition' review, which included recalculation of the modeling data, EPRI concluded that there were no other known reportable conditions associated with this deviation. "EPRI has completed all evaluation efforts and issued reportability notification letters in accordance with 10CFR Part 21 within the respective reporting timeframes." Notified the R1DO (Kennedy), R2DO (Musser) and R4DO (Gepford) and Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 21.21(a)(2) |  |  |  | 0 | 2015-06-25
51180 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-06-25 08:30 | 2015-06-25 14:18 | 2015-06-29 | AGREEMENT STATE REPORT - LOST RADIOGRAPHY CAMERA DURING TRANSIT The following information was received from the State of Louisiana via email: "Event date and time: On 06/25/2015 [at 0930 CDT, the licensee Radiation Safety Officer] called the Radiation Section of LDEQ [Louisiana Department of Environmental Quality] to report a lost/missing radiography camera. The camera was to be loaded on a rig truck and [to] be transported to a temporary site. The crew and site RSO had been looking for the camera since it was discovered missing at 0830 [CDT]. "A radiography exposure device was left on the bumper of a rig truck and not secured in the vault/overpack on the truck. The crew left the yard on Highway LA #30 and headed to I-10 and then East on I-10. About 5 miles down I-10, the crew remembered that they had not secured the camera in the rig truck. They stopped and found the camera missing. They backed tracked I-10 to LA # 30 and back to the office. They did not locate the missing camera. The LA State Police was notified in addition to LDEQ. "The Radiation Section [of LDEQ] was notifying the staff and dispatching a Radiation [Environmental Scientist] individual to respond. The media put out an alert of the missing camera. Homeland Security, QSA Global, and the Ascension Parish Sheriff responded and were aiding in locating the lost camera. They were combing the area on ATVs and utilizing sensitive radiation detection instruments. "At about 1130 [CDT] the LDEQ was given an update by [the licensee Radiation Safety Officer] which only includes responding agencies and the Site RSO for contact. About 1150 [CDT] the NRC Region IV was notified of the incident (Latisha Hanson) and given a preliminary notification and told the [NRC Operations Center] was being notified. "Event Location: A rig truck was dispatched from TIS at 37568 Hwy # 30, Gonzales, LA down LA #30 to Interstate-10. The rig went east on I-10 for about 5 miles when the crew remembered that the camera had not been secured in the rig. The crew check the back of the rig and backed tracked the I-10 to LA #30 route. The camera was not located. Notifications were made. "Event type: Loss of control over an exposure device. A QSA 880 Delta exposure device S/N 4586. The exposure device was loaded with about 30 Ci of Ir-192, QSA source Model # 84-9. The Category II, Quantity of Concern was released or lost into the general public. The radioactive exposure device was released into the general public by the two individuals not following the TIS's [Team Industrial Services] Radiation Safety Procedures or the IC [Increased Controls] Security Procedures. The exposure device was released to the general public unsupervised and not in direct control of an authorized company representative. "Event description: The equipment was a QSA 880 Delta exposure device S/N D4586. The source was about 30 Ci of Ir-192, model # 84-9. At this time LDEQ consider this incident still open and updates will be given when available. "Transport Vehicle: This was a TIS company crew truck being dispatched to a temporary jobsite. "Media attention: News Media was alerted and reporting agencies were notified." Louisiana Event: LA150010 Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, FDA(email), Nuclear SSA (email) FEMA National Watch Center (email), DNDO-JAC (email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf * * * UPDATE ON 06/29/2015 AT 1356 EDT FROM JOE NOBLE TO STEVEN VITTO * * * The following information was received from the State of Louisiana via email: "The exposure device was recovered at about 7:00pm [CDT] on 06/25/2015. "Device QSA/AEA Technologies, Model Delta 880, S/N 4586 Source QSA/AEA Technologies, Model A424-9, S/N 166306; 48.2 Ci Ir-192 "Recovered [approximately] 1.5 [Miles] on LA 61 east of US I-10 east. It was on the side of the road in a wet-muddy ditch area. [The device was found] by backtracking the trucks GPS device. "A health and safety survey was conducted and the shielding appeared to be intact. "The exposure device was loaded on to another Team Industrial vehicle, blocked and braced, and returned to the vault at the highway LA-30 address. "The device and source were leak tested and analysis was performed on the test. A QSA Global representative stated it appears the device (DU) and the Ir-192 source were not leaking or compromised. "With the exception of corrective actions and enforcement issues the department, LDEQ [Louisiana Department of Environmental Quality], considers this incident closed." Notified R4DO(O'Keefe), IRD MOC(Grant), ILTAB (Wray), and NMSS Events Resource (via email). Notified DHS SWO, FEMA, USDA, HHS, DOE, DHS NICC, EPA, FDA(via email), Nuclear SSA (via email) FEMA National Watch Center (via email), DNDO-JAC (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-07-03
51179 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-06-25 03:01 | 2015-06-25 09:27 | 2015-06-25 | SECONDARY CONTAINMENT PRESSURE INCREASE DUE TO VOLTAGE TRANSIENT "At approximately 0301 [CDT] on 6/25/15, the Main Control Room received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) caused by a voltage transient on the 138 kV feed due to thunderstorms in the area. The Division 1 Safety Bus was manually aligned from the reserve source to its normal source. As a result of the voltage transient, the Division 1 Fuel Building Ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no running VF fans, secondary containment differential pressure rose to slightly greater than 0 inches water gauge and which exceeded the Technical Specification requirement of greater than 0.25 inches vacuum water gauge. The Control Room entered EOP-8, Secondary Containment Control. This event is being reported as a condition that could have prevented fulfillment of a safety function under 10 CFR 50.72(b)(3)(v)(C). Secondary Containment differential pressure was restored within Technical Specification requirements at 0319 [CDT] by reopening the VF isolation dampers and restarting the VF supply and exhaust fans. The ERAT SVC was returned to service at 0457 [CDT]. "The NRC Resident Inspector has been notified." | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-06-25
51178 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-06-16 11:45 | 2015-06-24 19:29 | 2015-06-24 | UNANALYZED CONDITION DUE TO OPEN HIGH ENERGY LINE BREAK DOORS "On June 16, 2015 at 1145 EDT while in Mode 1 at 100% power steady-state conditions, two fire doors between the Reactor Auxiliary building (RAB) and steam tunnel were opened under administrative controls to support maintenance. These doors are credited in high energy line break equipment qualification and internal flooding analyses and opening of the doors is not addressed in the analyses. A high energy line break in the steam tunnel with the doors open could result in equipment in the RAB experiencing high temperature, pressure, or humidity beyond conditions analyzed for equipment qualification which has the potential to render redundant safety-related equipment inoperable. "The event was determined to be reportable on June 24, 2015 at approximately 1550 [EDT]. During that reportability evaluation, it was determined that the doors may have been in a similar condition multiple times in the May-June time frame. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition and in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident. "There was no adverse impact to public health and safety or to plant employees." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-06-24
51177 | 0 | NEW YORK STATE DEPT OF HEALTH |  |  |  |  | 2015-06-22 14:45 | 2015-06-24 14:48 | 2015-06-24 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE RUN OVER BY BULLDOZER The following was received from the State of New York via email: "On 6/23/15, at 0953 [EDT], the Radiation Safety Officer (RSO) of APPLUS RTD USA Inc., called The New York State Department of Health to report that on 6/22/15, a bulldozer ran over a Troxler Model 3440 Moisture Density Gauge, containing 8 mCi Cs-137 and 40 mCi Am-241/Be. This occurred at the University of Buffalo, South Campus in front of Clark Hall. From the RSO's description and the emailed photographs, the yellow casing was severely damaged on one side, the side farthest from the sources. The rod and source were not extended at the time of the accident. The East Region RSO for APPLUS RTD USA Inc. used a Teletector Model 6112M with an 8 foot arm while approaching the unit to ensure the sources were in the shielded position. No unusual radiation reading has been noted. The regional RSO secured the gauge in the transport container and it was transported back to the licensee's office for storage with 15 other Moisture Density Gauges. The RSO contacted MJW Technical Services for disposal of the damaged unit. The RSO of University of Buffalo has been notified. "This event is not a reportable event since the sources were in their shielded positions at the time of the incident. This event report is for informational purposes only." NYDOH - 15 - 05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-07-02
51176 | 0 | WASHINGTON STATE DEPT OF HEALTH |  |  |  |  | 2015-06-19 | 2015-06-23 19:53 | 2015-06-23 | AGREEMENT STATE REPORT - MEDICAL UNDER DOSE The following was received from the State of Washington via email: "This appears to be a medical event. Eleven Y-90 TheraSphere infusions were performed on eight patients. Five of the infusions involved the use of a smaller catheter, and for all five of these infusions the full dosage was not administered. This was determined when the nuclear medicine physician - who was the authorized user for all of the infusions - determined the percentage of dose delivered to the patient was less than 80 percent of the prescribed dose. The percentage of dose delivered calculation was performed in accordance with the procedure provided in the package insert. Waste for all five infusions was imaged using PET/CT and it was determined that a large amount of radioactive material was present at a hub in the catheter. The radiation safety officer was informed, who informed the hospital health physicist. The referring interventional radiology physicians were notified that the percentage of dose delivered was less than 80 percent, and that further investigations were underway. For these five infusions, the difference in prescribed dose and delivered dose for the organ (liver) exceeded 0.5 Sv; and the total dosage delivered differed from the prescribed dosage by 20 percent or more. The licensee is investigating this matter further and will provide a written report to the Washington State Department of Health within 15 days as required." WA Item # WA150003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2015-07-01
51175 | 0 | NC DEPT OF HEALTH AND HUMAN SVCS |  |  |  |  | 2015-06-23 09:30 | 2015-06-23 17:45 | 2015-06-23 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received via email: "[The State of North Carolina] is writing to provide notification of a stolen portable moisture/density gauge from a reciprocal license in NC [North Carolina]. Below are the current details: "The licensee is EAS Professionals, Inc. - SC [South Carolina] Radioactive Material License No. 849. They entered the state under an expired NC reciprocity approval. "The gauge was stolen 6/22/15 between 1700 [EDT] and 2230 [EDT] from a hotel parking lot in Greensboro, NC. Licensee contacted SC about the stolen gauge on 6/23/15 at about 0930 [EDT], SC immediately notified NC. "The stolen gauge is an InstroTek Model 3500, Serial Number 1360. Sources contained include 11 mCi of Cs-137 and 44 mCi of Am-241/Be. "The Greensboro Police Department was called by the licensee and performed an investigation that included taking fingerprints and looking for hotel surveillance footage. There was evidence that bolt cutters were used to free the case from the truck. Another note, there was a separate police report filed for a different vehicle break-in around the same time and hotel location. This suggests the thief did not target the radioactive gauge, but rather a perceived value in the locked up container. "NC notified various other local, state, and federal law enforcement agencies. "There is no mention of a press release at this time, but [The State of North Carolina] will encourage the licensee to publish a statement and possibly a reward to motivate the device's return. "Please do not hesitate to contact [The State of North Carolina] should you have additional questions. [The State of North Carolina] will update NMED with any additional details as they unfold." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-07-01
51174 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-05-13 | 2015-06-23 16:57 | 2015-06-23 | VOLUNTARY REPORT - INFORMATION ONLY "On May 13, 2015, with the unit shut down and the mode switch in Refuel, during the performance of plant procedure 3.M.2-12.4, 'Backfilling Reference Lines for Racks C2205, C2275, and C2251' a full reactor scram occurred. The scram occurred at Step [26](b) of Attachment #1 of the procedure. The plant had been shut down for refueling for a couple of weeks or more and was in 'cold' condition. This event was evaluated for potential reportability under both 10 CFR 50.72 and 50.73 and found to be not reportable as either a prompt report or LER. The following 'System Actuation' sections were most applicable. "10CFR50.72(b)(2)(iv)(B) Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical - Plant Response: Pilgrim was not critical at the time of the event. "10CFR50.72(b)(3(iv)(A) Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) - Plant Response: Pilgrim was in the process of refilling reference legs as part of restoration from the refueling outage. This was not a valid RPS signal. "10CFR50.73(a)(2)(iv)(A) Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, except when: (2) The actuation was invalid and; (i) Occurred while the system was properly removed from service - Plant Response: This was an invalid actuation that occurred when the system was already properly removed from service. All requirements of plant procedures for removing equipment from service had been met. That included required clearance documentation, equipment and control board tagging and properly positioned valves and power supply breakers. "Although this event is not reportable, we are making a courtesy notification to the NRC Operations Center." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW | [5 empty] | 0 | 2015-06-23
51173 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-06-23 03:42 | 2015-06-23 10:26 | 2015-06-23 | LOSS OF EMERGENCY PREPAREDNESS CAPABILITY DUE TO PHONE SYSTEM FAILURES "At 0342 [CDT], as a result of severe weather conditions in the area, Exelon Generation Company, LLC (EGC) identified that the Emergency Notification System (ENS), Health Physics Network (HPN) phone systems, and their associated back-up system, the commercial phone system, had failed at Dresden Nuclear Power Station (DNPS). A loss of the primary phone system concurrent with the loss of the associated back-up system is a reportable condition in accordance with 10 CFR 50.72 (b)(3)(xiii) - Major Loss of Emergency Preparedness Capabilities. "As a result of the failed communication systems, DNPS contacted the NRC to notify them of the issue and provided an alternate phone number for the Shift Manager for use until the systems were restored. "As of 0743 [CDT], ENS, HPN, and the commercial phone systems were restored and verified to be working properly." The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-23
51172 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-06-22 17:30 | 2015-06-22 23:54 | 2015-06-23 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the State of Oklahoma via email: "PSI (Professional Service Industries, Inc.) has reported the theft of a Troxler Model 3430 portable [moisture density] gauge from a truck located at a gas station in El Reno, OK about 1730 [CDT on 6/22/15]. The gauge was removed from the shipping container. A report has been filed with the Oklahoma City Police and a $500 dollar reward has been offered." The serial number of the gauge is 67614. The State of Oklahoma will be conducting a reactive inspection and submitting an NMED report on this event. Troxler Model 3430 typically contains 8 mCi Cs-137 and 40 mCi Am-241/Be sources. * * * UPDATE FROM KEVIN SAMPSON TO DANIEL MILLS AT 1445 EDT ON 6/23/15 * * * The following information was obtained from the State of Oklahoma via email: "Professional Service Industries, Inc. (PSI) has informed [the State of Oklahoma] that a Troxler 3430 portable gauge was stolen from a road construction site in Oklahoma City, OK on June 22, 2015. The technician finished his work about [1600 CDT], secured the gauge in the truck, then went to talk to the road construction workers. He returned to the truck and drove to a nearby gas station/convenience store where he went in for a few minutes, then drove back to the PSI office. He then went to unload the gauge and discovered that the case was unlocked and the gauge missing. The calibration block needed to use the gauge was not taken. The case was secured with two chains and two padlocks. When the theft was discovered, one padlock was missing, the other was undamaged and appeared to have been opened with a key. The case was also undamaged. When last seen, the source rod was locked in the retracted position. The investigation is on-going. "NMED # OK150007" Notified R4DO (Campbell), NMSS (email) and ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-07-01
51171 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-06-22 21:45 | 2015-06-22 23:43 | 2015-06-23 | SECURITY PRECAUTIONS TAKEN DUE TO SEVERE WEATHER Specific security measures have been suspended or modified due to severe/hazardous weather on site. Contact the Headquarters Operations Officer for additional details. The licensee will be notifying the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-06-23
51170 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-06-22 14:06 | 2015-06-22 20:55 | 2015-06-22 | SODIUM HYDROXIDE BELOW TECHNICAL SPECIFICATION REQUIRED CONCENTRATION "At 1406 [EDT] on 6/22/15, the chemistry sample results for the Salem Unit 1 Containment Spray Additive tank were below the minimum Technical Specification requirement for NaOH [Sodium Hydroxide] concentration. The Containment Spray Additive tank was declared inoperable at that time in accordance with Technical Specification 3.6.2.2.a. Based on the fact that there is no redundant equipment for the Containment Spray Additive tank, this condition could have prevented this Safety System from Controlling the Release of Radioactive Material and Mitigating the consequences of an accident. "This event is being reported under the requirements of 10 CFR 50.72(b)(3)(v)(C) and (D) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to Control the Release of Radioactive Material and Mitigate the Consequences of an Accident.' Actions are being taken to restore the NaOH concentration to within the Technical Specification limits. "The Licensee has notified the NRC Resident. No one was injured as a result of the event." The licensee will notify the Lower Alloways Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-06-22
51169 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2015-06-18 12:30 | 2015-06-22 11:29 | 2015-07-02 | AGREEMENT STATE REPORT - NUCLEAR FIXED GAUGE DAMAGED The following report was provided by the Arkansas Department of Health via email: "Nucor-Yamato Steel Company, Arkansas Radioactive Materials Licensee Number ARK-0722-03120, notified the Arkansas Department of Health, Radioactive Materials Program, via phone on Friday, June 19, 2015, at 1000 [CDT], of damage to one of their fixed gauges, manufacturer Ronan, Model #SA-1-F37, Serial #1224CG with a 5 Curie Cs-137 source. The event occurred on June 18, 2015 at approximately 1230 [CDT]. Licensee reported a wash-out of liquid steel which came into contact with the gauge. There was approximately 30 tons of molten rock (2800 øF) flowing onto the floor of the plant which caused a fire. Surrounding gauges were not affected. "The Licensee immediately closed the shutter, but was not sure if it was completely shut. The RSO indicated the only radiation levels were from the top of the gauge, nothing was measured on the sides. A steel plate was placed on top of the gauge to reduce radiation levels. The area was roped-off at 2 mR/hr to prevent public exposures. Chase Environmental Consulting was notified of the damaged gauge and arrived on Friday, June 19, 2015 to investigate and remove the gauge out-of-service. "The gauge is currently in storage awaiting the manufacturer (Ronan) to arrive to package for shipment on Friday, June 26, 2015. "The State is awaiting a written report from the licensee and will continue to investigate this event. The State will update this event as more information becomes available. "Arkansas Event Number: ARK-2015-008" * * * UPDATE ON 7/2/15 AT 1315 EDT FROM SUSAN ELLIOTT TO JEFF HERRERA * * * The following update was received from the Arkansas Department of Health via email: "The written report dated June 26, 2015, from Nucor-Yamato Steel Company, detailed safety procedures followed in securing the damaged gauge while removing it from service. The manufacturer, Ronan's Field Engineer, packaged and shipped the gauge to their facility. There was no radiation leakage from the gauge. The licensee confirms no exposure to the public. "The State considers this event closed." Notified the R4DO (Okeefe) and NMSS Events (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-06-30
51168 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-06-21 16:25 | 2015-06-21 20:25 | 2015-06-21 | MANUAL SECONDARY CONTAINMENT ISOLATION "In response to a trip of Unit 2 reactor enclosure HVAC [Heating, Ventilation and Air Conditioning], subsequent loss of reactor enclosure delta-p and rising reactor enclosure room temperatures, a Unit 2 manual secondary containment isolation was initiated per station procedures. This manual isolation also resulted in an isolation signal to containment atmosphere control (CAC) system valves and primary containment instrument gas (PCIG) system valves. System responses were as expected. "Unit 2 secondary containment delta-p and room temperatures were restored via the standby gas treatment system (SGTS), and Unit 2 secondary containment integrity remains intact and operable. "Investigation of the trip of Unit 2 reactor enclosure HVAC is ongoing. "This is being reported under 50.72(b)(3)(iv)(A) for containment isolation signal affecting containment isolation valves in more than one system." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-06-21
51167 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2015-03-04 | 2015-06-19 12:50 | 2015-06-19 | AGREEMENT STATE REPORT - MEDICAL EVENT DURING BRACHYTHERAPY TREATMENT The following information was received from the State of Maine via email: "Maine General Medical Center reported that a patient received less dose than prescribed to the treatment site and dose to an unintended site during HDR (Varian model GammaMed Plus) brachytherapy using an Ir-192 source. The patient was prescribed to receive a 1,350 cGy (rad) boost dose to the vaginal cuff in three weekly fractions of 450 cGy (rad) each. The first fraction was delivered on 2/25/2015 using a 3.5-cm applicator. Post insertion CT images were reviewed by the physician and the first fraction was delivered correctly. During the second fraction on 3/4/2015, a second physician was unable to insert the 3.5-cm applicator due to edema and tenderness. A new treatment plan was developed to deliver the prescribed 450 cGy (rad) dose using a 2.6-cm applicator. Upon review of the previous week's images, the second physician noted that the applicator was approximately 7 cm short of the intended position such that the tip of the applicator did not contact the vaginal cuff. On 3/11/2015, a fraction was correctly delivered using the 2.6-cm applicator. The second physician reviewed the treatment deviation with the patient and recommended that an additional fraction of 450 cGy (rad) be administered, which was scheduled for 3/18/2015. The cause was determined to be human error." This event was reported to the State of Maine on 03/11/2015. An NMED report was submitted on 03/12/2015 [NMED Item Number: 150165]. Maine Report Nr.: ME150002 and ME150002A A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2015-06-29
51166 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2014-08-21 | 2015-06-19 12:50 | 2015-06-19 | AGREEMENT STATE REPORT - THEFT OF FOUR TRITIUM EXIT SIGNS The following information was received from the State of Maine via email: "Colby College reported the theft of four radioluminescent exit signs (Isolite model SLX-60, serial #13-9009, 13-9010, 13-9011, and 13-9013), each containing 229.4 GBq (6.2 Ci) of H-3. The signs were discovered to be missing during an annual inventory performed on 8/21/2014." This event was reported to the State of Maine on 12/04/2014. An NMED report was submitted on 02/02/2015 [NMED Item Number: 150092]. Maine Report Nr.: ME150001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2015-06-29
51165 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-06-19 01:53 | 2015-06-19 10:03 | 2015-06-19 | SECONDARY CONTAINMENT INTERLOCK DOORS OPEN SIMULTANEOUSLY "On June 19, 2015, at 0153 CDT, two Secondary Containment interlock doors (1/2 EDG [Emergency Diesel Generator] room door and the Unit 1 reactor building door) were open simultaneously. The doors were immediately closed and secondary containment pressure remained negative. "This condition represents a failure to meet surveillance requirement 3.6.4.1.2 given two doors in a single access opening were open simultaneously. As a result entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to secondary containment being inoperable. "This event is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified. "The door has been posted to notify to restrict access. "The State of Illinois Emergency Management has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-06-19
51164 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-06-17 18:41 | 2015-06-17 23:39 | 2015-06-18 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM RETURN DAMPER FAILED CLOSED "On June 17th, 2015 at 1841 CDT, it was determined that the onsite Technical Support Center (TSC) Ventilation System return damper 0VS119Y was failed closed, the failed closed damper affects the TSC Emergency Makeup Train filtration efficiency. There is currently no emergency event in progress requiring TSC staffing. If an emergency is declared and the TSC ERO [Emergency Response Organization] activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable site procedures. "The licensee has notified the [NRC] Senior Resident Inspector of the issue." * * * UPDATE AT 1700 EDT ON 06/18/15 FROM TODD CASAGRANDE TO S. SANDIN * * * "After repairs were completed, the TSC Ventilation was restored to service at 1650 EDT on 06/18/2015. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Pelke). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-17
51163 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-06-17 11:05 | 2015-06-17 16:04 | 2015-06-17 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED OPERATOR A licensed [non-supervisor] operator was found in violation of the fitness-for-duty policy. The employee's access to the plant has been revoked. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2015-06-17
51162 | 0 | ECS MID-ATLANTIC, LLC |  |  |  |  | 2015-06-16 15:00 | 2015-06-17 14:23 | 2015-07-01 | MOISTURE/DENSITY GAUGE INVOLVED IN AUTOMOBILE FIRE A licensee employee working at a job site in Claymont, Delaware went to leave the job site at 1500 EDT on June 16, 2015. The employee got in his vehicle and turned on the ignition. A fire started under and around the dashboard. The employee exited his vehicle and called 911 and the licensee Radiation Safety Officer. The local fire department responded. The front portion of the vehicle had been totally engulfed. The vehicle trunk, where the gauge was stored, received heat and smoke damage. The carrying case of the gauge was partially melted. No visible damage occurred to the gauge itself. The gauge was transported to a service vendor for inspection and repair if needed. The gauge was a Troxler 3440 Moisture/Density gauge, serial number 20118, containing an 8 mCi Cesium-137 source and a 40 mCi Am-241source. The licensee notified NRC R1(Ragland), Delaware Department of Natural Resources and Environmental Control, Division of Waste and Hazardous Substances, Emergency Prevention and Response Section, and Delaware Health and Social Services, Division of Public Health. * * * UPDATE ON 07/01/15 AT 1827 EDT FROM IRVIN FISCHER TO STEVEN VITTO * * * The licensee provided the following update via email: "The gauge is back in service after being evaluated and recalibrated. " Notified R1DO (Dimitriadis) and NMSS Events (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 30.50(b)(4) |  |  |  | 0 | 2015-06-25
51161 | -1 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-06-16 23:43 | 2015-06-17 04:15 | 2015-07-01 | SERVICE WATER EFFLUENT RADIATION MONITOR OUT OF SERVICE The B train of the service water effluent radiation monitor failed at 2343 EDT and is being repaired. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 07/01/2015 AT 1411 EDT FROM THOMAS CLEARY TO STEVEN VITTO * * * "The purpose of this call is to retract a report made on June 17, 2015, NRC Event Number 51161. Event Report number 51161 describes a condition at Millstone Power Station Unit 3 (MPS3) in which a service water radiation monitor failed, was taken out of service for repair and was reported in accordance with 10 CFR 50.72(b)(3)(xiii) as a loss of emergency assessment capability. "Upon further review, MPS3 has concluded that the subject radiation monitor is not utilized for emergency assessment capability. Therefore, this condition is not reportable and NRC Event Number 51161 is being retracted. "The basis for this conclusion will be provided to the NRC Resident Inspector." R1DO(Dimitriadis) have been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-17
51160 | 0 | US FDA Ctr for Toxicological Resear |  |  |  |  | 2015-06-16 | 2015-06-16 18:01 | 2015-06-16 | SEALED SOURCE FOUND IN SHIPMENT OF SCRAP MATERIAL The licensee (US FDA) sent a shipment of scrap material which had been generated onsite, to a scrap recycling facility in Pine Bluff, Arkansas. The scrap facility detected a device containing radioactive material in the shipment. The device was returned to the licensee who identified the device as an Alnor Dewpointer. The source was removed from the device and the exposure rate was measured as 4.2 mR/hr on contact. The source is being stored pending disposal. The isotope is unknown, but is suspected to be either Radium 226 or Americium 241. The licensee has contacted the State of Arkansas. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-06-24
51159 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2015-06-16 04:52 | 2015-06-16 11:34 | 2015-06-16 | EMERGENCY DIESEL GENERATOR FOUND INOPERABLE "At 0452 EDT hours on June 16, 2015, during performance of a surveillance test for the Division 3 4160 Volt Bus Undervoltage/Degraded Voltage Channel Calibration and Logic System Functional Test, the K36 degraded voltage time delay relay was found outside of the Technical Specification 3.3.8.1 allowable value, resulting in an inoperable condition of the Division 3 Emergency Diesel Generator (EDG). The Division 3 EDG had previously been declared inoperable for performance of the surveillance testing. "The K36 degraded voltage time delay relay initiates load shedding, isolates the Division 3 bus, and starts the Division 3 EDG. The Technical Specification allowable value is 180 to 270 seconds. The as-found time was 272.66 seconds. The K36 relay was calibrated in accordance with plant procedures and returned to service at 0730 hours on June 16, 2015. "The Division 3 EDG is the on-site power source for the High Pressure Core Spray system which is a single train system. Therefore, this event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-06-16
51158 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2015-02-17 08:00 | 2015-06-16 10:39 | 2015-06-16 | QUALITY ASSURANCE PROGRAMMATIC ISSUES "10 CFR 50.55(e) initial notification for a failure to comply with requirements of 10 CFR 50 Appendix B associated with AP1000 nuclear power plant construction by Chicago Bridge & Iron Company (CB&I) at the V.C. Summer Units 2 & 3 construction site. "This 50.55(e) initial notification addresses a failure to comply by CB&I, an agent of South Carolina Electric & Gas Company (SCE&G) for V.C. Summer Units 2 & 3, to meet the requirements of Appendix B, Criteria V and XV. It is concluded that Quality Assurance programmatic issues, as identified by CB&I Root Cause Analysis 2015-0539, could have produced a defect and this condition is reportable in accordance with 10 CFR 50.55(e)(3)(iii)(C). Root Cause Analysis 2015-0539 investigated the causes that lead to impingement of safety related reinforcing steel and the steel containment vessel during concrete core drilling operations within the Unit 2 containment structure. No defect has been identified. "This condition is associated with NRC special inspection report number 05200027/2015-009. "This notification closes the Interim Part 21 report submitted on April 16th, 2015, by CB&I. "This 50.55(e) Initial Notification is being submitted pursuant to the requirements of 10 CFR 50.55(e)(3)(iii)(C)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 50.55(e) |  |  |  | 0 | 2015-06-16
51157 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-06-05 | 2015-06-16 10:29 | 2015-06-16 | AGREEMENT STATE REPORT - RADIOACTIVE SOURCE FOUND IN SCRAP METAL The following report was received via e-mail: "Scrap alarm was received at Gerdau Ameristeel, Jacksonville. Scrap bales were from KAS Metals (1912 Elman St. Orlando). Radiation surveys conducted with a Radcomm read 500 mR/hr at the front of trailer and 300 mR/hr at 2 meters. Readings in the cab were 10 mR/hr. All reading and units were confirmed. Due to the reading exceeding DOT levels the load was not granted an exemption and was left in a secure area until Bureau [Florida Bureau of Radiation Control] personnel arrive. The driver left Orlando at 1030 EDT and arrived in Jacksonville at 1430 EDT. The driver [works for] for CPG Enterprises." Florida event number: FL15-057 * * * UPDATE ON 6/16/15 AT 1208 EDT * * * The following was received via e-mail: "The source was found to be a broken Troxler handle assembly, [containing] 8 mCi of Cs-137, Dated April 1999, Serial# 50-5034, (ALT 60-5034) 1.5 R/hr [on contact] Issued Sample Tag # Z-011" Notified R1DO (Bickett) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-06-24
51156 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-06-15 19:20 | 2015-06-15 20:15 | 2015-06-16 | REACTOR TRIP DUE TO TURBINE TRIP "On June 15, 2015 at 1920 EDT, Indian Point Unit 3 received a Turbine trip which directly led to a Reactor trip. Operators entered [plant procedure] E-0, Reactor Trip or Safety Injection. All control rods fully inserted. All safety systems responded as expected. The Auxiliary Feedwater (AFW) system actuated as expected. Offsite power and electrical lineups are normal. No primary or secondary code safety valves lifted. All MSIVs are open and the Main Condensers are being used as the heat sink. The Reactor is in Mode 3 and stable. Unit 2 was unaffected and remains at 100% power. Preliminary investigation determined that Breaker Number 1 in the Ring Bus was intentionally opened [by plant personnel on switching orders from the district operator] due to a problem on W93 [output feeder from Ring Bus]. Subsequently Breaker #3 went open and caused a Turbine/Reactor trip of the Unit." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM BOB WALPOLE TO DANIEL MILLS ON 6/16/15 AT 1320 EDT * * * The licensee previously identified "a problem on W93" which was a mistake and should have been stated as "a problem on W97". All other information was stated correctly. The NRC Resident Inspector has been notified. Notified R1DO (Bickett). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-06-15
51155 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2015-06-12 | 2015-06-15 16:20 | 2015-07-06 | AGREEMENT STATE REPORT - STOLEN MOISTURE/DENSITY GAUGE The following information was received via E-mail: "On June 12, 2015, a portable gauge was being stored in a locked box in the back of a truck which was locked in one of the user's garages. An ex-girlfriend, who had a copy of the truck keys, broke into the user's house and stole the truck with the gauge still in the back. The truck was reported stolen to the RSO on the morning of June 13, 2015. The RSO then made a police report and contacted the Agency's [Arizona Radiation Regulatory Agency] duty officer. The RSO stated that someone spotted the truck in Mesa, Arizona on the night of June 13, 2015. The gauge is a Troxler Model 3400 series, Serial Number 5310, containing 7.4 millicuries of Cesium-137 and 40 millicuries of Americium-241. "The truck is a white, 2007 GMC Sierra crew cab with Arizona license plate number: 415ZGV. "The investigation into this event is ongoing. "The US NRC, Maricopa County sheriff's office, Arizona DPS [Department of Public Safety], California, New Mexico, Utah, Nevada, and Arizona governor's office are being notified of this event." Arizona First Notice Number: 15-009 * * * UPDATE ON 07/06/15 AT 1448 EDT FROM BRIAN GORETZKI TO JEFF HERRERA * * * The following update was provided by the Arizona Radiation Regulatory Agency via email: "On July 5, 2015, City of Mesa police identified the stolen truck in the parking lot of Mountain View Medical Center. The portable gauge was still with the vehicle and it was relocated to the licensee's office. The licensee will perform a leak test prior to the gauge being used." Notified the R4DO (Haire), ILTAB (Johnson), NMSS Events (via email) and CNSNS (MEXICO via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2015-06-23
51154 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-06-15 07:00 | 2015-06-15 17:42 | 2015-06-18 | TSC VENTILATION TO BE REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On 6/16/2015, planned preventive maintenance activities [will be] performed on the Braidwood Generating Station Technical Support Center (TSC), Ventilation System. The work will be completed within approximately 48 hours. This activity includes preventative maintenance that requires the TSC ventilation system to be out of service which will render the TSC ventilation system non-functional. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff as necessary. "This event is reportable per 10 CFR 50.72(b)(3)(xiii) for 'any event that results in a major loss of emergency assessment capability.' The planned maintenance will not be able to restore the TSC condensing unit or ventilation system to service within the facility activation time specified in the emergency plan (1 hour) in the event of an accident. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "The licensee has notified the NRC Resident Inspector." * * * UPDATE AT 1102 EDT ON 6/18/15 FROM DAVID KORTGE TO JEFF HERRERA * * * "Braidwood Generating Station TSC ventilation was restored to available status at 0700 CDT on June 18, 2015. "The previously reported system preventative maintenance has been completed." The licensee notified the NRC Resident Inspector. Notified the R3DO (Pelke). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-15
51153 | -1 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-06-12 10:30 | 2015-06-12 17:18 | 2015-09-10 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "On June 12, 2015 at 1030 CDT, the Browns Ferry Nuclear Plant Unit 3 High Pressure Coolant Injection (HPCI) system was declared inoperable due to the time to drain the Turbine Exhaust Drain Pot after running the system for periodic testing. The concern is that the turbine may be partially flooded after shutting down and a subsequent restart could cause a water hammer event, possibly damaging the system. This issue was previously analyzed by Engineering as acceptable, but the time to drain the pot after the latest test indicates more water in the exhaust than the maximum amount used in the analysis. "Technical Specification 3.5.1, ECCS Operating, Condition C, was entered as a result of the inoperable HPCI system. This constitutes an unplanned HPCI system inoperability and requires an 8-hour NRC notification in accordance with 10 CFR 50.72(b)(3)(v)(D) due to the failure of a single train system affecting accident mitigation, and a 60 day written report in accordance with 10 CFR 50.73(a)(2)(v) "The NRC Resident Inspector has been notified." The Technical Specification Action statement allows 14 days to restore the HPCI system to operable status. * * * RETRACTION FROM MATTHEW SLOUKA TO DANIEL MILLS AT 1623 EDT ON 9/10/15 * * * "Browns Ferry Nuclear Plant is retracting the 8-hour NRC notification (EN# 51153) made on June 12, 2015 at 1030 CDT. "The notification on June 12, 2015, reported a condition where the HPCI system was declared inoperable due to the time to drain the Turbine Exhaust Drain Pot after running the system for periodic testing. The concern was that the turbine may be partially flooded which could cause water hammer and damage the HPCI system. "Subsequent evaluation concluded that the HPCI system under the identified flooded turbine conditions will not produce a transient that exceeds design values, therefore, HPCI system operability was maintained and no reportable condition existed during this time. "The NRC Resident Inspector has been notified of this retraction." Notified R2DO (Shaeffer). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-06-12
51152 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-04-15 12:07 | 2015-06-12 14:52 | 2015-06-12 | INVALID ACTUATIONS OF THE CONTAINMENT VENTILATION ISOLATION SYSTEM "This 60-day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report two related invalid actuations of the Containment Vent Isolation System at Watts Bar Nuclear Plant Unit 1 (WBN-1). "On April 14, 2015 at 2101 EDT, a sample pump failed on the WBN-1 Train B containment purge exhaust radiation monitor (1-RM-90-131), prompting control room operators to enter Conditions A and B of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.6, Containment Vent Isolation Instrumentation and Condition A of LCO 3.6.3, Containment Isolation Valves. "On April 15, 2015 at 1207 EDT, 1-RM-90-131 radiation readings increased sharply (spiked), initiating an invalid Containment Vent Isolation (CVI) actuation. The spike occurred following troubleshooting and repairs to 1-RM-90-131 when maintenance technicians agitated the motor starter enclosure in an attempt to free a stuck auxiliary contact that controls local indication. As a result of the CVI actuation, flow to lower containment radiation monitor (1-RM-90-106) was isolated, prompting control room operators to enter Condition B of LCO 3.4.15, RCS Leakage Detection Instrumentation. At 1634 EDT, control room operators exited the TS 3.4.15 condition when 1-RM-90-106 was returned to service. "On April 17, 2015 at 1327 EDT, control room operators exited LCO 3.3.6 Conditions A and B and LCO 3.6.3 Condition A when sample pump repairs were completed on 1-RM-90-131. "On April 19, 2015 at 1550 EDT, 1-RM-90-131 radiation readings spiked and initiated a CVI, prompting control room operators to enter TS LCO 3.4.15 Condition B and LCO 3.3.6 Condition A, until flow was restored to 1-RM-90-106 at 1636 EDT and 1-RM-90-131 was returned to service on April 26, 2015 at 1229 EDT. "Each CVI was documented in accordance with the corrective action program, and TVA completed an equipment apparent cause evaluation (CR 1015781) that revealed the cause of the two CVI actuations was the result of a faulted Start/Stop control unit. TVA replaced the faulted control unit. "In both instances, the CVI actuations resulted from invalid signals and were limited to a single piece of Train B equipment. There was no loss of safety function and there were no actual safety consequences during the events." The NRC Resident Inspector has been informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-06-12
51151 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-06-12 09:24 | 2015-06-12 14:05 | 2015-06-16 | LOSS OF TONE ALERT RADIO SYSTEM "At 1027 [EDT] on June 12, 2015, with the James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management Center notified JAF that the Tone Alert Radio System had been out of service since 0924 [EDT]. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the JAF Nuclear Power Plant. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The county alert sirens which also function as part of the Public Prompt Notification System remain operable. "The loss of the Tone Alert Radio System constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local law enforcement personnel are also available for 'route alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program and the [NRC] Resident Inspector has been briefed." National Weather Service is investigating the failures. * * * UPDATE FROM BENJAMIN EGNEW TO DONALD NORWOOD AT 1436 EDT ON 6/16/2015 * * * "The Tone Alert System was restored to service on 6/16/15 at 1230 EDT." The licensee notified the NRC Resident Inspector. Notified the R1DO (Bickett). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-12
51150 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-06-11 20:56 | 2015-06-11 23:37 | 2015-06-11 | LOSS OF TONE ALERT RADIO SYSTEM "At 2205 [EDT] on June 11, 2015, with the James A. FitzPatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County 911 Center notified JAF that the tone alert weather radios had been out of service since 2056 [EDT]. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the JAF Nuclear Power Plant. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The [Oswego] County alert sirens which also function as part of the public prompt notification system remain operable. "The loss of the tone alert radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the prompt notification system be needed. This consists of utilizing the hyper reach system which is a reverse 911 feature available from the county 911 center. Local Law Enforcement personnel are also available for 'Route Alerting' of the affected areas of the EPZ. "JAF was notified by Oswego County 911 Center that the tone alert radio system was restored to service at 2257 [EDT]. "The event has been entered into the corrective action program and the [NRC] Resident Inspector has been briefed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-11
51149 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-06-11 16:54 | 2015-06-11 22:28 | 2015-07-10 | DEGRADED CONTAINMENT SPRAY FLOW CHECK VALVE During containment spray pump inservice testing the minimum flow recirculation line recorded negative flow indicating reverse flow in the line. After the troubleshooting, it was determined that a degraded minimum flow check valve was allowing a path to the refueling water storage tank (RWST) for certain post loss of coolant accident (LOCA) conditions. The minimum flow isolation has been closed to eliminate the path. No actuation occurred during this time. The NRC Resident Inspector, Connecticut Department of Energy and Environmental Protection (DEEP) Hartford, and Watertown Dispatch have been notified. * * * UPDATE FROM TOM CLEARY TO STEVEN VITTO ON 06/16/15 AT 1349 EDT * * * "The purpose of this call is to correct the record for the 10 CFR 50.72(b)(3)(v)(C) event report provided on June 11, 2015. Event report number 51149 states: 'During containment spray pump inservice testing ...' The condition of the degraded containment spray flow check valve was identified: 'During high pressure safety injection pump inservice testing...'." Notified R1DO (Bickett) * * * UPDATE FROM WILLIAM McCOLLUM TO DANIEL MILLS AT 1724 EDT ON 7/10/15 * * * "The purpose of this call is to update the record for the 10 CFR 50.72(b)(3)(v)(C) event report provided on June 11, 2015. During subsequent investigation, it has been determined that a second release path may have existed through ECCS system relief valves under certain post LOCA conditions as a result of the degraded check valve described in the original report." The licensee has informed the NRC Resident Inspector. Notified R1DO (Cahill). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-06-11
51148 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-06-10 15:20 | 2015-06-11 13:15 | 2015-06-15 | FITNESS FOR DUTY A licensed employee supervisor had a confirmed positive test for a controlled substance during a random fitness-for-duty test. The employee's plant access has been placed on administrative hold. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2015-06-11
51147 | -1 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-06-11 08:22 | 2015-06-11 12:10 | 2015-06-11 | OFFSITE NOTIFICATION DUE TO INADVERTENT EMERGENCY PLAN SIREN ACTUATION "This is a non-emergency notification to the NRC in accordance with 10 CFR 50.72(b)(2)(xi). "On 6/11/15, at 0822 [EDT], Miami-Dade Fire Department notified the site of an alarming single Emergency Plan siren. Investigation is ongoing for alarming siren. At no time was there an emergency requiring the siren activation. FPL [Florida Power and Light] has not issued a news release. "This notification is made in accordance with 10 CFR 50.72 (b)(2)(xi). "The Senior NRC Resident [Inspector] has been notified." * * * RETRACTION FROM ALEX CHOMAT TO DANIEL MILLS AT 1552 EDT ON 6/11/15 * * * "The investigation of the reported alarming EP siren did not confirm that it had been activated or had malfunctioned. The notification received from the Miami-Dade Fire Department apparently resulted from an erroneous call from a member of the public. "This event notification is retracted based on the fact that no EP siren activation occurred necessitating notifications. "The Senior NRC Resident [Inspector] has been updated." Notified R2DO (Guthrie) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-06-11
51146 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-06-10 13:00 | 2015-06-10 20:09 | 2015-06-10 | TEMPORARY LOSS OF METEOROLOGICAL DATA "This event is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for a loss of emergency assessment capability at the Harris Nuclear Plant. Between March 24, 2015, and April 28, 2015, the meteorological data transfer process from the sensors to the emergency response facilities stalled intermittently five times. The control room staff was unaware of this condition for a maximum of 6.6 hours at any given time. When the data transfer process was stalled and the control room staff was unaware of the issue, the staff may have used inappropriate information in implementing the emergency plan. There was no impact from this condition because there were no actual emergencies during this time. "On June 10, 2015, at approximately 1300 [EDT], further review of the impact of this equipment failure determined that this was reportable as a loss of emergency assessment capability. "The condition that caused the data transfer process to stall has been corrected. In addition, measures have been implemented to ensure that if the data transfer process stalls again, backup sources of information will be used in accordance with the emergency plan to preclude loss of the assessment capability. "There was no adverse impact to the public health and safety or to plant employees. "The NRC Resident Inspector has been informed of this condition." Until this information is captured in a plant procedure, the licensee has issued a standing instruction. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-10
51145 | 0 | DEPARTMENT OF THE ARMY |  |  |  |  | 2015-06-10 | 2015-06-10 15:48 | 2015-06-12 | CD-109 SOURCE IMPROPERLY SENT FOR DISPOSAL The Alabama Air National Guard (Montgomery, AL) had a thermal night time analyzer with a 40 mCi, Cd-109 source. The source was last inventoried on 1/30/2015. On 4/28/2015, the analyzer was transferred to the disposal facility at the Defense Logistics Agency (DLA) at Robins Air Force Base in Georgia. The Army does not send radioactive sources to this DLA for disposal. The Army has verified receipt of the source at the DLA and is currently trying to determine if the source is still there or has been destroyed. Source: XLP-303 with serial number 18540 * * * UPDATE AT 0840 EDT ON 6/12/2015 FROM MARCOS VICENTE TO DONG PARK * * * The following report was received from the licensee via e-mail: "[The following is] updated information concerning the improper transfer of the Thermo Niton Analyzer by the Alabama Army National Guard to Defense Logistics Agency (DLA) Disposition Services. We were successful in contacting the manufacturer and got information concerning the assay date of the Cd-109 source. Their records indicate an assay date of 15 April 2008. The analyzer was sent to DLA on 28 April 2015. According to our calculations, this drops the activity from 40 mCi to approximately 0.86 mCi from when it was shipped out to DLA. We are still working with DLA Disposition Services to track the location of the analyzer." Notified the R1DO (Dwyer) and NMSS Events Notification (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | AL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-06-18
51144 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-03-05 | 2015-06-10 14:13 | 2015-06-12 | AGREEMENT STATE REPORT - WELL LOGGING TRITIUM SOURCE BROKEN OPEN DURING MAINTENANCE The following report was received from the State of Texas via e-mail: "On June 10, 2015 the licensee contacted the Agency [Texas Department of State Health Services] reporting that an Agency inspector was at the site inspecting the facility. The inspector informed the licensee that a reportable event occurred and was not reported as required. The licensee was making notification that on March 5, 2015, during repair of a pulsed neutron generator tool, the work counter, internal casing and housing of the tool had contamination from a sealed tritium tube. The tube was manufactured by Thermo Fisher, ID 163-D101-S, on April 19, 2013 at an activity rating of 3 curies. The licensee explained that during the check on the tool, readings were seen on the meter. The area was checked and the contamination found and cleared from the tool and counter. The area was tested with wipes and counted. The highest count was 680 cps [counts per second]. The area was wiped clean and the clean up material is in a sealed drum awaiting disposal. The amount of contamination was calculated and the licensee explained he read through the regulations and determined the level of exposure was not reportable. The calculated dose was not provided. No badges were sent to the processor for reading. The tool itself was salvaged and reworked into a new usable tool with a new serial number. A detailed description of the event was requested from the licensee. Investigation into this case is ongoing. Update will be made in accordance with SA300 guidelines." Texas Report: I-9319 * * * RETRACTED AT 1000 EDT ON 6/12/15 FROM IRENE CASARES TO JEFF HERRERA * * * The following retraction was received from the Texas Department of State Health Services via email: "More complete information was obtained from the licensee. The pulse neutron generator tool was damaged and the tritium tube was leaking material, contaminating the internal tool and the countertop during repair process. The employee working on the tool noticed increased readings on his survey instrument and immediately checked the tritium tube to find the contamination. The material was confined to the tool and countertop. The tube activity is listed as 3 curies. The employee notified his radiation safety officer of the damaged tool and a dose rate was calculated. The RSO had calculated 40,800 CPM = 680 CPS (background was 120 CPS), 680 CPS x .20 [microSv]/hour (calibration factor) = 136 [microSv]/hour, 136 [microSv]/hour = 0.0136 REM / hour for the dose. The release did not exceed regulatory limits and was not in an operable condition when being repaired. The contaminated area did not require restricted access and the quantity of material did not meet the annual limits on intake exposure. The radioactivity detected in the tool was remediated immediately and contaminated waste [was placed in a] drum for disposal. No aspect of the event met any reporting criteria. It has been determined this was not a reportable event." Notified the R4DO (Werner) and NMSS Events Notification (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-06-18
51143 | 0 | BASIN ELECTRIC POWER COOPERATIVE |  |  |  |  | 2015-06-10 | 2015-06-10 14:00 | 2015-06-10 | DENSITY GAUGE SHUTTER STUCK OPEN "The gauge is a Kay-Ray Model 7063P, serial number 8289 with a nominal source of 1 Curie of Cesium 137. The gauge is used for lime slurry density measurements in the Unit 1 Scrubber. "The malfunctioning shutter was discovered on June 6, 2015 during semiannual shutter checks as required by the license. The checks were completed today, and [the Radiation Safety Officer (RSO)] became aware of the issue as [the RSO] reviewed the documentation. Independent verification of the malfunction was made, it was found to not close. The cause of the malfunction is not known at this time. "The gauge is located approximately sixteen feet above the ground level and presents no unusual risk to plant personnel. No maintenance activities will be conducted on the pipe or elbow the gauge is attached to until the shutter has been repaired. All plant personnel have been notified of the issue and the requisite restriction. "[The RSO] contacted a properly licensed contractor to arrange for the repair to the shutter." This gauge is normally open during plant operation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-06-18
51142 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2015-06-09 16:37 | 2015-06-09 16:52 | 2015-06-09 | LOST SOURCES An inventory could not ascertain the location of three sources that had been placed in storage. The licensee notified the NRC Resident Inspector. Notified DHS, FEMA, DOE, USDA, EPA, and HHS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 74.11(a) |  |  |  | 1 | 2015-06-09
51141 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2015-06-09 03:10 | 2015-06-09 09:13 | 2015-06-09 | HOPE CREEK TECHNICAL SUPPORT CENTER REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "On June 9, 2015 at 0310 [EDT] the Hope Creek Technical Support Center (TSC) ventilation system was removed from service to perform planned maintenance. The removal of the ventilation potentially affects the TSC habitability during a declared emergency requiring activation. Appropriate compensatory measures are in place while the ventilation is out of service. The Emergency Response Organization duty team has been notified of the maintenance and the possible need to activate in an alternate location. The ventilation system is scheduled to be out of service for approximately 93 hours. "The NRC Resident Inspector and Lower Alloways Creek Township will be notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-09
51140 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-06-08 07:00 | 2015-06-08 16:35 | 2015-06-08 | AGREEMENT STATE REPORT - UNATTENDED RADIOGRAPHY CAMERA The following report was received via fax: "The incident happened on June 8, 2015, and was corrected and under the licensee's control by 0840 CDT. It was not reported to the Department [Louisiana Department of Environmental Quality] until 1150 CDT on June 8, 2015. "A radiography exposure device was left in a company radiography rig parked at the Baton Rouge Metro Airport. A radiographer was flying out of the Baton Rouge Airport after working a job in the field. The radiographer went through security and boarded the plane departing at 0700 CDT. However, the person who was to retrieve the rig with the camera did not arrive at the airport until 0840 CDT. This means the camera alarm system was left unattended for 1 hour and 40 minutes. "The IC alarm system for the radiography rig sounds/alarms to a 'key fob' while in the field. One potential responder was in the air with one alarming device and the other alarming device had not made it to the airport. The radiography rig was parked in a parking lot unattended. The rig and camera were retrieved at 0840 CDT the same morning. "The camera was an AEA Delta 880, SN D8086 exposure device loaded with 34 Ci of Ir-192. The camera and the vehicle were locked and secured, but the alarming device was unmanned for approximately 2 hrs. "The Radiation Safety Officer called in his report at approximately 1150 CDT on 06/08/2015. The situation did not result in a radiation incident. However, the potential for a radiation incident or security breach was the problem. "At this time, LDEQ [Louisiana Department of Environmental Quality] considers this incident still open. The incident is still under investigation and review by the staff. Enforcement and corrective actions will be determined by the out-come of the investigation. The incident was considered under control by MISTRAS and reported after the exposure device was back at the MISTRAS'S Geismar, LA location." Louisiana Report: id No.: LA150009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-06-16
51139 | 0 | ECS MID-ATLANTIC, LLC |  |  |  |  | 2015-06-08 14:30 | 2015-06-08 15:51 | 2015-06-08 | MOISTURE/DENSITY GAUGE DAMAGED BY COMPACTOR ROLLER At a work site on the U.S. Naval Academy grounds, a compactor roller backed over and damaged a Troxler Model 3430 moisture/density gauge. The gauge contains an 8 mCi Cs-137 source and a 40 mCi Am-241/Be source. Upon inspection of the gauge and surrounding area, the gauge case was found to be separated, but no damage was noted to the sources. The sources were in the shielded position at the time of the incident. The licensee will place the gauge back in its case, transport it to its normal storage location, and contact the manufacturer for repair/disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PROTECTIVE ACTION PREVENTED | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 30.50(a) |  |  |  | 0 | 2015-06-16
51138 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2015-06-05 | 2015-06-08 13:03 | 2015-06-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following report was received via e-mail: "A Troxler 3450 moisture density gauge was run over by a soft tire roller. The gauge housing was cracked open with no apparent damage to the source or shielding. The gauge was placed in its case and transported to the CTL lab in Tacoma." The sources are: 10 mCi Cs-137 and 50 mCi Am-241 Washington Incident: WA-15-017 * * * UPDATE AT 1704 EDT ON 6/10/2015 FROM STEVE MATTHEWS TO MARK ABRAMOVITZ * * * "A Troxler 3450 moisture density gauge was damaged by a soft tire roller at 2140 [PDT] Friday night, June 5th. The location was 15433 West Snoqualmie Valley Road, between Woodinville and Duvall near Carnation. The gauge housing was cracked open but there was no apparent damage to sources or shielding. The gauge was placed in its Type A package and transported to the licensee's facility in Puyallup. From there, the gauge was picked up by a gauge manufacture representative for repair and leak test. The incident occurred because the portable gauge operator turned away momentarily to speak with another construction worker and didn't see the roller getting close and making contact with the gauge. The licensee will be conducting additional training on constant control. There will be a citation for lack of constant surveillance and not notifying our office [Washington Office of Radiation Protection]. The actual notification we received was from the licensees customer, King County Materials Lab." Notified the R4DO (Werner) and NMSS Events Notification (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2015-06-16
51137 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-06-07 22:59 | 2015-06-08 00:45 | 2015-07-09 | UNUSUAL EVENT - FIRE IN PROTECTED AREA LASTING GREATER THAN 15 MINUTES At 2359 EDT on June 7, 2015, the Grand Gulf Nuclear Station declared a Notice of Unusual Event in accordance with Emergency Action Level HU4 for a fire in the protected area lasting greater than 15 minutes. The fire started in the wiring of a terminal box for Electro Hydraulic Pump C, the running pump located in the turbine building. The running pump was then deenergized by operators and the standby pump started. The site fire brigade responded and extinguished the fire. The emergency was terminated at 0030 on June 8, 2015. The licensee notified state and local agencies and will inform the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, and FEMA NWC and Nuclear SSA via email. * * * RETRACTION AT 1645 ON 7/9/2015 FROM KEITH HUFF TO MARK ABRAMOVITZ * * * "The notification of an Unusual Event is being retracted because the event did not meet the definition of 'fire' in NEI 99-01 Revision 5, 'Methodology of the Development of Emergency Action Levels'. The document was endorsed by the NRC on February 22, 2008 (see ADAMS ascension # ML080450149) and is part of the Grand Gulf Nuclear Station's current licensing basis. Per the guidance, a 'fire' is defined as: 'Combustion characterized by heat and light. Sources of smoke such as slipping drive belts or overheated electrical equipment do not constitute as 'fires'. Observation of flame is preferred but is NOT required if large quantities of smoke and heat are observed.' "According to eyewitness reports from personnel, flames were not observed at any time and evidence of large quantities of heat and smoke were not observed. Additionally, the definition of 'fire' specifically excludes overheated electrical equipment. This information leads to the conclusion that the event did not meet the definition of a 'fire' per NEI 99-01 Revision 5. Therefore, the event is not an immediately reportable Unusual Event under 10 CFR 50.72(a)(1)(i)." The licensee notified the NRC Resident Inspector and will notify the state and local governments. Notified the R4DO (Haire) and NRR EO (Morris via e-mail). | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | MS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-06-08
51136 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-06-07 07:35 | 2015-06-07 12:03 | 2015-06-07 | AUTOMATIC REACTOR TRIP RESULTING FROM TURBINE TRIP ON LOW OIL PRESSURE "On June 7, 2015, at 0735 CDT, the Unit 2 Reactor automatically tripped while operating at 100 percent power due to an automatic Turbine trip due to low bearing oil pressure. The crew entered the reactor trip emergency operating procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. All safety functions operated as designed. The automatic Reactor trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the Auxiliary Feedwater Pumps as designed on low narrow range Steam Generator level and provided makeup flow to the Steam Generators. The Auxiliary Feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam Generator levels have been returned to normal. Auxiliary Feedwater has been secured. Steam Generators are being supplied by [the] 22 Main Feedwater Pump and decay heat is being removed by the condenser steam dump system. The cause of the Turbine trip remains under investigation. There was no effect on Unit 1 as a result of this trip. The health and safety of the public and site personnel were not at risk at any time during this event. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-06-07
51135 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2015-06-07 05:25 | 2015-06-07 05:46 | 2015-06-08 | NOTICE OF UNUSUAL EVENT FOR SECURITY CONDITION DUE TO NON-HOSTILE ACTION An individual approached the protected area and grabbed the fence. Local law enforcement assistance has been requested. The Security Team leader does not consider this to be hostile. An emergency declaration was made based on HU4.1, for a security condition that does not involve a hostile action. The licensee notified state and local agencies and informed the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer, and FEMA NWC and NuclearSSA via email. * * * UPDATE STEVE WILSON TO DAN LIVERMORE AT 0649 ON 06/07/2015 * * * The individual was taken into custody without incident. Notified R2DO (Rose), NRR EO (Morris), and IRD (GOTT). Notified DHS SWO, FEMA OPS Center, DHS NICC Watch Officer, and Nuclear SSA via email. * * * UPDATE AT 1616 EDT ON 6/8/2015 FROM MICHAEL MOORE TO MARK ABRAMOVITZ * * * "Update to correct description of where the individual was apprehended. "An individual approached the outside of the administrative fence near the circulating water intake structure. Local law enforcement assistance was requested. The Security Team Leader does not consider this to be hostile. "This declaration was made based on HU 4.1, a security condition that does not involve Hostile Action. "The NRC Resident Inspector has been notified." Notified the R2DO (Rose). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-06-08
51134 | 0 | DIABLO CANYON |  |  |  | ISFSI | 2015-06-06 17:03 | 2015-06-06 23:19 | 2015-06-09 | NOT MEETING TECHNICAL SPECIFICATIONS DUE TO INCORRECT LOADING OF CASKS "On June 6, 2015, during a review of Independent Spent Fuel Storage (ISFSI) cask loading, plant personnel discovered that for two casks, preferential loading was not used during uniform loading as required by ISFSI Technical Specification 2.1.2, Uniform and Preferential Fuel Loading. "ISFSI Technical Specification 2.1.2 requires that a preferential fuel loading configuration (i.e., that fuel assemblies with the longest cooling times shall be loaded into peripheral fuel storage locations) is used during uniform loading. Preferential loading was only partially met for two casks, designated MPC-253 and MPC-257. For these two casks, fuel assemblies with the longest cooling times were placed in the four center cask locations, which are only ones allowed for those assemblies containing control rods. "Engineering has performed an evaluation and determined that the fuel casks remain in a safe and analyzed condition.' "There is no adverse effect on the health and safety of the public. "The NRC Resident Inspector has been informed." * * * UPDATE FROM WESLEY FIANT TO DONALD NORWOOD AT 2100 EDT ON 6/9/2015 * * * "A full extent of condition review has determined that 17 of the 29 loaded casks in the Diablo Canyon ISFSI prior to the 2015 campaign were found to be out of compliance with ISFSI Technical Specification 2.1.2, Uniform and Preferential Fuel Loading. The casks were preferentially loaded based on heat load vs cooling time. "Engineering has performed an evaluation and determined that the fuel and casks remains in a safe and analyzed condition. "There is no adverse effect on the health and safety of the public. "The NRC Senior Resident Inspector has been informed." Notified R4DO (Werner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | CA | ISF | [5 empty] | 0 | 2015-06-06
51133 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-06-06 12:13 | 2015-06-06 17:22 | 2015-06-06 | LOSS OF TECHNICAL SUPPORT CENTER VENTILATION "This telephone notification is provided in accordance with Exelon Reportability manual SAF 1.1 0, 'Major Loss of Emergency Preparedness Capabilities', and 10CFR50.72(b)(3)(xiii). "On June 6th 2015 at 12:13 [CDT], it was determined that the onsite Technical Support Center (TSC) Ventilation System Supply Fan belts had failed, resulting in loss of ventilation for the facility. Repairs were not completed within the time required had the TSC needed to be staffed. There is currently no emergency event in progress requiring TSC staffing. If an emergency is declared and the TSC ERO activation is required, the TSC will be staffed and activated unless the TSC becomes uninhabitable due to ambient temperatures, radiological, or other conditions. If relocation of the TSC staff becomes necessary, the Station Emergency Director will relocate the staff to an alternate TSC location in accordance with applicable site procedures. "The licensee has notified the Senior Resident Inspector of the issue." *** UPDATE PROVIDED BY TODD CASAGRANDE TO NESTOR MAKRIS AT 2305 EDT ON 06/06/2015 *** "After repairs were completed, the TSC ventilation was restored to service at 2300 [EDT] on 06/06/2015. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Passehl) via email | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-06
51132 | 0 | THERMO FISHER SCIENTIFIC |  |  |  |  | 2015-03-03 | 2015-06-05 18:47 | 2015-07-01 | PART 21 - POSSIBLE SAFETY DEFECT IN NON-INSTALLED POWER RANGE DETECTOR AT PALISADES The following is an excerpt of a report that was received via email: "This letter provides information concerning an evaluation performed by Thermo Gamma-Metrics LLC, a part of Thermo Fisher Scientific, regarding potential noncompliance of our dual uncompensated ion chamber power range detector. "Based upon the evaluation, Thermo Gamma-Metrics has determined that a Reportable Condition under 10 CFR Part 21 exists for plant listed herein. The information contained in this document informs the NRC of the conclusions and recommendations derived from Thermo Gamma-Metrics' preliminary evaluation of this issue. "An evaluation [was] performed by Thermo Gamma-Metrics LLC, a part of Thermo Fisher Scientific, regarding potential noncompliance of our dual uncompensated ion chamber power range detector. "Based upon the evaluation, Thermo Gamma-Metrics has determined that a Reportable Condition under 10 CFR Part 21 exists for [Palisades]. The information contained in this document informs the NRC of the conclusions and recommendations derived from Thermo Gamma-Metrics' preliminary evaluation of this issue. "The detector in question is in storage at Entergy Palisades and has not yet been installed in their Power Range Systems per discussion with [the System Engineer at Palisades]. "A potential defect has been identified by Mirion IST. Thermo Gamma-Metrics cannot determine by itself if the potential defect would represent a substantial safety hazard to Entergy Palisades if installed in a safety related application. "We supplied just one potentially defective part from [Mirion] IST to Palisades. [Mirion] IST may have supplied two other potentially defective parts to other vendors per discussions with [Mirion IST.] "The immediate corrective action is for Thermo Gamma-Metrics to notify Entergy and the NRC of this potential defect. Thermo Gamma-Metrics notified Entergy Palisades on June 2, 2015. "Thermo Gamma-Metrics will supply a final report on this issue by July 2, 2015 that details the plan for all corrective actions. "Entergy Palisades should review the letter from Mirion IST. Thermo Gamma-Metrics will help the utility to address and remedy the situation before the power range detector is installed in the power plant." * * * UPDATE AT 1955 EDT ON 07/01/15 FROM ROB BARNES TO S. SANDIN * * * The following is an excerpt of a report that was received via email: "This letter provides information concerning an evaluation performed by Thermo Gamma-Metrics LLC, a part of Thermo Fisher Scientific, regarding noncompliance of our dual uncompensated ion chamber power range detector. "Based upon the evaluation, Thermo Gamma-Metrics has determined that a Reportable Condition under 10 CFR Part 21 exists for plant listed herein. The information contained in this document informs the NRC of the conclusions and recommendations derived from Thermo Gamma-Metrics' evaluation of this issue. "Report Notification Information (i) Name and address of the individual or individuals informing the Commission. Robert E. Barnes Technical Service Manager (858)449-2909 cell Clark J. Artaud Global Commercial Director Jeffery S. Tuetken Senior Electrical Engineer Thermo Gamma-Metrics LLC 10010 Mesa Rim Road San Diego, CA 92121 (ii) Identification of the facility, the activity, or the basic component supplied for such facility which fails to comply or contains a defect. "The detector in question is in storage at Entergy Palisades and has not yet been installed in their Power Range Systems per discussion with the System Engineer, Mr. Michael Knapp at Palisades. (iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. "Mirion IST Horseheads, New York (iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "A potential defect has been identified by Mirion IST as described in . . . [a letter] dated March 3, 2015. "Entergy Palisades has determined that the potential defect would represent a substantial safety hazard if installed in a safety related application and is returning the detector to Thermo Fisher Scientific for repair on Returned Material Authorization #950. Thermo Fisher will return the dual ion chamber to Mirion IST for repair and recertification. (v) The date on which the information of such defect or failure to comply was obtained. "March 3, 2015 (vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. "We supplied just one potentially defective part from IST to Palisades. IST may have supplied two other potentially defective parts to other vendors per discussions with Eric Brand at Mirion IST. (vii) The corrective action, which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "The immediate corrective action is for Thermo Gamma-Metrics to notify Entergy and the NRC of this potential defect. "Thermo Gamma-Metrics notified Entergy Palisades on June 2, 2015 . . . "Thermo Gamma-Metrics will work with Mirion IST to verify the presence or absence of the potential defect in this dual ion chamber and repair the dual ion chamber before returning it to Entergy Palisades, as soon as repairs can be arranged and expected no later than the end of 2015. (viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "Entergy Palisades has reviewed the letter from Mirion IST and is seeking reparations. Thermo Gamma-Metrics and Mirion IST will help the utility to address and remedy the situation before the power range detector is installed in the power plant. (ix) In the case of an early site permit, the entities to whom an early site permit was transferred. "Not applicable - this is not an early site permit concern. "Should you have any questions regarding this matter, please contact Rob Barnes Technical Service Manager, Thermo Gamma-Metrics LLC, at (858) 882-1356." Notified R3DO (Kozak) and PART 21/50.55 REACTORS (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-06-05
51131 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2015-06-05 13:30 | 2015-06-05 19:22 | 2015-06-05 | LOSS OF DECAY HEAT REMOVAL TO THE 'A' STEAM GENERATOR "Fort Calhoun Station is currently completing a scheduled refueling outage. On June 5, 2015 at 1330 during performance of surveillance testing on the auxiliary feed water system, [Hydraulic Control Valve] HCV-1107A, Steam Generator RC-2A Auxiliary Feedwater Inlet Valve, did not open when given an open signal. HCV-1107A has been declared inoperable. HCV-1107A is required to open to meet the decay heat removal safety function for Steam Generator A. Fort Calhoun Station is in Mode 3 (Reactor Coolant System temperature is greater than 515 degrees Fahrenheit and not critical). With HCV-1107A inoperable and unable to feed the A steam generator both auxiliary feedwater trains are considered inoperable. HCV-1107A is inside the Containment Building. "Fort Calhoun Station Technical Specifications 2.5(1)D. requires: With both AFW trains inoperable, then initiate actions to restore one AFW train to OPERABLE status immediately. Technical Specification (TS) 2.0.1 and all TS actions requiring MODE changes are suspended until one AFW train is restored to OPERABLE status. "Fort Calhoun Station is evaluating the best approach to repairing HCV-1107A. "The Resident Inspector has been notified." * * * UPDATE PROVIDED BY CHARLIES SMITH TO RICHARD SMITH AT 2300 EDT ON 06/05/2015 * * * "Fort Calhoun Station has determined plant cooldown required to perform repairs. Plant cooldown in progress." The licensee will notify the NRC Resident Inspector. Notified R4DO (Whitten) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2015-06-05
51130 | -1 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2015-06-04 | 2015-06-05 15:22 | 2015-07-06 | AGREEMENT STATE REPORT - MEDICAL TREATMENT INCORRECT DOSE The following was received via email: "On June 5, 2015, the Arkansas Department of Health (ADH) received notification from the licensee's Radiation Safety Officer (RSO) of a possible medical event that occurred during an Yttrium-90 TheraSpheres procedure on June 4, 2015. The licensee has not completed the investigation and has provided limited information to determine if the procedure constituted a medical event. "The patient was treated with Y-90 TheraSpheres. The written directive prescribed a dose of 114 Gy, but received a dose of 18.3 Gy. Preliminary findings seem to indicate that an incorrect dose may have been administered to the patient. "The patient and referring physician have been notified. "The licensee and ADH are continuing to investigate this event. ADH considers this event to be opened and will provide more information as it becomes available. "A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient." ARKANSAS EVENT #2015-005 * * * RETRACTION FROM JARED THOMPSON TO VINCE KLCO ON 7/6/2015 AT 1614 EDT * * * The following information was received from the State of Arkansas via email: "The Arkansas Department of Health (ADH) is requesting the retraction of NRC Event Number [51130]. "ADH received a report from the licensee dated June 18, 2015. The report and investigation conducted by the licensee determined that this event did not qualify as a reportable medical event. A review of the written directive indicated that the radiation dose that was prescribed by the authorized user was delivered to the patient. The authorized user had intended to prescribe 114 Gray. "This was confirmed by ADH after further review of the documentation obtained during the on-site investigation. "The patient completed this treatment on June 29, 2015. "The licensee has implemented revisions in the treatment procedures for further safety improvements. "The ADH considers this event to be closed." Notified the R4DO (Haire) and NMSS Events Notification Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-06-15
51129 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2015-06-05 18:12 | 2015-06-05 18:12 | 2015-06-05 | PART 21 - INCORRECT PART NUMBER RELAY SHIPPED TO BRUNSWICK NUCLEAR PLANT The following is an excerpt of communication received via fax: "Summary: Engine Systems Inc. (ESI) began a 10CFR21 evaluation on 04/13/15 upon discovery that governor control panels shipped to Brunswick Nuclear Plant contained an incorrect part number relay. The evaluation was concluded on 06/05/15 and it was determined that this issue is a reportable defect as defined by 10CFR Part 21. Under certain adverse conditions, a panel with the incorrect part number relay may lose power thereby resulting in inoperability of the electronic control portion of the control system. This could prevent the emergency diesel generator set from performing its safety-related function during an emergency event. "Discussion: The relay in question is the Governor Control At Setpoint (GCASP) relay installed in the governor control panel assembly P/N 8002096-PANEL. The panel provides speed control functions for the emergency diesel generator (EDG). In the original panel design the part number specified was 219XBX282NE. During the course of EMC testing, it was determined that the EMI suppression diode within in the GCASP relay must be removed in order for the EUT to comply with the requirements of [International Electrotechnical Commission] IEC 61000-4-5. When the diode was installed and the negative polarity portion of surge testing forward biased the diode, this resulted in a short circuit connection between the supply and return conductors of the control panel's power. This caused the fuses designed to protect the panel from overcurrent conditions to fail open; resulting in a loss of power to the control panel. "In place of the EMI suppression diode, a [Metal Oxide Varistor] MOV (P/N V150LA10AP) was added across terminals 6 & 7 of the GCASP relay socket. The MOV provides similar EMI suppression to the removed diode and responds appropriately to either polarity of surge waveform. The MOV is external to the relay and is considered a separate component. The MOV is not affected by this notification. "Removal of the internal EMI suppression diode for the GCASP relay resulted in a part number change. The relay part number that should have been installed is P/N 219XBX283NE. The part number of the relay actually installed was P/N 219XBX282NE. The difference between the two relays is that P/N 219XBX282NE contains an internal suppression diode whereas 219XBX283NE does not. "Impact on Operability: During normal operating conditions, the EDG will perform its safety related function with the incorrect GCASP relay installed in the governor control panel. Both relays provide the same switching function. "However, if a negative polarity surge similar to the requirements of IEC 61000-4-5 were to occur on the 125 VDC bus with the incorrect relay installed, the control panel may lose power. The 27GP relay would de-energize, alerting plant personnel of an under-voltage condition within the governor control panel. The EDG would remain operable on the mechanical governor though the electronic control portion would be inoperable. "Root cause evaluation: An error by a technician in conjunction with a lapse in oversight allowed this problem to occur. Contributing to the issue was that only one digit differentiates the two part number relays and both have the same overall appearance (size, shape, case style, etc). "Evaluation of previous shipments: This issue only affects one part number (qty 4) supplied on one customer purchase order. "Corrective Action: The customer was advised of the situation via letter 'Notice of GCASP Relay Discrepancy - Governor Control Panel' sent on 04/15/15. The correct relays were then supplied to the customer as dedicated, safety-related replacements on ESI IWO 8002474 (Brunswick PO 00786240) for installation in the panels. There are four panels affected, each containing one of these relays. ESI supplied four replacement relays which were [Certificate of Conformance] C-of-C'd and shipped on 04/17/15. These are plug-in style relays and to replace the relay only requires pulling out the old relay and plugging in the new relay. No special tools or instructions are necessary." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-06-05
51128 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-05-24 19:30 | 2015-06-05 14:19 | 2015-06-05 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "This 60-day report, as allowed by 10CFR 50.73(a)(1), is being made pursuant to 10CFR 50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of containment isolation valves. "At 1930 EDT on May 24, 2015, a loss of power to Reactor Protection System (RPS) Train B occurred. Initial investigation found the RPS Motor Generator (MG) Set B not running, with its Motor Off light illuminated caused by both Normal EPA breakers and MG Set B output breaker being tripped. Visual inspection at the distribution cabinet was inconclusive at the time and revealed no abnormalities and no abnormal odors in the area. Further investigation of the RPS MG Set B verified normal voltages on all fuse clips, and all power and control power fuses were operational. "As a result of the loss of RPS B, the following containment isolation valves closures occurred: Reactor Water Cleanup (RWCU) Outboard Isolation valves, Torus Water Management System (TWMS) Outboard Isolation valves, Division 2 Drywell Pneumatics Inboard and Outboard Isolation valves, Primary Containment Radiation Monitoring System Inboard and Outboard Isolation valves, Reactor Recirculation Pump Seal Purge Flow Outboard Isolation valves, and Drywell Floor and Equipment Drain Sump Inboard Isolation Valves. "The Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-06-05
51127 | 0 | INDIANA UNIVERSITY HEALTH |  |  |  |  | 2015-06-05 02:00 | 2015-06-05 09:27 | 2015-06-05 | RADIOACTIVE SURFACE CONTAMINATION EXCEEDS LIMITS The licensee nuclear medicine technologist ordered a package containing radioisotopesTc-99m and Xenon for a patient. The package was delivered by an offsite nuclear pharmacy to the Indiana University Health- Ball Memorial Hospital. When the technician surveyed the package, the surface contamination exceeded specified limits and nominally measured about 14,000 dpm. The package was quarantined and the vendor/shipper was notified concerning the surface contamination. The package was placed in a gamma camera and the indicated camera spectrum indicates Xenon package contamination. The Radiation Safety Officer has ordered the package to remain quarantined. No personnel contamination resulted from this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2015-06-15
51126 | -1 | DIABLO CANYON |  |  |  | ISFSI | 2015-06-04 13:45 | 2015-06-04 22:12 | 2015-06-30 | NOT MEETING TECHNICAL SPECIFICATIONS DUE TO OMISSION IN PREVIOUS LICENSE AMENDMENT "On June 4, 2015, plant personnel notified the Diablo Canyon shift manager that three casks loaded during the current ISFSI campaign were not in verbatim compliance with Technical Specification (TS) 2.3. These three casks utilized regionalized loading. TS 2.3 (Alternate MPC-32 Fuel Selection Criteria) specifies fuel assembly selection criteria based using information from corresponding Tables 2.1-7 (uniform loading) or 2.1-9 (regionalized loading). However, the associated formula in TS 2.3 refers only to using the values in Table 2.1-7 (uniform loading). "Engineering has performed an evaluation and determined there is no impact on the fuel stored in the three casks. Table 2.1-9 is described as being acceptable in Technical Specification 2.3, although omitted from the formula in TS 2.3. "It appears that the inconsistency in TS 2.3 was due to an error of omission in the previous License Amendment Request, which did not appropriately add the reference to Table 2.1-9 to the formula presented in TS 2.3 as originally intended. "This concern did not result in any adverse affect on the health and safety of the public. "The NRC Resident Inspector has been informed." * * * RETRACTION AT 1728 EDT ON 06/30/15 FROM DARRELL JOHNSON TO STEVE VITTO * * * "The fuel assembly loading of the three casks discussed in the original event notification has been re-evaluated. This evaluation was performed to determine that compliance to ISFSI Technical Specification 2.3.b was maintained using the uniform loading values of Table 2.1-7. The calculation revision demonstrates that the fuel placed in region 1 and 2 of the regionalized casks loads complied with the ISFSI Technical Specification requirements as written. "Therefore, the requirements of TS 2.3 were met for the subject casks and this event notification is being retracted." The NRC Resident Inspector, R4DO(O'Keefe), and NMSS Events (via email) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | CA | ISF | [5 empty] | 0 | 2015-06-04
51125 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-06-03 | 2015-06-04 18:10 | 2015-06-04 | AGREEMENT STATE REPORT - FAILURE OF SHUTTERS ON FOUR FIXED NUCLEAR GAUGES TO CLOSE The following information was received via E-mail: "On June 4, 2015, the licensee notified the Agency [Texas Department of State Health Services] that on June 3, 2015, it was performing routine shutter checks on fixed nuclear gauges at its facility and found the shutters on four of the gauges would not close. All four gauges were Ronan Model SA-1 containing cesium-137 sources (20, 40, 50, and 200 millicuries). The licensee lubricated the shutter mechanisms on all four gauges and let them sit overnight. Two of the gauges closed the next morning (June 4th) with no problem. The other two shutters still would not close. The licensee contacted an outside service group and it recommended using a different lubricant. The licensee followed the suggestion and both became operable that afternoon. These gauges normally operate with the shutter in the open position. There were no radiation exposures or increased risk of exposure as a result of this event. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident Number: I-9318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-06-12
51124 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-06-04 15:56 | 2015-06-04 16:55 | 2015-06-04 | SALE OF A CONTROLLED PRESCRIPTION DRUG WITHIN THE PROTECTED AREA "In accordance with safeguards events reportable under paragraph 10 CFR 73.71(b) and described in Appendix G to 10 CFR Part 73, (specifically as described in Regulatory Guide 5.62, Section 2.2), Southern Nuclear makes the following report: "An SNC [Southern Nuclear Company] employee that had unescorted access reported that another individual with unescorted access sold prescription medication to him on site and within the protected area." Plant access for both employees has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | SAFEGUARDS REPORTS |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 | 73.71(b)(1) |  |  | 1 | 2015-06-04
51123 | 0 | NUTHERM INTERNATIONAL, INC |  |  |  |  | 2015-06-04 | 2015-06-04 14:34 | 2015-06-04 | PART 21 - POTENTIAL FAILURE OF A TIME RELAY The following was received via facsimile: "Allen Bradley relay base model 700RTC contains an unevaluated CPLD (Complex Programmable Logic Device). This was an unpublished design change that did not result in a part number change from Allen Bradley. There was no change to the appearance of the relay that would identify any design changes made to the relay configuration. Allen Bradley has indicated that the change occurred in mid-2009 and that it was a rolling change with no specific manufacturing date to distinguish between the old and new configuration. Based on this information, all units manufactured during 2009 and later are suspect. "Nutherm International, Inc. has concluded its review of all procurements of the 700RTC series relays and have found two (2) units manufactured during or after 2009 dedicated and shipped to customers. The following facility was determined to be impacted by this condition: Utility: Exelon Plant: Quad Cities Purchase Order: 00447625 Part Number: 700-RTC11110U1 Nutherm Traceability Number: 11340-02R01 1/01, 11340-02R01 1/02. "In a separate 10CFR Part 21 notification, Event Number 51095, reported to the NRC [on] 5/28/2015 indicated that the CPLD can be affected by electrical noise from operation of nearby relays which can reset the timing of the relay. The plant should evaluate whether the installed relays are subjected to unevaluated EMI/RFI [electromagnetic interference/radio-frequency interference] conditions when installed in the plant." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-06-04
51122 | 0 | ARCELORMITTAL BURNS HARBOR |  |  |  |  | 2015-06-04 08:30 | 2015-06-04 15:12 | 2015-06-04 | STUCK GAUGE SHUTTER The following was received via email: "On June 4, 2015 at approximately 0830 [EDT], [the Radiation Safety Officer] was contacted by radiation trained employees at the licensee's Hot Rolling Facility. The employees indicated that the shutter on one of the slab detection radiation gauges would not close. The employee also indicated he noticed a shiny metallic material adjacent to the gauge housing on one side. As a result, they contacted the Radiation Safety Officer (RSO) and [he] proceeded to the site to investigate. "[The RSO] informed them to barricade the area until [he] arrived. Upon arrival, [the RSO] conducted a survey of the area and compared the levels to prior surveys (including the installation survey). [The RSO] found no significant difference in radiation levels. [He] also performed a wipe test on the gauge and checked it with a survey meter and pancake probe, finding no detectable radiation. The melted metallic material appeared to possibly be lead from the device shielding. As a result, [he] believes some shielding may have overheated and blocked the shutter open. "Because radiation levels were normal and the device was functioning normally, the device was left in its operating position on the furnace. This was the safest possible scenario until resources can be obtained to safely remove and store the device with the shutter open. The RSO will obtain a container that will house the device safely and will transport the device to a secure location in the plant (controlled by the RSO) until it can be retrieved and repaired by Ronan Engineering (manufacturer). The furnace will be in operation until the device is removed so there is no physical possibility of anyone being inside the furnace and being exposed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-06-12
51121 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-06-03 | 2015-06-04 14:32 | 2015-06-04 | AGREEMENT STATE REPORT - STOLEN MOISTURE/DENSITY GAUGE The following information was received via E-mail. "On June 3, 2015, Leighton & Associates notified RHB [California Department of Public Health, Radiologic Health Branch] that a moisture/density gauge was stolen from a pick-up truck's bed at a temporary job site in Riverside that morning. The gauge is a 2014 InstroTek model MC-3 Elite, s/n 30481, containing a 10 mCi Cs-137 source, s/n CZ4587 and a 50 mCi Am-241/Be source, s/n 038/14. "The authorized gauge technician reported the security cables were cut and the density gauge was missing while he was parked at the job site but away from his vehicle. He immediately notified his RSO and the Riverside Police, who took report number P15-082748. RHB's inspector spoke with the RSO and recommended that a lost and found ad be placed in the local newspaper offering a cash reward for the return of the stolen gauge and requested additional information from the responsible technician. The Inspection/Compliance/Enforcement section will review the security measures that were in place to determine if a violation of their license condition took place." California 5010 Report Number: 060315 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-06-12
51120 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-06-04 10:03 | 2015-06-04 12:56 | 2015-09-04 | UNANALYZED CONDITION FOR A POSTULATED FIRE "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48(c) (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Unit 1 and Unit 2 Reactor Buildings. This updated analysis has identified circuit configurations in four Fire Areas where an Appendix R postulated fire could impact the ability to achieve safe shutdown conditions. These are Category 1 barrier impairments. "In the Unit 1 Safe Shutdown Analysis, RCIC (1E51C001) (Path 1) components are impacted by a fire in Fire Area 1203. The postulated failure described above impacts HPCI (1E41C001) (Path 2) operation. Therefore, in the updated analysis there is no safe shutdown method for high pressure injection that remains free of fire damage for an Appendix R postulated fire in Fire Area 1203. While this represents an unanalyzed condition for Appendix R, the described scenario is only possible given a fire has occurred in Fire Area 1203. "In the Unit 1 Safe Shutdown Analysis, Path 2 components are impacted by a fire in Fire Area 1205. The postulated failure described above impacts the 1E 4160 Kv (1R22S005) emergency bus power to Path 1 components. Therefore, in the updated analysis there is no safe shutdown method that remains available for an Appendix R postulated fire in Fire Area 1205. While this represents an unanalyzed condition for Appendix R, the described scenario is only possible given a fire has occurred in Fire Area 1205. "In the Unit 2 Safe Shutdown Analysis, Path 2 components are impacted by a fire in Fire Area 2205. The postulated failure described above impacts the 2E 4160 Kv (2R22S005) emergency bus power to Path 1 components. Therefore, in the updated analysis there is no safe shutdown method that remains available for an Appendix R postulated fire in Fire Area 2205. While this represents an unanalyzed condition for Appendix R, the described scenario is only possible given a fire has occurred in Fire Area 2205. "In the updated post-fire safe shutdown model, both safe shutdown paths include the same three options for Torus Water Temperature indication (1T48R072, 1T47R611 or 1T47R612). Only one of these three components is required to succeed, however, all are impacted by the postulated fire. Thus, there is no Unit 1 Torus Water Temperature Indication available for a fire in Fire Area 1205. While this represents an unanalyzed condition for Appendix R, the described scenario is only possible given a fire has occurred in Fire Area 1205. "Based on the updated Plant Hatch Appendix R Safe Shutdown analysis recommendations and the plant's Fire Hazard Analysis (FHA), compensatory measures have been taken and will remain in place until the conditions are resolved. "The presence of the compensatory measures, in addition to portable fire protection equipment and installed fire protection and detection equipment, ensures the safe shutdown paths are preserved until the conditions are resolved. CR 10079009, 10079019, 10079022, 10079025" The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM STANLEY STONE TO DONALD NORWOOD AT 1634 EDT ON 6/17/2015 * * * "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48(c) (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Unit 1 and Unit 2 Turbine Building. This updated analysis has identified circuit configurations in two Fire Areas where an Appendix R postulated fire could impact the ability to achieve safe shutdown conditions. These are Category 1 barrier impairments. "1) In the Unit 1 Safe Shutdown Analysis, Path 1 RCIC components are impacted by a fire in Fire Area 1105. The postulated failure would impact Path 2 (HPCI) operation. Therefore, in the current analysis for the credited safe shutdown method for high pressure injection may be affected for an Appendix R postulated fire in Fire Area 1105. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1105. "2) In the updated post-fire safe shutdown model, both safe shutdown paths include the same two options for Torus Water Level Indication: 2T48-R622A and 2T48-R622B. Only one of these two components is required to succeed, however both would be impacted by a postulated fire in Fire Area 2104. Consequently, both credited paths of Unit 2 Torus Water Level Indication could potentially be affected due to a fire in Fire Area 2104. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2104. "Based on the updated Plant Hatch Appendix R Safe Shutdown analysis recommendations and the plant's Fire Hazard Analysis (FHA), compensatory measures have been taken and will remain in place until the conditions are resolved. "The presence of the compensatory measures, in addition to portable fire protection equipment and installed fire protection and detection equipment, ensures the safe shutdown paths are preserved until the conditions are resolved. The analysis associated with the transition of the Plant Hatch Fire Protection Licensing Basis from Appendix R to NFPA 805 is continuing, and this and any subsequent similar conditions that meet reporting requirements will be in included in an ENS Update Report. CR 10084753, CR 10084757." The licensee notified the NRC Resident Inspector. Notified R2DO (HAAG). * * * UPDATE FROM SCOTT BRITT TO VINCE KLCO ON 6/24/15 AT 2114 EDT * * * "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48(c) (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Diesel Generator Building. This updated analysis has identified circuit configurations in five Fire Areas where an Appendix R postulated fire could impact the ability to achieve safe shutdown conditions. These are Category 1 barrier impairments. "1) An Appendix R postulated fire in Fire Area 1404 is assessed to impact a cable required for RHR Inboard Injection Valve A, 1E11-F015A, to open. This cable was not identified in the current Safe Shutdown Analysis Report (SSAR) for this component. This valve is normally closed and is required to open to support the operation of RHR Loop A in LPCI mode, which is the credited Low Pressure Injection system for Unit 1 in support of Inventory Control to the RPV for a fire in Fire Area 1404. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1404. RHR Loop B is not available in this fire area due to fire impacts. 2) An Appendix R postulated fire in Fire Area 1408 is assessed to impact cables required for RHR Inboard Injection Valve B, 1E11-F015B, to open. These cables were not identified in the current Safe Shutdown Analysis Report (SSAR) for this component. This valve is normally closed and is required to open to support the operation of RHR Loop B in LPCI mode, which is the credited Low Pressure Injection system for Unit 1 in support of Inventory Control to the RPV for a fire in Fire Area 1408. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1408. RHR Loop A is not available in this fire area due to fire impacts. 3) An Appendix R postulated fire in Fire Area 1412 is assessed to impact a cable required for RHR Inboard Injection Valve B, 1E11-F015B, to open. This cable was not identified in the current Safe Shutdown Analysis Report (SSAR) for this component. This valve is normally closed and is required to open to support the operation of RHR Loop B in LPCI mode, which is the credited Low Pressure Injection system for Unit 1 in support of Inventory Control to the RPV for a fire in Fire Area 1412. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1412. RHR Loop A is not available in this fire area due to fire impacts. 4) An Appendix R postulated fire in Fire Area 2404 is assessed to impact a cable required for RHR Inboard Injection Valve B, 2E11-F015B, to open. This cable was not identified in the current Safe Shutdown Analysis Report (SSAR) for this component. This valve is normally closed and is required to open to support the operation of RHR Loop B in LPCI mode, which is the credited Low Pressure Injection system for Unit 2 in support of Inventory Control to the RPV for a fire in Fire Area 2404. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2404. RHR Loop A is not available in this fire area due to fire impacts. 5) An Appendix R postulated fire in Fire Area 2408 is assessed to impact cables required for RHR Inboard Injection Valve B, 2E11-F015B, to open. These cables were not identified in the current Safe Shutdown Analysis Report (SSAR) for this component. This valve is normally closed and is required to open to support the operation of RHR Loop B in LPCI mode, which is the credited Low Pressure Injection system for Unit 2 in support of Inventory Control to the RPV for a fire in Fire Area 2408. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2408. RHR Loop A is not available in this fire area due to fire impacts. "Based on the updated Plant Hatch Appendix R Safe Shutdown analysis recommendations and the plant's Fire Hazard Analysis (FHA), compensatory measures have been taken and will remain in place until the conditions are resolved. "The presence of the compensatory measures, in addition to portable fire protection equipment and installed fire protection and detection equipment, ensures the safe shutdown paths are preserved until the conditions are resolved. The analysis associated with the transition of the Plant Hatch Fire Protection Licensing Basis from Appendix R to NFPA 805 is continuing, and this and any subsequent similar conditions that meet reporting requirements will be in included in an ENS Update Report. "CR 10088142" The licensee will notify the NRC Resident Inspector. Notified the R2DO (O'Donohue). * * * UPDATE AT 1739 EDT ON 08/13/15 FROM PAUL UNDERWOOD TO JEFF HERRERA * * * "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48(c) (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Control Building. This updated analysis has identified circuit configurations in a Fire Area where an Appendix R postulated fire could impact the ability to achieve safe shutdown conditions. This is a Category 1 barrier impairment. "1) An Appendix R postulated fire in Fire Area 0014 is assessed to impact a cable that is required for Diesel Building MCC 1C, 1R24-S027, to remain energized. Further analysis has shown that an inter-cable hot short between two conductors could cause the feeder breaker to this MCC to trip. This MCC is required to support the operation of Diesel Generator 1C, which is a credited power source in the Safe Shutdown analysis for both Unit 1 and Unit 2 in the event of a fire in this area. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 0014. "Based on the updated Plant Hatch Appendix R Safe Shutdown analysis recommendations and the plant's Fire Hazard Analysis (FHA), compensatory measures have been taken and will remain in place until the conditions are resolved. "The presence of the compensatory measures, in addition to portable fire protection equipment and installed fire protection and detection equipment, ensures the safe shutdown paths are preserved until the conditions are resolved. "CR 10108999." The licensee notified the NRC Resident Inspector. Notified the R2DO (Nease). * * * UPDATE AT 1331 EDT ON 08/25/15 FROM JOHN MITCHELL TO JEFF HERRERA * * * "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48c (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Diesel Building. This updated analysis has identified circuit configurations in a Fire Area where an Appendix R postulated fire could impact the ability to achieve safe shutdown conditions. This is Category 1 barrier impairment. "1) An Appendix R postulated fire in Fire Area 1408 is assessed to impact a cable that is required for Station Battery Chargers 1D, 1E, and 1F to remain energized. These chargers support 125V DC Switchgear 1B which is the credited DC Switchgear for Unit 1 Path 2 Safe Shutdown in the event of a fire in this area. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1408. "2) An Appendix R postulated fire in Fire Area 2408 is assessed to impact a cable that is required for Station Battery Chargers 2D, 2E, and 2F to remain energized. These chargers support 125V DC Switchgear 2B which is the credited DC Switchgear for Unit 2 Path 2 Safe Shutdown in the event of a fire in this area. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2408. "Based on the updated Plant Hatch Appendix R Safe Shutdown analysis recommendations and the plant's Fire Hazard Analysis (FHA), compensatory measures have been taken and will remain in place until the conditions are resolved. "The presence of the compensatory measures, in addition to portable fire protection equipment and installed fire protection and detection equipment, ensures the safe shutdown paths are preserved until the conditions are resolved. The analysis associated with the transition of the Plant Hatch Fire Protection Licensing Basis from Appendix R to NFPA 805 is continuing, and this and any subsequent similar conditions that meet reporting requirements will be in included in an ENS Update Report. "CR 10113740, CR 10113745" The Licensee notified the NRC Resident Inspector. Notified the R2DO (Rose). * * * UPDATE FROM KENNY HUNTER TO DONALD NORWOOD AT 1717 EDT ON 8/28/2015 * * * "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48(c) (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Turbine Building. This updated analysis has identified circuit configurations in a Fire Area where an Appendix R postulated fire could impact the ability to achieve safe shutdown (SSD) conditions. This is a Category 1 barrier impairment. "1) An Appendix R postulated fire in Fire Area 1105 is assessed to impact cables which are required for HPCI Steam Supply Isolation MOV, 1E41-F002, to remain open. This valve is required open in support of HPCI (SSD Path 2), which is the credited form of high pressure injection in this fire area. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1105. "2) An Appendix R postulated fire in Fire Area 1104 is assessed to impact a cable required for the RCIC Vacuum Breaker Isolation MOV, 1E51-F105, to remain open. This valve is required open to ensure operability of the RCIC turbine if RCIC is required to stop and restart. Failure of this valve to remain open could cause a siphon that would impact the operability of RCIC, and thus disable Safe Shutdown Path 1 High Pressure Injection. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1104. "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48(c) (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Reactor Building. This updated analysis has identified circuit configurations in a Fire Area where an Appendix R postulated fire could impact the ability to achieve safe shutdown conditions. This is a Category 1 barrier impairment. "1) An Appendix R postulated fire in Fire Area 1203 is assessed to impact a cable required for HPCI Steam Supply Isolation MOV, 1E41-F002, to remain open. This valve is required open to ensure steam flow to the HPCI turbine. Failure of this valve to remain open would isolate steam to the HPCI turbine, which would disable HPCI, and thus disable Safe Shutdown Path 2 High Pressure Injection. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 1203. "2) An Appendix R postulated fire in Fire Area 2203 is assessed to impact cables required for RHR Outboard Injection Valve B, 2E11-F017B, to remain open. This valve is required open to support RHR Loop B in LPCI mode, which is the credited lineup for Path 2 Safe Shutdown Decay Heat Removal. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2203. "3) An Appendix R postulated fire in Fire Area 2203 is assessed to impact cables required for HPCI Vacuum Breaker Isolation Valve, 2E41-F104, to remain open. This valve is required open in support of Safe Shutdown Path 2 High Pressure Injection. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2203. "Based on the updated Plant Hatch Appendix R Safe Shutdown analysis recommendations and the plant's Fire Hazard Analysis (FHA), compensatory measures have been taken and will remain in place until the conditions are resolved. "The presence of the compensatory measures, in addition to portable fire protection equipment and installed fire protection and detection equipment, ensures the safe shutdown paths are preserved until the conditions are resolved. The analysis associated with the transition of the Plant Hatch Fire Protection Licensing Basis from Appendix R to NFPA 805 is continuing, and this and any subsequent similar conditions that meet reporting requirements will be in included in an ENS Update Report. "CR 10115432, CR10115473, CR10115436, CR10115446, CR10115444" The licensee will notify the NRC Resident Inspector. Notified R2DO (Rose). * * * UPDATE PROVIDED BY GUY GRIFFIS TO JEFF ROTTON AT 1815 EDT ON 09/04/2015 * * * "In preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10CFR50.48(c) (NFPA 805), an update to the Plant Hatch Appendix R Safe Shutdown Analysis has been performed for the Control Building and Reactor Building. This updated analysis has identified circuit configurations in Fire Area's where an Appendix R postulated fire could impact the ability to achieve safe shutdown (SSD) conditions. These are Category 1 barrier impairments. "1) An Appendix R postulated fire in Fire Area 0024 is assessed to impact a cable that is required for Torus Suction Valve, 1E11-F065B to remain open. This valve is required to remain open in support of LPCI train B which is credited for Unit 1 Safe Shutdown in the event that the RPV has spuriously depressurized and low pressure inventory control is performed from the remote shutdown panel. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 0024. "2) An Appendix R postulated fire in Fire Area 0024 is assessed to impact a cable required for Torus Suction Valve, 2E11-F065B to remain open. This valve is required to remain open in support of LPCI train B which is credited for Unit 2 Safe Shutdown in the event that the RPV has spuriously depressurized and low pressure inventory control is performed from the remote shutdown panel. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 0024. "3) An Appendix R postulated fire in Fire Area 0014 is assessed to impact all three Air Handling Units; 1Z41-B003A, 1Z41-B003B, and 1Z41-B003C. The fire impacts a cable required for MCC 1C, 1R23-S003 to remain energized. This MCC supports the operation of Air Handling Unit B, 1Z41-B003B which is required in support of Main Control Room HVAC. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 0014. "4) An Appendix R postulated fire in Fire Area 0031 is assessed to impact all three Air Handling Units; 1Z41-B003A, 1Z41-B003B, and 1Z41-B003C. These AHUs are required in support of MCR HVAC. MCR HVAC was not required in the current Safe Shutdown Analysis Report, and thus these failures were not evaluated in this fire area. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 0031. "5) An Appendix R postulated fire in Fire Area 2014 is assessed to impact a cable required for Station Battery Chargers 2A (2R42-S026) 2B (2R42-S027) and 2C (2R42-S028) to remain energized. These chargers support 125 VDC Switchgear 2A (2R22-S016), which is the credited DC Switchgear for Path 1 Safe Shutdown. Path 2 Safe Shutdown is not available in this fire area due to fire impacts. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2014. "6) An Appendix R postulated fire in Fire Area 2014 is assessed to impact a cable required for 125 VDC Switchgear 2A (2R22-S016) to remain energized. This is the credited DC Switchgear for Path 1 Safe Shutdown. Path 2 Safe Shutdown is not available in this fire area due to fire impacts. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 2014. "7) An Appendix R postulated fire in Fire Area 0014 is assessed to impact cables required for Station Battery Chargers 1D (1R42-S029), 1E (1R42-S030), and 1F (1R42-S031) to remain energized. These chargers support 125VDC Switchgear 1B (1R22-S017) which is the credited DC Switchgear for Path 2 Safe Shutdown. Path 1 Safe Shutdown is not available in this fire area due to fire impacts. While this represents an unanalyzed condition for Appendix R, the described scenario presumes a fire has occurred in Fire Area 0014. "Based on the updated Plant Hatch Appendix R Safe Shutdown analysis recommendations and the plant's Fire Hazard Analysis (FHA), compensatory measures have been taken and will remain in place until the conditions are resolved. "The presence of the compensatory measures, in addition to portable fire protection equipment and installed fire protection and detection equipment, ensures the safe shutdown paths are preserved until the conditions are resolved. The analysis associated with the transition of the Plant Hatch Fire Protection Licensing Basis from Appendix R to NFPA 805 is continuing, and this and any subsequent similar conditions that meet reporting requirements will be in included in an ENS Update Report. "CR 10118312, CR 10118328, CR10118333, CR10118338, CR10118345" The licensee will notify the NRC Resident Inspector. Notified R2DO (Seymour) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-06-04
51119 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-06-04 08:39 | 2015-06-04 12:30 | 2015-06-04 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISORY EMPLOYEE A non-licensed supervisory employee had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2015-06-04
51118 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2015-06-02 | 2015-06-04 12:28 | 2015-06-04 | AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO MIS-ADMINISTRATION OF Y-90 SIR-SPHERES The following information was received via E-mail: "The Director of Radiology at Riverside Medical Center, Kankakee, IL called the Agency [Illinois Emergency Management Agency] to advise that a medical event had occurred during the administration of a Y-90 SIR-Sphere treatment on the morning of June 2, 2015. 35.2 mCi of Y-90 was intended to be delivered to the patient's liver to treat metastatic cancer lesions via the hepatic artery. However, when the patient was imaged immediately following the treatment, the kidney was observed as the organ which had received the dose with no material evident in the liver. It was determined that the infusion catheter was improperly placed. Instead of placement in the patient's hepatic artery, the renal artery was the infusion site. This was the facility's first patient to undergo this treatment modality. As a result, the manufacturer's proctor was present in addition to the treatment team members which included the radiologist, the radiation safety officer, the nuclear medicine technologist as well as others. "The radiologist immediately informed the patient of the error while he was in post-op. As the facility had a second dose of Y-90 on hand of the same amount, and the patient consented, a second attempt was made that same afternoon where the infusion went as expected and the intended dose was delivered as originally planned to the liver with no complications. "Although normally, an outpatient procedure, the patient was held overnight. Universal precautions were implemented throughout the time period and although the patient's sweat and saliva were not sources of contamination, the hospital managed the patient as they would an I-131 therapy patient and routine collection and measurement of the patient's urine was performed before discharge to the sewer system.. Radioactivity was confirmed as present in the urine when measured with a Geiger counter near the surface of the container. No other contamination was noted in the room. The patient was discharged the next day and follow up appointments are pending with the radiologist as well as a urologist. "Dose estimates to the patient's kidney as a result of the event are being performed by the manufacturer as well as the medical center's consultant. The Agency is investigating this event and the licensee has been advised that a written report must be submitted per regulation." Illinois Item Number: IL15013 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2015-06-12
51117 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-04-12 13:20 | 2015-06-04 11:18 | 2015-06-04 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID CONTAINMENT ISOLATION ACTIVATION. "This 60-day telephone notification is being submitted in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to report an invalid actuation of the Train B Phase A Containment Isolation at Sequoyah Nuclear Plant. "At 1320 EDT on April 12, 2015, during planned performance of the Containment Isolation Train-A, Phase A Isolation Testing and Emergency Gas Treatment System (EGTS) Cleanup System Test, the main control room received several Train-B annunciators. Upon investigation, it was determined that an invalid signal to the Train-B Solid State Protective System (SSPS) actuated the Train B, Phase A Containment Isolation. The invalid isolation signal was the result of a human performance error during the performance of the Phase A Isolation Test surveillance procedure. Operations personnel responded to the SSPS initiation, testing was aborted, ensured that all equipment operated as designed and restored affected systems in accordance with plant procedures. Approval to restart testing was obtained. All prerequisites were met and testing of the SSPS Train-A, Phase A Isolation was completed satisfactorily. "As part of the prerequisite test alignment of the Train-A, Phase A, Unit 2 had entered a planned 7 day action for EGTS being inoperable. During the test when the Train-B of Phase A actuated, the suction dampers for Unit 1 supply to EGTS were closed per plant procedures. This prevented Train-B EGTS from aligning to Unit 1 and allowed Train-B of EGTS to remain operable for Unit 2. An SSPS Phase A signal can be generated automatically by a Safety Injection Signal (SIS) or manually. At the time of the event, plant conditions for an SIS did not exist; therefore, the Phase A actuation was invalid. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-06-04
51116 | 0 | WATERFORD | 3 |  |  | [3] CE | 2015-06-03 17:05 | 2015-06-03 21:36 | 2015-06-03 | MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEEDWATER PUMP "This is a non-emergency notification from Waterford 3. "At 1705 [CDT] the reactor was manually tripped in anticipation of an automatic trip due to loss of main feedwater pump 'A'. "The plant is currently in mode 3 and stable with emergency feedwater feeding and maintaining both steam generators due to an automatic emergency feed actuation signal. "During the trip, the 'B' electrical safety and non safety busses did not automatically transfer from the unit auxiliary transformer to the startup transformer causing a loss of off-site power to the 'B' electrical busses. This resulted in a loss of main feedwater pump 'B'. "The 'B' emergency diesel generator started as designed and reenergized the 'B' safety related buses. "The plant entered the emergency operating procedure for loss of main feedwater. "Off-site power has been restored to the 'B' safety and non safety busses, and the emergency diesel generator 'B' is secured. All control rods fully inserted into the core following the trip. Decay heat is being removed by the main condenser using the turbine bypass valves. The electric plant is in a normal shutdown lineup. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-06-03
51115 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-06-01 10:26 | 2015-06-03 16:02 | 2015-06-03 | LOSS OF UNIT 2 VENTILATION RADIATION MONITOR OPERABILITY "On June 2, 2015 at 2027 CDT, it was discovered that the unit vent radiation monitor was inoperable beginning on June 1, 2015 at 1026 CDT. Compensatory measures were not taken in accordance with the Offsite Dose Calculation Manual (ODCM) during this time period and the radiation monitor was unable to be used to assess Emergency Action Levels in accordance with the Emergency Plan. On June 3, 2015 it was recognized that because no compensatory measures were implemented during the period of inoperability that the condition resulted in a major loss of emergency assessment capability which is reportable under 10CFR50.72(b)(3)(xiii). Compensatory measures were implemented per the ODCM upon discovery on June 2 at 2027, thus there is currently no major loss of emergency assessment capability. "This event did not result in any challenges to the fission product barriers and it did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector will be notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-03
51114 | 0 | FABRI-FORM COMPANY |  |  |  |  | 2015-06-02 | 2015-06-03 11:53 | 2015-06-03 | MISSING IONIZERS The following was excerpted from information received via facsimile: "This letter follows up on an [initial] telephone report provided to the NRC Operations Center [at 1153 EDT] today pursuant to 10 CFR 20.2201(a)(i) regarding potentially missing NRC-regulated devices. During that call, Fabri-Form was asked to also submit [additional information] via facsimile to the NRC, providing information about the material contained in the devices, their serial numbers, and explaining how we became aware of the loss. Fabri-form is also submitting this letter pursuant to that request. We are also conducting an internal investigation into the matter and will submit a written report, as required under 10 CFR 20.2201(b), within 30 days. "It appears that the potentially missing devices are six P-2021-8000 Ionizers, which are manufactured by NRD LLC. As we understand, these ionizers originally contained 10 mCi of polonium 210 and the serial numbers for the devices are A2FG071- 076. "Fabri-Form became aware that it might possess NRC generally licensed devices on March 31, 2015, when it received a standard letter from the NRC's Office of Nuclear Material Safety and Safeguards, stating that the company possesses generally licensed devices subject to NRC oversight. The letter did not specify what those devices were and after internal inquiry, Fabri-Form was unable to determine what those devices were. Fabri-Form contacted Hector Rodriguez-Luccioni, the NRC contact listed in the letter [on 6/2/2015] and based on information provided by the manufacturer to the NRC, he was able to provide us with additional information, including what these devices were, the manufacturer, device serial numbers, and that their delivery date to Fabri-Form was August 2006. Fabri-Form also contacted the manufacturer yesterday, who confirmed the NRC's information. Fabri-Form has only one employee that has been with the company since 2006, and that individual was unable to recall specific details about these devices when we initially contacted them. Thus, after conversations with the NRC and NRD LLC yesterday, Fabri-Form first determined what these devices were and that they are potentially missing yesterday, and we promptly notified the NRC within 24 hours, as required under 10 CFR 20.2201(a)(i). "Fabri-Form will continue to investigate this matter and detail the findings of our investigation in the required written report." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-06-11
51113 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2015-05-07 | 2015-06-02 17:08 | 2015-06-02 | AGREEMENT STATE REPORT - LOST Co-57 SOURCE "This event was reported by Digirad Imaging Solutions, Inc. that occurred at a client facility in Melrose, MA. Digirad Imaging Solutions is a mobile nuclear medicine company that provides imaging services at client facilities in MA. They are a licensee in Massachusetts under State License Number 44-0362. "A Cobalt-57 flood source used for nuclear medicine camera imaging calibration was discovered to be missing. The source is 10 mCi (05/01/2015) in strength and is 8 inch x 8 inch in area. The source is typically stored in a leaded sleeve 12 inch x 12 inch in area. The date of discovery appears to be May 8, 2015, but the details are still uncertain at this point. "Digirad Imaging Solutions is providing a 30 day report of the incident shortly. The incident was reported to us [Massachutetts Radiation Control Program] on the day of this report to the NRC (6/2/2015)." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-06-10
51112 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-06-01 21:11 | 2015-06-02 02:00 | 2015-06-02 | REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "At 2111 [CDT] River Bend Nuclear Station sustained an Automatic Reactor Scram due to low Reactor Water Level (Level 3). The plant is currently stable, with level being maintained in a normal band of 10 - 51 inches with Condensate and Feedwater. Reactor Pressure is in the prescribed band of 500-1090 psig. The plant is in Mode 3, Hot Shutdown, and will remain in Mode 3 until investigation of the scram is complete. The transient began with a trip of Reactor Feed Pump 'A', followed by a Reactor Scram and a trip of Reactor Feed Pump 'C'. Reactor water level was recovered with Reactor Feed Pump 'B' to a normal post scram level band. There was a problem noted with the Reactor Feedwater Master Level Controller; this was mitigated by the Operator placing the controller to manual. There was no subsequent Level transient. Reactor Pressure was stabilized in normal pressure band with Turbine bypass valves. During the transient, a Reactor Recirculating Flow Control Valve Runback was not received as expected. Reactor Recirculating Pump 'A' responded as expected to transient [switching to low pump speed], Reactor Recirculating Pump 'B' tripped during transient. A Level 3 isolation signal was received, all expected isolations occurred. "The cause of the transient is currently under investigation." The reactor is stable in Mode 3 with decay heat being removed via turbine bypass valves, and a normal electrical line up. The NRC Resident Inspector has been notified. * * * UPDATE FROM JACK MCCOY TO HOWIE CROUCH AT 0712 EDT ON 6/2/15 * * * "At 2231 on 6/1/15, Reactor Water Cleanup System isolated on High Reactor Water Cleanup System Heat Exchanger room temperature due to loss of Turbine Building chill water during the initial transient. All Reactor Water Cleanup System Valves isolated as expected. Reactor Water Cleanup was the only system affected by this isolation signal." The licensee has notified the NRC Resident Inspector. Notified R4DO (Whitten). | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-06-02
51111 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-05-29 18:00 | 2015-06-01 18:49 | 2015-06-01 | AGREEMENT STATE REPORT - POLONIUM 210 SOURCE MISSING "Loss of control of source: Data Control Device (DCD) containing a 500 microCurie Po-210 source was transferred from the Utah State University campus by an unnamed researcher. The source was removed and was transported to a city in India. The RSO [Radiation Safety Officer] is currently making efforts to locate the researcher in India and verify the source is under his control." This event occurred on 5/29/2015 and was reported to the state at 1300 MDT on 6/1/2015. Utah Report: UT150002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-06-09
51110 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-05-29 | 2015-06-01 14:10 | 2015-06-01 | AGREEMENT STATE REPORT - TRANSPORTED PACKAGE EXCEEDS EXTERNAL RADIATION LIMITS The following report was received from the Commonwealth of Pennsylvania via email: "The Department [Pennsylvania Department of Environmental Protection] was notified on May 29, 2015, after the close of business, of a package received by the licensee that exceeded the external radiation limits. This event is reportable immediately per 20.1906(d)(2). "On Friday May 29, 2015, a package was received at the Madison location of Westinghouse. Receipt surveys determined that the package containing 'tri-nuc filters' exceeded the contact dose rate of 200 mR/hr as noted in 10 CFR 71.47. Confirmatory instruments used indicated a dose rate of around 300 mR/hr on contact (75 mR/hr at one foot, and 16 mR/hr at three feet). No removable contamination is present. The package was shipped from Westinghouse's European service center in Belgium. They maintain that the package met all transportation requirements prior to departure. It is believed that either the package shielding or material may have shifted during transport. No exposures in excess of regulatory limits are expected. "The Department [Pennsylvania Department of Environmental Protection] plans a reactive inspection and the facility is preparing a full report. More information will be provided upon receipt." Pennsylvania Event Report ID No: PA150016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-06-09
51109 | 0 | ABB MEDIUM VOLTAGE SERVICE |  |  |  |  | 2015-06-01 | 2015-06-01 10:30 | 2015-06-01 | PART 21 - DEFECTIVE CIRCUIT BREAKER SECONDARY CLOSE LATCH The following is an excerpt of communication received via email: "This letter provides notification of a failure to comply with specifications associated with a secondary close latch, part number 716610K01, used in K-Line 225/800 and 1600/2000 amp electrically operated Model 7 circuit breakers. "Nature of the deviation: During installation of a primary close latch and subsequent bench testing at a nuclear utility, mechanical binding was observed between the primary and secondary close latches. This binding prevented the breaker from operating. Inspection of both latches by ABB showed that the issue lies with the secondary close latch. It was determined that the secondary close latch dimension from the centerline of the hub that the latch rotates about, to the edge of the secondary latch surface with the half pin on the primary latch, was oversized. The failure to comply was identified when replacing latches and verified with a calculated dimension. "The additional length from the center of the hub in the secondary close latch to the corner of the latch surface caused an interference between the pin cam interface and the half pin on the primary close latch, where it rolls off of the latch surface on the secondary close latch. "It is recommended that affected licensees with this latch in inventory, ensure that bench testing is performed prior to installation to verify that the primary and secondary close latches work together without any evidence of binding. "ABB currently cycles K-Line breakers that are refurbished approximately 55 close/open operations before they ship from the Florence facility. New breakers get at least the same number of close/open operations before shipment. This level of operational testing validates that there is no binding between the primary and secondary close latches. "Questions concerning this notification should be directed to the Quality Manager at the Medium Voltage Service Center in Florence, SC at (843) 413-4727 or Fax (843) 413-4853." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-06-01
51108 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2015-06-01 07:00 | 2015-06-01 06:57 | 2015-06-01 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "A planned maintenance evolution at the Oyster Creek Generating Station has removed the Technical Support Center (TSC) ventilation system from service. The TSC ventilation system will be rendered non-functional during the course of the work activities. The TSC ventilation is expected to be out of service for approximately sixteen hours and will return to service at approximately 2200 [EDT] June 1, 2015. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to potential loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation." The NRC Resident Inspector has been notified. * * * UPDATE FROM JOSHUA MCGUIRE TO JOHN SHOEMAKER AT 2324 EDT ON 6/1/15 * * * At 2240 EDT on 6/1/15, the TSC ventilation system was restored. The licensee will notify the NRC Resident Inspector. Notified the R1DO (Powell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-06-01
51107 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2015-05-31 22:20 | 2015-06-01 02:25 | 2015-06-01 | MANUAL REACTOR TRIP DUE TO TRIP OF CONDENSATE AND MAIN FEEDWATER PUMP "On May 31, 2015 at 2220 CDT, the Unit 1 reactor was manually tripped while operating at 100 percent power due to a lockout trip of 11 Condensate Pump followed by a lockout trip of 11 Main Feedwater Pump. Manual Reactor Trip is directed by the annunciator response procedure for the lockout alarm, C47010-0101, 11 Feedwater Pump Locked Out. This also resulted in a turbine trip. The crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. The manual trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels have been returned to normal. Following the reactor trip, 15A Feedwater Heater relief lifted and failed to reseat. 12 Main Feedwater Pump was subsequently secured resulting in 15A Feedwater Heater relief valve reseating successfully. Steam generators are being supplied by 12 Motor Drive Auxiliary Feedwater Pump and decay heat is being removed by the condenser steam dump system. The cause of 11 Condensate Pump trip remains under investigation. There was no effect on Unit 2 as a result of this trip. The health and safety of the public and site personnel were not at risk at any time during this event. The NRC Senior Resident Inspector has been notified." Unit 2 is unaffected and remains at 100 percent power. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-06-01
51106 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-05-31 16:00 | 2015-05-31 16:32 | 2015-06-02 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO FAILURE OF AN EMERGENCY DIESEL GENERATOR "At 1600 [EDT] on May 31, 2015, [DC Cook] operations commenced a shutdown of DC Cook Unit 1 to comply with LCO 3.8.1 Condition G, when the 14 day limit to complete Condition B Required Action could not be met. "At 0010 [EDT] on May 18, 2015, Unit 1 AB Emergency Diesel Generator was removed from service for planned maintenance. LCO 3.8.1 Condition B was entered which allows 14 days to restore diesel to operable. "At 1049 [EDT] on May 21, 2015, Unit 1 AB Emergency Diesel Generator tripped during post maintenance testing due to high bearing temperatures. Subsequent actions to repair and restore the diesel to operable status have been unsuccessful. "This event is reportable under 10 CFR 50.72(b)(2)(i), the initiation of any nuclear plant shutdown required by the plant's Technical Specifications, as a four (4) hour report. The DC Cook Sr. Resident NRC Inspector has been notified." Unit 1 is expected to be in Mode 5 by 2030 EDT on June 1, 2015. There is no impact on Unit 2. * * * UPDATE FROM CHRIS PEAK TO JOHN SHOEMAKER ON 6/1/15 AT 1704 EDT * * * "This update is to correct the information contained in the block titled 'Power/Mode After'. The power and mode after the event requiring notification (TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INABILITY TO RESTORE UNIT 1 AB EDG WITHIN THE COMPLETION TIME PRESCRIBED IN LCO 3.8.1 CONDITION B) was 99% power and mode 1. "The licensee has notified the NRC Resident Inspector." D.C. Cook Unit 1 is currently in Mode 3 and conducting a normal cooldown to Mode 4. Notified R3DO (Passehl). * * * UPDATE FROM CHRIS PEAK TO HOWIE CROUCH AT 0734 EDT ON 6/2/15 * * * "DC Cook Unit 1 reactor was shut down (Mode 3) at 0231 hours [EDT] June 01, 2015 and achieved Mode 5 at 0410 hours [EDT] June 02, 2015 to comply with LCO 3.8.1 Condition G with all systems operating normally. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Passehl). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2015-05-31
51105 | 0 | MISTRAS GROUP |  |  |  |  | 2015-05-29 22:10 | 2015-05-30 15:39 | 2015-05-30 | RADIOGRAPHY SOURCE STUCK IN GUIDE TUBE "The equipment supporting the collimator, guide tube, and extension tube fell from a height of 9 feet causing the guide tube to become entangled in the piping below. [The guide tubes fell on equipment below and the short radius bends prevented source retrieval.] "Equipment Involved: 7 foot flexible guide tube Serial Number GT060 7 foot flexible extension tube serial number EXT-15 Exposure device model: Sentinel Delta 880D, serial # D11876 Isotope: Ir-192, source Serial Number 17211G Source Activity: 102.3 Ci 35 foot Control Assembly S/N 16681 "Place: Salt Water Treatment Plant, Central Operating Area, Prudhoe Bay, Alaska "Actions taken to establish normal operations: The radiographer extended his restricted area and contacted the plant operator to inform him of the situation. He and the assistant radiographer then maintained security of the restricted area throughout the duration of the event. At no time did any member of the public enter the restricted area. The Radiation Safety Officer was contacted by the radiographer and arrived on the scene at 2320 hours [AKDT]. Remote handling tools were used to untangle the guide tube and extension tube. Once the equipment was properly laid out the source was retracted to the shielded position using the control assembly. "Corrective actions taken and planned to prevent reoccurrence: Retrain personnel on setup techniques with an increased focus on the stabilization of equipment. "Qualifications [and dose] of personnel involved in incident: (1) IRRSP card holder, dose received, 7mR (2) Assistant Radiographer, dose received, 17mR (3) IRRSP card holder, dose received, 2mR (4) Jeremey A. Dunning, Site Radiation Safety Officer, IRRSP card holder, Source Retrieval trained by LAMCO & Associate February 25, 2011, dose received, 23mR (Dosimeter)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-06-08
51104 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2015-05-30 04:58 | 2015-05-30 11:58 | 2015-06-03 | RHR PUMP TRIP IN COLD SHUTDOWN MODE "At 0458 CDT on 05/30/2015, with Cooper Nuclear Station Unit 1 in Mode 4 [cold shutdown], an inadvertent trip of Residual Heat Removal (RHR) Pump B was experienced which resulted in a loss of shutdown cooling. The cause of the trip is currently not known and is under investigation. Shutdown cooling was restored with B RHR Pump at 0520 on 05/30/2015, and there have been no other issues with the system. During the loss of shutdown cooling, forced circulation of the core was not lost due to the Reactor Recirculation System remaining in service. Based on indication from the in-service Reactor Recirculation System A loop, reactor coolant temperature experienced a 7 (seven) degree Fahrenheit increase during the event. Reactor coolant temperature did not exceed 212 degrees Fahrenheit during the event. "This condition is reportable under 10CFR50.72(b)(3)(v) - any event or condition that, at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to: B) remove residual heat. "The NRC Senior Resident inspector has been notified of this event." * * * UPDATE PROVIDED BY DAVID VANDERKAMP TO JEFF ROTTON AT 1646 EDT ON 06/03/2015 * * * "After further evaluation of the reported transient, it was determined that the Reactor Recirculation System A Loop increased from 186 degrees F to 204 degrees F for a heatup of 18 degrees during the loss of Shutdown Cooling. The Vessel Drain temperature increased from 190 degrees F to 210 degrees F for a heatup of 20 degrees during the same time frame." The licensee will notify the NRC Resident Inspector. Notified R4DO (Whitten) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2015-05-30
51103 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-05-29 12:30 | 2015-05-29 20:17 | 2015-06-12 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO DISCOVERED CONDITION "This is non-emergency eight hour notification for a loss of Emergency Assessment Capability. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affects the functionality of an emergency response facility. "A condition impacting functionality of the TSC [Technical Support Center] Ventilation system was discovered on 05/29/2015 at 1230 [EDT]. The issue involves a loss of cooling capability of the TSC ventilation system due to a failed relay. Maintenance will begin repairs at 0700 [EDT] on 05/30/2015. Estimated time to repair is unknown at this time. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Coordinator will relocate the TSC staff to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team will be notified of the condition and the possible need to relocate during an emergency. This condition does not affect the health and safety of the public or station employees. An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector will be notified." * * * UPDATE FROM AARON MICHALSKI TO DANIEL MILLS AT 1557 EDT ON 6/12/15 * * * The TSC ventilation system has been returned to service. The licensee will notify the NRC Resident Inspector. Notified R2DO (Guthrie). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-29
51102 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-05-27 | 2015-05-29 18:47 | 2015-05-29 | AGREEMENT STATE REPORT - LEAKING CS-137 SOURCE The following was received from the State of Texas via email: "On May 27, 2015, the licensee reported to the Agency [Texas Department of State Health] that while performing a routine survey of its source storage area, it discovered that a Barium-137 generator, originally containing 50 millicuries of Cesium-137, had leaked. The licensee investigated and found small amounts of the Cesium had been tracked into its office area (floor only and it has been remediated) and some of the licensee's work vehicles. Employees' vehicles were surveyed and no contamination was detected. The licensee continues its surveys of tools, tool boxes, and other items in the trucks. The area where the generator was stored is a restricted area (security). Access has been further restricted for greater than 24 hours due to the contamination. The licensee is working to identify and remediate all contamination outside the storage room before beginning to remediate there. The licensee has placed the generator into a type A drum to contain the material. The licensee was unable to determine the source or cause of the leak prior to placing it in the drum. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident: I-9316 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-06-08
51101 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-14 | 2015-05-29 17:11 | 2015-10-23 | AGREEMENT STATE REPORT - CS-137 FOUND IN WASTE ENTERING A LANDFILL The following report was received via e-mail: "On April 13, 2015, the Agency [Texas Department of State Health Services] was notified by a landfill operator that material in a waste container set off their radiation alarms. The landfill provided a spectrum which showed the isotope as Cesium-137. An on-site investigation by this Agency confirmed the material to be dirt/mud contaminated with Cesium-137. The waste material at the landfill was isolated. The waste collection route sheet used to collect the waste was requested by the Agency. The Agency drove the route traveled by the collection vehicle using an RSI identifier in an attempt to locate the source of the contamination. The detector indicated the presence of radiation in a bar ditch along the intersection of two streets northeast of the City of Houston. Surveys conducted by the Agency identified a reading of 16 millirem on contact with the ground in one spot. Additional surveys indicated additional activity as far as 70 feet from the spot previously mentioned. The Agency received cost estimates from contractors to collect the material from both areas for proper disposal. The city of Houston had been contacted about the contamination and the steps that had been taken by the Agency. The City of Houston decided since the area of contamination was in their jurisdiction, they would be responsible for the remediation of the area. The Agency returned to the area on the evening of May 26, 2015, to inspect the area. The Agency discovered the road the bar ditch was running along had been closed by the city at both ends. There are no homes or businesses that require access to this section of road. The contractor was contacted on May 29, 2015. He stated they had begun work on remediating the area on May 21, 2015. He stated the road was blocked by the Houston City Works Department on that day. He stated they had dug down about 3 feet from the original surface of the ditch. He stated readings on contact at that location are 1 rem/hr. He stated they had come across a water line while they were digging and that it has restricted their use of tools. He stated that due to the dose rates they are seeing now (1 rem/hr) they are now using a low pressure water blaster to excavate the area. He stated they are sucking the water into barrels and monitoring the suction line for dose rates. He stated they would contact the state once the source has been located. "On May 29, 2015, the Agency decided that due to the city closing the road to any access, the event should be reported to the Nuclear Regulatory Commission Headquarters Operations Officer (HOO.)" Event location: Near the intersection of Sunbury and Bacher Streets. Texas Event: I-9303 * * * UPDATE ON 10/23/2015 AT 1153 EDT FROM ARTHUR TUCKER TO DONG PARK * * * The following report was received via e-mail: "On April 13, 2015, the Agency was notified by a landfill operator that a load of waste had caused its radiation monitor to alarm. The operator provided a spectrum and the radioisotope was identified as cesium-137. An on-site investigation confirmed the material to be dirt/mud contaminated with cesium. Further investigation was initiated to find the source of the material. Using the waste collection vehicle's route sheets and the Agency's radiation detection equipment, the Agency identified the area where the mud had originated in a drainage ditch along the side of a street, which was within the city's easement. The waste material was isolated and a cost estimate was obtained for a contractor to remediate the area. The initial surface readings obtained in the ditch ranged from 430 microR/hr to 16 mR/hr. During remediation, the readings ranged up to 1Rem/hr and the depth of the material to be removed was within a few inches beneath the soil to a max depth of 14 feet in the most concentrated area. Site remediation was completed by the end of July 2015. The property was released for unrestricted use on September 1, 2015 after final soil samples were analyzed. The highest concentration of contamination, point of origin, was identified at a depth of approximately 14 feet below the ground surface. Ownership of the source of the radioactive material could not be determined. No violations were cited. File closed." Notified R4DO (Werner) and NMSS EVENTS NOTIFICATION via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-06-08
51100 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2015-05-29 10:30 | 2015-05-29 16:26 | 2015-05-29 | AGREEMENT STATE REPORT - MEDICAL TREATMENT TO INCORRECT LOBE OF THE LIVER "The Minnesota Department of Health was notified on May 29, 2015, by a representative from Abbott Northwestern Hospital of a Medical Event. A patient was given 23.62 mCi of Y-90 TheraSpheres with an intended dose of 125.3 Gy to segment 4 of the liver. The 125.3 Gy dose was unintentionally given to the right lobe of the liver (segments 1, 5, 6, 7, and 8). The licensee was planning on treating the right lobe in the future. The patient and referring physician will be notified on May 29, 2015. The Minnesota Department of Health will follow-up with the licensee early next week." Minnesota Event: MN150003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2015-06-08
51099 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-05-27 | 2015-05-29 13:41 | 2015-05-29 | AGREEMENT STATE REPORT - LOST IODINE-125 MEDICAL SEEDS The following report was received from the State of Texas via email: "On May 29, 2015, a licensee notified the Agency [Texas Department of State Health Services] that it was unable to locate a package containing approximately 41.2 millicuries of Iodine-125 seeds. The package had been received at the licensee's facility on May 26, 2015, and per the licensee's procedures, it was delivered to the nuclear medicine department and left in the designated area. However, the staff in the nuclear medicine department had been allowed to leave due to a slow schedule. On May 27, 2015, when staff returned, they were unable to locate the package. The licensee conducted a facility wide search. The [licensee's] materials management employee that placed the package in the nuclear medicine department and the housekeeping employee that cleaned the department the previous night were interviewed. The housekeeper reported, [to have] not removed any boxes from the department. The licensee was unable to identify anyone else had entered the department. The facility's waste container had been picked up and taken to the landfill earlier that morning. The licensee checked with the landfill and learned it does have a radiation monitor but the container from the hospital had not set it off. The contents of the container had already been covered over in the landfill. The patient's procedure was canceled and re-scheduled. The licensee has changed its procedures for radioactive material package delivery by the facility's materials management to the nuclear medicine department to prevent reoccurrence. The licensee is continuing its search for the package. An investigation into this event is ongoing. The Agency [Texas Department of State Health Services] has withheld the name of the licensee [and license number and location] in accordance with Texas state law. Further information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9317 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-06-08
51098 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2015-03-10 | 2015-05-29 13:32 | 2015-05-29 | AGREEMENT STATE REPORT - TWO LOST NUCLEAR THICKNESS GAUGES The following information was received via fax: "Genpac, LLC reported that two NCR Systems thickness gauges, SS&D No. CA0471D102B, device model No. 103, each containing 150 millicuries of Americium-241 were unaccounted for. The loss was discovered after Genpac was contacted by the [New York State] Department in February 2015, in order to initiate their periodic License Renewal process. At that time the company requested a license termination. A phone interview revealed that the company no longer had any gauges with radioactive materials (RAM) in use and that the Radiation Safety Officer had left the company. However, they could not provide documentation showing that the RAM had been transferred to an authorized recipient. The company has no knowledge of its disposition. The sources were last identified as being on site during a Department inspection conducted on February 10, 2010. The facility failed to maintain inventories and leak testing after the Radiation Safety Officer (RSO) left the company in 2010. The Department was not notified of the departure of the RSO. "A Reactive Inspection was conducted by [New York State] Department staff on March 10, 2015. During the inspection, a thorough search of the authorized storage locations and potential storage locations for surplus equipment was completed and the devices were not located. The consequences for the potential loss of Licensed RAM was discussed with Genpac management during the exit interview. At that time, an acceptable action plan was developed in order to locate the potentially missing RAM. "On May 15, 2015, the company management notified the [New York State] Department that they had determined that they are unable to locate these sealed sources. This comes after interviewing staff with potential knowledge of the location of the devices and an extensive in-house search of their premises, the storage out-buildings and other locations within the Genpac organization that make use of Radioactive Materials (RAM) in the United States." New York State ID: NYDOH-15-04 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-06-08
51097 | -1 | C&D TECHNOLOGIES, INC. |  |  |  |  | 2015-03-04 | 2015-05-29 10:21 | 2017-10-30 | INTERIM PART 21 REPORT - INABILITY TO COMPLETE EVALUATION REGARDING CRACKING IN KCR-13 STANDBY BATTERY JARS The following was received via email: "The purpose of this letter is to provide the NRC a report in general conformity to the requirements of 10 CFR Part 21.21(a)(2). On March 4, 2015, C&D Technologies, Inc. (C&D) was informed by Entergy Nuclear Northeast that a KCR-13 battery installed at the Indian Point Nuclear Energy Center had developed a crack in the polycarbonate jar material. This is the second KCR-13 at this site that has experienced a crack in the jar material [see EN 49667]. The jar is a safety related component with the primary function of containing electrolyte. The battery has not been returned to C&D for analysis, and analysis of the previous issue was inconclusive. "C&D is submitting this interim report to the NRC and notifying C&D's customers that use C&D KCR-13 batteries, of this Interim report, and is initiating an action plan to evaluate the reported potential defect and determine whether it could pose a substantial safety hazard for any US licensee using such batteries. "KCR-13 Batteries manufactured in 2005, battery manufacturing date is on the label. Note: C&D has not completed its evaluation of the reported potential defect and whether it could pose a substantial safety hazard at any US licensee using such batteries. "The cracked jar has not been fully evaluated and may or may not indicate a potential defect which could create a substantial safety hazard. "KCR -13 batteries used at Nuclear Plants in 1E applications made in 2005: "Utility/Plant Name/Battery Model/Quantity of Batteries "Entergy/Indian Point /KCR-13 NUC/72 "Xcel Energy/Monticello/KCR-13 NUC/62 "Concurrent Actions underway to complete the evaluation: "a) On receipt of the battery from Indian Point, C&D will perform a failure analysis with the intent of determining the root cause of the cracking issue. Maximum time 30 days from receipt of the battery. "b) In conjunction with the licensees identified in Section VI, C&D will recommend maintenance assessment of all KCR-13 batteries at these locations to determine their status and specifically, the presence of any evidence of potential defects via visual examination. For any cells exhibiting the presence of potential defect, C&D shall further recommend that they be returned for analysis. Estimated completion date of analysis is thirty (30) days from the receipt of the returned batteries. "U.S. Licensees using batteries possibility containing the alleged defect have been notified of the filing of this interim report with recommendations that they examine their batteries for any signs of problems. NOTE: A similar notification and advice was provided in December 2013 with the previous battery. C&D did not receive any reports of similar problems from other product users. "If you have any questions or wish to discuss this matter or this report, please contact:" Robert Malley VP Operational Excellence bmalley@cdtechno.com (215) 619-7830 The similar notification and advice provided in December 2013 is EN 49667. * * * RETRACTION AT 1409 EDT ON 10/30/17 FROM ROBERT MALLEY TO S. SANDIN VIA EMAIL * * * The following information was received from C&D Technologies via email: "Subject: Retraction of Interim Report - Inability to Complete 10CFR Part 21 Evaluation Regarding Cracking in KCR-13 Standby Battery Jars "On May 29, 2015 C&D Technologies submitted an interim Part 21 report (ML15155A575, Part 21 log 2015-34-00) regarding jar cracks discovered in a KCR-13 battery at Indian Point Nuclear Energy Center. This report was issued as the analysis of this battery jar had not yet been completed. The analysis was subsequently completed, and it was determined that the jar cracking was not related to the design or production of this battery, and thus is not a defect reportable under Part 21. Indian Point Nuclear Energy Center was notified of the findings of the report; however, no final Part 21 report was issued by C&D to the NRC, leaving the interim Part 21 report open. "Based on the results of the analysis the Interim Report (NRC Log No. 2015-34-06) dated May 29, 2015 is retracted." Notified R1DO (McKinley), R3DO (Stone) and Part 21/50.55 Reactors via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-05-29
51096 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-05-27 | 2015-05-28 15:37 | 2015-05-28 | AGREEMENT STATE REPORT - LICENSEE DID NOT PROVIDE REQUIRED SECURITY FOR A CATEGORY 2 SOURCE Inadequate security provided for a category 2 source. The Commonwealth of Pennsylvania performed an emergency inspection to ensure that the source has been secured. Pennsylvania Report: PA150015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 1 | 2015-06-05
51095 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-05-26 15:36 | 2015-05-28 13:18 | 2015-05-28 | PART 21 NOTIFICATION - ALLEN BRADLEY 700RTC RELAY CONFIGURATION "This is a non-emergency notification, required by 10 CFR 21.21(d)(3)(i). "Brunswick has determined that Allen Bradley relays, base model 700RTC, contain an unevaluated Complex Programmable Logic Device (CPLD). This was an unpublished design change that was implemented to replace an obsolete integrated circuit chip. The undocumented design change did not result in a part number change from Allen Bradley. There was no change to the external appearance of the relay that would indicate that a design change had been made to the relay configuration. Therefore, qualification/dedication of the modified relays have not included additional testing for the new CPLD component. Testing, performed by Duke Energy, has demonstrated that this CPLD can be affected by electrical noise from operation of nearby relays which can reset the timing of the relay. This condition was discovered as a result of a post-maintenance test of an emergency diesel generator. Additional details associated with the discovery of this condition are contained in Brunswick Licensee Event Report 1-2015-002, dated May 20, 2015. "Brunswick purchased, as commercial grade, 25 of the modified Allen Bradley 700RTC relays beginning in October, 2008. Duke Energy dedicated these relays for use in safety related applications at Brunswick. The dedicated relays were not provided to any third party customers. "The NRC Senior Resident Inspector has been notified." Brunswick has taken applicable compensatory measures to insure no equipment is inoperable because of these relays. This problem was previously reported by AZZ/NLI Nuclear Logistics, Inc. in EN #51030. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2015-05-28
51094 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-05-27 22:17 | 2015-05-28 03:35 | 2015-05-28 | AREA RADIATION MONITORS NON-FUNCTIONAL DURING PLANNED BUS OUTAGE "A planned outage of the Division 2 medium voltage switchgear (SM-8) was initiated at 22:17 PDT on 5/27/15. The bus outage results in all area radiation monitors required for emergency classification being non-functional. Compensatory measure monitoring equipment has been established prior to the loss to provide alternate means of monitoring area radiation levels. The SM-8 outage window is scheduled to last 124 hours. Although the monitoring function is maintained by the compensatory monitoring equipment, the planned loss of area radiation monitors for greater than 72 hours is being reported as a major loss of emergency assessment capability in accordance with 10 CFR 50. 72(b )(3)(xiii). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-28
51093 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-05-27 09:52 | 2015-05-27 18:37 | 2015-05-27 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "On May 27, 2015, at 0952 CDT, the Control Room Emergency Ventilation (CREV) system was declared inoperable due to opening a ventilation duct hatch to facilitate fire damper inspection without administrative controls. The hatch was opened and upon discovery was immediately shut, re-establishing the boundary of the Control Room Envelope. As a result, Technical Specification 3.7.4, Condition C, was entered and subsequently exited. "The CREV system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions as well as protection of the operators from a high dose environment assumed during a design basis accident. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV system could impact the plant's ability to mitigate the consequences of an accident as stated in Chapter 6 of the UFSAR. This event is also reportable under 10 CFR 50.72(b)(3)(xiii) since this condition also impacts the control room as an Emergency Response Facility. "At 0955, Technical Specification 3.7.4, Condition C, for CREV System Inoperable due to inoperable Control Room Envelope was exited. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(xiii) |  |  | 0 | 2015-05-27
51092 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-05-27 09:45 | 2015-05-27 10:45 | 2015-05-27 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "On 5/27/15, planned preventive maintenance activities are being performed on the Braidwood Generating Station Technical Support Center (TSC), Ventilation System. The work will be completed within approximately 10 hours. This activity includes preventative maintenance that requires the TSC ventilation system to be out of service which will render the TSC ventilation system non-functional. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff as necessary. "This event is reportable per 10CFR50.72(b)(3)(xiii) for 'any event that results in a major loss of emergency assessment capability.' The planned maintenance will not be able to restore the TSC condensing unit or ventilation system to service within the facility activation time specified in the emergency plan (1 hour) in the event of an accident. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency." The licensee informed the NRC Resident Inspector. * * * UPDATE FROM PETER MOODIE TO VINCE KLCO ON 5/27/2015 AT 2153 EDT * * * Planned work is complete and the Technical Support Center was restored to service on May 27, 2015 at 1808 CDT. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Lipa). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-27
51091 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-08-07 17:07 | 2015-05-26 17:45 | 2015-06-03 | THIS IS A CONTINUATION OF EN #50351 AND EN #50998 * * * UPDATE ON 05/26/15 AT 1745 EDT FROM SCOTT BRITT TO JEFF HERRERA * * * "During an expanded scope inspection, deficiencies in the Control Building 147[foot] elevation were observed that caused the affected barrier to be considered nonfunctional: - Gaps were identified around cables in the foam cable tray penetration seal for penetration 1Z43H006F in the floor of the Cable Spreading Room (separating Fire Areas 0024A and 1104). "The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Units 1 and 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10074859" The licensee will be notifying the NRC Resident Inspector. * * * UPDATE FROM STANLEY STONE TO JOHN SHOEMAKER AT 2017 EDT ON 6/1/15 * * * "During an expanded scope inspection for penetration seals, using more intrusive tools and methods, fire barriers in the Control Building El. 112 [foot] were found not to meet acceptance criteria. The fire protection engineering staff has examined the situations and recommends that these conditions be considered NON-FUNCTIONAL. - An issue was identified with the wall separating the el. 112 [foot] Control Building Working Floor, Fire Area (FA) 0001 from the Station Battery Room 1B, FA 1005. - An issue was identified with the wall separating the Station Battery Room 2A, Fire Area (FA) 2004 from the Station Battery Room 2B, FA 2005, on el. 112 [foot]. "The nonconforming conditions observed for the affected fire barriers were identified as affecting both safe shutdown paths for Units 1 and 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. CR 10077573 & 10077574." The licensee has notified the NRC Resident Inspector. Notified the R2DO(O'Donohue). * * * UPDATE FROM PAUL UNDERWOOD TO DONG PARK AT 1704 EDT ON 6/2/15 * * * "During an expanded scope inspection for penetration seals, using more intrusive tools and methods, fire barriers in the Control Building El. 112 [foot] were found not to meet acceptance criteria. The fire protection engineering staff has examined the situations and recommends that these conditions be considered NON-FUNCTIONAL: - Issues were identified with the wall separating the el. 112 [foot] Control Building Working Floor, Fire Area (FA) 0001 from the Unit 1 AC Inverter Room, FA 1008. "The nonconforming conditions observed for the affected fire barriers were identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. CR 10078011." The licensee has notified the NRC Resident Inspector. Notified the R2DO (Rose). * * * UPDATE FROM PAUL UNDERWOOD TO DONG PARK AT 1501 EDT ON 6/3/15 * * * "During an expanded scope inspection for penetration seals, using more intrusive tools and methods, fire barriers in the Control Building El. 112 [foot] were found not to meet acceptance criteria. The fire protection engineering staff has examined the situations and recommends that these conditions be considered NON-FUNCTIONAL: - Issues were identified with the wall separating the el. 112 [foot] Control Building U2 Water Analysis Room, Fire Area (FA) 2006 from the Control Building East Corridor, FA 0007 "The nonconforming conditions observed for the affected fire barriers were identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. CR 10078561." The licensee has notified the NRC Resident Inspector. Notified the R2DO (Rose). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-05-26
51090 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2015-05-21 16:00 | 2015-05-26 16:04 | 2015-05-26 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE DAMAGED AT CONSTRUCTION SITE The following report was received from the Illinois Emergency Management Agency via email: "On the afternoon of May 21, the Agency [Illinois Emergency Management Agency] received a call from the licensee's radiation safety officer (RSO) who explained that their portable moisture density gauge had been involved in an accident at a construction site in Barrington, IL. The gauge operator had been briefly called away from the device and during his absence, the device was struck by a piece of heavy machinery. The RSO indicated that the operator had gathered up the pieces and put them into the transportation case and was in the process of returning the broken device to the company's Chicago storage facility at the time of the RSO's notification. Pictures provided by the RSO showed that the rod which contained the Cs-137 was significantly bent some 4 inches from its end and was no longer in its shielded position. The operator secured the device in a remote location upon his return to the storage facility that night until Agency inspectors could be dispatched to the location. "The next morning, inspectors arrived at the storage location and conducted surveys including field leak tests of the sources. Those tests showed no leakage of radioactive material but determined that elevated radiation levels of up to 60 [millirem/h] were present at the surface of the transportation case. After providing additional storage suggestions, the pieces of the gauge were reconfigured and secured at the site. Dose rates were lowered to 16 [millirem/h] near the surface of the case and less than 1 [millirem/h] at 1 foot by those efforts. "The gauge manufacturer was contacted and asked to provide a shipping container and additional shielding for return of the damaged device. When those materials are received, Agency inspectors will return to the site and verify the gauge is properly packaged and documented for return. This item remains open at this time pending this additional action and receipt of the licensee's written report which is due in 30 days. "Device manufacturer: Troxler Model Number: 3430 Serial Number: 68332 Device activity content: 0.008 Ci - Cs-137, 0.040 Ci - Am/Be "Illinois Event Number: IL15011" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2015-06-03
51089 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-05-26 11:25 | 2015-05-26 15:20 | 2015-05-26 | FITNESS FOR DUTY - ALCOHOL CONTAINER FOUND IN PROTECTED AREA On May 26, 2015, at approximately 1125 CDT, an empty beer can was found by a mechanical maintenance worker performing scaffolding work. Site Security took possession of the can and it was removed from the protected area. The can appears to be extremely old (20 plus years) with dust and debris on it. This report is submitted pursuant to 10 CFR 26.719(b)(1) based on the presence of an alcohol container within the protected area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2015-05-26
51088 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2015-05-04 | 2015-05-22 17:08 | 2015-05-22 | AGREEMENT STATE REPORT - TRANSPORTABLE HIGH DOSE RATE UNIT DAMAGED WHILE BEING UNLOADED The following report was provided by the Virginia Department of Health via facsimile: "On May 4, 2015, a transportable HDR [high dose rate] unit (Elekta microSelectron Model 106.900, serial number 14514) licensed for use by a Virginia licensee was damaged while being unloaded from its transport trailer. The source activity at the time was approximately 8 curies of IR-192. The damage appeared to be limited to the unit's covers. The licensee contacted Elekta, Inc., (which performs work in Virginia under reciprocal recognition of its Georgia license) and a field service engineer was sent to investigate. The service engineer found the head covers and collar cover were broken and other damages, but tests indicated the unit functioned properly. New covers were ordered. During the following week the source was uploaded into an emergency container while the covers were replaced. After the source was returned to the HDR it was found to be stuck in the safe. A kink was found in the cable and a new source was ordered. A source exchange was scheduled on May 19th, but the source could not be manually unloaded as before. Instead, it had to be removed from the back of the HDR. The frayed cable was cut and the source was placed in the emergency container by the service engineer. The source fell to the bottom of the emergency container and the service engineer could not retrieve it. The container was placed in storage at the Virginia licensee's facility after additional shielding was placed around it to reduce the exposure rate to 200 microR/hour. The dose received by the service engineer as a result of the event was estimated by Elekta, using a worst case scenario, as 327 mrem whole body. The service engineer's dosimeter was sent to the dosimetry supplier for an emergency evaluation. Elekta has contacted the source manufacturer (Alpha-Omega Services) [AOS] to assist in the retrieval of the source from the emergency container and to send it to AOS for further investigation. Elekta will provide additional information as it investigates the event. "Virginia Event Report ID No.: VA-15-06" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2015-06-01
51087 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-05-22 10:02 | 2015-05-22 13:36 | 2015-05-24 | MANUAL REACTOR SCRAM DUE TO LOSS OF CONDENSER VACUUM "On Friday, May 22, 2015 at 1002 EDT, with the Reactor Mode Select Switch in the Start-Up position and the reactor at approximately 3 percent core thermal power, while returning to power from Refueling Outage Number 20, a manual reactor scram was inserted due to degrading main condenser vacuum. The cause of the degraded vacuum is currently under investigation. "Following the reactor scram, all rods were verified to be fully inserted and no Emergency Operating Procedure entry conditions existed. "All plant systems responded as designed. "Currently reactor pressure is being maintained at 400 psig with the Mechanical Hydraulic Control System (turbine by-pass valves). Reactor water level is being maintained in normal bands with the Condensate and Feedwater System. Off-site power is being supplied to the station by the Startup Transformer (normal power supply for shutdown operations). "This event had no impact on the health and/or safety of the public. The NRC Resident Inspector is on-site and has been notified. "The licensee has notified the Massachusetts Emergency Management Agency." The licensee will be issuing a press release. * * * UPDATE FROM EVERETT PERKINS TO DONALD NORWOOD AT 1110 EDT ON 5/24/2015 * * * The following was provided by the licensee as clarifying information to the first paragraph of the original event notification: "As a conservative measure, the operating crew had previously started reducing power from 20 percent core thermal power when it was first noticed that main condenser vacuum was degrading. This was well before any low condenser vacuum alarms were received. "During the shutdown, after already securing the main turbine, the operating crew established benchmark values for degrading condenser vacuum for a normal plant shutdown and for a manual reactor scram should vacuum continue to decline to preclude an automatic scram." The licensee notified the NRC Resident Inspector. Notified R1DO (Dwyer). | 0 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-05-22
51086 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-05-22 00:14 | 2015-05-22 10:43 | 2015-05-22 | EMERGENCY DIESEL GENERATOR START DUE TO ACTUATION OF UNDERVOLTAGE CIRCUITRY "At 0014 PDT on 05/22/2015, Columbia experienced an unexpected momentary loss of SM-7, a Division 1 4.16 kV vital bus, resulting in a start of Emergency Diesel DG-1 . Additionally, under voltage circuitry prevented Standby Service Water pump 1A from starting to support DG-1 in response to the valid under voltage condition, and operators tripped the diesel at 0016 PDT. The SM-7 bus was reenergized by a 115 kV offsite source through backup transformer TR-B. "The cause of this event was an inadvertent trip of under voltage circuitry while connecting test equipment in preparation for Diesel and Loss of Power logic testing. Division 1 was inoperable due to ongoing maintenance during the current refueling outage and was not being relied upon for decay heat removal or core circulation. "Columbia is in Mode 5 with a coolant temperature of 96 degrees F, water level is at the normal refueling flooded level with fuel pool cooling gates removed. Division 2 is providing required electrical power and supporting components required for decay heat removal and inventory control. There was no impact to Shutdown Safety Assessment." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-05-22
51085 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-04-05 04:35 | 2015-05-22 09:31 | 2015-05-22 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. "On April 5, 2015 at 0435 CDT, during replacement of a failed fuse (2-FU1-64-16A-K33A), Unit 2 Primary Containment Isolation System (PCIS) logic received the B half of the Unit 2 Group 6 isolation signal. This caused initiation of the B and C Standby Gas Treatment, B Control Room Emergency Ventilation, isolation of the Unit 2 reactor zone and all three refueling zone ventilations. This was not a valid initiation of PCIS. "Operations personal responded to the PCIS initiation, ensured that all equipment operated as designed, and returned the affected systems back to service. "Plant conditions which initiate PCIS Group 6 actuations are Reactor Vessel Low Water (Level 3), High Drywell Pressure, and Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as PER 1010651. "The NRC Resident Inspector was notified of this event." | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-05-22
51084 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2015-03-26 16:29 | 2015-05-22 09:24 | 2015-05-22 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID PRIMARY CONTAINMENT AND DRYWELL ISOLATION VALVE ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 1629 EDT on March 26, 2015, the plant received a Division 1 balance of plant outboard containment and drywell isolation signal. The isolation signal was received while removing fuses to establish a clearance for the replacement of an average power range monitor bypass switch. The removal of two fuses removed power to the manual initiation logic resulting in an isolation signal. "The following component actuations occurred: valves 1P51F0150 and 1P51F0652, isolating service air to the containment and drywell; valves 1G61F0155 and 1G61F0170, isolating the containment and drywell floor drain sumps; valves 1D17F0071A and 1D17F0079A, isolating the drywell radiation monitor; valves 1D17F0081A and 1D17F0089A, isolating the containment radiation monitor; valve 1P11F0080, isolating the containment pools drain; valves 1P50F0060 and 1P50F0150, isolating the containment vessel chilled water system; valves 1P53F0070 and 1P53F0075, isolating the upper and lower airlock local leak rate air supply; valves 1P52F0160 and 1P52F0170, isolating the upper and lower airlock air supply; valve 1P22F0015, isolating mixed bed water to the drywell; and valve 1P54F0395, isolating fire protection carbon dioxide to the drywell. "This event is considered an invalid system actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). "The isolation was not initiated in response to actual plant conditions or parameters, and was not a manual initiation. Therefore, this notification is provided via a 60-day optional phone call in accordance with 10 CFR 50.73(a)(1) instead of submitting a written Licensee Event Report. "The event meets reporting criteria specified in 10 CFR 50.73(a)(2)(iv)(B)(2) as a general containment isolation valve signal affecting containment isolation valves in more than one system. All affected systems functioned as expected in response to the loss of power to the manual initiation logic. The valves were reopened in accordance with plant procedures. The inadvertent isolation signal was the result of a human performance error. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-05-22
51083 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-05-21 03:09 | 2015-05-21 12:03 | 2015-05-21 | DC ELECTRICAL ROOM HEAT LOAD CALCULATIONS NOT UPDATED AFTER NEW INVERTERS INSTALLED "At 0309 CDT on May 21, 2015, with the plant operating at 100 percent power, the shift manager was notified of a condition that could potentially lead to the failure of safety-related inverters in the DC electrical distribution system. This condition was identified while reviewing completed probabilistic risk analysis (PRA) calculations. It was discovered that control building ventilation system heat load calculations were not updated when new AC/DC inverters, with significantly higher heat output, were installed in 2007. Since the heat load calculations were not updated, it was not realized at the time that, under post-accident conditions involving a specific single failure, the DC electrical equipment rooms (i.e., inverters and battery chargers) could exceed their design basis ambient temperature, potentially leading to the failure of the inverters or battery chargers, and the loss of DC power in both divisions of the distribution system. The postulated scenario is the loss of offsite power (LOP)/loss of coolant accident (LOCA), followed by the failure of a single emergency diesel generator. If within 20 minutes prior to the onset of the event, the control building ventilation system had been shifted to the division in which the emergency diesel generator successfully started, the chiller in that division would, by design, be prevented from re-starting for as much as 20 minutes by its anti-recycle feature. (That feature limits successive starts of a chiller to prevent over-heating the motor.) The other chiller in that same division must be manually aligned for service, so it is not assumed to be available for these purposes. During the period in which the anti-recycle timer is running, no chiller would be in service, and the actual heatup rate of the inverters/battery charger could lead to room temperatures in excess of their design basis assumptions. As stated above, this condition (no ventilation cooling) would only exist for a maximum of 20 minutes from the time the associated divisional chiller was started, concurrent with a LOP/LOCA and a single failure. After expiration of the 20 minute timer, the chiller would perform the required function and lower room temperatures as expected. For best estimate PRA purposes, River Bend assumes an equipment survivability criteria of exposure to temperatures above 122 degrees F, but below 150 degrees F, for up to four hours. This is based upon the industry Station Blackout guidance of NUMARC 87-00, which was endorsed by the NRC as the basis for industry response to the Station Blackout Rule. This condition exists only after planned chiller swap and can be mitigated by opening the door to the inverter room should a LOP/ LOCA occur prior to the expiration of the 20 minute timer. Measures are in place for a dedicated operator to perform this function pending a modification to resolve the issue. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v) as the potential loss of the safety function of the DC electrical distribution system." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2015-05-21
51082 | -1 | WATERFORD | 3 |  |  | [3] CE | 2015-05-21 08:48 | 2015-05-21 10:47 | 2015-07-15 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to the monitoring of contraband inside the protected area. The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 07/15/2015 AT 1640 EDT FROM MARIA ZAMBER TO JEFF HERRERA * * * Further investigation determined that there was no reduction of the effectiveness of the physical security program nor was there any malevolent intent. The licensee has notified the NRC Resident Inspector. Notified the R4DO (Gaddy) and the Safeguards group (via email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-05-21
51081 | 0 | MAINE YANKEE |  |  |  | ISFSI | 2015-05-19 13:53 | 2015-05-19 15:41 | 2015-05-19 | SUSPICIOUS ACTIVITY INVOLVING SITE PHOTOGRAPHY Five individuals in a vehicle stopped at the gatehouse and took photographs and then departed the area. The licensee informed local law enforcement and the Maine State Police Fusion Center. Entered into the Protected Webserver (PWS) as SID-02666. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SUSPICIOUS ACT INVOLV CAT 1/2 RAD MATL | [9 empty] | NON EMERGENCY | 1 | ME | ISF |  | 37.57(b) |  |  |  | 1 | 2015-05-19
51080 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-05-19 11:30 | 2015-05-19 15:22 | 2015-05-19 | OFFSITE NOTIFICATION DUE TO ON-SITE SANITARY SEWER LEAK "At approximately 1130 EDT on May 19, 2015, Fermi-2 determined that a sanitary sewer system leak had occurred from underground lines beneath the parking lot near Warehouse E. Some of the sewage entered the storm sewer. The leak has been secured. A local sanitary contractor is currently responding to the site to clean the affected areas. The duration and quantity of the spill is unknown, however, current estimates of the sewage entering the storm sewer are less than 200 gallons. Reports to the Michigan Department of Environmental Quality (MDEQ), the local health department and the local news media are required in accordance with Michigan Act 451, Public Acts of 1994, as amended, Part 31, Section 342.3112a. Since reports are in the process of being made, this is considered a News Release or Notification of Other Government Agency, and therefore is reportable under 10 CFR 50.72(b )(2)(xi). "The NRC Resident Inspector has been notified." The release was onsite only and did not reach navigable waters. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-05-19
51079 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-03-17 13:06 | 2015-05-18 15:45 | 2015-05-18 | INVALID ACTUATION OF AUXILIARY FEEDWATER SYSTEM DURING ELECTRICAL TESTING "This 60-day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report an invalid actuation of the Auxiliary Feedwater (AFW) system at Watts Bar Nuclear Plant Unit 1. "On March 17, 2015, at 1306 EDT, Watts Bar Unit 1 was in Mode 1 at 100% power, when during the performance of 6.9 Kv phase verifications for the FLEX Diesel Generator, maintenance technicians were installing a multimeter (Simpson 260 Series) which resulted in starting the Unit 1 train B: motor-driven auxiliary feedwater pump, centrifugal charging pump, component cooling pump and thermal barrier booster pump, and isolated steam generator 1 and 3 blowdown. A secondary 6 ampere fuse opened due to an overcurrent and actuated (dropped-out) the associated blackout relays which started the identified pumps. At the time of the event, the train B standby diesel generator was removed from service for maintenance. The 6.9 Kv shutdown board did not lose power during the event and safety injection system and standby diesel generator features were not actuated. "The maintenance technicians performing the phase verifications immediately recognized that several supply breakers had closed after the last test lead was connected and promptly reported the event to the control room. Work was halted and TVA conducted a prompt investigation. While not conclusive, it is likely that the maintenance technicians created a shunt or ground condition while installing test equipment, causing a circuit overcurrent which opened the fuse, activating the black-out relays and actuating the identified pumps and valves. Plant operators responded appropriately to the event and the applicable Technical Specification Required Actions were exited at 1612 EDT, when equipment restoration had been completed. TVA is continuing to evaluate this event in accordance with the corrective action program (reference: PER nos.1003213 and 1027101). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-05-18
51078 | 0 | AECOM ENERGY & INDUSTRIAL CONST. |  |  |  |  | 2015-05-18 | 2015-05-18 15:18 | 2015-05-18 | INTERIM 10 CFR PART 21 REPORT REGARDING DEVIATIONS WHILE UTILIZING BENTLEY SOFTWARE STAAD.PRO ON SAFETY RELATED CALCULATIONS "This letter provides an Interim report in accordance with 10 CFR 21.21(a)(2) pertaining to the identification of deviations associated with calculations that were supplied to various licensees. The deviations stemmed from recently identified errors in vendor supplied software that is used in various structural analysis and design applications. "The software that was used, STAAD.Pro, is provided by Bentley Systems Incorporated. The present QA validated version of STAAD.Pro, V8i SELECT Series 4 Version 20.07.09.31, and prior versions have been used on various safety related calculations for nuclear power plants as well as a general analysis and design tool for non-safety related calculations for nuclear and non-nuclear power plants and facilities. "In accordance with our [AECOM] Nuclear QA Program, URS Energy & Construction (an AECOM Company) became aware of the deviations as a result of our periodic review of vendor issued error reports; specifically, STAAD.Pro Critical Error Report SPRO5336 and STAAD.Pro Critical Error Report SPRO5682. The noted errors can create instances that generate incorrect internal forces and moments in a structural member at various locations along the member's length. The result can be non-conservative evaluations of structural members (i.e., can under estimate the stress level in the analyzed members) and can potentially result in the inadequate design of structural components. "The software vendor is actively working to correct the noted deviations. Bentley anticipates that a modified version to STAAD.Pro will be issued in the third quarter of 2015. Alternate approaches are being pursued to accelerate completion of the evaluation of the noted deviation. We [AECOM] are notifying our clients of this issue and will provide follow-up written notification to the NRC within 30 days. "If you have any questions concerning this information, please contact Steve Mannon, Director of Licensing, at 803-412-5145. "At this time the potentially affected customers that have been notified concerning this issue are Exelon and DTE Energy. We [AECOM] are continuing our evaluation of potentially affected customers." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-05-18
51077 | 0 | MAINE YANKEE |  |  |  | ISFSI | 2015-05-10 11:31 | 2015-05-18 10:15 | 2015-05-18 | SUSPICIOUS ACTIVITY AT A SPENT FUEL FACILITY This event was copied from SID-02662: "On 5/10/15, at approximately 1131 hours [EDT], an older blue Toyota Camry was seen driving slowly by Maine Yankee (MY) via the Old Ferry Road. The same vehicle drove past MY and towards the Wiscasset Boat Launch and came back towards MY again slowly. "At 1136 hours, the blue Toyota Camry was seen stopped on Old Ferry Road in front of Maine Yankee. Using CCTV #28, two females were seen inside the vehicle. The passenger handed the driver an item that appeared to be a camera. The driver then exited the vehicle and proceeded to take photos of MY. The same female was seen in the roadway trying to take photos at many different angles. "The ISFSI Shift Supervisor (ISS) made contact with the female taking pictures at 1137 hours. The ISS was able to relay the name of the driver ([Deleted]), her phone number [Deleted] and the vehicle registration of Maine passenger car 3515TC to the Central Alarm Station. Furthermore, he identified that she was taking photos with a cell phone. [The driver] informed the ISS of the following: she wanted to take pictures of the casks. [The driver] was asked why she wanted to take photos and she stated 'because they are nuclear.' The ISS made her aware that there are concern's with her taking photos of the site. [The driver] stated, 'I am not a terrorist' and that 'she was angry, but not that angry.' "As a note [the driver] was asking lots of peculiar questions to include the temperatures of the casks, the ISS's salary and made a reference to Chernobyl. [The driver] and her passenger left the area at approximately 1147 hours. "As a note, after the event using the internet and searching for [the driver], we [ISS] were able to see that she has participated in different protests in the past. "At 1154 hours [EDT], MY management was notified of the above incident. Furthermore, Lincoln County Communications Center was notified of the incident at 1254 hours." From the driver's vantage point on the public highway, no security details could be photographed. The licensee informed NRC Region I. Notified R1DO (Schroeder) and ILTAB (Wray) on 5/10/2015. Notified the R1DO (Welling), NMSS Events Notification, and ILTAB (Johnson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SUSPICIOUS ACT INVOLV CAT 1/2 RAD MATL | [9 empty] | NON EMERGENCY | 1 | ME | ISF |  | 37.57(b) |  |  |  | 1 | 2015-05-18
51076 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2015-05-15 21:30 | 2015-05-18 08:52 | 2015-05-18 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL DISPOSED IN MEDICAL WASTE "On May 15, 2015, at about 2130 hours [EDT], Maryland Emergency Management Agency (MEMA) received an emergency notification from Stericycle located at 5800 Chemical Road, Curtis Bay [Baltimore], Maryland 21226. Apparently the biohazardous waste service received I-131 therapy waste from MedStar Washington Hospital (NRC licensee in Washington, D.C.). The waste was an immediate concern; temporarily closing the facility, with some I-131 contamination of facilities. Surveys indicated hot spot contact readings as high as 30 mR/hr with areas of general contamination. A private radiation consultant, Radiation Service Organization (RSO), was called and responded to the scene on 5/16/15. The area is being remediated and has now been reopened. Maryland is investigating the incident." Stericycle is not licensed to receive radioactive waste. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2015-05-26
51075 | 0 | CHICAGO BRIDGE AND IRON |  |  |  |  | 2015-03-18 | 2015-05-17 11:28 | 2015-05-17 | MEASURING AND TEST EQUIPMENT DEFICIENCIES The following information was received by facsimile: "This report is being provided as an interim report in accordance with 10CFR 21.21. "(i) Name and address of the individual or individuals informing the Commission. Adam Mohr; President, Fabrication and Manufacturing; CB&I; One CB&I Plaza; 2103 Research Forest Drive; The Woodlands, TX; 77380. "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. This is an interim report. The deviations being evaluated pertain to deficiencies identified within the Measuring and Test Equipment program at Chicago Bridge and Iron (CB&I) Laurens, 366 Old Airport Road, Laurens, SC. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. This is an interim report. The construction activities for the V.C. Summer [Units 2 and 3] and Vogtle AP1000r [Units 3 and 4] nuclear projects, which include procurement of the piping assemblies, are being performed by CB&I Power, 128 S. Tryon St., Charlotte, NC 28202. "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. This is an interim report. The evaluations of vendors and previously performed calibrations is under evaluation and equipment in question is being re-calibrated by an approved lab and evaluated for extent of condition. Additionally, causal analysis is being performed that is expected to provide relevant information pertaining to the cause of the deviations and if any quality assurance breakdowns may have occurred that could have produced a defect. Evaluation of the condition is expected to be completed by June 26, 2015. "(v) The date on which the information of such defect or failure to comply was obtained. The discovery date of the deviations that require evaluation is March 18, 2015, based on the nonconformance reports and C/PAR that identify the deviations. Evaluation of reportability in accordance with 10 CFR Part 21 was not able to be completed within the 60 day evaluation period. Additional time is needed to collect additional data pertaining to the identified nonconformances, perform causal analysis, and complete the evaluation. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured. or being manufactured for one or more facilities or activities subject to the regulations in this part. No basic components have been determined to fail to comply or contain a defect. This is an interim report. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. No basic components have been determined to fail to comply or contain a defect. This is an interim report. "(viii) Any advice related to the defect or failure to comply about the facility, activity. Or basic component that has been, is being, or will be given to purchasers or licensees. None at this time. "(ix) In the case of an early site permit, the entities to whom an early site permit was transferred. Not applicable." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-05-17
51074 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-05-15 21:48 | 2015-05-15 23:48 | 2015-05-18 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO 2 AC INVERTERS INOPERABLE "Class 1E A/C Unit SGK05A cools safety related electrical train 'A' and was found tripped at 2148 [CDT]. As a result, the following supported safety related electrical equipment were declared inoperable: 4.16 KV Bus NB01, 480 Volt Buses NG01 and NG03, 120 volt Instrument AC Inverters and Buses NN11, NN13, NN01 and NN03, 125 VDC Chargers and Buses NK11, NK13, NK01 and NK03. T/S 3.0.3 was entered from T/S 3.8.7 due to two out of four 120 volt AC Inverters (NN11 and NN13) being inoperable. All electrical systems listed above remain available but are declared inoperable due to inadequate room cooling capability. Plant shutdown to mode 5 commenced at 2244 [CDT]. No major equipment is out-of-service. All systems have functioned normally. Plant is currently at 99% with power ramping down. Plant must be in mode 3 by 0448 CDT. No compensatory measures have been established. "The NRC Resident Inspector has been notified." See EN #51071 for an earlier T/S required shutdown required at 0436 CDT on 5/15/15, due to the same conditions. * * * UPDATE FROM BRET DAVIS TO VINCE KLCO ON 5/18/15 AT 1600 EDT * * * "For both EN 51071 and 51074, the low lube oil pressure switch tripped the SGK05A unit. Oil pressures were verified to be normal and the SGK05A unit was successfully started. The plant shutdown each time was terminated. A fault in the Electronic Oil Pressure control which monitors the low lube oil pressure switch was identified. A jumper has been installed that bypasses the oil switch while maintenance is being conducted. The unit was declared functional but degraded. Indication of low oil pressure is still provided. " The licensee notified the NRC Resident Inspector. Notified the R4DO (Okeefe). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2015-05-16
51073 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-05-15 17:53 | 2015-05-15 21:03 | 2015-05-15 | INADVERTENT SIREN ACTUATION "A South Texas Project Offsite Emergency Notification siren was [inadvertently] going off. The Matagorda County Sheriff's office notified the Emergency Response organization at the station that a siren had actuated during a severe thunderstorm moving through the area. Station personnel are addressing the issue with the siren. "The Matagorda County Sheriffs office was the only offsite agency that was contacted during this event." The licensee notified the NRC Resident Inspector. | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-05-15
51072 | 0 | MAINE YANKEE |  |  |  | ISFSI | 2015-05-15 15:23 | 2015-05-15 18:42 | 2015-05-15 | SUSPICIOUS ACTIVITY DUE TO UNKNOWN AIRCRAFT FLYOVER The following information was excerpted from a received email: The following is being reported in accordance with 10CFR37.57(b) because the greater than Class C (GTCC) materials stored at Maine Yankee includes Category 1 and 2 material. An unknown aircraft made multiple passes over Maine Yankee property. The licensee notified the local law enforcement, Maine State Police, Federal Aviation Administration and the FBI. On May 15, 2015 at 1523 EDT, a Maine Yankee security force member reported seeing a large unmanned aircraft flyover the west side of the Maine Yankee property. A few minutes after this report the ISFSI shift supervisor investigated the situation with no results. At 1548 EDT, a second report from multiple security force members saw the aircraft flyover the Security/Operations Building and possibly the Protected Area. The aircraft was flying from south to north. The Wiscasset Police, Lincoln County Sheriff and Maine State Police arrived on site and discussed the situation with the licensee Shift Supervisor. After leaving the site to continue the investigation, the Wiscasset Police Department notified Maine Yankee that the local airport manager (Wiscasset Airport) stated that a single occupant rear prop aircraft had flown in and fueled and then departed. The airport manager stated when the aircraft departed, it banked left (East) towards Maine Yankee property. The manager believes the last two digits of the tail number were 'VS'. No information of the pilot was gathered while at the airport. The event was believed to have been an unmanned aircraft at the beginning and was later determined to most likely to be a single occupant aircraft. No information was gathered of the pilot of the aircraft so it is unknown if it was in fact the aircraft that flew over Maine Yankee property. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SUSPICIOUS ACT INVOLV CAT 1/2 RAD MATL | [9 empty] | NON EMERGENCY | 1 | ME | ISF |  | 37.57(b) |  |  |  | 1 | 2015-05-15
51071 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-05-15 04:36 | 2015-05-15 07:22 | 2015-05-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO 2 AC INVERTERS INOPERABLE "Class 1E A/C Unit SGK05A cools safety related electrical train 'A' and was found tripped at 0436 [CDT]. As a result, the following supported safety related electrical equipment were declared inoperable: 4.16 KV Bus NB01, 480 volt Buses NG01 and NG03, 120 volt Instrument AC Inverters and Buses NN11, NN13, NN01 and NN03, 125 VDC Chargers and Buses NK11, NK13, NK01 and NK03. T/S 3.0.3 was entered from T/S 3.8.7 due to two out of four 120 volt AC Inverters (NN11 and NN13) being inoperable. All electrical systems listed above remain available but are declared inoperable due to inadequate room cooling capability. Plant shutdown to mode 5 commenced at 0530 [CDT]. No major equipment is out-of-service. All systems have functioned normally. Plant is currently at 95 % power ramping down. Plant must be in mode 3 by 1136 CDT. No compensatory measures have been established. "The NRC Resident Inspector has been notified." | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2015-05-15
51070 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-05-14 16:00 | 2015-05-14 23:02 | 2015-07-08 | UNANALYZED CONDITION DUE TO EXCESSIVE TOXIC CHEMICALS ONSITE "On May 14, 2015, it was determined that the number of 55 gallon drums of 2-Butoxyethanol analyzed to be transported and stored within the owner-controlled area (OCA) at any one time had been exceeded. It was discovered that contrary to the toxic gas analysis performed, fourteen 55-gallon drums of 2-Butoxyethanol were transported and stored in the OCA to support the construction of a dome being built to provide storage for FLEX equipment. The number of drums exceeded the limitation specified in the toxic gas analysis performed as part of the design project for transportation and storage could potentially impact Control Room habitability, emergency diesel generator air intake and have an adverse impact on security personnel. "Upon determination that an unanalyzed condition existed, Operations placed the control room ventilation system in the 'isolation mode' until the number of drums on-site was reduced within the analyzed number. A substantial covering had been placed over the drums which also decreased the likelihood that any of the drums would fail and would also limit the potential dispersion of chemicals should a breach occur. "The excess number of drums of 2-Butoxyethanol being transported and stored on-site is considered an unanalyzed condition that significantly degraded plant safety and is reportable in accordance with 10CFR50.72(b)(3)(ii)(B)." The allowed number of 55 gallon drums of 2-butoxyethanol allowed per the current toxic gas analysis is 4 drums. The number of drums has been reduced to 2 as of 2024 EDT. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM PAUL UNDERWOOD TO VINCE KLCO ON 7/8/2015 AT 1657 EDT * * * "Further investigation into the chemicals transported on-site (F183M, of which 2-Butoxyethanol is a component) revealed that an on-site spill of all fourteen 55-gallon drums will not adversely affect Main Control Room Habitability, Security Personnel, or the Emergency Diesel Generators (EDGs). "The Control Room Habitability Determination flowchart in Attachment 3 of NMP-CH-002-002 establishes a 10 mmHg vapor pressure threshold for determining if chemicals need to be evaluated for impact on the Main Control Room. Chemicals with a vapor pressure less than 10 mmHg do not need to be evaluated for control room habitability. The basis for the threshold is found in Reg Guide 1.78 Revision 0 section C.5.a, 'For chemicals that are not gases at 100F and normal atmospheric pressure but are liquids with vapor pressures in excess of 10 torr (10 mmHg), consideration should be given to the rate of flashing and boil off to determine the rate of release to the atmosphere and the appropriate time duration of the release.' The individual chemical component (including 2-Butoxyethanol) vapor pressures are less than 10 mmHg. "As their vaporization rate is too low to adversely affect Control Room Habitability, it is also too low to create a hazard for Security personnel or to adversely affect the Emergency Diesel Generators. "Based on this information, the transportation and storage of these chemical barrels did NOT represent a condition that significantly degraded plant safety. As such, this condition has been determined to no longer meet reporting requirement 10CFR50.72(b)(3)(ii)(B) and is therefore NOT reportable. Based on this information the previous notification for Event 51070 is being retracted." The licensee notified the NRC Resident Inspector Notified the R2DO (McCoy). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-05-14
51069 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2015-02-24 | 2015-05-13 16:37 | 2015-05-13 | INCORRECT DOSE RECORDED ON PRESCRIPTION DIRECTIVE "This is a notification, pursuant to 10 CFR 35.3045(a)(1), of a medical event that occurred at the VA Salt Lake City Health Care System, Salt Lake City, Utah. "On February 24, 2015, a dosage of 30.8 millicuries of I-131 sodium iodide (capsule form) was administered to a patient for a thyroid ablation. The prescribed dosage on the written directive was incorrectly annotated as 3 millicuries. "The basis for identifying this as a medical event is the administered dosage differed from the prescribed dosage, as annotated on the written directive, by more than 20 percent. "The medical event was discovered today (May 13, 2015) during an inspection, conducted by the National Health Physics Program (NHPP). "Interview of the Radiation Safety Officer revealed the standard dosage for a thyroid ablation is 30 millicuries of I-131 sodium iodide (capsule form). Interview of the authorized user (a physician) revealed the intended prescription was for 32 millicuries of I-131 sodium iodide (capsule form). "No biological harm to the patient is expected since the thyroid ablation was successfully performed. The patient and attending physician were not informed of the incorrect annotation on the written directive since the thyroid ablation was successfully performed, as clinically intended, with a dosage of I-131 sodium iodide (capsule form) within an acceptable range of the authorized user's intent. "The inspection is ongoing with causal factors and corrective actions being developed. Additional information will be provided in a 15-day written report, to be submitted to NRC Region III. National Health Physics Program notified NRC Region III (Patricia Pelke, Chief, Materials Licensing Branch Chief) of the medical event by telephone. "The Department of Veterans Affairs holds NRC License No. 03-23853-01VA, a master materials license. Permits are issued under the license to Veterans Health Administration facilities. The VHA permit number for the facility involved in this medical event is 43-03299-01. National Health Physics Program makes required notifications to NRC. " A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | UT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-05-21
51068 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-04-03 | 2015-05-12 22:13 | 2015-05-12 | LOSS OF RADIOLOGICAL ASSESSMENT CAPABILITY DUE TO NON-FUNCTIONAL RADIATION MONITOR "On 4/21/2015, during performance of source check surveillance on the liquid effluent radiation monitor for the Plant Service Water (TSW), a non-radioactive system, it was discovered that the instrument was determined to be nonfunctional. It was determined on 4/25/15 that the failure was due to an incorrect 'as left' setting from testing conducted on 4/3/2015. The instrument was determined to be non-functional from the period 4/03/15 to 4/25/15 when the setting was corrected. "On 5/12/15 it was recognized that because no compensatory measures were implemented during the time the instrument was non-functional that this condition constituted a major loss of radiation assessment capability which is reportable in accordance with 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector will be notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-12
51067 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-05-11 16:30 | 2015-05-12 19:32 | 2015-05-22 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation related to the monitoring of the plant boundary. Compensatory actions taken. The NRC Resident Inspector has been notified. * * * RETRACTION PROVIDED BY DAVID HENSON TO JEFF ROTTON AT 1745 EDT ON 05/14/2015 * * * 10 CFR 73.67 one hour reporting requirement originally reported determined to not be applicable to this facility. Based on that information, it is appropriate for the one-hour report (NRC # 51067) to be formally retracted The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Bonser), NMSS EO (Sampson), 73.71 Safeguards Group, and NMSS Events Notification Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2015-05-20
51066 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-05-12 01:04 | 2015-05-12 09:08 | 2015-05-12 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "On May 12, 2015, at 0104 CDT, during performance of 3-SR-3.3.6.1.2(3B), High Pressure Coolant Injection (HPCI) System Steam Supply Pressure Low Functional Test, an inadvertent PCIS Group 4 (HPCI) isolation occurred. All automatic actions occurred as designed. HPCI was declared inoperable and Technical Specification LCO 3.5.1.C was entered with required action to verify immediately that RCIC is operable administratively and to restore HPCI to operable within 14 days. HPCI was returned to service at 0125 CDT, declared operable and TS LCO 3.5.1.C was exited. The cause of the isolation is unknown with an investigation in progress. "This condition is reportable as an 8-hour ENS notification under 10CFR 50.72(b)(3)(v)(D) due to the failure of a single train system affecting accident mitigation. "This condition also requires a 60 day written report. "The NRC Resident Inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-05-12
51065 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-05-12 04:30 | 2015-05-12 05:48 | 2015-05-12 | REACTOR TRIP DUE TO MAIN GENERATOR DIFFERENTIAL TRIP "This is an non-emergency notification to the NRC [Headquarters] Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the reactor protection system (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation (eight hour notification) due to auxiliary feedwater (AFW) initiation. "On 5/12/15 at 0430 EDT, Unit 4 experienced an automatic reactor trip due to Generator Differential Trip. Investigation is underway to determine the cause. Auxiliary feedwater automatically initiated as expected. All systems operated correctly in response to the reactor trip. Unit 4 is currently in Mode 3 and stable." All control rods fully inserted. Normal offsite power is available with decay heat is being removed by the atmospheric steam dumps. There is no known primary to secondary reactor coolant system leakage. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 81 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-05-12
51064 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-05-11 16:29 | 2015-05-11 20:38 | 2015-05-11 | LOSS OF POWER TO DIGITAL RADIATION MONITORING SYSTEM "At 1629 EDT on May 11, 2015, Beaver Valley Power Station (BVPS) Unit 1 (Mode 6 Refueling) opened circuit breaker PCB-92 to de-energize system service transformer 1A due to an emergent issue with a transformer bushing. This resulted in a loss of power to the ERF [Emergency Response Facility] substation which powers various plant support equipment at both units. The BVPS Unit 2 Digital Radiation Monitoring System (DRMS) was non-functional for approximately 21 minutes. This was a loss of radiation monitor capability to alarm and indicate in the control room. Following power restoration to the ERF substation, the radiation monitor system was restored at 1650 EDT. Both Unit 1 and Unit 2 remain stable. "Since the BVPS Unit 2 DRMS was non-functional, this event resulted in a loss of emergency assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-11
51063 | 0 | BNL INDUSTRIES, INC. |  |  |  |  | 2015-05-01 | 2015-05-11 13:59 | 2015-05-11 | PART 21 - DEFECT IDENTIFIED 6 INCH GEAR OPERATED BALL VALVES The following is excerpted from a reported submitted by BNL Industries, INC.: "On May 1, 2015 BNL identified a discrepant condition in which material was identified by an audited third-party material testing facility as meeting the requirements of ASME SA-105, despite having a test yield strength of 35.6ksi (vice 36ksi required by the specification). "The discrepant material has already been manufactured and incorporated into a basic component and shipped to the end users. "Based on BNL engineering evaluations of the design criteria, code requirements and supplied material, BNL has determined there to be no safety hazard. Engineering evaluations EE-A150217 Rev. 0 and EE-A141009-23 Rev. 0 are being supplied to the purchasers. "First Energy - Perry - 1 endcap supplied, P/N GBV-B2-60-0020 PC. 3, Serial Number A150217-1-1 (Trace Number 547G-1) "First Energy - Beaver Valley - 7 endcaps supplied, GBV-B2-60-0112 PC. 3, Serial Numbers A141009-23-3 (2pcs.), A141009-23-4 (2pcs.), A141009-23-5 (2pcs.), A141009-23-6 (1 pc.) (Trace Number 547G-1)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-05-11
51062 | 0 | U.S. AIR FORCE |  |  |  |  | 2015-04-13 10:30 | 2015-05-11 09:48 | 2015-05-11 | LOST/MISSING CALIBRATION SOURCE The following was received by email: "Notification from Master Material License [MML] No. 42-23539-XXAF, issued to the Department of the Air Force. The following report of a possible lost or missing source likely involves a source not specifically licensed under the MML: "On 13 April 2015 at 1030 hours, an officer newly assigned to Cannon AFB [Air Force Base] discovered a source on the radioactive material inventory he could not physically locate. The source was listed as an Am-241 check source for a Smiths model 1500 instrument, with no information provided except for a previous storage location. The officer could not locate any records of disposition for this source, but continues to investigate disposition records for the base. The officer interviewed a predecessor who asserted the Am-241 line item on the inventory could be a clerical error. "The licensee contacted Smiths Detection which to date could not verify the existence of a Smiths Model 1500 or an Am-241 check source. "They are unaware of any exposures at this time. "The base will ensure complete/accurate data entry for radioactive material inventories and subsequent verification of inventory through physical 'eyes-on' inventories." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-05-19
51061 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2015-05-09 18:55 | 2015-05-09 19:45 | 2015-05-09 | UNUSUAL EVENT DECLARED DUE TO STEAM LEAK IN THE TURBINE BUILDING At 1855 EDT, a steam leak from the #1 moisture separator reheater in the turbine building was reported to the control room. Operators performed a rapid down power to approximately 30% at which time the reactor was manually tripped. At 1910 EDT an Unusual Event was declared. The steam feed rupture control system was manually initiated (this includes actuation of both turbine-driven Auxiliary Feedwater Pumps) and the steam leak was isolated. Station air compressor #2 (non-safety related) tripped. Station air compressor #1 automatically started. The unit is currently in mode 3 (Hot Standby) and stable. Steam is being discharged through the atmospheric dumps as a means of decay heat removal. There is no known primary to secondary leakage. All systems functioned as expected. There were no reported injuries and personnel accountability is in progress. The licensee notified state and local agencies and informed the NRC Resident Inspector. Notified DHS SWO, FEMA Ops Center, NICC Watch Officer and FEMA NWC and NuclearSSA via email. * * * UPDATE AT 2201 EDT ON 5/9/15 FROM GERRY WOLF TO S. SANDIN * * * The licensee exited the Unusual Event at 2121 EDT based on the following: "At 2121 hours EDT, the Unusual Event at the Davis-Besse Nuclear Power Station was terminated. The steam leak has been isolated and plant conditions are stable. Cooling continues to be maintained via the auxiliary feedwater system. "The initiation of auxiliary feedwater at the start of the event is reportable as a Specified System Actuation per 10CFR50.72(b)(3)(iv)(A)." The licensee notified state and local agencies and informed the NRC Resident Inspector. Notified R3DO (Skokowski), NRR EO (Morris) and IRD (Grant). Notified DHS SWO, FEMA Ops Center, NICC Watch Officer and FEMA NWC and NuclearSSA via email. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  | 0 | 2015-05-09
51060 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-05-09 17:50 | 2015-05-09 18:19 | 2015-05-09 | UNUSUAL EVENT DECLARED DUE TO MAIN TRANSFORMER FIRE "At 1750 EDT [05/09/15,] Indian Point Unit 3 experienced a fire on the 31 Main Transformer resulting in a unit trip. An Unusual Event was declared at 1801 EDT. The onsite fire brigade was mobilized. Offsite fire fighting assistance was requested. The fire was reported extinguished at 1815 EDT. The reactor was shutdown by an automatic trip. Plant response to the trip was as expected with no complications. The 31 and 33 Auxiliary Feed Pumps are operating and feeding the steam generators. Accountability is being performed." The plant is stable in mode 3, all control rods fully inserted, with normal offsite electrical power, and decay heat is being released to the main condenser. There was no impact on Unit 2 which continues to operate at 100% power. The licensee has notified the NRC Resident Inspector and state and local authorities. Notified DHS SWO, FEMA OPS Center, DHS NICC Watch Officer, and Nuclear SSA via email. * * * UPDATE FROM LUKE HEDGES TO JOHN SHOEMAKER AT 2037 ON 5/9/15 * * * "Oil from 31 Main Transformer has spilled into the discharge canal and has made its way into the river. Plant personnel are sandbagging drains and release paths. IPEC [Indian Point Energy Center] has contacted its environmental contractor, who is expected onsite at 2100 EDT to assist with cleanup. The National Response Center was notified at 1945 EDT and issued notification number 1116011. A message was left with the Westchester County Department of Health at 1953 EDT. The NY State DEC [Department of Environment Conservation] was contacted at 1955 EDT and issued notification number 1501459." The licensee has notified the NRC Resident Inspector. Indian Point Unit 3 remains in an Unusual Event at this time. Notified R1DO (Schroeder). * * * UPDATE FROM LUKE HEDGES TO JOHN SHOEMAKER AT 2141 ON 5/9/15 * * * "Indian Point Unit 3 exited the Unusual Event at 2103 EDT. The basis for exiting the Unusual Event is that the fire is out and field operators report they have been successful in cooling the transformer." The licensee has notified the NRC Resident Inspector and state and local authorities. Notified R1DO (Schroeder), R1RA (Lew), NRR (Dean), NRR EO (Morris), NRR EO (Howe), and IRD (Grant). Notified DHS SWO, FEMA OPS Center, DHS NICC Watch Officer, and Nuclear SSA via email. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2015-05-09
51059 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-10-01 | 2015-05-08 12:33 | 2015-05-08 | AGREEMENT STATE REPORT - SHUTTER STUCK OPEN ON A FIXED GAUGE The following information was received from the State of California via email: "At 1510 [PDT] on May 7, 2015, the licensee notified us [California Radiation Control Program] that the shutter on their belt weight scale on the Coarse Gangue Belt in Plant 1 is stuck in the open position. This is a generally licensed device (Berthold Technologies, Model: LB300L, s/n: 17729-1061-10003 containing 18 mCi Cs-137). The shutter malfunction was initially found during their six month shutter check in October 2014, however, the licensee only became aware of the reporting requirement last week when they contacted the manufacturer to repair the device. The device is in a restricted area 100 feet above the ground on a conveyance structure. The source is below the belt and the beam path is upward with no real exposure potential to any personnel in the area. The only way to access the belt and the source is via a catwalk which is not in the beam path. The dose rate on the catwalk is approximately 0.4 mRem/hr." CA 5010 Number: (Date Notified): 050715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-05-18
51058 | 0 | BROOKE ARMY MEDICAL CENTER |  |  |  |  | 2015-05-07 11:11 | 2015-05-08 11:53 | 2015-05-08 | LOST IODINE-125 SEED "On May 7, 2015, [Command Radiation Safety Officer (CRSO)] was notified by Brooke Army Medical Center [BAMC] Pathology that they could not find a I-125 seed. The seed was from a radioactive seed localization procedure for a breast biopsy. [The licensee's] Health Physics Service sent two personnel to investigate the loss and attempt to find the seed. After tracking the chain of custody and attempting to find the seed [the licensee] concluded that the seed was thrown away into the bio-hazard waste in pathology with the specimen tray. "On May 6, 2015, the pathologist transferred a biopsy specimen from a receiving tray to an examination tray. [The pathologist] then discarded the receiving tray in the bio-waste and used an RSL [radioactive seed localization] node seeker to confirm seed presence in the specimen. [The pathologist] misread the meter, marking on the seed tracking chain of custody form that the seed was present. [The licensee] examined the radiograph of the specimen, taken just before arriving at pathology, and found that the seed was on the edge of the biopsy specimen. [The licensee] believes the seed fell into the receiving tray upon transfer of the specimen and the seed was discarded along with that tray. "The bio-hazard waste was disposed after this point, [approximately] 0600 [CDT] on May 7, 2015. On May 7, 2015, during clinical examination of the specimen and during the procedure to extract the seed, the pathologist could not find the seed. The RSO was called at this point and the investigation began. [The licensee] notified our environmental services branch and the waste disposal company to notify them that they may encounter a radioactive seed. "The seed is I-125. The initial activity was 0.300 mCi on March 27, 2015, and was 0.185 mCi as of May 7, 2015. "Today, BAMC Health Physics Service conducted an inventory and has accounted for all other I-125 RSL seeds besides the one mentioned in this email. [The licensee] will retrain the pathology section on proper procedures and conduct an in-service on how to read the RSL node seeker for confirming the presence of the seeds. [The licensee] will also discuss with pathology additional physical measures that can be implemented to ensure this does not happen again. "[The CRSO] will send a full report along with memorandums and status on measures taken to prevent future occurrences." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-05-18
51057 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-05-07 15:15 | 2015-05-08 11:02 | 2015-05-08 | INADVERTENT INTRODUCTION OF ALCOHOL INTO THE PROTECTED AREA "On May 7, 2015, at 1515 hours, B&W NOG-L Security management determined alcohol had been inadvertently introduced into the Protected Area through the shipping and receiving process. 10 CFR 26.719(b)(1) requires that the licensee report to the Operations Center within 24 hours of discovery, the use, sale distribution, possession, or presence of illegal drugs, or the consumption or presence of alcohol within a protected area. The item in question was a six pack of bottled beer which was part of a box of promotional items personally delivered by a sales representative from Graybar Electric. "The B&W employee addressee first became aware of the package through an email and voicemail left by the salesman advising of a package delivery and indicating the presence of alcohol in the package. The B&W employee immediately contacted Shipping and Receiving management at approximately 1300 hrs. in an effort to intercept the package before delivery; however the package had already been processed into the Protected Area. "Shipping and Receiving Management contacted the delivery driver via radio and instructed the driver not to deliver the package. The delivery driver separated the package from the delivery items. The package was removed from the Protected Area and returned to the Shipping and Receiving Manager located in the Owner Controlled Area at approximately 1500 hrs. The package was returned unopened. B&W Security Management was notified of the incident at approximately 1515 hrs. "All items processed through Shipping and Receiving undergo security x-ray inspection. Containers of liquid are commonly processed items and therefore did not create an elevated level of suspicion which would have led to the officers conducting a visual inspection. "B&W NOG-L Management will conduct an evaluation of the incident to include root cause analysis and corrective actions to prevent recurrence." The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 0 | 2015-05-15
51056 | 0 | CARDINAL HEALTH NUCLEAR PHARMACY |  |  |  |  | 2015-05-08 05:40 | 2015-05-08 08:05 | 2015-05-08 | STOLEN RADIOPHARMACEUTICALS The following event occurred in Kansas City, MO. The corporate office of Cardinal Health Nuclear Pharmacy was notified that a vehicle being used to deliver material to the VA [Veterans Affairs] Hospital in Kansas City, MO had been stolen at approximately 0540 CDT on 5/8/2015. Inside the vehicle were two packages, each containing Tc-99m. The maximum combined activity of the Tc-99m in the two packages was less than 250 millicuries. Both VA security and the Kansas City, MO police were notified. VA security is reviewing security videos for possible leads. The Kansas City, MO police case number is 15-31091. * * * UPDATE FROM DAN HILL TO DONALD NORWOOD AT 1052 EDT ON 5/8/2015 * * * The following information was received via E-mail: "The vehicle was located in Overland Park, KS by the police in Overland Park. Cardinal Health Kansas City sent drivers to retrieve the vehicle. It is now back at the Cardinal Health Kansas City nuclear pharmacy as of 0935 CDT on May 8, 2015. Packages containing radioactive materials in the vehicle with tamper resistant seals are intact and unopened." Apparently the vehicle was stolen by a patient of the VA Hospital. The identity of this individual was able to be confirmed. Notified R3DO (Skokowski), ILTAB (Wray), and NMSS Events Notification.. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-05-18
51055 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2015-05-07 17:27 | 2015-05-07 18:55 | 2015-05-07 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "Today at 1727 EDT, an automatic scram from a turbine trip occurred. The cause of the turbine trip is currently under investigation. All rods inserted into the core and all systems functioned as expected during the scram. "The event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." Plant response to the scram was uncomplicated and the plant is stable in Mode 3. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-05-07
51054 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-05-07 15:30 | 2015-05-07 17:51 | 2015-05-07 | OFFSITE NOTIFICATION DUE TO A BOATING ACCIDENT ON THE STATION COOLING LAKE "This report is being made pursuant to 10CFR50.72(b)(2)(xi), News Release or Notification of Other Government Agency. Operations received a report from Security that a fishing boat has capsized on the station cooling lake. At 1530 [CDT] the LaSalle County Operating Department was notified that the LaSalle County Coroner confirmed that there was a fatality. The Illinois Department of Natural Resources (IDNR), LaSalle County Sheriff, Seneca Rescue Team, and NRC Senior Resident Inspector have been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-05-07
51053 | 0 | QUALTECH NP |  |  |  |  | 2015-05-07 | 2015-05-07 14:31 | 2015-05-07 | POTENTIAL PART 21 INVOLVING STRUTHERS DUNN RELAYS WITH CONTACT RESISTANCE GREATER THAN ONE OHM The following is excerpted from a report submitted by QualTech NP, Nuclear Division, Curtiss-Wright Corporation: "Subject: "PSEG reported failures for Struthers Dunn 219BBX200 relays related to greater than 1 ohm contact resistance. Two relays were evaluated by Exelon Power Labs. Of these, one had a failure consisting of a contact resistance greater than one ohm. Struthers Dunn has also provided an evaluation in this regard and does not agree with the failure mode as inferred in the Exelon Power Labs report. "Lab and OEM report key difference: "The Power Labs' Report(s) shows fiberglass fiber(s) embedded into gold plated contacts on one relay believed to result in a contact resistance greater than one Ohm (1.7 Ohm Max). The second relay, from stock, had evidence of fiberglass present but was not considered to have affected functionality. "The Struthers Dunn evaluation suggests that the fiber embedded on the gold contact is not at the mating point of the contacts and should not impact operability. Struthers Dunn also indicates that the relay's application is operating below their minimum current. "Discussion: "The actuator board on the evaluated relays is manufactured from a printed circuit board (PCB) type fiber board. The fibers from the edges of the board could become airborne. [. . . ] this specific board material was utilized beginning in March 2010. Since there have been no prior reports of this issue, it is possible that the 2010 material change introduced a foreign materials exclusion (FME) concern. Since then, and solely for those relays manufactured in the USA, the material changed again in November 2014 and was incorporated into the products starting January 2015. The newest version of the actuator board is a molded material that does not contain fiberglass fibers. "Struthers Dunn relays with base part numbers 219, 236, 237, and 255 have the common PCB type fiber board. This fiber board was used in relays with date code 1009 through 1452 with or without letter suffix (where the letter indicates made outside of the USA). "Customer Input: "1st 219 series relay failed due to contact issue, considered a random failure & discarded. 2nd 219 series relay failed due to contact resistance & sent to Exelon Power Labs. Five parts from inventory bench tested. One had high resistance and it was sent to Power Labs "Note: All parts provided were 100% functionally tested for contact resistance during dedication process and passed testing at QTNP. "Vendor Input: "Struthers Dunn has, since 2010, experienced only one field complaint (PSE&G) on continuity issues related to fiberglass on these 219 relays. The material change to ULTEM 2300 was considered an ongoing quality/process improvement process to reduce potential defects proactively. Over the four years using this PCB type material, 13,000 relays were sold. "Struthers Dunn has also questioned the application having current below the manufacturer's recommended value of 50mA, requiring bifurcated contacts. Please see their attached report and current product catalog for details. "Recommendation: "The root cause of the failure is inconclusive. Exelon Power Labs said 'The irregular contact surface patterns in conjunction with the presence of the embedded fiberglass fibers are the most likely cause of the excessive resistance. This finding is considered to be a manufacturing defect.' While the manufacturer sees the failure as a misapplication of its product and that the fiber 'was not located at the 'mating point' of the 2 contacts so therefore has no effect on the performance of the contacts or relay.' "QualTech NP recommends an application review for the named relays. A review of the Exelon Power Labs reports and the vendor's report should also be completed by the utility to evaluate the impact on the safety function." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-05-07
51052 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2015-01-27 | 2015-05-07 16:12 | 2015-05-07 | AGREEMENT STATE REPORT - STOLEN THERMO FISHER XRF ANALYZER The following information was received from the New York Department of Health [DOH] via fax: "The Department of Health (DOH) became aware of this incident on 5/6/15. The DOH phoned the Vice President of Metro Metal Recycling, LLC on an unrelated detail of license C3062 renewal. The licensee stated on 5/6/15 that he did not need the license anymore because on 1/27/15, his Thermo Fisher XRF, Model XLP 818, Serial Number 13149, had been stolen. He had not contacted DOH to report the stolen XRF, which contained 30 millicuries of americium-241. He did notify Colonie Police and obtained a police report. He e-mailed a copy of the police report and photographs of a damaged metal fence to DOH. The police report states that an unknown person broke the lock to their gate, broke an office window and entered the office where they stole the XRF from an unlocked desk drawer. There was no surveillance video. The guard dogs have access to the metal storage area but not the office area. The Vice President was sent an e-mail requesting additional information." The Thermo Fisher XRF (X-Ray Fluorescence) Analyzer is used to identify metal alloys. NY Event Report ID No.: NY-15-03 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-05-15
51051 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-05-05 10:00 | 2015-05-07 12:21 | 2015-08-21 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING LESS THAN THE PRESCRIBED DOSE DELIVERED TO PATIENT The following report was received from the State of California via email: "At approximately 1000 PDT on May 5, 2015, a medical event occurred during a Y-90 Therasphere procedure. The prescribed dose to the organ (liver) was 12,000 rem, but the delivered dose was 6,920 rem. This event meets the 10 CFR 35.3045(1)(i) 24-hour report criteria since the dose differed from the prescribed dose by more than 50 rem to an organ (5080 rem under dose) and the total dose delivered differed from the prescribed dose by 20 percent or more (42% under dose). Although the equipment indicated the entire dose had been delivered to the patient, a large amount of the dose was is still in the tubing and vial and had not actually been delivered to the patient as indicated. The licensee will contact the manufacturer to assist in finding the root cause of the malfunction to determine whether it was an equipment malfunction, operator error, or both. The treating physician is also the prescribing physician. The licensee has contacted the physician to verify if the physician has notified the patient and if there was any effect on the individual from this event. The licensee will provide the written report within 15 days as required which will also describe what actions will be taken to prevent reoccurrence." California Report Number: 050616. * * * RETRACTION AT 1229 EDT ON 8/21/2015 FROM ROBERT GREGER TO MARK ABRAMOVITZ * * * The following was received via e-mail: "The California Radiation Control Program would like to retract the subject event notification for the medical event at UCLA. Subsequent evaluation determined that the patient received the prescribed dosage. Some contamination on the exterior of the equipment utilized in the therapeutic dosage administration was determined to have misled the licensee staff to initially believe that an under-dosage to the patient had occurred." Notified the R4DO (Hay) and NMSS Events Resource (via e-mail). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-05-15
51050 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-23 | 2015-05-07 12:52 | 2015-05-07 | AGREEMENT STATE REPORT - MISSING TROXLER MOISTURE DENSITY GAUGE The following information was provided by the State of Texas via email: "A representative of the licensee called [the Texas Department of State Health Services] and stated that two weeks ago a Troxler 3430 (sn 24971) had gone missing. He [the licensee] could not find it after calling his service companies and employees. He further said that the serial numbers for the sources are 75-3877 and 47-17874. He does not know what the activity of these sources is. He says that he will begin a written report. Further information will be provided in accordance with SA300 guidelines." The licensee notified the Houston Police Department (report #0496748-15). Texas Incident #: I-9312 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-05-15
51049 | 0 | HOWARD UNIVERSITY HOSPITAL |  |  |  |  | 2008-02-01 | 2015-05-07 11:20 | 2015-05-07 | CONTAMINATION DETECTED IN SOURCE STORAGE ROOM IN 2008 The following is excerpted from statements recorded by the RSO on Aug 26th, 2009, concerning contamination discovered by the licensee in [the source storage room] Feb/Mar 2008, of their facility: "1. A source being held in storage was discovered to have external contamination about Feb/Mar 2008. The source was being prepared for an upcoming disposal of sources. The source was in storage in a vault in the [source storage room at their facility]. This room is primarily used to do survey meter calibrations. "2. When the contamination was discovered the techs were directed to not use the room. Any activities (detector calibrations) requiring that area were conducted by the RSO. The area was evaluated for contamination. Spots of contamination were found and found to exist only in the back room area. Decontamination of the area was done. The room was back into use for all techs to use by the summer of 2008. "3. [The RSO] was made aware of the question of personnel contamination the spring of 2009. A device to assess such contamination is not readily available. A scanner to assess any such contamination does exist at the Bethesda Naval Medical Center. [The RSO] has recently made contact with the Commander in charge of the unit and have obtained information necessary to have access to the device. The basic detail for access is a cost of $1200 to have a scan performed. "4. There are policies and procedures in place to deal with contamination. "5. The question of contamination has only been raised recently and through the union as a grievance. An assessment of any contamination requires the availability of the device to obtain the information. Access to a scanner has been found and steps are to be taken to schedule the scan. The initial step will be the approval and allocation of funds to pay for the scan. Then arrangements can be made to have access to the Bethesda Naval Medical Center in order to do the scan." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2015-05-15
51048 | 0 | MALLINCKRODT |  |  |  |  | 2015-04-21 | 2015-05-07 09:46 | 2015-05-07 | INDIUM-111 SOURCE LOST IN TRANSIT A consolidated package was shipped to New York on April 7. When the shipment arrived it was missing one of the packages within the consolidated shipping container. At the time of shipment, the package contained 12.7 mCi of In-111 (half-life 2.8 days). The package was a UN 2915 Type A with a 0.1 TI (transportation index) and a weight of 3 lbs. An investigation was conducted with the common carrier. The package was not located. It was declared lost on April 21. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-05-15
51047 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2015-05-07 05:09 | 2015-05-07 09:45 | 2015-05-07 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO REACTOR COOLANT PUMP TRIP "This notification is being made as required by 10 CFR 50.72(b)(2)(i) due to a Farley Nuclear Plant Unit 1 shutdown required by Technical Specifications. "At 0509 CDT on 5/7/2015, 1B Reactor Coolant Pump (RCP) tripped during transfer of 1B 4160V bus to 1B unit auxiliary transformer. Technical Specification LCO 3.4.4 Condition A was entered for loss of a Reactor Coolant System (RCS) loop. Unit 1 reactor was shut down per operating procedures and entered Mode 3 at 0740 CDT. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2015-05-07
51046 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-05-07 07:00 | 2015-05-07 07:11 | 2015-05-07 | OFFSITE NOTIFICATION DUE TO SHUTDOWN FOR AN UNISOLABLE STEAM LEAK "At 0700 on 5/7/15, Indian Point Unit 3 commenced a shutdown due to the inability to isolate a steam leak on a feedwater instrument line. "Offsite power is available. "Indian Point Unit 2 is unaffected and remains in Mode 1 at 100% power. "The NRC Resident Inspector, the NYISO (New York Independent System Operator), and NY Public State Commission have been notified." | 0 | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-05-07
51045 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2015-05-05 | 2015-05-06 12:01 | 2015-05-11 | AGREEMENT STATE REPORT - DAMAGED AND MISSING RADIOACTIVE MATERIAL DURING SHIPMENT The following was received from the State of Arkansas via email: "The Arkansas Radioactive Materials [RAM] licensee shipped a Yellow-II Radioactive Materials Package containing two 5 mCi/capsule/plastic vial of Iodine-131 via [common carrier] (overnight package) on Monday, April 27, 2015. The recipient rejected the RAM package prior to the receipt of the RAM package. The RAM package was re-routed back through the [common carrier] Memphis Distribution Center to the licensee, via [common carrier] Ground, and was received by the [common carrier] Little Rock warehouse on Tuesday, May 5, 2015. The Department was notified of the RAM package being damaged at the [common carrier] Little Rock warehouse. "The Department [Arkansas Department of Health] responded to perform surveys and wipe tests at the [common carrier] Little Rock warehouse. The Yellow-II RAM package appeared to have one seam smashed open, the styrofoam crushed, and the lead shipping container's interior side of cap damaged. One I-131 capsule/vial appears to be inside the lead shipping container smashed; one I-131 capsule/vial appears to be missing. "The Department performed exposure measurements and/or contamination wipes of the [common carrier] Little Rock warehouse, RAM package and RAM package contents. No contamination or exposures of concern were noted of the [common carrier] Little Rock warehouse or RAM package. The licensee identified I-131 contamination inside the lead shipping container. "Vehicle surveys were not performed by the Department, due to the vehicle was at the [common carrier] Memphis Distribution Center. The State of Tennessee was notified of this event on Tuesday, May 5, 2015. "It is unknown at this time if there has been any exposure(s) to the public. "The State [of Arkansas] is awaiting a written report from the licensee and will continue to investigate this event with [the common carrier]. "The State will update this event as more information becomes available. "Arkansas Event Number: ARK-2015-003" * * * UPDATE FROM ANGIE D. HILL TO RICHARD L. SMITH AT 1459 EDT ON 5/11/2015 * * * The following was received from the State of Arkansas via email: "The activity of prescription number 46596 (missing I-131 capsule) is 5.418 mCi/1 capsule I-131 Sodium Iodide at 11:30 am on April 29, 2015 and for prescription number 46597 is 5.005 mCi/1 capsule I-131 Sodium Iodide at 10:00 am on April 29, 2015. "The Arkansas Department of Health (ADH) conducted interviews and performed radiation surveys at the Common Carrier's Express Warehouse in Jonesboro, Arkansas, on May 7, 2015, where the RAM package had been received by and shipped to the Common Carrier's Distribution Center. It appeared that the missing I-131 capsule/vial was not at this location. "ADH received a telephone call from the Common Carrier's Radiation Safety Consultant on May 8, 2015. The missing I-131 capsule/vial had been found 'intact' that morning at the Common Carrier's Memphis Distribution Center, whom took possession of the material. "The State of Tennessee has been notified by ADH. "Licensee's Corrective Action: Change in Procedure. "ADH considers this event closed." Notified R1DO (Welling), R4DO (Vasquez), NMSS via email, ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-05-14
51044 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2015-05-04 23:00 | 2015-05-05 13:55 | 2015-05-05 | AGREEMENT STATE REPORT - SUSPICIOUS ACTIVITY INVOLVING A RADIOGRAPHY TRUCK The information for this report was received via E-mail: Suspicious activity related to possible theft of category 2 quantities of radioactive material. The licensee informed the LLEA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 1 | 2015-05-13
51043 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2015-05-05 04:22 | 2015-05-05 13:05 | 2015-05-05 | AUXILIARY FEEDWATER PUMP AUTO START SIGNAL INITIATED DURING STARTUP "At 0422 CDT on 5/5/2015, with Farley Nuclear Plant Unit 1 in Mode 2, and the 1A Steam Generator Feedwater Pump (SGFP) in the tripped condition, the 1B SGFP was manually tripped during troubleshooting. The trip of the second SGFP initiated the auto start signal for the MDAFWPs [motor driven aux feedwater pumps] due to the auto start signal not being defeated. Both MDAFW pumps were in service supplying AFW to the steam generators (SG) when the actuation signal was received. The effects of the auto start signal were to fully open the AFW Flow Control Valves and isolate SG blowdown and SG blowdown sample valves. These actions occurred successfully and the auto start signal was reset. There was no adverse impact to the plant and decay heat continued to be removed through the condenser throughout the event. "The NRC Resident Inspector has been notified." | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-05-05
51042 | 0 | DEPARTMENT OF VETERAN AFFAIRS |  |  |  |  | 2015-05-05 06:15 | 2015-05-05 10:44 | 2015-05-05 | SURFACE CONTAMINATION ON OUTSIDE OF PACKAGE EXCEEDING REPORTING LIMITS "Per 10 CFR 20.1906(d)(1), [the Veterans Health Administration (VHA) is] reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. "The package was received today (May 5, 2015) and surveyed for contamination around 0615 CDT by Captain James A. Lovell Federal Health Care Center, North Chicago, Illinois. The health care center holds permit number 12-10057-04 issued by VHA per the MML [Master Materials License]. "Wipe tests performed on the external surface of the package indicated a removable contamination level of 690 dpm/cm2 as compared to the regulatory reporting limit of 240 dpm/cm2 for beta-gamma emitters. "The package contained five unit dosages of Technetium-99m (about 144 millicuries total) and was shipped and delivered by Triad Isotopes in Elk Grove, Illinois. The nuclear medicine technologist who surveyed the package immediately notified, by telephone, the Pharmacy Manager at Triad Isotopes about the contaminated package. "The exterior of the package was able to be decontaminated by the nuclear medicine technologist to levels below reporting limits by performing successive wipes on the surface. The inner packaging materials and dosage containers were surveyed and no contamination was identified such that the dosages were not impacted. There was no spread of contamination at the health care center from the package. The contaminated materials have been isolated in a restricted area at the health care center and will be held for decay. "Veterans Health Administration (T. Huston) has also notified NRC Region III (K. Null) by telephone of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2015-05-13
51041 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2015-05-04 03:20 | 2015-05-05 00:48 | 2015-05-05 | SEISMIC MONITORING SYSTEM OUT OF SERVICE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for a loss of emergency assessment capability at the Palo Verde Nuclear Generating Station (PVNGS). On May 4, 2015 at 0320, seismic monitoring (SM) system force balance accelerometer R0006 was determined to be non-functional due to an emergent equipment failure. On May 4,2015, at approximately 1600, further review of this equipment failure and the related impact to the capability of the SM system determined that this was a reportable loss of emergency assessment capability. "This specific accelerometer functions to provide indication that the Operational Basis Earthquake threshold has been exceeded following a seismic event and is used in the PVNGS Emergency Plan to perform classification for emergency action level HA1.1, Natural or Destructive Phenomena affecting Vital Areas. As a compensatory measure, PVNGS procedures for seismic event evaluation provide alternative methods for HA1.1 event classification with accelerometer R0006 out of service. Maintenance to correct the condition is in-progress. "The NRC Resident Inspector has been informed of this condition." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-05
51040 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-05-04 14:39 | 2015-05-04 21:44 | 2015-05-04 | LOW DIFFERENTIAL PRESSURE RESULTING IN LOSS OF SECONDARY CONTAINMENT "On May 4, 2015 at 1439 [EDT], during maintenance activities on Unit 2 Zone 3 fan discharge exhaust dampers, the control room received a low DP [Differential Pressure] alarm and other confirmatory indications of a loss of building DP. "Secondary Containment DP was restored after approximately 2 minutes. The fan exhaust dampers are outside the isolation dampers, therefore, there was no impact on the SGTS [Standby Gas Treatment System] ability to drawdown secondary containment. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3. section 3.2.7, as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." The licensee has notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-05-04
51039 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2015-05-01 | 2015-05-04 17:52 | 2015-05-18 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED Y-90 DOSE The following was received from the State of Wisconsin via email: "On May 4, 2015, the Wisconsin Radiation Protection Section received a notice from an Authorized Medical Physicist [AMP] at Gundersen Lutheran Medical Center, Inc., of a medical event that occurred during a Yttrium-90 Therasphere procedure on May 1, 2015. The licensee did not have enough information to determine if the procedure constituted a medical event on May 1, 2015. Upon further evaluation, the AMP determined it was a medical event as of 3 pm CST May 4, 2015. The patient was scheduled to receive two separate Y-90 Therasphere doses to two separate segments of the liver. During the first injection, the overpressure valve opened and filled the overflow vial with the Authorized User applying very little pressure to the saline filled syringe. The patient was to get 147 Gy to Segment 6 of the liver. From residue measurements, the patient received 35.5 percent or 52.2 Gy to Segment 6. The Radiation Protection Section will perform an investigation and update through NMED [Nuclear Material Events Database]. "Event Report ID No.: WI150006" * * * UPDATE AT 0938 EDT ON 5/18/2015 FROM CAL WALTON TO MARK ABRAMOVITZ * * * The correct Wisconsin event ID is WI150007. Notified the R3DO (Peterson) and NMSS (via e-mail). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2015-05-12
51037 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-30 | 2015-05-04 11:46 | 2015-05-20 | AGREEMENT STATE REPORT - RUPTURED IODINE SEED DURING REMOVAL The following was received from the State of Texas via email: "On May 4, 2015, licensee's Radiation Safety Officer (RSO) reported to the Agency [Texas Department of State Health Services] that he had been notified today that on Thursday, April 30, 2015, a physician had ruptured an I-125 seed during removal from a patient. The seed was used for localization in a breast treatment procedure. The seed activity was 357 microCuries at the time of treatment on 4/30/15. The seed was identified as leaking after removal and in a container in the pathology department. The physician had screened the patient with a probe in the tissue/lesion and no radioactivity was found. No overexposure to the patient or doctor had occurred. The RSO stated he was preparing a full detailed report. Further information will be provided in accordance with SA300 guidelines." Texas Incident # I-9310 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION AT 1347 EDT ON 05/20/15 FROM KAREN BLANCHARD TO S. SANDIN VIA EMAIL * * * This report is retracted based on the following: "More complete information was obtained from the licensee. The seed covering was damaged by the physician during excision of tissue from patient. The patient was thoroughly checked following the excision (standard procedure) and there was no radiation detected. There was radioactivity detected in the excised tissue by pathology after seed was removed from the tissue. The licensee identified and remediated all contamination and managed processing of tissue to prevent further contamination. No aspect of the event met any reporting criteria. It has been determined this was not a reportable event." Notified R4DO (Taylor) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-05-12
51036 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-05-03 10:22 | 2015-05-03 12:56 | 2015-05-03 | FEEDWATER ISOLATION, TURBINE TRIP AND MANUAL REACTOR TRIP DURING POWER ASCENSION "On 5/3/2015 during power ascension following Refueling Outage 20, Steam Generator 'C' water level increased rapidly, causing a Feedwater isolation on high Steam Generator water level and an associated Turbine trip. The reactor was subsequently manually tripped. "At the start of the event, reactor power was approximately 22%. Plant staff was in the process of transferring from Main Feedwater Bypass Feed Regulating Valve control, used for low power control, to Main Feedwater Regulating Valve control as part of power ascension. When the Main Feedwater Regulating Valve for 'C' Steam Generator (AEFCV-530) was opened, it went to about 80% open, causing an overfeed of the 'C' Steam Generator. High Steam Generator water level in 'C' Steam Generator initiated an automatic Feedwater Isolation Signal, automatic Turbine Trip and automatic trip of the operating main feed pump. The operating crew initiated a manual reactor trip. "The Auxiliary Feedwater System automatically initiated as part of the plant response to the feedwater system transient. "The plant is presently stable in Mode 3. All equipment functioned normally, except the 'C' Main Feedwater Regulating Valve (AEFCV0530) which did not function to properly control Steam Generator level. This valve did function as designed to close on the Feedwater Isolation Signal. "NRC Resident Inspector has been contacted." | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-05-03
51035 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-05-02 21:30 | 2015-05-03 00:05 | 2015-05-03 | NORMAL AND HI RANGE VENTILATION PROCESS RADIATION MONITORS OUT OF SERVICE "Loss of assessment capability due to unplanned removal from service of a radiation monitor due to process flow monitor indication failing hi. The normal and hi range ventilation vent process radiation monitors (3HVR*RE10A/B are out of service. This condition was discovered during control room rounds. The condition is reportable per 10CFR50.72(b)(3)(xiii)." Compensatory measures are in place. The licensee notified the NRC Resident Inspector and applicable State and Local authorities. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-03
51034 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-05-02 12:47 | 2015-05-02 20:57 | 2015-05-02 | LOSS OF SHUTDOWN COOLING DUE TO LOSS OF 4KV BUS "On 5/2/2015 at 1247 CDT, while the plant was in MODE 5 for a refueling outage with the vessel cavity flooded, during logic testing of the non-credited essential 4kV bus, MNGP [Monticello Nuclear Generating Plant] experienced a human performance error that caused a loss of the 4kV bus and essential load center. Loss of the load center de-energized valve position indication on one shutdown cooling isolation valve. This tripped the shutdown cooling pump on a pump suction interlock, resulting in the loss of shutdown cooling. This is being reported under 10 CFR 50.72(b)(3)(v)(B) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. "Following the event, the safety related load centers were cross-tied to allow restoration of shutdown cooling. Shutdown cooling was restored at 1603. While shutdown cooling was out of service, vessel water temperature rose approximately 10øF to 91.1øF, which is within the allowed temperature band. "This event did not result in the release of any radioactive material and did not challenge the health and safety of the public. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2015-05-02
51033 | 0 | PALISADES | 1 |  |  | [1] CE | 2015-05-02 12:23 | 2015-05-02 12:58 | 2015-05-02 | UNUSUAL EVENT DECLARED DUE TO SEISMIC ACTIVITY FELT ON SITE At 1241 EDT, Operations staff at Palisades declared an Unusual Event under EAL HU1.1 due to seismic activity felt on site. No seismic alarms were initiated. No plant equipment was affected. The epicenter of the 4.2 magnitude earthquake was located south of Galesburg, MI. Palisades continues to operate at 100% power. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM JC RANEY TO DANIEL MILLS AT 1601 EDT ON 5/2/15 * * * The licensee terminated the Unusual Event at 1541 EDT on 5/2/15. The licensee has notified the NRC Resident Inspector and the state and local government. Notified R3DO (Orlikowski), IRD MOC (Stapleton), NRR EO (Morris), NRR ET (Dean), and R3RA (Pederson). Notified other Federal Agencies (DHS SWO, FEMA Ops, FEMA NWC, NICC Watch Officer and NuclearSSA). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-05-02
51032 | 0 | NORTH CAROLINA DEPT OF HHS |  |  |  |  | 2014-03-30 | 2015-05-01 19:10 | 2015-05-01 | AGREEMENT STATE REPORT - IODINE 125 SEED LEFT IN PATIENT The following was received from the State of North Carolina via email: "During a recent facility inspection at Duke University Medical Center (License# 0247-4), it was discovered that a lost I-125 seed (National NMED Item #140177) was actually found a couple months later still in the patient's breast tissue. The seed was intended for radioactive seed localization (RSL) of a breast lesion and thought to be excised with the targeted tissue during surgery. "Events as follows: -Seed was implanted to patient with 213 uCi on 1/23/2014. -Discovered missing by licensee on 2/27/2014. -Reported lost to NC on 3/21/2014. -Found in patient 3/30/2014, no update given to NC. -Removed from patient breast on 4/1/2014. "As of 5/1/2015, the licensee maintains that there was only 12.5 rads received to the 250g of breast tissue and not above the 50 rem for medical event reporting. This is currently under investigation by the NC Radioactive Materials Branch as our preliminary numbers suggest the breast tissue dose could be as high as 66 rem in the maximally exposed 100g of tissue. "The licensee is not concerned with overall adverse reaction to the patient health due to them receiving a subsequent external beam radiation treatment that deposited between 300-1100 rads to the affected breast. "This possible medical event is tied to the former local NMED Incident# NC 140014 where the source was lost, and it is now being tracked by a new local NMED Incident# NC 150010." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2015-05-11
51031 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-05-01 10:00 | 2015-05-01 17:56 | 2015-05-01 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED MOISTURE DENSITY GAUGE The following was received from the State of Texas via email: "On May 1, 2015 the licensee's corporate office notified the Agency [Texas Department of State Health Services] that one of its vehicles had been stolen at 10 am today with a moisture density gauge secured on the back of the truck. The gauge was a Troxler 4640 with an 8 millicurie Cesium-137 and 40 millicurie Americium/Beryllium source in the gauge. The truck was stolen at a gas station and local police were immediately called by the driver/technician. The police recovered the vehicle with the gauge still secured in the back of the truck. Details of the event will be provided as the local radiation safety officer and technician are still on-site with the police. Additional information will be provided in accordance with SAE 300." Texas Incident # I-9309 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-05-11
51030 | 0 | AZZ/NLI NUCLEAR LOGISTICS, INC |  |  |  |  | 2015-04-30 | 2015-05-01 13:32 | 2016-08-26 | POTENTIALLY UNQUALIFIED COMPONENT IN CERTAIN ALLEN BRADLEY TIMING RELAYS The following is an excerpt from a document received from the licensee via email: "Report of potential 10 CFR Part 21, Allen Bradley Timing Relay Model 700RTC "Pursuant to 10 CFR 21.21(d)(3)(ii), AZZ/NLI is providing written notification of the identification of a potential failure to comply. "On the basis of our evaluation, it is determined that AZZ/NLI does not have sufficient information to determine if the subject condition would, or has, created a Substantial Safety Hazard or would have created a Technical Specification Safety Limit violation as it relates to the subject plant applications. "The specific part which fails to comply or contains a defect: "As of 2009-2010, Allen Bradley relays base model 700RTC, contain an unevaluated CPLD (Complex Programmable Logic Device). This was an unpublished design change that was implemented to replace an obsolete integrated circuit chip. The undocumented design change did not result in a part number change from Allen-Bradley. There was no change to the appearance of the relay that would identify any design changes were made to the relay configuration. Therefore, NLI qualification/dedication of the relays after 2009 have not included additional testing for the new CPLD component. "The timing relay model 700RTC has been dedicated/qualified for multiple applications for various plants. "Between 2009-2010 Allen Bradley made a design change without changing the part number of the commercial relay or providing any documented evidence of a design change. The manufacturer specification data sheets maintain the classification that the relays are 'solid state', which would imply that there are no digital devices installed in the relay. However, after inspection of the internals of the timing relay (Figure 2), it has been identified that the unit does contain a CPLD which meets the definition of a digital device under the guidance of NEI 01-01." Potentially affected plants include Browns Ferry, Ginna, Millstone, Nine Mile Point, North Anna, Ft. Calhoun, Perry, River Bend, South Texas Project, and St. Lucie. * * * UPDATE FROM TRACY BOLT TO JOHN SHOEMAKER AT 1744 EDT ON 4/8/16 * * * AZZ/NLI Nuclear Logistics provided additional information regarding Part 21 Report No: P21-04302015, Rev. 1. Notified R1DO (Rogge), R2DO (Nease), R3DO(Skokowski), R4DO (Kellar), and PART 21/50.55 REACTORS via email. * * * UPDATE FROM LES TAGGART TO BETHANY CECERE AT 0951 EDT ON 5/26/16 * * * AZZ/NLI Nuclear Logistics provided Revision 2 to Part 21 Report No: P21-04302015 to correct the referenced EPRI TR-102323 Rev. 3 to Rev. 4 and change 'timing' contacts to 'instantaneous' contacts as shown below: "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "The relays that are currently in stock at NLI have been placed on hold until after the units have been determined to be qualified for the specific application. NU has completed the EMC qualification testing per the requirements of EPRI TR-102323 Rev. 4 for the following tests, as applicable: CE101, CE102, RE101, RE102, RS101, RS103, CS101, CS114, CS115 and CS116. "The results were satisfactory with exception of the following condition: During Conducted Susceptibility CS114 onto the power lines, with the timing circuit in operation, the instantaneous contacts exhibited chatter in the range of 2.6 MHz to 20.3 MHz. The unit requires a ferrite to be installed onto the input power lines of the relay with 3 turns through the ferrite core. In this modified configuration, the relay was not susceptible to Conducted Susceptibility and successfully passed the required test per CS114." Notified R1DO (Lilliendahl), R2DO (Guthrie), R3DO(Kunowski), R4DO (Werner), and PART 21/50.55 REACTORS via email. * * * UPDATE FROM TRACY BOLT TO DONG PARK AT 1807 EDT ON 8/15/16 * * * AZZ/NLI Nuclear Logistics provided additional information regarding Part 21 Report No: P21-04302015, Rev. 3, correcting the date the change occurred to October 2008. Notified R1DO (Jackson), R2DO (Shaeffer), R3DO (Riemer), R4DO (Proulx), and PART 21/50.55 REACTORS via email. * * * UPDATE FROM TRACY BOLT TO DONG PARK AT 1833 EDT ON 8/26/16 * * * AZZ/NLI Nuclear Logistics is making a word correction in Part 21 Report No: P21-04302015, Rev. 4. Notified R1DO (Dimitriadis), R2DO (Michel), R3DO (Cameron), R4DO (Kellar), and PART 21/50.55 REACTORS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-05-01
51029 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2015-05-01 16:00 | 2015-05-01 16:14 | 2015-05-01 | LOSS OF SEISMIC MONITORING DUE TO PLANNED MAINTENANCE "This notification is conservatively being made in accordance with 10 CFR 50.72(b)(3)(xiii) as an event that will result in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g. significant portion of control room indication, Emergency Notification System or offsite notification system.) "The emergency preparedness plan requires seismic monitoring instruments to diagnose an earthquake for emergency action levels (EAL) HU6 (Natural or destructive phenomena affecting PROTECTED AREA) and HA6 (Natural and destructive phenomena affecting VITAL AREAS). "At approximately 1600 [CDT] on May 1, 2015, ANO plans to remove Motor Control Center B33 from service for maintenance. This will render the alarm functions for the seismic monitors nonfunctional. It is expected that this maintenance will take approximately 72 hours to complete. ANO procedures provide compensatory measures of using offsite sources to obtain seismic data." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-05-01
51028 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-04-30 23:44 | 2015-05-01 08:36 | 2015-06-29 | HIGH PRESSURE CORE SPRAY SYSTEM INOPERABLE "River Bend Station personnel declared the High Pressure Core Spray (HPCS) system inoperable at 2344 CDT on 4/30/2015. "The HPCS system at River Bend Station includes a test return line to the Condensate Storage Tank (CST). The test return line is isolated by two motor operated valves (E22-MOVF010 and E22-MOVF011), with both having a safety function to close on an ECCS initiation signal to ensure that injection flow is directed to the reactor vessel. There is currently a blind flange installed downstream of these two valves. While the HPCS pump is normally aligned to the CST, the credited source of water for the pump is the suppression pool. Accordingly, the pump suction is realigned to the suppression pool on low level in the CST or when suppression pool level rises to a certain point. While performing maintenance on the downstream test return valve (E22-MOVF011), station personnel identified leakage past the upstream test return valve (E22-MOVF010) which was being used as an isolation boundary. In evaluating this condition, engineering personnel noted that the observed leakage past the upstream isolation MOV might be sufficient to deplete suppression pool inventory such that it would not be capable of performing its specified function for the duration of the 30-day mission time. The issue of concern is that once HPCS is aligned to the suppression pool post-LOCA, pool inventory would be lost due to the leaking upstream isolation valve (E22-MOVF010) and out the disassembled downstream isolation valve (E22-MOVF011). "Based on that concern, the HPCS pump suction valve from the suppression pool was disabled in the closed position to preserve pool inventory. This action caused the HPCS system to be declared inoperable at 2344 CDT. This action results in a 14 day shutdown LCO and is reportable to the NRC in accordance with 10CFR50.72(b)(3)(v)D. "The HPCS pump remained available with its suction aligned to the CST. "Message has been left with NRC Senior Resident Inspector." * * * RETRACTION AT 1009 EDT ON 6/29/2015 FROM MICHAEL BRANSCUM TO MARK ABRAMOVITZ * * * "The licensee is retracting the report for Event No. 51028. "On April 28, the High Pressure Core Spray System (HPCS) was inoperable to support planned maintenance. During repairs on the HPCS pump test return valves, leakage through the upstream isolation valve was observed when the downstream valve was disassembled. At 2315 [CDT] on April 30, it was conservatively determined that the leakage represented a potential challenge to the 30-day inventory of the suppression pool, and the pool was declared inoperable. At 2344 [CDT] on April 30, the HPCS pump suction valve to the suppression pool was closed to isolate that potential leakage path until the maintenance could be completed. This action returned the suppression pool to an operable status. "On June 24, a quantitative leak rate test was performed on the upstream isolation valve (E22-MOVF010). That test determined that the leakage through the valve was not of such magnitude to have had the potential to deplete the 30-day inventory of the suppression pool during post-accident operation of the HPCS system. Additionally, when the HPCS pump suction valve on the suppression pool was closed on April 30, the system was already in a planned outage that commenced on April 28. As such, this condition need not have been reported." The licensee notified the NRC Resident Inspector. Notified the R4DO (Campbell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-05-01
51027 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2015-04-29 18:11 | 2015-04-30 21:24 | 2015-04-30 | ROD POSITION INDICATOR SYSTEM (RPIS) UNPLANNED OUTAGE "At 1811 PDT on 04/29/2015, the station declared the RPIS system inoperable when a Control Room panel alarmed the loss of indication. The cause of the equipment loss is under investigation. This unplanned equipment outage is being conservatively reported as a major loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "No other safety equipment has been impacted by this event and the plant continues normal operation." The NRC Resident Inspector has been notified. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-30
51026 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2015-04-30 18:40 | 2015-04-30 19:38 | 2015-04-30 | UNUSUAL EVENT DECLARED DUE TO ELECTRICAL FAULT "Unusual Event (4.6.U.1) was declared by the Shift Manager at Oconee Nuclear Station at 1840 EDT on 4/30/15 due to scorched 4160V cable and a hole created in metal connector coming into the top of 1C condensate booster pump motor electrical junction box. Unit 1 experienced a decrease in power to approximately 98.6% power due to the perturbation in condensate flow from the loss of 1C condensate booster pump. Unit 1 is currently stable at 98.6%. 1A condensate booster pump auto-started as expected. Smoke was observed and quickly dissipated. No visible fire or flame was observed. No Fire Brigade response required." The Unusual Event was terminated at 1945 EDT on 4/30/15. The licensee informed state/local agencies and the NRC Resident Inspector and does not plan to issue a press release. Notified other Federal Agencies (DHS SWO, FEMA Ops, FEMA NWC, NICC Watch Officer and NuclearSSA). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-04-30
51025 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2015-04-29 | 2015-04-30 11:32 | 2015-04-30 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following was received from the State of Minnesota via email: "Please note the medical event reported today to the Minnesota Department of Health Radioactive Materials Unit by Mayo Clinic in Rochester, MN. "The licensee reports that on April 29, 2015, a male patient was treated with Y-90 TheraSpheres. The written directive prescribed 62.1 mCi of Y-90 (120 Gy dose). The administration proceeded as expected with the assistance of interventional radiology and nuclear medicine. As part of the procedure, the licensee uses a survey meter to survey the Y-90 microsphere vial to determine that microspheres have been administered to the patient. The procedure was described as 'uneventful' and following the initial flushing the dose rate from the vial/tubing had not decreased to zero. The physician continued with three additional flushes as part of the normal procedure. The vial/tubing dose rate did not reduce to zero. "The waste material was collected and counted according the manufacturer's instructions. The licensee determined approximately 33% of the Y-90 activity was not delivered to the patient. Administered activity was estimated to be 41.85 mCi (84 Gy). Physicians anticipate no negative impact to the patient since the 'tumoricidal' dose, according to the manufacturer, is 80-150 Gy, "The patient has been notified. The referring physician was out of town on the day of the event and the licensee notified his fellow. "The licensee is continuing with an investigation. "The Minnesota Department of Health considers this investigation open and will provide more information will be as it becomes available." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2015-05-08
51024 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2015-04-29 10:00 | 2015-04-30 09:30 | 2015-04-30 | VALVE CLASSIFIED AS ITEM RELIED ON FOR SAFETY FAILED TO OPERATE AS DESIGNED "On April 29, 2015 at 1000 [EDT], it was reported to EH&S [Environmental Health and Safety] that the spring loaded valve on the deionized (DI) water line, which supplies rinse water to an in-line gamma monitor in the conversion scrap recovery area, was found to have the spring-return damaged such that the valve would not automatically return to the closed position when released. This valve is listed as IROFS ADUSCRA-102. While production activities had already ceased in preparation for a Special Nuclear Material (SNM) inventory and planned maintenance outage, liquid wastewater processing activities were on-going. "Liquid wastewater processing activities were immediately stopped, and EH&S was notified of the event by phone and the 'Redbook' reporting system (Redbook Issue #68460). At no time was there any actual or potential health and safety consequences to the workers, the public, or the environment. "The safety function of this IROFS is to automatically close when released by hand to prevent possible backflow of Uranium-235 containing wastewater into the DI water supply and potentially to an unfavorable geometry tank. During this time, IROFS ADUSCRP-153, a three-way valve that prevents the commingling of wastewater and DI water, remained available and reliable to prevent potential backflow of the wastewater into the DI water supply. Based on available IROFS, this accident sequence was 'Unlikely' (a failure probability of 10E-3), and not 'Highly Unlikely' (a failure probability of 10E-4 or less), and therefore does not meet the performance requirements of 10 CFR 70.61 [which requires that an accident sequence be 'Highly Unlikely']. The actual configuration remained safe at all times, and no external conditions affected the event. A process upset would have to occur to enable a potential backflow condition, and the remaining IROFS would have had to simultaneously fail. "Immediate Corrective Actions: As stated above, the process was shut down, and the upstream DI water valve was locked closed. After evaluation and with EH&S approval, maintenance replaced the valve and a functional test was completed. The event was reviewed in the conversion huddle meetings held before the start of each shift, and operations initiated a check to validate the operability of the spring loaded valve after each use until a long term corrective action is in place. Operating Experience is being shared with the site and industry personnel. "An Extent of Condition inspection was performed for all safety-significant spring loaded valves. All other valves functioned properly. "This event has been entered into the facility Corrective Action Prevention And Learning system (CAPAL) #100267824." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2015-05-08
51023 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-04-01 | 2015-04-29 12:09 | 2015-04-29 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE STUCK OUTSIDE THE CAMERA The following report was received via e-mail: "[The Oklahoma Department of Environmental Quality was] notified by SGS North America, Inc. Industrial Division (OK-32124-01) that one of their crews experienced an equipment failure on April 1, 2015 while working at a temporary job site in Oklahoma. The failure, a drive cable break, made it impossible for the crew to retract the source. The RSO [Radiation Safety Officer] was called to the site and was able to cut the drive cable sheath and successfully retract the source. SGS is licensed for source recoveries. Investigation is ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-05-07
51022 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-28 07:29 | 2015-04-28 17:29 | 2015-04-28 | FITNESS FOR DUTY REPORT INVOLVING A SUPERVISORY CONTRACT EMPLOYEE A contract supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2015-04-28
51021 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-04-28 09:35 | 2015-04-28 14:50 | 2015-04-28 | TWO SECONDARY CONTAINMENT INTERLOCK DOORS OPEN SIMULTANEOUSLY "On April 28, 2015, at 0935 CDT, the Shift Manager was notified that two Secondary Containment interlock doors (1/2 EDG room door and the Unit 1 reactor building door) were open simultaneously. The doors were immediately closed and secondary containment pressure remained negative. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2 given two doors in a single access opening were open simultaneously. As a result entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to secondary containment being inoperable. "This event is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified. Personnel were posted in the area as a compensatory measure. The State of Illinois Emergency Management has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-04-28
51020 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-04-06 16:15 | 2015-04-28 11:16 | 2015-04-28 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA LOST AND RETRIEVED The following report was received via e-mail: "A radiography exposure device was found by a citizen in some weeds on the side of a road. The citizen called the New Iberia Fire Department who contacted the Iberia Parish Sheriff's Department. The Fire Department then contacted QIT [Quality Inspection & Testing, LLC] by the information posted on the side of the radiography exposure device, (I R Camera). The camera was discovered in some weeds in a parking lot located at 1000 Parkview Dr., New Iberia, LA. A company official for QIT was contacted by the Fire Department who relayed the information to the Business Manager for QIT and the Assistant RSO. Background: "The on April 6, 2015, two 'trained and trustworthy individuals' were preparing a 'crew' truck to perform radiography work at a temporary jobsite. [The first Radiographer] was preparing the documentation while [the Assistant Radiographer] was equipping and securing the truck with a Category II radiography source. [The Assistant Radiographer] got distracted and placed the exposure device on the vehicle's rear bumper. Before leaving QIT's office, [The first Radiographer] questioned [the Assistant radiographer] about securing the exposure device for transport. "The crew left QIT in route to the temporary job. They passed up the jobsite and did a U-turn where the exposure device was later discovered. They arrived at the temporary jobsite and began to setup for the job. They became aware that they did not have the exposure device that [the Assistant Radiographer] stated he had placed in the truck's 'vault.' The crew decided to back-track their route in an attempt to locate the missing exposure device. They did not locate the device because [the QIT RSO] had already retrieved the device from the lot at 1000 Parkview Dr. and returned it to QIT's office. "The RSO and the assistant RSO began their investigation into this incident. It began with interviewing and getting statements from both individuals directly involved in this incident. "The next morning April 7, 2015, approximately 11:00 AM, [the QIT RSO] called in a preliminary notification to LDEQ's [Louisiana Department of Environmental Quality], Assessment, Radiation Licensing Section. The incident was assigned to an investigator/inspector in our Acadiana Regional office. "At this time, LDEQ considers this incident still open. The incident is still under investigation and review by the staff. Enforcement and corrective actions will be determined by the out-come of the investigation. The incident was considered under control by QIT and reported after the exposure device was back at the QIT office. "The equipment was a S.P.E.C., Model 150 exposure device, S/N 1114 device loaded with approximately 79 Ci of Ir-192. The device was surveyed, secured, placed in the QIT vault and labelled 'NON-USE'." Louisiana ID Number: LA150008 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-05-06
51019 | 0 | FEDERAL AGROMAN |  |  |  |  | 2015-04-28 10:45 | 2015-04-28 11:00 | 2015-05-14 | STOLEN MOISTURE DENSITY GAUGE IN CARJACKED VEHICLE A Federal Agroman truck was transporting a moisture/density gauge. The driver stopped at the side of the road and the truck was carjacked. The licensee contacted the Puerto Rico State Police. Gauge: Troxler model 3430 with serial number 37246. The sources are 8 mCi Cs-137 and 40 mCi Am-241. * * * UPDATE FROM FERNANDO CORTES TO VINCE KLCO ON 5/14/15 AT 1804 EDT * * * The following excerpted information was received from the licensee by email: "On April 28, 2015 around 09:50am ET (Eastern Time) [the] operator of the Troxler 3430 nuclear gauge arrived to the construction site on highway PR-21 near of the old state penitentiary, known as Oso Blanco, in Rio Piedras, Puerto Rico. At the time [the operator] was driving a 2005 Mazda pickup truck with license plate 785-337 where compaction tests would take place. Suddenly and out of no where an individual entered the premises and drove away with the vehicle, the gauge/accessories and other personal belongings. "At this moment, no trace of the machine (gauge/accessories) that was stolen have been found since April 28, 2015 and there is no information about its likely location to date. "Actions that have been taken, or will be taken, to recover the material: a. Immediately [the licensee] called the 9-1-1 Emergency Management of Puerto Rico b. A complaint was performed with the Puerto Rico Police Department. (Complaint num. Q-2015-1-162-4467, Badge 30858, Rio Piedras, Puerto Rico) c. Ferrovial Agroman LLC began an investigation of the incident. d. There was an interview with an agent of Homeland Security due to the investigation of the incident. e. The situation ('EMERGENCY' Stolen Machine) was notified to all local newspapers in Puerto Rico (Nuevo Dia, Primera Hora and El Vocero.) f. [The licensee notified] Mr. Sattar Lodhi, Region I, from the U.S. Nuclear Regulatory Commission on April 28, 2015. Also [the licensee] had communication with Mr. Hector Bermudez on April 29, 2015. g. On April 29 of 2015, the stolen vehicle was recovered but there were no trace of the machine (nuclear gauge and accessories). h. A picture of a similar machine was published by 'EI Vocero' newspaper. "Procedures or measures that have been, or will be, adopted to ensure against a recurrence of the loss or theft of licensed material: a. The method and procedure for the use and handling machine with radioactive sources was reviewed. b. The procedure in case of any event, damage, loss, or theft of a machine with sources radioactive was also reviewed. c. Owners, operators and authorized personnel are encouraged and oriented on the procedure before the use or the procedure in case of any emergency before the use of this instrument (Troxler 3430) Nuclear Dosimeter." Notified R1DO (Welling), NMSS Events and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-05-06
51018 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2015-04-27 15:27 | 2015-04-27 18:56 | 2015-04-27 | OFFSITE NOTIFICATION TO LOCAL AGENCY Notification was made to the San Diego Regional Water Quality Control Board, and a message was left for exceeding the daily maximum parts per million (ppm) of oil and grease in the North Industrial Area Yard Drain Sump. Sump pumps are currently in "OFF" and the site is investigating. The oil in the drain sump did not reach "reportable quantities" and did not require notifying other Federal Agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-04-27
51017 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-27 08:50 | 2015-04-27 15:46 | 2015-04-27 | SECONDARY CONTAINMENT BOUNDARY DOOR FOUND AJAR "On 4/27/2015 at 0850 [EDT], Secondary Containment (Unit 1 Reactor Building) Boundary Door-721 was found ajar. The door was closed by operators. A status walkdown was performed and no other doors were found in this condition. "Although, Secondary Containment differential pressure was maintained throughout the time period that the door was not fully closed and latched. The door serves as a Secondary Containment boundary and is required to be closed for Secondary Containment Operability. "This event is being reported under 10 CFR 50.72(b)(3)(v) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System." This door is in the railroad bay and was posted as a containment boundary door. Investigation into why this door was not closed and latched is continuing. The licensee notified the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-04-27
51016 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-04-23 11:00 | 2015-04-27 13:11 | 2015-04-27 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER STUCK OPEN The following report was received via fax: "TDEC [Tennessee Department of Environment and Conservation] was notified on 4/24/2015 by [the licensee's] Radiation Safety Officer that during the performance of a 6-month shutter check on a Vega Model SHGL-1 gauge, the shutter was found to be inoperable and couldn't be moved to the closed position. The isotope involved was 30 mCi of Cs-137 (sealed source) contained in a Vega Model SHLG-1 level gauge, S/N OV0604. No radiation exposure occurred as a result of the incident. Current levels at the gauge are the same as dose rates under normal operating conditions." Tennessee Event: TN-15-071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-05-05
51015 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-26 19:08 | 2015-04-26 20:24 | 2015-04-27 | INFORMATION ONLY REPORT - SECURITY PLAN COMPENSATORY ACTIONS TAKEN DUE TO SEVERE WEATHER Safeguards system degradation related to patrols of the Protected Area boundary due to severe weather in the area. Compensatory actions taken. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM BRIAN MITCHELL TO DONALD NORWOOD AT 0043 EDT ON 4/27/2015 * * * At 2341 CDT on 4/24/15, normal security measures were restored. The licensee notified the NRC Resident Inspector. Notified R4DO (Drake) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW | [5 empty] | 1 | 2015-04-28
51014 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-25 22:10 | 2015-04-26 01:37 | 2015-04-26 | OFFSITE MEDICAL TRANSPORT FOR POTENTIALLY CONTAMINATED WORKER "At 2125 [EDT] on 4/25/15 the control room was notified of a medical emergency in the Radiologically Controlled Area [RCA]. "The individual was considered potentially contaminated since a complete frisk could not be performed prior to transport. "An ambulance entered the Susquehanna Owner Controlled Area and the Protected Area at 2154 and exited at 2210 to transport the individual to the hospital. "Radiological survey performed during transport by an SSES [Susquehanna Steam Electric Station] RP [Radiation Protection] Technician verified at 2255 the individual was not contaminated. The ambulance was verified not contaminated at 2303. "This event is reportable under 10CFR50.72(b)(3)(xii). "An Event of Potential Public Interest (EPPI) was made to the Pennsylvania Emergency Management Agency (PEMA) due to an emergency vehicle accessing company property." The licensee informed the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2015-04-26
51013 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2015-04-24 21:25 | 2015-04-25 04:10 | 2015-04-25 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO OUT-OF-SERVICE RADIATION MONITORS "At 2125 on 4/24/15, 1R-2, Containment Vessel Area Radiation Detector failed. Previously, 1R-7, Incore Seal Table Area Radiation Detector, had failed on 4/20/15. The compensatory measure for 1R-2 out-of-service is to verify 1R-7 operating properly and the compensatory measure for 1R-7 out-of-service is to verify 1R-2 operating properly. With both monitors out-of-service and Unit 1 operating in Mode 5, no compensatory measure is available that will allow timely classification of two Emergency Action Levels (EALs) - Notification of Unusual Event (NUE) classification (RU2.2) and Alert classification (RA3.2). This results in a Loss of Emergency Assessment Capability while 1R-2 and 1R-7 are concurrently out-of-service. This is a reportable condition per 10 CFR 50.72(b)(3)(xiii). "Monitoring of radiological conditions in Unit 1 Containment showed no indication of RCS leakage or elevated radiation levels prior to the failure of 1R-2. Unit 1 Containment also remains monitored by 1R-48, Containment Hi Range Area Radiation Detector A and 1R-49, Containment Hi Range Area Radiation Detector B, which currently indicate normal radiation levels. Unit 1 Shield Building Stack is also monitored by 1R-50, Shield Building High Range Vent Gas Radiation Detector, which also currently indicates normal radiation levels. Additionally, a temporary portable radiation monitor has been placed near the location of 1R-2 and is being continuously monitored. "The plant remains in a safe condition and there was no effect to the health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-25
51012 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-24 17:40 | 2015-04-24 18:59 | 2015-04-24 | INFORMATION ONLY REPORT - SECURITY PLAN COMPENSATORY ACTIONS TAKEN DUE TO SEVERE WEATHER Safeguards system degradation related to patrols, monitoring and detection of Protected Area boundary due to severe weather in the area. Compensatory actions taken. The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY BRIAN MITCHELL TO DONG PARK ON 04/24/2015 A 2000 EDT * * * All security systems and patrols have been restored at 1857 CDT. Licensee notified the NRC Resident Inspector. Notified R4DO (Drake) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW | [5 empty] | 1 | 2015-04-28
51011 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-04-04 11:20 | 2015-04-24 16:13 | 2015-04-24 | POWER LOST TO CONTROL ROOM NORMAL OUTSIDE AIR INTAKE DAMPERS DURING TESTING "On April 4, 2015, during testing of the Control Room ventilation system while in Mode 5 at 0% power during shutdown for a refueling outage, the 1CZ-1 and 1CZ-2 Control Room Normal Outside Air Intake dampers lost power due to circuit breaker trips, preventing closure. Harris personnel immediately closed the dampers as required by Harris Nuclear Plant Technical Specifications. During subsequent evaluation, this event was determined to be reportable on April 24, 2015, at approximately 1200 EDT. "This event is being reported under the non-emergency notification requirement of 10 CFR 50.72 (b)(3)(v)(A), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition,' and 50.72(b)(3)(v)(D), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "There was no adverse impact to public health and safety or to plant employees. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-04-24
51010 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2015-04-23 15:32 | 2015-04-24 14:14 | 2015-04-24 | VIOLATION OF THE FITNESS FOR DUTY PROGRAM A contract employee supervisor tested positive for a follow-up fitness-for-duty test. The employees access to the site has been denied. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2015-04-24
51009 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2015-04-22 | 2015-04-24 09:22 | 2015-04-24 | AGREEMENT STATE REPORT - BULK DOSE ADMINISTERED TO PATIENT The following information was received from the Commonwealth of Massachusetts via email: "The licensee's Radiation Safety Officer (RSO) reported on April 23, 2015 that, on the morning of April 22, 2015, the licensee mistakenly administered to a patient the wrong radioactive drug, a 118 mCi Tc-99m bulk dose instead of the prescribed 12.9 mCi Tc-99m Sestamibi dose, at the licensee's Baystate Franklin Medical Center facility. "The wrong radioactive drug administered was reported by the licensee's RSO to have resulted in 5.6 rem effective dose equivalent to the patient, a reportable medical event in accordance with 105 CMR 120.594(A)(1)(b)1. "The licensee's RSO reported that the patient and the referring physician have been notified and that the RSO did not expect any harm to the patient. "The RSO reported the cause included that proper procedures were not followed. "The Agency (Massachusetts Radiation Control Program) plans to perform a special inspection and considers this event to be open." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-05-04
51008 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-04-23 17:17 | 2015-04-24 00:15 | 2015-04-24 | OFFSITE NOTIFICATION DUE TO WORKER FATALITY NOT RELATED TO PLANT OPERATION "This notification is being reported to NRC in accordance with 10 CFR 50.72(b)(2)(xi) for notification of an on-site fatality of a contract employee. In addition, the contracting company plans to notify the Occupational Safety and Health Administration (OSHA) of a fatality per 29 CFR 1904.39. "At approximately 1717 CDT on 4/23/15, a 911 call was received in the Control Room regarding a contract employee who was found unresponsive and unattended in a temporary break room set up on the Turbine Deck during the Unit 1 refueling outage. Resuscitation by first responders and paramedics from a nearby town was unsuccessful. Resuscitation efforts were suspended at 1750. "The Houston County Sheriff's Office was notified at approximately 1800 and they responded to the site at 1822. The county coroner was notified and arrived on site at 1850. "[Farley Nuclear Plant] received notification at approximately 2035 that the contractor company intended to notify OSHA. "A press release is not planned at this time. The NRC Resident Inspector has been notified. "Unit 1 remains in Mode 6 and Unit 2 remains in Mode 1 at 100% power." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-04-24
51007 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-23 20:45 | 2015-04-23 23:13 | 2015-04-24 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following information was provided by the State of Texas via email: "On April 23, 2015, at 2117 [CDT], the Agency [Texas Department of State Health Services] was contacted by the licensee's radiation safety officer (RSO) and informed that one of their InstroTek model 3500 moisture/density gauges containing an 8 millicurie cesium - 137 source and a 40 millicurie americium/beryllium source was lost by a technician at a work site [Midland, Texas]. The technician had placed the gauge on the back of his pickup truck. He walked around the job site with the work area supervisor for a few minutes, then returned to his truck and drove to the new work site. When he arrived at the new site he notice the gauge was missing. The technician notified the RSO and local law enforcement. He then began looking for the gauge. The RSO stated he was responding to the location to help look for the gauge. The RSO stated the operating rod for the cesium source was locked in the shielded position. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9307 * * * UPDATE ON 4/24/15 AT 1508 EDT FROM ART TUCKER TO DONG PARK * * * The following information was provided by the State of Texas via email: "On April 24, 2015, at 0929 CDT the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that the gauge had been recovered. The RSO stated they had been contacted by a contractor who had found the gauge yesterday and taken it to their [location] where they stored it over night. The RSO stated the operating handle for the cesium source was still locked. The gauge did not appear to be damaged. The RSO stated a leak test was performed of the gauge sources and the gauge has been placed in storage until the results of the leak test are received. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Drake), NMSS Events Notifications, ILTAB, and Mexico via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-05-01
51006 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-04-23 10:50 | 2015-04-23 18:51 | 2015-05-08 | SAFETY SYSTEMS DECLARED INOPERABLE DUE TO EQUIPMENT MALFUNCTION "At 1050 [CDT] on 4/23/2015, an equipment malfunction resulted in DAEC [Duane Arnold Energy Center] declaring the Division 1 Essential Electrical Bus inoperable. The LPCI [ Low Pressure Coolant Injection] system was inoperable but available as part of a planned evolution at the time of the malfunction. Declaring the Essential Electrical Bus inoperable caused the 'A' Core Spray System to be considered inoperable. LPCI and 'A' Core Spray being inoperable simultaneously constituted a loss of safety function. The 'B' Core Spray system remained operable and available. The equipment malfunction was resolved promptly, allowing the Division 1 Essential Electrical Bus to be returned to an operable status. "The notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(D). "The [NRC] Resident Inspector has been notified." The licensee entered and exited TS LCO 3.5.1 condition B. * * * RETRACTION FROM BOB MURRELL TO DONALD NORWOOD AT 0835 EDT ON 5/8/2015 * * * "The purpose of this notification is to retract a previous report made on 4/23/15 at 1851 EDT (EN 51006). Notification to the NRC was initially made as a result of an event or condition that could prevent the fulfillment of the safety function of Emergency Core Cooling System (ECCS) due to an equipment malfunction associated with the Division 1 Essential Electrical Bus Breaker 1A306. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the Division 1 Essential Electrical Bus was fully capable of performing its intended safety function with the malfunction on Bus Breaker 1A306. "Therefore, this event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73. "The NRC Resident Inspector has been notified." Notified R3DO (Skokowski). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-04-23
51005 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2015-04-22 15:28 | 2015-04-23 13:18 | 2015-04-23 | VIOLATION OF THE FITNESS FOR DUTY PROGRAM A contract employee supervisor willfully acted to avoid a random fitness-for-duty test. The individual left the construction site after the notification to report to the fitness-for-duty office. The employees access to the plant has been terminated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2015-04-23
51004 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-23 02:10 | 2015-04-23 05:25 | 2015-04-23 | MANUAL REACTOR TRIP DUE TO A SECONDARY PLANT TRANSIENT "On April 23, 2015 DC Cook Unit 2 Reactor was manually tripped due to an uncontrolled cooldown due to two (2) failed open steam dump valves. The cause of the failure is still under investigation. "This event is reportable under 10 CFR 50.72(b)(2)(i) Tech Spec Required Shutdown, as a four (4) hour report; 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, as a four (4) hour report; and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Reactor Protection System (RPS), as an eight (8) hour report. "The electrical grid is stable and Unit 2 continues to be supplied by offsite power. All control rods fully inserted. Decay heat is being removed via steam generator Power Operated Relief Valves due to steam dump valves being manually isolated. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the post Trip Review. No radioactive release is in progress as a result of this event. "The DC Cook Resident NRC Inspector has been notified." There is no indication of primary to secondary leakage and there is no impact on Unit 1. | 0 | 0 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2015-04-23
51003 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-02-24 17:02 | 2015-04-22 14:18 | 2015-04-22 | 60-DAY OPTIONAL TELEPHONE NOTIFICATION OF INVALID SYSTEM ACTUATION DUE TO MOTOR GENERATOR OUTPUT BREAKER TRIP "On February 24, 2015, at approximately 1702 CDT, while the plant was in cold shutdown, power was lost on the Division 1 reactor protection system (RPS) bus. This event resulted in the automatic closure of the Division 1 primary containment isolation valves in the residual heat removal (RHR) and reactor water cleanup systems. Additionally, the primary containment atmospheric monitoring system automatically actuated, and ventilation systems in the fuel building, auxiliary building, and control building shifted to emergency mode. The closure of the isolation valves in the residual heat removal system caused an automatic trip of the 'A' RHR pump, which had been in the shutdown cooling alignment. The equipment response to the isolation signal was as expected. This event is being reported in accordance with 10 CFR 50.73(a)(1) as an invalid actuation of the Division 1 primary containment isolation system. "The isolation was promptly diagnosed as having resulted from a trip of the output breaker of the RPS motor generator (MG) set 'A,' and not from a valid signal. Operators implemented the appropriate response procedures to align power to the bus via the alternate source, and began restoring the affected systems. The 'A' RHR pump was re-started within twelve minutes, during which time coolant temperature increased approximately seven degrees to a maximum of approximately 100F. Other affected systems were restored over the next few hours. "The causal analysis concluded that the MG set output breaker tripped due to an overly conservative setpoint on the overvoltage trip relay. The low trip setpoint was a latent condition that had existed since the output voltage was raised in 1988 at the recommendation of the vendor, but at which time the trip setpoint was not changed. To correct this condition, the MG overvoltage trip setpoint was raised to restore adequate operating margin to the normal MG output voltage. "At the time of the event, the plant was in MODE 5 with the reactor cavity flooded to greater than 23 feet above the vessel flange. The shutdown cooling system was promptly restored to service. This event was of minimal safety significance to the health and safety of employees and the public." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-04-22
51002 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2015-04-21 23:30 | 2015-04-22 03:17 | 2015-04-22 | OFFSITE NOTIFICATION DUE TO WORKER FATALITY NOT RELATED TO PLANT OPERATION "At approximately 2330 [EDT] on April 21, 2015, a worker collapsed in the turbine building inside the protected area. Initial response by on-site responders found the person unresponsive. Subsequent response by off-site medical responders determined the person had died and the station was notified at approximately 0130 on April 22, 2015. The fatality was due to an apparent personal medical issue and not work related . The individual was not contaminated. The individual was transported off-site via onsite Site Protection personnel. Plant operation was not impacted by the event." The licensee informed Lower Alloways Creek Township and will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-04-22
51001 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-21 22:58 | 2015-04-22 01:58 | 2015-04-22 | INOPERABLE SECONDARY CONTAINMENT On April 21, 2015 at 2258 [EDT], Secondary Containment became inoperable requiring a Technical Specification 3.6.4.1 entry for failure to meet SR 3.6.4.1.1 on Unit 1 and Unit 2. The inoperability was caused by Zone 3 differential pressure lowering to less than 0.25 [inches Water Column] when Zone III fans tripped during 30mph wind gusts. Fans were restarted and differential pressure restored to greater than 0.25 [inches Water Column] at 2314 hrs. April 21, 2015. This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-04-22
51000 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-21 21:45 | 2015-04-22 00:18 | 2015-04-22 | AGREEMENT STATE REPORT - RADIOGRAPHY TRUCK ACCIDENT RESULTING IN A FATALITY The following information was received by the State of Texas via email: "On April 21, 2015 at 2209 [CDT] hours, the Agency [Texas Department of State Health Services] was contacted by Andrews County Emergency Management (ACEM). They informed the Agency that an accident had occurred 12 miles south of Andrews, Texas, on highway 385, which involved a radiography truck. The Agency contacted ACEM chief who stated he was at the scene of a three vehicle accident which included a truck from Desert NDT. The driver was killed in the accident and the truck cab had separated from the frame. He stated the dark room had separated from the truck bed. He stated a person from the Andrews County WCS [Waste Control Specialist] was there and had performed a radiation survey and measured a dose rate of 15 millirem 10 feet from the truck. He stated the licensee had been contacted. He stated they had taken care of the survivors and had backed out of the area until the licensee's radiation safety officer arrived on the scene. He stated they had not seen the shipping papers, only the radiation symbol on the truck. I asked him to have the licensee contact the Agency as soon as they arrived on site. "The licensee's (Desert NDT) RSO arrived at the scene at 2223 hours and contacted the Agency. He stated his priority was to locate the source. He agreed to call the Agency as soon as he had control of the source. "At 2240, the RSO contacted the Agency and stated he had control of the source. The iridium source was inside a INC 100 radiography camera and the RSO believed the activity was between 20 and 26 curies. He stated the camera did not appear to be damaged. He stated the dark room had separated from the truck and split into two pieces. The camera was located still in its transport box in a section of the darkroom. He stated the dose rate on contact with the camera was 16 millirem an hour and 0.4 millirem at 1 foot. The dose rate at 1 meter was not distinguishable from background. He stated no individual at the scene would have received an exposure to radiation that would have exceeded any limits. The RSO stated he was taking the source back to the licensee's office for storage. The RSO stated they would send the exposure device to the manufacturer for inspection. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident: I-9305 * * * UPDATE FROM ARTHUR TUCKER TO VINCE KLCO ON 4/22/15 AT 1014 EDT * * * The following information was received by the State of Texas via email: "The licensee's corporate radiation safety officer contacted the Agency [Texas Department of State Health Services] and informed them that two radiographers were killed in this event. He stated the source activity was only 13 curies. He stated that local law enforcement in Andrews, Texas will not release any details of the accident until their investigation is completed. "Additional information will be provided as it is received in accordance with SA-300." Notified the R4DO (Drake), IRD MOC (Gott) and the NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-05-06
50999 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-04-21 | 2015-04-21 12:06 | 2015-04-21 | LOSS OF ASSESSMENT CAPABILITY DUE TO NON-FUNCTIONAL SEISMIC MONITOR LAPTOP "Clinton Power Station (CPS) has completed a review of the station seismic monitor performance. The CPS seismic monitor laptop is currently operable; however, this review identified 3 times in the last 3 years that the seismic monitoring laptop was declared non-functional such that the capability to perform an EAL assessment in accordance with the Radiological Emergency Plan Annex would be adversely impacted. A loss of the seismic laptop computer prevents active seismic data from processing through the central recording unit and will not alarm in the main control room. The seismic monitor laptop became non-functional and unresponsive on the following dates: 1) January 4, 2013 2) July 19, 2013 3) November 2, 2014 "The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72 (b)(3)(xiii) This report is required per 10 CFR 50.72(1)(1)(ii) as an event that occurred within 3 years of the date of discovery." The NRC Resident Inspector has been notified. Notified the R3DO (Valos). | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-21
50998 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-08-07 17:07 | 2015-04-20 21:26 | 2015-05-26 | THIS IS A CONTINUATION OF EN #50351 * * * UPDATE FROM STEVE BRUNSON TO CHARLES TEAL ON 4/20/15 AT 2126 EDT * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - A gap 1/4" wide, 1" tall, and 6" deep was found at penetration 1Z43H594D on the west wall of the U1 East Cableway (separating Fire Area 1104 and Fire Area 1020) - Near penetration 1Z43J837D, and approximately 12" south and above 1Z43H837D, gaps were observed in the mortar joint between CMU on the west wall of the U1 East Cableway (separating Fire Area 1104 and Fire Area 1020) - A triangular gap 1" wide, 1" tall and 6" deep was found at penetration 1Z43H592D on the west wall of the U1 East Cableway (separating Fire Area 1104 and Fire Area 1020) - A gap 4" tall and 3" wide was found behind Turn Box TB1-1272 which covers penetrations 1Z43H590D, 1Z43H589D, 1Z43H588, and 1Z43H587D on the west wall of the U1 East Cableway (separating Fire Area 1104 and Fire Area 1020) - At the architectural joint between the vertical wall to the horizontal floor/ceiling assembly above door 1C-22, above and to the south of 1Z43H1105D, a gap was observed approximately 1/4" tall, 3" wide, and 6" deep on the west wall of the U1 East Cableway Foyer (separating Fire Area 1105 and Fire Area 0014K) - Gap between the grout and the conduit of penetration 1Z43H778D approximately 1/4" tall x 1.5" wide x 6" deep on the east wall of the Unit 1 130' Elevation Control Building Working Floor Hallway (separating Fire Area 0014K and Fire Area 1105) "The nonconforming conditions observed for the affected fire penetrations and fire barriers were identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensure the safe shutdown paths are preserved until the degraded conditions are repaired. "CR 10058276; CR 10058278 "The following deficiencies were also observed causing the affected penetrations to be considered nonfunctional: - A gap 1/4" wide, 1" tall, and 6" deep was located at penetration 1Z43H532D on the west wall of the U1 East Cableway (separating Fire Area 1104 and Fire Area 0014M) - A gap 1/8" wide, 1" tall and 6" deep was located at penetration 1Z43H780D on the west wall of the U1 East Cableway (separating Fire Area 1104 and Fire 0014M) - A gap 1/2" wide, 1" tall, and 6" deep was located at penetration 1Z43H781D on the west wall of the U1 East Cableway (separating Fire Area 1104 and Fire 0014M). A 1/4" x 1/2" defect was also identified at penetration 1Z43H781D on the east wall of the Men's Restroom in the Control Building (separating Fire Area 0014M and Fire Area 1104) "The nonconforming conditions observed for the affected penetrations were identified as affecting both safe shutdown paths for Unit 1 and Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until degraded conditions are repaired. "CR 10058277 "The expanded scope inspection activity is continuing and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity." The licensee has notified the NRC Resident Inspector. Notified R2DO (Blamey). * * * UPDATE FROM SCOTT BRITT TO DONG PARK ON 4/23/15 AT 1654 EDT * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: - A gap 1/4" wide, 1" tall and 7" deep was found at penetration 1Z43H1138D on the east wall of the U1 RPS MG Set Room (separating Fire Area 1013 and Fire Area 0040). No seal material was seen between the sleeve and the cinderblock on the north side of penetration. - A void 1" tall, 1" wide, and 7" deep was found in the south upper corner under a concrete beam at column line T12 above penetration 1Z43H941D on the east wall of the U1 RPS MG Set Room (separating Fire Area 1013 and Fire Area 0040). - At penetration 1Z43H1139D, it appears that combustible neoprene insulation is used around the pipe within the plane of the west wall of the Vertical Cable Chase Room (separating Fire Area 0040 and Fire Area 1013). Combustible materials would not be part of a rated pen seal. - A gap 1" wide, 1" tall and 7" deep was observed at penetration 1Z43H1138D on the west wall of the Vertical Cable Chase Room (separating Fire Area 0040 and Fire Area 1013). "The nonconforming conditions observed for the affected fire penetrations and fire barriers were identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10060228" The licensee will notify the NRC Resident Inspector. Notified R2DO (Blamey). * * * UPDATE FROM STANLEY STONE TO DONG PARK ON 4/27/15 AT 2047 EDT * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers to be considered nonfunctional: -An opening in the grout 1/4" wide, 1/2" tall and over 7" deep was found between the wall and the outside sleeve for penetration 2Z43H028D on the west wall of the U2 Transformer Room (separating Fire Area 2019 and Fire Area 2016). -A 1/4" diameter hole in the grout approximately 2.5" deep was found above conduit 2MI2128 on the west wall of the U2 Transformer Room (separating Fire Area 2019 and Fire Area 2016). "The nonconforming conditions observed for the affected penetration and fire barrier were identified as affecting both safe shutdown paths for Unit 1 and Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10061830" The licensee notified the NRC Resident Inspector. Notified R2DO (Blamey). * * * UPDATE FROM PAUL UNDERWOOD TO DONG PARK ON 4/28/15 AT 1640 EDT * * * "During an expanded scope inspection, deficiencies in the following areas were observed that caused the affected barriers in the Unit 2 Control Building 130' elevation to be considered nonfunctional and represented degraded conditions of penetrations through the wall separating the Unit 2 Switchgear Access Hallway - Fire Area 2014, from the U2 West 600 V Switchgear Room - Fire Area 2016. "The following conditions were located on the south wall of the Unit 2 Switchgear Access Hallway (Fire Area 2014). 1. An opening between the conduit and the wall 1/4" wide, 2" long and probed to be at least 2 1/2" deep was identified for penetration 2Z43H668D. A similar condition exists for this penetration on the opposite side of the wall in Fire Area 2016. 2. An opening between the conduit and the wall 1/4" wide, 1/2" long and probed to be at least 3" deep was identified for penetration 2Z43H667D. A similar condition exists for this penetration on the opposite side of the wall in Fire Area 2016. The following conditions were located on the opposite side of the same wall. This is the north wall of the U2 West 600V Switchgear Room (Fire Area 2016): 3. An opening between the conduit and the wall 1/8" wide, 1" long and probed to be at least 4" deep was identified for penetration 2Z43H668D. 4. An opening between the conduit and the wall 1/8" wide, 1/2" long and probed to be at least 3" deep was identified for penetration 2Z43H667D. 5. An opening between the conduit and the wall 2 1/2" wide, 2 1/2" long and probed to be at least 4" deep was identified around the 2" continuous run conduit located above cable tray penetration 2Z43H031D. 6. An opening between the conduit and the wall 1/4" wide, 3/4" long and probed to be at least 6" deep was identified above a 3/4" continuous run conduit (first of three) located at the ceiling near column line TE. 7. An opening between the conduit and the wall 1/4" wide, 1/2" long and probed to be at least 6" deep was identified above a 3/4" continuous run conduit (second of three) located at the ceiling near column line TE. 8. An opening between the conduit and the wall 1/4" wide, 3/4" long and probed to be at least 5" deep was identified above a 3/4" continuous run conduit (third of three) located at the ceiling near column line TE. "The nonconforming conditions observed for the affected penetration and fire barrier were identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10062254" The licensee notified the NRC Resident Inspector. Notified R2DO (Ehrhardt). * * * UPDATE FROM PAUL UNDERWOOD TO DANIEL MILLS ON 4/29/15 AT 1804 EDT * * * "During an expanded scope inspection, deficiencies in the Unit 2 Control Building 130 foot elevation were observed that caused the affected barriers to be considered nonfunctional and represented degraded conditions of penetrations through the wall separating the Unit 2 West DC Switchgear Room 2A (Fire Area 2018) and the Unit 2 Switchgear Access Hallway (Fire Area 2014). "The following conditions were located on the west wall of the Unit 2 Switchgear Access Hallway (Fire Area 2014). 1. An opening between the conduit and the wall 1/4 inch wide, 1 inch long and probed to be greater than 2 inch deep, was identified for penetration 2Z43H673D. 2. There is insufficient masonry material to fill the full depth of the wall above the ductwork that passes through penetration 2Z43H032D. This deficiency affects a small area on the south side of the ductwork and penetrations 2Z43H789D, 2Z43H790D, and 2Z43H791D. 3. An opening between the conduit and the wall 1/4 inch wide, 1 inch long and probed to be 4 inch deep was identified for penetration 2Z43H671D. A similar condition exists for this penetration on the opposite side of the wall (see Item 5 below). "The following conditions were located on the east wall of the Unit 2 West DC Switchgear Room 2A (Fire Area 2018). 4. There are openings between the conduits and the wall 1/2 inch wide and 1 inch long for penetrations 2Z43H789D, 2Z43H790D, and 2Z43H791D. These penetrations are affected in Item 2 above. 5. An opening between the conduit and the wall 1 inch wide, 1 inch long and probed to be greater than 6 inch deep, was identified for penetration 2Z43H671D. 6. An opening between the conduit and the wall 1/4 inch wide, 1 inch long and probed to be at least 2 inch deep, was identified for penetration 2Z43H673D. 7. An opening between the conduit and the wall 1/4 inch wide, 1 inch long and probed to be at least 2 1/2 inch deep, was identified for penetration 2Z43H676D. "The nonconforming conditions observed for the affected penetrations were identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR10062955" The licensee notified the NRC Resident Inspector. Notified R2DO (Ehrhardt). * * * UPDATE FROM JOHN MITCHELL TO HOWIE CROUCH AT 2137 EDT * * * "During an expanded scope inspection, deficiencies in the Control Building 130' elevation were observed that caused the affected barriers to be considered nonfunctional and represented degraded conditions of the following penetrations through the wall separating the Unit 2 East Cableway (Fire Area 2104) and the Health Physics Hallway and Counting Room (Fire Areas 0014B and 0014G). - Penetration 2Z43H783D terminates open within a foot of the east wall of the Health Physics Counting Room (Fire Area 0014G) - Penetration 2Z43H603D contains no visible seal material and is located on the east wall of the Health Physics Hallway (Fire Area 0014B). "The nonconforming conditions observed for the affected penetrations were identified as affecting both safe shutdown paths for Unit 1 and Unit 2. "Deficiencies were also observed that caused the affected barriers to be considered nonfunctional and represented degraded condition of the wall separating the Unit 2 East Cableway (Fire Area 2104) from the common East Cableway Foyer (Fire Area 1105). - Gap near penetration 2Z43H170D between a conduit and the concrete masonry unit (CMU) wall located on the south wall of the Unit 2 East Cableway (Fire Area 2104). "The nonconforming conditions observed for the affected fire barriers were identified as affecting both safe shutdown paths for Unit 1. "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas but were modified based on the nature of the degradations noted in the condition report and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR10063642" Notified R2DO (Ehrhardt). * * * UPDATE FROM JOHN MITCHELL TO JOHN SHOEMAKER AT 1638 EDT ON 5/7/15 * * * "During an expanded scope inspection, deficiencies in the Control Building 147' elevation were observed that caused the affected barriers to be considered nonfunctional. These deficiencies represented degraded conditions of the following penetrations through the wall separating the Unit 1 CO2 Tank Room (Fire Area 0025) and the Computer Room (Fire Areas 0024B) as well as a discrepancy in the affected wall. - In Fire Area 0024B, a small gap in the foam, approximately 6 [inch] deep was identified in Penetration 1Z43H592F. The adjacent Fire Area is FA 0025. - In Fire Area 0024B, penetration 1Z43H325F was identified with no sealant for the penetration sleeve. The adjacent Fire Area is FA 0025. - In Fire Area 0024B, foam sealant was missing in cable-tray, 1Z43H061F. The adjacent Fire Area is FA 0025 - In Fire Area 0024B, a gap was identified in a concrete masonry unit (CMU) wall joint, directly above 1Z43H062F. "The nonconforming conditions observed for the affected fire barriers were identified as affecting both safe shutdown paths for Unit 1 and Unit 2. "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR10066678" The licensee has notified the NRC Resident Inspector. Notified the R2DO (Sandal). * * * UPDATE AT 2151 EDT ON 05/07/15 FROM SCOTT BRITT TO S. SANDIN * * * "During an expanded scope inspection, a deficiency in the Control Building 147 ft. elevation was observed that caused the affected barrier to be considered nonfunctional. This deficiency represented degraded conditions of the following fire barrier separating the Unit 1 CO2 Tank Room (Fire Area 0025) and the Cable Spreading Room (Fire Areas 0024A). - A 1/4 inch x 2 inch x approximately 4 inch deep gap in the east CMU wall of Unit 1 CO2 Tank Room above penetration 1Z43H046F. "The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Unit 1 and Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR10066844" The licensee will inform the NRC Resident Inspector. Notified R2DO (Sandal). * * * UPDATE AT 2029 EDT ON 05/08/15 FROM SCOTT A. BRITT TO S. SANDIN * * * "During an expanded scope inspection, deficiencies in the Control Building 147 ft. elevation were observed that caused the affected barrier to be considered nonfunctional. These deficiencies represent degraded conditions of the following fire barrier separating the Cable Spreading Room (FA 0024A) and the CO2 Tank Room (FA 0025). - Multiple gaps in the caulk at the top of the ceiling of the west wall of the Cable Spreading Room (separating FA 0024A and FA 0025). "The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Unit 1 and Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10067163" The licensee will inform the NRC Resident Inspector. Notified R2DO (Sandal). * * * UPDATE FROM PAUL UNDERWOOD TO DANIEL MILLS ON 5/11/15 AT 1711 EDT * * * "During an expanded scope inspection activity, multiple fire penetrations on the Control Building El. 130' elevation were identified that resulted in the affected barriers being considered NON-FUNCTIONAL. "An issue was identified with the wall separating the Vertical Cable Chase, Fire Area 0040, from the Unit 2 RPS MG Set Room, Fire Area 2013. - A 1/4" wide x 1/2" long x approximately 6" deep gap in the grout of a 2" continuous run conduit, 6" away from 2Z43H581D was identified. - A 1/4" wide x 3" long x approximately 6" deep gap in the grout of penetration 2Z43H581D was identified. - A 1/2" wide x 2" long x approximately 6" deep gap in the grout of penetration 2Z43H580D was identified. "The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Unit 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10068138" The NRC Resident Inspector has been notified. Notified R2DO (Bonser). * * * UPDATE FROM GUY GRIFFIS TO DANIEL MILLS ON 5/12/15 AT 2151 EDT * * * "During an expanded scope inspection activity, a fire barrier on the Control Building El. 164' elevation was identified as being NON-FUNCTIONAL as follows; - A discrepancy was identified with the fire barrier separating the Unit 1 Turbine Building Main Floor Area, Fire Area 0101A from the Main Control Room, Fire Area 0024C. The condition consists of a small gap 1/4" wide, 3" long and probed to be greater than 6" deep between the wall and conduit at penetration 1Z43H605J on the Turbine Building side of the wall. "The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Units 1 and 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10068842" The NRC Resident Inspector has been notified. Notified R2DO (Bonser). * * * UPDATE FROM GUY GRIFFIS TO VINCE KLCO ON 5/14/15 AT 2121 EDT * * * "During an expanded scope inspection, deficiencies in the Control Building 164' elevation were observed that caused the affected barrier to be considered nonfunctional: - A 1/4 inch x 1/2 inch x approximately 6 inch deep gap in the grout of the annulus of penetration 1Z43H602J was identified in the east wall of the Main Control Room (separating Fire Areas 0024C and 0101A). - A 1/4 inch wide x 8 inch long vertical crack, approximately 6 inch deep was identified in the CMU below penetration 1Z43H602J was identified in the east wall of the Main Control Room (separating Fire Areas 0024C and 0101A). - Three abandoned anchor holes, 1/2 inch in diameter and approximately 4 inch deep, were identified below penetration 1Z43H604J in the east wall of the Main Control Room (separating Fire Areas 0024C and 0101A). - A 1 inch diameter abandoned anchor hole, approximately 6 inch deep, was identified directly above a 1/4 inch pipe penetration in the east wall of the Main Control Room (separating Fire Areas 0024C and 0101A). - A 1/2 inch to 3/4 inch gap exists between the top of each of the 3 concrete block (CMU) walls enclosing the HVAC chase and the underside of the floor/ceiling assembly separating the Main Control Room (Fire Area 0024C) and the HVAC Room Chase (Fire Area 0014L). - A 1/2 inch diameter hole exists in the CMU at the upper right corner of penetration 1Z43H1184J separating the Main Control Room (Fire Area 0024C) and the HVAC Room Chase (Fire Area 0014L). "The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Units 1 and 2. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10069898; CR 10069995" The licensee will notify NRC Resident Inspector. Notified the R2DO (Bonser). * * * UPDATE FROM R.S. STONE TO VINCE KLCO ON 5/15/15 AT 1807 EDT * * * "During an expanded scope inspection for penetration seals, the following discrepancies were identified with the wall separating the Unit 1 Working Floor, Fire Area 0001, from the Unit 1 AC Inverter Room, Fire Area 1008 that caused the affected barriers to be considered nonfunctional: A 1/4 inch x 1 inch x approximately 2 inch deep gap in the grout of the annulus of penetration 1Z43H553C. A 1/4 inch x 1 inch x approximately 2 inch deep gap in the grout of the annulus of penetration 1Z43H546C. A 1/8 inch wide x 1/2 inch tall x approximately 6 inch deep gap in the foam block out, below penetration 1Z43H546C. A 3 inch x 3 inch x 10 inch deep gap in the grout around a 2-1/2 inch continuous run conduit. A 1/4 inch x 1 inch x 10 inch deep gap in the grout around 1-1/2 inch continuous run and 1-1/4 inch continuous run conduits. 2 inch deep gaps in the grout around 1-1/2 inch and 2-1/2 inch continuous run conduits. A 1/4 inch hole x 1 inch deep gap in the grout around penetration 1Z43H060C. A 1/4 inch x 1/4 inch x 2 inch deep gap around the annulus of a 1-1/4 inch continuous run and 2 inch continuous run conduits. "The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Unit 1. Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR 10070439" The licensee notified the NRC Resident Inspector. Notified the R2DO (Bonser). * * * UPDATE ON 1638 EDT ON 05/21/15 FROM GUY S. GRIFFIS TO JEFF HERRERA * * * "During an expanded scope inspection, the following discrepancies were identified in the Unit 1 Control Building 130[foot] elevation that caused the affected fire barrier to be considered nonfunctional: - Six 3[inch] x 3[inch] holes in the wall of the Men's Rest Room (separating Fire Areas 0014M and 1104). The nonconforming conditions observed for the affected barrier were identified as affecting both safe shutdown paths for Unit 1 and Unit 2. "Deficiencies were also observed in the Diesel Generator Building 130[foot] elevation that caused the affected fire barrier to be considered nonfunctional: - Through-wall gap around the conduit that passes through penetration 2Y43H511D on the south wall of the U2 Diesel Generator Switchgear Room 2F (separating Fire Areas 2408 and 2409). The nonconforming condition observed for the affected fire barrier was identified as affecting both safe shutdown paths for Unit 2. "Compensatory measures were already in place in accordance with the plant's Fire Hazard Analysis (FHA) as a result of previous conditions involving degraded barriers in the same fire areas and will remain in place until the fire barriers are repaired. The presence of the compensatory measures in addition to portable fire protection equipment located in adjacent areas ensures the safe shutdown paths are preserved until the degraded conditions are repaired. The expanded scope inspection activity is continuing, and this and any subsequent similar condition(s) that meets the reporting requirements will be included in an ENS Update Report as required and will be documented in a revised LER at the end of the inspection activity. "CR10073041; CR10073187" The licensee notified the NRC Resident Inspector. Notified the R2DO (Ernestes). | 100 | 90 | 0 | 100 | 90 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-04-21
50997 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2015-04-17 22:45 | 2015-04-20 17:57 | 2015-04-20 | FITNESS FOR DUTY REPORT - DISCOVERY OF A PROHIBITED ITEM IN THE PROTECTED AREA The licensee discovered evidence of prohibited material inside the protected area. The material has been removed. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Defueled | Power Operation | Power Operation | Defueled | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2015-04-20
50996 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-03-13 | 2015-04-20 16:43 | 2015-04-20 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA FAILED SOURCE DISCONNECT/MISCONNECT TEST The following was received from the State of Louisiana via email: "A radiography inspection was being performed on a Central Testing crew at the Tri-7 facility in Sulphur, LA. At a point during the inspection, the inspector requested that the crew demonstrate a misconnect/disconnect test on the camera and drive cables in use. The crew stated that the equipment had passed the test before the equipment was put into service for the day. However, during the demonstration, the 'control assembly' on the crankout set functioned in a test failure mode. The control assembly easily slipped into position without the drive cable being attached to the source assembly, 'pigtail.' With this failure, the RSO was contacted and an additional set of crankouts were brought to the jobsite. "The crankout was evaluated and it was determined that the control assembly is what failed during the test. The control assembly was replaced on the crankout and it corrected the misconnect/disconnect test failure. This test is to be performed on the equipment daily with use. This is a requirement of LA Radioactive Material License LA-2393-L01A, Condition # 16. "The exposure device was a SPEC Model 150 camera, S/N 1057, loaded with a 63 Ci Ir-192 source, SPEC Model G-60. The associated equipment was manufactured by SPEC, crankout and control assembly, with unknown model and s/ns. When the equipment was replaced, the radiography crew was allowed to resume their work." LA Event Report ID: LA 15-0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-04-28
50995 | 0 | OAKWOOD HOSPITAL AND MEDICAL CENTER |  |  |  |  | 2015-04-08 | 2015-04-20 16:24 | 2015-04-21 | LOST BRACHYTHERAPY SEED The medical center performed a procedure where an I-125 seed (0.3 mCi) was implanted in a breast lumpectomy site. The Brachytherapy Radiation Safety Officer believes that when the lump was removed, the implanted seed was also discarded as bio-waste. The seed dimensions are 4.5 mm long by 0.1 mm in diameter. The biological waste is no longer on site. * * * UPDATE FROM TALJIT SANDHU TO DAN LIVERMORE ON 04/21/2015 AT 1441 EDT * * * Corrected the event date from 04/20/2015 to 04/08/2015 and corrected the CFR section from 20.2201(a)(1(i) to 20.2201(a)(1)(ii). Notified R3DO (Valos) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-04-28
50994 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-04-19 17:45 | 2015-04-19 23:04 | 2015-04-19 | UNANALYZED CONDITION DUE TO NON COMPLIANCE WITH 10 CFR 50 APP R "On April 19, 2015, it was determined that in the event of an Appendix-R fire in the Control Room/Relay Room, fire induced circuit damage can potentially result in Reactor Coolant Pump's (RCP) restarting. Procedure F5 APP B does not take actions to open RCP DC knife switches as required per Appendix R calculation GEN-PI-026, GEN-PI-054, and GEN-PI-055. Neither unit is currently susceptible to this condition due to the installation of improved RCP seals which allow adequate time to restore seal cooling prior to seal failure. However, the condition has occurred within three years of the time of discovery and is reportable under 10 CFR 50.72(b)(3)(ii)(B). "The Appendix R analysis requires that manual actions are taken to ensure that the RCPs are tripped and actions are taken to prevent restarting of the RCPs. The RCPs breaker must be verified open at the associated bus and DC knife switches located in the breaker cubicles are to be opened. These actions are required due to fire induced, loss of remote trip (spurious breaker closure) and loss of RCP seal cooling water and loss of Component Cooling (CC) water to the thermal barrier heat exchanger. These actions are required to achieve and maintain Mode 3, Hot Standby in the event of a catastrophic fire that results in the functional loss and/or evacuation of the Control Room/Relay Room. "Current procedures verify the RCP breakers are open; however, they do not open the DC knife switch and therefore a hot short could result in a RCP restarting. This procedure omission meets the reporting criteria for 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. "The protection of the health and safety of the public was not affected by this issue. The licensee has notified the NRC Senior Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-04-19
50993 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2015-04-13 | 2015-04-17 19:34 | 2015-04-17 | AGREEMENT STATE REPORT - RADIUM SOURCE FOUND The following report was received via e-mail: "Reported by Weld County DPHE [Department of Public Health and Environment] on behalf of Vista Ridge Academy, Erie, Colorado on Monday April 13, 2015. "The material was discovered in a glass vial marked 'radium dust' which was verified as Radium 226 using a portable MCA (IdentiFINDER 2, S/N 910383-80, background 0.01 mrem/hr). The readings on contact and at one foot from the vial were 2.8 mrem/hr and 0.1 mrem/hr respectively. Due to the elevated nature of the readings, it was determined shielding should be put in place to protect individuals from exposure. The material was placed in plastic bags to contain the material in the event the lid falls off or the glass is broken. Additionally, ceramic bricks were used to build a temporary storage area for the vial to reduce the exposure in the area. The exposure on the outside of the brick shielding was 0.3 mrem/hr on contact. The material is stored in a secured closet. The mass of the contents in the vial were determined to be 204.5 grams with an approximate volume of 84.78 cubic centimeters. (The mass was determined using a school scale and a similar empty vial. The volume was determined by approximation of the diameter and height of the material in the vial.) "Surveys were performed around the work bench area, storage shelf and a removable contamination wipe was done on the vial. It was determined during the site visit no contamination was present in the lab or storage area indicating no exposures to students or staff. "Using the information gathered and making a few assumptions about efficiency, there is an estimated 50 to 100 uCi in the vial. "Report ID number: CO15 - I15 -12 "A provisional license will be issued until the material can be properly disposed." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2015-04-27
50992 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-04-15 15:50 | 2015-04-17 17:10 | 2015-04-17 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILED OPEN The following report was received via e-mail: "Installed fixed level gauge on a process. The shutters on a fixed level gauge would not close properly due to a breakage of a shutter pin. The situation is the result of extended usage. The gauge was purchased and put into service in 1985. The problem with the shutter function is considered equipment failure of this device. Corrective action will be to de-install this device and [dispose of it]. The gauge will be replaced with a new lower activity source device. The failure is that the shutter blades would not open and close due to a shutter pin breaking. There was no removable radiation released into the environment. The gauge/source holder was 'fixed', and the RSO tagged and posted the broken device. Additionally, all personnel working in the vicinity of the devise were informed of the problem. The RSO advised the employees the radiation exposure levels were in the normal operational range. "The gauge was an Accuray Mfg. device, SH302, s/r HS302-S6, approximately 200 mCi of Cs-137 when installed and manufactured in 1985. The source serial number is CS11166." Louisiana Report: LA150007, T163028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-04-27
50991 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2015-04-15 | 2015-04-17 12:43 | 2015-04-17 | AGREEMENT STATE REPORT - SOURCE MOVED DURING MEDICAL TREATMENT "On 4-15-15 the patient was to receive a fractionated dose of 4 Grays to the 'vaginal cuff' region using a 10.175 Curie Ir-192 source. The dose was to be administered using a Varian Model VariSource 200t remote HDR [High Dose Rate] afterloader, serial number 600349. "The plan was to administer 6 radiation treatments using a cylinder applicator and holder, the treatment length intended to be 5 cm. Imaging was done after placement of the cylinder prior to treatment to verify location, however, post-treatment imaging showed that the cylinder applicator had come loose from the holder and shifted 3 cm. This was the first of the six fractions. "Hospital staff physicists are currently working to determine the delivered dose to the target and why the shift occurred. Physician notification has not been verified at this time. The patient has been notified." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2015-04-27
50990 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2015-04-13 | 2015-04-16 19:26 | 2015-04-16 | POTENTIAL OVEREXPOSURE TO RADIOGRAPHER A radiographer dropped his film badge on the floor before his first exposure. The floor was approximately three feet below the collimator for a two minute exposure. After his second exposure, he found his film badge. The licensee's RSO had the film developed with a result of 14.069 Rem. The source was Ir-192 at 78.6 Ci. Estimated dose by the licensee and REAC/TS expected a dose of closer to one and a half Rem. The licensee is continuing his investigations because of this discrepancy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2015-04-24
50989 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-04-16 13:20 | 2015-04-16 18:06 | 2015-04-16 | BOTH SECONDARY CONTAINMENT AIRLOCK DOORS OPEN SIMULTANEOUSLY "At 1320 CDT, on April 16, 2015, both doors of a Secondary Containment Airlock were reported to be open. The doors being open at the same time caused a failure to meet SR 3.6.4.1.2 to verify that either the outer door(s) or inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered inoperable per TS LCO 3.6.4.1. Upon discovery, immediate action was taken to close the doors. The doors were open concurrently for a momentary amount of time. The action to close the door allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to an operable status. "The notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(C). "The NRC Resident Inspector has been notified." The licensee is investigating how the electrical interlock failed to prevent this occurrence. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-04-16
50988 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-16 05:00 | 2015-04-16 01:35 | 2015-04-16 | SCHEDULED MAINTENANCE AFFECTING TECHNICAL SUPPORT CENTER HVAC "On April 16, 2015, Byron Station will remove part of the Technical Support Center (TSC) emergency ventilation system from service to facilitate necessary surveillance work on the fire protection system. This work is expected to last approximately 4 hours. This maintenance affects the ability of the TSC ventilation to maintain adequate habitability during the duration of an emergency. If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. If the TSC becomes uninhabitable, the Station Emergency Director will relocate the TSC staff to an alternate TSC location in accordance with applicable procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the potential loss of an emergency response facility because of the unavailability of the ventilation system. An update will be provided once the TSC ventilation has been restored to normal operation." The NRC Resident Inspector has been notified. * * * UPDATE FROM SHANE HARVEY TO JOHN SHOEMAKER AT 1646 EDT ON 4/16/15 * * * Maintenance has been completed and the TSC emergency ventilation system was restored to service at 1300 CDT on 4/16/15. The NRC Resident Inspector will be notified. Notified the R3DO (McCraw). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-16
50987 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-14 16:00 | 2015-04-15 18:41 | 2015-04-21 | AGREEMENT STATE REPORT - SOURCE CAPSULE BREACHED RESULTING IN CONTAMINATED AREA AND INDIVIDUAL "On April 15, 2015, the licensee notified the Agency that on April 14, 2015, one of its technicians was removing a cesium-137 source, with a current activity of 694 millicuries (original activity was 1200 millicuries in 06/1991), from an Ohmart SHLG-1 nuclear gauge. When he opened up the gauge, the source was ruptured. The cause of the rupture has not yet been determined. Areas of the workroom and the technician were contaminated. The technician was immediately [externally] decontaminated. The licensee swabbed the technician's nasal passages and found contamination. The licensee has sent the technician's dosimetry for immediate processing and is in the process of determining the internal dose estimate. Surveys confirmed that no contamination was carried outside the work room. Cleanup and surveys of the workroom are being performed. Access has been restricted since the incident. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300. Texas Incident I-9302 * * * UPDATE FROM ART TUCKER TO DAN LIVERMORE AT 1326 ON 04/21/15 * * * "Currently 3 homes of employees have been found to have contamination, characterization has not been performed. Various articles of clothing have been confiscated by the company and residents have been moved to hotels, with all objects brought along cleared. "The room in which the incident occurred has been sealed off. Additional licensee personnel have arrived to assist with surveys and cleanup. Assay of the source to determine what activity remains within the capsule has not yet been performed. Interviews of involved individuals are ongoing. "Full body counts have been performed with initial readings of 4.86 mrem CEDE for one employee and 290 mrem CEDE for another." Notified R4DO (Drake) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-04-23
50986 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2015-04-15 15:15 | 2015-04-15 16:02 | 2015-04-15 | AGREEMENT STATE REPORT - SOURCE DISCOVERED AT A TRANSFER STATION The following information was excerpted from a Commonwealth of Massachusetts facsimile: A radiation source was detected in a trash load at the Roxbury Transfer Station (RTS) by radiation detectors at the transfer station entrance. The RTS consultant performed a survey to separate the radiation source from the remainder of the trash. The consultant transported radioactive trash to Atlantic Nuclear (MA license #56-0477) to perform isotope identification. Atlantic Nuclear' s analysis indicates the radiation source contains about 90 microCuries of Ra-226. A dose rate of 15 millirem/hour was measured at about 1 inch from the object. The consultant separated the single object from the trash bag. The source is stored at Atlantic Nuclear and is waiting for proper disposal. The Agency [Massachusetts Radiation Control Program] continues to investigate and considers this event to be open. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-04-23
50985 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2015-04-15 04:11 | 2015-04-15 07:32 | 2015-04-15 | MANUAL REACTOR TRIP DUE TO THE LOSS OF A CONDENSATE PUMP "At 0411 EDT on April 15, 2015, Beaver Valley Power Station (BVPS) Unit 1 manually tripped the reactor from approximately 85% power due to the trip of a condensate pump. The unit was performing an emergent power reduction due to a degraded condensate pump prior to the manual reactor trip. An end of cycle Tave coastdown was in progress at the time of the event. All control rods fully inserted into the core. All three auxiliary feed water pumps started as expected and were subsequently secured in accordance [with] station procedures. The main feedwater system remains available and in service. The unit is currently stable in Mode 3. "Unit 2 was unaffected and remains at full power." Decay heat removal is via main feedwater system with steam discharge to the main condenser via the steam bypass valves. Unit 1 is in a normal shutdown electrical lineup. No primary or secondary reliefs or safeties lifted during the transient. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-04-15
50984 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2015-04-14 19:20 | 2015-04-15 02:07 | 2015-04-15 | OFFSITE NOTIFICATION DUE TO SODIUM HYDROXIDE SPILL ONSITE EXCEEDING REPORTABLE QUANTITY "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "Arizona Public Service Co. made an offsite notification to the National Response Center regarding an approximately 3500 gallon caustic (8% sodium hydroxide) spill due to an improper valve lineup. The spill occurred at the Water Reclamation Facility (produces water for cooling towers and power plant and is located outside the Security Owner Controlled Area) in the area of the Fire Protection tanks (additional liquid was contained in a containment structure at the release location, and in a nearby concrete lined storm ditch on site). The release has been isolated, the immediate area has been barricaded. The quantity released exceeded the Reportable Quantity for sodium hydroxide (RQ of 1,000 pounds) and was therefore reported. Additionally, the state [Arizona] and county [Maricopa] have also been notified. There was no impact to the operation of the power units, aquifer or personnel onsite or offsite. "The NRC Resident [Inspector] has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Defueled | Power Operation | Power Operation | Defueled | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-04-15
50983 | -1 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2015-04-14 10:00 | 2015-04-14 11:44 | 2015-04-14 | Y-90 MICROSPHERE DOSE LESS THAN PRESCRIBED A medical event involving Y-90 microspheres (TheraSpheres) occurred at approximately 1000 EDT on 4/14/15. The prescribed dosage was 34.6 mCi and the delivered dosage was 25.5 mCi. This equates to a 26.3 percent underdose. The patient was notified by the authorized user following treatment and before discharge on 4/13/15. The referring physician was notified by the authorized user via electronic mail at 1149 EDT on 4/13/15. The initial hypothesis on cause may have been related to difficult access to an anatomical region in the liver, resulting in the need to use lower than normal pressure on the syringe used for microsphere delivery. All established administration procedures were followed. A written report to the appropriate NRC offices will follow within 15 days. * * * RETRACTION FROM MACK RICHARD TO VINCE KLCO ON 4/14/15 AT 1515 EDT * * * The following information was excerpted from the licensee email: "The reason for this retraction is based upon discussions with the Authorized User [AU] who performed the Y-90 treatment and additional questions raised and clarifications made by the NRC Region III Office. During that discussion, the AU indicated that he utilized a lower syringe pressure than normal to prevent reflux of the Y-90 microspheres which would have resulted in a less than optimal treatment. The AU acknowledged that the amount administered was acceptable, given the need to use the lower syringe pressure and that he will modify the written directive to appropriately reflect a change in the written directive based upon those circumstances." Notified the R3DO (McCraw) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-04-22
50982 | 0 | ST VINCENT HOSPITAL AND HEALTH CENT |  |  |  |  | 2015-04-13 08:42 | 2015-04-13 14:51 | 2015-04-13 | DUMMY WIRE JAMMED DURING BRACHYTHERAPY TREATMENT A patient was receiving brachytherapy treatment using a SAVI device that used 11 channels. The patient was treated with 2 channels when the dummy wire jammed in the out position. The patient was prescribed a fractional dose 340 cGy, but received only received 60 cGy. There are no adverse effects expected to the patient. The prescribing physician has been informed. The licensee has contacted a company to repair the device and has ceased all operations until repairs can be made. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-04-21
50981 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-13 02:20 | 2015-04-13 09:56 | 2015-04-13 | MANUAL REACTOR SCRAM INITIATED "Following a pre-planned scram for entry into the U2 Refueling Outage, the 'B' Reactor Protection system (RPS) was unable to be reset due to a deficiency with the '2H' Intermediate Range Power Monitor. Due to this failure to reset RPS, a manual full scram was initiated as required by plant procedures." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-04-13
50980 | -1 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-12 12:40 | 2015-04-12 22:06 | 2015-06-02 | SAFEGUARDS REPORT - DISCOVERY OF A VULNERABILITY OF A SAFEGUARD SYSTEM The licensee discovered a vulnerability of a safeguard system that could have allowed undetected access to a controlled access area for which compensatory measures were not employed. The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM SHAWN KIRVEN TO DANIEL MILLS ON 6/2/15 AT 1052 EDT * * * The licensee determined that the discovered vulnerability should not have been reported per Generic Letter 91-03. Notified R4DO (Whitten) and 73.71 Safeguards Group (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-04-12
50979 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2015-04-12 18:00 | 2015-04-12 20:51 | 2015-06-01 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "The purpose of this report is to provide a telephone notification under 10 CFR 50.72(b)(3)(v)(D) to notify the NRC of a temporary loss of the Control Room Envelope (CRE) boundary. The safety function of the CRE boundary is to ensure the in-leakage of unfiltered air into the CRE will not exceed the in-leakage assumed in the licensing basis analysis of design basis accident (DBA) consequences to CRE occupants. In addition to an intact CRE boundary maintaining CRE occupant dose from a large radioactive release below the calculated dose in the licensing basis consequence analysis for DBAs, it also ensures the occupants are protected from hazardous chemicals and smoke. "The loss of the CRE boundary was due to a failed latching mechanism for a CRE boundary door used for normal passage of personnel into and out of the CRE. The failure of the door to latch as designed is considered a condition that could have prevented the fulfillment of a safety function at the time of discovery, and is therefore reportable as required by paragraph 50.72(b)(3), 'Eight-hour reports.' "Procedural controls have restored the safety function of the CRE boundary by mechanically locking the subject door in the closed position through the use of a specifically designed mechanical strong-back until a permanent repair is made. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM MARK HAWES TO JOHN SHOEMAKER AT 1642 EDT ON 6/1/15 * * * "The main control room corridor fire door (76FDR-A-300-10) was found to not be able to latch. The latch was stuck in the latch mechanism because the latch bolt was bent. The latch was replaced on 4/15/2015. "The Control Room Emergency Ventilation Air Supply System (CREVAS) provides a protected environment from which occupants can control the plant following an uncontrolled release of radioactivity, hazardous chemicals, or smoke. The Control Room Envelope (CRE) is the physical boundary around the CREVAS environment. The Operability of the CRE boundary depends on its ability to minimize in-leakage of unfiltered air such that after a design bases accident a habitable environment can be maintained for 31 days without exceeding 5 rem whole body dose or its equivalent to any part of the body. "The control room is normally pressurized greater than the 0.125 inches water gauge. This causes air to leak out rather than allowing infiltration of air from surrounding areas into the CRE boundary. The pressurized control room pushes this door (76FDR-A-300-10) outward, toward the open direction; however, even though the latch to the door did not work the door was still able to close. The closed door minimized in-leakage and a positive differential pressure was maintained in the control room during this event. These doors are kept closed against the door seals primarily by the closure mechanism. The latch is a secondary means of ensuring that the doors remain closed as well as a means to control personnel access to the control room. "The Control Room Envelope (CRE) remained Operable with this deficiency and there was no loss of safety function per 10 CFR 50.72(b)(3)(v)(D). The original notification may be retracted." The licensee has notified the NRC Resident Inspector. Notified the R1DO (Powell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-04-12
50978 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-04-12 12:50 | 2015-04-12 16:01 | 2015-04-12 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED OFFSITE DUE TO HEAT EXHAUSTION "On 4/12/2015 at approximately 1230 CDT, an Xcel Energy employee performing activities in the drywell (currently shut down for a planned refueling outage), experienced heat exhaustion. Upon discovery, the plant emergency medical team was dispatched to aid the individual. The individual was immediately transported, via ambulance, to a local hospital for treatment without verification that no contamination existed. Accompanying the individual were two (2) radiation protection individuals. The individual was transported out of the Protected Area at approximately 1250 CDT. Because the potentially contaminated individual could not be surveyed prior to being transported offsite, the individual was considered potentially contaminated. As such, this event is being reported as an 8-hour prompt report pursuant to 10 CFR 50.72(b)(3)(xii). "On 4/12/2015 at approximately 1340 CDT, the radiation protection personnel that accompanied the individual to the medical facility reported that the individual, ambulance, gurney, hospital travel path and exam room were determined not to be contaminated. As a result, no follow-up status report is planned. "The licensee notified the NRC Resident Inspector." The licensee will be notifying the State Duty Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2015-04-20
50977 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2015-04-11 21:00 | 2015-04-11 22:15 | 2015-04-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO SAFETY INJECTION TANK OUTLET PIPING LEAK "During investigation of a small leak on the 2B2 Safety Injection Tank inside Saint Lucie Unit 2 containment, a through wall flaw was identified on Class 2 piping associated with the 2B2 Safety Injection Tank. The 2B2 Safety Injection Tank was declared inoperable on April 11, 2015 at 1204 EDT and Unit 2 entered a 24-hour shutdown action statement for Technical Specification 3.5.1.b. On April 11, 2015 at 2100 EDT, Unit 2 initiated a plant shutdown in compliance with Technical Specifications. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(i)" The electrical grid is stable and no safety-related equipment that would affect a safe shutdown was out of service at the time of the report. The licensee has notified the NRC Resident Inspector. | 0 | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2015-04-11
50976 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-11 09:58 | 2015-04-11 11:23 | 2015-04-11 | DRYWELL LEAKAGE POINT IDENTIFIED "On 4/11/15, Unit 2 drywell entry was performed during a planned Unit 2 refueling inspection outage. At 0958 EDT, the licensee identified leakage from a weld on the 3/4 inch seal vent piping connected to the 2A reactor recirculation pump seal area. The location is within the reactor recirculation loop isolation valves, therefore it is isolable from the reactor vessel. The piping is ASME Class 2 and is a reactor coolant pressure boundary. The reactor was in mode 3 at the time of discovery. "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii)(A)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-04-11
50975 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-04-09 12:05 | 2015-04-11 08:04 | 2015-04-20 | SAFEGUARDS REPORT FOR INADEQUATE COMPENSATORY MEASURES Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been properly employed. The licensee notified the Region IV Duty Officer and will be notifying the NRC Resident Inspector. * * * RETRACTION FROM MARCY BLOW TO CHARLES TEAL AT 1400 EDT ON 4/20/15 * * * This event has been retracted. The NRC Resident Inspector has been notified. Notified the R4DO (Drake) and 73.71 Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | KS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-04-11
50974 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-11 00:51 | 2015-04-11 05:22 | 2015-04-11 | SECONDARY CONTAINMENT INOPERABLE DUE TO FAILURE OF RUNNING FANS "On April 11, 2015 at 0051 EDT, Secondary Containment became inoperable requiring a Technical Specification 3.6.4.1 entry for failure to meet SR [Surveillance Requirement] 3.6.4.1.1 on Unit 1 and Unit 2, loss of required differential pressure. "The inoperability was caused by a loss of normal Zone 2 differential pressure due to loss of running fans and failure to start of standby fans. The cause is being investigated. "Engineering and maintenance personnel implemented a Temporary Engineering Change, which allowed restoration of one set of fans and dampers. Normal secondary containment differential pressure was restored. Technical Specification 3.6.4.1 was exited at 0320 EDT. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system. "The NRC Resident Inspector was notified." Temporary Engineering Change consisted of removing air to a previously running fan discharge damper so it would close and allow standby fans to start. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-04-11
50973 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-10 23:46 | 2015-04-11 01:52 | 2015-04-11 | AUTOMATIC REACTOR SCRAM CAUSED BY MAIN TURBINE TRIP DUE TO DEGRADING MAIN CONDENSER VACUUM "At 2346 EDT on April 10, 2015, Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed due to a main turbine trip caused by loss of turbine steam seals and degrading main condenser vacuum. "Unit 2 reactor was being shutdown for a refueling outage. At approximately 37 percent power, turbine steam seals were lost resulting in a degrading vacuum. The vacuum degraded quickly, resulting in a main turbine trip before the reactor operator could insert a manual scram. At 37 percent power, the turbine trip caused an automatic scram. This occurred during a transfer from normal steam seal supply to the auxiliary boiler supply. All control rods [fully] inserted. Reactor water level lowered to +2 inches causing Level 3 (+13 inches) isolation. No ECCS actuations occurred. The Operations crew subsequently maintained reactor water level at the normal operating band using RCIC [Reactor Core Isolation Cooling]. No steam relief valves opened. The reactor recirculation pumps tripped on EOC-RPT due to the turbine trip at power. "The reactor is currently stable in Mode 3. Investigation into the cause of the loss of turbine steam seals is underway. "The NRC Resident Inspector was notified. A voluntary notification to PEMA [Pennsylvania Emergency Management Agency] and press release will occur." Unit 2 is in a normal shutdown electrical lineup. Turbine steam seals were restored to the normal steam supply and condenser vacuum was restored. Decay heat is being removed via the steam bypass valves to the condenser. Unit 2 is proceeding with their cooldown to support the scheduled refueling outage. | 0 | 0 | 0 | 0 | 37 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-04-11
50972 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2015-04-10 | 2015-04-10 14:39 | 2015-04-10 | AGREEMENT STATE REPORT - RADIUM-226 SOURCE FOUND IN LOAD OF SCRAP METAL The following report was provided by the Massachusetts Radiation Control Program via email: "The Agency [Massachusetts Radiation Control Program] provided an on-site response to Turner, Inc., Lynn, MA, a scrap metal facility that had previously received a source back from Prolerized, another scrap metal facility in Everett, MA. "The source was originally detected by a radiation detector at the Prolerized site where the dose rate of the source, shielded by scrap metal in a truck, was measured to be 0.1 mrem/hr inclusive of a background of 0.05 mrem/hr. "The Agency surveyed the source at the Turner, Inc. site with a multi-channel analyzer and identified the source to contain radium-226 with a contact dose rate of 113 mrem/hr. The detector of the analyzer was approximately 1 cm from the source. Based upon the survey performed, the source contains approximately 15 microCuries of radium-226 and therefore is immediately reportable in accordance with 105 CMR 120.281(A)(1). "The source is rectangular and measures approximately 7.5 mm length by 2.5 mm width and height and is without any observed marking or serialization. The source might be of type used for calibration of a liquid scintillation counter. "The source is in a plastic bag, inside a container that is segregated, secured and shielded from workers at the scrap metal facility. "Turner, Inc. had obtained the services of a radiation safety consultant who had originally isolated the source from the truck and secured the source at Turner, Inc. Exposures, if any, to the public and workers from the source are negligible due to the storage location and interposed shielding. "The Agency continues to investigate and considers this event to be open." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-04-20
50971 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-04-09 | 2015-04-09 16:44 | 2015-04-09 | AGREEMENT STATE REPORT - STUCK SHUTTER ON FIXED INDUSTRIAL GAUGE The following was received from the State of Florida via email: "The RSO for Georgia-Pacific Corporation, Palatka, Florida called to report a fixed Cesium-137 source installed on a tank has the shutter stuck open. The device is 936 mCi [Cesium-137], Kay-Ray Sensall Model 7063P. It is located in the overhead in an isolated area. "They were in the process of conducting an inspection and leak test of the device when it was discovered. The last time the shutter was cycled was last year. The RSO reports there is no over exposure of personnel, no leaks. The location of device prohibits access to personnel so there is no chance of accidental exposure. "The area has been posted and a work order has been submitted to replace/repair the device." Florida Incident Number: FL15-035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-04-17
50970 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-04-09 05:40 | 2015-04-09 14:25 | 2015-04-09 | OFFSITE NOTIFICATION DUE TO ON-SITE EMPLOYEE FATALITY "On April 9, 2015, a NOG-L [Nuclear Operations Group - Lynchburg] employee passed away shortly after arriving to work. The employee arrived to work at 0534 [EST]. He proceeded to his work center and collapsed at 0540 while clocking in. CPR was administered to the employee by a co-worker who was at the scene and the site Emergency Team was called. The Emergency Team arrived in three minutes and used an AED to attempt to resuscitate the employee. At 0555, the Emergency Team transported the employee in our onsite Advanced Life Support ambulance to Lynchburg General Hospital (arrived 0623). CPR was maintained in transit to the hospital. The employee was pronounced dead at the hospital from an apparent heart attack. "NOG-L reported this event to the Occupational Safety and Health Administration (OSHA) at 1110 on April 9, 2015." The Licensee notified the NRC Resident Inspector and will notify the NRC Regional Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2015-04-17
50969 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-08 | 2015-04-08 16:48 | 2015-04-08 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was received from the State of Texas via email: "On April 8, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee's site radiation safety officer (RSO) of a source disconnect. The RSO stated a radiography crew had contacted him [from a field site in Charco, TX] and informed him that after the first exposure of a 62.2 curie Iridium - 192 source, they could not retract the source back into a QSA 880D exposure device. The RSO stated he arrived at the site and found dose rates at the boundaries to be less than 0.5 millirem per hour. The RSO, who is on the license to retrieve a source, detached the guide tube from the camera and using a pair of tongs, lifted the collimator and the source slid out on the ground. The RSO placed bags of lead over the source. The RSO cranked the drive cable through the camera and connected the drive cable to the source. The RSO then retracted the source into the camera locking it in place. The RSO stated he inspected the camera and crankout device in the field and could not find any cause for the disconnect. The maximum dose during the event was received by the RSO who received 24 millirem to his hand and 16 millirem to his chest. "No member of the general public was exposed as a result of this event. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-04-16
50968 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2015-04-08 03:30 | 2015-04-08 11:40 | 2015-04-08 | REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE IDENTIFIED "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "At approximately 0030 [MST] on April 7, 2015, while performing planned routine visual examinations of Unit 3 components, the differential pressure instrumentation nozzle on the suction side of the 2A reactor coolant pump (RCP) was observed to have white deposits that appeared to originate at the nozzle penetration. At this time, no additional indications of leakage have been identified for other inspected reactor coolant pressure boundary nozzles. "Following insulation removal, the piping was examined by qualified engineering personnel. At 0330 [MST] on April 8, 2015, it was determined, based on isotopic analysis, that the white residue is consistent with reactor coolant system fluid. Technical Specifications Limiting Condition of Operation (LCO) 3.4.14 permits no reactor coolant system pressure boundary leakage and therefore, the discovery of leakage from the nozzle is a degradation of a principal safety barrier. This notification is being made for a degraded condition pursuant to the requirements of 10 CFR 50.72(b)(3)(ii)(A). "The unit had been shutdown for its 18th refueling outage on 4/3/15 at 0000 [MST]. The NRC Resident Inspectors have been informed of this condition." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-04-08
50967 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2015-03-12 | 2015-04-08 10:10 | 2015-04-08 | AGREEMENT STATE REPORT - TREATMENT UNDERDOSE The following was received from the Commonwealth of Kentucky via email: "On 19 March 2015, the patient was receiving an HDR cylinder treatment using the HDR Ir-192 source for treatment of her vaginal cuff. The prescribing physician inserted the vaginal cylinder in the patient's vagina until resistance was present, indicating the tip of the cylinder had reached the vaginal cuff. Before each treatment is delivered a radiographic image of the inserted treatment device is reviewed to ensure consistent device location across each fraction (this image is not intended as a placement verification for treatment). Comparison of images taken on 19 March 2015 and 12 March 2015, revealed that the cylinder placement during treatment on 12 March 2015, was 3cm distal to the cylinder placement on 19 March 2015, implying the dose delivered during the patient's first treatment on 12 March 2015 was located 3cm distal to its intended location. The effect of relocating the cylinder to a 3cm distal position has the effect of under dosing the vaginal cuff, while providing additional dose to the vaginal wall in an unintended location. The RHB [Kentucky Radiation Health Branch] has requested additional dose information to the vaginal wall area. Some of the vaginal wall is dosed during this procedure just not in this location. The prescribing physician has deemed the additional dose to the vaginal wall as medically insignificant. Vaginal cuff treatments are planned to deliver a prescribed dose to a reference line located 0.5cm outside the cylinder wall. A new treatment plan depicting the true location of the 12 March 2015, treatment has been generated and a comparison of the dose to the reference line has been made to estimate the extent to which the vaginal cuff has been under dosed. The average dose delivered to the vaginal cuff area was 80% lower than intended. Due to the fact that the dose to the vaginal cuff from the first treatment is so low, the physician has decided to ignore the patient's first treatment and change the patient's prescription to deliver the intended dose over the remaining fractions. The authorized user notified the patient upon completion of her treatment on 19 March 2015. Two possible scenarios have been determined to be the most likely cause of the event: "1. The first is that the cylinders used for treatment are segmented. Typically 4 segments are locked together into one larger cylinder. The larger cylinder is then attached to a clamping device that allows the cylinder to be locked into position after the authorized user (AU) inserts the device into the patient. During this particular treatment only 3 segments were used to form the cylinder leaving less space for the clamping device to attach to the cylinder. As the AU was inserting the cylinder, the cylinder clamping device may have pushed up against the patient's perineum prematurely causing resistance to further insertion prompting the AU to believe the cylinder had reached the vaginal cuff. "a. In order to prevent future occurrences from happening, the staff involved will be required to always use all 4 segments when constructing a cylinder. "2. The other possibility is due to the non-compliance of the patient herself. As the cylinder was being inserted, the patient was having a hard time remaining still. Once the cylinder was locked into place, it is possible that the patient pulled away from the cylinder a small amount causing the change in location. This is believed to be the most likely scenario based on the patient's common reaction and motion upon insertion of the cylinder. "a. In order to minimize a patient's ability to adjust the cylinder position, staff will be instructed to pay close attention to the patient's movements and additional imaging of the device location will be taken if movement is a concern. A phone call was made to the KY Radiation Health Branch of the incident with intent to meet the notification requirements to the KY RHB. The Physicist had left a phone message but did not report to a person. There is no record of this message however a record of a phone call is noted received 19 March 2015 at 1450 EDT. Upon receipt of an email to the Radiation office, the required 24 hour notification is made to the NRC Headquarters Operations Officer." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. Kentucky Incident # 150002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2015-04-16
50966 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-04-07 17:45 | 2015-04-07 22:33 | 2015-04-07 | INADVERTENT EMERGENCY SIREN ACTIVATION "At approximately 1833 CDT on April 07, 2015, the licensee was notified by the siren vendor (NELCOM) that Dakota County Dispatch reported an inadvertent activation of an emergency siren (D-1), in Dakota County, MN. The cause of the siren activation is unknown. The siren was deactivated at 1810 CDT after sounding for approximately 25 minutes. The siren vendor (NELCOM) has been contacted to repair the siren. The siren remains out of service. This is the only siren out of service within the 10 mile Emergency Planning Zone (EPZ). "There are 123 Emergency Notification sirens. Of the seven (7) credited sirens in Dakota County, six (6) remain in service. Thus, emergency notification capabilities remain in effect. "NRC Resident has been informed." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-04-07
50965 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-07 11:00 | 2015-04-07 18:50 | 2015-04-07 | INOPERABLE SEISMIC INSTRUMENTATION IDENTIFIED DURING HISTORICAL REVIEW "Luminant Generation Company LLC (Luminant Power) has completed a review of seismic monitor performance at the Comanche Peak Nuclear Power Plant (CPNPP) over the last three years. The CPNPP emergency preparedness plan requires seismic monitoring instruments to diagnose an earthquake for emergency action levels (EAL) HA1.1 seismic event greater than OBE (operating basis earthquake) and HU1.1 identified seismic event that is less than the OBE. The seismic monitor performance review identified one unplanned instance of monitor unavailability and three instances when planned monitor outage durations exceeded 24 hours. Any loss of seismic monitoring capability results in a major loss of assessment capability for the Alert (HA1.1) and a degraded assessment capability for the Unusual Event (HU1.1) emergency classification. The seismic monitor is currently functional, however, it was determined to be non-functional on the following dates: "Unplanned out-of-service: 12/4/2013 through 12/10/2013 Planned out-of-service lasting greater than 24 hours: 5/16/2012 through 5/24/2012 3/20/2013 through 3/27/2013 9/29/2014 through 10/1/2014 "The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). This report is required per 10 CFR 50.72(a)(1)(ii) as an event that occurred within 3 years of the date of discovery. The seismic monitor issues and the missed reporting of the loss of assessment capability have been documented in the CPNPP corrective action program." This review was prompted by a licensee evaluation of industry operating experience. A similar report was received from Limerick Generating Station - EN # 50951. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-07
50964 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-04-07 15:41 | 2015-04-07 17:54 | 2015-04-07 | SECURITY REPORT INVOLVING DEGRADATION IN SAFEGUARDS SYSTEM Degradation in safeguards system that could allow unauthorized access to controlled access area. Compensatory measures taken upon discovery. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-04-07
50963 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-07 | 2015-04-07 17:31 | 2015-04-07 | AGREEMENT STATE REPORT - STUCK SHUTTER ON A FIXED GAUGE The following information was received from the State of Texas via fax: "On April 7, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that they were unable to close the shutter on a Berthold Model LB 300 IRL Type 1 source holder containing three Cobalt - 60 sources. The licensee found the problem during routine checks. The RSO stated they had contacted the manufacturer for assistance. The RSO stated there was no increased risk of exposure to members of the general public or the employees at the facility. This Agency contacted the manufacturer on April 7, 2015 and requested the seal source and device (SSD) data sheet for the device. At 1206 hours [CDT], the Agency received an email from the manufacturer containing the SSD sheet for the gauge. The email also stated the gauge had been repaired and was now operating properly. The specifics of the event were not provided by the RSO as he was still investigating the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-04-15
50962 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-04-07 11:47 | 2015-04-07 16:38 | 2015-04-09 | REACTOR VESSEL HEAD PENETRATION FLAW IDENTIFIED DURING INSERVICE INSPECTION "This is a non-emergency report. "On April 7, 2015, while the Harris Nuclear Plant was shut down for a scheduled refueling outage, the reactor vessel head penetrations were being examined in accordance with Inservice Inspection Program. Ultrasonic examinations identified a flaw in a head penetration nozzle. The unit is in a safe and stable condition. The flaw will be repaired prior to startup from the refueling outage. "The flaw and repair have no impact to the health or safety of the public. "The NRC Resident Inspector has been informed." An extent of condition investigation is on-going. * * * UPDATE AT 1644 EDT ON 4/9/15 FROM JOHN CAVES TO JEFF HERRERA * * * "During the ongoing reactor vessel head penetration examinations, two additional flaws were identified in head penetration nozzles. The unit remains in a safe and stable condition. All of the identified flaws will be repaired prior to startup from the refueling outage. The remaining examinations are in progress to determine the extent of condition. "The NRC Resident Inspector has been notified." Notified R2DO (Heisserer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-04-07
50961 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2015-04-07 12:45 | 2015-04-07 15:45 | 2015-04-09 | DUAL UNIT AUTOMATIC REACTOR TRIPS DUE TO A VOLTAGE TRANSIENT RESULTING IN GENERATOR TRIPS "A loss of Main Generator Load which caused a Reactor Trip on Units 1 & 2. A switchyard voltage transient from a highline occurred, which caused an undervoltage condition on both units' safety related 4KV buses. "Unit 1 is on normal heat removal to the condenser. "Unit 2 is on auxiliary feedwater and normal condenser bypass valves for temperature control. An Auxiliary Feedwater Actuation System (AFAS) actuation occurred on Unit 2. "The [Unit 2] 2B emergency diesel generator did not start and load on its respective 24-4 KV bus. The 24-4KV Bus was repowered from the alternate feeder breaker. Cause of the emergency diesel failure to start is under investigation. "All safety functions are met for both units." All control rods fully inserted. The site is in a normal shutdown electrical configuration powered from offsite. The site plans to stay in Mode 3 pending restart. The licensee notified the NRC Resident Inspector, State and local authorities. A press release is planned. * * * UPDATE FROM JAY GAINES TO DANIEL MILLS AT 0129 EDT ON 4/9/2015 * * * "During post trip review, it was determined that the 21 saltwater pump had to be manually started. With the failure of 2B emergency diesel generator, there were no saltwater pumps running for approximately 12 minutes. Additional troubleshooting determined the 2A emergency diesel generator sequencer did not automatically start 21 saltwater pump. The 2B emergency diesel generator was returned to service on 4/8/2015 at 1730 [EDT]. The loss of saltwater [pump] and emergency diesel generator is reportable as an event that could have prevented fulfillment of a safety function and is also an unanalyzed condition." The licensee has notified the NRC Resident Inspector. Notified R1DO (Ferdas), IRD MOC (Grant), NRR EO (Morris). | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | POT RHR INOP | UNANALYZED CONDITION | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(ii)(B) | 0 | 2015-04-07
50960 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-04-06 17:00 | 2015-04-06 19:11 | 2015-04-06 | UNANALYZED CONDITION DUE TO VOLUME CONTROL TANK ISOLATION TIME ANALYSIS ERROR "On April 6, 2015, Watts Bar determined that the current Unit 1 Fire Protection Report (FPR) analysis for 10 CFR 50, Appendix R contained a non-conservative time for isolation of Volume Control Tank (VCT) following a postulated fire in room 737.0-A1A. Due to multiple fire-induced failures, Component Cooling System (CCS) cooling of letdown flow to the VCT will be lost in conjunction with increased Reactor Coolant System (RCS) injection flow through Reactor Coolant Pump (RCP) seals and Boron Injection Tank (BIT) flowpaths. As a result, VCT temperature and pressure would increase, which could cause RCP seal damage and loss of RCS inventory, and net positive suction head (NPSH) to the Centrifugal Charging Pumps (CCPs) could be lost. In this postulated fire scenario, Thermal Barrier Cooling is also not available due to fire-induced failures. The current FPR analysis assumes a time of 70 minutes for closure of VCT outlet isolation valves. Preliminary analysis performed by TVA showed that VCT outlet isolation is required in approximately 4 minutes. "As a result, Watts Bar Unit 1 is in an unanalyzed condition. This condition significantly degrades plant safety because operator action to isolate the VCT in the event of a postulated fire in room 737.0-A1A would not have been performed in time to prevent RCP seal damage and loss of RCS inventory and eventual loss of NPSH to the CCPs. "Watts Bar is utilizing previously established fire watches in the affected fire areas as a compensatory measure. "This issue is being reported under 10 CFR 50.72(b)(3)(ii)(B), 'unanalyzed condition that significantly degrades plant safety.' "The Watts Bar NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-04-06
50959 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-04-04 | 2015-04-06 14:22 | 2015-04-06 | AGREEMENT STATE REPORT - INABILITY TO RETRACT A RADIOGRAPHY SOURCE TO ITS SHIELDED POSITION The following information was received from the Commonwealth of Pennsylvania via email/fax: "An 84 curie iridium-192 (lr-192) source being housed in a Source Production & Equipment Company (SPEC) 150 industrial radiography camera could not be retracted back into the exposure device. The source eventually was able to be retrieved without any over exposures to either the workers or the general public.. "The cable broke and became dislodged from the gear mechanism within the exposure device itself. The cable was manually pulled to return the lr-192 source to its locked position within the exposure device. It is unknown at this time why the cable broke." PA Event Report ID No.: PA150009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-04-14
50958 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-04-06 | 2015-04-06 15:22 | 2015-04-06 | AGREEMENT STATE REPORT - DENSITY GAUGE BROKEN SHUTTER The following information was received via E-mail: "On April 6, 2015, the licensee radiation safety officer reported that a density measuring device, ThermoFisher Scientific model 5201, with Texas Nuclear Source Cesium-137, 100 millicuries, serial number GV-2806 had a broken shutter. The shutter block is disconnected from the arm. A ThermoFisher Scientific service technician has been contacted and scheduled to repair the gauge at the site. The shutter remains in the closed position until repairs are completed. There is no exposure hazard to any individual. Updates will be provided in accordance with SA300 guidelines." Texas Incident Number: I-9297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-04-14
50957 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-06 08:09 | 2015-04-06 09:09 | 2015-04-08 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED MAINTENANCE "On 04/06/2015, planned preventive maintenance activities are being performed on the Braidwood Generating Station Technical Support Center (TSC) Ventilation System. The work will be completed within approximately 42 hours. This activity includes preventive maintenance on the TSC condensing unit which affects the TSC ventilation. During the planned maintenance, the TSC condensing unit will be rendered non-functional. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff as necessary. This planned maintenance will not impact the emergency filtration capability of the TSC. "This event is reportable per 10CFR50.72(b)(3)(xiii) for 'any event that results in a major loss of emergency assessment capability.' The planned maintenance will not be able to restore the TSC condensing unit to service within the facility activation time specified in the emergency plan (1 hour) in the event of an accident. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM GREG HARNOIS TO JOHN SHOEMAKER AT 1013 EDT ON 4/8/15 * * * "The TSC ventilation system has been restored to normal operation as of 0600 CDT on April 8, 2015. "The NRC Resident Inspector has been notified." Notified R3DO (Skokowski). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-06
50956 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-05 15:37 | 2015-04-05 16:06 | 2015-04-05 | ALERT DECLARED DUE TO FIRE IN MOTOR CONTROL CENTER "An Alert was declared due to a fire in a Unit 2 Division 2 Safeguard [250 volt] DC Motor Control Center. This has made the High Pressure Core Injection system inoperable and unavailable. The fire is out. The emergency response organization has been activated and investigation / repair planning will commence. Unit 2 is stable with no other system affects." The fire was extinguished by on-site personnel. No off-site responders were required. The Reactor Core Isolation Cooling system remains operable. A Fire Watch has been stationed to monitor for fire reflash. There were no injuries resulting from this event. There was no effect on Unit 1. The licensee notified the NRC Resident Inspector and State and local government agencies. Notified the following organizations: DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, FDA EOC, FEMA NWC, and Nuclear SSA. * * * UPDATE FROM DAN BOYLAN TO DONALD NORWOOD AT 1812 EDT ON 04/05/15 * * * The Alert was terminated at 1742 EDT. The licensee notified the NRC Resident Inspector and State and local government agencies. Notified R1DO (Kennedy), IRD (Gott), and NRR EO (Morris). Notified the following organizations: DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, FDA EOC, FEMA NWC, and Nuclear SSA. | 0 | 82 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-04-05
50955 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-04-05 08:52 | 2015-04-05 13:55 | 2015-04-05 | LOSS OF BOTH PRIMARY AND BACKUP METEOROLOGICAL TOWERS DUE TO PARTIAL LOSS OF 25kV POWER DISTRIBUTION "At 0852 CDT on 04/05/2015, a partial loss of the 25kV Plant Support Power Distribution System caused a loss of both the Primary and Backup Meteorological Towers at Comanche Peak Nuclear Power Plant. Loss of both Meteorological Towers constitutes a major loss of emergency assessment capabilities in regard to meteorological conditions. "The 25kV Plant Support Power Distribution System feeds certain non-safety related equipment and does not affect plant operation. "An investigation into the cause of the loss of power is in progress." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-05
50954 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-04-04 11:51 | 2015-04-05 06:58 | 2015-04-10 | UNPLANNED CONTAMINATION EVENT "On April 4,2015, at approximately 1151 [EDT], a chemical reaction occurred in a 2-liter bottle of cleanup materials. The bottle was located in a storage rack. The chemical reaction caused the bottle to breach, releasing some of the contents into the immediate area around the storage rack. There were no individuals in the area where the bottle was stored when the breach occurred. The area has been roped off and is in the process of being cleaned up. There were no personnel injuries or exposures. The event is currently being investigated. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM RANDY SHACKLEFORD TO HOWIE CROUCH AT 1257 EDT ON 4/10/15 * * * The licensee is also making a courtesy notification for an unplanned chemical reaction in accordance with Information Notice 97-23. Additionally, on April 7, 2015, the area was cleaned up and access restrictions were removed. The licensee notified the NRC Resident Inspector. Notified R2DO (Heisserer), NMSS EO (Habighorst), IRD (Grant) and NMSS Events Notification (E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2015-04-16
50953 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-04-03 16:31 | 2015-04-03 19:37 | 2015-04-03 | LIQUID PENETRATION EXAMINATION RESULTS IN INDICATION ON REACTOR VESSEL HEAD PENETRATION "On April 3, 2015, during the Braidwood Station Unit 1 refueling outage (A1R18), an in-service Liquid Penetration examination was performed on the previously repaired control rod drive mechanism (CRDM) penetration 69. During the examination on the weld build up for CRDM penetration 69, a 3/8 inch rounded indication was discovered located at 0 degrees on the reactor head portion of the weld build up, and it is 4 inches from the transition of the head to penetration. 0 degrees is located at the outermost portion of the penetration on the flange side. The transition is the point where the vertical portion of the penetration meets the horizontal area of the reactor head. "Rounded indications that exceed 3/16 inch are rejectable per ASME Code Case N-729-1. "This is reportable pursuant to 10CFR50.72(b)(3)(ii)(A), 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded' since the as found indication did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-1 to remain in-service without repair. "The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2015-04-03
50952 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2015-04-03 15:00 | 2015-04-03 14:17 | 2015-04-03 | TECHNICAL SUPPORT CENTER VENTILATION NONFUNCTIONAL DURING PREPLANNED MAINTENANCE "On April 3, 2015, at 1500 EDT, the Control Room Emergency Ventilation System on St. Lucie Unit 1 will be declared inoperable due to pre-planned maintenance during the current refueling outage. The Technical Support Center (TSC) ventilation system is part of the Unit 1 Control Room Emergency Ventilation System, therefore, the TSC ventilation system has been rendered non-functional during the course of the work activities. The TSC ventilation is expected to be returned to service in approximately 24 hours. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. Should the TSC become uninhabitable, the TSC staff will relocate to an alternate TSC location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72 (b)(3)(xiii) due to the potential loss of an emergency response facility. An update will be provided once the TSC ventilation system has been restored to normal operation. "The NRC Resident Inspector has been notified." * * * UPDATE PROVIDED BY DAVE FIELDS TO JEFF ROTTON AT 2240 EDT ON 4/03/2015 * * * "The TSC ventilation system has been restored to normal operation as of 2230 EDT on April 3, 2015. The NRC Resident Inspector has been notified." Notified R2DO (Walker). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-03
50951 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-04-03 10:00 | 2015-04-03 11:54 | 2015-04-03 | INOPERABLE SEISMIC INSTRUMENTATION IDENTIFIED DURING HISTORICAL REVIEW "Limerick Generating Station (LGS) has completed a review of recent seismic monitor performance. The seismic monitor is currently capable of fulfilling its emergency assessment support function. The review of the system performance over the last three years identified two occasions when the system was degraded and incapable of performing its emergency assessment support function such that emergency classification at the UNUSUAL EVENT and ALERT levels could not be declared within fifteen minutes as required with site instrumentation. The seismic monitor was determined to be degraded and incapable of performing its emergency assessment support function on the following dates: 1) January 17, 2014 - Unit 1 100% power, Unit 2 97% power 2) March 22, 2014 - Unit 1 Refueling, Unit 2 100% power "These unplanned inoperable conditions of the seismic monitor were entered into the LGS Corrective Action Program (CAP) when they occurred. "While Exelon procedural direction allowed the use of offsite sources to obtain seismic data when the seismic monitor is incapable of assessing emergency plan Emergency Action Levels (EALs), this was not explicitly referenced in the approved EALs. The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). This report is required per 10 CFR 50.72(a)(1)(ii) as an event that occurred within 3 years of the date of discovery." For the two dates above, the 1/17/14 failure was related to function of the system CPU (central processing unit) and the 3/22/14 failure was due to a failed instrument backup battery. There was no seismic event on either of these two dates. The licensee informed the NRC Resident Inspector. | 100 | 82 | 0 | 100 | 82 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-03
50950 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-04-03 06:52 | 2015-04-03 10:12 | 2015-04-03 | MANUAL REACTOR SCRAM DUE TO LOSS OF MAIN FEEDWATER PUMP "On April 3, 2015 at 0652 CDT, the Unit 2 reactor was manually tripped while operating at 100 percent power due to a lockout trip of 21 Main Feedwater Pump as required by the annunciator response procedure for the lockout alarm. This also resulted in a turbine trip. The crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. The manual trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels have been returned to normal. The auxiliary feedwater pumps have subsequently been secured and returned to automatic. Steam generators are being supplied by 22 Main Feedwater Pump and decay heat is being removed by the condenser steam dump system. "The cause of 21 Main Feedwater Pump trip has been determined to be a failed suction pressure switch. "There was no effect on Unit 1 as a result of this trip. The health and safety of the public and site personnel were not at risk at any time during this event. "The NRC Senior Resident Inspector has been notified." The licensee plans to issue a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-04-03
50949 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2015-04-02 21:33 | 2015-04-03 01:32 | 2015-04-03 | MANUAL REACTOR SCRAM DUE TO STEAM LEAK "On April 2, 2015 at 2133 CDT, a manual scram was inserted on Unit 1 following discovery of a steam leak in the Turbine Building at the D-ring, near the Turbine Bypass valves. Following the reactor scram, reactor water level decreased to approximately -2 inches, which resulted in an automatic Group II and Group III isolation (expected response). The steam leak was isolated by manual closure of the Main Steam Isolation Valves. All systems responded properly to the event. Unit 1 remains in Mode 3, with cooldown in progress. Reactor water level is in the normal level band. The cause and details of the event are under investigation. Unit 2 was unaffected by the event and remains at 100 percent power." Operators reduced reactor power to 20 percent before initiating a SCRAM. All rods fully inserted and the reactor is shutdown and stable. The electrical supply is in a normal shutdown lineup. The reactor is being supplied by normal feedwater, and decay heat is being controlled by use of the ADS valves. The licensee is currently cooling down and depressurizing the reactor in preparation for repair of the steam leak. The licensee has notified the NRC Resident Inspector and the State of Illinois Resident Inspector. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-04-03
50948 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-04-02 12:30 | 2015-04-02 17:29 | 2015-04-02 | SEISMIC MONITOR NOT AVAILABLE FOR EMERGENCY PLAN ASSESSMENT "Northern States Power Company - Minnesota (NSPM) has completed a review of seismic monitor performance at the Prairie Island Nuclear Generating Plant (PINGP) over the past 3 years. The emergency preparedness plan requires seismic monitoring instruments to diagnose an earthquake for emergency action levels (EAL) HA1.1 (Seismic Event Greater Than Operating Basis Earthquake (OBE) as indicated by 'OBE Exceedance' alarm on Seismic Monitoring Panel) or HU1.1 (Earthquake felt in plant as indicated by Valid 'Event' alarm on Seismic Monitoring Panel). Contrary to that requirement, this review identified 6 unplanned instances where the seismic monitor was non-functional that were not previously reported, and 3 planned instances where the seismic monitor was non-functional for greater than 24 hours that were not previously reported. Since there was no compensatory measure that could be credited when the seismic monitor was non-functional, an emergency classification at the ALERT or UNUSUAL EVENT level could not be obtained with site instrumentation for a seismic event. "The seismic monitor is currently functional, however it was determined to be non-functional on the following dates: Unplanned out of service: 1. August 14, 2012 2. November 16, 2012 3. November 18 2012 4. November 21, 2012 5. December 5, 2012 6. January 16, 2013 Planned greater than 24 hour out of service: 1. December 14, 2012 2. September 3, 2014 3. September 30, 2014 "The unplanned non-functional conditions of the seismic monitor have been corrected and were entered into the NSPM Corrective Action Program. "The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). This report is required per 10 CFR 50.72(a)(1)(ii) as an event that occurred within 3 years of the date of discovery. "Corrective actions are in progress to address the missed reporting of seismic monitor unavailability." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-02
50947 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2015-04-02 01:49 | 2015-04-02 10:48 | 2015-04-02 | LOSS OF METEOROLOGICAL SYSTEM DUE TO LIGHTNING STRIKE "At 0149 CDT on 4/2/2015, Cooper Nuclear Station received an alarm indication that the primary and backup Meteorological System (MET) had gone off-line as a result of a lightning strike on the MET tower. This resulted in a major loss of emergency assessment capabilities in regard to meteorological conditions. Technicians responded to the plant and restored the system at 0418 CDT. Loss of the MET system is considered a major loss of emergency assessment capability and is reportable under 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-02
50946 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2015-04-02 04:26 | 2015-04-02 06:55 | 2015-04-02 | MANUAL REACTOR TRIP DUE TO MAIN GENERATOR VOLTAGE REGULATOR FAILURE "On April 2, 2015 at 0426 EDT, the Unit 1 reactor was manually tripped while operating at 100 percent power due to a failure of the main generator voltage regulator. This also resulted in a turbine trip. The operations crew entered the reactor trip procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. This reactor protection system actuation is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated as designed and provided makeup flow to the steam generators. The automatic start of the Auxiliary Feedwater pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 1 is in a normal shutdown electrical lineup. "The NRC Resident Inspectors have been notified. The Louisa County Administrator will be notified." There was no effect on Unit 2 as a result of this trip. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-04-02
50945 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2015-04-01 14:40 | 2015-04-01 18:53 | 2015-04-01 | LOSS OF EMERGENCY OPERATING FACILITY ELECTRICAL POWER AND PHONE SYSTEM "At 1210 CDT the transformer supplying power to the Emergency Operating Facility (EOF) stopped working due to the failure of a capacitor bank. The EOF is located adjacent to OPPD's [Omaha Public Power District] North Omaha facility, approximately 17 miles south of Fort Calhoun Station. The event caused a small grass fire which was quickly extinguished. The local fire department was called. The backup emergency diesel generator for the EOF started and supplied power to the facility, as designed. With the EOF diesel operating, the facility is able to function as required during emergency conditions. "At 1440 CDT the EOF emergency diesel generator stopped running. At 1545 CDT the Conference Operations (COP) network phone system failed. The COP network is the primary emergency notification system between OPPD, state and county agencies. It is used to provide initial and updated notifications and for general information flow between these agencies. Alternate means of communication have been established (commercial lines) and a dedicated communicator is stationed in the control room to ensure that we can facilitate communication should the need arise. "Power to the EOF was restored at 1713 CDT. At time 1720 CDT the COP tested as normal." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-04-01
50944 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-03-30 11:00 | 2015-04-01 13:26 | 2015-04-01 | AGREEMENT STATE REPORT - LOSS OF CONTROL OF MOISTURE/DENSITY GAUGE The following report was received from the State of California Department of Public Health via email: "This is to report a nuclear gauge was 'lost' by the licensee, but was found by the licensee within a couple of hours at the jobsite where it was being used. The gauge was not damaged. "At 1334 PDT on March 30, 2015, the Department [State of California Department of Public Health] was notified by the corporate RSO [Radiation Safety Officer] that a nuclear gauge (Troxler model 3440, serial number 18204, containing 8 mCi Cs-137 and 40 mCi Am-241:Be) could not be found by the licensee. The gauge user reported he had driven from a job site at the corner of Fairview Road and Walkabout Drive to the McDonalds at 1607 Panama Lane in Bakersfield which is about 1 mile away. When he returned to his truck, he noticed the tailgate was down and the gauge/transport case were missing. The gauge user drove back to the jobsite and looked to see if the gauge had fallen off of the truck when he had driven to McDonalds. He did not see it on the roadside. He returned to the jobsite and found the transport case with no gauge inside. He looked around the jobsite and did not see the gauge near where he had been working. He asked others on the jobsite if they had seen the gauge, but no one had. The gauge user drove back to the McDonalds one more time and still did not see a gauge along the roadside. The Bakersfield police and the Department were notified that they had lost a gauge. "At 1452 PDT on the same day, the Bakersfield police emailed [the Department] stating the licensee had found the gauge. [The Department] confirmed this with the licensee. The RSO had gone to the jobsite himself and had found the gauge in a culvert on the jobsite. At this point no one knows how the gauge ended up in the culvert. The gauge is now back in the possession of the licensee and does not show any damage. The gauge user was counseled for not keeping control over the gauge and retraining will be given to all gauge users regarding control and security of the gauge when in use and when it is not in use." California Report Number: 033015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-04-09
50943 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-03-31 15:09 | 2015-03-31 18:29 | 2015-03-31 | UNANALYZED CONDITION DUE TO DEGRADED TORUS COATING "The issue described in this report was addressed during the station's most recent refueling and maintenance outage in October of 2014 and no longer exists. "During an inspection of Suppression Pool (torus) during the October 2014 outage, degradation of the torus coating was discovered. Some of the coating had become delaminated. NextEra Energy DAEC [Duane Arnold Energy Center] took immediate action to restore the coating to within design parameters during the refueling outage and the degraded condition no longer exists. Extensive analysis was performed to determine effect of the delaminated material. Upon completion of this investigation, NextEra Energy DAEC has determined an unanalyzed condition existed as a result of the coating degradation and is reporting the condition under 10 CFR 50.72(b)(3)(ii)(B). "A root cause evaluation has been performed to determine causes and corrective actions. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-03-31
50942 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-03-27 | 2015-03-31 14:33 | 2015-03-31 | AGREEMENT STATE REPORT - FIXED GAUGE STUCK SHUTTER The following was received from the State of Texas via email: "On March 31, 2015 the Agency [Texas Department of State Health Services] was notified by the radioactive materials reciprocity coordinator that it received a notice of an engineering company scheduled to complete work on a nuclear source stuck shutter. The licensee [Westlake Longview Corporation] was called without contact. A message was left on voicemail. The engineering company was contacted and stated that it was hired to complete work on a sealed source gauge for level measurements due to a stuck shutter. The item is a Ronan Model 4F6S, Cs-137, 40 mCi, Serial Number M7352. The investigation into this case is ongoing. Further updates will be provided in accordance with SA 300 guidelines." Texas Incident # I-9293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-04-08
50941 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-03-30 17:30 | 2015-03-31 14:33 | 2015-03-31 | AGREEMENT STATE REPORT - IRRADIATOR STUCK SOURCE The following was received from the State of Texas via email: "On March 4, 2015, the licensee [University of Texas MD Anderson Cancer Center] reported that a malfunction had occurred involving its JL Shepherd Mark I, Model 30, self-contained irradiator. Device source: 10,000 curies [Cs-137], June 25, 1986, Cs-137, JL Shepherd Type 6810, SN 85CS26; Device mounting: JL Shepard Mark I Model 30 Irradiator, SN 1039. The source would not fully raise nor would it lower into the fully shielded position. The interlock system functioned as designed and the irradiator door remained locked in the source shielded position. The manufacturer was contacted and a service representative will be servicing the irradiator. This is the second incident with this device within the past month (see EN 50862). Investigation ongoing, file open." Texas Incident # I-9294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-04-08
50940 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2015-03-30 06:25 | 2015-03-30 15:48 | 2015-04-08 | AGREEMENT STATE REPORT -TROXLER MOISTURE DENSITY GAUGE STOLEN FROM TEMPORARY JOB SITE The following information was provided by the State of Arkansas via email: "On March 30, 2015, at 0703 [CDT], McGeorge Contracting Company, Inc., Arkansas Radioactive Material License Number ARK-0785-03121, reported a stolen moisture density gauge. The gauge has been stolen from a temporary jobsite on Interstate 40, near North Little Rock, sometime between 1600 [CDT] on Friday, March 27, 2015 and 0625 [CDT] on Monday, March 30, 2015. "The gauge is identified as a Troxler Electronic Laboratories, Model 3440, Serial Number 25959, with original source activities of 40 millicuries of Am-241:Be and 8 millicuries of Cesium-137. "The gauge was stolen along with other engineering equipment utilized by the licensee. "The Arkansas State Police has investigated and the Arkansas Department of Health has issued a press release. "The Radioactive Materials Program is monitoring this event under Arkansas Event Number AR-2015-002." * * * UPDATE AT 1137 EDT ON 04/08/15 FROM ANGELA HILL TO JEFF HERRERA * * * The following was received from the Arkansas Department of Health, Radioactive Materials Program via email: "The Arkansas Department of Health received a telephone call approximately at 1245 [CDT] hours on April 7, 2015, in regards to the stolen gauge near North Little Rock, Arkansas. "The Department [Arkansas Department of Health] verified the Troxler gauge and there appears to be no damage. The Cs-137 source rod lock was confirmed to be locked, secured and not tampered with. There was minor physical damage to the transport package. The Department [Arkansas Department of Health] verified exposure surveys of gauge, identifying no areas of concern. The licensee confirms leak tests prior to use and/or transferring the gauge. The licensee took possession and transported the gauge to the authorized permanent storage location. "It appears that there are no radiation exposures to the members of the public. "The Department will issue a press release on April 8, 2015. "The Department considers this event closed." Notified the R4DO (Azua), NMSS Events Notification (Email) and the ILTAB (Totterer) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-04-07
50939 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-03-30 12:00 | 2015-03-30 12:23 | 2015-03-30 | REPORT TO NEW YORK PUBLIC SERVICE COMMISSION REGARDING MAIN GENERATOR VOLTAGE REGULATOR The licensee reported that there was an unscheduled removal of service of the Unit 3 Main Generator automatic voltage regulator. This is required to be reported per IP-SNM-LI-108, "Event Notification and Reporting". This does not significantly affect the unit operation. The investigation into the loss of automatic voltage regulation is under investigation. The licensee notified the New York Public Service Commission and the New York Independent System Operator. The licensee will be notifying the NRC Resident Inspector. | 0 | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2015-03-30
50938 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2015-03-27 16:30 | 2015-03-28 12:53 | 2015-03-28 | ACCUMULATION OF SAMPLE CYLINDERS IN THE CHEMISTRY LAB EXCEEDS AMOUNT ALLOWED "Event Summary: An amount of Uranium greater than that analyzed in the associated HAZOP [Hazardous Operation] for the Chemistry Laboratory is present in the laboratory. The HAZOP states that approximately 5 kg at any given time, and a maximum of 9 kg per year, will exist in the laboratory. This HAZOP was never updated for changes in customer orders and the resultant accumulation of 1S cylinders which has exceeded the original 9 kg limit. "Nuclear Criticality Safety (NCS) staff have identified the condition as stable and safe. At no time were the enrichment levels or quantities of U235 in an unsafe condition. "This is a condition different than that analyzed in the Integrated Safety Analysis (ISA). "An NCS posting has been applied to prevent the removal or introduction of any material until a detailed evaluation of the condition and measures necessary for resolution are determined." Samples in 1S cylinders are provided to the Chemistry Lab which is located in the CRDB [Chemistry Receipt Dispatch Building] prior to shipment of product to the customer. Due to a slowdown in business these samples have accumulated to an amount exceeding the approved ISA which had not been updated to reflect current business practices. This condition was discovered by the MC & A [Material Control & Accounting] Group during a review of the process and will be addressed at an Emergency ISA Meeting on Monday, 3/30/15. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2015-03-28
50937 | 0 | CARMEUSE LIME & STONE |  |  |  |  | 2015-02-19 | 2015-03-28 12:19 | 2015-03-28 | BROKEN SHUTTER SHIELDING BLOCK ON A FIXED PROCESS GAUGE During a routine shutter check on 2/19/15, the licensee discovered the shutter shielding block had fallen off a fixed process gauge for the #2 lime conveyor. The licensee had a representative from Vega America inspect the gauge on 3/25/15. Vega America determined that the shutter shield block cannot be repaired. The licensee is considering having Vega America replace the gauge with a new model and disposing of the old gauge. The shutter is normally open and the gauge remains in service. The gauge does not present a hazard to plant personnel due to it's normally inaccessible location. The gauge is 1960s vintage, Ohmart SH-100, Model # A-2102, Serial #73799, with a 100 mCi Cs-137 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-04-06
50936 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2015-03-28 | 2015-03-28 02:21 | 2015-04-02 | SAFEGUARDS REPORT - DISCOVERY OF A VULNERABILITY IN A SAFEGUARD SYSTEM The licensee discovered a vulnerability in a safeguard system that could have allowed unauthorized access to a controlled access area. The vulnerability was corrected upon discovery. * * * RETRACTION FROM ROB DOEING TO VINCE KLCO ON 4/2/15 AT 1336 EDT * * * Based upon further licensee review, the event is being retracted, The licensee will notify the NRC Project Manager (Kellar). Notified the R4DO (Whitten). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-03-28
50935 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2015-01-30 | 2015-03-27 17:33 | 2016-03-22 | PART-21 NOTIFICATION - SENSE AND TRANSFER MODULE RESISTIVE SHORT The following excerpted report was received via e-mail: "Sense & Transfer Module (part number 41-09-339904) was provided to PSEG under purchase order 4500726553. The customer identified an abnormal curve trace (resistive short) on the integrated circuit installed at location IC825 pin 6 on this printed circuit board. The customer performed an evaluation which included dissection of the subject IC [integrated circuit] however, this dissection provided inconclusive results as to the cause of the IC anomaly. "At this time, UCI requires additional time to evaluate the results provided by PSEG and to work with the manufacturer in identifying the root cause. UCI currently considers this issue to be an isolated event as no previous instances of this failure have been observed by UCI to date. PSEG has returned the item to UCI for evaluation and rework [received by UCI on 3/25/2015]. "If you have any questions or wish to discuss this matter or this report, please contact: Wesley Hickle Procurement Engineer whickle@unitedcontrols.com 770-496-1406 x 165" Potentially affected plants are Salem and Hope Creek. * * * UPDATE ON 3/22/16 AT 1511 EDT FROM KORINA LOOFT TO DONG PARK * * * The following excerpted report was received via e-mail: "Follow up to previously reported by United Controls International (UCI) as requiring additional evaluation time and to correct purchase order information previously reported to the NRC with a report in general conformity of the requirements of 10 CFR Part 21.21." Notified R1DO (McKinley) and Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-03-27
50934 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2015-03-25 12:00 | 2015-03-27 17:28 | 2015-03-27 | AGREEMENT STATE REPORT - MEDICAL EVENT DURING PROSTATE BRACHYTHERAPY The following report was received via e-mail: "RHB [Kentucky Radiation Health Branch] was notified by telephone on 3/26/15, by the licensee's RSO [Radiation Safety Officer] of a medical event involving an I-125 permanent prostate brachytherapy implant. A CT [computerized tomography] scan performed approximately 5 weeks post-implant revealed that 30% of the implanted activity was administered outside the treatment site (PTV). The delineation of PTV corresponds to a 3 mm margin around the contoured prostate gland, except in the direction of the rectum, prostate base and apex. The error was caused by the inherent difficulty in ultrasound imaging of the prostate, changes in the prostate volume before, during, and after an implant, subjectivity in the contouring of the prostate gland, and a common tendency to drop the seeds slightly inferior to the gland as the needle is retracted. The authorized user reviewed the post plan metrics with the patient and referring physician within 24 hours of the discovery of the medical event. The KY RHB [Kentucky Radiation Health Branch] has requested additional information." Kentucky Report #: KY150002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2015-04-06
50933 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-03-27 09:41 | 2015-03-27 17:12 | 2015-03-27 | SEISMIC MONITOR NOT AVAILABLE FOR EMERGENCY PLAN ASSESSMENT "Braidwood Generating Station has completed a review of seismic monitor performance. The emergency preparedness plan requires seismic monitoring instruments to diagnose an earthquake for emergency action levels (EAL) HA4 (natural and destructive phenomena affecting vital areas) or HU4 (natural and destructive phenomena affecting the protected area). Contrary to that requirement, this review identified 5 times in the past 3 years that the seismic monitor was non-functional such that emergency classification at the ALERT or UNUSUAL EVENT level could not be obtained with site instrumentation. "The seismic monitor is currently functional; however, the seismic monitor was determined to be non-functional on the following dates: 1. April 24, 2012 2. December 5, 2012 3. December 20, 2012 4. June 17, 2013 5. October 8, 2014 "These non-functional conditions of the seismic monitor have been corrected and were entered into the Braidwood Corrective Action Program. "While Exelon procedural direction allowed the use of offsite sources to obtain seismic data when the seismic monitor is incapable of assessing emergency plan Emergency Action Levels (EALs), this was not explicitly referenced in the Braidwood approved EALs. The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). This report is required per 10 CFR 50.72(a)(1)(ii) as an event that occurred within 3 years of the date of discovery. "Corrective actions are in progress. "The licensee has notified the NRC Resident Inspector." | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-03-27
50932 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2015-03-27 13:00 | 2015-03-27 16:57 | 2015-03-27 | SEISMIC MONITOR NOT AVAILABLE FOR EMERGENCY PLAN ASSESSMENT "Three Mile Island Station has completed a review of seismic monitor performance. The seismic monitor is currently operable however, this review identified 1 time in the past 3 years that the seismic monitor was inoperable such that emergency classification at the ALERT level could not be obtained with site instrumentation. The seismic monitor was determined to be inoperable on the following date: 1) August 7, 2012 ''This unplanned inoperable condition of the seismic monitor was entered into the Three Mile Island Corrective Action Program when it occurred. "While Exelon procedural direction allowed the use of offsite sources to obtain seismic data when the seismic monitor is incapable of assessing emergency plan Emergency Action Levels (EALs), this was not explicitly referenced in the approved EALs. The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). This report is required per 10 CFR 50.72(a)(1)(ii) as an event that occurred within 3 years of the date of discovery. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-03-27
50931 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2015-03-25 | 2015-03-27 16:06 | 2015-03-27 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE STUCK IN GUIDE TUBE The following report was received via e-mail: "Radiograph work was being performed on March 25, 2015, at Dominion Power in Dumfries, VA. After the second exposure was finished, the magnetic stand holding the source fell on the guide tube. The source became stuck inside the guide tube. [The radiographers] tried multiple times to retract the source, but did not succeed. At that time, the licensee secured the area and called the RSO [Radiation Safety Officer]. This occurred around 1830 EDT. The RSO and President [of MQC Labs] arrived at approximately 2200 EDT. The RSO called QSA Global, Inc. to retrieve the source. Subsequently, the RSO contacted the Virginia EOC to notify the VRMP [Virginia Radiation Materials Program] of the incident. QSA Global, Inc. arrived at 1330 EDT on March 26,2015, to retrieve the source at Dominion Power in Dumfries, VA. VRMP staff was present to observe the source retrieval. MQC LABS will submit its written report within 30 days. VRMP will review the report and discuss any corrective action with MQC Labs and Maryland RMP [Radiation Materials Program]". MQC was performing work in Virginia under a reciprocity program with Maryland. Virginia Report # VA-15-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2015-04-06
50930 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-03-10 | 2015-03-27 14:17 | 2015-03-27 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING AN EXCESSIVE DOSE DELIVERED TO THE WRONG SITE The following report was received from the State of Illinois via email: "On March 25, 2015, Agency [Illinois Emergency Management Agency] representatives were advised via voicemail message by a medical physicist associated with the licensee's facility that a medical event had occurred at a point in the past. The medical physicist had been conducting a retrospective review of cases performed at the site which were similar to another case that had resulted in a medical event at another facility. "The review included all 5 cases performed at the licensee's facility since August of 2013 when treatments were first started. The treatment protocols involved using a Strut Adjusted Volume Implant (SAVI) catheter, a Nucletron high dose rate afterloader and the Oncentra treatment planning system which was also used in the similar situation. They determined that at least one of the treatments conducted March 10-14, 2014, involved an error of greater than 20 percent which would meet the criteria of a medical event and dose to an unintended organ exceeding 50 rem. "On March 26, 2015, a radiation oncologist from the licensee contacted the Agency with information to confirm the medical event. The patient had been treated twice a day for five days for a total intended V95 dose of 34 Gy in ten equal fractions. The target only received 43 percent of the intended dose with the majority instead being delivered to the catheter insertion site (approximately 30 Gy). It was determined that although the patient had later returned on June 24, 2014, with pain and redness at the incision site of the left breast, the cause of damage to the 21 cc tissue area was not attributed to radiation damage. The patient was referred to their surgeon who excised the affected area during an outpatient procedure. "The licensee has suspended treatments using the protocol pending a full investigation and evaluation of appropriate corrective measures to prevent a recurrence by a physicist not associated with the treatments. The Agency is conducting its own investigation as well. This matter remains open at this time." This event strongly parallels that of an event which the State of Illinois reported on February 13, 2015, see EN #50818. Illinois State Item Number: IL15009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2015-04-06
50929 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-02-24 | 2015-03-27 13:49 | 2015-03-27 | AGREEMENT STATE REPORT - RADIOGRAPHIC SOURCE FAILS TO RETRACT The following report was received via e-mail: "A radiographic source tube was damaged which temporarily restricted retraction of the source. "The guide tube became crushed by a falling object thereby preventing the source from retracting. The assistant RSO performed a source recovery with help from an assistant radiographer. The damaged guide tube was removed from service. Licensee personnel were trained on proper stabilization techniques. No individual received a dose in excess of limits. "Manufacturer: QSA Model: 880D Serial No.: 9212 Source: lr-192 Activity: 29 Ci" PA Event #: PA150008. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-04-06
50928 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-03-26 13:30 | 2015-03-26 16:36 | 2015-03-26 | SEISMOGRAPH NOT AVAILABLE FOR EMERGENCY PLAN ASSESSMENT "Quad Cities Station has completed a review of the station strong motion seismograph's performance. The seismograph is currently functional; however, this review identified 3 times in the past 3 years that the seismograph was non-functional such that emergency classification at the ALERT level could not be obtained with site instrumentation: 1) 02/03/2014 2) 10/07/2014 3) 10/19/2014 "These unplanned non-functional conditions of the seismograph were entered into the Quad Cities Corrective Action Program when they occurred. "While Exelon procedural direction allowed the use of offsite sources to obtain seismic data when the seismograph was nonfunctional, this was not explicitly referenced in the approved Emergency Action Levels. The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). This report is required per 10 CFR 50.72(a)(1)(ii) as an event that occurred within 3 years of the date of discovery." Corrective actions are in progress. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-03-26
50927 | -1 | OREGON STATE UNIVERSITY |  |  |  | 1100 KW TRIGA MARK II | 2015-03-25 16:00 | 2015-03-26 15:23 | 2015-04-08 | RESEARCH AND TEST REACTOR TECHNICAL SPECIFICATION VIOLATION "We would like to report a potential violation of our Technical Specifications, section 6.7.2.a.8 which states an observed inadequacy in the implementation of administrative or procedural controls such that the inadequacy causes or could have caused the existence or development of an unsafe condition with regard to reactor operations. The details of the event are as follows: - January 14, [2015,] the Reactor Supervisor submitted paperwork for license renewal of an SRO [Senior Reactor Operator] to the director for signature. The director signs the paperwork. It was then assumed that the paperwork would be routed to the NRC for license renewal. The paperwork was signed but not sent to the NRC. - March 10, [2015,] the license for the SRO expires. - March 19, [2015,] the SRO completes the control room portion of the startup checklist. This includes manipulation of console controls and placing the reactor in 'OPERATING' condition. The SRO does not perform the reactor startup. - March 25, [2015,] staff determines that the reactor was placed in an OPERATING condition without a licensed operator at the console on March 19. No other staff was present in the control room during the performance of the startup checklist. - March 26, [2015,] reactor operation was suspended. "It has been determined that the SRO did not perform any other license duties after his license had expired. The SRO will not perform license duties until his license is officially renewed." * * * UPDATE AT 1905 EDT ON 04/08/15 FROM STEVEN REESE TO S. SANDIN * * * "On March 26, 2015, the Oregon State TRIGA Reactor staff self-reported a potential violation of Technical Specifications, section 6.7.2.a.8 which states 'an observed inadequacy in the implementation of administrative or procedural controls such that the inadequacy causes or could have caused the existence or development of an unsafe condition with regard to reactor operations.' The report was submitted due to the fact that the license of an SRO had expired on March 10, 2015, but that the operator performed licensed duties including placing the reactor in the 'operating' state on March 19, 2015. This individual did not perform any other license duties between the date his license expired and the date that a new license was issued. The initial notification e-mail sent by the reactor staff on 3/26/2015 (event notification 50927) informed the NRC of the event. "In retrospect, we [Oregon State University] believe this event falls well below the threshold that would constitute a violation of Technical Specification 6.7.2.a.8. The individual has been a licensed operator of the Oregon State TRIGA Reactor for six years. None of the activities he [the operator] performed during the short period that his license was expired could realistically be construed as 'development of an unsafe condition with regard to reactor operations.' All duties that were performed during the event were reviewed by a licensed SRO as part of the daily start-up checklist. "A new license was issued on April 2, 2015 (SOP-70794, Docket# 55-70933). The staff currently tracks all licensee due dates and it has been emphasized that maintenance of one's license is the responsibility of each licensed operator as well. The staff intends to add a tracking item to verify that 1) a license renewal is submitted at least 2 months prior to license expiration and 2) a license renewal is received at least one month prior to license expiration. It is expected that this information will reviewed during our [Oregon State University] next normally scheduled NRC inspection. No other follow-up or remedial actions are planned. "This letter serves to retract the initial self-reported potential technical specification violation. Since it is deemed that a violation did not actually occur, there will be no subsequent 14-day written report." Notified NRR PM (Adams) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | OR | NPR | [5 empty] | 0 | 2015-03-26
50926 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-03-26 13:30 | 2015-03-26 15:19 | 2015-03-26 | SEISMIC MONITOR NOT AVAILABLE FOR EMERGENCY PLAN ASSESSMENT "LaSalle Station has completed a review of seismic monitor performance. The seismic monitor is currently operable; however, this review identified 6 times in the past 3 years that the seismic monitor was inoperable such that emergency classification at the ALERT level could not be obtained with site instrumentation. The seismic monitor was determined to be inoperable on the following dates: 1) January 28, 2015 2) May 28, 2014 3) January 1, 2014 4) August 5, 2013 5) April 17, 2013 6) April 10, 2012 "These unplanned inoperable conditions of the seismic monitor were entered into the LaSalle Corrective Action Program when they occurred. "While Exelon procedural direction allowed the use of offsite sources to obtain seismic data when the seismic monitor is incapable of assessing emergency plan Emergency Action Levels (EALs), this was not explicitly referenced in the approved EALs. The loss of assessment capability is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). This report is required per 10 CFR 50.72(a)(1)(ii) as an event that occurred within 3 years of the date of discovery." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-03-26
50925 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-03-25 14:57 | 2015-03-25 21:37 | 2015-03-25 | OFFSITE TRANSPORTATION OF CONTAMINATED AND INJURED INDIVIDUAL "On March 25, 2015, at approximately 1413 CDT, a Browns Ferry Nuclear (BFN) employee fell approximately 6 feet and sustained a laceration to his forehead and potential other injuries. The individual had been working in the Unit 2 drywell, which is a contaminated area. The individual was able to be removed from his anti-contamination clothing prior to leaving the Radiological Controlled Area (RCA). "The individual was surveyed by a Radiation Protection (RP) technician and had slight contamination (150 cpm [counts per minute]) on his forehead in the area near the laceration. No survey of his back was performed due to being on a stretcher. At 1457 CDT, the individual was transported to an off-site medical facility. A BFN RP technician accompanied the individual to the hospital. Subsequent survey of the individual at the medical facility determined that no other areas of contamination existed. The individual was successfully decontaminated at the medical facility during initial treatment and all locations have been free released. All contaminated materials have been properly controlled. "This event is reportable in accordance with 10CFR50.72(b)(3)(xii) any event requiring the transport of a radioactively contaminated person to an offsite medical facility for treatment. "This event has been entered into the Corrective Action Program (CAP) in SR# 1004507. "The NRC Resident Inspector has been notified." The individual was transported to Decatur Morgan General Hospital in Decatur, Alabama for decontamination and follow-up medical treatment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2015-03-25
50924 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2015-03-25 17:19 | 2015-03-25 21:33 | 2015-03-25 | OFFSITE NOTIFICATION DUE TO EFFLUENT BELOW NATIONAL POLLUTANT DISCHARGE ELIMINATION SYSTEM PH LIMITS "At time 1719 CDT it was determined that notification of the Nebraska Department of Environmental Quality (NDEQ) was required based on the results of a quarterly sample drawn at 1632 CDT on 3/25/2015 from the headwall effluent flow 002C sample point identifying a Ph of 4.4 which is below the allowable levels of the National Pollutant Discharge Elimination System (NPDES) requirements for Ph of 6.5-9.0. Notification of NDEQ will be made within 24 hours in-accordance with the requirements of NPDES Permit NE0001244. The notification to the NDEQ will be made during normal business hours 3/26/15. "This sample point is supplied by floor drains in Auxiliary Steam Boiler room, Turbine Building HVAC Fan room and DG [Diesel Generator] Building sumps. Discharge from this line is approximately 76 gallons per day. All flow from this sample point was isolated at 2008 CDT. Investigation of the cause of the low Ph levels is on-going." No indications of environmental impact were reported by the licensee. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-03-25
50923 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-03-15 | 2015-03-25 17:58 | 2015-03-25 | AGREEMENT STATE REPORT - EXTREMITY OVEREXPOSURE WHILE OPERATING A RADIOGRAPHY CAMERA The following report was received from the Texas Department of State Health Services via email: "On March 25, 2015, the licensee reported that on March 15, 2015, one of its industrial radiographer trainees had experienced a possible overexposure to his right hand while using a QSA Model 880 camera that contained a 54.5 curie iridium-192 source. Initial information reported by the licensee: Following the 10th and final exposure of the day, the radiographer trainee climbed a ladder to the first deck and approached the camera from the rear with a survey meter. He performed a 360 degree survey of the camera and full length of the guide tube noting a zero reading on the survey meter. He then attempted to disconnect the guide tube by attempting to rotate the outlet port cover. When it would not rotate, he looked at the back of the camera to ensure the selector was in the correct position, and then attempted to disconnect the guide tube a second time. Again, the outlet port cover would not rotate and he looked at the back of the camera and noticed the slide bar of the lock was showing red, indicating the source was not in the fully shielded and secure position. He climbed down the ladder and informed the radiographer trainer what had happened. "The radiographer trainer exposed the source approximately 1/4 turn and forcibly retracted it to its fully locked and shielded position. They checked the survey meter (battery function check) and determined it was not working properly. The meter was disassembled, battery terminals were adjusted, and the meter functioned properly. "The radiographer trainer surveyed the camera and determined the source was fully retracted. The radiographer trainee stated he did not hear his alarming rate meter due to the noise level at the job site. The radiographer trainer did not receive any additional exposure as a result of this event. The radiographer trainee's pocket dosimeter was off-scale. His dosimetry badge was sent for processing and from the results the licensee determined he had received 384 millirem whole body dose from this event. Calculations will be made following a re-enactment of the event on 03/30/2015 to determine the dose to his hand. "Exposure Device: QSA Model 880D SN: D1123, Source: 54.5 curies iridium-192 SN: 14191G" The State of Texas is continuing to investigate the issue. Texas report ID #: I-9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-04-02
50922 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-03-16 08:30 | 2015-03-25 17:12 | 2015-03-25 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER WOULD NOT CLOSE PROPERLY The following information was received via fax: "On 03/17/2015, the RSO for MOTIVA ENTERPRISES called in a preliminary report about a shutter that would not close properly on a gauge installed on a process. The shutter could not be closed or locked out. This situation reoccurs periodically due to the corrosive operating environment of this gauge or device. Routine maintenance was performed by BBP Sales and the device again functioned as designed. "This situation is reoccurring about every 11 to 14 months. The corrosive and caloric operating environment is the source of this operational problem. The problem with the shutter function is corrected by cleaning and lubricating the mechanism. The equipment/source holder is not broken, just in need of preventive maintenance. "There was no removable radiation detected in the leak test results and the rotor moved freely when the top plate was removed for the maintenance. BBP Sales was called to perform the maintenance to correct the problem. The gauge/source holder was 'fixed.' The repairman/technician was never exposed to a radiation field greater than 3.0 mR/hr. "The Department [Louisiana Department of Environmental Quality] considers this item closed and the records will be reviewed during the next inspection." Gauge is an Ohmart Vega S/N 3211CO with a 175 Ci Cs-137 source. Louisiana Report: LA 15-0006, T162348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-04-02
50921 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-03-25 15:25 | 2015-03-25 17:01 | 2015-03-25 | SHEEPSHEAD MINNOW MORTALITY IN COOLING CANAL SYSTEM "This is a non-emergency notification in accordance with 10 CFR 50.72(b)(2)(xi) for notification to 'other government agencies.' "On March 25, 2015 at approximately 1525 EDT, Florida Power & Light Company notified the State of Florida Fish and Wildlife Conservation Commission of an observed increase in the mortality of sheepshead minnows in the cooling canal system; an industrial wastewater facility. No other animal or fish species were affected. The impact is estimated to be a very small fraction of the total minnow population. The condition has had no adverse impact on station operations. "The NRC Resident Inspector has been notified." Sheepshead minnows are not an Endangered Species. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-03-25
50920 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-03-01 | 2015-03-24 16:53 | 2015-03-25 | AGREEMENT STATE REPORT - RADIATION TECHNICIAN POTENTIAL OVEREXPOSURE The following information was obtained from the State of Florida via email: "An employee of Cardinal Health had a dosimeter reading of 140 REM. The employee routinely wears one whole-body badge and two ring dosimeters assigned to him. These findings are for the wear period of 2/16/2015-3/1/2015. The whole body badge had a reported dose of 140884 mRem DDE and 241488 mRem SDE. [Cardinal Health] stated that the individual didn't have any reportable readings from their rings badges for this wear period. The individual is showing no symptoms of overexposure and has been removed from handling radioactive material as a safety precaution. It is believed that the badge may have become contaminated therefore distorting the correct exposure reading. Cardinal Health is reportedly conducting an investigation to find the cause and extent of this incident. Pending the Landauer report and some additional information, an investigator will be assigned to inspect their laboratory for safety and confirm Cardinal Health's investigative conclusions." Florida Incident Number: FL15-023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-04-01
50919 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-02-26 13:00 | 2015-03-24 15:20 | 2015-03-24 | AGREEMENT STATE REPORT - MISSING FIXED GAUGE SHUTTER The following report was received via e-mail: "On 02/26/2015, the RSO for Boise Cascade called in a preliminary report [to the Louisiana Department of Environmental Quality] about a shutter missing on a gauge to be 'locked out' during a 24 hour turn-a-round. The shutter is a manual sliding port cover that has to be removed when the gauge is used on the process. The removed shutter is stored by placing it on an adjacent surface until needed. Vibrations on the process had caused the port cover to fall approximately 50 ft. below the storage locations. However, this time the cover could not be located and the gauge could not be locked out. The gauge remained on the process until it could be repaired. "On 02/26/2015, a replacement shutter/port cover was ordered from Thermo Measuretech. The shutter was delivered on 02/27/2015 and installed the same day. There was no radiation exposure risk to the public or workers. The gauge is installed on a 50 ft. elevation and the unshielded radiation field is approximately 0.3 mR/hr at 1 ft. from the surface of the device. "The gauge was a Texas Nuclear Device, TN 5192, s/n B3421 containing approximately 100 mCi of Cs-137 when installed during the mid-1980s. "The Department [Louisiana Department of Environmental Quality] considers this item closed and the records will be reviewed during the next inspection." Louisiana Event Report ID No.: LA 15-0005, T162439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-04-01
50918 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2015-03-23 15:26 | 2015-03-23 16:28 | 2015-03-23 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED OFFSITE DUE TO MEDICAL CONDITION "At approximately 1526 EDT, the control room received a report of an individual experiencing chest pains. An ambulance was called to transport the individual to an offsite medical facility. The initial Radiation Protection survey did not detect any contamination, however the protective clothing the individual wore could not be removed. The individual is considered 'potentially contaminated' due to not being able to perform a complete frisk. Radiation Protection personnel escorted the individual offsite. The individual will be frisked at the medical facility." The licensee has notified the NRC Resident Inspector and will notify the state and local government. * * * UPDATE AT 1722 EDT ON 3/23/2015 FROM ED CONDO TO MARK ABRAMOVITZ * * * "At approximately 1652 [EDT], Perry Radiation Protection confirmed the individual was not contaminated. Additionally no contamination was found in the ambulance or at the hospital. Perry Radiation Protection is in possession of and returning all protective clothing worn by the individual to the plant." The licensee notified the NRC Resident Inspector. Notified the R3DO (Cameron). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2015-03-23
50917 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2015-03-23 07:17 | 2015-03-23 11:16 | 2015-03-23 | OFFSITE NOTIFICATION DUE TO DEATH OF EMPLOYEE "At approximately 0605 EDT on March 23, 2015, the Oconee Nuclear Station main control room and Security received an emergency call for an employee experiencing a non-work related medical issue. Site first responders were dispatched in conjunction with a request for off-site medical assistance. The individual was transported by ambulance to the Oconee Medical Center and was pronounced dead at 0717 EDT. The individual was outside of the protected area (within the owner controlled area) and no radioactive material or contamination was involved. The cause of death has not been determined. "This notification is being made in accordance with 10 CFR 50.72(b )(2)(xi) for situations related to the health of on-site personnel for which a notification to other government agencies has been made. The South Carolina Occupational Safety and Health Administration (SCOSHA) was notified at 0920 EDT. "The NRC Resident Inspector has been notified." The licensee notified Pickens County, South Carolina and Oconee County Emergency Managements. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-03-23
50916 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2015-03-22 14:14 | 2015-03-22 15:17 | 2015-03-22 | REACTOR SCRAM DUE TO APRM HI HI SIGNAL "RPS Actuation (scram) on a Hi-Hi APRM [average power range monitor] signal [which] occurred due to a pressure spike following a failure of the EPR (Electric Pressure Regulator). All Rods Inserted. All systems responded normally. No other safety system actuations occurred. Plant will proceed to a cold shut down condition." The plant is in a normal electrical lineup. Core cooling is being maintained by the bypass valves to the condenser. The licensee has notified the NRC Resident Inspector and will notify the local and state governments. A press release is planned by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-03-22
50915 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-03-21 05:37 | 2015-03-21 13:55 | 2015-05-11 | HIGH PRESSURE COOLANT INJECTION INOPERABLE DUE TO CONDENSATION IN STEAM LINE "At 0537 CDT on March 21, 2015, following the High Pressure Coolant Injection (HPCI) system quarterly pump and valve surveillance, after HPCI was removed from service, an alarm for the HPCI Turbine Inlet High Drain Pot Level did not reset. This indicated that LS-23-90 (HPCI Steam Supply Drain High Level Bypass) did not reset, which could be an indication that condensate exists in the steam line. The system responded as designed but the alarm did not clear as expected. Without assurance that the condensate has been removed from the HPCI steam line, HPCI remains inoperable for reasons other than the planned surveillance. As a result, this condition is being reported under 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented fulfillment of the safety function at the time of discovery. "The health and safety of the public was maintained as the plant was in a normal condition with no initiating event in progress. "The NRC Resident Inspector has been notified." The State of Minnesota will be notified. * * * RETRACTION FROM RANDY SAND TO DANIEL MILLS AT 1445 EDT ON 5/11/15 * * * "On March 21, 2015, Northern States Power Minnesota reported a condition that could have prevented the fulfillment of a safety function under 10 CFR 50.72(b)(3)(v)(D). The High Pressure Coolant Injection (HPCI) System was declared inoperable for a reason other than planned maintenance due to the failure of the HPCI Steam Supply Drain Hi Level Bypass Level Switch to clear the high level alarm subsequent to actuation. "An engineering evaluation was performed and concluded that the function of the primary pathway to remove condensate remained unchallenged by the condition present on the level switch This conclusion was also validated via thermography with the HPCI steam supply pressurized and bypass valve open. The verification that the primary pathway was functional provides reasonable assurance that the HPCI steam supply was always clear of condensate supporting the ability of HPCI to perform its required safety function. Therefore, the condition present on the level switch did not render HPCI inoperable. The conclusions of the engineering evaluation provide the basis for retraction of the ENS report made on March 21. "The NRC Resident Inspector has been notified." The licensee will also notify the State of Minnesota. Notified R3DO (Peterson). | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-03-21
50914 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-03-21 00:30 | 2015-03-21 04:15 | 2015-03-21 | BOTH SECONDARY CONTAINMENT DOORS OPENED SIMULTANEOUSLY "At 0030 CDT, on March 21, 2015, both doors of a Secondary Containment Airlock were opened concurrently by two separate individuals. The doors being open at the same time caused a failure to meet SR [Surveillance Requirement] 3.6.4.1.2 to verify that either the outer door(s) or the inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered inoperable per TS LCO [Technical Specification Limiting Condition for Operation] 3.6.4.1. Upon discovery, immediate action was taken to close the doors. The doors were open concurrently for a momentary amount of time. The action to close the door allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to an operable status. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(C). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-03-21
50913 | 0 | DEPARTMENT OF THE ARMY |  |  |  |  | 2015-03-20 13:30 | 2015-03-20 19:35 | 2015-03-20 | LOST GENERAL LICENSED RADIOACTIVE MATERIAL The following occurred at Joint Base Lewis-McChord which is located in the State of Washington. At 1330 PDT on 3/20/2015, it was confirmed that items containing general licensed radioactive material had been converted into scrap material and then sent offsite to an as yet undetermined smelter. It is believed that the disposition of this material occurred on 4/30/2014. The lost general licensed radioactive material was contained in the following equipment with activities as listed: Smiths Detection, Sabre 4000, Serial #: 43105, 15 mCi Ni-63 Smiths Detection, Sabre 4000, Serial #: 43135, 15 mCi Ni-63 GE, VaporTracer2, Serial #: K190014411, 10 mCi Ni-63 GE, VaporTracer2, Serial #: K190014412, 10 mCi Ni-63 Safran, Itemiser 3, Serial #: 050449010283, 10 mCi Ni-63 The Department of the Army is continuing to try to ascertain where this material ended up. There are no known exposures, injuries or contaminations due to this event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-03-30
50912 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-03-20 12:30 | 2015-03-20 16:49 | 2015-03-20 | UNPLANNED MEDICAL TREATMENT "A nuclear operator sustained a laceration to the right hand on a piece of metal flashing while working in a radiological controlled area onsite. The individual was transported to the onsite NFS medical facility for treatment. Radiological surveys of the individual taken at the onsite medical facility indicated no contamination. The individual was subsequently transported to an area hospital for further medical care. Follow-up radiological surveys performed in areas where the injury occurred, in the vehicle used for onsite transport, and in the onsite medical facility also indicated no contamination." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(3) |  |  |  | 0 | 2015-03-24
50911 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2014-06-06 | 2015-03-20 14:49 | 2015-03-20 | PART-21 REPORT - VALVE SEAT LEAKAGE DEFECT The following is a summary of a submitted facsimile: "A valve plug originally supplied as a spare parts order was returned to Fisher after the customer discovered a machining error was present on the plug. The Type 461 valve plug has a groove machined across the seating surface of the plug. This groove is required to provide a controlled leak rate thru the valve when the plug is on the seat. The issue recently identified shows that the machined groove did not extend through the full length of the seat. This could lead to a situation in which the intended/required leakage for this design is not fully achieved." Affected plants are: Waterford-3 and St Lucie. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | CONSTRUCT DEFICIENCY | [8 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) | 50.55(e) |  |  | 0 | 2015-03-20
50910 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-03-17 | 2015-03-20 12:29 | 2015-03-20 | AGREEMENT STATE REPORT - ORPHAN SOURCE FOUND IN SCRAP METAL The following report was received via fax: "The Department [Pennsylvania Department of Environmental Protection] received notification on March 18, 2015 regarding a source that set off an alarm at a steel mill facility. "A truck load of scrap set off a radiation monitor alarm at the ATI Midland steel mill. ATI rejected the load and sent it back to the scrap yard which contacted an approved service provider. Applied Health Physics isolated and identified the source as Americium-241 (Am-241). Contact reading of the source was 30 mR/hr and 1 mR/hr at 1 meter. "Source: Am-241 Manufacturer: Unknown Manufacturer Date: 4-13-88 SN: # 7435LV" Pennsylvania Report: PA150007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-03-30
50909 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2015-01-21 10:00 | 2015-03-19 22:45 | 2015-03-19 | 60-DAY OPTIONAL NOTIFICATION - INVALID CONTAINMENT ISOLATION SIGNAL "This 60-Day telephone notification is being made per the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation signal affecting containment isolation valves. "On January 21, 2015, Nine Mile Point Unit 1 (NMP1) received a partial primary containment isolation signal which resulted in the closure of primary containment isolation valves (PCIVs) in the following systems: "Containment Monitoring System Drywell floor drain sump and Drywell equipment drain sump "All affected PCIVs responded as designed. The containment isolation signal was generated due to the failure of a relay for Hi Drywell Pressure on Channel 11 during surveillance testing of the same relay on Channel 12. Drywell pressure was reading normal at the time of the relay failure. Since the isolation signal was not initiated in response to actual plant conditions or parameters satisfying the requirements for initiation, the isolation signal was determined to be invalid. "The event was entered into the corrective action program as Issue Report 02440213. The moveable contacts on the failed relay were replaced and retested satisfactorily. There were no safety consequences and no impact to the health and safety of the public as a result of this event." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-03-19
50908 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2015-03-18 | 2015-03-19 17:18 | 2015-03-19 | AGREEMENT STATE REPORT - UNDER DOSAGE OF PATIENT UNDERGOING TREATMENT The following report was received from the State of Wisconsin Department of Health Services via email: "On March 18, 2015, the Wisconsin Radiation Protection Section received a notice from the Radiation Safety Officer (RSO) at Wheaton Franciscan Healthcare-Franklin of a medical event that occurred from a halted administration of Yttrium 90 SIR-Spheres. During the administration, air bubbles were noticed to be collecting in the tubing delivering the dose. The procedure was stopped in order to avoid injecting air bubbles into the patient. The prescribed dose was 33.26 mCi. 26.35 mCi had been delivered to the patient, based on pre-and post-procedure assays of the material. This is 79.2% of the prescribed dose. The licensee believes placement of the needles drawing the solution was to blame for the collection of air bubbles. The Radiation Protection Section will perform an investigation and update through NMED." Wisconsin Event Report ID No.: WI150005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2015-03-27
50907 | 0 | PALISADES | 1 |  |  | [1] CE | 2015-03-19 16:00 | 2015-03-19 16:44 | 2015-03-19 | OFFSITE NOTIFICATION OF TRITIUM IN GROUND WATER "On February 26, 2015, as a result of routine monitoring well sampling, Palisades Nuclear Plant identified tritium in temporary wells 7 and 8, located within the plant protected area. Tritium concentrations were less than the threshold value (20,000 pCi/L) for initiating voluntary communications in accordance with Nuclear Energy Institute Ground Water Protection Initiative. The station promptly isolated and rerouted the likely source. Subsequent sample concentrations from samples obtained on March 18, 2015, have resulted in concentrations of tritium less than the minimum detectable activity. The wells are currently used only for on-site sampling and not for drinking water. There is no threat to public health and safety. "These results confirm that a leak from the pipe that runs from the turbine sump oil separator to the turbine building drain tank was the likely cause. The volume of the leak cannot be determined but is potentially greater than 100 gallons. Therefore, voluntary communications have been made to state and local stakeholders. The Licensee has notified the Michigan Department of Environmental Quality, Van Buren County Administrator, the Township Supervisors in Covert, Geneva, and South Haven Townships, as well as the City of South Haven Mayor and City Manager. "The licensee has notified the NRC Resident Inspectors." The tritium is suspected to be migrating through the steam generator tubes to the turbine building waste water. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-03-19
50906 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-03-17 | 2015-03-19 14:45 | 2015-03-19 | AGREEMENT STATE REPORT - OHMART SH-F2 GAUGE SHUTTER HANDLE PIN SHEARED The following report was received from the Texas Department of State Health Services via email: "On March 19, 2015, the licensee notified the Agency [Texas Department of State Health Services] that on March 17, 2015, while preparing for a shutdown for maintenance, it closed the shutter on an Ohmart SH-F2 gauge, which contained a 200 milliCurie cesium-137 source, and the pin on the shutter handle sheared off. The licensee performed a survey to confirm the source was in the fully shielded position and placed a lock on the shutter. No individual received any exposure as a result of this event. The licensee contacted a service company and the gauge was repaired and returned to service on March 19, 2015. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I 9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-03-27
50905 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-03-04 | 2015-03-19 14:45 | 2015-03-24 | AGREEMENT STATE REPORT - OHMART SHLM-CR3 CABLE DETACHED FROM SOURCE The following report from the Texas Department of State Health Services was provided via email: "On March 19, 2015, the licensee notified the Agency [Texas Department of State Health Services] that on March 4, 2015, while preparing for a shutdown for maintenance, it retracted a cesium-137 source back into its Ohmart SHLM-CR3 source holder when the cable came off of the source. The gauge contains a 2,400 milliCurie (original activity 04/1991) cesium-137 source. The licensee performed a survey to confirm the source was in the fully shielded position and placed a lock on the shutter. No individual received any exposure as a result of this event. The licensee is coordinating with the manufacturer to have the gauge repaired. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I 9285 * * * UPDATE AT 1804 EDT ON 3/24/2015 FROM KAREN BLANCHARD TO MARK ABRAMOVITZ * * * The following was received by e-mail: "The licensee initially reported the wrong event date. The licensee has advised the Agency [Texas Department of State Health Services] that the event actually occurred on March 2, 2015 (and not March 4, 2015 as previously reported)." Notified the R4DO (Gaddy) and NMSS Events Notification (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-03-27
50904 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2015-03-17 21:30 | 2015-03-19 13:17 | 2015-03-30 | AGREEMENT STATE REPORT - RADIOGRAPHER POTENTIAL OVEREXPOSURE The following information was received via fax: "On March 18, 2015, the Radiation Safety Officer for Vital Inspection Professionals, Alabaster, Alabama notified the Office of Radiation Control [for the State of Alabama] in regards to a potential overexposure which may have occurred while conducting radiography at the Alabama Power, Miller Steam Plant. "On March 17, 2015 at approximately 2130 CDT, a crew was conducting radiography. The crew consisted of one radiographer and three assistants. They were completing two exposures lasting 35 seconds, and with a set-up time of approximately 15 to 18 minutes. After completing the two exposures, the radiographer noticed that his pocket dosimeter (200 mR) was off-scale. The first assistant's pocket dosimeter was reading 50 mR, the second assistant's pocket dosimeter was off scale and the third assistant was not wearing any dosimetry. The radiographer and first assistant acknowledged that their alarming rate meters were functioning correctly, the second assistant and third assistant were not wearing an alarming rate meter. "The crew notified their Radiation Safety Officer at 2130 CDT, but did not contact him until around midnight. The crew immediately stopped work and was told to meet the Radiation Safety Officer the next morning to discuss the events. All available dosimetry was sent off for emergency processing and [dose information] should be received by noon, March 19, 2015. From the discussion it was determined that the survey meter had an apparent electrical short and was not measuring properly. The camera was checked and determined to be functioning properly. Based on the licensee's preliminary dose estimates it was determined that one crew member may have received up to 45 Rem whole body. * * * UPDATE AT 1205 EDT ON 3/30/2015 FROM MYRON RILEY TO JEFF HERRERA * * * The following update was received from the Alabama Department of Public Health via fax: "On March 25, 2015, Agency representatives visited Alabama Power Miller Steam Plant and met with representatives of the plant and reviewed the area where the incident took place. Also during this time the Radiation Safety Officer, the Assistant Radiation Safety Officer and the Radiographer, for Vital Inspection Professionals, were interviewed while at the plant. "Starting the afternoon of March 25, 2015 and concluding the afternoon of March 26, 2015 visit, Agency representatives [Alabama Department of Public Health] met with personnel for Vital Inspection Professionals at their office and interviewed one shift foreman and the four individuals involved in the incident. The preliminary findings from interviews and a re-creation of the events is that the source was outside of its fully shielded position, but not in the guide tube. "Since the incident, all four individuals involved have been seen by an Occupational Physician and have had blood samples sent to REAC/TS for review. Results should be received by April 3, 2015. Further review of all associated paperwork and training will be accomplished by April 1, 2015." Alabama Incident 15-16 Notified R1DO(Kennedy), NMSS_EVENTS_NOTIFICATION via email | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2015-03-27
50903 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-03-19 07:02 | 2015-03-19 10:51 | 2015-03-19 | AUTOMATIC REACTOR SCRAM DUE TO AN OSCILLATION POWER RANGE MONITOR UPSCALE ACTUATION "At 0702 EDT on March 19, 2015, Fermi 2 received an automatic scram due to actuation of the Reactor Protection System (RPS) function of Oscillation Power Range Monitor (OPRM) Upscale. The plant had recently transitioned to Single Loop Operation after securing the 'A' Reactor Recirculation Pump due to loss of normal and emergency cooling water supply. The lowest reactor water level was 134 inches above top of active fuel. Reactor water level is being maintained in the normal band by the Feedwater and Control Rod Drive Systems. No Safety Relief Valves (SRV) actuated. Reactor pressure is being maintained via the Main Turbine Bypass Valves and Main Condenser. Reactor Pressure Vessel Level 3 isolation occurred. No additional safety system actuations occurred. All off-site power sources were available throughout the event. The plant is currently in Mode 3 and in a stable condition. Investigation into the cause of the event is ongoing. "This event is being reported under the four hour Non-Emergency reporting criteria of 10CFR50.72(b)(2)(iv)(B). The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-03-19
50902 | 0 | MALLINCKRODT PHARMACEUTICALS |  |  |  |  | 2015-02-26 | 2015-03-19 10:39 | 2015-03-19 | MOLYBDENUM-TECHNETIUM GENERATOR LOST DURING SHIPMENT A Mo-Tc Generator was sent to Baptist Hospital in Miami, Florida. The generator was used for approximately 2 weeks before being shipped back on 1/18/14. It was picked up by the common carrier on 1/19/14. The Mo-Tc generator did not make it back to the Mallinckrodt facility. A search was initiated at the Mallinckrodt facility and Baptist Hospital. When the Mo-Tc generator could not be located, it was declared missing on 2/26/15. The generator is approximately 65 lbs. total and contains 8.1 mCi of depleted uranium-238. The shield was stamped with the number 2116. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-03-27
50901 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-03-17 17:55 | 2015-03-17 18:24 | 2015-04-23 | SAFEGUARDS REPORT - DISCOVERY OF A POTENTIAL VULNERABILITY IN A SAFEGUARD SYSTEM The licensee discovered a potential vulnerability in a safeguards system. The vulnerability was corrected immediately. The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 4/23/15 AT 1721 EDT FROM RANDY SHACKELFORD TO DONG PARK * * * The licensee discovered an additional potential vulnerability in a safeguards system. The licensee has notified the NRC Resident Inspector. Notified R2DO (Blamey) and Part 73.71 Safeguards group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2015-04-23
50900 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2015-03-17 | 2015-03-17 09:59 | 2017-02-03 | INTERIM PART 21 REPORT - POTENTIAL TEST INDUCED DEFECT IN A 0867F MAIN STEAM SAFETY RELIEF VALVES The following report was received from Curtiss - Wright via email: "This letter provides interim notification of a potential test induced defect in a 0867F Series Main Steam Safety Relief Valves (MS-SRVs) manufactured and supplied by Target Rock (TR). The information required for this notification is provided below: "(i) Name and address of the individual or individuals informing the Commission. William Brunet Director of Quality Assurance James White General Manager Target Rock, Business Unit of Curtiss-Wright Flow Control Corporation 1966E Broadhollow Road East Farmingdale, NY 11735 "(ii) Identification of the basic component supplied for such facility or such activity within the United States which may fail to comply or contains a potential defect. Target Rock 0867F Series of Main Steam-Safety Relief Valves Manufactured by Target Rock. This is a 3-stage piloted valve consisting of a main valve (the 'Main') with an actuator mounted to it (the 'Topworks'). The 0867F is the latest generation of the 67F line of MS-SRVs, including the original 3-Stage and 2-Stage designs, and this product line has over 40 years of plant operational experience. Only the 0867F is under investigation. This is due to the differences between the 0867F design and the other designs. "(iii) Identification of the firm supplying the basic component which fails to comply or contains a defect. Target Rock, Business Unit of Curtiss-Wright Flow Control Corporation 1966E Broadhollow Road East Farmingdale, NY 11735 "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. As we understand it, the Pilgrim Station recently manually opened the Target Rock Main Steam Safety Relief Valves (MS-SRVs) as part of cooling down the reactor following a loss of offsite power. One of the four installed MS-SRVs may not have fully opened. As-found steam testing of the affected MS-SRV did not duplicate this failure; the valve opened on demand. However, the valve did not re-close as expected. Internal inspections found damaged parts in the main stage subassembly that could potentially affect the ability of the MS-SRV to operate as designed. We are investigating potential root causes for this damage. However, we are still unable to determine if a specific defect exists. GE SIL-196, Supplement 17 determined Main Spring relaxation was caused by 'extreme dynamics encountered during limited flow testing . Valve dynamics under full flow conditions (i.e. discharge not gagged) are much less severe than those under limited flow conditions.' These extreme dynamics, under limited flow test conditions, are the focus of our investigation. Specific areas of investigation include; a) Testing of materials to verify they are consistent with our material specifications, b) evaluation of differences between the 0867F and earlier designs, and c) evaluation of the differences between different limited flow test loop configurations and test procedures "(v) The date on which the information of such defect or failure to comply was obtained. The Pilgrim event occurred on January 27, 2015. As-found testing occurred on February 2, 2015. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. While we have yet to determine if a specific defect exists, the following plants were supplied 0867F MS-SRVs: - Pilgrim (Model 09J-001) Quantity Shipped = 8 - Fitzpatrick (Model 09H-001) Quantity Shipped = 4, Quantity on order= 8 - Hatch 1 and 2 (Model 09G-001) Quantity Shipped= 24, Quantity on order= 12 The following plants will be supplied 0867F MS-SRVs: - Hope Creek (Models 14J-001, 14J-002) Quantity on order = 7 "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. The root cause of the potential test induced defect has not yet been confirmed as of the date of this report. Therefore, no specific corrective actions have been initiated. Target Rock Problem Report 080 will document the corrective actions when they are determined and complete the 10 CFR Part 21 evaluation of the potential test induced defect. This determination will be based on further mechanical and material evaluations. TR anticipates completing these evaluations within 45 days; however, in the event the evaluations are not completed, TR will forward another interim report within 45 days. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. We are working with all three (4) sites to identify appropriate precautions. "(ix) In the case of an early site permit, the entities to whom an early site permit was transferred. Not applicable. "Should you have any questions regarding this matter, please contact Michael Cinque, Director of Program Management at (631 ) 293-3800." * * * UPDATE FROM JOHN DeBONIS (VIA EMAIL) TO HOWIE CROUCH AT 1355 EDT ON 5/1/15 * * * Curtiss-Wright provided an update to state that their root cause analysis is still in progress and they anticipate completion within 60 days. Notified NRR Part 21 Group (via email), R1DO (Gray), and R2DO (Ehrhardt). * * * UPDATE FROM JOHN DeBONIS (VIA EMAIL) TO STEVEN VITTO AT 1256 EDT ON 6/30/15 * * * Curtiss-Wright provided an update to state their root cause analysis findings and corrective actions. Corrective actions are estimated to be completed within 12 months. "The following plants were supplied 0867F MS-SRVs: Pilgrim (Model 09J-001) Quantity Shipped = 8 FitzPatrick (Model 09H-001) Quantity Shipped = 4, Quantity on order= 8 Hatch 1 and 2 (Model 09G-001) Quantity Shipped = 24, Quantity on order= 12 "The following plants will be supplied 0867F MS-SRVs: Hope Creek (Models 14J-001, 14J-002) Quantity on order = 7 "Valves Currently Installed "Target Rock recommends valves currently installed be inspected to ensure the main piston shoulder has contact with the main disc stem shoulder. These inspections should be scheduled based on plant-specific indications of the potential for fretting. These inspections can be performed by removing the base assembly from the main body and physically measuring for shoulder-to-shoulder contact. "Should you have any questions regarding this matter, please contact Michael Cinque, Director of Program Management at (631 ) 293-3800." Notified NRR Part 21 Group (via email), R1DO (Dimitriadis), and R2DO (Suggs). * * * UPDATE AT 0803 EST ON 02/03/17 FROM JOHN DEBONIS TO JEFF HERRERA * * * "Target Rock, a business unit of Curtiss-Wright Flow Control Corporation (TR), previously submitted NID# 15428 (Ref. 1) regarding 0867F Series of Main Steam Safety Relief Valves (MSSRV). The purpose of this letter is to provide a final update on the status of the actions identified in NID# 15428 (Ref. 1 ). "TR has developed a design change that we have verified, though analysis and qualification testing, ensures testing on the available limited flow test facilities will not impart damage to our product. Qualification included both limited and full flow testing. Target Rock confirms this design change has no effect on either National Board certification or the performance required by the applicable Specification to support the plant safety analysis.TR will offer this design change as our recommended long term solution to all utilities who currently have installed or plan to install the 0867F Series Main Steam Safety Relief Valve model in their respective plants. Should you have any questions regarding this matter, please contact me [Alex DiMeo] at (631) 293-3800." Notified R1DO (Gray), R2DO (Walker) and Part 21 Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-03-17
50899 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-03-16 18:20 | 2015-03-17 02:57 | 2015-05-11 | HIGH PRESSURE COOLANT INJECT DECLARED INOPERABLE FOLLOWING SCHEDULED MAINTENANCE "At 1820 on March 16th, 2015, the High Pressure Coolant Injection (HPCI) system steam lines were re-pressurized following scheduled maintenance. Upon restoration, an alarm was received that indicated condensate may exist in the steam line. The system responded as designed but the alarm did not clear as expected. Without assurance that the condensate has been removed from the HPCI steam line, HPCI remains inoperable for reasons other than the planned maintenance. As a result, this condition is being reported under 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented fulfillment of the safety function at the time of discovery. "The health and safety of the public was maintained as the plant was in a normal condition with no initiating event in progress. "The NRC Resident Inspector has been notified." The licensee will also notify the State of Minnesota. * * * RETRACTION FROM RANDY SAND TO DANIEL MILLS AT 1445 EDT ON 5/11/15 * * * "On March 16, 2015, Northern States Power Minnesota reported a condition that could have prevented the fulfillment of a safety function under 10 CFR 50.72(b)(3)(v)(D). The High Pressure Coolant Injection (HPCI) System was declared inoperable for a reason other than planned maintenance due to the failure of the HPCI Steam Supply Drain Hi Level Bypass Level Switch to clear the high level alarm subsequent to actuation. "An engineering evaluation was performed and concluded that the function of the primary pathway to remove condensate remained unchallenged by the condition present on the level switch. This conclusion was also validated via thermography with the HPCI steam supply pressurized and bypass valve open. The verification that the primary pathway was functional provides reasonable assurance that the HPCI steam supply was always clear of condensate supporting the ability of HPCI to perform its required safety function. Therefore, the condition present on the level switch did not render HPCI inoperable. The conclusions of the engineering evaluation provide the basis for retraction of the ENS report made on March 17. "The NRC Resident Inspector has been notified." The licensee will also notify the State of Minnesota. Notified R3DO (Peterson). | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-03-17
50898 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-03-13 | 2015-03-16 15:10 | 2015-03-16 | AGREEMENT STATE REPORT - LOST NUCLEAR DENSITY GAUGE The following information was obtained from the Commonwealth of Pennsylvania via email and fax: "The Department [Pennsylvania Department of Environmental Protection] received a phone call on March 13, 2015 regarding a lost/missing nuclear density gauge. This event is reportable within 24-hours per 10 CFR 20.2201 (a)(1)(i). "The gauge was last used on December 16, 2014 at a job site in New Brighton, PA and discovered missing during the next routine quarterly inventory. The case and lock were both intact inside a locked storage area. There were no signs of forced entry and nothing else was missing. The employee, after being questioned, claims no knowledge of the whereabouts of the gauge. "[Gauge] Model: Troxler 3411B Serial #: 8254 Isotope: Cs-137 & Am-241 Activity: 9 mCi Cs-137 and 44 mCi Am-241 "The police have been notified. The Department will conduct an in depth reactive inspection. A press release will be issued requesting information from the public. More information will be provided upon receipt." Event Report ID No: PA 150006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-03-24
50897 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-03-12 | 2015-03-16 15:05 | 2015-03-16 | AGREEMENT STATE REPORT - INABILITY TO RETRACT SOURCE TO ITS SHIELDED POSITION The following information was obtained from the Commonwealth of Pennsylvania via email and fax: "The Department [Pennsylvania Department of Environmental Protection] was notified of this event on Friday, March 13, 2015. It is reportable within 24 hours as per 10 CFR 34.101(a)(2) and 30.50(b)(2). "A 68 curie (Ci) iridium-192 (lr-192) source could not be retracted back into the exposure device. The guide tube had become disconnected when the lr-192 source was in the collimator. "The guide tube was not properly connected to the front of the exposure device, therefore preventing the source to be fully retracted back into the device. This event was due to human error. "The repair/retrieval was performed quickly by the assistant RSO who received a total of 5 mR during the entire process. A reactive inspection is planned by the [Pennsylvania DEP] regional office." Event Report ID No: PA150005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-03-24
50896 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-03-15 12:27 | 2015-03-15 13:29 | 2015-03-15 | PLANT SHUTDOWN DUE TO FAILURE TO RESTORE CONTAINMENT FAN COOLER UNIT "This 4 hour notification is being made pursuant to the requirements of 10 CFR 50.72(b)(2)(i), for 'The initiation of any nuclear plant shutdown required by the plant's Technical Specifications'. "Salem Unit 1 has initiated a unit shutdown at 1227 [EDT] in accordance with Technical Specification Action Statement 3.6.2.3, Action A, for inoperability of the 14 Containment Fan Cooler Unit. Technical Specification 3.6.2.3, Action A requires that with one or two Containment Fan Cooler Units inoperable, operability must be restored within 7 days, or be in at least Hot Standby (Mode 3) within the next 6 hours and in Cold Shutdown (Mode 5) within the following 30 hours. "The 14 Containment Fan Cooler Unit was declared inoperable on March 8, 2015, at 1158 EDT, following a trip of its low speed breaker on thermal overload during a scheduled surveillance test. "13 Chiller is tagged for scheduled maintenance. "The NRC Resident Inspector has been notified." Unit 1 is proceeding to Mode 5. There is no effect on Unit 2. The licensee will notify the Lower Alloways Creek Township, the State of New Jersey, and the State of Delaware. | 55 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2015-03-15
50895 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-03-14 17:08 | 2015-03-14 23:32 | 2015-03-14 | DIGITAL RADIATION MONITORING SYSTEM FAILED "At 1708 EDT on March 14, 2015, Beaver Valley Power Station (BVPS) Unit 2 determined that the Digital Radiation Monitoring System (DRMS) was not operating. This resulted in a loss of radiation monitor capability to alarm and indicate in the control room. BVPS Unit 2 DRMS was declared non-functional. Repair efforts were initiated and compensatory measures were initiated. "The radiation monitoring computer system is a stand-alone system. No cyber interference is suspected. "At 2056 EDT on March 14, 2015, following initial investigation and repairs, BVPS Unit 2 emergency assessment capability was restored in conjunction with DRMS restoration. "Since the BVPS Unit 2 DRMS was non-functional, this event resulted in a loss of emergency assessment capability and is reportable per 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-03-14
50894 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-03-14 12:07 | 2015-03-14 19:19 | 2015-03-14 | UNPLANNED ACTUATION DURING SURVEILLANCE TEST "On March 14, 2015 at 1207 EDT, operators were performing steps to disable an automatic actuation signal to the B-train Auxiliary Feedwater system (AFW), when a valid actuation signal was received on B-train only. Both motor driven Auxiliary Feedwater pumps were already running and feeding forward. The B-train discharge valves went from throttled to fully open. The AFW discharge valves were restored to their previous positions without any adverse impacts on the plant. Decay heat removal was still being removed through the Atmospheric Relief Valves." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-03-14
50893 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-03-14 04:29 | 2015-03-14 08:07 | 2015-03-14 | AUTOMATIC REACTOR TRIP ON SYSTEM INJECTION ACTUATION SIGNAL "Vogtle Unit 2 was operating in Mode 1 at 100% rated thermal power. At 0429 EDT a Unit 2 automatic Reactor Trip and Safety Injection / Steamline Isolation occurred. All systems operated as expected and all control rods fully inserted. The Safety Injection was terminated at 0447 EDT and the emergency operating procedures were exited at 0522 EDT. Unit 2 is stable in Mode 3 with decay heat removal via the Auxiliary Feedwater system and the atmospheric relief valves. A response team is investigating the cause of the event. Unit 1 was unaffected by the event. "NRC Senior Resident Inspector was notified and is at plant site for investigation." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2015-03-14
50892 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2015-03-04 | 2015-03-13 19:29 | 2015-03-13 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER OPEN IMPROPERLY DURING MAINTENANCE WORK The following is a synopsis of information received from the State of Utah: Two workers entered a confined space to perform work near a fixed gauge. One of the workers remained in the area for 9 minutes and the other remained in the area for 90 minutes. It was later determined that the fixed gauge shutter had not been closed. Surveys conducted by the licensee to measure dose rates in the area where the workers had been present indicated dose rates ranging from 0.5 mR/hr to 4 mR/hr. Utah inspectors performed confirmatory measurements that indicated dose rates between 0.97 mR/hr and 2.2 mR/hr. Utah Event ID Number: UT150001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2015-03-23
50891 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-03-13 12:30 | 2015-03-13 18:59 | 2015-04-23 | LOW PRESSURE COOLANT INJECTION DECLARED INOPERABLE "This condition is reported in accordance with 10 CFR 50.72(b)(3)(v). On 3/12/15, during surveillance testing on LPCI [Low Pressure Coolant Injection] Loop Select Instrumentation, a degraded component was discovered. At 1230 CDT on 3/13/15, LPCI was declared INOPERABLE in accordance with Technical Specification requirements. All remaining ECCS systems remain available and operable. "The NRC Resident Inspector has been informed." * * * UPDATE AT 0210 EDT ON 03/14/15 FROM SCOTT AREBAUGH TO S. SANDIN * * * "At 0105 CDT on 3/14/15, the subject component has been replaced and retested with satisfactory results. LPCI INOPERABLE condition was exited at 0105 CDT and the LPCI System is OPERABLE." The licensee informed the NRC Resident Inspector. Notified R3DO (Orth). * * * RETRACTION AT 1737 EDT ON 04/23/15 FROM BOB MURRELL TO DONG PARK * * * "The purpose of this notification is to retract a previous report made on 3/13/15 at 1859 EDT. Notification of the event to the NRC was initially made as a result of an event where Low Pressure Coolant Injection (LPCI) was declared inoperable due to the discovery of a degraded LPCI Loop Select timing relay. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the LPCI Loop Select timing relay was tested in a configuration that affected time delay measurements. This testing configuration was revised in 2012 following a modification to the LPCI Loop Select Logic, STP 3.3.5.1-29. The inadequate testing configuration adversely affected the time delay when the test equipment was installed. A revision to STP 3.3.5.1-29 was completed to resolve the inadequate testing configuration. Subsequent bench testing, performed to mimic plant installed configuration, of the affected relay, was completed. This testing demonstrated that the relay could be tested in a manner that provided acceptable results, and it has been concluded that the relay would have performed its required safety function up to when it was tested on 3/13/15. "Therefore, this event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73. "The NRC Resident Inspector has been notified." Notified R3DO (Valos). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-03-13
50890 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-03-13 11:08 | 2015-03-13 17:12 | 2015-03-13 | POSITIVE RANDOM FITNESS FOR DUTY TEST RESULT A contract employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2015-03-13
50889 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2015-03-13 10:34 | 2015-03-13 17:08 | 2015-03-13 | PLANT EMPLOYEE TESTED POSITIVE FOR BANNED SUBSTANCE A non-licensed corporate employee tested positive for a banned substance. The individual's unescorted access has been revoked. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2015-03-13
50888 | 0 | WEIR VALVES AND CONTROLS USA INC. |  |  |  |  | 2015-03-13 | 2015-03-13 15:48 | 2015-03-13 | IMPROPER WELD USED ON GATE VALVE COVER The following was received from the licensee via email: "This notification is being submitted pursuant to the guidelines of 10 CFR Part 21 to report that, during the manufacturing of a replacement cover for a 24 inch gate valve on the reactor recirc line at Exelon LaSalle, Weir Valves and Controls used a weld that was not compliant to ASME Ill Subsection NB requirements. "During review of the weld at site, the question was raised based on site procedures required a 2:1 profile in accordance to EPRI guidelines. During review of the documentation to determine if the 2:1 profile was required in this case, Weir Valves and Controls determined that improper weld call out was used on the design prints. The weld was corrected at site to meet the both ASME Ill Subsection NB requirements and EPRI guidelines. "Weir Valves and Controls has performed an extent condition review and has concluded that no other undersized welds were made and delivered to any other operating sites. "The root-cause of the issue was the improper call-out of the weld by design engineering. "Weir Valves and Controls is performing corrective actions to ensure future re-occurrences cannot occur in design engineering." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-03-13
50887 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-03-13 11:00 | 2015-03-13 14:25 | 2015-03-13 | UNANALYZED CONDITION "On March 13, 2015, Watts Bar determined that information received from Westinghouse represented an unanalyzed condition. The information challenged the current Unit 1 Fire Protection Report (FPR) analysis for 10 CFR 50 Appendix R. The current FPR analysis used a duration of 120 seconds before a low pressurizer pressure safety injection (SI) signal would be received due to a postulated failed open pressurizer power operated relief valve (PORV) from an Appendix R fire outside of the control building. During discussions with Westinghouse, Watts Bar determined that the 120 second value was non-conservative and not intended for this application. Recent information from Westinghouse indicates that a Sl signal would be received in approximately 34 seconds. "This information places Watts Bar Unit 1 in an unanalyzed condition because the original analysis assumed that a Sl signal would not be received from fire-induced failures in the associated fire areas. While the existing Watts Bar Unit 1 Appendix R procedures direct operators to isolate the pressurizer PORV, the procedures did not have steps to mitigate and terminate the Sl. Without mitigating actions, the Sl would likely challenge the reactor coolant system boundary due to water relief through the remaining pressurizer PORV and/or safety valves. "As a compensatory measure, Watts Bar has established administrative equipment controls to preclude the consequences of a spuriously opening pressurizer PORV. In addition, a compensatory measure in the form of fire watches has been established in areas where a fire could result in a spurious opening of a pressurizer PORV. "This issue is being reported under 10 CFR 50.72(b)(3)(ii)(B), 'unanalyzed condition that significantly degrades plant safety.' "The Watts Bar Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-03-13
50886 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-03-05 | 2015-03-13 11:20 | 2015-03-13 | AGREEMENT STATE REPORT - RESEARCH IRRADIATOR DOOR FAILED TO OPEN The following was received from the State of Tennessee via email: "The door to a J. L. Shepherd Mark 1-68 irradiator containing 10,000 curies (assayed 2/11/2002) of Cesium 137, being used to irradiate mice, would not open. The source was determined to be in the safe position. St. Jude trustworthiness-approved radiation safety and biomedical engineering (BME) personnel responded and attempted to extract the mice without success. A call to the licensed service representative went unanswered. The Associate Radiation Safety Officer who was present approved BME [personnel] to take measures to disengage the door. This involved breaking security seals on the timer control mechanism and door interlock box. Also, the lock on the interlock box was cut since the key was not present. Strict radiological controls were employed including; badging all personnel, survey meter present, continuous health physicist presence, confirmation of source in safe position, and unplugging irradiator to ensure the source could not move. The animals were extracted without incident. The irradiator was locked and removed from service. The service representative came March 11, 2015, and repaired the unit such that it was fully operational. Evidently, the door interlock switch that had been replaced in January had failed." TN Event Report ID Number: TN-15-036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-03-23
50885 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-03-13 09:19 | 2015-03-13 12:56 | 2015-03-13 | LOSS OF SECONDARY CONTAINMENT DUE TO VENTILATION PLENUM DOOR OPEN "On March 13, 2015 at 0919 [EDT], Secondary Containment became inoperable, requiring a Technical Specification 3.6.4.1 entry for failure to meet SR [Surveillance Requirement] 3.6.4.1.1 on Unit 1 and Unit 2. "The inoperability was caused by Zone 2 differential pressure lowering to less than 0.25 inches WC [water column] when an air handling plenum door was opened for an extended period. "The plenum door was closed and differential pressure restored to greater than 0.25 inches WC at 0930 on March 13, 2015. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev. 3 Section 3.2.7, as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-03-13
50884 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2015-03-13 09:28 | 2015-03-13 12:48 | 2015-03-13 | OFFSITE NOTIFICATION TO OSHA DUE TO ONSITE PLANT EMPLOYEE PASSING AWAY "On March 13, 2015 at 0928 EDT, a notification to OSHA [Occupational Safety and Health Administration] was initiated due to an employee experiencing a non-work related medical event that resulted in the employee passing. When the issue was identified, the station first aid team responded to administer first aid. Subsequent to the employee passing, a report was made to OSHA in accordance with federal requirements. This event is reportable to the NRC per 10 CFR 50.72(b)(2)(xi) since another governmental agency was notified of this employer referral medical event." The plant employee was in a building within the protected area and was not contaminated. The licensee notified the NRC Resident Inspector and will notify the local government of the event. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-03-13
50883 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-03-12 19:13 | 2015-03-13 11:17 | 2015-03-13 | POSITIVE RANDOM FITNESS FOR DUTY TEST "A licensed employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2015-03-13
50882 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2015-03-13 01:00 | 2015-03-13 08:43 | 2015-04-07 | FUEL ASSEMBLY MIS-ORIENTED RESULTING IN A UNANALYZED CONDITION "On March 13, 2015 at 0100 [CDT], it was identified that fuel assembly QAD224 was mis-oriented 180 degrees at core location 51-40. The intended orientation was [southeast]. However the assembly was identified as being [northwest]. This issue was identified during the core verification process. In the current core configuration, there is not a bounding analysis that assures adequate Shutdown Margin. "This event is reportable under 50.72(b)(3)(ii) as an unanalyzed condition that significantly degraded plant safety. "The NRC Resident Inspector has been notified." * * * EVENT RETRACTION FROM RICK MOON TO JOHN SHOEMAKER AT 1051 EDT ON 4/7/15 * * * "The purpose of this notification is to retract the ENS notification made on March 13, 2015 (ENS 50882). An evaluation has determined that Shutdown Margin was met with the mis-oriented fuel bundle. Therefore, the threshold for reporting the issue as a degraded or unanalyzed condition was not met (NUREG 1022 Revision 3 - Event Report Guidelines Section 3.2.7). "The NRC Resident Inspector has been notified." Notified the R3DO (Skowkowski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-03-13
50881 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-03-12 09:00 | 2015-03-12 16:06 | 2015-03-19 | LOSS OF THE SEISMIC MONITORING COMPUTER "In accordance with 10 CFR 50.72(b)(3)(xiii), this notification reports a loss of Emergency Preparedness assessment capability with the unplanned inoperable condition for the Byron seismic monitor. Specifically, the seismic monitor was declared non-functional at 0345 CST on March 7, 2015 following an unplanned loss of the seismic monitoring central computer. This condition adversely impacted the capability to perform an ALERT EAL (HA4) assessment in accordance with the Radiological Emergency Plan Annex. The loss of assessment capability is reportable to the NRC within 8 hours of the discovery in accordance with 10 CFR 50.72(b)(3)(xiii) "The seismic recorder was reset by Plant Engineering at 0440 CST on March 8 2015, which restored the seismic monitoring system to full capability. "The unplanned non-functional condition of the seismic monitor was entered into the Byron CAP [Corrective Action] Program when the condition was discovered. Initially it was determined that the condition did not meet the requirements for an ENS notification as it was concluded that it did not substantially impair Byron station's emergency assessment capability in the event of an earthquake. Upon further review, at 0900 CDT on March 12, 2015, it was concluded that an ENS notification was warranted because the monitor was specifically Cited in the Emergency Action Level (EAL) HA4 threshold for identifying an ALERT due to an OBE (Reference procedure EP-AA-1002, Addendum 3, 'Emergency Action Levels for Byron Station'). "A follow-up written notification is not required for this notification under 10 CFR 50.73. The NRC Resident Inspector has been notified." The State of Illinois Resident Inspector has been notified. * * * UPDATE AT 1144 EDT ON 3/19/15 FROM BRIAN CURRIER TO MARK ABRAMOVITZ * * * "Upon further review of this event for the time period of 3/07/12 through 3/17/15, Byron Station has identified six previous occurrences where the Seismic Monitor was declared non-functional, which impacted the capability to perform an ALERT EAL (HA4) assessment in accordance with the Radiological Emergency Plan Annex. These occurred on November 6, 2014; April17, 2013; January 2, 2013; October 10, 2012; July 18, 2012 and July 9, 2012. "The NRC Resident Inspector has been notified." Notified the R3DO (Roach). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-03-12
50879 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-03-10 18:14 | 2015-03-11 11:54 | 2015-03-11 | NON-LICENSED SUPERVISORY EMPLOYEE TESTED POSITIVE FOR ALCOHOL A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector was notified and the NY Public Service Commission will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2015-03-11
50878 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-03-11 06:21 | 2015-03-11 09:30 | 2015-03-11 | AUTOMATIC REACTOR TRIP DUE TO A NUCLEAR INSTRUMENTATION SIGNAL "At [0621 EDT] on 3/11/2015, Sequoyah Unit 1 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 1 is currently being maintained in Mode 3 at NOT/NOP, approximately 547 F and 2235 psig, with auxiliary feedwater supplying decay heat removal via the steam generators and condenser steam dumps. "The immediate cause of the trip was a Power Range Nuclear Instrumentation negative rate signal, caused by a malfunction in the rod control system. There was no associated work in progress related to this and all systems were normally aligned. "Current Temperature and Pressure - temperature is 547 degrees F and stable, pressure is 2235 psig and stable. There is no indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from Off-Site power. There is no operational impact to Unit 2. Unit 2 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-03-11
50877 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2015-02-27 | 2015-03-10 16:50 | 2015-07-13 | AGREEMENT STATE REPORT - NUCLEAR MEDICINE TECHNOLOGIST RECEIVED OVEREXPOSURE The following was received from the State of Arizona via email: "On February 27, 2015, the licensee received notification from Landauer that one of their nuclear medicine technologists received a dynamic whole body dose of 11 Rem for the wear period of September 1, 2014 to October 31, 2014. The technologist only works at the hospital 1 day a week. "The Agency [State of Arizona] continues to investigate the event." Arizona First Notice: 15-006 * * * UPDATE ON 7/13/15 AT 1650 EDT FROM BRIAN GORETZKI TO JEFF HERRERA * * * The following update was received from the State of Arizona via email: "The Agency [Arizona Radiation Regulatory Agency] has made a determination that the 11 Rem exposure to the individual at Phoenix Baptist Hospital is valid and has assigned the technologist 10 Rem in year 2014 and 1.01 Rem in year 2015." Notified R4DO (Gaddy), INES National Officer (Milligan) and NMSS Events (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2015-03-18
50876 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-03-09 10:00 | 2015-03-10 16:23 | 2015-03-10 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL GAUGE SOURCE NOT FULLY RETRACTED The following report was received from the Tennessee Department of Environment and Conservation Division of Radiological Health via email: "The licensee called to report a radioactive material gauge with stuck source in the closed position. The gauge is a Vega Model SHLM-C2, with three 37 millicurie Cs-137 rod sources, SNs 2609, 2611, and 2612. Radiation measurements indicated the source was in the shielded position. On March 9, 2015, a Vega service representative visited the site and inspected the gauge. It was discovered the source was not completely retracted. The gauge remains bolted to the process vessel, and is scheduled for replacement after additional retraction or equivalent means to secure the source has been implemented. No additional radiation exposure to personnel occurred. Current radiation levels are the same as found under normal conditions when the source is in the retracted position." TN State Event Report ID No: TN-15-031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-03-18
50875 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2015-03-09 15:00 | 2015-03-10 12:28 | 2015-03-10 | TEMPORARY LOSS OF POWER TO AIR MONITORING PUMPS "The air monitoring vacuum pumps were disabled for approximately 20 minutes. Due to an unplanned power outage, the soft water supply to the air monitoring vacuum pump seals on the 2nd floor of the Feed Materials Building (FMB) was lost. These pumps provide vacuum for the stack monitoring and personnel area monitoring systems in the FMB. The secondary and tertiary water supplies to the pumps were not available when needed. This caused the vacuum pumps to be shut down until a temporary water supply could be established. A temporary water supply was reestablished to the pump seals. The pumps were restored to service at approximately 1520 CDT on 03/09/2015." The licensee has contacted NRC Region II inspector David Hartland regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2015-03-10
50874 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-03-09 15:21 | 2015-03-09 17:38 | 2015-03-10 | TECH SPEC REQUIRED SHUTDOWN DUE TO SWING BUS AUTOMATIC THROWOVER FAILURE "While performing a Technical Specification surveillance functional test of the [Low Pressure Coolant Injection] LPCI swing bus automatic throwover scheme, the throwover function failed, rendering LPCI Loop Select inoperable. Time of [the] event was 1521 [EDT]. Inoperable LPCI Loop Select results in entry into Tech Spec 3.0.3. Power reduction activities were briefed and power reduction commenced at 1615. Maintenance is currently implementing a contingency work order to correct the auto throwover failure. "This report is made pursuant to 10 CFR 50.72(b)(2)(i), initiation of plant shutdown required by the plant's Technical Specifications; and 10 CFR 50.72(b)(3)(v)(D), an event or condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident." Offsite and Emergency power remain available. The NRC Resident Inspector was notified. * * * UPDATE FROM KELLEY BELLENKY TO DANIEL MILLS AT 0123 EDT ON 3/10/2015 * * * "On March 9, 2015, at approximately 1521 [EDT], while performing a functional test of the LPCI swing bus automatic throwover scheme, the throwover function failed, rendering LPCI Loop Select inoperable. Tech Spec 3.0.3 was entered and power reduction commenced at 1615 [EDT]. Power was lowered to approximately 80%. Maintenance led a troubleshooting process that found and corrected the equipment problem. At approximately 2311 [EDT], the limiting condition for operating was cleared and LPCI Loop Select was declared operable. Tech Spec 3.0.3 was exited at that time." The licensee notified the NRC Resident Inspector. The plant has returned to 100% power. Notified R3DO (Orth). * * * UPDATE FROM DAVID COSIO TO CHARLES TEAL AT 1253 EDT ON 3/10/15 * * * The LCO and LPCI operability declared was at 2211 EDT NOT 2311 EDT. Notified R3DO (Orth). | 83 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-03-09
50873 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-03-09 09:57 | 2015-03-09 13:10 | 2015-03-09 | MILLSTONE UNIT 2 SITE STACK RADIATION MONITOR SAMPLE PUMP TRIP On March 9, 2015 at 0957 EDT, the Millstone Site Stack Radiation Monitor RM 8169 sample pump tripped. This resulted in a loss of assessment capability. Compensatory measures have been put in place to provide chemistry sampling. The cause is under investigation and the Instrument & Controls Department is troubleshooting and repairing the sample pump. The NRC Resident Inspector, Connecticut Department of Environmental Protection, and the Town of Waterford have been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-03-09
50872 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2015-03-07 21:40 | 2015-03-08 05:21 | 2015-03-08 | SPECIFIED SYSTEM ACTUATION DUE TO LOSS OF ONE RESERVE STATION SERVICE OFFSITE POWER SOURCE "On March 7, 2015, at 2140 CST, with the plant in Mode 5, Refueling, the RSS#2, one of two Reserve Station Service offsite power sources, de-energized. This loss of RSS#2 caused the de-energization of the Division 2 Safety Bus, which caused a valid start signal to the logic of the Division 2 Emergency Diesel Generator. No start occurred, however, due to the diesel being in the maintenance mode. Division 2 Standby Service Water, which was being run for system fill and vent as well as surveillance testing, also lost power. "At the time RSS#2 was lost, the Division 2 Diesel generator and Division 2 Standby Service Water were inoperable for the Refuel Outage 18 Division 2 maintenance window. "Division 1 systems and RSS#1 were not affected by the power loss and continued to operate normally. There were 5 control building dampers and 1 floor drain air operated valve that repositioned due to the loss of power. "The cause of RSS#2 de-energization is still under investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-03-08
50871 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  | 20000 KW TEST | 2015-03-07 08:30 | 2015-03-07 16:55 | 2015-03-07 | LIMITING CONDITION FOR OPERATION NOT MET DUE TO EMERGENCY SUMP PUMP INOPERABLE "On March 7, 2015, at 0830 EST, the NCNR (NIST Center for Neutron Research) discovered a probable violation of the Limiting Condition for Operations of the TR-5 Technical Specifications (TS), 3.3.2, Specification (1), while performing maintenance during the scheduled reactor shutdown period. This initial report is being made in accordance with TR-5 TS 6.7.2.d. "The TS is as follows: 'TS 3.3.2 Emergency Core Cooling; Specification: The reactor shall not be operated unless: (1) The D2O (deuterium oxide) emergency core cooling system is operable, and (2) A source of makeup water to the D2O emergency cooling tank is available.' "The discovery was made at 0830 EST on March 7, 2015, that the local disconnect switch for the emergency sump pump was in the disconnect position. The last time that it was verified operable was on July 2, 2014, when the annual surveillance of operability was performed. There was no maintenance performed on the emergency sump pump, nor is there any other known reason that the switch would have been placed in the disconnect position since July 2, 2014. "After the discovery the sump pump disconnect switch was immediately placed in the connect position. "The emergency core cooling system, in the event of loss of core coolant, provides sufficient D2O, to passively provide adequate coolant for ~ 2.5 hours to cool the fuel and protect against the release of fission products. That part of the emergency core cooling system was and remains operable and is not part of this violation. "The emergency core cooling system employs one sump pump to return spilled coolant to the overhead storage tank. There is only enough D2O in the overhead storage tank to provide cooling for 2.5 hours on a once through basis. Because there is only one sump pump, it must be operational whenever the reactor is operational (TS 3.3.2 (1)). In the event that that pump fails or is inoperable and the D2O supply in the overhead storage tank is exhausted, domestic water or a suitable alternative would be used to furnish water for once through cooling (TS 3.3.2 (2)). A source of makeup water to the D2O emergency cooling tank was and remains available and is not part of this violation. "The violation that is the subject of this report is that the sump pump was discovered inoperable and may have been inoperable since July 2, 2014, which includes periods of reactor operation. That is a violation of TS 3.3.2 (1)." The licensee is conducting an investigation into this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | MD | NPR | [5 empty] | 0 | 2015-03-07
50870 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-03-07 11:55 | 2015-03-07 15:05 | 2015-03-07 | CONTAINMENT DECLARED INOPERABLE DUE TO CONTAINMENT FAN COIL LEAK "At 1155 CST on March 7, 2015, a small cooling water leak was identified on the 21 Containment Fan Coil Unit east face u-bend on the north east corner bottom bundle. Unit 2 Containment was declared inoperable, which required entry into Technical Specifications (TS) LCO 3.6.1, Condition A, Containment inoperable, applicable in MODES 1, 2, 3, and 4. Immediate actions were taken to isolate the Fan Coil Unit within 1 hour from the initial identification of the leak. 21 Containment Fan Coil Unit was isolated, Containment was declared operable and TS 3.6.1 Condition A was exited at 1220 CST on 3/7/15. "This condition is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. "The plant remains in a safe condition and there was no effect to the health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | [9 empty] | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-03-07
50869 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-03-05 16:18 | 2015-03-05 18:20 | 2015-03-26 | UNATTENDED SAFEGUARDS INFORMATION Discovered improperly controlled safeguards information. A compensatory evaluation was conducted. The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1722 EDT ON 3/36/2015 FROM RAFAEL GONZALES TO MARK ABRAMOVITZ * * * This event is being retracted because the event was determined to be a loggable event and not a one hour report. The licensee notified the NRC Resident Inspector. Notified the R4DO (Gaddy), ILTAB (Allston), and the 73.71 Group (via e-mail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-03-05
50868 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2015-03-04 | 2015-03-05 17:38 | 2015-03-05 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENTS DUE TO A MISALIGNED GAMMA KNIFE On March 4, 2015, the licensee notified the State of Oregon that they discovered that their Elekta Leksell Gamma Knife was off target by approximately 1.87mm. This was allegedly due to maintenance performed in early January 2015, that resulted in a misaligned couch. Since the misalignment, eight patients have undergone gamma knife surgery. The licensee Medical Physicist is currently evaluating each case to determine whether an underdose/overdose occurred to any of the patients. The Elekta Leksell Gamma Knife is licensed for up to 6.6 kCi of Co-60. The State of Oregon will update this report as more information becomes available. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2015-03-13
50867 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-03-05 | 2015-03-05 15:42 | 2015-03-05 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO ASSISTANT RADIOGRAPHER The following information was obtained from the State of Oklahoma via email: "We [Oklahoma Department of Environmental Quality] have been notified by Desert NDT (OK-32104-01) located in Elk City, OK, that the dosimetry report for the February 2015 monitoring period showed a dose of 5780 mR for one of their assistant radiographers. They also report that the individual's daily pocket dosimetry readings for this period do not correlate with this result. The investigation is ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-03-13
50866 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-03-05 04:06 | 2015-03-05 05:35 | 2015-03-06 | UNIT 2 DECLARES UNUSUAL EVENT DUE TO INABILITY TO VALIDATE A CONTAINMENT FIRE ALARM WITHIN 15 MINUTES "The Instrument Air Containment Isolation failed closed on Unit 2. This isolated normal letdown / excess letdown and required Pressurizer level to be maintained by diverting Pressurizer level to the Pressurizer Relief Tank. The Pressurizer Relief Tank rupture disc ruptured which resulted in a fire alarm in Unit 2 Containment. The fire alarm could not be validated within 15 minutes which resulted in a declaration of an Unusual Event based on EAL HU2.1. The loss of Instrument Air to Unit 2 Containment resulted in a loss of cooling to the reactor vessel gap and support cooling systems. Due to the loss of reactor vessel ventilation systems a plant shutdown to Mode 3 has been initiated. No radioactive releases to the environment are in progress or expected to occur. The public health and safety has not been jeopardized." The licensee informed state/local agencies and the NRC Resident Inspector and does plan to issue a press release. Notified other Federal Agencies (DHS SWO, FEMA Ops, FEMA NWC, NICC Watch Officer and NuclearSSA). * * * UPDATE AT 0130 EST ON 03/06/15 FROM TERRY BACON TO DANIEL MILLS * * * "At 1725 [CST] on 3/5/15 Instrument Air to Unit 2 containment was established. Letdown was then reestablished. These actions stabilized the plant and stopped the 30 GPM [gallons per minute] identified leakage out of the PZR Relief Tank rupture disc into containment. This condition is what caused the fire detection alarm in containment, and is also Unusual Event criteria. Unit 2 containment was entered and it was confirmed that NO fire existed in containment. The Unusual Event was terminated at 0018 CST on 3/6/15 based on no fire and no identified RCS leakage into containment. The plant is currently in Mode 3. The health and safety of the public was not jeopardized." The licensee informed state/local agencies and the NRC Resident Inspector and does plan to issue a press release. Notified R3DO (Stone), EO (Ross-Lee) and IRD (Stapleton). Notified other Federal Agencies (DHS SWO, FEMA Ops, FEMA NWC, NICC Watch Officer and NuclearSSA). | 0 | 92 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 3 | MN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-03-05
50865 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-03-04 09:00 | 2015-03-04 19:31 | 2015-03-04 | AGREEMENT STATE REPORT - SHUTTER NOT OPERATING PROPERLY ON NUCLEAR PROCESS GAUGE The following information was received from the Los Angeles Radiation Management Department via facsimile: "On March 4, 2015, the Radiation Safety Officer (RSO), Exxon Mobil Oil Corporation (License #0113-19) reported to LA County Radiation Management that the shutter on one of their Thermo Nuclear gauges was not operating such that it could be completely closed per the manufacturer's design/specifications. This issue was discovered while Exxon Mobil was testing the integrity of all sources and source holders located in the area affected by the explosion that took place on February 18, 2015 (5010 #021815). "At approximately 0900 [PST], [the RSO], along with a licensed Thermo Nuclear technician discovered that the Thermo Nuclear source holder, would not close completely, despite multiple attempts by the Thermo Nuclear technician. A radiation survey was performed around the source holder and the surrounding area was taped off with caution tape. The radiation level surrounding the source holder was found to be approximately 4 mR/hr. Exxon Mobil identified the source holder as Thermo Nuclear Model 5197, S/N CN-2435, with a 100 mCi Cs-137 source (S/N B8849). "Upon discovery, [the RSO] immediately contacted LA County Radiation Management to report the findings. In addition to taping off the area, [the RSO] stated that the source is still in its normal position, approximately 10 feet from the ground and away from any routine traffic. Exxon Mobil has 24 gauges in the area that [were] impacted by the explosion on February 18, 2014. [The RSO] stated that only 11 gauges have been inspected thus far for leakage and damage. The remaining gauges will be inspected by the end of the week. Should Exxon Mobil discover another damaged source or source holder, they have been instructed to report the findings to LA County Radiation Management immediately." California 5010 Number: 030415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-03-12
50864 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2015-03-04 14:08 | 2015-03-04 14:41 | 2015-03-04 | OFFSITE NOTIFICATION DUE TO ELEVATED TRITIUM DETECTED ONSITE "On March 3, 2015, PSEG [Public Service Enterprise Group] confirmed the presence of tritium at a concentration of approximately [0.01] microCurie/ml in ice samples taken in a small area immediately adjacent to the north side of the Hope Creek Turbine Building. The New Jersey Department of Environmental Protection Bureau of Nuclear Engineering was notified at 1408 [EST] on March 4, 2015, in accordance with NEI 07-07, Industry Ground Water Protection Initiative. "Samples were taken and analyzed in response to ice which was observed to be forming along the exterior of the north Turbine Building wall. Sample results show detectable tritium is confined within the site boundary and there is no impact to the health and safety of the employees or the public. "A catch containment was installed in the affected area. PSEG is continuing to evaluate this issue and develop corrective actions. "The licensee has notified the NRC Resident Inspector." The local Township will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-03-04
50863 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-03-04 10:55 | 2015-03-04 14:11 | 2015-03-04 | SUPPLEMENTAL WORKER FOUND WITH SYNTHETIC URINE A non-licensed, non-supervisory supplemental worker was found with synthetic urine on their person during a search at the security entrance station. The individual's access was terminated on site and in PADS. The NRC Resident Inspector and NRC Regional Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 26.719 |  |  |  | 0 | 2015-03-04
50862 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-03-03 16:01 | 2015-03-04 11:52 | 2015-03-04 | AGREEMENT STATE REPORT - IRRADIATOR SOURCE WOULD NOT FULLY LOWER TO SHIELDED POSITION The following report was received from the Texas Department of State Health Services via email: "On March 4, 2015, the licensee reported that a malfunction had occurred involving its J.L. Shepherd Mark I, Model 30, self-contained irradiator. [The] irradiator contains a J. L. Shepard Type 6810, 10,000 curie, Cs-137 source with serial number 85CS26. The source would not fully raise nor would it lower into the fully shielded position. The interlock system functioned as designed and the irradiator door remained locked. No one received any exposures and there is no risk for exposure as a result of this event. The licensee has contacted the manufacturer and scheduled repair. An investigation into this event is ongoing. An update will be forwarded in accordance with SA-300." Texas Incident #: I-9282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-03-12
50861 | 0 | UNIVERSITY OF MISSOURI |  |  |  |  | 2015-03-04 | 2015-03-04 10:50 | 2015-03-04 | MISSING TRITIUM EXIT SIGN A tritium exit sign was discovered missing during a December 2014 inventory. The missing tritium exit sign is an Isolite Model 2000 containing two (2) 10 Ci sources, S/N 11-38620 and 11-38621. It was originally scheduled for installation in December 2012 at the University of Missouri Power Station but not installed due to other extensive renovations. The licensee conducted an investigation contacting both the contractor who was to perform the install and the manufacturer before concluding that the sign was missing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-03-12
50860 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2015-03-03 08:37 | 2015-03-03 15:18 | 2015-03-03 | MOMENTARY LOSS OF SECONDARY CONTAINMENT DUE TO BOTH AIRLOCKS OPENING AT SAME TIME "Nine Mile Point Unit 1 (NMP1) had a momentary loss of Secondary Containment due to both Reactor Building Airlock doors being opened at the same time. "At 0837 [EST] on 03/03/2015, both Reactor Building Airlock doors at NMP1 were opened simultaneously for approximately 2 seconds. This results in a momentary loss of Secondary Containment operability (TS 3.4.3). The doors were closed and operability was restored. "Secondary Containment being inoperable is an 8 hour notification per 10CFR50.72(b)(3)(v)(C), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the Senior Resident NRC Inspector was notified." The licensee notified the State of New York. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-03-03
50859 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-03-03 11:01 | 2015-03-03 14:21 | 2015-03-03 | AUTOMATIC REACTOR TRIP DUE TO MAIN POWER TRANSFORMER BUSHING SHORT "In accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), this notification reports an automatic reactor trip on Byron Unit 1. The trip occurred following a trip of the Byron Unit 1 East Main Power Transformer (MPT). Initial indications appear that the MPT trip was caused by a large (~ 5 foot) section of ice that fell from a bus bar over the 1E MPT. This ice shorted out a MPT bushing, resulting in the unit trip. Reactor operators performed a manual start of the Auxiliary Feedwater System in response to the unit trip. All other safety systems responded as expected. "The plant trip occurred at 1101 CST on March 03, 2015. Unit 1 is presently in Mode 3 and stable. Unit 2, the opposite unit, is operating at 100% power and stable. This condition was entered into the Byron CAP Program. An investigation is in progress to determine the extent of required repairs, if any, required prior to unit restart. "This event resulted in the actuation of the Reactor Protection System with a subsequent Reactor Trip and therefore, requires notification to the NRC within 4 hours of discovery in accordance with 10 CFR 50.72(b)(2)(iv)(B). This event resulted in the manual actuation of the Auxiliary Feedwater System and therefore, requires notification to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(iv)(A). "This ENS call will be followed up with a Licensee Event Report (LER) within 60 days." All rods inserted during reactor trip, offsite power and emergency power sources are currently available and decay heat is being removed via the startup feedwater systems. No safety relief valves lifted as a result of the transient. The NRC Resident Inspector and the State of Illinois were notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-03-03
50858 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2015-03-02 09:20 | 2015-03-03 09:33 | 2015-03-03 | VACUUM PUMP SEAL WATER SUPPLY FAILURE "The air monitoring vacuum pumps were disabled for approximately 70 minutes. The soft water supply to the air monitoring vacuum pump seals on the 2nd floor of the Feed Materials Building (FMB) was shut down for annual shut down. These pumps provide vacuum for the stack monitoring and personnel area monitoring systems in the FMB. While the soft water system was shut down a sanitary well water supply was being used for the vacuum pump seals. A restriction in the sanitary water supply line interrupted the flow to the pump seals. This caused the vacuum pumps to be shut down until a temporary water supply could be established. A temporary water supply was reestablished to the pump seals. The pumps were restored to service at approximately 1030 CST on 03/02/2015." The licensee notified NRC Region II (Hickey) and will notify the state. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2015-03-03
50857 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2015-03-02 08:25 | 2015-03-02 18:31 | 2015-03-02 | NON-LICENSED SUPERVISORY CONTRACTOR TESTED POSITIVE FOR ALCOHOL "On March 2, 2015, Southern Nuclear Operating Company (SNC) had a non-licensed supervisory contractor employee confirmed positive result for alcohol during a fitness-for-duty test. The contractor employee's unescorted access to the plant has been terminated." The NRC Senior Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2015-03-02
50856 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-03-02 06:45 | 2015-03-02 10:22 | 2015-03-02 | AUTOMATIC REACTOR TRIP "At 06:45 EST on 3/2/2015, Sequoyah Unit 2 reactor/turbine automatically tripped. "Following the reactor trip, all safety-related equipment operated as designed. Auxiliary Feedwater automatically initiated as expected from the Feedwater Isolation Signal. "Unit 2 is currently being maintained in Mode 3 at NOT/NOP [normal operating temperature and pressure], approximately 548 F and 2235 psig, with auxiliary feedwater supplying decay heat removal via the steam generators and condenser steam dumps. "The immediate cause of the trip was a main generator C phase differential relay actuation. There was no associated work in progress related to this and all systems were normally aligned. It is currently not understood why the relay actuated. "Current Temperature and Pressure - temperature is 548 degrees F and stable, pressure is 2235 psig and stable. There is no indication of any primary/secondary leakage. All rods are inserted. Electrical alignment is normal, supplied from Off-Site power. The 2B Emergency Diesel Generator is currently unavailable for planned maintenance and will be returned to service prior to unit restart. There is no operational impact to Unit 1. Unit 1 continues to operate in Mode 1 at 100%. "There was no impact on public health and safety. Post-trip investigation is in progress and planned restart timeline has not yet been determined. "The licensee notified the NRC Resident Inspector" and the state. No primary or secondary safety valves lifted during this event. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-03-02
50855 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-02-28 | 2015-02-28 05:24 | 2015-03-11 | AUTOMATIC AUXILIARY FEEDWATER ACTUATION DUE TO PLANNED REACTOR TRIP "Wolf Creek Generating Station performed a planned shutdown for the start of a refueling outage. As part of the procedure GEN 00-005, Minimum Load to Hot Standby, a planned manual reactor trip was initiated from 25 percent power level with the plant in Mode 1. As part of this planned shut down sequence, an anticipated automatic Auxiliary Feedwater [AFW] actuation signal was generated. This is a non-emergency event notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to preplanned manual actuation of the reactor protection system and auto-initiation of auxiliary feed water system. "All systems and components operated as designed with the exception of the main generator output breakers. They did not open as designed. They were manually opened using the main control room hand switches as directed by EMG ES-02, Reactor Trip Response. "The plant is stable in Mode 3 with AFW secured, with plans to cool down and enter Mode 5 for the planned refueling outage. "The NRC Resident Inspector has been notified." * * * EVENT RETRACTED ON 03/11/15 AT 13:05 EDT FROM BRET DAVIS TO JEFF HERRERA * * * "WCNOC [Wolf Creek Nuclear Operating Corporation] is retracting the 10 CFR 50.72(b)(3)(iv)(A) notification based on further review of the event. A valid AFAS [Auxiliary Feedwater Actuation signal] actuation occurred during the planned shutdown as a result of SG [Steam Generator] water level reaching the lo lo level setpoint. The AFAS actuation was an expected actuation that occurred due to preplanned activities covered by GEN 00-005. On-shift control room personnel were aware that an AFAS actuation would occur as a result of tripping the plant between 30% and 25% power. The AFAS actuated consistent with the planned shutdown with no anomalies. This is consistent with NUREG-1022, Rev. 3, Section 3.2.6 that states, in part: 'With regard to preplanned actuations, operation of a system as part of a planned test or operational evolution need not be reported. Preplanned actuations are those that are expected to actually occur due to preplanned activities covered by procedures. Such actuations are those for which a procedural step or other appropriate documentation indicates that the specific actuation is actually expected to occur. Control room personnel are aware of the specific signal generation before its occurrence or indication in the control room.'" The NRC Resident Inspector was notified. Notified R4DO(Okeefe). | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2015-02-28
50854 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2015-02-27 17:56 | 2015-02-28 01:20 | 2015-04-16 | UNANALYZED CONDITION CONCERNING CONTROL ROOM HABITABILITY ANALYSIS "Cooper Nuclear Station became aware of the installation of two 12,000 gallon anhydrous ammonia tanks approximately 1.5 miles from the site. This amount of anhydrous ammonia at that distance exceeds the control room habitability hazardous chemical analysis previously evaluated for the nuclear station. The control room staff has been informed of the condition and have reviewed the appropriate abnormal procedures for actions to take in the case of a leak. This potentially represents an unanalyzed condition that significantly degrades plant safety and is reportable under 10 CFR 50.72(b)(3)(ii)(B)." The licensee has notified the NRC Resident Inspector. * * * RETRACTION AT 1153 EDT ON 4/16/2015 FROM DAVE VANDERKAMP TO MARK ABRAMOVITZ * * * "Subsequently it was determined that the Control Room Habitability Analysis that was performed in response to the NRC's post-TMI requirements bounds the identified condition. This analysis includes the potential of a toxic chemical leak from a 725-ton tank on a river barge carrying anhydrous ammonia. The volume of chemical, and distance from the control room, included in the post-TMI habitability analysis bounds the conditions found with the newly constructed anhydrous ammonia tanks." The licensee notified the NRC Resident Inspector. Notified the R4DO (Farnholtz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-02-28
50853 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-02-27 13:05 | 2015-02-27 17:04 | 2015-02-27 | EMERGENCY NOTIFICATION SYSTEM AND HEALTH PHYSICS NETWORK TELEPHONE LINES OUT OF SERVICE "On February 27, 2015, from 1305 to 1323 [EST], a loss of the ENS [Emergency Notification System] communication line, the HPN [Health Physics Network] line, and the other communication systems that the MCR [Main Control Room] operators use as part of the emergency plan occurred at TVA Sequoyah Units 1 and 2. A loss of these systems was experienced when transferring from a backup generator to an uninterruptible power supply (UPS) during fueling of the backup generator. Earlier in the day the normal power supply to the two (2) plant communications buildings was deenergized due to an unrelated electrical issue and backup diesel generators were supplying power to the buildings. While refueling one of the backup generators, the power supply was transferred to the UPS for personal safety reasons, however, the load on the UPS was greater than its capacity and its output [breaker] tripped. "This loss of communications was corrected in approximately 18 minutes once the fuel tank was filled and the generator was started. Phone line capability has been restored and verified to be functional. Sequoyah is currently investigating why the load was greater than the UPS capacity. The radiological emergency plan (REP) was reviewed and other acceptable methods for communications were available. There were no personnel injuries as a result of this event and no impact on plant operations. Both units remain at 100% power. The NRC Resident Inspector has been notified. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the loss of communications capability which includes events that would significantly impair the ability of the licensee to implement the functions of its emergency plans if an emergency were to occur." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-02-27
50852 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2015-02-27 15:18 | 2015-02-27 16:10 | 2015-02-27 | SHIPMENT OF CONTROL ROD MECHANISMS EXCEEDED EXTERNAL RADIATION LIMITS "At 1518 EST on Feb 27, 2015, the Perry Shift Manager received notice from the Radiation Protection group that an Exclusive Use closed transport vehicle arrived on site exceeding the 10 CFR 71.47 radiation levels on contact with a box on the vehicle. The truck that arrived had two boxes containing four rebuilt control rod drive mechanisms to be used during the Perry refueling outage. One of the boxes had a contact dose reading of 1290 MR/HR. This is above the 1000 MR/HR limit as noted in 10 CFR 71.47. No other limits were exceeded on the exterior of the vehicle. Specifically, the cab of the truck was reading 0.1 MR/HR which is less than the 2 MR/HR limit. Also at 2 meters around the truck, the highest level reading was 1.2 MR/HR which is below the 10 MR/HR [limit]. Also on direct contact with the outside of the vehicle, the highest reading was 30 MR/HR, which is below the 200 MR/HR limit. "The Site Radiation Protection Shipping Coordinator contacted the shipping organization of this finding at Perry. This was the Director of Operations of Energy Solutions in Memphis, Tennessee. The box was taken into the Perry Fuel Handling Building and is posted per the Perry Radiation Control Program. The vehicle is parked outside the Fuel Handling Building and is being controlled." The NRC Resident Inspector has been informed. | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2015-02-27
50851 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2015-02-26 15:11 | 2015-02-26 16:39 | 2015-02-26 | AUTOMATIC REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE FAILING CLOSED "On February 26, 2015, at 1511 EST, with Unit 1 operating at 95% power in an end of cycle coastdown, the 'B' Main Feedwater Reg Valve failed closed which resulted in a Unit 1 automatic reactor trip due to 'B' Steam Generator low/low level. The operations crew entered the reactor trip procedure and stabilized Unit 1 in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. This reactor protection system actuation is reportable per 10CFR50.72(b)(2)(iv)(B). The Auxiliary Feedwater pumps actuated as designed as a result of the reactor trip and provided makeup flow to the steam generators. The automatic start of the Auxiliary Feedwater system is reportable per 10CFR50.72(b)(3)(iv)(A) for the valid actuation of an ESF system. The Auxiliary Feedwater pumps were subsequently secured and returned to automatic. Decay heat is being removed by the condenser steam dump system. Unit 1 is in a normal shutdown electrical lineup. "The NRC Resident Inspectors have been notified and are in the Control Room. The Louisa County Administrator will be notified." | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-02-26
50850 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2015-02-25 | 2015-02-25 16:49 | 2015-02-25 | AGREEMENT STATE REPORT - MOISTURE/DENSITY GAUGE DAMAGED AT A TEMPORARY JOBSITE The following information was received from the Commonwealth of Virginia via email: "While performing testing at a temporary jobsite in Alexandria [VA], the portable moisture/density gauge (CPN MC1DR, Serial # MD40907569) was run over by a bulldozer. The sources were in the shielded position and the shielding integrity was not damaged. A survey of the gauge was performed by the licensee and readings observed were between 1 and 2 mrem/hr on contact. The gauge was packaged and returned to the office where a wipe test was taken and the analysis was performed by the manufacturer/distributor with results showing no contamination. The gauge is being returned to the manufacturer/distributor. The VRMP [Virginia Radioactive Materials Program] is reviewing the licensee's report and corrective actions." The gauge contains two (2) sources; 50 mCi Am-241/Be and 10 mCi Cs-137. Virginia Event Report ID # VA-15-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2015-03-05
50849 | 0 | NANTICOKE MEMORIAL HOSPITAL |  |  |  |  | 2015-02-13 | 2015-02-25 15:00 | 2015-07-02 | GERMANIUM-68 SOURCES LOST DURING SHIPMENT On 1/30/2015, two packages containing radioactive materials were shipped via common carrier from Nanticoke Memorial Hospital in Seaford, DE to Sanders Medical Products, Inc. in Knoxville, TN for disposal. One package arrived on 2/3/2015. The second package has not arrived, and on 2/13/2015, the second package was declared lost. The lost package contained two Germanium-68 source rods used in daily calibration of the hospital's PET scanner. Activity of the source rods was less than 0.3 millicuries each (0.6 millicuries total). Serial numbers for the source rods are: K4-124 and K4-125. The common carrier has completed a search for the lost package with negative results. The last known location of the lost package was in Harrington, DE where it was scanned on 1/30/2015. * * * UPDATE FROM MARIANNA RETZLAFF TO DONALD NORWOOD AT 1133 EDT ON 7/2/2015 * * * On Monday, June 29, 2015, the lost package was returned by the common carrier to Nanticoke Memorial Hospital. The package had not been opened and was undamaged. When opened by hospital personnel, the package contained the two Germanium-68 source rods that had originally been placed in the package. When questioned, the common carrier had no explanation as to what had happened to the package and could not explain where the package had been or even how it came to be returned to the hospital. The hospital plans to repackage the source rods and ship them via a different common carrier to Sanders Medical Products in the near future. Notified R1DO (Dimitriadis) and ILTAB (Johnson) and via E-mail, NMSS Events Notification. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-03-05
50848 | 0 | DOMINION NUCLEAR CONNECTICUT, INC. |  |  |  |  | 2015-01-22 | 2015-02-25 10:24 | 2015-02-25 | ABB K-LINE CIRCUIT BREAKER SECONDARY CLOSE LATCH BINDING The following was received from the licensee via email: "Pursuant to 10 CFR Part 21, this is a non-emergency notification by Dominion Nuclear Connecticut, Inc. (DNC) concerning a defect identified in ABB K-Line secondary close latches at Millstone Power Station Unit 3 (MPS3). A written report to the NRC will follow within 20 days. "On January 12, 2015, during the overhaul of an ABB K600 load center circuit breaker at MPS3, a defect in a new safety-related secondary close latch (Part No. 716610K01, Batch No. 0000150471) was identified when the latch did not fit properly into the breaker mechanism. The vertical piece on the front edge of the latch was contacting the manual close lever. Upon closer inspection, it was found that the angle of the bend in the secondary close latch was not correct, causing it to bind on the manual close lever when actuated. When the manual close lever was actuated, it too would bind due to the secondary latch pressing it into the left mechanism side sheet. "Of the eight (8) additional secondary close latches in stock in the Millstone warehouse, all four (4) latches from Batch No. 0000150471, as well as two (2) latches from Batch No. 0000153854, were found to have improper bends. The two (2) remaining latches from Batch No. 0000119420 were found to have the correct bend angle. "DNC determined that the defect meets the criteria of a substantial safety hazard since it could prevent a breaker from staying open following a trip signal. "DNC notified ABB of this defect on January 22, 2015. Following this notification, one of the defective latches was returned to the vendor for evaluation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-02-25
50847 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2015-02-23 21:40 | 2015-02-24 01:02 | 2015-02-24 | AUTOMATIC REACTOR SCRAM ON REACTOR HIGH PRESSURE SIGNAL "At 2140 EST on 02/23/2015, Unit 1 reactor automatically scrammed on a valid reactor high pressure signal (1096#). The reactor high pressure signal was caused by the closure of the 1C inboard main steam isolation valve (MSIV), causing reactor pressure to rise, exceeding the reactor protection system (RPS) setpoint of 1096# pressure. "The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the main steam bypass valves to the main condenser and normal level control using the feedwater system. "The closure of the 1C inboard MSIV appears to have been caused by a loss of primary containment instrument gas (PCIG) pneumatic supply to the valve. Instrument air was aligned to the remaining MSIV's. "Limerick Unit 1 will remain in Hot Shutdown until repairs can be made." All rods inserted into the core during the scram. No relief or safety valves actuated during the transient. The electric grid is stable and supplying all plant loads. There was no affect on Unit 2. The licensee notified the NRC Resident Inspector, Pennsylvania Emergency Management Agency, and Berks, Chester and Montgomery counties. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-02-24
50846 | 0 | CURTISS WRIGHT |  |  |  |  | 2015-02-20 | 2015-02-23 17:05 | 2015-11-23 | PART 21- POTENTIAL DEFECT IN A SOCKET USED SEPARATELY OR IN A CONNECTOR KIT The following information was received by facsimile: "[The Curtiss-Wright] letter is issued to provide notification of a potential defect in Socket (PIN: GB-1 A-5) sold separately or supplied as part of a GRAYBOOT 'A'' (GB-1A) Connector Kit. There is one affected lot of Sockets (Lot#: 092413). The potential defect is that the socket was not zone annealed which will possibly affect the ability to crimp the socket onto the wire conductor. Zone annealing is specified for the crimp barrel to return the crimp barrel to a soft condition to counteract the effects of previous heat treating required to develop spring tension in the socket tines that mate with the pin contact. "The nine affected Customers and their associated Purchase Orders are listed below. All Customers will be notified by February 24, 2015 and supplied with the information we have at this time. 1. Vattenfall- Forsmark Kraftgrupp AB, P.O. 4500301916 2. Vattenfall- Forsmark Kraftgrupp AB, P.O. 4500301916 3. Decon International (HK) Ltd., P.O. DIL00590 4. Ringhals AB, P.O. 641511-090 5. Dremel Inc., P.O. 13-040 6. Bruce Power L.P., P.O. 00185336 7. Kanata Electronic Services Limited, P.O. 34513 8. Meggitt Safety Systems Inc., P.O. 104057 9. Meggitt Safety Systems Inc., P.O. 104345 "Based on our recent in-house testing of socket Lot #: 092413, the defective sockets appear to be more difficult to crimp than sockets that have been zone annealed. Some of the Lot #: 092413 sockets showed cracking or bending under magnification. We did not have any sockets actually break apart during the crimping process. All the test specimens crimp barrels remained intact. If a severe fracture had occurred at the time of crimping we believe it would have been very noticeable to the technician installing the contact. Once crimped, the socket appears to function well by conducting electricity and exhibiting acceptable electrical resistance. Many of these sockets from Lot #: 092413 may already be installed. Customers will need to determine if replacing the sockets is required. "All customers listed may choose to replace already installed sockets. It is requested that any uninstalled sockets be returned for replacement. All customers requesting replacement sockets should contact Bambi Rhoades at brhoades@curtisswright.com or by phone at 256-924-7424 for arrangements or Jim Tumlinson, contact information listed below. "Send all defective sockets to QualTech NP; 120 West Park Loop; Huntsville, AL 35806. Customer can contact Cindy Tidwell at ctidwell@curtisswright.com or by phone at (256) 924-7436 for help with international or freight collect shipping instructions. Ship all defective sockets collect to UPS Account No. 35254E. "Additional details, corrective actions and root causes will be provided once our report of the recent testing complete. If you require additional information or would like to discuss this further please do not hesitate in contacting [Jim Tomlinson; Office Phone: (256) 924-7429; email:jtomlinson@curtisswright.com]." * * * UPDATE AT 1304 EST ON 11/23/2015 FROM BAMBI RHOADES TO MARK ABRAMOVITZ * * * The following report was received via fax: "This letter provides for the formal close out of notification QTHuntsville 10CFR21-2015-01. The initial notification was made on February 20, 2015 (NRC Event# 50846). All customers were notified and received the test data. All customers were given the opportunity to receive replacement sockets, as they deemed necessary. These replacement parts have been delivered. All actions have been completed. "To prevent reoccurrence in the future, the following internal documents have been revised. The procurement and dedication guidelines for both the original GRAYBOOT and GRAYBOOT 'A' connectors were revised. "GRAYBOOT 'A' Report No.: SAIC-TR-l038.2-03 currently at Revision P, dated July 16, 2015. GRAYBOOT Report No.: EGS-TR-880708-01 currently at Revision Y, dated July 16, 2015. "Both the reports above now contain additional destructive testing as well as visual inspection under magnification to provide more reasonable assurance that the annealing is acceptable. Also, additional training was conducted at our sub-supplier and additional requirements have been added to our purchase orders to prevent any reoccurrence . "Based on the above information and corrective actions, this part 21 file is considered closed. If you would like to discuss this further, please contact Tony Gill (QualTech NP Quality Assurance Manager) at 256-924-7438 (office). 256-426-4558 (mobile) or tgill@curtisswright.com. Notified the R2DO (Ernstes) and Part-21 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-02-23
50845 | 0 | SAINT LOUIS UNIVERSITY |  |  |  |  | 2015-02-23 12:00 | 2015-02-23 17:04 | 2015-02-23 | MEDICAL UNDER DOSE DUE TO EQUIPMENT MALFUNCTION A patient was under dosed approximately 21.9% due to an equipment malfunction (SIR-Spheres). The isotope is Yttrium 90, the prescribed dose was 13.23 mCi and the delivered dose was 10.3 mCi. The prescribing physician and patient will be informed. The manufacturer will follow up and investigate the hardware issue and subsequent corrective actions. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-03-03
50844 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2015-02-23 | 2015-02-23 16:59 | 2015-02-23 | AGREEMENT STATE REPORT - DAMAGED GUIDE TUBE ON RADIOGRAPHY CAMERA PREVENTING SOURCE RETRACTION The following information was received from the State of Wisconsin via email: "The Wisconsin Radiation Protection Section received notice from the licensee's Corporate Radiation Safety Officer (RSO) that a radiography crew working at a temporary jobsite on February 23, 2015 had a source become stuck during radiography operations. The crew was using an Ir-192 source in a QSA Global 880 Delta camera. While the source was cranked out in the collimator, a pipe fell on the guide tube and crimped the tube such that the radiographers were unable to retract the source. Two radiographers who are trained in source retrieval were dispatched to the jobsite. They cut out a one-inch section of the guide tube and were able to retract the source into the camera. As indicated by pocket dosimeters, radiation doses received by the radiographers were beneath regulatory limits. "The Wisconsin Radiation Protection Section will follow up with the licensee after receiving its 30-day written report. Additional updates will be provided through NMED." The licensee is sending the camera drive cable to the manufacturer for evaluation and has disposed of the damaged guide tube. Wisconsin Event Report ID No.: WI150004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2015-03-03
50843 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2015-02-23 07:30 | 2015-02-23 16:34 | 2015-02-23 | AGREEMENT STATE REPORT - SPRINKLER PIPE BREAK OVERFLOW FROM CONTROLLED AREA The following information was received from the Tennessee Division of Radiological Health via facsimile: "[A] sprinkler pipe break in the Waste Water Treatment Plant of Building B [resulted] in water accumulation in [the] berms overflowing [the] berms and [flowing] from a controlled area [into a] storm water collection basin and runoff system." The State is performing sampling to determine if there is any contamination of the water that passed through the controlled area. TN Event Report: TN-15-023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2015-03-03
50842 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-02-21 21:22 | 2015-02-22 02:36 | 2015-02-22 | REACTOR VESSEL LEVEL MONITORING SYSTEM INOPERABLE The licensee declared the reactor vessel level monitoring system (RVLMS) inoperable when an intermittent failure occurred in the 'B' train reactor vessel level monitoring system (RVLMS) concurrent with the loss of the 19% level sensor in the 'A' train. This caused entry into a 7-day LCO action statement under Technical Specification 3.3.6, Action E. The 'B' train instrumentation was reset and indication returned to normal and the LCO action was exited after 36 minutes. A Condition Report was submitted to determine cause and repair, if needed. The licensee has notified the NRC Resident Inspector as well as state and local authorities. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-02-22
50841 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-02-21 19:50 | 2015-02-21 21:35 | 2015-02-21 | SITE STACK RADIATION MONITOR FAILURE The Millstone site stack radiation monitor, RM-8169, failed and was declared inoperable at 1950 EST on February 21, 2015. Repairs are in progress. This event is reportable pursuant to 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability, off-site response capability, or off-site communications capability. The Instrument and Controls Department is conducting troubleshooting and repair. The cause of the radiation monitor failure was sample pump failure. The licensee has notified the NRC Resident Inspector and applicable State and Local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-02-21
50840 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-02-21 15:35 | 2015-02-21 16:24 | 2015-02-21 | SAFEGUARDS REPORT CONCERNING INADEQUATE COMPENSATORY MEASURES Discovered vulnerability in a safeguard system that could allow access to the controlled access area for which compensatory measures were employed late. The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2015-02-21
50839 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2015-02-21 10:32 | 2015-02-21 12:46 | 2015-02-21 | MANUAL REACTOR TRIP INSERTED DUE TO RAPID LOSS OF MAIN CONDENSER VACUUM "On February 21, 2015 at 10:32 EST, Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to rapidly dropping main condenser vacuum. Concurrent with the reactor trip the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and S/G PORVs. Main Steam Isolation Valves are closed. The Station is in a normal shutdown electrical alignment. "The cause is currently under investigation. "This is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "The NRC Senior Resident has been notified." This event had no affect on Unit 2 (Under Construction) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2015-02-21
50838 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-02-19 16:30 | 2015-02-20 13:14 | 2015-02-20 | AGREEMENT STATE REPORT - UNABLE TO RETRACT CAMERA SOURCE The following information was received from the State of Texas via email: "On February 20, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee that on February 19, 2015, one of its radiography crews working at a remote field site [near Kennedy, Texas] was unable to retract a 31.9 Curie Iridium 192 source into a QSA 880D exposure device. The radiographers were examining a pipe on a pipe pad with the collimator being held in place with a magnetic stand. As the radiographer began to retract the source after a shot, the stand fell and struck the source guide tube crimping the tube to a point where the source could not be moved. The radiographers stopped work in the area and moved their boundaries to prevent exposures to members of the general public. The radiographers contacted their radiation safety officer (RSO), but he was located 8 hours from the work site. The RSO contacted the licensee's office in Corpus Christi, Texas and the RSO from that location responded to the event. The Corpus Christi RSO is [at the location] to perform source retrieval. The event occurred at 1630 [CST] and the source was retracted at 2400 [CST]. No over exposures occurred and no member of the general public received any additional exposure from this event. The guide tube has been removed from service for inspection. The dosimetry badges for the individuals involved in the event have been sent to the licensee's processor for reading. The licensee is investigating the event. Additional information will be provided as it is received in accordance with SA-300. "On February 20, 2015, the licensee agreed to send the source involved in this event to the manufacturer for inspection." Texas Incident: I-9281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-03-02
50837 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2015-01-31 | 2015-02-20 11:30 | 2015-02-20 | AGREEMENT STATE - POTENTIAL RADIOGRAPHER OVER-EXPOSURE The following information was received from the State of Oklahoma via email: "[The Oklahoma Department of Environmental Quality has] been notified by Globe X-Ray Services (OK-15194-02) that one of their assistant radiographers received a reported dose of 5.083 R for the month of January, 2015. The assistant has been suspended and stated that he dropped his badge at some point during the monitoring period but did not report it until now. Landauer reported that the reading was 'inconclusive'. Investigation is ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2015-03-02
50836 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-01-19 20:18 | 2015-02-20 00:49 | 2015-02-20 | HIGH ENERGY LINE BREAK BOUNDARY DOOR NOT LATCHING "A High Energy Line Break (HELB) boundary door was discovered not latching. HELB boundary affects both trains of safety related [480V] switchgear and was not operable for approximately seven minutes. [The licensee] entered the technical specification action statement, restored the door to functional, and exited the technical specification action statement." The licensee notified the NRC Resident Inspector, the State of Connecticut and local officials. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-02-20
50835 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-02-19 16:00 | 2015-02-19 20:18 | 2015-02-19 | UNANALYZED CONDITION INVOLVING NORMALLY CLOSED WATERTIGHT DOORS "During Main Steam Safety Valve testing conducted prior to refueling outages, normally closed watertight doors are opened in support of the testing. If a postulated one square foot non-mechanistic crack were to occur within the Break Exclusion Area during the test, safety related equipment located just outside of these doors could be adversely affected. With these watertight doors open, compliance with the Comanche Peak licensing basis may not be assured. "This condition has been conservatively determined to be reportable as an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B). Currently, the watertight doors on both Units 1 and 2 are closed, therefore, all safety related equipment is currently operable. Comanche Peak Engineering is performing a review of the original Comanche Peak licensing basis regarding the non-mechanistic crack event to determine what equipment impacts are required to be assessed." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-02-19
50834 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-02-19 | 2015-02-19 17:35 | 2015-02-19 | AGREEMENT STATE REPORT - UNABLE TO CLOSE SHUTTER ON NUCLEAR GAUGE The following information was received from the Texas Department of State Health Services via email: "On February 19, 2015, the Agency [Texas Department of State Health Services] was notified by the licensee's Radiation Safety Officer (RSO) that during routine gauge testing, they were unable to close the shutter on a nuclear gauge. The gauge is an Ohmart model SHLG-2 containing 8,000 millicuries of cesium-137. The RSO stated the gauge is used for level indication on a vessel and open is the normal operating position for the gauge. The RSO stated the gauge does not present an increased exposure risk to their employees or members of the general public. The RSO stated they had lubricated the gauge operating mechanism in an attempt to free up the shutter, but the shutter remained stuck. The RSO stated they intend to contact the manufacturer for repairs to the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I 9280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-02-27
50833 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2014-12-29 | 2015-02-19 15:40 | 2015-02-19 | MEDICAL EVENT - UNDERDOSE "This is a notification, pursuant to 10 CFR 35.3045(a)(1), of a medical event that occurred at the VA Medical Center, Durham, North Carolina. "On December 29, 2014, a dosage of 1.569 millicuries of I-131 sodium iodide was administered to a patient for a diagnostic whole body scan, and the prescribed dosage on the written directive was 2 millicuries. "The basis for identifying this as a medical event is that the administered dosage differed from the prescribed dosage by more than 20 percent and the absorbed dose is estimated to differ from that dose that would have resulted from the prescribed dose by more than 50 rem to remnant thyroid tissue. "The medical event was discovered today (February 19, 2015) during a routine audit by the facility Radiation Safety Officer. The facility has notified the referring physician and the patient of the medical event. No biological harm to the patient is expected from this under-dosing event. "The NHPP [National Health Physics Program] plans to perform a reactive inspection regarding the medical event within the next 10 working days. A 15-day written report for the medical event will be submitted to NRC Region III. National Health Physics Program notified NRC Region III (Patricia Pelke, Chief, Materials Licensing Branch Chief) of the medical event by telephone. "Additional information: The Department of Veterans Affairs holds NRC License No. 03-23853-01VA, a master materials license. Permits are issued under the license to Veterans Health Administration facilities. The VHA permit number for the facility involved in this medical event is 32-01134-01. National Health Physics Program makes required notifications to NRC." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-02-27
50832 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2012-02-10 | 2015-02-19 10:15 | 2015-02-19 | AGREEMENT STATE REPORT - MEDICAL OVERDOSE The following report was received via e-mail: "During a routine inspection, an Agency [Massachusetts Radiation Control Program] inspector identified a past possible gamma stereotactic radiosurgery (GSR also known as gamma knife) medical event that occurred on February 10, 2012 and had not been reported by the licensee. "The licensee's written directive was incomplete. Page three of the written directive that described plug placement in the helmet used for treatment was not printed. As a result of the missing information, sixteen gamma knife plugs were not placed in position as intended and instead collimators were placed, the same size collimators used for the remaining plug pattern. Consequently, the patient received an 8.8% overdose to the treatment site. Based on the initial exposure determination to the treatment site by the licensee, the licensee concluded this was not a reportable medical event. "However, the dose to tissue other than the treatment site exceeded 0.5 Sv (50 rem) and 50% of the dose expected from the administration defined in the written directive. This is a reportable medical event in accordance with 105 CMR 120.594(A)(1)(c). "The dose to tissue other than the treatment site, tissue located beneath the skin and each of the sixteen collimators was calculated to be 71 rem, and greater than 50% of the dose expected from the administration. The dose expected to the tissue, tissue beneath the skin other than the treatment site from the administration defined in the written directive was expected to be less than 710 mrem. "The gamma knife, a Leksell Gamma System model 24001 Type C device contained 201 Elekta model 43685 sealed sources totaling approximately 2,519 total curies of cobalt-60 on the date of the event, February 10, 2012. "The licensee reported that the authorized user determined that the plug omission error would have no significant detrimental effect on the outcome of the treatment or patient condition and that no further action was necessary in the care of the patient. The licensee reported that that the authorized user reported the event in detail to the patient and provided a written description to the referring physician. "The Agency issued notice of violations to the licensee and the licensee described its corrective actions in its response to the notice of violations. "Corrective action: The licensee reported that following the omission of the plugs, the Radiation Oncologist Authorized User would designate on page 1 of the written directive if plugs were used and that this would alert the treatment team to identify and implement the appropriate plug pattern; that the licensee replaced the model 24001 Type C gamma knife with a model Perfexion gamma knife that does not use plugs; and that written directive printouts now contain both the individual page number and the total number of pages in the written directive." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-02-27
50831 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2015-02-19 03:04 | 2015-02-19 09:55 | 2015-04-15 | SECONDARY CONTAINMENT BUILDING DECLARED INOPERABLE DUE TO VENTILATION SYSTEM TRIP "At 0304 EST on February 19, 2015, Fermi 2 experienced a trip of the Reactor Building Ventilation (RB) (HVAC) during plant operations associated with very cold temperatures outside. At the time of the trip, outside air temperature was -1 degrees Fahrenheit and RB HVAC tripped due to a Freeze-Stat actuation [a freeze protection feature]. "The plant Technical Specifications require that Secondary Containment pressure be maintained greater than or equal to -0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1). This specification was not maintained and the highest pressure observed was -0.11 inches of vacuum water gauge. Subsequently, at 0450, during restoration activities, RB pressure degraded again to higher than -0.125 inches of vacuum water gauge for 38 seconds. The lowest observed pressure was -0.11 inches of vacuum water gauge. RB HVAC has been restored by resetting the Freeze-Stat and the Standby Gas Treatment System (SGTS) has been placed back in a standby condition. "The technical specification requirement is to maintain secondary containment at -0.125 inches of vacuum water gauge for secondary containment operability. Declaring secondary containment inoperable is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM WARREN PAUL TO DANIEL MILLS AT 1035 ON 4/8/2015 * * * "After reviewing the events that occurred on February 19, 2015 against the accident analyses in Chapter 15 of the UFSAR and design functions of the Standby Gas Treatment System and Secondary Containment structure, it is concluded that a condition that could have prevented the fulfillment of a safety function to control the release of radioactive material did not occur as a result of momentarily exceeding the Technical Specification for Secondary Containment vacuum after a loss of the normal Reactor Building Ventilation System. "The Fermi 2 accident analysis for a LOCA does not assume that secondary containment is under vacuum throughout the duration of an accident and contains conservative leakage assumptions to bound the effects of a postulated ground level release. The accident analysis credits the operation of the Standby Gas Treatment System (SGTS); both divisions of SGTS were operable at the time of the event. Although secondary containment was declared inoperable due to exceeding the Technical Specification value for secondary containment vacuum, the structural integrity of the secondary containment was not degraded at the time. Upon receipt of an accident signal, SGTS would have automatically started and restored secondary containment vacuum to within the bounding analyses of Chapter 15 of the UFSAR. Secondary containment was capable of performing its design function of minimizing any ground level release of radioactive material by maintaining boundary integrity so that the SGTS may draw a vacuum in the Reactor Building and filter radioactive material at all times. The event reported in EN # 50831 did not result in a condition that could have prevented the fulfillment of a safety function to control the release of radioactive material. This event report is being retracted." The licensee informed the NRC Resident Inspector. Notified R3DO (Skokowski). * * * UPDATE FROM WARREN PAUL TO CHARLES TEAL ON 4/15/15 AT 1348 EDT * * * "Upon further review of NUREG-1022 section 3.2.7, the original Non-Emergency Event Notification, 50831, remains valid." The NRC Resident Inspect has been informed. Notified R3DO (McCraw). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-02-19
50830 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2015-02-18 14:06 | 2015-02-18 16:01 | 2015-02-18 | MANUAL SCRAM DUE TO RAPIDLY RISING REACTOR WATER LEVEL "At 1406 [EST] Nine Mile Point Unit 2 inserted a manual scram due to rapidly rising reactor water level. "The cause of the rapidly rising water prior to the manual scram is unknown and under investigation. "Reactor water level is currently being maintained in normal control band post scram. "The reactor scram is reportable in accordance with 10 CFR 50.72(b)(2)(iv)(B) as, 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical.' "The NRC Resident has been notified." All rods fully inserted. Nine Mile Point Unit 2 is in a normal electrical shutdown configuration. The licensee reported no impact on Unit 1. The New York State Public Service Commission was also notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-02-18
50829 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2015-02-17 15:55 | 2015-02-17 16:55 | 2015-02-17 | OFFSITE NOTIFICATION DUE TO WASTEWATER SPILL "At approximately 1555 EST on February 17, 2015, Duke Energy personnel determined that the following event required notification of North Carolina state agencies for an NPDES [National Pollutant Discharge Elimination System] permit event and a voluntary reporting of tritium. At approximately 2200 EST on February 16, 2015, plant personnel identified a wastewater spill of more than 100 gallons containing a low level of tritium (9,415 picocuries per liter, less than half the EPA drinking water limit of 20,000 picocuries per liter). No additional plant-related radionuclides were detected. The wastewater was released as a result of an overfilled basin and entered the plant's storm drain system. The storm drain system releases to an alternative discharge outfall. The release from the settling basin has been stopped. The report to the state of North Carolina also fulfills Harris Nuclear Plant's voluntary communication to state agencies in accordance with the NEI 07-07 Groundwater Protection Initiative. "There is no impact to public health and safety or the environment due to this incident. "This event is reportable per 10 CFR 50.72(b)(2)(xi), an event related to protection of the environment for which a notification to other government agencies has been made. "The NRC Resident Inspector has been notified." The licensee will notify the State of North Carolina. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-02-17
50828 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-02-12 | 2015-02-17 15:22 | 2015-02-17 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS Walmart store #2949 in Long Beach, CA, reported the loss of two exit signs containing tritium. The signs were replaced with non-tritium exit signs and were scheduled to be collected for disposal. The production date and activity of the missing signs are unknown at this time. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-02-25
50827 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2015-02-17 11:45 | 2015-02-17 15:35 | 2015-02-17 | CONTAINMENT INOPERABLE DUE TO INTERLOCK DOORS OPEN SIMULTANEOUSLY "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(C), event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and 10 CFR 50.72(b)(3)(v)(D), event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. LaSalle's Station Unit 1 was in Mode 1 and Unit 2 was in Mode 5 for its scheduled refuel outage. There was no movement of irradiated fuel or CORE ALTERATIONS at the time. OPDRVs [Operations with Potential to Drain the Reactor Vessel] were in progress in the secondary containment on Unit 2. An employee entered a secondary containment interlock and identified that both doors of the interlock opened simultaneously when the door on the reactor building side was opened. The employee immediately secured both doors in the interlock and notified the main control room supervisor. Both doors in the interlock were open for somewhere between 5-10 seconds. With both doors open, TS SR 3.6.4.1.2 was not met and this rendered secondary containment inoperable per TS 3.6.4.1. Reactor building differential pressure, in the main control room, was never observed to be less than -0.25 inches of water column. Initial investigation determined that the interlock for the doors was malfunctioning. Administrative controls have been put in place to ensure the doors remain closed pending repairs to the interlock." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-02-17
50826 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-02-16 16:44 | 2015-02-17 00:13 | 2015-02-24 | CONTROL ROOM SPECIAL VENT BOUNDARY INOPERABLE "On February 16, 2015, at 1644 [CST], Prairie Island Nuclear Generating Plant (PINGP) Unit 1 and Unit 2 Control Room Envelope Boundary was declared inoperable when it was discovered that Door 158, Auxiliary Building to 122 Control Room Chiller Room, would not latch. Both trains of Control Room Special Ventilation were declared inoperable and Tech Spec LCO 3.7.10 Condition B was entered. In addition, with the Control Room Envelope Boundary inoperable, Tech Spec 3.7.11 Condition E was required to be entered due to both Control Room Chillers inoperable. The required actions of Tech Spec 3.7.11 Condition E required both Units to enter Tech Spec LCO 3.0.3. As a mitigating action, station personnel were dispatched to secure Door 158. This condition was corrected on February 16, 2015, at 1709 [CST] when the deadbolt was engaged to maintain Door 158 closed. Tech Specs 3.7.10 Condition B, 3.7.11 Condition E, and 3.0.3 were all exited at 1709 [CST] February 16, 2015. "This condition is reportable under 10 CFR 50.72 (b)(3)(v)(D), Event or Condition that Could Have Prevented Fulfillment of a Safety Function to Mitigate the Consequences of an Accident. "Based on immediate implementation of mitigating actions and restoration of the Control Room Envelope, the protection of the health and safety of the public was not affected by this issue. "This event has been entered into the sites Corrective Action Program. "The licensee has notified the NRC Senior Resident Inspector." * * * UPDATE AT 1220 EST ON 02/24/15 FROM NATHAN BIBUS TO S. SANDIN * * * The licensee is retracting this report based on the following: "After discussions and interviews with personnel involved, it was determined that the Aux Building Operators found Door 158 latched. After passing through the door, the Operators checked to ensure the door was latched and discovered it was sticking and required assistance to latch by agitating the latch operating mechanism. The door was checked additional times and the door would latch with assistance. The Operators ensured the door was latched and notified the Control Room at 1644 [CST]. When the Operators installed the dead bolt and padlock at 1709 [CST], the door was still latched. As the door was never left unlatched and was always able to latch, the door was operable and there was no loss of safety function. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Orlikowski). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-02-17
50825 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-02-15 09:00 | 2015-02-15 09:27 | 2015-02-15 | SAFEGUARDS REPORT DUE TO ADVERSE WEATHER Safeguards system degradation related to monitoring and detection of the Owner Controlled Area and Protected Area. Compensatory measures taken. The licensee has notified the NRC Resident Inspector and NRC Region I. * * * UPDATE AT 1827 EST ON 2/15/2015 FROM PHILLIP BEABOUT TO MARK ABRAMOVITZ * * * The degradation has been remedied and status returned to normal. The licensee notified the NRC Resident Inspector. Notified the R1DO (Powell) and 73.71 Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-02-15
50824 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2015-02-13 18:50 | 2015-02-13 23:24 | 2015-02-13 | SECURITY VULNERABILITY FOUND San Onofre Nuclear Generating Station discovered vulnerability in a safeguards system that could allow access to a controlled access area. Compensatory measures have been initiated. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-02-13
50823 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2015-02-13 | 2015-02-13 17:34 | 2015-02-13 | AGREEMENT STATE REPORT - GAMMA KNIFE UNIT FAILED TO FUNCTION AS DESIGNED The following information was received from the State of Wisconsin via email: "On Friday, February 13, 2015, the Wisconsin Radiation Protection Section received notice from the Radiation Safety Officer (RSO) of Marshfield Clinic that their Leksell Gamma Knife Perfexion gamma stereotactic radiosurgery unit failed to function as designed. The Gamma Knife unit became stuck open and staff had to manually retract the patient bed and close the shielding doors on the unit. It is not believed that the patient received a dose higher than was planned but it is unknown if it is a medical event at this time. "The Wisconsin Radiation Protection Section will conduct an investigation on Monday, February 16, 2015 and provide updates through NMED." WI Event ID: WI150001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2015-02-23
50822 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-02-13 13:15 | 2015-02-13 15:55 | 2015-02-13 | OFFSITE NOTIFICATION TO MICHIGAN OSHA "At 1123 EST on 2/13/2015, an emergency medical report was received in both unit's Control Rooms that an individual was having a personal medical issue outside the protected area. Onsite Emergency Medical personnel were dispatched to the scene. Off-site medical assistance was immediately requested. CPR was administered and the individual was transferred by off-site medical ambulance service to a local hospital. "The Operations Shift Manager received confirmation of a fatality at 1315 EST on 2/13/2015. Notification was made to the Michigan Occupational Safety and Health Administration (MIOSHA). "Both Units remain at 100% power. This Event Notification is being made due to the fatality and notification to a government agency. "The NRC Resident Inspector has been notified." The individual was at the workout facility when this incident occurred. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-02-13
50821 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-02-13 13:40 | 2015-02-13 14:46 | 2015-02-13 | AGREEMENT STATE REPORT - ONE I-125 SEED LOST/RECOVERED DURING SHIPMENT The following information was received from the State of Florida via email: "[The common carrier] was delivering 2 packages from CA to Isoaid in Port Richey (they dispose of the used material sent in by customers). The boxes at some point fell out of the truck and they were not discovered missing until the driver reached Isoaid. It is not known the exact time this [occurred], the phone call to the BRC [Bureau of Radiation Control] was at 1:40 pm. They did locate them but one package was run over and (1) I-125 seed was missing from the box. As of 2:35 pm they have found the missing seed." Florida Incident No.: FL15-008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-02-23
50820 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2015-02-13 12:35 | 2015-02-13 14:35 | 2015-02-17 | AGREEMENT STATE REPORT - CAT 1 IRIDIUM-192 SHIPMENT LOST/FOUND DURING TRANSIT The following information was received from the Commonwealth of Massachusetts: "QSA Global reported that [the common carrier] has initiated a trace of the shipment or packages to find the missing materials. "Abstract: "At 12:35 p.m. February 13th, the licensee (QSA Global, Inc.) made a telephone notification to the Massachusetts Radiation Control Program. "At 9:30 a.m. February 13th, QSA Global, Inc. was notified by [the common carrier] that a shipment of 6 packages was missing and that [the common carrier] had initiated a trace on the shipment or packages. "QSA Global reported [the common carrier] stated that the packages were last observed by [the common carrier] to be at [their] facility on Thursday, February 12th. "The total activity of all 6 packages was reported by QSA Global to be 73,000 curies of lridum-192. "QSA Global described the packages to each be Model 702 bulk shipping containers. Two of the packages each contain four Model 849 special form capsules and four of the packages each contain three Model 849 special form capsules. All special form capsules contain iridium-192 wafers. QSA Global reported that it was not certain whether or not the six packages were together or separated at the [common carrier] facility. "QSA Global reported that the shipment originated from the Netherlands and was intended for delivery to their QSA Global's Burlington, MA facility. "The reporting requirement is immediate. 105 CMR 120.281(A)(1), missing licensed radioactive materials in aggregate quantity equal to or greater than 1,000 times quantity specified in 105 CMR 120.297, Appendix C." * * * UPDATE AT 1515 EST ON 02/13/15 FROM JOSHUA E. DAEHLER TO S. SANDIN * * * "The Agency (Massachusetts Radiation Control Program) was notified at 3:15 p.m. today by our licensee (QSA Global, Inc.) that the iridium-192 missing sources had been located at [common carrier hub] and are under their control . Notified NMSS (Dudes), IRD (Stapleton), R1DO (Powell) and NMSS Event Notification via email. Notified the following Federal Agencies: DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, NICC Watch Officer, USDA Ops Center, EPA EOC, FDA EOC, FEMA NWC (email), Nuclear SSA (email) and, DNDO-JAC (email). * * * UPDATE AT 1428 EST ON 02/17/15 FROM EDWARD SALOMON VIA EMAIL * * * "The licensee (QSA Global, Inc.) notified our Agency [Massachusetts Radiation Control] (email message, dated 2/16/2015) that the formerly missing packages were physically delivered to their QSA Global, Inc. facility in Burlington , MA on Monday, 2/16/2015. "The Agency considers this matter to still be OPEN pending follow-up report from licensee. The licensee is expected to file a written report to our agency within 30 days of the immediate notification related to 105 CMR 1281 (A)(1), an immediate report." Notified R1DO (Powell) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 1" LEVEL OF RADIOACTIVE MATERIAL Category 1 sources, if not safely managed or securely protected would be likely to cause permanent injury to a person who handled them, or were otherwise in contact with them, for more than a few minutes. It would probably be fatal to be close to this amount of unshielded material for a period of a few minutes to an hour. These sources are typically used in practices such as radiothermal generators, irradiators and radiation teletherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-02-23
50819 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2014-08-15 | 2015-02-13 13:58 | 2015-02-13 | AGREEMENT STATE REPORT - STUCK SHUTTER ON BERTHOLD MLT300 FIXED GAUGE The following information was received from the Commonwealth of Kentucky: "On 8/15/14, Gallatin Steel discovered a problem with the source holder (serial number 6596) on a Berthold MLT300 fixed gauge. The gauging device contained 27 mCi of Co-60, serial# 165-02-13. The source holder was closed and locked, removed from service, placed in storage, and service was scheduled with Berthold service group. On 8/20/14 Radiametrics Technologies shutter-checked, surveyed and leak tested the device. The shutter was found to be stuck in the closed position which was caused by the lifting mechanism. Excessive wear on the lifting mechanism caused it to indent the edge of the shutter and the top plate causing an inoperable condition. The shutter was repaired and rechecked for proper operation and no problems were found. On 2/13/14 Gallatin Steel sent the KY RHB [Kentucky Radiological Health Branch] notification of the event. Corrective actions include repair of the gauge, and service/inspection of the lifting device every 6 months. Gallatin Steel informed all personnel involved, including Berthold Service Group, of the incident and the notification requirements to the KY RHB." Kentucky Event ID: KY150001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2015-02-23
50818 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2014-11-21 | 2015-02-13 10:43 | 2015-02-13 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING HIGH DOSE RATE AFTERLOADER The following information was obtained from the State of Illinois via email: "Licensee reported that while following up with a patient who had undergone radiation treatments following surgical removal of a breast tumor, redness, pain and swelling were occurring near the catheter insertion site. It was determined that the intended dose had been delivered with the connector end of the applicator interface identified as the reference location instead of the tip of the applicator as planned in the treatment. As a result, the 10 fractions of 340 cGy each were offset by over 4 cm for all the dwell positions within the applicator. The treatments were conducted with a strut adjusted volume implant (SAVI) applicator following an accelerated partial breast irradiation treatment regime. The catheter insertion site is estimated as having received a dose of over 13,000 R. The patient received medical treatment for the damaged tissue which would not heal. The Agency [Illinois Emergency Management Agency] is conducting an investigation into the matter to determine if the event is isolated or if other similar treatments may have had associated errors. Additional precautions have been taken by the licensee to prevent future occurrences including changing treatment planning systems, implementing additional quality assurance procedures and involving additional personnel to verify plans before treatment commences. "This event was reported to the US NRC Operations Center on February 13, 2015 and assigned event number 50818. "This item remains open pending additional investigation results." The HDR source was 6.95 Ci of Ir-192. As a result of the damage to the tissue, a mastectomy was performed. IL Report Number: IL15001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2015-02-23
50817 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2015-02-12 13:30 | 2015-02-13 08:31 | 2015-02-13 | VIOLATION OF FITNESS FOR DUTY POLICY "This event is being reported pursuant to the requirements of 10 CFR 26.719 because a non-licensed licensee supervisor violated the fitness for duty policy. The individual's access has been terminated. "The Licensee has notified the NRC Resident Inspectors." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 26.719 |  |  |  | 0 | 2015-02-13
50816 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2015-02-12 13:36 | 2015-02-12 20:45 | 2015-02-12 | HPCI DECLARED INOPERABLE DURING WEEKLY INSPECTION "EVENT DESCRIPTION: On February 12, 2015, at 1336 Eastern Standard Time (EST) the Unit 1 High Pressure Coolant Injection (HPCI) system was declared inoperable due to a failure of the HPCI Auxiliary Oil Pump. During performance of a routine HPCI weekly inspection, the auxiliary oil pump was started and subsequently experienced a loss of discharge oil pressure. The HPCI Auxiliary Oil Pump provides hydraulic pressure required to open the HPCI Turbine Stop Valve and the HPCI Turbine Control Valve during initial HPCI startup. Failure of the HPCI Auxiliary Oil Pump prevents the HPCI system from performing its design safety function. As such, this event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. "This event did not result in any adverse impact to the health and safety of the public. "INITIAL SAFETY SIGNIFICANCE EVALUATION: The safety significance of this condition is minimal. All other Emergency Core Cooling Systems and the Reactor Core Isolation Cooling (RCIC) system remain operable [per the requirements of 14-day LCO (Limiting Condition of Operation) 3.5.1]. "CORRECTIVE ACTIONS: Troubleshooting activities are in progress. The HPCI system will remain inoperable until the cause of the failure has been corrected. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-02-12
50815 | 0 | SUMMER |  | 2 | 3 | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2014-08-25 08:00 | 2015-02-12 17:19 | 2015-02-12 | BREAKDOWN IN THE QUALITY ASSURANCE PROGRAM FOR V. C. SUMMER 2 & 3 CONSTRUCTION PROJECT "This is a 10 CFR 50.55 initial notification for a significant breakdown in the Quality Assurance (QA) Program of Chicago Bridge & Iron (CB&I), an agent for the Licensee of the V. C. Summer 2 & 3 Construction Project. "In August 2014, deviations were found in sub-modules CA03-06, -08, and -09 for the Vogtle 3 Construction Project, which initiated the discovery and evaluation processes for both Part 21 and 10 CFR 50.55. The conditions were determined to be not reportable by CB&I under 10 CFR 21, but an evaluation of the root cause analysis results concluded that a significant QA program breakdown had occurred that could have produced a defect. No defect has been identified. "This initial notification is being made in accordance with 10 CFR 50.55(e)(4)(iii) and 10 CFR 50.55(e)(5)(i). "The NRC Resident Inspector has been notified.". | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction | NON EMERGENCY | 2 | SC | POW |  | 50.55(e) |  |  |  | 0 | 2015-02-12
50814 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-02-10 | 2015-02-12 10:38 | 2015-02-12 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING THE ADMINISTRATION OF Y-90 MICROSPHERES The following information was obtained from the Commonwealth of Pennsylvania via facsimile: "Notifications: The Department [Pennsylvania Department of Environmental Protection] was notified of this event on Wednesday, February 11, 2015. It is immediately reportable as per 10 CFR 35.3045(a)(1)(i). "Event Description: A patient was receiving Y-90 Sirtex Sirspheres when the administering device failed and a portion of the dose was lost in the apparatus. The patient received 10.4 mCi, or 58% of the prescribed 17.82 mCi dose. "Cause of the event: The device came apart during the procedure and the remainder of the dose was contained in the packaging. "Actions: The Department plans a reactive inspection." Pennsylvania Event Report ID No: PA150004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-02-20
50813 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2015-02-11 19:41 | 2015-02-11 23:15 | 2015-02-11 | NINE MILE POINT MOMENTARY LOSS OF SECONDARY CONTAINMENT "Nine Mile Point Unit 1 (NMP1) had a momentary loss of Secondary Containment due to both Reactor Building Airlock doors being opened at the same time. "At 1941 EST on 02/11/2015, both Reactor Building Airlock doors at NMP1 were opened simultaneously for approximately 1 second. This results in a momentary loss of Secondary Containment operability (TS 3.4.3). The doors were closed and operability was restored. "Secondary Containment being inoperable is an 8 hour notification per 10 CFR 50.72(b)(3)(v)(C), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' "The condition has been entered into the station's corrective action program and the Senior Resident NRC Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-02-11
50812 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-02-11 08:20 | 2015-02-11 16:16 | 2015-02-11 | HIGH PRESSURE COOLANT INJECTION SYSTEM SUCTION PATH ISOLATION "While performing 3-SR-3.5.1.2(HPCI) High Pressure Coolant Injection System Monthly Valve Position Verification, Operators closed the supply breaker for 3-FCV-2-166, CST #3 EMERGENCY HEADER ISOLATION VALVE, in order to verify the valve is in its required OPEN position. When the breaker was closed, the position indication 3-ZI-2-166 indicated OPEN and it was observed that the valve was traveling closed. The operator at the breaker reported that the breaker contactor energized when the breaker was closed. Control Room Operators re-opened 3-FCV-2-166 using the hand switch in the control room and when the valve indicated full open, directed the operator in the field to open the breaker for 3-FCV-2-166. Valve 3-FCV-2-166 isolates both the HPCI and [Reactor Core Isolation Cooling] RCIC suction path from the Condensate storage tank, both HPCI and RCIC were declared inoperable. "The duration of the loss of suction path the HPCI and RCIC was 4 minutes. "Applicable Technical Specification required actions were entered for the concurrent HPCI and RCIC inoperability and exited when the suction path was restored. "This incident is reportable as an 8-hour ENS notification under 10 CFR 50.72 (b)(3)(v) as 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "It also requires a 60 day written report in accordance with 10 CFR 50.73(a)(2)(vii) "The NRC Resident Inspector has been notified" | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-02-11
50811 | 0 | WEIR VALVES & CONTROLS USA, INC. |  |  |  |  | 2015-02-10 | 2015-02-11 14:52 | 2015-02-11 | PART 21 REPORT - WEIR VALVES AND CONTROLS SPLINE ADAPTER VIBRATED LOOSE This report was received from Weir Valves & Controls via email: During a walk down it was discovered that one of the spline adapters had slipped down the shaft of a TRICENTRIC valve supplied by Weir Valves & Controls, USA. This condition could have allowed the valve disc/stem to move from its normally open position to a partially closed or fully closed position. Weir Valve and Controls determined that the valve is designed with a single set screw tightened against the stem key and is susceptible to Human Performance Factors if it is not properly tightened against the shaft. Name of Manufacturer: Weir Valves and Controls, USA Affected Component: TRICENTRIC Triple Offset Valve Affected Plant(s): Peach Bottom Atomic Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-02-11
50810 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2015-01-12 | 2015-02-11 12:27 | 2015-02-11 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION DURING CANCER TREATMENT The following information was received from the New York State Department of Health Bureau of Environmental Radiation Protection via fax: "[The New York State Department of Health] NYSDOH received telephone notification from a licensee reporting a therapy misadministration involving a patient undergoing treatment of vaginal cancer. The treatment involved the use of a GammaMedplus iX brachytherapy HDR remote afterloader utilizing an Iridium-192 radiation source. The patient was administered the treatment using a vaginal applicator for proper placement of the therapy source. However, the vaginal applicator was improperly placed within the organ, which resulted in the irradiation of healthy tissue and significantly less radiation to the cancer site. Three treatments were given to the patient by the same oncologist over a three week period. Each treatment was prescribed to provide approximately 600 to 700 centigray of absorbed radiation. Preliminary investigations show that the therapy equipment was functioning properly and the treatment plan was appropriate. The licensee is investigating the oncologist's procedures. A written report will be sent to [the New York State Department of Health] DOH within seven days with more detailed information." NY Report #: NY-15-02 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2015-02-19
50809 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2015-02-10 13:00 | 2015-02-11 09:41 | 2015-02-11 | CONFIRMED POSITIVE TEST FOR CONTROLLED SUBSTANCE On February 10, 2015, at approximately 1300 EST, the Dominion Medical Review Officer determined that a licensed operator had a confirmed positive follow up test for a controlled substance. The individual's unescorted access has been denied at all of the Dominion sites. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2015-02-11
50808 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2015-02-10 22:05 | 2015-02-11 05:12 | 2015-02-11 | CONTAINMENT DECLARED INOPERABLE DUE TO CONTAINMENT FAN COIL LEAK "At 2205 CST on February 10, 2015, a cooling water leak of approximately 60 to 90 drops per minute was identified on the 14 Containment Fan Coil Unit Cooling Water face gasket. As a result, Unit 1 Containment was declared inoperable. This required entry into Technical Specifications (TS) LCO 3.6.1 Condition A, Containment inoperable, applicable in MODES 1, 2, 3, and 4. Immediate action was taken to isolate the fan coil unit within 1 hour from the initial identification of the leak. "After isolating the cooling water leak to 14 Containment Fan Coil Unit, containment was declared operable and TS 3.6.1 Condition A was exited at 2232 CST. A Work Request (WR) has been initiated to restore 14 Containment Fan Coil Unit to an operable condition. "This condition is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. "The plant remains in a safe condition and there was no effect to the health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-02-11
50807 | -1 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-02-10 17:50 | 2015-02-11 01:03 | 2015-03-31 | HIGH HEAD SAFETY INJECTION INOPERABLE DUE TO MISSING PIPING SUPPORT "This is a non-emergency 8 hour report in accordance with 10 CFR 50.72(b)(3)(ii)(B). "At 1750 [EST] hours on 2/10/15, Unit 4 entered Technical Specification 3.0.3 due to missing tubing supports identified for two separate high point vent lines. This condition is unanalyzed and potentially rendered the cold leg High Head Safety Injection flow path inoperable. Upon discovery, the vent line root isolation valves were closed and Technical Specification 3.0.3 was exited at 1805. Investigation has been initiated to determine cause." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1250 EDT ON 03/31/15 FROM ERIC JUERGENS TO S. SANDIN * * * The licensee is retracting this report based on the following: "On 2/11/2015 at 0103 EST, Event Notification 50807 reported to the Nuclear Regulatory Commission Operations Center (NRCOC) the potential inoperability of the Unit 4 cold leg High Head Safety Injection (HHSI) piping due to missing tubing supports on two separate high point vent lines. "Subsequent analysis has determined that the Unit 4 HHSI cold leg injection flow path to the reactor coolant system (RCS) remained operable with the missing vent line tubing supports and its safety related function was not affected. "The Unit 4 HHSI system discharge flow path to the RCS had been operable with the missing vent line tubing supports, Technical Specification (TS) requirements were met, and entry into TS 3.0.3 was not required. The HHSI system remained capable of fulfilling the safety function to mitigate the consequences of an accident on Unit 4. Therefore, the immediate notification to the NRCOC on 2/11/2015 at 0103 EST in accordance with 10 CFR 50.72(b)(3)(ii)(B) is hereby retracted." The licensee informed the NRC Resident Inspector. Notified R2DO (Walker). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-02-11
50806 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2015-02-10 12:40 | 2015-02-10 20:39 | 2015-04-03 | UNANALYZED CONDITION IN STATION BLACKOUT IMPLEMENTATION AT MONTICELLO "On February 10, 2015, at 1240 EST, Northern States Power-Minnesota (NSPM) determined that the Station Blackout (SBO) implementation at Monticello Nuclear Generating Plant (MNGP) was not consistent with the NRC Safety Evaluation (SE). Specifically, the High Pressure Coolant Injection (HPCI) system was not being utilized in a manner consistent with the NRC SE for SBO. Current battery calculations do not reflect a full complement of HPCI system equipment running for the duration (coping requirements) of the SBO event. The calculation assumed a manual action to remove the HPCI auxiliary oil pump from operating during an SBO event in order to preserve the station battery. "NSPM is reporting this as an Unanalyzed Condition pursuant to the requirements of 10 CFR 50.72(b)(3)(ii)(B). The health and safety of the public was not affected since no SBO event occurred. All station batteries and the HPCI system remain operable in accordance with the plant Technical Specifications. "The NRC Resident Inspector was notified of the event." * * * RETRACTION PROVIDED BY MICHAEL BURTON TO JEFF ROTTON AT 1254 EDT ON 04/03/2015 * * * "An engineering analysis was performed updating the battery calculations for Station Blackout (SBO) implementation demonstrating the ability of the safety related station batteries to provide sufficient capacity and capability to ensure that the core is cooled and appropriate containment integrity is maintained in the event of the SBO for the specified four hours. Therefore, the battery calculation is analyzed and specifically the High Pressure Cooling Injection (HPCI) System is analyzed to run in automatic for the entire duration of the SBO event meeting the site licensing basis for SBO. The SBO procedure has been revised to incorporate HPCI running in automatic for the entire duration of the SBO event. "The NRC Resident Inspector has been notified." Notified R3DO (Duncan) | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-02-10
50805 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-02-09 | 2015-02-10 17:17 | 2015-02-10 | AGREEMENT STATE - RADIOACTIVE SHIPMENT DELIVERED TO THE WRONG LOCATION The following information is an excerpt from a report received from the Louisiana Department of Environmental Quality via email: "On 02/09/2015, the Director of Regulatory Affairs for QSA Global Notified the [Louisiana Department of Environmental Quality] LDEQ about an incident where the common carrier delivered a 'crate/container' of [Radioactive Materials] RAM to the Baton Rouge, LA address that was intended for Seoul, South Korea. The call was received approximately 9:00 am CST at the Department. The caller stated the shipment was Ir-192 wafers/disc that were to be assembled into radioactive sealed sources. [The Director of Regulatory Affairs for QSA Global] stated he believed the shipment involves Category #1 quantities that should be reported. "The delivery error resulted in a partial shipment bound for Asia being delivered to the Corporation's Baton Rouge, LA location. "One of the Asia bound containers was 'bound/attached' to the container destined for Baton Rouge location at the Memphis Hub belonging to the common carrier. The other container went on to Asia. The international paperwork would document the partial receipt of the first container and the other when it was delivered. The common carrier was notified of the incorrect delivery. The common carrier was to pick up the Asia container on 02/10/2015 at QSA Baton Rouge facility and take it to the common carrier terminal in Kenner, LA. Then the container would be forwarded to Asia from Kenner, LA. "Three containers, each having radioactive material in excess of Category 1 quantities were being shipped from the QSA Global Burlington, MA facility. Two were addressed to Seoul, South Korea and one was being shipped to Baton Rouge, LA. The labeling on one of the Korean containers was not legible or missing and it was bound to the container going to Baton Rouge, LA. After the delivery was made to Baton Rouge and the shipment was being surveyed/assessed it was learned they had received a wrong container and was in excess of the licensed activity for Ir-192. "The Baton Rouge facility was compliant for the IC principles and Radiation Safety procedures/aspects for the receipt activities. The Department, LDEQ, determined that it would grant an emergency verbal activity increase for this situation. This would hold the radioactive material safe and secure until the common carrier could retrieve the excess material. The NRC, Region IV, was made aware of this situation on 02/09/2015, and the circumstances involving the common carrier error. Region IV was told QSA Global Burlington was going to be making the proper notifications/reports to the regulatory agencies. This was the information provided by [The Director of Regulatory Affairs for QSA Global]. "However, on the morning of 02/10/2015, the NRC Region IV notified LDEQ that a report about this situation could not be located within his agency. [the Director of Regulatory Affairs for QSA Global] was notified and he was unaware the notifications had not been made. He stated he would look into the situation. A call was placed to the Baton Rouge facility around 9:00 am [EST]. At that time, it was learned the common carrier was at the Baton Rouge facility to retrieve the container of radioactive material and forward it to South Korea. At this time LDEQ is still waiting on [The Director of Regulatory Affairs for QSA Global]'s explanation for the notifications not being made. "A fact finding discussion resulted in a plan of control and containment until the common carrier could take possession of the container. "LDEQ considers this incident closed." Louisiana Event Report ID No: LA15004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-02-18
50804 | 0 | BAYHEALTH MEDICAL CENTER |  |  |  |  | 2013-07-24 | 2015-02-10 15:32 | 2015-02-10 | MEDICAL MISADMINISTRATION DURING IODINE 125 SEED IMPLANTATION During a medical procedure to implant 70 Iodine-125 seeds (0.4 mCi each) into the prostate, 20 were implanted into the bladder. The 20 implanted into the bladder were recovered during the procedure. There was no effect to the patient. The patient and prescribing physician have been notified. The licensee is working on corrective actions to prevent a recurrence. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-02-18
50803 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-02-10 10:55 | 2015-02-10 14:09 | 2015-02-10 | SECONDARY CONTAINMENT INTERLOCK DOORS OPEN SIMULTANEOUSLY "On February 10, 2015, at 1055 CST, the Shift Manager was notified that both [High Pressure Coolant Injection] HPCI Secondary Containment interlock doors were open simultaneously. The doors were immediately closed and secondary containment pressure remained negative. "This condition represents a failure to meet Surveillance Requirement 3.6.4.1.2 given two doors in a single access opening were open simultaneously. As a result entry into Technical Specification 3.6.4.1, Condition A, was made momentarily due to secondary containment being inoperable. "This event is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." The licensee reported that personnel were posted in the area as a compensatory measure. The State of Illinois Emergency Management will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-02-10
50802 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-02-10 09:26 | 2015-02-10 11:35 | 2015-02-10 | AGREEMENT STATE REPORT - SOURCE DISCONNECTED The following was received from the Ohio Bureau of Radiation Protection via email: "A crew working near Cambridge, Ohio this morning experienced a source disconnect on a QSA Model 880D camera containing 60.5 Curies of Iridium-192, which occurred at 9:26 AM EST. "The disconnect was discovered after a shot, when the crew's survey instrument indicated that the source was still exposed after the guide cable had been fully retracted. The cause for the source disconnect has not yet been determined. "The area has been secured, roped off, and is under constant surveillance by the radiography crew. Two Acuren supervisors trained in source recovery are enroute from their Akron office. The customer has been advised and is cooperating in keeping all personnel away from the area. "There has been no exposure to workers or members of the public from the disconnect. "An ODH [Ohio Department of Health] Investigator is enroute to the site to observe recovery options." The QSA Global Camera (Model: 880D; Serial number: 4192) contained an Ir-192 source of 60.5 Ci (Serial number:13665G) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2015-02-18
50801 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2015-02-10 02:50 | 2015-02-10 10:41 | 2015-04-11 | VOIDS IDENTIFIED THAT RESULT IN AN UNANALYZED CONDITION "On February 10, 2015, Prairie Island Unit 1 was shutdown in Mode 3 during a planned outage. Ultrasonic testing in support of Unit 1 Emergency Core Cooling System (ECCS) void verifications identified existing voids with calculated volumes in excess of the OPERABILITY limits specified by the procedure. This rendered both trains of Residual Heat Removal (RHR) systems inoperable requiring entry into Technical Specification 3.0.3 at 0250 [CST]. "The station took prompt actions to vent the identified voids. The void at 1 RH-12 was vented to within acceptable limits allowing LCO 3.0.3 to be exited at 0538 on February 10. Venting at 1RH-11 is in progress. "Voiding was identified at location 1-RH-11 with a calculated volume of 62.21 cubic inches with an OPERABILITY limit of 11.62 cubic inches. "Voiding was identified at location 1-RH-12 with a calculated volume of 350 cubic inches with an OPERABILITY limit of 22.84 cubic inches. "There was no impact to the health and safety of the public as Safety Injection was available and the time both trains of RHR were INOPERABLE was limited. "This event is being reported as a unanalyzed condition that significantly degrades plant safety and a condition that could have prevented the fulfillment of a safety function (i.e., remove residual heat) under 10CFR50.72(b)(3)(ii) and 10CFR50.72(b)(3)(v)." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM TOM HOLT TO JEFF HERRERA AT 1444 EDT ON 4/11/15 * * * "Further analysis was performed on the two void locations, 1RH-11 and 1RH-12. Based on this additional analysis from AREVA, it was determined that the void located at 1RH-11 (RHR Train A) was operable. The calculations for past operability at inspection location 1RH-11 provides reasonable assurance that a void of 65 cubic inches will not generate forces that will fault any piping and supports. The void location at 1RH-12 (RHR Train B) was considered inoperable due to exceeding current procedural operability limits. The void located at 1RH-11 was determined to be nonconforming due to exceeding procedural design basis limits. "Therefore, with RHR Train A determined to be operable, this event was not an 8-hour notification for an unanalyzed condition that significantly degrades plant safety, nor a condition that could have prevented the fulfillment of a safety function (i.e., remove residual heat) under 10CFR50.72(b)(3)(ii) and 10CFR50.72(b)(3)(v). "The licensee has notified the NRC Resident Inspector." Notified the R3DO (Skokowski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2015-02-10
50800 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2015-02-09 17:30 | 2015-02-10 01:25 | 2015-03-12 | SAFETY INJECTION TANK LEVEL RESULTS IN AN UNANALYZED CONDITION "On October 14, 2013 a calculation for the containment internal structural analysis was revised and accepted by the station. This calculation limited the Safety injection tank level to 74%. On October 16, 2013 Safety injection tank level was raised to 100% for approximately 13 hours in preparations for plant start-up. While the plant was safely in a cold shutdown condition, this represents a reportable unanalyzed condition. This issue is of a historical nature and does not question the current operability of any plant systems or structures. This was self identified during a Fort Calhoun calculation review." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM MICHAEL PEAK TO DANIEL MILLS AT 2335 EDT ON 3/12/15 * * * "Following review of the reported event, attendant calculations and associated documentation, engineering personnel determined that the condition described in event notification EN50800 did not place the plant in an unanalyzed condition. "Revision 1 of a calculation for the containment internal structural analysis demonstrated that when the safety injection tanks 'B' and 'D' are 100% filled in an outage condition, approximately a 10% safety margin is maintained. This revision was the calculation of record at the time the safety injection tank levels were raised above 74%, in October, 2013. "Revision 2 of the calculation was completed to remove excess conservatism and to provide a closer representation of available margin. In addition, margin was also improved by limiting tank level to 74%. However, improving margin by limiting tank level to 74% does not result in an unanalyzed condition when tank level is 100%, as adequate margin remains. "Therefore this event is being retracted." The licensee will notify the NRC Resident Inspector. Notified the R4DO (Okeefe). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-02-10
50799 | 0 | VALCOR ENGINEERING CORPORATION |  |  |  |  | 2015-02-09 | 2015-02-09 17:17 | 2015-02-09 | PART 21 REPORT - POSSIBLE ASSEMBLY ERROR IN SOLENOID VALVE "[The licensee] has discovered a possible assembly error that may result in compromising the capability to isolate the solenoid housing internals from a LOCA environment on some of our solenoid valve models that use grafoil packing for sealing the NEMA 4 enclosure. We are in the process of identifying the valve models affected and will notify all customers affected." Description of Defect/Non-Compliance: "As noted on MRR997W the packing ring which seals the solenoid on valve model V526-5631-36 used in Qualification and Production were not matched to the procedure invoked on valve drawing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-02-09
50798 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2014-08-25 08:00 | 2015-02-09 11:36 | 2015-02-09 | BREAKDOWN IN THE QUALITY ASSURANCE PROGRAM FOR VOGTLE 3&4 CONSTRUCTION PROJECT "This is a 10 CFR 50.55 initial notification for a significant breakdown in the Quality Assurance (QA) Program of Chicago Bridge & Iron (CB&I), an agent for the Licensee of the Vogtle 3&4 Construction Project. "In August 2014, deviations were found in sub-modules CA03-06, -08, and -09, which initiated the discovery and evaluation processes for both Part 21 and 10 CFR 50.55 . The conditions were determined to be not reportable by CB&I under 10 CFR 21, but an evaluation of the root cause analysis results concluded that a significant QA program breakdown had occurred that could have produced a defect. No defect has been identified. "This initial notification is being made in accordance with 10 CFR 50.55 (4)(iii) and 10 CFR 50.55 (5)(i)." The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | CONSTRUCT DEFICIENCY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 50.55(e) |  |  |  | 0 | 2015-02-09
50797 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-02-09 08:24 | 2015-02-09 11:05 | 2015-02-09 | STACK HIGH RANGE RADIATION MONITOR OUT OF SERVICE FOR PLANNED MAINTENANCE The Unit 2 Stack High Range Radiation Monitor (RM-8168) was removed for service for planned maintenance. There is no significant effect of this planned maintenance on the plant. The licensee notified the NRC Resident Inspector, the State of Connecticut and Waterford township. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-02-09
50796 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2015-02-07 08:48 | 2015-02-08 08:12 | 2015-02-16 | OFFSITE NOTIFICATION TO OCCUPATIONAL SAFETY AND HEALTH ADMINISTRATION (OSHA) "At approximately 0848 [EST] on February 7, 2015, a contract employee was found unresponsive at a VC Summer Unit 1 facility outside the Owner Controlled Area. The VC Summer Medical Emergency Response Team responded to the scene and provided assistance until offsite medical personnel arrived. Emergency Medical Services arrived on the scene and transported the individual to a local area hospital. VC Summer has reported this to OSHA and is reporting this to the NRC in accordance with 10 CFR 50.72 (b)(2)(xi). "The NRC Resident Inspector has been notified." * * * UPDATE AT 1300 EST ON 02/16/15 FROM MICHAEL MOORE TO S. SANDIN * * * "At 0935 EST, on February 16, 2015 SCE&G notified OSHA that the contract employee had passed away. This update also corrects the second sentence of the initial notification that station personnel versus the Medical Emergency Response Team responded to the scene. "The NRC Resident Inspector has been notified." Notified R2DO (Nease). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-02-08
50795 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-02-07 18:56 | 2015-02-07 21:47 | 2015-02-07 | AUTOMATIC REACTOR SCRAM "A reactor SCRAM occurred at 1856 CST on 2/7/15 from 100 percent core thermal power. The cause of the SCRAM appears to be a Generator/Turbine trip, but it is still under investigation. "Appropriate off-normal event procedures were entered to mitigate the transient with all systems responding as designed. No loss of offsite or ESF power occurred. No ECCS initiation signals were reached, and no ECCS or Emergency Diesel Generator initiations occurred. "Main Steam Isolation Valves remained open and Safety Relief Valves lifted and reseated as designed. Currently, reactor water level is being maintained by the Condensate and Feedwater system in normal band, and reactor pressure is being controlled via turbine bypass valves to the main condenser." Following the reactor SCRAM, all rods fully inserted and all systems functioned as expected. The plant is in a normal electrical lineup. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-02-07
50794 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2015-02-06 23:55 | 2015-02-07 07:37 | 2015-02-07 | LEAKAGE DETECTION SYSTEM INOPERABLE "On 2/6/15 at 2300 (CST) the Division 1 Reactor Water Cleanup (RT) system differential flow instrument was declared inoperable due to erratic indication. The Division 1 RT differential flow instrument was declared inoperable in accordance with Technical Specification 3.3.6.1 Action D.1. At time 2355 Division 2 RT differential flow instrument failed downscale and was declared inoperable in accordance with Technical Specification 3.3.6.1 Action D.1 and also Technical Specification 3.3.6.1 Action E.1 (entered due to Division 1 RT differential flow already inoperable). Since this condition renders the Leakage Detection System incapable of performing its safety function, it is reportable under 10CFR50.72(b)(3)(v)(C). Division 1 RT differential flow was declared Operable at time 0036 on 2/7/15. Division 2 RT differential flow was restored to Operable at time 0225 on 2/07/2015. "The NRC Resident [Inspector] has been notified." | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-02-07
50793 | 0 | MCLAREN MEDICAL CENTER - BAY REGION |  |  |  |  | 2015-02-06 08:00 | 2015-02-06 18:39 | 2015-02-06 | MEDICAL MISADMINISTRATION DURING BRACHYTHERAPY A patient underwent brachytherapy utilizing a vaginal cylinder. The prescribed dose was 5.5 Gray (550 rem) to the target volume, but due to mispositioning of the source, the target volume received only a negligible dose. The source was positioned such that the skin received a dose of up to 2.5 Gray (250 rem). The patient and prescribing physician have been notified. The patient is unlikely to suffer any permanent effects, but could experience mild erythema. The patient has been scheduled for an additional treatment. The hospital will take steps to prevent a future recurrence before the next patient is treated. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-02-16
50792 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-02-06 12:27 | 2015-02-06 16:53 | 2015-02-06 | AUTOMATIC REACTOR SCRAM DUE TO LOSS OF FEEDWATER "At 1227 CST on 06 Feb 2015, Dresden Unit 2 automatically scrammed due to a Reactor Water Level transient. Set up activities for weekend maintenance were being performed on the feedwater system at the time of the event. "All rods inserted to their full-in positions. "Systems operated as expected. "Reactor vessel inventory and pressure are being maintained in normal control bands. The ultimate heat sink was maintained. "The source of the transient was a loss of Feedwater Level Control and the reactor automatically scrammed on low reactor water level. Cause of the failure is under investigation. All three feed pumps tripped as a result of the transient. The 2B reactor feed pump was restored following the transient in accordance with station operating procedures. Level is being maintained with normal feedwater. "High Pressure Coolant Injection initiated on a valid low-low reactor water level. Manual operator action was taken to prevent unneeded injection into the reactor coolant system. "Group 2 Primary Containment and Group 3 Shutdown Cooling and Reactor Water Clean-up system isolations occurred as expected. "Unit 2 and 2/3 [swing diesel] EDGs started as expected, but did not load onto their associated busses as offsite power was maintained." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2015-02-06
50791 | 0 | THERMO GAMMA-METRICS LLC |  |  |  |  | 2015-02-06 | 2015-02-06 13:17 | 2015-02-06 | PART 21 REPORT - SHUTDOWN MARGIN MONITOR ENVIRONMENTAL QUALIFICATION NONCOMPLIANCE The following is an excerpt of a report received from the vendor via email: "A deviation has been identified in the SDMM supplied by Thermo Gamma-Metrics LLC. The SDMM will fail during conditions of simultaneous high temperature and high humidity less than the values reported in Qualification Test Report (QTR) 010. Testing has indicated the SDMM would not properly operate above a certain value of moisture content corresponding to a dew point of around 128øF. QTR 010 listed qualified temperature and humidity conditions corresponding to a dew point of around 136øF." The vendor has issued a revised qualification test report which documents the revised qualified conditions for the affected SDMMs. The following plants are potentially affected: ANO U2; Millstone U3; Prairie Island U1 & U2; Seabrook U1 & U2; South Texas U1 & U2; St. Lucie U1; Catawba U1 & U2; McGuire U1 & U2; Salem U1 & U2; Calvert Cliffs U1 & U2; Almaraz U1 & U2; Sequoyah U1 & U2; Watts Bar U1 & U2; Vogtle U1 & U2; Byron U1 & U2; Ringhals U2, U3 & U4. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-02-06
50790 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-02-05 13:00 | 2015-02-05 20:47 | 2015-02-05 | LOSS OF SEA WATER INTAKE BAY LEVEL INSTRUMENTATION DUE TO LOSS OF INSTRUMENT AIR "On January 27, 2015, during winter storm JUNO, there was a loss of instrument air at the Pilgrim Nuclear Power Station (PNPS). Follow-up evaluations of the plant events that occurred on that day revealed that the loss of instrument air resulted in a loss of water level indicators in the seawater intake bays. The affected instruments, LI-3831 A/B, are utilized in assessing conditions for entry into the Emergency Action Levels. PNPS Emergency Plan Implementing Procedure (EPIP) EP-IP-100.1 specified a compensatory action of 'visual inspection required' should these instruments be unavailable. However, there was not a clear linkage between the EPIP compensatory actions and the operations procedure for loss of instrument air. Neither the EPIP nor operations procedure identified the specific actions necessary to perform the local monitoring action. Based on the above, we have concluded that this event was reportable pursuant to 10CFR50.72(b)(3)(xiii), Any event that results in a major loss of emergency assessment capability. "The review of the event revealed actual sea water levels in the intake bay did not meet plant specified EAL entry conditions at any time during the winter storm and therefore no plant equipment was impacted. The capability to assess intake bay water level locally in the intake bay was available. "Subsequent to the winter storm event, the instrument air system and sea water bay level instrumentation were restored to service. Public health and safety were not adversely affected. "The licensee has notified the NRC Senior Resident Inspector. The licensee will notify the Commonwealth of Massachusetts." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-02-05
50789 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-02-05 11:30 | 2015-02-05 18:34 | 2015-02-05 | TECHNICAL SUPPORT CENTER VENTILATION NON-FUNCTIONAL "At approximately 1130 EST on 2/5/15, the site discovered degradation of the technical support center ventilation air handling unit. Compensatory measures were established during the period that the ventilation system was non-functional. The TSC ventilation system was subsequently restored to functional status." The TSC ventilation system was restored at approximately 1834 EST on 2/5/15. The issue was a failure of the automatic TSC air recirculation function due to a tripped circuit breaker. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-02-05
50788 | 0 | HELLER AND JOHNSEN |  |  |  |  | 2015-01-16 12:00 | 2015-02-05 14:00 | 2015-02-05 | MOISTURE DENSITY GAUGE IN TRUNK OF STOLEN CAR The licensee reported that a technician had a Troxler moisture/density gauge, Model #3430 (Serial #19531), locked in the trunk of his car. The technician's brother took the car for a "joy ride" and the car was reported to the Fairfield police as stolen. The brother was pulled over by the police roughly 1/2 hour later. The gauge was recovered undamaged and still locked in the trunk of the car. The licensee reported that they lost possession of the gauge for no more than 1/2 hour and that the brother probably did not intend to steal the gauge. The gauge contains 27mCi of Cesium 137 and 132 mCi of Americium 241. The Fairfield police, bomb squad, and the local FBI responded to the event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2015-02-13
50787 | -1 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-02-03 19:01 | 2015-02-04 19:15 | 2015-02-09 | SAFETY EQUIPMENT DISABLED DUE TO SNOW "On 2/3/2015 at 1901 [CST], equipment important to safety failed to function as designed: 33 NAC MAGNASTOR systems containing Spent Nuclear Fuel, and 1 NAC MAGNASTOR system containing GTCC [Greater than Class C] waste, had air inlet vent partial blockage, totaling 50 percent or greater, due to environmental conditions, i.e., snow. (Please Note, no VCC systems reached full blockage.) "NO personnel radiation exposure. "Actions Taken lAW the NAC FSAR, Rev. 5, which included actions to immediately return the systems to less than 50 percent blockage and ongoing maintenance activities to return all systems to full operability. "Additional information: 1. On 2/4/2015 at 0445 hrs. All 34 failed systems were restored to less than 50 percent blockage. 2. lAW the NAC FSAR we have 30 days from time of discovery to return each system to full operability. 3. A report will be followed up within 60 days per 10 CFR 72.75.g" The licensee will notify the NRC Inspector and the State of Illinois. * * * RETRACTION FROM MARK BITTMAN TO JEFF HERRERA ON 2/9/15 AT 1736 EST * * * "This phone notification is being made to retract an earlier '24 Hour Report' made on February 4, 2015 at 1815 CST, NRC event #50787. On February 4, 2015 at 1810 CST, Zion Station notified NRC that on February 3, 2015 at 1901 CST, Equipment Important To Safety failed to function as designed that being 33 NAC MAGNASTOR systems containing Spent Nuclear Fuel and 1 NAC MAGNASTOR containing GTCC waste had their Inlet vents partially blocked, totaling 50% or greater, due to environmental conditions, i.e. Snow. "This appeared to meet criteria of Non-Emergency notification under 10 CFR 72.75d(1)(i). "NAC International has provided documentation stating we have 58 hours to perform the immediate action to unblock the VCC vents to greater than 50% and 30 days to completely unblock all the vents. This documentation is attached to this notification. "Upon further review by Exelon Management, Zion Solutions Management and NAC, using criteria established in Sections 4.3.7.1 and 12.2.2 of the SER for CoC 72-1031, Amendment 0, no limits were exceeded. Actions were immediately initiated to restore the 34 failed systems to less than 50% blockage and were completed in less than 10 Hours. This is well within the 58 hour SAR basis. This is the basis for retracting the notification. "Based on the above, [the licensee] management concludes this event does not meet the 24-hour reporting criteria established in 10 CFR 72.75d(1)(i)." The R3DO(Pelke) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW |  | 72.75(d)(1) |  |  |  | 0 | 2015-02-04
50786 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2015-02-04 09:34 | 2015-02-04 17:57 | 2015-02-13 | CONTROL ROOM VENTILATION INOPERABLE DUE TO MISPOSITIONED VENTILATION INSPECTION PORT "At 0934 CST hours on Wednesday, February 4, 2015 during a housekeeping inspection, an inspection port (18x18 inch opening) on the Control Room Fresh Air (CRFA) System was discovered open. The opening of the inspection port resulted in the loss of safety function for both trains of CRFA as a loss of control room envelope boundary. "The cause of the inspection port being open is currently unknown and is under investigation. The Control Room was notified and an operator immediately secured the inspection port returning both trains of CRFA to operable status. "The reactor was at approximately 100 percent power at the time of the discovery of the event. The Limiting Condition for Operation (LCO) Technical Specification 3.7.3, Control Room Fresh Air (CRFA) System, is two CRFA subsystems shall be OPERABLE. This Technical Specification is applicable in MODES 1, 2, and 3, and during operations with a potential for draining the reactor vessel. "This condition is reportable as an 8 hour call in accordance with 10 CFR 50.72(b)(3)(v)." The licensee has notified the NRC Resident Inspector. * * * RETRACTION AT 1520 EST ON 02/13/15 FROM PAUL SALGADO TO S. SANDIN * * * "Grand Gulf Nuclear Station is retracting this event notification based on the following: Regulatory Guidance in NUREG-1022, Revision 3, Event Reporting Guidelines 10 CFR 50.72 and 50.73, Sections 2.8 Retraction and Cancellation of Event Reporting and 4.2.3 ENS Notification Retraction. "Once the inspection port was discovered open, the control room was notified and an operator immediately secured the inspection port. After the port was secured, detailed engineering calculations were initiated to analyze the situation. Due to the time needed to perform the detailed calculations versus the time required for notification (8 hours) a conservative decision was made to report the event based on knowledge at the time of the event and rough calculations. Subsequently detailed calculations were performed to evaluate and support system operability evaluation. The calculations evaluated dose sensitivity analysis for the increased Control Room in-leakage due to the open inspection port. A test determined the control building in-leakage to be 585 cfm, the in-leakage from other sources to be 15 cfm, and the calculation determined the flow rate through the opening to be 1245 cfm. This total in-leakage rate of 1845 cfm is below the maximum allowable control building in-leakage of 2000 cfm. The calculation performed a sensitivity analysis with recent ILRT results applied and concluded that 4200 cfm in-leakage is permissible to maintain within the limits of 10CFR50.67. By subtracting the measured in-leakage assuming all ports closed ( 585+15= 600 cfm) from the in-leakage permissible to maintain within the limits of 10CFR50.67 (4200 cfm), there Is a resulting margin of 3600 cfm. "Technical Specification 3.7.3, Control Room Fresh Air (CRFA) System, requires TWO CRFA subsystems shall be OPERABLE, and the calculations show that the CFRA was OPERABLE. The calculations lead to the conclusion that the system would have fulfilled its safety function needed to mitigate the consequences of an accident. "Therefore, this event is not an 8-hour notification under 50.72(b)(3)(v)." The licensee informed the NRC Resident Inspector. Notified R4DO (Allen). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-02-04
50785 | -1 | IU HEALTH BALL MEMORIAL HOSPITAL |  |  |  |  | 2014-01-15 | 2015-02-04 17:23 | 2015-02-26 | INERT CAPSULE ADMINISTERED TO PATIENT DURING TREATMENT The following was received from the licensee via email: "A 40 year old adult male patient was scheduled to receive 150 mCi of radioactive Iodine 131 as a thyroid cancer therapy. The dose, in pill form, was assayed as prescribed on Wednesday 1/15/14 and was believed to have been [administered to the patient]. "On 1/23/14, the patient returned for a whole body scan, [which is] a routine part of the procedure. After scanning the patient, it was noted that there was no activity remaining, which could not be possible under normal circumstances, because Iodine 131 has an 8 day physical half-life. Even with biological excretion occurring, one would expect significant detectable activity 8 days after administration. "Two technologists were involved, one assayed the dose and put it back in temporary storage, the other subsequently retrieved the capsule and administered it. Upon investigation it was found that an inert capsule was inadvertently retrieved rather than the patient's capsule. The capsule the patient should have received was discovered and assayed, and found to be the actual capsule that should have been delivered. "The tablet given to the patient had an activity of 30 mCi of Iodine 131 on 8/2/13, this was some 20 half-lives prior to the January 2014 date of this incident and [the capsule] was therefore completely inert, therefore no dose was administered. "[The licensee] talked with [the licensee's] Nuclear Medicine consultant, to review the regulations. Upon review of USNRC regulations and based upon advice from [the consultant], this was not deemed a medical event but rather a self-identified violation of our procedures. "Based upon an NRC review during an inspection on 2/3/15 we were advised that this occurrence, in [the NRC inspector's] opinion, constitutes a Medical Event based on Title 10 of the Code of Federal Regulations Part 35.3045. "We were advised to contact the USNRC offices in Region III by the end of business on 2/4/15 and report the occurrence as a Medical Event. "With respect to patient impact, papillary/follicular cancers are slowing grow and indolent, and a delay in treatment would not be expected to adversely affect the outcome. The patient was subsequently rescheduled and administered the [prescribed] dose of Iodine 131. "In order to determine cause and institute corrective measures, a root cause analysis investigation was conducted and as a result, procedure revisions were implemented to prevent the likelihood of additional errors of this type." * * * RETRACTION FROM ALVIS FOSTER TO CHARLES TEAL AT 1558 EST ON 2/26/15 * * * Since the patient received no dose as a result of this procedure, it was determined that this event was not a medical event. Notified R3DO (Stone) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-02-12
50784 | 0 | OPERATION TECHNOLOGY, INC./ETAP |  |  |  |  | 2015-01-23 | 2015-02-03 14:44 | 2015-02-03 | PART 21 REPORT - ERROR IDENTIFIED IN POWER SYSTEM ANALYSIS SOFTWARE The vendor identified an error in their power system analysis ETAP software (releases 11.0.0N to 12.6.0N) that could result in an inaccurate analysis result. A letter explaining the errors, and the way to avoid the errors, was submitted to the user community on January 23, 2015. A software revision correcting the errors is scheduled for release in February 2015. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2015-02-03
50783 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-01-30 | 2015-02-03 14:18 | 2015-02-03 | AGREEMENT STATE REPORT - REMOVABLE CONTAMINATION FOUND ON FLOURINE-18 PACKAGE The following information was received from the Pennsylvania Department of Environmental Protection via email: "Event type: Removable contamination greater than the limits specified in 10 CFR 20.1906(d)(1). "Notifications: The Department became aware of this event on Tuesday, February 3, 2015. The event is immediately reportable as per 10 CFR 20.1906(d)(1). "Event Description: A package containing Fluorine-18 was found to have removable radioactive surface contamination upon receipt at the Philadelphia facility. An average of five wipe tests performed on the container resulted in 39,000 dpm of removable contamination; however the wipe area dimensions have not been provided. This will be clarified during the reactive inspection. The distributing radiopharmacy (PETNET Solutions) has been contacted but it is unknown at this time if the courier was contacted. "Cause of the Event: Unknown at this time. "The [Pennsylvania DEP Bureau of Radiation Protection] plans a reactive inspection. More information will be given when known." PA Event Report ID No: PA150002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-02-11
50782 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2015-02-02 09:19 | 2015-02-02 16:54 | 2015-02-02 | NON-LICENSED SUPERVISOR TESTED POSITIVE FOR ALCOHOL DURING RANDOM TESTING "At 2/2/15, at approximately 0919 EST, a non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. Due to the confirmed positive test, the employee's access to the plant has been revoked." "The NRC Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2015-02-02
50781 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2015-01-31 14:31 | 2015-01-31 18:00 | 2015-01-31 | MANUAL RPS ACTUATION DUE TO OSCILLATIONS IN THE FEEDWATER SYSTEM "At 1431 EST on 1/31/15, Oconee Unit 3 was manually tripped due to oscillations in the feedwater system in anticipation of an automatic trip. At 1427 EST, Unit 3 began experiencing small feedwater oscillations. Specifically, 3FDW-32, the 3A main feedwater control valve, appeared to be oscillating with corresponding feedwater flow oscillation. Feedwater oscillations continued to grow in magnitude and at 1431 EST a manual trip was directed by the Unit 3 control room supervisor. The shutdown was orderly and the unit is currently stable and in Mode 3 (Hot Standby). Units 1 and 2 were unaffected by the trip and are currently 100% power (Mode 1). "Due to the RPS actuation while critical, this event is being reported as a 4-hour non-emergency per 10CFR50.72(b)(2)(iv)(B). "Following the reactor trip, a main steam relief valve (MSRV) failed to reseat as expected. Emergency Operating procedure guidance was utilized to reduce main steam system pressure by approximately 80 psig to reseat the valve (valve reseated at 1506 EST). All of the main steam relief valves are now seated. In addition, the 3B condensate booster pump experienced a mechanical seal leak (approximately 4-5 gpm). The pump was subsequently secured at 1447 EST. "All other post trip conditions were normal and all other systems performed as expected. Unit 3 is currently in Mode 3 and stable." All rods fully inserted. Main Feedwater is feeding the steam generators and decay heat is being removed to the Main Condenser. The cause of the trip is under investigation. There is no known primary to secondary leakage. The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-01-31
50780 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2015-01-30 08:20 | 2015-01-30 16:31 | 2015-02-05 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILED TO CLOSE While attempting to close the shutter on a Kay-Ray fixed gauge at a coal fired power plant located at 24th and Craig Street in Omaha, NE, the cable operating the shutter mechanism broke. The gauge contained 50 mCi of Cs-137. Plant operators manually closed the gauge shutter. There were no exposures to workers in the area. The state will provide additional information when it is available. * * * UPDATE FROM BRYAN MILLER TO JOHN SHOEMAKER AT 0908 EST ON 2/5/15 * * * The following event update was received from the State of Nebraska via email: "The Nebraska Department of Health and Human Services, Radioactive Materials Program, was notified at 1455 hours [CST] on 01/30/2015 by the Tech. Supervisor, at Omaha Public Power District that a Kay Ray fixed gauge Model Number 7080, housing serial number 16784Y, source shutter failed to close. The device originally installed in 1984 with approximately 50 millicuries Cesium 137 now contains approximately 25 millicuries. The gauge which is part of a hopper level sensor is mounted between two fly ash hoppers approximately 20 feet off of the floor. The source closure mechanism on the gauge is connected to a handle located at floor level by a flexible cable. The closure cable are secured so that when the floor handle is operated, the control cable slides inside of the sheath thus opening/closing the shutter. One of the station's chemists was restoring the source to service following a maintenance outage. The 'external' source closure mechanism for Unit 4 precipitator was being placed in the open position when a metallic snap was heard when opening the source shutter. The source handle was half way to the open position when this noise was heard. The operator then proceeded to check the cables function by trying to move the shutter to the closed position . The source shutter did not move. Scaffolding was erected and an inspection of the device showed the source shutter was in the open position and that the cable was not connected to the gauge operating mechanism. The source shutter mechanism was moved manually to the closed position and the cable reattached and tested several times using the remote actuator. All functions were noted to be in working condition. "No personnel were unintentionally exposed to radiation during this event. "Cause: Defective or Failed Part. "Corrective Action Information: Equipment maintenance and repairs made without engineering change to the system." Device/Associated Equipment: Kay-Ray/Sensall/Fixed Gauge, Model Number 7080, Serial Number 16784Y. Source of Radiation: Amersham, Sealed Source Gauge, Model CDC 800, Serial Number 15112-V, with a CS-137 .025 Ci source Nebraska Item Number: NE150001 Notified the R4DO (Miller) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2015-02-09
50779 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-01-30 | 2015-01-30 15:42 | 2015-01-30 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the State of California via email: "On January 30, 2015, a telephone report was made to the [California Department of Public Health] CDPH Director's office that a gauge had been stolen. The person making the report was difficult to understand, but the Director's office was able to ascertain the contact telephone number. Upon receiving notice of the call, a representative from [Radiologic Health Branch] (RHB) immediately called that telephone number (at approximately 1100 PST on January 30, 2015), and spoke with the RSO of Giles Engineering Associates, RML #4592-30. [The RSO] stated that a moisture/density gauge (CPN, MC-1DRP, serial #MD20506575 containing 0.370 GBq of Cs-137 and 1.85 GBq of Am-241) had been stolen from a transport vehicle in front of a Comfort Inn at 1185 Admiral Callahan Lane, Vallejo, CA. The authorized gauge user had left the radioactive gauge chained and locked in the back of his vehicle at approximately 0600 PST and went back inside the Comfort Inn to complete some paper work. When he returned to his vehicle at approximately 0625 PST to go to the worksite, [the authorized gauge user] noticed that the chains had been cut through and that the radioactive gauge had been removed from his vehicle. [The authorized gauge user] contacted the RSO of Giles Engineering Associates, who stated he had attempted to notify Local Law Enforcement officials in Vallejo to report the theft. [The RSO] was directed to fill out a report online as that was the policy of the Vallejo Police Department in regards to all theft cases not involving immediate threats to persons. When [the RSO] receives [the authorized user's] written report and the police report, he will forward them to RHB Brea. [The RSO] will utilize local papers in the Vallejo area to attempt to retrieve the stolen gauge. Additionally he will notify local vendors who service radioactive gauges to be alert for the serial number of the stolen gauge in case it turns up at any of their facilities." CA 5010 #: 013015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-02-09
50778 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2015-01-28 19:57 | 2015-01-28 20:55 | 2015-01-28 | SAFETY SYSTEM WILL NOT FUNCTION AS REQUIRED "At 1957 EST on 01/28/2015, with the unit in Mode 1 at 100 percent power, it was discovered that a modification installed during the fall 2013 refueling outage at H. B. Robinson inadvertently cross connected both trains of reactor protection. This cross connection resulted in both trains of safety injection being required to actuate in order to produce a reactor protection reactor trip. This is reportable pursuant to 10 CFR 50.36(c)(1)(ii)(A) since it was determined that an automatic safety system does not function as required. "The cross connection of the reactor protection trains presented an unanalyzed condition and is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B). An additional unanalyzed condition was identified in which the 'A' and 'B' DC Train systems were cross connected by the same condition and is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B). This condition is also being reported as an eight hour non-emergency under 10 CFR 50.72(b)(3)(v)(D) condition that could prevent fulfillment of safety functions. "At no time during this occurrence was the public or plant staff at risk as a result of this event. "The NRC Resident Inspector has been notified." This condition did place the unit in Technical Specification 3.0.3 for the reactor protection system and the DC vital buses, but the condition causing the issue was cleared at 2048 EST prior to any lowering of reactor power. The licensee will be notifying appropriate State, local and other government agencies as required. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT | UNANALYZED CONDITION | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2015-01-28
50777 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-01-27 | 2015-01-28 18:08 | 2015-01-28 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following report was received from the State of California via email: "On 01/28/15, [the licensee] RSO contacted [the California] RHB [Radiologic Health Branch] to notify [the state] of a damaged nuclear gauge incident that occurred on 01/27/15. The gauge involved was a Troxler Model 3440, S/N 21101 containing 9 mCi of Cs-137 and 44 mCi of Am-241. Gauge user had left the gauge on a wheel barrow and walked away [approximately] 25 feet to look for a foreman. User then noticed a CAT scrapper backing off towards the gauge. His attempt to stop the scrapper failed, resulting in a damaged gauge. After the incident, it was noted that the gauge was intact with damage only to the face plate area. The operator contacted the RSO, and then transported the gauge to Instrotek for further testing. Leak tests performed indicated no contamination. The gauge is still at Instrotek for repairs." California Event: #012815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-02-05
50776 | 0 | B&W NUCLEAR OPERATING GROUP, INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-01-09 16:00 | 2015-01-28 16:22 | 2015-03-16 | UNANALYZED CONDITION WHILE CLEANING THE CATCH TRAY "I. EVENT DESCRIPTION "Scrap material resulting from various operations at B&W NOG-L's facilities is processed in the Low Level Dissolver (LLD) to reclaim as much of the uranium as possible. Since the material is scrap (e.g., filters, vacuum cleaner bags, etc.), it contains only small amounts of uranium bearing materials. On occasion during processing a slight amount of material will spill over the edge of the dissolver trays, filter bowls, or when hand-transferring material between the trays and filter bowls. These small spills collect on a large catch tray in the bottom of the enclosure. Periodically the catch tray is cleaned to limit the amount of material buildup. By procedure the solid material is to be scraped up and collected in a [less than or equal to] 2.5 liter container. During the cleanout the LLD process is shutdown. "On January 9, 2015, the LLD process was shutdown and the enclosure was undergoing a routine cleanout. However on this occasion the operators scraped the material on the tray into several piles for subsequent collection into containers. The volume of most of the piles exceeded the 2.5 liter limit. However, the spacing between the piles was greater than the 15 inch limit, and the net weight of any single pile was less than the 7 kg limit for a 2.5 liter volume containing an unknown amount of U-235 . NDA [Non-Destructive Assay] measurements later determined the U-235 content of the piles ranged from 6.5 to 20.8 grams. There was no risk of a criticality accident. The accident scenarios for [less than or equal to] 2.5 liter containers of an unknown amount of U-235 were reviewed to analyze the event. At that point in time it was concluded the performance requirements of 10 CFR 70.61 were maintained. "At 0900 EST on January 28, 2015, during discussion with the NRC as part of a regularly scheduled NCS inspection the applicability of these scenarios to the event came into question. The scenarios assume the material is containerized rather than in piles. Some of the IROFS [item relied on for safety] were therefore considered not available in this particular situation. "II. EVALUATION OF THE EVENT "The cleanup process as analyzed assumed the material was scraped up and collected in [less than or equal to] 2.5 liter containers. The scraping of the material into piles for subsequent collection into containers is a different process than what had been analyzed. The scenarios for the handling of materials containing an unknown amount of U-235 assume the material is containerized rather than in piles. Some of the IROFS credited in these scenarios were therefore not available for the collection of the material in piles. Although the as-found condition presented no safety concern, the scenarios as documented in the ISA [Integrated Safety Analysis] did not demonstrate the performance requirements of 10 CFR 70.61 were maintained. "There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. "Ill. NOTIFICATION REQUIREMENTS "B&W is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61. "IV. STATUS OF CORRECTIVE ACTIONS "An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM TONY ENGLAND TO JOHN SHOEMAKER AT 0908 EST ON 2/11/15 * * * "I. EVENT DESCRIPTION "On January 28, 2015 B&W NOG-L notified the NRC of an unanalyzed condition that occurred during the cleanup of residual solids from the Uranium Recovery Low Level Dissolver that failed to meet the performance requirements of 10 CFR 70.61. As part of the subsequent investigation of the event an Extent of Condition Review was performed. During the Extent of Condition Review of cleanup of residual solids from the High Level Dissolver, a similar potential condition was identified at 10:00 a.m. EST on February 10, 2015. A cleanup activity was not in process at the time of discovery. "II. EVALUATION OF THE EVENT "The Uranium Recovery High Level Dissolvers process scrap fuel materials. Undissolved residual solids collect in the Dissolvers' recirculation columns over time. These solids contain some amounts of U-235 that did not go into solution. The Dissolvers periodically undergo cleanup operations during inventory or contract changes. During this cleanout a small amount of solids are emptied from the horizontal recirculation columns onto drip pans and then transferred to a favorable volume less than or equal to 2.5 liter container. Although a cleanup was not in process at the time of the Extent of Condition Review, it could not be readily determined that the performance requirements of 10 CFR 70.61 would be met if a cleanup operation were to be performed. There was no immediate risk of a criticality or threat to the safety of workers or the public. No actual event occurred. "Ill. NOTIFICATION REQUIREMENTS "B&W is revising Event Report #50776 dated January 28, 2015. A potentially unanalyzed condition was identified that could not be demonstrated as meeting the performance requirements. B&W is making this 24 hr. report in accordance with 10 CFR 70, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61. "IV. STATUS OF CORRECTIVE ACTIONS "An investigation of the root causes of this event is ongoing. Corrective actions will be determined as a result of the investigation. No cleanouts of the High Level Dissolvers' recirculation columns will occur until it can be demonstrated the performance requirements of 10 CFR 70.61 are met for this maintenance task." The licensee has notified the NRC Resident Inspector. Notified R2DO (Nease), NMSS EO (Rahimi), Fuels Group, and NMSS Events Notification via email. * * * UPDATE FROM TONY ENGLAND TO HOWIE CROUCH AT 1619 EDT ON 3/16/15 * * * "On February 11, 2015 Babcock & Wilcox (B&W) revised Event Report #50776 dated January 28, 2015. An Extent of Condition Review identified an unanalyzed condition associated with the cleanout of a High Level Dissolver (HLD) recirculation column. Although a cleanup was not in process at the time, it could not be readily determined that the performance requirements of 10 CFR 70.61 would be met if a cleanup operation were to be performed. There was no immediate risk of a criticality or threat to the safety of workers or the public. B&W amended the initial Event Report in accordance with 10 CFR 70, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 70.61. "The HLDs process scrap fuel materials. Undissolved residual solids collect in the Dissolvers' recirculation columns over time. These solids contain some amount of U-235 that does not go into solution. The Dissolvers periodically undergo cleanup operations during inventory or contract changes. During this cleanout a small amount of solids are emptied from the horizontal recirculation columns onto drip pans and then transferred to a favorable volume less than or equal to a 2.5 liter container. Further evaluation has determined that a criticality resulting from the cleanout of a recirculation column is not credible. This determination was made utilizing the guidance found in NUREG 15-20 which defines 'not credible' in part as: 'A process deviation that consists of a sequence of many unlikely human actions or errors in which there is no reason or motive... ' or 'Process deviations for which there is a convincing argument, given physical laws, that they are not possible, or any unquestionably extremely unlikely... ' "The inherent design and process intent of the trough dissolvers, the nature of the chemical reactions involved, and the number of unlikely human errors that would have to occur to accumulate a sufficient amount of fuel and have it collect with a low enough packing fraction and entrained water, combine to make a criticality on the drip pans not credible. "Although the facility was in a state that was not analyzed, was improperly analyzed, or different from that analyzed in the Integrated Safety Analysis, a criticality was not credible. Therefore, B&W is correcting Event Notification #50776 in accordance with 10 CFR 70.74(a)(4) and withdrawing the 10 CFR 70, Appendix A, (b)(1) notification of February 11, 2015." The licensee will notify the NRC Resident Inspector. Notified R2DO (Shaeffer), NMSS EO (Araguas) and FUELS OUO Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2015-02-18
50775 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-01-28 08:49 | 2015-01-28 15:24 | 2015-01-28 | SITE STACK RADIATION MONITOR FAILURE The Millstone site stack radiation monitor, RM-8169, failed and was declared inoperable at 0849 EST on January 28, 2015. Repairs are in progress. This event is reportable pursuant to 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability, off-site response capability, or off-site communications capability. The Instrument and Controls Department is conducting troubleshooting and repair. The cause of the radiation monitor failure was pump failure. Estimated return to service is 1600 EST on 1/29/15. The licensee has notified the NRC Resident Inspector and applicable State and Local authorities. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-28
50774 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-12-06 10:12 | 2015-01-28 13:50 | 2015-01-28 | 60 DAY OPTIONAL REPORT - HALF SCRAM AND A DIVISION 2 PRIMARY CONTAINMENT ISOLATION SIGNAL "On December 6, 2014, at approximately 1012 CST, while the plant was operating at 100 percent power, the Division 2 reactor protection system (RPS) bus de-energized unexpectedly. This resulted in a half-scram and a Division 2 primary containment isolation signal. Operators executed the appropriate abnormal operating procedures to begin an orderly restoration of the affected systems. Atmospheric pressure in the primary containment momentarily reached the high-pressure alarm setpoint, necessitating entry into the emergency operating procedure for that condition. "Automatic isolation valves in the following systems closed as designed: - reactor plant component cooling water - drywell unit cooler water supply - reactor building floor and equipment drains - reactor building HVAC chilled water supply - containment airlock seal air supply - reactor recirculation system flow control valve hydraulics - main steam line drains - reactor water cleanup - auxiliary building and annulus HVAC systems "These engineered safety systems actuated as designed: - standby gas control filter trains - fuel building filter trains - control building filter trains "The event occurred approximately 25 hours after the Division 2 RPS motor-generator (MG) was aligned to the bus following replacement of the voltage regulator. Following the event, the MG set was found running with its output breaker tripped. "A failure analysis determined that the spike suppressor and the field flash card were potential sources of the MG breaker trip. The spike suppressor was replaced. Inspection of the field flash card found a strand of wire from one of the attached leads nearly touching a trace on the circuit board. Testing determined that the wire strand was the most likely cause for the breaker trip. With no spare card readily available, the wire strand was removed and the field flash card was re-installed. Other cards were inspected, and no similar conditions were found. The MG set was load tested for 30 hours, and was placed in service on December 17[, 2014]. "Additionally, it is suspected that there is an intermittent failure occurring in the field flash card. A design change will be developed to correct that condition." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-01-28
50773 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-01-28 10:18 | 2015-01-28 11:38 | 2015-03-11 | EMERGENCY OPERATIONS FACILITY UNAVAILABLE DUE TO PLANNED VENTILATION MAINTENANCE "The Comanche Peak Primary Emergency Operations Facility (EOF) will be unavailable during planned maintenance on the EOF ventilation system. "On January 28, 2015, CPNPP [Comanche Peak Nuclear Power Plant] began planned work to improve the reliability of the EOF ventilation system. The EOF will be unavailable for approximately three weeks. During the time the primary EOF is unavailable, the affected ERO members will respond to the Backup EOF in Granbury, Texas for any declared emergency event. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time the primary EOF is unavailable. "The extended unavailability of the primary EOF is being reported in accordance with 10CFR50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. The NRC Resident [Inspector] has been notified. A follow-up ENS communication will be made when the primary EOF availability is restored." * * * UPDATE ON 03/11/2015 AT 1811 EDT FROM BRIAN MITCHELL TO JEFF HERRERA * * * "The availability of the Comanche Peak Primary Emergency Operations Facility (EOF) has been restored following planned maintenance on the EOF ventilation system. "On January 28, 2015, CPNPP (Comanche Peak Nuclear Power Plant) began planned work to improve the reliability of the EOF ventilation system. The unavailability of the primary EOF was reported in accordance with 10 CFR 50.72(b)(3)(xiii). This report serves as a follow-up to Event Number 50773." The licensee notified the NRC Resident Inspector. The R4DO (Okeefe) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-28
50772 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-01-28 05:35 | 2015-01-28 08:56 | 2015-01-28 | RESIDUAL HEAT REMOVAL CAPABILITY AFFECTED BY VALVE CLEARANCE "At 0535 CST on 1/28/15, control room staff identified that valve EJHV8716A, RHR A To SIS [Safety Injection System] Hot Leg Recirc Loops 2&3 [isolation valve], had been closed per clearance order C20-D-EJ-A-005 to support maintenance on the A RHR system. Closing valve EJHV8716A placed Wolf Creek in TS 3.0.3. At 0550 CST on 1/28/15, power was restored to valve EJHV8716A and the valve was opened, allowing the unit to exit from TS 3.0.3. Subsequent reviews of clearance order C20-D-EJ-A-005 identified that valve EJHV8809A had been energized and closed per direction of the clearance order. TS 3.0.3 was reentered at 0635 CST due to discovery of this condition. At 0650 CST, valve EJHV8809A was opened and deenergized allowing exit from TS 3.0.3." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2015-01-28
50771 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-01-27 09:48 | 2015-01-27 16:56 | 2015-01-27 | LOSS OF HIGH PRESSURE COOLANT INJECTION "On Tuesday, January 27, 2015, at 0948 EST, with the Reactor Mode Select Switch (RMSS) in the Shutdown position and Pilgrim Nuclear Power Station (PNPS) at 0% core thermal power, the High Pressure Coolant Injection (HPCI) system was isolated by the main control room operating crew and declared INOPERABLE. HPCI had been in service for reactor pressure control following the automatic reactor scram experienced during winter storm 'Juno' reported in EN# 50769. It appears there was a malfunction of the HPCI turbine gland seal condenser blower or associated condensate pump. Reactor pressure control was transitioned to the safety relief valves and the reactor cooldown was continued. The plant is stable. The Emergency Diesel Generators are powering the safety related 4KV buses and reactor water level is being maintained by the Reactor Core Isolation Cooling (RCIC) system. HPCI is required to be OPERABLE in accordance with Technical Specification 3.5.C.1. Since HPCI is a single train system, the INOPERABILITY is reportable in accordance with 10CFR50.72(b)(3)(v)(D). The cause of the HPCI malfunction is not known at this time and troubleshooting continues. "This event had no impact on the health and/or safety of the public. "The USNRC Senior Resident Inspector has been notified." Shutdown cooling is in service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-01-27
50770 | -1 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2015-01-26 14:30 | 2015-01-27 14:49 | 2015-03-26 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following report was received from the State of Maryland via email: "On 1/27/15 at 0830 EST, [Maryland Department of the Environment (MDEP) personnel] discussed preliminary findings [with the licensee] regarding an alleged medical misadministration at the Cancer Center at Gaithersburg with the Medical Physicist and RSO [Radiation Safety Officer]. The initial notification came to [the Maryland] RHP [Radiological Health Program] on 1/26/15 at 1600 EST. "The incident occurred on 1/26/15 at about 1430 EST at the licensees address at 808 West Diamond Avenue, Gaithersburg, Maryland 20878. "The incident involved a skin cancer therapy treatment to the bridge of the nose to a female patient with a Elekta/Nucletron HDR [High Dose Rate]. "The licensee has done previous skin treatments but this was the first skin treatment performed at the bridge of the nose. "[The Licensee] stated no history of previous medical incidents. "The written directive was for 3900 centiGray to be delivered over 6 fractions. The first fraction was intended to be 650 centiGray, but the licensee administered 1300 centiGray. "Preliminary discussion of root cause indicated that the patient was not fully conscious and in distress with the use of a 3 centimeter diameter applicator and a decision was made to change the applicator size to 2 centimeters. The treatment plan initially determined for the 3 centimeter diameter applicator was mistakenly added to the treatment plan determined for the 2 centimeter applicator. The Medical Physicist says there is no dialog warning on the software to indicate that an addition will occur. "The licensee stated that the husband of the patient has been notified. Potential future erythema of the patient skin will be followed. "Present at the therapy - Oncologist, Medical Physicist, and Therapist. "[The Medical Physicist] stated that the licensee will re-examine all quality assurance oversight for HDR therapies. "Preliminary consideration for corrective actions: All new treatment plans will be given new identities [and] the licensee will explore ways to delete previous treatment plans. "The licensee is working to have the written report to RHP prior to end of the 1/27/15 business day. "[The Medical Physicist] was informed that RHP will investigate the incident." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM ALAN JACOBSON TO JEFF HERRERA ON 01/28/2015 AT 0828 EST * * * The following information was provided by the State of Maryland via email: The female patients age is 67 and the Elekta/Nucletron HDR Model is 105.002 Microselectron 3. The activity of the source is approximately 5.2 Ci. Notified the R1DO (Cahill) by phone and NMSS Events Notification (Email). * * * EVENT RETRACTED AT 1205 EDT ON 3/26/2015 BY RAY MANLEY TO MARK ABRAMOVITZ * * * This event is retracted because the dose delivered matched the written directive. Due to a software error, the dose was reported as double the actual dose. The patient, doctor and NMED have been notified. Notified the R1DO (Jackson) and NMSS Events Resource (via e-mail) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2015-02-04
50769 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-01-27 04:02 | 2015-01-27 06:41 | 2015-01-27 | AUTOMATIC REACTOR SCRAM ON TURBINE TRIP DUE TO LOSS OF OFFSITE POWER "On Tuesday January 27, 2015 at 0402 hours, with the Pilgrim Nuclear Power Station (PNPS) Reactor Mode Select Switch (RMSS) in Run and reactor power approximately 52% an automatic reactor scram signal was received due to the automatic trip of the main turbine that was initiated by the opening of the main generator breaker, ACB-104. The event occurred during winter storm 'Juno.' Prior to the event off-site transmission Line 355 was de-energized due [to] weather conditions and its associated PNPS switchyard breakers (ACB-105, a main generator breaker and ACB-102), were open. Per station procedures, reactor power was being lowered, a reactor protection system bus had been placed onto a back-up power supply, the Emergency Diesel Generators had been started and were powering the associated safety related 4 KV buses. The second off-site transmission Line 342 de-energized and the associated PNPS switchyard breakers (ACB-104 main generator breaker and ACB-103) opened. The Shutdown Transformer off-site power supply has remained available throughout this event. All control rods were verified to be fully inserted. Per plant design, Primary Containment Isolation System (PCIS) Group lI sampling systems, Group VI Reactor Water Clean-up (RWCU) system and Reactor Building Isolation System (RBIS) isolations occurred. Currently, the EDG's are powering the safety related 4KV buses, reactor water level is being maintained by the Reactor Core Isolation Cooling (RCIC) system and reactor pressure is being maintained by High Pressure Coolant Injection (HPCI) system. The station is conducting a plant cool down at this time. All systems responded as designed with the exception of a non-safety-related diesel air compressor, K-117 that failed to start." The licensee will notify the State and local governments and plans on issuing a press release. The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 52 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2015-01-27
50768 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2015-01-27 02:00 | 2015-01-27 02:00 | 2015-01-28 | SAFEGUARDS REPORT DUE TO ADVERSE WEATHER Safeguards system degradation related to monitoring and detection of the OCA (Owner Controlled Area). Compensatory measures taken. The licensee will inform the NRC Resident Inspector and NRC Region I (Caron). * * * 0410 EST ON 01/27/15 FROM PHILLIP BEABOUT TO S. SANDIN * * * Safeguards system degradation related to monitoring and detection of the PA (Protected Area). Compensatory measures taken. The licensee will inform the NRC Resident Inspector and NRC Region I (Caron). * * * UPDATE FROM PHILLIP BEABOUT TO J. HERRERA ON 01/28/2015 AT 0650 EST * * * Partial physical protection measures being restored due to improving weather conditions. The licensee informed the NRC Resident Inspector and NRC Region 1 (Caron). Notified R1DO (Cahill) and Part 73 Group via email.. * * *UPDATE FROM PHILLIP BEABOUT TO JEFF ROTTON ON 01/28/2015 AT 1806 EST * * * All physical protection measures have been restored due to improving weather conditions. The licensee informed the NRC Resident Inspector and NRC Region 1 (Caron). Notified R1DO (Cahill) and Part 73 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2015-01-27
50767 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-01-26 16:50 | 2015-01-27 00:24 | 2015-01-27 | TURBINE BUILDING STACK VENTILATION RADIATION PROCESS MONITORS REMOVED FROM SERVICE Normal and High Range Ventilation Process Radiation Monitors (3HVR*RE10A/B) were removed from service due to low process flow affecting sample flow. The cause of the low process flow is unknown and under investigation at this time. Maintenance was performed yesterday, 1/26/15, including a successful calibration. Action taken includes placing temporary sampling in service and estimating process flow. A priority one work package has been issued with repairs in progress. The licensee informed the State of Connecticut, Waterford Township Police and the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-27
50766 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-01-26 | 2015-01-26 18:55 | 2015-02-18 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following report was received from the State of Texas via email: "On January 26, 2015, the licensee notified the Agency [State of Texas] that one of its technicians had left a temporary job site in Fort Worth and after traveling approximately 30 minutes toward another job site, he realized the tailgate was down [and the gauge was missing]. When he left the first site, he had left the Humboldt 5001EZ moisture/density gauge (SN: 3613), containing one 10 millicurie cesium-137 source and one 40 millicurie americium-241/beryllium source, on the tailgate and not secured in the back of the vehicle. The technician returned to the site and looked for the gauge. Other construction workers at the site did produce the carrying case and the lock that had been on it, the standard block, and the flattening plate but not the gauge. The licensee is notifying local law enforcement and will return to the site in the morning with reward offer. Further information will be provided as it is obtained in accordance with SA-300." Texas Report Number: I-9272 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-02-03
50765 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2015-01-26 | 2015-01-26 17:09 | 2015-01-26 | AGREEMENT STATE REPORT - STOLEN DOSE CALIBRATOR SOURCES The following report was received from the State of Georgia via email: "Georgia Radioactive Materials Program discovered through a Law Enforcement List Server that 2 Co-57 sources and 1 Cs-137 source (what appear to be Dose Calibrator Sources as indicated in the example photo provided by LE) were stolen from a vehicle at or around Atlanta Hartsfield Airport. "Activities of the sources are: The 2 Co-57 are 2.47 mCi and .365 mCi sources. The Cs-137 is a .232 mCi source. "The individual transporting the sources was from Florida [Florida Department of Radiation Services]. Florida Radiation Control has been notified and Atlanta FBI has been notified. "Updates to follow when more information is available." State of Georgia Event Report 1-26-2015. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2015-02-03
50764 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-08-15 | 2015-01-26 17:20 | 2015-01-26 | AGREEMENT STATE REPORT - STOLEN TRITIUM EXIT SIGN The following information was obtained from the State of California via facsimile: "On 01/22/15, RHB [California Radiologic Health Branch] was notified of a stolen tritium exit sign from an AMC Theatre in San Jose, CA. The police report No. 142273216 filed by the AMC theatres on 08/15/14 stated the following: 'The management was doing a walkthrough of the building on 08/15/14 at AMC Saratoga 14. In theatre No. 13, the manager noticed one of the exit signs missing.' "The model, S/N or the activity of the exit sign is unknown. RHB will be contacting AMC theatres and the Ultimate Lighting Source (vendor) to get further details." California Report Number: 5010-012215 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-02-03
50763 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-01-25 | 2015-01-26 15:17 | 2015-01-26 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA WITH STUCK SOURCE The following report was received from the State of Texas via email: "On January 26, 2015, the licensee notified the Agency [State of Texas] that on January 25, 2015, one of its industrial radiography crews had experienced a source disconnect. The crew was using a QSA Delta 880 exposure device (SN: 12916) containing a 98.5 curie iridium-192 source. After the first exposure of the day, the crew was unable to retract the source and it was determined that it was in the collimator. Barriers were extended. The licensee's site radiation safety officer (SRSO), who is authorized to perform source retrieval, responded. (The SRSO) was unable to get the source to slide back down the guide tube and had to use pliers to remove the collimator to recover the source and complete the retrieval. None of the 4 radiographers present at the site exceeded doses of 30 millirem according to their self-reading pocket dosimeters. The SRSO's self-reading pocket dosimeter indicated a whole body dose of 73 millirem. [The SRSO's] dosimetry badge is being sent for immediate processing. The SRSO's dose to both hands is being calculated. [The SRSO] affixed pocket dosimeters to both hands, but two of the 3 times he handled the source guide tube or collimator, they went off-scale. No member of the public received any exposure as a result of this event. The SRSO reported he consulted with the manufacturer and thoroughly inspected the equipment. [The SRSO] found no issues. [The SRSO] reported, he attempted, unsuccessfully, to replicate the disconnect. Based on [the SRSO's] findings, the camera was put back into use and not removed from service." Texas Incident #: I - 9271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-02-03
50762 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2015-01-23 10:30 | 2015-01-26 12:58 | 2015-01-26 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED AT CONSTRUCTION SITE The following report was received from the State of Florida via email: "A Troxler Gauge Model No. 3440 was run over by a Bobcat tractor on a road construction site around 1030 EST [on 1/23/15] . The source was retracted when the gauge was hit. [The Florida State] Inspector arrived on scene and found gauge on truck tail gate. The gauge had been moved to tail gate before calling [the State]. [The State] Inspector surveyed the ground where gauge was hit and read background readings. Other readings: 6ft from gauge 23 uR/hr, gauge handle 71 uR/hr, top of gauge housing 13.3 mR/hr, source door 8.44 mR/hr. The guide rod and housing were broken but source was secure and there was no leakage of radiation. The gauge released to owner to be returned for repair. No further action will be taken on this incident." This incident occurred at the intersection of S. Andrews and SE 30th St, Ft. Lauderdale, Fl. Troxler Gauges, Model No. 3440, have a Cs-137 source not exceeding 9 mCi and a Am-241 source not exceeding 44 mCi. Florida Incident Number: FL15-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2015-02-03
50761 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2015-01-24 | 2015-01-26 12:30 | 2015-01-28 | AGREEMENT STATE REPORT - ATTEMPTED THEFT OF RADIOGRAPHIC EQUIPMENT The following information was obtained from the State of Kansas via email: "The Team Industrial office in Wichita was broken into. They have video evidence of attempt to access the licensed material of concern. All material is accounted for. Missing items include UT equipment, computers, vehicle keys (vehicles were not taken), files were ransacked including the sensitive information files. Unknown at this time if sensitive information was taken. "Police notified." Kansas Case Number: KS150001 * * * UPDATE FROM JAMES HARRIS TO JEFF HERRERA ON 01/28/2015 AT 1327 EST * * * The following updated information was provided by the Kansas Department of Health and Environment via email: The Kansas Department of Health and Environment provided additional detail regarding the event and the items stolen. Radioactive material was not stolen as a result of the break in attempt(s). Local law enforcement and FBI were notified and investigated the event. Additional corrective actions were taken by the licensee to secure sensitive materials and equipment. A reward has not been offered for return of the stolen items. A detailed list of the missing items has been provided to the Wichita police department. Notified R4DO (Vasquez), ILTAB (Wray) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2015-02-03
50760 | 0 | BIOSTORAGE TECHNOLOGIES, INC |  |  |  |  | 2014-12-31 | 2015-01-26 11:11 | 2015-01-26 | LOST RADIOACTIVE MATERIAL INADVERTENTLY INCINERATED The licensee lost 9 vials of Carbon 14 (each vial containing 2 mCi). It was later determined that the vials were mistakenly disposed of with a large amount of non-radioactive medical waste on 12/31/2014. The medical waste and all 9 vials were incinerated on 1/7/2015 by Stericycle in Clinton, IL. The licensee has instituted corrective actions including more robust labelling to identify radioactive material. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2015-02-03
50759 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-01-26 03:55 | 2015-01-26 05:04 | 2015-01-27 | TECHNICAL SUPPORT CENTER OUT OF SERVICE FOR PLANNED PREVENTATIVE MAINTENANCE "At 0355 [CST] on Monday, January 26, 2015, the Dresden Nuclear Power Station (DNPS) Technical Support Center (TSC) emergency ventilation system was removed from service for planned preventative maintenance activities on the TSC air handling unit, air compressor units, and TSC air filtration unit. During the maintenance, the TSC Ventilation will be shut down. The TSC air filtration fan and dampers will be non-functional, rendering the TSC HVAC accident mode non-functional. This maintenance is scheduled to minimize out of service time. The planned TSC ventilation outage is scheduled to be completed within 38 hours. Contingency plans are in place so that if an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing Emergency Planning (EP) procedures and checklists. If radiological or environmental conditions require TSC facility evacuation during ventilation system restoration; the Station Emergency Director will evacuate and relocate the TSC staff in accordance with station procedures. "The NRC Resident Inspector has been notified." * * * UPDATE FROM RYAN SEARS TO JOHN SHOEMAKER AT 2012 EST ON 1/27/15 * * * "At 1740 CST on January 27th, 2015, Dresden TSC Ventilation was restored. The Dresden TSC Ventilation is functional at this time. "The NRC Resident Inspector has been notified." Notified the R3DO (Dickson). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-26
50758 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2015-01-23 | 2015-01-23 16:02 | 2015-02-23 | AGREEMENT STATE REPORT - LOAD OF GARBAGE REJECTED AT LANDFILL DUE TO ELEVATED RADIATION READINGS The following information was obtained from the State of New Jersey via email: "A Pennsylvania landfill rejected a load of garbage based on elevated radiation readings (188 uR/h) and sent it back to NJ. PA identified the nuclides as Mn-54 and Co-57. [A New Jersey Department of Environmental Protection (NJDEP)] inspector went to the NJ garbage facility to verify the readings and nuclides. "[NJDEP informed] the waste facility that [they] would be coming to observe the separation/isolation process, but [before the] inspector got there, they had already done everything. According to the facility personnel, there was a bag of metal parts (they opened it up), but had double bagged it by the time [the inspector] got there. [The] inspector got 23 mR/h on contact, 849 uR/h at 1 foot and 62 uR/h at 1 meter. Discussions revealed that no one picked it up with their hands and they were not near the source for very long. [NJDEP] identifier/Ortec readings confirm Co-57 and Mn-54 also Co-60 and Co-56. It appears to be activated metal. [A certified contractor] has been hired to package [the material]. He will be there sometime later next week. [The inspector did] not see any identifying markings. [The inspector] also took wipes of the bag and the floor area where it was dumped. These were clear. The garbage that was taken out along with the source was scanned and found to be background. That material will remain in NJ. [The] inspector surveyed the original truck with the remainder of the garbage, and [it] was found to be clear. They are running [the truck] through their portal monitor and if ok, will send [it] back to PA. The truck did not leave from this facility originally so it did not go through a monitor before going to PA. The activated metal has been isolated and secured." * * * UPDATE FROM JENNY GOODMAN TO JOHN SHOEMAKER AT 1331 EST ON 1/26/15 * * * The following update was received via email from the State of New Jersey via email: "Upon NJDEP arrival at the waste facility on 1/23/15, the [landfill] facility staff had already isolated the material causing the radiation levels. The bag of waste they isolated measured as follows with a 1.5 by 1.5 NaI probe: Near contact: 23 mR/hr At ~1 foot: 840 microR/hr At ~3 feet: 62 microR/hr At ~6 feet: 10 microR/hr Background: 3-4 microR/hr "The tipping floor, where material had been laid out, and the three individuals involved in sorting the load were surveyed with a pancake probe. No radiation levels above background were detected. A wipe of the bag revealed no removable contamination. "[NJDEP] surveyed the truck carrying the remainder of the MSW [Municipal Solid Waste] load and detected no elevated [radiation] levels. The truck was released to return to the PA landfill. [NJDEP] has not received an update from the facility to confirm acceptance of that material. "[NJDEP] obtained a spectrum with the Ortec Detective-EX which identified Co-56, Co-57, Co-60, & Mn-54. A manual review of the spectrum additionally indicated Co-58. These isotopes are typical for metal activated from operation of an accelerator. Today, [NJDEP] contacted the DNDO [Domestic Nuclear Detection Office] JAC [Joint Analysis Center] for secondary reachback analysis of the spectrum. [NJDEP] received verbal confirmation of the isotopes detected. A written report is expected by tomorrow. Subsequently, [NJDEP] received a telephone call from an FBI bomb tech who had been informed of [NJDEP's] request for analysis. [The FBI] was seeking confirmation that there was no suspicious packaging or other threat associated with the package. [NJDEP] explained that we routinely find items in the waste stream and there was no specific threat or suspicious packaging. "[NJDEP] is still awaiting follow-up from the waste facility to confirm acceptance of the remainder of the load released Friday and details for their plans for disposal. [NJDEP] will plan to return when their consultant packages the material to see if any other information can be gathered to identify a possibly point of origin for the material." Notified R1DO (Cahill), ILTAB (Wray), and NMSS Events Notification via email. * * * UPDATE FROM JAMES MCCULLOUGH TO HOWIE CROUCH AT 0913 EST ON 2/23/15 * * * "On 2/18/2015 the facility's consultant removed the material for proper disposal. The radioactive item was determined to be a small metal foil. No specific point of origin could be determined." New Jersey Department of Environmental Protection considers their investigation closed. Notified R1DO (Powell), ILTAB (Whitney) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2015-02-02
50757 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-01-23 11:50 | 2015-01-23 15:09 | 2015-01-23 | OFFSITE NOTIFICATIONS DUE TO OIL SHEEN ON INTAKE BAY "On 1/23/2015 at 1150 EST, an oil sheen was verified to be in the waters of the U.S. (Sequoyah's Intake Forebay). At 1221 [EST], a notification to the National Response Center [report #1106407] was made as a result of the oil sheen (< 1 pint total). The source of the oil is from temporary connections in support of maintenance. Cleanup efforts are in progress. "The following additional agencies have also been notified: EPA Region 4, Tennessee Department of Environment and Conservation (TDEC), and Tennessee Emergency Management Agency (TEMA)." The licensee also notified the Hamilton County Emergency Management Agency and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-02-02
50756 | 0 | DANBURY HOSPITAL |  |  |  |  | 2015-01-07 | 2015-01-23 14:52 | 2015-02-03 | RECEIVED DOSE DIFFERED FROM PRESCRIBED DOSE OF I-125 On December 17, 2014, a patient had a 123 microCurie I-125 seed implanted in her breast as part of a treatment plan for non-palpable breast cancer. The treatment plan was to remove the seed after 5 days. Due to illness, the patient was unable to return to the hospital to have the seed removed until January 7, 2015. This resulted in the patient receiving an 83.6 cGy exposure versus the prescribed 18.4 cGy exposure. The prescribing physician and the patient were notified. No permanent damage due to the exposure is expected. The licensee coordinated this report with NRC Region 1 Senior Health Physicist Penny Lanzisera. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM RUTH SHANLEY TO CHARLES TEAL AT 1529 EST ON 2/3/15 * * * The licensee called to report two additional patients whose dose exceeded 50 cGy. The first patient was not medically cleared for the procedure. The patient received 57.9 cGy instead of the prescribed dose after 5 days of 21.8 cGy of I-125. The second patient refused to undergo the procedure until genetic testing was completed. The patient received 54 cGy instead of the prescribed dose after 5 days of 20.3 cGy of I-125. The licensee will modify their procedures to wait until patients are medically cleared and wait until all other testing is done prior to undergoing the procedure. Notified R1DO (DeFrancisco) and NMSS Events Notifications via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-02-02
50755 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-01-21 | 2015-01-23 14:03 | 2015-01-23 | AGREEMENT STATE REPORT - MISSING 10 MILLICURIE CS-137 SOURCE The following information was received from the State of Louisiana Department of Environmental Quality Assessment Division via fax: "On 11/21/2014, Berthold Technologies reported that Morehouse Bioenergies, LLC called to replace a density gauge source, 10 mCi Cs-137, for a gauge they were installing on a process. However, Berthold Technologies had sold and shipped the whole unit to BioEnergies in March 2014. The reorder peaked the interest of Berthold Technologies who notified the LDEQ. Attempts to reach Drax Biomass International, Inc., the radiation responsible company and owners of Morehouse Bioenergies, LLC, were unsuccessful on numerous occasions. "Berthold Technologies supplied shipping documents, quarterly distribution records and signed records of receipts for the source/gauge. The record of receipt was signed and transferred back to the construction foreman and the site on March 25, 2014. The location of the source from March to November 2014, is unknown and continues to be a mystery. "This site is a wood yard for manufacturing wooden pellets. Its location is in the deep woods of north Louisiana and is only accessible from the state of Arkansas. The scintillation detector has been installed, but the box with the Cs-137 source is nowhere to be found. All communication with Drax Biomass International, Inc. is done by remote access and usually by return phone call. "The gauge was a Berthold Technologies unit shielding Model LB 7440-F-CR, Serial Number 37625-11972. The source was 10 mCi of Cs-137 serial number 0038/13. "Event Location: The Morehouse Bioenergies, 7070 Carl Road, Bastrop, LA 71220. This was a construction site for a wood pellet plant. An investigator made a site visit, but there was only a person with Haskell Contractors to interview. "Event Type: This was a loss of control incident that has not been resolved to this date. The freight company delivered the gauge to the site and it has since disappeared. This incident is considered still open." Louisiana Department of Environmental Quality, Radiation Assessment report number: LA-150003, T160317. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-02-02
50754 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2014-11-26 14:27 | 2015-01-23 11:00 | 2015-01-23 | INVALID ACTUATION OF A GENERAL CONTAINMENT ISOLATION SIGNAL AFFECTING MORE THAN ONE SYSTEM "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On November 26, 2014, at approximately 1427 hours Central Standard Time (CST), the Browns Ferry Nuclear Plant (BFN), 1A Reactor Protection System (RPS) Motor-Generator (MG) Set Power Supply unexpectedly de-energized resulting in a BFN Unit 1 half scram and Primary Containment Isolation System (PCIS) Groups 1, 2, 3, 6, and 8 isolation signals. The PCIS Groups 1, 2, 3, 6, and 8 isolations caused the initiation of all three trains of the Standby Gas Treatment (SBGT) system and Control Room Emergency Ventilation (CREV) subsystem 'A', and isolations of the BFN, Unit 1, Reactor Zone ventilation and BFN, Units 1 and 2, Refuel Zone ventilation (Unit 3 Refuel Zone ventilation was tagged out under 3-TO-2014-0001 at the time of this event). Operations personnel responded to the PCIS initiation, ensured all equipment operated as designed, placed the BFN 1A RPS on alternate power, and reset the RPS logic and PCIS isolations. "Plant conditions which initiate PCIS Group 1 actuations are Reactor Pressure Vessel (RPV) Low Low Low Water Level (Level 1), Main Steam Line (MSL) High Flow, MSL Area High Temperature, or MSL Low Pressure. Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The apparent cause for this condition was an intermittent problem with the BFN 1A RPS MG Set voltage adjust potentiometer. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Problem Evaluation Report 961518. "The NRC Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-01-23
50753 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-01-23 06:13 | 2015-01-23 09:34 | 2015-01-23 | OFFSITE NOTIFICATION DUE TO NON-WORK RELATED ON-SITE CONTRACTOR FATALITY "At approximately 0531 EST on January 23, 2015, the Brunswick Nuclear Plant main control room received an emergency call for a contract employee experiencing a non-work related medical issue. Site first responders were dispatched in conjunction with a request for off-site medical assistance. At approximately 0613 EST, the responding off-site paramedics determined that the efforts to revive the patient were unsuccessful. The individual was outside of the protected area (within the owner controlled area), and no radioactive material or contamination was involved. The cause of death has not been determined. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) for situation related to the health of on-site personnel for which a notification to other government agencies is planned. The Occupational Safety and Health Administration (OSHA) will be notified. A press release is not planned at this time. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-01-23
50752 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2015-01-22 17:45 | 2015-01-22 18:51 | 2015-03-13 | UNANALYZED HEAT EXCHANGER LINEUP COULD EXCEED DESIGN BASIS TEMPERATURES "On 1/20/15, it was determined that a certain line up of component cooling heat exchangers and shutdown cooling heat exchangers could exceed the design basis temperatures for the component cooling water system following a design basis accident. Although not a safety concern at this time because of low ultimate heat sink temperatures (which cools component cooling water), in the past the ultimate heat sink temperatures have been high enough to create this condition. This particular heat exchanger line up was unanalyzed in that the ultimate heat sink temperature limits were not known until 1/22/15. This issue has been entered into the corrective action program. "A review of Control Room logs for 2014 showed that in 1 instance for Unit 1 and 1 instance for Unit 2, the Units were in an unanalyzed lineup with ultimate heat sink temperature greater than the maximum now calculated. During these instances, both Units had an unanalyzed condition that had potential to significantly degrade plant safety and is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." * * * RETRACTED ON 03/03/15 AT 1410 EST FROM CHARLES MORGAN TO JEFF HERRERA * * * "Further engineering analysis has refined the ultimate heat sink temperature that provides an acceptable safety system response with the component cooling water and shutdown cooling heat exchanger lineups in question. The revised information demonstrates that the system lineups that occurred in the last 12 months did not result in an unanalyzed condition that significantly degrades plant safety. This event notification is retracted." The NRC Resident Inspector will be notified. The R1DO (Burritt) was notified. * * * UPDATE ON 03/12/15 AT 1303 EDT FROM ED SCHINNER TO DANIEL MILLS * * * "The retraction statement provided on 3/3/15 incorrectly addressed system lineups limited to the last 12 months. The original withdrawal was prematurely submitted and therefore the original notification (Event report 50752) is not retracted and remains valid. "The NRC Resident Inspector has been notified." The R1DO (Cook) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2015-01-22
50751 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2015-01-22 18:13 | 2015-01-22 18:31 | 2015-01-22 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO TOXIC GAS IN THE SECURITY DIESEL BUILDING At 1801 EST, the control room received multiple fire alarms in the control room. At 1803, site security notified the control room of the presence of smoke in the security diesel building. At 1813, the licensee declared a Notification of Unusual Event due to the presence of toxic gas in the security diesel building on the battery/UPS side of the building. The fire suppression (NOVEC) system had discharged. Both the Technical Support Center and the Operations Support Center were fully manned. The site fire brigade made entry into the building and saw no evidence of fire but they did see and smell an acrid odor from an apparent electrical fire as well as the presence of the NOVEC fire suppressant. Offsite assistance was requested but not required to mitigate the event. Investigation of the cause of the toxic gas is under investigation. At this time, no security equipment is affected. Both the Technical Support Center and the Operations Support Center were fully manned. The licensee notified the State of North Carolina, New Hanover and Brunswick counties, and the NRC Resident Inspector. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA National Watch Center (email) and Nuclear SSA (email). * * * UPDATE FROM BRUCE HARTSOCK TO MARK ABRAMOVITZ AT 1936 EST ON 1/22/15 * * * At time 1923 EST, the Notification of Unusual Event was terminated after normal access to the security diesel building was restored. The cause of the event is under investigation. The licensee notified the State of North Carolina, New Hanover and Brunswick counties, and the NRC Resident Inspector. Notified R2DO (McCoy), IRD (Stapleton), NRR (Evans), DHS SWO, FEMA Operations Center, DHS NICC, FEMA National Watch Center (email) and Nuclear SSA (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2015-01-22
50750 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2015-01-21 15:00 | 2015-01-22 14:44 | 2015-01-22 | DRY CONVERSION PROCESS IMPROPERLY ANALYZED IN THE CURRENT INTEGRATED SAFETY ANALYSIS "During a GNF-A review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA), it was determined at approximately 3:00 PM (EST) yesterday (1/21/15) that a quantitative risk assessment associated with the Dry Conversion Process (DCP) cylinder cold trap operation was improperly analyzed in the current ISA. The item relied on for safety (IROFS) and other controls associated with preventing overfilling the cold trap system remained available and reliable. However, the initiating event frequency for a particular accident sequence was determined to be higher than that documented resulting in a failure to meet performance requirements. "At no time was the postulated condition present; therefore no potential unsafe condition occurred. The affected equipment has been shut down and an investigation is underway to provide additional corrective actions and determine extent of condition. "While this did not result in an unsafe condition, this event is being reported pursuant with the reporting requirements of 10 CFR 70 Appendix A (b)(1) within 24 hours of discovery." The licensee will be notifying the State of North Carolina Radiation Protection Division and the New Hanover City of Environmental Management. The NRC Region II office and NRC Project Manager will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2015-01-30
50749 | 0 | TEXAS A&M (AGN) |  |  |  | 0.005 KW AGN-201 #106 | 2015-01-21 | 2015-01-22 13:31 | 2015-01-22 | VIOLATION OF TECHNICAL SPECIFICATION AT RESEARCH AND TEST REACTOR FACILITY The following information was obtained from the licensee via email: "Notification of Reportable Occurrence at the Texas A&M University AGN 201M Reactor: Transgression of Technical Specification 5.3 Reactor Room, Reactor Control Room, Accelerator Room (item d). "During a review of the AGN 201M reactor facility boundary, it was discovered that the facility was not in compliance with Technical Specification 5.3.d. More specifically, the reactor control console is located in the reactor room contrary to the specification. This specification reads: 'The reactor room, reactor control room, and accelerator room are separate rooms in the Zachry Engineering Center, constructed with adequate shielding and other radiation protective features to limit doses in restricted and unrestricted areas to levels no greater than permitted by 10 CFR 20, under normal operating conditions, and to a level below criterion 19, Appendix A, 10 CFR 50 recommendations under accident conditions.' "On April 2, 1984, a memo was sent to the Texas A&M University Reactor Safety Board (RSB) Chairman requesting the control console be moved to the reactor room. In this memo, it was noted that a submittal of changes to the security plan and emergency plan would be required to the Nuclear Regulatory Commission (NRC). Approval for this modification was authorized by the RSB on April 20, 1984. The reactor control console was relocated to the reactor room on September 20, 1984. The University subsequently submitted the revised security plan and emergency plan to the NRC, dated October 11, 1984. Upon review of the changes, the NRC agreed with the changes to the emergency plan and requested further review at Headquarters for implementation of the new security plan. The University then requested a license amendment on September 2, 1985 for implementation of the revised security plan. This amendment (No. 13) was issued on November 5, 1985. "It appears Technical Specification 5.3.d was not taken into account during the process of moving the control console to its current location in 1984. Currently the AGN 201M is not operating in accordance with Confirmatory Action Letter EA-2013-154, limiting the impact to the health and safety of facility personnel. "Prior to restoration of reactor operations, this issue will be addressed and an appropriate solution will be implemented. Solutions are being investigated to return the facility to compliance." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | TX | NPR | [5 empty] | 0 | 2015-01-22
50748 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2015-01-21 10:40 | 2015-01-21 18:32 | 2015-01-21 | UNPLANNED FIRE IN BUILDING 110 R&D LABORATORY VENTILATION HOOD "During calcining of a water-rinsed polypropylene cartridge filter, flames were observed at the top of the furnace door. The flames were contained in ventilation hood H-103. The flames lasted for 5-10 minutes, always limited to the top of the furnace door. The glass in the sash for hood H-103 broke, most likely from the heat of the flame. The glass is spider-webbed, but contained in the sash. The testing in the hood has been stopped and the hood and furnace have been tagged out of service. "There were no actual consequences due to this event. Potential consequences could have involved worker exposure and/or environmental releases." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(4) |  |  |  | 0 | 2015-01-22
50747 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-01-20 15:30 | 2015-01-21 13:05 | 2015-01-21 | AGREEMENT STATE REPORT - STUCK GAUGE SHUTTER The following information was received by email: "On January 21, 2015, the licensee notified the Agency [Texas Department of State Health Services] that on January 20, 2015, during the process of closing fixed nuclear gauge shutters at its facility in order to perform detector calibrations, it discovered that the shutter on one of its Ohmart-Vega SH-F2 gauges, containing a 500 millicurie cesium-137 source, would not close. The gauge normally operates with the shutter in the open position and the failure does not pose a risk of exposure to any person. The licensee is coordinating to have repairs made. Further information will be provided as it is obtained in accordance with SA-300." Texas Incident: I 9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-01-29
50746 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2015-01-14 | 2015-01-20 15:44 | 2015-02-09 | AGREEMENT STATE REPORT - LOST GENERALLY LICENSED TRITIUM EXIT SIGNS The following information was received by email: "Event Description: A specific licensee reported the loss (potential theft) of two generally licensed tritium (H-3) exit signs. The signs had been removed from installation and are missing from the storage location. The licensee became aware of the missing material on 1/14/2015, however, it is possible the material was missing for approximately one month. The devices were last seen by licensee staff in mid-December 2014. Specific details about the device model and activity have not yet been provided, potentially up to 15 Ci H-3 per device. An NJDEP [New Jersey Department of Environmental Protection] inspector will visit the site to investigate the incident." New Jersey Event: #C545467 * * * UPDATE FROM JAMES MCCULLOUGH TO JEFF HERRERA ON 2/9/15 AT 1638 EST * * * The following update was received from the New Jersey Department of Environmental Protection via email: "The College of New Jersey (TCNJ) reported the loss or possible theft of two radioluminescent exit signs. The signs had been removed from installation and were placed into storage. The signs were discovered to be missing from the storage location on 1/14/2015. However, TCNJ stated that it was possible the signs had been missing for approximately one month. The signs were last seen by TCNJ in mid-December 2014. Each sign contained approximately 137 GBq (3.7 Ci) of H-3. A New Jersey Department of Environmental Protection inspector visited the site on 1/21/2015 and determined the most likely scenario was accidental disposal. The licensee submitted a full report in accordance with N.J.A.C. 7:28-6.1 [10 CFR 20.2201]. The missing signs were not located. Although there was no evidence of contamination, the licensee estimated a dose of 8.5 mrem if the signs had been broken. "NJDEP tracked the event as Incident # C545467 and Investigation #: 507375-INV15001. "Corrective Actions: Commitment to increased security should they be in possession of other sources. [The College of New Jersey] reports no inventory of generally licensed devices. "Device Number: 1 Device/Equipment: RADIOLUMINESCENT EXIT SIGN Model Number: LE Manufacturer: SAFETY LIGHT CORP Serial Number: 201864 "Device Number: 2 Device/Equipment: RADIOLUMINESCENT EXIT SIGN Model Number: LE Manufacturer: SAFETY LIGHT CORP Serial Number: 201865" Notified R1DO(Powell), NMSS Events Notification and ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2015-01-28
50745 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-01-16 15:15 | 2015-01-20 15:19 | 2015-01-20 | AGREEMENT STATE REPORT - POTENTIAL RADIOGRAPHER EXCESSIVE EXPOSURE The following report was received from the State of Louisiana via email: "Event Date and Time: 01/16/2015, around [1515 CST] a radiography crew was working at the ExxonMobil Refinery on Scenic Highway, Baton Rouge, LA. The event was reported [about 1645 CST] on January 17, 2015, by a phone call from [an individual] who represented himself as the Corporate RSO. He stated he drove down on January 17, to evaluate and investigate this incident. He reported this incident appears to be a Human Error Potential Excessive Exposure. "Event Location: ExxonMobil Refinery 4999 Scenic Highway. Baton Rouge, LA 70805. A temporary jobsite for Acuren Inspection. "Event type: This is a potential excessive exposure involving a radiographer attempting to breakdown a radiography exposure setup. He attempted to disconnect the guide tube from the exposure device and the source was not locked in the shielded position. It was noticed that the locking device was red after the guide tube was handled to disconnect it from the exposure device. "Notifications: LA DEQ [Department of Environmental Quality], Assessment, Radiation by direct phone call to our after hours answering system. The notification came in around [1645 CST] on January 17, 2015. "Event Description: The radiography crew was making exposures on lower level equipment at the ExxonMobil Refinery. The crew was utilizing [about] 38 Ci of Ir-192. The crew attempted to breakdown/disconnect the equipment after the exposures. The guide tube would not disconnect. The 2nd hand of the crew manipulated the drive cable that returned the source into the shielded position. A quarter turn on the crank shielded the source. "The radiographer and his equipment were checked. His pocket dosimeter was off scale, but he claims his Alarm Rate Alarm meter did not alarm. A second check of the Alarm Rate Meter revealed the unit did alarm, but it was a weak alarm. "Estimated dose calculations were done for his whole body and extremities. His whole-body estimated dose was 3.3 Rads and his extremity dose was estimated at 206 Rads to his hands. These were calculated on a one minute exposure where a .5 minute is more realistic. The exposed radiographer was taken to Core Occupational Medicine for examination, x-rays and blood work. He is being monitored and examined every other day. At this time he has been asymptomatic for an excessive radiation exposure. The Licensee is conducting reenactments. "This incident is not considered closed by the Department [LA DEQ]. The investigation findings will be updated when they become available. "The equipment was all QSA equipment loaded with 38 Ci Ir-192. This appears to be an operator error exposure. "The source is secure from removal and unnecessary exposure. This event is not closed and additional investigation and evaluation will continue. The source is in a safe shielded position and no threat to workers or the general public. "Transport vehicle description : N/A This was at a temporary job site inside the ExxonMobil Refinery located in Baton Rouge, LA." License Numbers: LA-7072-L01, AI 126755 Louisiana Event Number: LA1500002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-01-28
50744 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2015-01-19 11:00 | 2015-01-19 14:24 | 2015-03-16 | MISSILE DOOR MISALIGNED RESULTS IN A REDUCTION IN ACCIDENT MITIGATION "The missile door (door 33012) protecting Class 1E Engineered Safety Features (ESF) buses NB01/NB02 switchgear rooms was discovered misaligned on its hinge and stuck partially open and not capable of being closed. The missile door has since been repaired and closed. Technical Specification (TS) 3.8.9, 'Distribution Systems- Operating,' was declared not met and Condition F entered when the immediate operability determination identified that buses NB01 and NB02 were inoperable. Condition F of TS 3.8.9 requires immediate entry into Limiting Condition for Operation (LCO) 3.0.3. LCO 3.0.3 was entered at 1100 CST and subsequently exited when the missile door was repaired at 1118 CST. The unit was in and still is in MODE 1 at 100% power. No actions were initiated to commence a unit shut down. The NRC resident inspector was contacted regarding this event. All systems functioned as expected." * * * RETRACTION FROM TRAVIS ROHLFING TO HOWIE CROUCH AT 1458 EDT ON 3/16/15 * * * "The licensee is retracting this event based on the following: "An engineering evaluation concluded that the weather conditions during the period of the event did not result in the threat of a tornado. Given that the weather during the event would not have presented a valid threat of a tornado, the stuck open missile door would not have prevented the ESF busses and the DGs [Diesel Generators] from performing their specified safety function. The ESF busses and the DGs were considered OPERABLE but degraded. This is analogous to Example 4 in RIS 2001-09, 'Control of Hazard Barriers', with the exception that this event did not occur as a result of planned maintenance or a plant modification. As such, this event has been determined to not be reportable per 10 CFR 50.72(b)(3)(v)(D)." The licensee has notified the NRC Resident Inspector. Notified R4DO (Gepford). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-01-19
50743 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2015-01-18 21:31 | 2015-01-19 02:30 | 2015-01-21 | LOSS OF NORMAL TECHNICAL SUPPORT CENTER POWER "At 2131 CST on January 18, the Duane Arnold Energy Center [DAEC] Technical Support Center (TSC) Normal Power was lost when a single phase to the T4 '36KV-12.5KV DAEC SITE TRANSFORMER' was lost due to a blown primary side fuse. Automatic power transfer occurred to maintain power to the TSC from the TSC Emergency Diesel Generator (EDG) which automatically started. The TSC remained functional throughout the incident. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii) due to the loss of an emergency assessment capability. An update will be provided once the normal power supply has been restored." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DOUG PETERSON TO VINCE KLCO AT 1419 EST AT 1/21/15 * * * Normal power restored to the TSC. The licensee notified the NRC Resident Inspector. Notified the R3DO (Duncan). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-19
50742 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2015-01-15 11:00 | 2015-01-16 18:17 | 2015-01-16 | AGREEMENT STATE REPORT - STUCK SOURCE IN RADIOGRAPHY CAMERA The following information was received via E-mail: "This event occurred at a permanent shooting cell at the licensee's facility in Amite LA. "The RSO was performing the semi-annual leak test on his radiography cameras. One is loaded for use in radiography and the other is essentially considered in storage. He removed the guide tube to swab the port entry and finished the paperwork for the leak test. Later he went to make an exposure and the source extended the length of the drive cable and would not retract into the shielded position. The source was stuck out into the vault shooting bay area. "The equipment was an Amersham Model 680-BE, s/n BE 178 loaded with approximately 50 Ci of Co-60, a QSA Global source s/n 45274B. The associated equipment was an Amertest Automatic Exposure Control, Model 957, s/n 67. "This was operator error. The RSO did not reattach the guide tube after performing a leak test at the camera's port. The source was being utilized in a fixed shooting cell/vault when it would not retract. "[In order to retrieve the source] the side panel was removed from the camera and a manual source retraction was performed. The source was shielded from unnecessary exposure, ALARA [as low as reasonably achievable], during the source retrieval. Again, this was operator error, not equipment failure. "The source is secure from removal and unnecessary exposure. This event is not closed and additional investigation and evaluation will continue. The source is in a safe shielded position and no threat to workers or the general public." Louisiana Event Report ID No.: LA150001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2015-01-26
50741 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2015-01-15 14:00 | 2015-01-16 15:48 | 2015-01-27 | AGREEMENT STATE REPORT - SMALL QUANTITIES OF UO2 AND U-235 FOUND IN THE PUBLIC DOMAIN The following information was received from the Arkansas Department of Health via email: "The University of Arkansas (U of A), Arkansas Radioactive Materials Licensee Number ARK-0064-01120, notified the Arkansas Department of Health, Radioactive Materials Program, via e-mail on Thursday, January 15, 2015 at 1400 hours, of the following labeled items found in the public domain (private home): (1) UO2 (3% U-235) in a small glass vial with lid and (2) U-235 in a medium size glass jar with lid. The isotopes and weights of these items will be identified and/or confirmed once in State possession. "The U of A's Radiation Safety Officer reported exposure readings of item (1), listed above, at '2 mR/hr' and stated item (2), listed above, 'did not produce any readable dose.' The Radiation Safety Officer also performed swipe tests and surveys for contamination. "The State requested the U of A to take immediate possession, properly store and secure the items. The State will retrieve these items promptly, which will be properly secured and stored at the State's authorized storage location. "It is unknown at this time if there has been any exposure(s) to the public. The State is awaiting a written report from the licensee and will continue to investigate this event. The State will update this event as more information becomes available." Arkansas Department of Health event number: ARK-2015-001 * * * UPDATE FROM DAVID B. STEPHENS TO JEFF HERRERA AT 01/27/2015 AT 1144 EST * * * The following was received from the State of Arkansas via email: "On January 20, 2015, Health Physicists retrieved two samples recovered from a private residence in Fayetteville, Arkansas and returned them to secure storage at the Arkansas Department of Health. Analysis of these samples are as follows: "ADH Inventory Item #38 [U-235 in jar] has a mass of 71.7 grams, in appearance resembling a piece of ore. Contact readings on the container with a survey meter gave readings at background. Gamma spectrum analysis indicated U-235 activity at 18.3 pCi/gram. "ADH Inventory Item #37 [UO2 in vial] has a mass of 12.6 grams, in appearance a cylindrical black item approximately 1 centimeter in length and 1 centimeter in diameter. Contact readings on the container with a survey meter gave beta readings of 3 mR/hr. and gamma readings of 0.15 mR/hr. Gamma spectrum analysis indicated U-235 activity at 4.05 E+3 pCi/gram. "Analysis of all swipes taken in the location where the items were found and of the containers themselves show no evidence of contamination. From interviews conducted with involved parties it appears that there was no radiation exposure to members of the public. "The Arkansas Department of Health considers this event closed." Notified the R4DO (Campbell) and NMSS Events Notification (Email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2015-01-26
50740 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2015-01-15 17:04 | 2015-01-15 19:12 | 2015-01-15 | INADEQUATELY SEALED PIPING PENETRATIONS AND POSTULATED FLOODING EVENT "On November 19, 2014, inadequately sealed piping penetrations were discovered in the Residual Heat Removal (RHR) piping and valve gallery walls that could have allowed a postulated flooding event to potentially impact both RHR pumps. The same configuration was identified on both Units. Following analysis of the postulated flooding leakage sources and flow paths, it was discovered that there was a time when an unacceptable volume of flood water could have entered the pipe and valve gallery areas. This condition was found to have been previously corrected on 12/16/14, following changes to Operations flood mitigation strategies and installation of seals in upstream pipeway trenches. Therefore, this issue is reported as an unanalyzed past condition that had the potential to adversely impact the RHR pumps. "This condition was determined to be reportable per 50.72(b)(3)(ii)(B) and 50.72(b)(3)(v)(B)." The licensee has informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2015-01-15
50739 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2015-01-15 15:45 | 2015-01-15 17:29 | 2015-01-15 | OFFSITE NOTIFICATION DUE TO HOSPITALIZED INJURED EMPLOYEE "This notification is being made in accordance with NUREG-1022, Event Report Guidelines 10 CFR 50.72 and 50.73 Section 3.2.12, News Release or Notification of Other Government Agency. "On January 15, 2015 at 0720 CST, with Arkansas Nuclear One, Unit 2 (ANO-2) at 100% power, an on-site injury occurred at ANO-2. "An individual fell while descending stairs and was injured. Pope County EMS transported the individual to a local medical facility. No contaminated individuals were transported off-site. No individuals were contaminated during the event. The individual was admitted to the local hospital. "29 CFR 1904.39(a) requires a report to the Occupational Safety and Health Administration (OSHA), US Department of Labor with twenty-four (24) hours after the in-patient hospitalization of one or more employees as a result of a work-related incident. At 1545 CST, ANO determined that this is a 24-hour OSHA reportable occurrence." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-01-15
50738 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2015-01-07 | 2015-01-15 15:36 | 2015-01-15 | AGREEMENT STATE REPORT - DOSE ADMINISTERED EXCEEDED 50 REM The following information was provided by the State of California Department of Public Health - Radiological Health Branch (RHB) via email: "On 01/14/15, RHB received an email from the RSO reporting a Medical Event. On 1/7/15 a patient was scheduled for a thyroid uptake scan. Instead of the prescribed dose of 300 microcuries of Sodium Iodide 123, 3.69 mCi [3690 microcuries] of the isotope was administered to the patient. Due to quality of the scan, the error was noted. An initial calculation performed on 1/8/15 indicated target organ [dose] exceeding 50 rem. On 1/9/14, another calculation performed by the consulting physicist using patient's actual measured uptake values, the target organ [dose] was deemed less than 50 rem and it was decided to be non-reportable. On 1/13/15, the chief of Nuclear Medicine reviewed the reference source and contacted the same physicist to review his calculations, and the physicist realized that he made an error in calculations, and informed the facility that the organ dose exceeded 50 rem. On 1/14/15, the Kaiser Medical Physicist confirmed the [dose] to be 53.6 rem to the thyroid, and the RSO notified RHB of the Medical Event. RHB will be following up on this matter." CA Event Report Number: 011415 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-01-23
50737 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2015-01-15 08:08 | 2015-01-15 12:28 | 2015-01-15 | A&B SWITCHGEAR ROOM BOUNDARY DOOR LATCH DISCOVERED NOT FUNCTIONING PROPERLY "On January 15, 2015 a high energy line break door affecting both trains of safety related switchgear rooms was discovered not latching after passage. The boundary was not operable for approximately 19 minutes. The door has been repaired. "Dominion is reporting that this condition could have prevented the fulfillment of the safety function to mitigate the consequences of an accident pursuant to 10 CFR 50.72(b)(3)(v)(D). "The NRC Senior Resident Inspector has been notified." The State of Connecticut Department of Energy, and Environmental Protection and Waterford Dispatch were also notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-01-15
50736 | 0 | SAINT VINCENTS MEDICAL CENTER |  |  |  |  | 2015-01-14 13:30 | 2015-01-15 12:00 | 2015-01-15 | MEDICAL EVENT INVOLVING A Y-90 SIR-SPHERE UNDER DOSE Notification of a medical event that occurred on January 14, 2015 at 1330 EST, in which the Y-90 SIR-Sphere dose delivered to the patient's liver was less than the prescribed dose. The intended dose to the patient was 22 mCi, however the catheter disconnected during administration, resulting in a spill on the table which caused the underdose to the patient. It is estimated the patient received only 11.5 mCi or approximately 52% of intended dose and there was no harm to the patient. The patient and prescribing physician have been informed and a follow-up treatment is planned. There was no contamination or exposure to other personal. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2015-01-23
50735 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2015-01-14 13:47 | 2015-01-14 16:15 | 2015-01-14 | AGREEMENT STATE REPORT - TWO CATEGORY 2 IRIDIUM SOURCES UNACCOUNTED FOR DURING SHIPMENT The following information was provided by the Commonwealth of Massachusetts via email. QSA Global (Shipper) initially provided notification to the Commonwealth of Massachusetts of the following: "On Tuesday, January 13, 2015, QSA was notified by the customer a routine shipment of two Ir-192 sources from QSA Global, Inc. to Huntington Testing and Technology did not arrive as expected. They (HT&T) contacted the carrier and were told that the shipment could not be located. A trace was initiated. This trace is still actively being pursued by [the carrier's representative] and as of the writing of this email, the shipment is suspected of being at a US Postal Service facility in Charleston, SC." QSA Global subsequently provided notification to the Commonwealth of Massachusetts of the following: "Please be advised that QSA has received notification by [the carrier's representative] that the shipment to Huntington Test and Technologies reported missing has been located and physically verified in Memphis, TN at the [shipper's] hub. Additional information will be forthcoming in a followup 30 day report. " The two Iridium-192 sources are 102.8 Ci (SN: 14381G) and 102.7 Ci (SN: 14382G), respectively shipped in an SC-650L Source Changer (SN: 202). The shipment has no indication of tampering and is currently enroute to HT&T. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2015-01-22
50734 | 0 | CB&I NUCLEAR |  |  |  |  | 2015-01-13 | 2015-01-14 14:10 | 2015-01-14 | 10 CFR PART 21 REPORT REGARDING DEVIATIONS OF COATINGS FOR PIPE SUPPORTS FOR AP1000 PROJECTS The following report was received via email: "This report is being provided in accordance with 10 CFR 21.21. "(i) Name and address of the individual or individuals informing the Commission. "Michael Hickey CB&I Nuclear 128 S. Tryon St., Suite 1000 Charlotte, NC 28202 "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. "The basic components being supplied are pipe supports to be used inside the containment for the V. C. Summer and Vogtle AP1000 nuclear projects. The pipe supports are classified as ASME B31.1 Code and Quality Assurance (QA) Categories II and III. These supports are associated with various non-safety-related portions of several systems inside containment, including Component Cooling, Passive Core Cooling, Spent Fuel Pool Cooling, Waste Liquid, and others. The material being procured was not basic component materials and 10 CFR Part 21 was not applicable. The basic component aspect became inadvertently introduced based on the decision to use a coating that was based on inorganic zinc (IOZ) in lieu of the appropriate coating, which is a Self-Priming High Solids Epoxy (SPHSE). Use of the IOZ coating required the application to be performed as a safety-related application. Due to misinterpretation of the design specification requirements, the wrong safety-class was invoked and the wrong coating material was selected. The piping supports are not impacted by this use of the IOZ coating and would have not been impacted for meeting the pipe support design function. The use of the incorrect coatings, with the incorrect safety classification, could have impacted the ability of the required systems to perform the long-term cooling function, which is considered a safety-related functional impact. The approximate number of supports that are impacted for each unit is provided as follows: 952 Vogtle Unit 3, 275 Vogtle Unit 4, 967 V. C. Summer Unit 2, and 625 V. C. Summer Unit 3. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. "The affected piping supports are being supplied by LISEGA Inc. USA, 370 East Dumplin Valley Rd., Kodak, TN 37764. Note that LISEGA supplied the pipe supports with coating material as specified in the procurement documents. Subsequent review has determined that the procurement documents specified incorrect information for many of the supports, which should have been coated with a different material. The procurement documentation was provided to the supplier by CB&I Power, 128 South Tryon Street Charlotte, NC 28202. "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "The use of the incorrect coating inside containment impacts debris generation and long-term cooling analyses performed for the AP1000 design. It is estimated that the amount of unqualified IOZ coating that could have been added to the containment would have eventually caused impairment of the long-term cooling function during events that require that capability. Therefore, if left uncorrected this condition could have caused a substantial safety hazard for the V. C. Summer and Vogtle AP1000 nuclear projects. "(v) The date on which the information of such defect or failure to comply was obtained. "The discovery date of these deviations is based on the date of the associated CB&I Power Corrective Action Report (CAR). That CAR was initiated on March 10, 2014. Interim Part 21 reports dated October 15, 2014, and December 11, 2014, were submitted to the NRC. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. "The impacted materials are pipe supports with incorrect coatings intended to be used inside containment for the V. C. Summer and Vogtle AP1000 nuclear projects. The approximate number of supports that are impacted for each unit is provided as follows: 952 Vogtle Unit 3, 275 Vogtle Unit 4, 967 V. C. Summer Unit 2, and 625 V. C. Summer Unit 3. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "The nonconforming pipe supports were initially placed into a hold status and are being corrected. A corrective action report (CAR 2014-2574) has been entered in the CB&I Power Corrective Action Program that describes the circumstances that led to the identification of this potential substantial safety hazard. That CAR is identified as a Level 1, significant condition adverse to quality, and a root cause analysis of the condition is required by CB&I Power Corrective Action Program. The actions necessary to correct the identified conditions and the causes for these conditions will be established and tracked to completion under the CB&I Power Corrective Action Program. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "The condition was discovered by CB&I Power prior to installation of the affected components and the components are being corrected. Therefore, there is no additional action or advice needed for the licensees at this time. The condition has also been evaluated by CB&I Power for potential 10 CFR 50.55(e) reporting by the affected combined operating license holders. CB&I Power has recommended to the licensees that this condition is reportable under 10 CFR 50.55(e). "(ix) In the case of an early site permit, the entities to whom an early site permit was transferred. "Not applicable. "This condition was previously identified by interim report letters dated October 15, 2014 [ML14296A427 - Log No. 2014-76-00], and December 11, 2014. "If you have any questions pertaining to this information, please contact Curtis Castell, Licensing Manager, at 980-321-8314." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-01-14
50733 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2015-01-13 19:04 | 2015-01-13 22:10 | 2015-01-13 | UNIT 2 MANUAL REACTOR SCRAM DUE TO REACTOR WATER LEVEL TRANSIENT "At 1904 Central Time 13 Jan 2015, Dresden Unit 2 was manually scrammed by Operators due to a Reactor Water Level transient. "All rods inserted to their full-in positions. "All systems operated as expected. "Reactor vessel inventory and pressure are being maintained in normal control bands. "The source of the transient was a failure of both controllers in the Feedwater Level Control system. Cause of the failure is under investigation. "This condition is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical." There was no on-going work or testing during this time which could have caused failure of the level controllers. Unit 2 is in a normal post scram electrical line-up and maintaining normal pressure and temperature. RHR cooling is available if required. Unit 3 was unaffected by this transient. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2015-01-13
50732 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2015-01-12 19:39 | 2015-01-12 23:17 | 2015-01-12 | DEGRADED SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "At 1939 [EST] on January 12, 2015, Nine Mile Point Unit 2 entered Tech Spec 3.6.4.1 when secondary containment was declared inoperable due to secondary containment differential pressure being above the Tech Spec Surveillance Requirement of -0.25 inches vacuum water gauge. This condition is related to sustained high winds. At 1956 on January 12, 2015 the differential pressure was restored, the secondary containment was declared operable and the Tech Spec 3.6.4.1 exited. "Secondary containment being inoperable is a 8-hour report for 10 CFR 50.72(b)(3)(v)(c), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident'. "The NRC Resident Inspector has been notified." The licensee notified the New York Public Service Commission. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2015-01-12
50731 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2015-01-12 11:00 | 2015-01-12 13:37 | 2015-01-12 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK OPEN The following information was received from the State of Texas via email: "On January 12, 2015, the licensee notified the Agency [Texas Department of State Health Services] that during routine fixed nuclear gauge inspections and shutter checks, it discovered that the shutter on one of its Ronan Model SA1-C5 gauges, containing a 300 millicurie cesium-137 source (SN: 6409GK), was stuck in the open position. [The event occurred at the licensee site located in Evadale, Texas.] This gauge normally operates with the shutter in the open position. The gauge is mounted on a vessel that the licensee does not enter. There is no risk of exposure to any individual. The licensee is contacting the manufacturer to schedule repair. Further information will be provided as it is obtained in accordance with SA-300. Texas Incident: I-9266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-01-20
50730 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2015-01-12 05:00 | 2015-01-12 09:03 | 2015-01-12 | PLANNED MAINTENANCE ON RADIOLOGICAL MONITOR "At 0500 [CST] today (January 12, 2015), planned maintenance activities commenced on the Reactor Building Separate Particulate Iodine and Noble Gas (SPING) monitor. Work on the SPING affects classification and assessment of the Emergency Plan for a radiological release through the Reactor Building Vents. In the case of a radiological event, the Reactor Building Ventilation will be isolated via Area Radiation Monitors (ARM) in the ducting and the Main Chimney SPING will be used for classification and assessment. This would be the normal response for a radiological event. "This maintenance activity is expected to be longer than 72 hours. The Reactor Building SPING is scheduled to be restored on Friday, January 16. "This event is reportable per 10CFR50.72(b)(3)(xiii) since the maintenance activity affects classification and assessment. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-12
50729 | 0 | ELKHART GENERAL HOSPITAL |  |  |  |  | 2015-01-08 10:00 | 2015-01-09 14:18 | 2015-01-09 | PATIENT RECEIVED WRONG FORMULATION OF TECHNETIUM RADIOPHARMACEUTICAL A patient who was to be given a myocardial stress profusion exam was incorrectly given a 160 mCi dose of technetium pertechnetate [instead of prescribed Tc-99m sestamibi]. The cause of the incident was the medical technologist deviated from established procedures. There is no expected adverse impact on the patient as a result. The patient and physician have been informed. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2015-01-19
50728 | 0 | NOVELIS |  |  |  |  | 2015-01-09 | 2015-01-09 14:14 | 2015-01-09 | GAUGE SHUTTER OPERATED SLOWLY IN THE CLOSE DIRECTION On December 18-19, 2014, Operations personnel detected a local indicating light showing the gauge shutter in the open position. Control room indication and local area surveys indicated the gauge shutter was closed. During the annual Christmas maintenance shutdown, a gauge contractor was onsite and the licensee requested that the suspect gauge shutter be investigated. On January 3, 2015, the gauge technician changed sensors for shutter open/close indication noticed slow operation of the shutter in the close direction. The technician made adjustments to the gauge shutter so that it would slide freely. The technician also recommended routine lubrication to prevent this issue in the future. The gauge contains 300 mCi Sr-90 source. Gauge serial number 3737622, Source serial number S432-A. No adverse personnel exposures are expected as a result of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-01-19
50727 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2015-01-08 | 2015-01-09 13:40 | 2015-01-09 | AGREEMENT STATE REPORT - GAUGE FAILED TO FUNCTION AS REQUIRED The following information was provided by the Commonwealth of Pennsylvania via email: "During a daily routine maintenance inspection [at the Edgar Thomson Plant in Braddock, PA], the licensee observed that the Berthold moisture analyzer gauge was at an odd angle when compared to the chute that it was attached. A mounting bracket had broken causing the gauge to become dislodged. An area survey check was performed and determined no elevated radiation readings. The shutter was placed into the closed position and a service provider was notified. The gauge was then removed by the service provider and transported to their warehouse to determine the repair method. The licensee is also awaiting a response from the manufacturer. "Manufacturer: Berthold Technologies, Isotope: Am-241, Activity: 300 mCi "CAUSE OF THE EVENT: The bracket had broken allowing the device to shift. The device was still in place but not completely flush with the chute. "ACTIONS: The device was removed from the site without incident and transported to the service provider's warehouse for repair. The Department plans a follow-up inspection with the licensee. More information will be provided when received." PA Event Report ID NO: PA150001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2015-01-19
50726 | 0 | AZZ - NUCLEAR LOGISTICS INC. |  |  |  |  | 2015-01-08 | 2015-01-08 18:42 | 2015-01-08 | POTENTIAL FAILURE OF SBM TYPE SWITCHES The following is a summary of information that was provided by the reporting organization via facsimile: "Pursuant to 10 CFR 21.21 (b), AZZ - NLI [AZZ - Nuclear Logistics Inc.] has provided written notification to the affected licensees of the potential failure of GEH SBM type switches manufactured (by GEH) [General Electric - Hitachi] in the period from January 2012 to December 2014. "This condition has been reported in GEH document SC 14-19 (dated Dec. 11, 2014) in which GEH notified their affected licensees of the potential failure of SBM type switches, manufactured and shipped January 2012 through December 2014, due to incorrect installation of a conical spring. AZZ - NLI procured and dedicated commercial grade SBM type switches, manufactured during this time-frame, and subsequently provided to: Exelon - Peach Bottom; OPPD - Fort Calhoun; TVA- Watts Bar; KHNP [Korea Hydro & Nuclear Power]. "On the basis of our evaluation, it is determined that AZZ - NLI does not have sufficient information to determine if the subject condition would, or has, created a Substantial Safety Hazard or would have created a Technical Specification Safety Limit violation as it relates to the subject plant applications. "Therefore, purchasers are being advised to perform a visual inspection of the switches at the earliest opportunity to determine if the condition exists. "The following information is provided per 10 CFR 21.21(d) (4). Name and address of the individual or individuals informing the Commission: Tracy Bolt, Director of Quality Assurance, AZZ - Nuclear Logistics Inc., 7410 Pebble Drive, Ft. Worth, TX 76118" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2015-01-08
50725 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-01-08 16:26 | 2015-01-08 18:14 | 2015-01-08 | OFFSITE NOTIFICATION DUE TO LOW LEVEL TRITIUM SPILL "On January 7, 2015, at approximately 0700 CST, a leak to the environment was identified. Tritium was present at a concentration of 7.52E-3 uCi/mL, which is above the US Environmental Protection Agency (EPA) drinking water standard of 20,000 picocuries per liter. No other radioactive isotopes were identified. The leak rate was estimated at approximately 0.5 gpm and determined to be from the condensate head tank. Water was accumulating on the concrete-lined reactor/refuel air zone air intake plenum with some accumulation of water on the ground in the area. The intake plenum contains three floor drains. Actions were immediately taken to terminate the leak once the flowpath was identified. The flowpath was terminated two hours and 45 minutes after identification. Based on system review and analysis, any tritiated water that would have made it to the floor drains would then be mixed with incoming raw water at two million gallons per minute. This mixed volume of water would then be circulated through the plant and discharged to the river with a resultant tritium concentration that is much less than detectable levels and well below US EPA drinking water standards. The station has established increased monitoring of groundwater at designated sample wells. On January 8, 2015, at approximately 1645 CST in accordance with TVA procedures and the guidance of NEI 07-07 [Nuclear Energy Institute] for the Groundwater Protection Initiative, the licensee notified the Alabama Radiological Protection Department and Alabama Department of Environmental Management. The Limestone County Emergency Management Department will be notified." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-01-08
50724 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2014-11-12 | 2015-01-08 13:13 | 2015-01-08 | AGREEMENT STATE REPORT - LOST I-125 SEED IN STRAND LAB The following information was provided by the State of Georgia via facsimile: "Theragenics was packing radioactive seeds for transport to customer when one of the seeds was lost in the strand lab and could not be found. This was an Iodine 125 seed manufactured by Medi-Physics, model Oconoseed 6711. At the time of production the seed had a radioactivity of 0.696 mCi, but by the time of the report had decayed to 0.492 mCi radioactivity. "On November 12, 2014, licensee personnel were filling an order for stranded seeds when a seed could not be accounted for. After searching the lab area continually and personnel when they left the lab (portal monitor scanning), the seed still has not been found. The licensee made a report via phone notification of the missing seed on December 12, 2014. "License has conducted refresher training for employees who work in the lab areas. An emphasis was noted on handling technique, especially during mid-late October through November, when the change in weather and humidity have traditionally resulted in an increase of seed-handling errors, i.e., seeds 'popping' out of tweezers during manipulation. Additionally, the strand lab is scheduled for its semi-annual cleaning (per General Lab Practice) on December 19-20, 2014. During that process, crews will look for this seed and the one that was reported missing from September 2014." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2015-01-16
50723 | 0 | US ARMY |  |  |  |  | 2014-12-11 | 2015-01-08 11:34 | 2015-01-12 | UNINTENDED DOSE TO FETUS On December 11, 2014, a patient was receiving a thyroid ablation treatment containing 97 mCi of I-131. A pregnancy test performed prior to the treatment was negative. On December 29, 2014, the patient reported to the medical center that it had been determined that she was pregnant on the day of the treatment, and that the gestational age of the fetus was determined to be 4 weeks at the time of the thyroid ablation treatment. The US ARMY Fort Bragg Radiation Safety Officer was notified of this event on January 5, 2015 by the authorizing physician of the exposure to the fetus via email. The calculated dose to the uterus was 20.43 Rad. The expected impact to the fetus was determined to be either miscarriage or no effect. The medical center is performing a root cause analysis to determine any potential corrective actions. The licensee will ensure the patient has been notified of the potential medical consequences to the fetus of this treatment. * * * UPDATE AT 1510 EST ON 01/12/15 FROM KACEY McGEE TO S. SANDIN * * * The patient was informed by the medical staff on 12/31/14. The root cause investigation is on-going. Notified R1DO (Burritt) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 35.3047(a) |  |  |  | 0 | 2015-01-16
50722 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2015-01-08 07:00 | 2015-01-08 10:09 | 2015-01-08 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF BOTH CHANNELS OF REFUELING WATER STORAGE TANK INSTRUMENTATION "At 0400 [EST], Indian Point Unit 3 entered LCO 3.5.4 Condition C due to both Refueling Water Storage Tank (RWST) Low Low Level Alarm channels failing. The failure was a result of freezing in the instrument lines. LCO 3.5.4 Condition C requires at least one channel of RWST Low Low Level Alarm be restored to Operable within 1 hour. At 0500, Unit 3 entered Condition D due to the required action and completion time of Condition C not being met. This requires the unit be placed in Mode 3 in 6 hours and Mode 4 in 12 hours. This failure also has resulted in a loss of safety function. Operators rely upon the RWST Low Low Level Alarms during an accident to alert them of the need to transfer injection from the RWST as a source of water to the containment sump. At 0700, Indian Point Unit 3 commenced a shutdown to be in compliance with the requirements of LCO 3.5.4 Condition D. Investigation and repair efforts were immediately put in place to correct the failure and return the function to operable. At 1000, one Channel of RWST Low Low Level Alarm was returned to operable. LCO 3.5.4 Conditions C & D were exited. The shutdown was stopped and safety function was restored. Unit 3 remains in a 7-day shutdown [LCO action statement] for one RWST Low Low Level Alarm Channel inoperable as per LCO 3.5.4 Condition B. "Unit 2 is unaffected and remains at 100% power." The State of New York and the NRC Resident Inspector were notified. | 0 | 45 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2015-01-08
50721 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2015-01-07 | 2015-01-07 16:21 | 2015-01-07 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received via email: "This morning, the Columbus, GA Police Department was dispatched to the Building and Earth Sciences business located at 5045 Millgen Court in Columbus. It was reported that unknown person(s) had stolen a Model 3440 Nuclear Density Gauge Serial Number 22740. The gauge had been locked and secured in the back of a truck in the facility and the individual(s) had taken bolt cutters and cut the chains securing the device. No further information is available at this time." The stolen gauge contains approximately 8 mCi of Cesium-137 and 40 mCi of Americium-241. A regional law enforcement bulletin was issued and the Columbus, GA and Atlanta, GA FBI field offices were notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2015-01-15
50720 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-11-15 23:55 | 2015-01-07 12:27 | 2015-01-07 | INVALID ACTUATION OF 1A EMERGENCY DIESEL GENERATOR (EDG) "This 60-day telephone notification is being made under the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of the 1A EDG. The 1A EDG start resulted from a degraded component during the testing of the 1A Emergency Load Sequencer. "At 2355 [EST] on November 15, 2014, the 1A EDG auto started during performance of the monthly 1A Emergency Load Sequencer test. The test was terminated by personnel prior to a full actuation of the Emergency Load Sequencer due to the unexpected response of the sequencer. The 1A EDG started and functioned normally. Troubleshooting identified a degraded relay downstream of the under voltage sensing circuit which made up the invalid 2/3 logic necessary to start the EDG. There were NO actual plant conditions or parameters (i.e. under voltage, degraded voltage, safety injection or manual initiation) involved in this actuation. The degraded relay would NOT have prevented the 1A Emergency Load Sequencer or the EDG from performing their safety related functions. "Following troubleshooting, replacement of the relay and an evaluation for extent of condition, the 1A Emergency Load Sequencer and EDG were returned to service. "The health and safety of the public was not affected by this issue. "The NRC Resident Inspector has been notified." | 17 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2015-01-07
50719 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2015-01-06 12:27 | 2015-01-06 17:27 | 2015-01-06 | OFFSITE NOTIFICATION DUE TO OIL LEAK "On January 6, 2015 at approximately 1227 CST, a visible oil sheen was reported from a TVA owned boat that sank next to the dock on the Tennessee River near Cooling Tower 1. This oil spill is reportable to the EPA (National Response Center) under 40CFR112. Notification to the National Response Center will be made. "This oil sheen was determined to be more than minor to enter US waters. The source of the oil sheen has been contained using oil booms. "Additional notifications will be made to Alabama Emergency Management. "The licensee has notified the NRC Resident Inspector." The licensee notified the Environmental Protection Agency and the National Response Center. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-01-06
50718 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2015-01-06 16:30 | 2015-01-06 17:18 | 2015-01-06 | NOTIFICATION MADE TO OFFSITE GOVERNMENT AGENCY "In accordance with 29 CFR 1904.39(a)(2), notification was made to the Occupational Safety and Health Administration regarding the in-patient hospitalization of an individual while in the owner controlled area. "The licensee has notified the NRC Resident Inspector." The licensee notified the State of Ohio and local authorities The individual employee is currently under medical treatment and is not contaminated. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-01-06
50717 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-01-06 00:01 | 2015-01-06 15:31 | 2015-01-15 | FITNESS FOR DUTY - ALCOHOL FOUND IN PROTECTED AREA On January 6, 2015, at approximately 0001 EST, a partially empty can of beer was found by a security officer. Site Security took possession of the can and it was removed from the protected area. An investigation has been initiated by Site Security. This condition has been documented in TVA's corrective action program. This report is submitted pursuant to 10 CFR 26.719 (b)(1) based on the presence of alcohol within the protected area. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ZACHARY KITTS TO JEFFREY HERRERA AT 1503 EST ON 1/15/15 * * * Additional information provided by the Licensee of the origination of the beer can. The licensee notified the NRC Resident Inspector. Notified the R2DO (Musser). | 100 | 86 | 0 | 100 | 86 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2015-01-06
50716 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-01-05 17:45 | 2015-01-05 20:49 | 2015-01-05 | OFFSITE NOTIFICATION DUE TO DEATH OF EMPLOYEE "At approximately 1545 CST on 1/5/15, an employee was found unconscious by fellow teammates. His teammates, who are certified in cardiopulmonary resuscitation (CPR), commenced resuscitation until Matagorda County EMS arrived on the scene and transported the individual to Matagorda County Regional Hospital for medical treatment. The individual was evaluated by the Emergency Room Physician and was later pronounced deceased due to Cardiopulmonary Arrest. "STP is investigating the incident. STP has reported this to the Occupational Safety and Health Administration (OSHA) and as such is reporting this in accordance with 10 CFR 50.72 (b)(2)(xi). A press release is not planned at this time." The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2015-01-05
50715 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-01-03 05:38 | 2015-01-03 14:14 | 2015-01-03 | LOSS OF METEOROLOGICAL EMERGENCY ASSESSMENT CAPABILITY "At 0538 [CST] on 01/03/2015, a partial loss of the 25KV Power Distribution System caused a loss of both the Primary and Backup Meteorological Towers at the Comanche Peak Nuclear Power Plant. This resulted in a major loss of emergency assessment capabilities in regard to meteorological conditions. "The 25KV Plant Support Power Loop feeds certain non-safety-related support equipment and did not result in an impact to plant/unit operation. "Meter and Relay technicians are performing ongoing investigation of the cause of the breaker trip. "A similar incident occurred 01/02/2015 at 0314 [CST]. Reference [NRC] EN# 50713." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-03
50714 | -1 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2015-01-02 09:25 | 2015-01-02 16:45 | 2015-03-11 | HIGH HEAD SAFETY INJECTION INOPERABLE DUE TO VOIDS IDENTIFIED IN PIPING "At 0925 [EST] on 1/2/2015, Engineering personnel identified a gas void in each of two Unit 4 cold leg High Head Safety Injection (HHSI) discharge lines which exceeded procedural gas accumulation acceptance criteria. This condition rendered the cold leg HHSI flow path inoperable and required entry into Technical Specification 3.0.3. The voids were vented and Technical Specification (TS) 3.0.3 was exited at 1032. "The testing for gas voids conducted on 1/2/2015 was a follow-up to a gas void found in one Unit 4 HHSI line on 12/26/2014. On 12/26/14, TS 3.0.3 was entered at 1020 and exited at 1048 after the gas void was vented. After further review, the 12/26/2014 event was also reportable in accordance with 10 CFR 50.72(b)(3)(v)(D). "Engineering evaluation will be performed for both events to determine the specific impact of the gas voids on HHSI system function. Cause evaluation is being conducted to determine the source of the gas and any needed corrective actions." Unit 3 was verified to not have this voiding issue. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM SEAN BLOOM TO VINCE KLCO AT 1120 EDT ON 3/11/15 * * * "On 1/2/2015 at 1645 [EST], Event Notification 50714 reported to the NRCOC [Nuclear Regulatory Commission Operations Center] gas voids detected on 12/26/2014 and 1/2/2015 in Unit 4 cold leg High Head Safety Injection (HHSI) piping which exceeded procedural gas accumulation acceptance criteria. "Subsequent analysis has determined that if a HHSI pump started with the measured gas voids present, the resulting system conditions would not have impacted the integrity of the Unit 4 HHSI discharge flow path to the reactor coolant system (RCS) and therefore its safety related function would not be impaired. "The Unit 4 HHSI system discharge flow path to the RCS had been operable with the voids present, Technical Specification (TS) requirements were met, and entry into TS 3.0.3 was not required. The HHSI system remained capable of fulfilling the safety function to mitigate the consequences of an accident on Unit 4. Therefore, the immediate notification to the NRCOC on 1/2/2015 at 1645 in accordance with 10 CFR 50.72(b)(3)(v)(D) is hereby retracted." The NRC Resident Inspector has been informed. Notified R2DO (Shaeffer). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-01-02
50713 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2015-01-02 03:14 | 2015-01-02 11:43 | 2015-01-02 | LOSS OF METEOROLOGICAL EMERGENCY ASSESSMENT CAPABILITY "At 0314 [CST] on 01/02/2015, a partial loss of the 25KV Power Distribution Systems caused a loss of both the Primary and Backup Meteorological Towers at the Comanche Peak Nuclear Power Plant. This resulted in a major loss of emergency assessment capabilities in regard to meteorological conditions. "The 25 KV Plant Support Power Loop feeds certain non-safety-related equipment and does not affect plant operation. "An investigation by Meter and Relay Technicians revealed no abnormal conditions/damaged equipment. The supply breaker was re-closed at 0915 on 01/02/2015. Power was restored to both Meteorological Towers and proper operation was verified." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2015-01-02
50712 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2015-01-01 19:25 | 2015-01-01 22:02 | 2015-01-08 | MAIN CONTROL ROOM BOUNDARY DOOR DID NOT PROPERLY LATCH "During [surveillance] checks of Control Room doors, a boundary door did not latch after being accessed until the door was opened and closed. This is being reported as it could have prevented the fulfillment of a safety function to mitigate the consequences of an accident per 10CFR50.72(b)(3)(v)(D). The door is currently closed and latched. The door was in this condition for between 5 and 10 seconds." The licensee notified the Connecticut Department of Environmental Protection, Town of Waterford and the NRC Resident Inspector. * * * RETRACTION PROVIDED BY THOMAS CLEARY TO JEFF ROTTON ON 01/08/2015 AT 1539 EST * * * "Upon further review, Millstone Power Station Unit 2 has concluded that there was no loss of safety function, because even with the control room door latch degraded, the control room door and its closing mechanism would still be able to maintain the control room envelope's boundary intact. Therefore, this condition is not reportable and NRC Event Number 50712 is being retracted. "The basis for this conclusion will be provided to the NRC Resident Inspector." The licensee notified the NRC Resident Inspector. Notified R1DO (Jackson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2015-01-01
50711 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2014-12-31 11:05 | 2014-12-31 20:44 | 2014-12-31 | THROUGH WALL SEEPAGE AFFECTING RHR SYSTEM "At 1105 PST, plant personnel identified through-wall seepage in a Diablo Canyon Power Plant Unit 1 socket weld inside containment that provides a flow path to a relief valve protecting a common portion of both trains of the Residual Heat Removal (RHR) System. The as-found condition falls under the requirements of the ASME acceptance criteria. Unit 1 was already in Mode 3, or offline, due to a planned maintenance outage. PG&E accordingly declared both Unit 1 trains of RHR inoperable and has initiated a transition from Mode 3 to Mode 4 in accordance with requirements of Technical Specification 3.0.3. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2014-12-31
50710 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2014-12-25 | 2014-12-30 16:04 | 2014-12-30 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the State of California via email: "A CPN Portable gauge containing 10 mCi of Cesium 137 and 50 mCi of Americium 241 was stolen from the technician's residence [Campbell, CA] on December 25, 2014. According to the RSO [Radiation Safety Officer], a police report was filed on December 25th and RHB [California Radiologic Health Branch] was notified on December 26, 2014. "RHB North was notified of this theft on December 30, 2014 at 1300 PST. The RSO was requested to provide a reward in the local paper and on Craigslist and to provide RHB North a copy of the Police Report and description of the circumstances as soon as possible, as the RSO was not in the office and did not have access to the pertinent information. "Additional information will be forwarded when it is received" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2015-01-07
50709 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-12-29 18:00 | 2014-12-30 18:14 | 2014-12-31 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE: The following was received from the State of Texas via email: "On December 30, 2014, at 1630 [CST] the Agency [Texas Department of State Health Services] was notified by the licensee [TSI Labs, Inc.] that a Humboldt model 5001-c gauge containing a 40 millicurie source and a 10 millicurie source was stolen out of the back of a company pickup truck [in San Antonio, TX]. The licensee stated the technician had parked the truck at a movie theater and entered the theater to be with family. The licensee stated the gauge was unattended for one hour and forty five minutes. The licensee stated when the technician returned to the truck he found the chains securing the gauge to the truck were cut and the gauge and locks were missing. The licensee stated marks on the portion of the chain still in the truck showed it took several attempts to cut the chains. The technician notified a sheriff standing in the area of the theft. The technician searched for the gauge, but did not find it. The licensee will continue searching the area for the gauge. The licensee stated they are contemplating offering a reward for the gauges return. The licensee stated it believed the locks were still on the gauge hasps at the time of the theft, but the operating rod for the cesium source was probably not locked. The licensee stated the outside of the box was labeled with the radiation symbol. The licensee is continuing its investigation. Additional information will be provided as it is received in accordance with SA-300." The licensee reported the theft to local law enforcement. Texas Incident # I - 9264 * * * UPDATE PROVIDED BY ARTHUR TUCKER TO JEFF ROTTON AT 1028 EST ON 12/31/2014 * * * The following information was provided by the State of Texas via email: "The licensee reported that they are offering a $400.00 reward for the return of the gauge. The Federal Bureau of Investigation, Customs and Border Patrol, and the Texas Association of Pawnbroker's have been notified of the theft." Notified R4DO (Hay), NMSS Events Notification (email), and Mexico (fax). * * * UPDATE PROVIDED BY ARTHUR TUCKER TO VINCE KLCO AT 1925 EST ON 1//19/2015 * * * The following information was provided by the State of Texas via email: "On January 19, 2015, the Agency was notified by a regional inspector that they had been contacted by an individual who stated they had found the missing gauge. The inspector received the gauge from the individual and verified the gauge and source serial numbers matched the serial numbers reported by the licensee as being stolen. The inspector returned the gauge to the licensee that later same night. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Proulx), NMSS Events Notification (email), and Mexico (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2015-01-07
50708 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2014-12-30 08:16 | 2014-12-30 10:03 | 2014-12-30 | PLANNED TECHNICAL SUPPORT CENTER MAINTENANCE AFFECTING THE AIR HANDLING SYSTEM "Planned maintenance activities will commence today (December 30, 2014) on the Quad Cities Station TSC. The activity involves maintenance on the TSC Air Handling Unit (AHU). Work on the AHU affects the TSC habitability during a declared emergency requiring activation since the AHU supports habitability. The duration of maintenance is currently unknown, and is dependent on the conditions discovered during maintenance. Restoration from maintenance is expected to take longer than the required activation time of the TSC. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Station Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. This event is reportable per 10CFR50.72(b)(3)(xiii) since the maintenance activity affects an emergency response facility. "The NRC Resident Inspector has been notified." The licensee will be notifying the onsite Illinois Emergency Management Agency representative. * * * UPDATE FROM CHAD BRITTON TO DANIEL MILLS AT 1527 EST ON 12/30/2014 * * * "At 1230 CST on December 30, 2014, the maintenance activity was completed and the TSC ventilation was restored. "The NRC Resident Inspector was notified." Notified R3DO (Cameron). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-12-30
50707 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2014-12-29 23:30 | 2014-12-30 03:51 | 2014-12-30 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE DUE TO LEAK ON DIVISION 3 DIESEL GENERATOR COOLING WATER PUMP "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Mitigate the Consequences of an Accident. During routine surveillance testing of the Unit 2 Division 3 Emergency Diesel Generator (LOS-DG-M3) a small pinhole leak was identified in the pump casing of the Division 3 Diesel Generator Cooling Water Pump. This condition has been evaluated and the Division 3 Diesel Generator Cooling Water Pump has been declared inoperable. The Division 3 Diesel Generator Cooling Water Pump is a support system for the Division 3 Emergency Diesel Generator and the High Pressure Core Spray System (HPCS). The required actions of Technical Specification (TS) 3.5.1 were entered on 12/29/14 at 2330 [CST] when the HPCS system was determined to be inoperable. This condition could have prevented the High Pressure Core Spray System (HPCS), a single train safety system, from performing its design function." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2014-12-30
50706 | 0 | HEMLOCK SEMICONDUCTOR |  |  |  |  | 2014-12-29 15:00 | 2014-12-29 17:33 | 2014-12-29 | FIXED GAUGE SHUTTER STICKING WHEN MOVED At approximately 1500 EST on December 29, 2014, an operator attempted to open the shutter on a fixed gauge Vega America source holder and determined that the shutter was sticking. The shutter was locked in the closed position and tagged out. The licensee performed a radiation survey and confirmed that the shutter was in the closed position. The licensee previously reported a stuck shutter on a nearby device (EN 50667). The licensee will contact the vendor to repair both devices. Fixed gauge: Vega America Source Holder Model SHF 2-B with Cs-137 800 millicurie source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2015-01-06
50705 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2014-12-28 20:23 | 2014-12-29 03:40 | 2014-12-29 | TWO INOPERABLE EMERGENCY DIESEL GENERATORS "While the 12 Emergency Diesel Generator (EDG) was inoperable for performance of the monthly surveillance, adjustments were inadvertently made to 11 EDG which made it inoperable. As a result, Technical Specification [TS] 3.8.1 Condition E, for both EDG's inoperable was entered. Monticello has subsequently restored 12 EDG to an operable status within the 2 hour TS LCO [Limiting Condition for Operation] completion timer requirement. The station remained in a safe condition during this discovery with 12 EDG available at all times. The plant continues to operate in a normal condition with no initiating events present. The health and safety of the public was not impacted as a result of this condition. "The NRC Resident Inspector has been notified." EDG 12 was restored to operable status at 2214 CST and EDG 11 will remain inoperable until a surveillance test is performed to start the EDG and restore the local governor control idle speed to the correct setting. The licensee will be notifying the Minnesota State Duty Officer. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2014-12-29
50704 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2014-12-25 08:37 | 2014-12-25 12:41 | 2014-12-25 | AUTOMATIC REACTOR SCRAM "At 0837 [CST] on 12/25/14, a loss of Reactor Protection System (RPS) 'B' occurred which resulted in a Division 2 RPS half SCRAM. This occurred concurrent with a Division 1 RPS half SCRAM which had been inserted for LCO 3.3.1.1 Action 'A' due to issues with the #2 turbine control valve RPS logic on 12/23/14. This resulted in a full RPS actuation and Reactor SCRAM. During the SCRAM, a reactor water Level '8' occurred which tripped the running reactor feed pump. Reactor water level peaked at 56 inches. This Level '8' is under investigation. Once reactor water level lowered below 51 inches the Level '8' signal was reset, and the team attempted to start the 'C' reactor feed water pump. "The 'C' reactor feed pump failed to start upon attempt. The 'A' reactor feed pump was then started successfully. The startup feed regulating valve failed to open in automatic or manual mode, resulting in an RPV Level '3' signal (lowering to 8.1 inches). The operators manually aligned the 'C' feed water regulating valve and restored reactor water level to normal band. The plant is stable in Mode 3 pending investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-12-25
50703 | 0 | BALDOR ELECTRIC CO. |  |  |  |  | 2014-10-29 | 2014-12-23 13:55 | 2014-12-23 | PART 21 NOTIFICATION - BALDOR AC MOTORS WITH POTENTIAL BEARING END CAP ALIGNMENT ISSUES The supplier, Baldor Electric Company, identified a potential fitment issue between the motor shaft journal, bearing cap and bracket that could allow the bearing cap to cock in the bracket. This misalignment would cause the motor to fail within hours of being placed in service. Therefore, all motors in service for greater than 24 hours would not be affected by the defect. The supplier has notified its vendor and provided corrective actions and/or parts replacement as appropriate. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-12-23
50702 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2014-10-26 03:40 | 2014-12-23 13:00 | 2014-12-23 | 60-DAY OPTIONAL TELEPHONE NOTIFICATION OF INVALID ACTUATION OF RESIDUAL HEAT REMOVAL PUMP "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of the Unit 1 11 RHR Pump while Unit 1 was at NO MODE. It was a complete actuation. This was not the result of a preplanned sequence during testing and the system was not removed from service. "At 0340 CDT on October 26, 2014, the Unit 1 11 RHR Pump was noted to have started while investigating an NSSS [nuclear steam supply system] annunciator system ground. The operator verified that the pump had adequate suction path via the RCS Cold Leg and stable pump discharge pressure. The 11 RHR Pump was stopped per the plant's abnormal operating procedure. "Evaluation of this event has shown that the auto-start of 11 RHR pump was due to a human performance error while performing relay replacements. "Following troubleshooting of the auto-start and completion of the relay maintenance, the 11 RHR pump was run; the pump and system operated properly. The health and safety of the public was not affected by this issue. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION | OTHER UNSPEC REQMNT |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2014-12-23
50701 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2014-12-23 03:00 | 2014-12-23 12:31 | 2015-01-27 | TEXAS AGREEMENT STATE REPORT - SOURCE DISCONNECTED ON A RADIOGRAPHY CAMERA The following information was obtained from the State of Texas via email: "On December 23, 2014, the licensee notified the Agency [Texas Department of State Health Services] that one of its radiography crews, who was performing radiographic operations at one of its licensed sites in Houston, Texas, had experienced a source disconnect. "After completing an exposure, the radiographers cranked the 79 curie cobalt-60 source back into the SPEC300 exposure device. However, as they started to walk toward the end of the guide tube, their survey meter and alarming rate meters indicated the source was still in the guide tube. They moved their boundaries back, secured the area, and called their supervisor. The licensee's radiation safety officer and two employees who are approved on the license for source retrieval responded to the site. They found that the source assembly (pigtail) cable had broken a couple of inches back from the source. The source was retrieved from the guide tube and placed back inside the exposure device. A survey confirmed the source was in the shielded position. The licensee is sending the exposure device and all associated equipment from this event to the manufacturer for evaluation. No member of the public received any exposure and there were no overexposures to any of the radiographers or source retrieval team. "An investigation into this event is ongoing. More information will be provided in accordance with SA-300 as it is obtained." Texas Incident No: I-9263 * * * UPDATE FROM ART TUCKER TO JOHN SHOEMAKER AT 1434 EST ON 1/27/15 * * * The following report was received from the State of Texas via email: "On January 27, 2015, the Agency received a copy of the manufacturer's inspection report for this device. The report stated the source pigtail had been repaired once before in January 2012. The repair involved placing a splice on the pigtail about 3.75 inches from the source to repair a section of severely frayed cable. The manufacturer's report states that this pigtail failure occurred immediately behind this connection. The report states that the connector did not fail, but the cable broke due to cable fray or abrasion. The report states the crimped sleeve on the connector created a section of the source assembly that cannot flex. This causes the cable adjacent to the connector to flex more than is typical in a normal (unrepaired) cable. This repeated local extreme flexures combined with a potential abrasion eventually resulted in the failure. The manufacturer's report also states the manufacturer inspected the inside of the camera's s-tube. This inspection found an area where the tube was slightly crushed causing a small flange area that could potentially cause the pigtail to become snagged or damaged. The report states the pigtail connector body and piston showed significant wear indicating the device was used extensively. The manufacturer stated all other spliced cobalt sources in service with a similar splice installed by them would be inspected. The manufacturer stated they believed there was only one additional camera in service with similar splice. The manufacturer's report states it is investigating a different design of splice used on the cable to prevent this problem in the future. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Campbell) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2014-12-31
50700 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2014-12-22 22:30 | 2014-12-23 00:57 | 2014-12-23 | UNIT 1 TECHNICAL SPECIFICATION SHUTDOWN DUE TO RCS PRESSURE BOUNDARY LEAKAGE "On December 22, 2014 at 2230 hours [EST] while performing a containment walkdown due to increased RCS [Reactor Coolant System] unidentified leakage, a leak was identified upstream of 1-RC-68, B Loop Cold Leg Drain Isolation Valve. The source of this leakage cannot be isolated and is considered RCS pressure boundary leakage. [Unit 1] Entered TS LCO 3.4.13 RCS Operational Leakage, Condition B for the existence of pressure boundary leakage. TS 3.4.4 RCS Loops - Modes 1 and 2 condition A, TR 3.4.6 ASME Code Class 1, 2, and 3 components, Condition B. Unit 1 will be taken to Mode 5 for repair. "This event is reportable in accordance with 10 CFR 50.72(b)(2) for "initiation of plant shutdown required by Technical Specifications" and 10 CFR 50.72(b )(3)(ii)(A) for "any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded." The RCS leakage has been quantified as 0.053 gallons per minute from a containment sump in-leakage calculation. The exact location of the leak has not been identified due to the installation of lagging on the RCS components. The licensee anticipates entering Mode 3 (Hot Standby) within the next 30 minutes. There is no safety-related equipment out-of-service at this time. The licensee will inform Louisa County and has informed the NRC Resident Inspector. | 12 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2014-12-23
50699 | 0 | DASSAULT AIRCRAFT SERVICE |  |  |  |  | 2014-12-03 | 2014-12-22 15:15 | 2014-12-22 | LOST STATIC ELIMINATOR "Dassault Falcon Jet Wilmington Corp. has lost a leased piece of equipment that contains radioactive materials. The tool in question is an air blow gun leased from NRD, LLC. The blow gun model number is P-2021-1000, Serial number A2JT781 and was on lease number 055641 shipped on 12/03/2013. The blow gun [contains] 1.7 mCi (61 MBq) [of Po-210]. "The tool was used to remove static from aircraft interior windows and also to remove static from interior wood paneling between decorative finish coats. It was used primarily in the cabinet department of the company for the purposes described above. The tool was believed to last be used in June of 2014. "Since discovering the tool was lost, every effort has been made to locate it by posting lost tool messages throughout the company and searching all tool storage locations and employee tool boxes. To prevent this from happening again, the company has placed tools like this into our inventory tool control program where employees will be required to sign out tools and return them after jobs are complete." The tool was in use at the company's New Castle, DE facility. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2014-12-30
50698 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2014-11-24 | 2014-12-22 13:05 | 2014-12-22 | KENTUCKY AGREEMENT STATE REPORT - FAILURE OF FIXED GAUGE ACTUATORS The following information was obtained from the Commonwealth of Kentucky via facsimile: "Failure of on/off mechanisms on three fixed gauges to function as designed. Failure discovered during routine testing of on/off mechanism by [the] licensee. The licensee has contacted the manufacturer to schedule removal/repair." The fixed gauges are in a normally inaccessible area and don't present a personnel exposure concern. The gauges contain Cs-137 with 100 mCi, 25 mCi, and 10 mCi respectively and are used at a coal fired facility. Kentucky Event Report ID: KY-14-0005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2014-12-30
50697 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-12-20 12:12 | 2014-12-20 13:39 | 2014-12-22 | OFFSITE NOTIFICATION DUE TO OIL LEAK FROM MAIN TURBINE LUBE OIL SYSTEM "At 1212 EST on December 20, 2014, D.C. Cook notified the State of Michigan and local authorities of an oil leak from the Unit 2 Main Turbine Lube Oil Cooler to Lake Michigan. Approximately 2000 gallons have leaked into Lake Michigan since October 25, 2014. No visible oil or oil sheen is present on Lake Michigan or the shore line. The leak is currently isolated as of 1030 EST on December 20, 2014. Leak repairs will be made to the cooler prior to placing back in service. "The NRC Resident Inspector was notified. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to notification of offsite agencies." Notified DOE, EPA, USDA, HHS, and FEMA. * * * UPDATE FROM PERRY GRAHAM TO HOWIE CROUCH AT 1432 EST ON 12/22/14 * * * The licensee issued a press release about this event this afternoon. Notified R3DO (Dickson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-12-20
50696 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-12-19 11:00 | 2014-12-19 14:57 | 2014-12-19 | FITNESS FOR DUTY REPORT - CONTRACT SUPERVISOR TESTED POSITIVE FOR ILLEGAL DRUGS A contract supervisory employee had a confirmed positive test for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 26.719 |  |  |  | 0 | 2014-12-19
50695 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2014-12-18 | 2014-12-19 12:19 | 2014-12-19 | AGREEMENT STATE REPORT - SHUTTER FAILURE The following was received via email from the Commonwealth of Pennsylvania: "Notifications: The [Pennsylvania] Department [Bureau of Radiation Protection] was notified on 12/18/2014 of a shutter malfunction. This event is reportable within 24-hours per 10 CFR 30.50(b)(2). "Event Description: An operator tried to open the shutter handle, and it was hard to move. When the shutter did move, it spun freely and was put in the open position but no activity was observed. However, when the shutter was placed in the closed position activity was seen, thus verifying a malfunction. "Manufacturer: Berthold Technologies Model: LB8010 Serial Number: 10204 Isotope: Cs-137 Activity: 20 mCi "Cause of the event: Unknown at this time, possible sheared roll pin. "Action: Berthold, the manufacturer, was called to fix the damaged shutter handle. The [Pennsylvania] Department [Bureau of Radiation Protection] plans to follow-up with the licensee and the manufacturer. More information will be provided when received. "Event Report ID No: PA140024" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2014-12-29
50694 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-12-17 15:55 | 2014-12-18 14:47 | 2014-12-18 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following report was received from the State of New Jersey via fax: "A source disconnect occurred during normal radiography operations. The exposure device was a SPEC 150 containing 29 Ci of lr-192. The operators immediately adjusted perimeter barriers and notified their RSO. A source retrieval team arrived in an hour and were able to successfully return the source to its shielded position within another hour. No overexposures were received. Direct reading dosimeters showed no exposure to the radiography team, and a dose of 33 mR and 5 mR were received by the source retrieval two-person team. The event was reported to be caused by operator error in failing to assure that the source tube was securely connected to the camera." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-12-26
50693 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2014-12-17 14:00 | 2014-12-18 12:45 | 2014-12-18 | AGREEMENT STATE REPORT - PATIENT RECEIVED MORE THAN PRESCRIBED DOSE A patient received 150 mCi instead of the 30 mCi of I-131 that was prescribed for thyroid ablation treatment. The cause of the overdose was the patient was misidentified. The patient and prescribing physician has been informed. No adverse health effects are expected. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2014-12-26
50692 | 0 | AIR FORCE MEDICAL SUPPORT AGENCY |  |  |  |  | 2014-12-16 18:00 | 2014-12-18 12:57 | 2014-12-18 | PRESCRIBED DOSE CHANGED BY UNAUTHORIZED USER "On 16 December 2014, at 1800 [PST], a patient was prescribed to receive 8-12 mCi of I-123 MIBG [metaiodobenzylguanidine]. The dose was delivered late to the Nuclear Medicine clinic and fell below the prescribed dosage range. The Nuclear Medicine OIC [Officer-in-Charge] changed the prescribed dosage from 8-12 mCi to 7-12 mCi, and the patient was subsequently dosed with 7.81 mCi. The procedure was successful and did not result in any medical/health impact or further need to repeat the study. [The Nuclear Medicine OIC] is currently not an authorized user (AU) on USAF Radioactive Material Permit No. CA-07840-03/07 AFP; therefore, he does not have the authority to adjust the prescribed dosage range. It is worth noting that [the Nuclear Medicine OIC] meets all the requirements to be an AU, and a request to add him was included with our pending permit renewal application provided to the Radioisotope Committee Secretariat (RICS) (USAF Licensee). "Location: Travis AFB, David Grant USAF Medical Center" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2014-12-26
50691 | 0 | ABB GROUP |  |  |  |  | 2014-12-17 | 2014-12-17 17:38 | 2016-11-17 | PART 21 REPORT - POTENTIAL DEFECT REGARDING KF RELAYS "Recent seismic testing results of the above Class 1E KF under-frequency relays uncovered inaccurate qualification by similarity to the tested relay 1328D72A03 (qualified in 2011). The subject relays do not meet the previously published ZPA rating, but meet a rating of 1.7g in accordance with IEEE C37.98-1987 requirements. "Records show a total of 37 suspect relays were provided to seven customers. ABB does not have the capability to perform the evaluation to determine if a defect exists, thus we are notifying the purchasers or affected licensees of this determination so that they may evaluate the deviation, pursuant to 10 CFR. 21.21(b). "If you have any questions regarding this notice, please contact the ABB Technical Support 954-752-6700. "Dennis Batovsky Managing Director" * * * UPDATE FROM DENNIS BATOVSKY TO HOWIE CROUCH VIA FAX ON 3/5/15 AT 1522 EST * * * "This letter is an update to the Part 21 Notification submitted on December 17, 2014, 'Potential defect regarding KF relay zero period acceleration (ZPA) rating'. "ABB reminds all licensees, that per ABB KF Under-frequency relays, Instruction Leaflet 41-503.21A effective April 1997, 'the normally closed contact at terminal number 2 should not be used for critical circuits due to a low fragility rating'. "ABB [has] conducted the following actions: -ABB has performed an initial extent of condition evaluation to determine if this situation exists in other electromechanical IE qualified relays. There are no additional findings at this time. -ABB issued a corrective action to improve existing engineering qualification procedures that govern qualification by similarity. "If you have any questions regarding this notice, please contact the ABB Technical Support 954-752-6700." Notified R1DO (Burritt), R2DO (Sykes), R3DO (Cameron), R4DO (Kellar) and Part 21 Group (via email). * * * UPDATE FROM DENNIS BATOVSKY TO DONALD NORWOOD AT 1621 EST ON 11/17/2016 VIA FAX * * * The following is a synopsis of the updated information received: The seismic testing results for 1328D72A01 and 1328D72A02 Class 1E KF Under-frequency relays met a ZPA rating of 1.72g. This was previously communicated as 1.7g. In lieu of previously communicated actions, future orders for 1328D72A01 and 1328D72A02 Class 1E KF Under-frequency relays will be only available at the published ZPA rating of 1.72g. Customers requiring higher ZPA will need to procure Class 1E KF style 1328D72A03 or 1328D72A04, as appropriate. Notified R1DO (Bickett), R2DO (Lopez), R3DO (Peterson), R4DO (Azua) and Part 21 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2014-12-17
50690 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2014-12-17 13:35 | 2014-12-17 15:07 | 2014-12-17 | OFFSITE NOTIFICATION DUE TO SEWAGE LEAK "This report is made due to notification from PPL Susquehanna to Pennsylvania Department of Environmental Protection (DEP) regarding a sewerage leak at the plant property. The notification was made at 1335 EST hours on 12/17/14. "During a routine inspection by a contractor who performs checks for PPL Susquehanna, an area was identified as a potential leak location. When the sewerage grinder pump was run, there was visible evidence in the soil that a leak existed. "Extent and duration of the leak is not know at this time. This event requires notification to Pennsylvania DEP." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2014-12-17
50689 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  |  | 2014-11-20 | 2014-12-17 14:28 | 2014-12-18 | LOST AM-241 SOURCE While conducting an inventory, the licensee was unable to locate a Standard Reference Material Electro-Plated AM-241, 0.079 uCi source that is used for calibration. It is believed the source may have been disposed as radioactive waste or transferred to another facilty. The licensee will continue searching for the missing source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2014-12-26
50688 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2014-12-17 10:14 | 2014-12-17 12:56 | 2014-12-17 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF LOAD "At 1014 [CST] on 12/17/2014, the reactor automatically tripped due to loss of load on RPS [Reactor Protection System]. Preliminary information indicates turbine-generator trip caused an uncomplicated reactor trip . All safety functions are met. Currently maintaining Mode 3, Hot Shutdown. At time of trip, non-safety related house transformers, T1A1 and T1A2 became inoperable as expected due to generator trip. Entered Technical Specification 2.7 (2)a, 72 hr LCO [for the inoperable T1A1 and T1A2 transformers]." All control rods fully inserted. All busses are energized via offsite power. Decay heat is being released via AFW and the condenser bypass valves. The unit is stable in Mode 3. Cause of the loss of load is being investigated. The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2014-12-17
50687 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2014-12-17 04:17 | 2014-12-17 12:10 | 2014-12-17 | MAIN PLANT VENT RADIATION MONITORING UNAVAILABLE "At 0417 EST on December 17, 2014, the Shift Manager was notified by Radiation Protection (RP) personnel that the Unit 2 AMP-200 radiation monitor used for backup monitoring of the Unit 2 Main Plant Vent when the Unit 2 Wide Range Noble Gas Monitor (WRNGM) is [Out of Service] OOS had experienced a malfunction that caused it to spike high for approximately five minutes before returning to a baseline value of 0 mR/hr. At the same time, the Unit 2 WRNGM was already out of service for the completion of a planned surveillance test. The Unit 2 WRNGM had been removed from service at 0740 EST on December 16, 2014. "While the WRNGM is OOS, the AMP-200 radiation monitor is procedurally relied upon for being used as the means for determining Alert, Site Area Emergency, and General Emergency entry criteria under the applicable Emergency Action Level (EAL) Initial Conditions (ICs). The Unit 2 Main Vent Gaseous Monitor is procedurally relied upon for being used as the means for determining Unusual Event entry criteria for the same EAL ICs and remained in service during this time. "After investigation by site RP and Maintenance personnel, the functionality of the Unit 2 AMP-200 was restored at 0700 EST on December 17, 2014 following a successful source check of the instrument. The investigation identified that the AMP-200 cable contacts were found wet and were subsequently cleaned and dried. Actions have been taken to prevent reoccurrence of the wetting condition. "During the time from 0417 to 0700 EST on December 17, 2014, Unit 2 had a condition that represented a loss of emergency assessment capability and is a reportable condition in accordance with 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified and the NRC the notification time with the NRC Headquarters was 1210 EST." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2014-12-17
50686 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2014-12-13 17:00 | 2014-12-16 17:31 | 2014-12-16 | DEGRADED REACTOR COOLANT PRESSURE BOUNDARY "On 12/13/14 at 1700 [EST] hours, during a planned Unit 1 maintenance outage the licensee identified leakage from a weld on the [.75 inch] lower seal vent piping connected to the 1B reactor recirculation pump lower seal area. The location is within the reactor recirculation loop isolation valves, therefore isolable from the reactor vessel. The piping is ASME Class 2 and is a reactor coolant pressure boundary. The reactor was in mode 3 at the time of discovery. Control Room notified at 1345 [EST] on 12/16/14, that requirements for 10CFR50.72(b)(3)(ii)(A) were not met. "This event is being reported as a degraded condition pursuant to 10CFR50.72(b)(3)(ii)(A)." The unit was taken to Mode 4 and the seal vent piping repair was completed. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2014-12-16
50685 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2014-12-16 13:00 | 2014-12-16 17:07 | 2014-12-16 | FITNESS FOR DUTY REPORT - DISCOVERY OF A PROHIBITED ITEM IN THE PROTECTED AREA The licensee discovered evidence of prohibited material inside the protected area. The material has been removed. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2014-12-16
50684 | -1 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-12-16 13:40 | 2014-12-16 16:16 | 2015-04-27 | AGREEMENT STATE REPORT - INDIVIDUAL EXCEEDS OCCUPATIONAL DOSE LIMIT OF 50 REM TO THE SKIN The following report was received from the State of New Jersey via fax: "Event Description: [The licensee,] IBA is a PET [Positron Emission Tomography] manufacturer and radiopharmacy. When the dosimetry reports for November 2014, were reviewed, it was noted that one individual exceeded the 20.1201(a)(2)(ii) occupational dose limit of 50 rem to the skin of an extremity. This was caused by a November dose of greater than 46 rem to the left extremity, bringing the year to-date dose to greater than 62 rem. The licensee is investigating this unusual November dose and will be preparing a written report. The individual has been removed from work with radioactive materials and the dosimeter for December has been sent in early for processing." * * * RETRACTION AT 1512 ON 4/27/2015 FROM CATHY BIEL TO MARK ABRAMOVITZ * * * After discussions with the licensee, the dose to the left hand was reduced from 46 Rem to 20.592 Rem which gives an annual dose to the extremity of 37 Rem. This dose is below the reporting requirements and the event is retracted. Notified the R1DO (Gray) and NMSS Events Notification Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-12-24
50683 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2014-12-15 15:00 | 2014-12-16 15:36 | 2014-12-16 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following report was received from the State of New Jersey via fax: "Event Description: [The licensee] is a trash-to-steam facility and uses generally and specifically - licensed fixed gauges as level indicators. One of their registered, generally licensed gauges was found to be damaged during the 6-month shutter check. The damage appears to be a result of impact and the plunger needed to close the shutter is inoperable. The gauge is a Berthold Model LB 7440 L, S/N 838-3-90, containing 50 mCi of Cs-137. The gauge is in a fairly inaccessible area of the plant, and personnel do not work in the area. No overexposures are thought to have occurred at this time. An investigation is being performed and a 30-day report will be provided." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2014-12-24
50682 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2014-12-12 | 2014-12-16 13:44 | 2014-12-17 | WISCONSIN AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following information was obtained from the State of Wisconsin via email: "The licensee reported that a radiography crew working at a temporary jobsite on the night of December 12, 2014, had a failure of a drive cable mechanism on a QSA Global Model 880D radiography camera. The drive cable severed, and the radiography crew was unable to retract the source into the camera. The crew re-established boundaries and maintained appropriate surveillance of the area. An individual who is licensed to perform source retrievals responded to the jobsite and was able to retract the source into the safe position in the camera. Direct-reading dosimeters did not indicate any exposures exceeding regulatory limits. The licensee has sent permanent record dosimetry for emergency processing, and the licensee has sent the failed equipment to QSA for analysis. "The Wisconsin Radiation Protection Section will provide updates through NMED after receiving the licensee's written report." Wisconsin Event Report ID No.: WI140014 * * * UPDATE FROM MEGAN SHOBER TO JOHN SHOEMAKER AT 1213 EST ON 12/17/14 * * * The following information was obtained from the State of Wisconsin via email: "The drive cable in question broke near the junction between the cable and the metal ball on the end of the cable. On December 17, 2014, the licensee submitted a report of the radiographer's permanent record dosimetry. Exposures from the source retrieval were less than regulatory limits. "Because the radiography crew and equipment involved in this incident are based in Illinois, the Wisconsin Radiation Protection Section notified the Illinois Emergency Management Agency." Notified R3DO (McCraw) and NMSS Events Notification (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2014-12-24