44260 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-04-09 04:16 | 2008-06-03 12:50 | 2008-06-03 | 60-DAY OPTIONAL NOTIFICATION FOR INVALID SPECIFIED SYSTEM ACTUATION "On Wednesday April 9, 2008 at 0416 hours, an invalid actuation of the 1B Refueling Floor Ventilation Exhaust Radiation Monitor occurred. The actuation caused a Division 2 Group 6C isolation signal, which caused primary containment isolation valves (PCIVs) to automatically close on the Containment Leak Detector Radiation Monitor (10-S182) and the Drywell Hydrogen/Oxygen Analyzer (10-S205). The 1A, 1C, and 1D channels were unaffected and indicated normal ventilation exhaust radiation levels during the event. "The cause of the event was a failure of the K2 relay in the 1B Refueling Floor Ventilation Exhaust Radiation Monitor. The failed relay has been replaced and the radiation monitor was declared operable on Wednesday April 9, 2008 at 2024 hours. "The portion of the primary containment isolation system that received an actuation signal functioned successfully. All of the affected open isolation valves automatically closed. The only equipment malfunction during the event was the failed K2 relay. The Division 2 Group 6C isolation was a partial actuation. "This event is reportable per 10CFR50.73(a)(2)(iv)(A) since isolation valves for the Containment Leak Detector Radiation Monitor and Drywell Hydrogen/Oxygen Analyzer automatically closed due to an invalid signal." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-06-03
44259 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-06-03 | 2008-06-03 12:08 | 2008-06-03 | LOUISIANA AGREEMENT STATE REPORT - LOST WELL LOGGING TOOL "[On the morning of May 29, 2008], a Pulsed Neutron Generator (Source #183619) belonging to Baker Hughes Oilfield Operations, Inc. dba Baker Atlas, containing approximately 900 millicuries of Tritium (H-3) was lost into the waters of the Mississippi River. The events were as follows: "A commercial hotshot carrying two complete Pulsed Neutron Tools was dispatched to the Hilcorp dock in Cocodrie, La., from the Baker Atlas facility in Broussard, La. at approximately 3 A.M. this morning [5/29/08]. "The tools arrived at the Hilcorp dock at approximately 5 A.M.. The shipment was verified by the Hilcorp dock dispatcher and loaded onto a Hilcorp contracted Crew Boat. Note: there were no Baker Atlas employees included in the transport of this shipment. The Baker Atlas crew was already at the rig when this equipment was ordered. "The shipment arrived at Hilcorp S/L 3090 #7, in the Little Pass field at approximately 7 A.M.. At arrival, the Hilcorp company representative noted that the aluminum tubes containing the Baker atlas downhole tools were not strapped down and were extended over the rail of the boat. "The Hilcorp representative alerted the Baker Atlas crew, who conducted an inventory of the equipment and found that one tube containing both the upper section and lower section [containing the 900 milliCurie H-3 source] of a Pulsed Neutron Generator Tool was missing. "The Hilcorp representative dispatched the crew boat back to the dock to conduct a visual search of the route and dock, but nothing was found. Due to the weight and density of the equipment, it is most likely that the tube (and tools in it) sank to the bottom of the river. Note: the rig is approximately 20 nautical miles from the dock. "The customer (Hilcorp) has accepted financial responsibility for this loss and does not believe that a search for the missing equipment would be cost effective." The State of Louisiana considers this event closed. Louisiana DEQ Event Report ID: LA0800011 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-06-06
44258 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-06-02 14:15 | 2008-06-03 10:54 | 2008-06-03 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER MOISTURE DENSITY GAUGE On June 2, 2008 at approximately 2:15 pm a Troxler Moisture Density Gauge, Model 3430, was run over by a skid steer at a construction site in the Denver Metro area . The licensee notified the Colorado Radiation Management Unit at approximately 4:00 pm that the gauge had been transported back to the main office in Golden, Colorado. Subsequent preliminary testing indicated that the sources were intact and not leaking. Results of the formal leak test are pending. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-06-06
44257 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-06-02 14:40 | 2008-06-02 17:17 | 2008-06-02 | SHIPPING CASK ARRIVES WITH A LOOSE BOLT "The following is a 4 Hr Non-Emergency notification in accordance with 10 CFR 50.72(b)(2)(xi), Offsite Notification. "At 1440, June 2, 2008, Susquehanna LLC was notified by the Barnwell South Carolina waste disposal facility, of an issue with a shipping cask containing irradiated hardware shipped from Susquehanna LLC. The cask was received at the facility on 5/31/08 and the incoming radiological survey was completed with no out of specification values. On June 2, 2008, the cask had the impact limiter removed and was in the process of being offloaded when it was discovered that one of the twelve bolts that secure the cask base plate to the cask body was found hand tight. The remaining eleven bolts were not loose, There was no radiological safety concern associated with the bolting condition as survey results confirmed that no radioactivity leaked from the cask. The waste facility will issue a condition report for Susquehanna's response. "The site South Carolina Department of Health and Environmental Controls (SC DHEC) Inspector was notified by Barnwell facility personnel of the issue." The licensee's QC inspector is required to verify bolt torque before the cask leaves the site. This will be confirmed by the licensee. The licensee will be notifying PEMA (Pennsylvania Emergency Management Agency). The licensee notified the NRC Resident Inspector. | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-06-02
44256 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-06-02 | 2008-06-02 17:18 | 2008-06-03 | FLORIDA AGREEMENT STATE REPORT - LOSS OF CONTROL OF REFERENCE SOURCES State of Florida Bureau of Radiation Control reported that the licensee, Indian River Radiology, sold two gamma cameras to another entity. By mistake, the purchaser of the cameras also took the reference sources that are used for calibrations. The sources will be returned to the licensee (seller) by Wednesday, June 4, 2008. This is considered a loss of control of radioactive material. The sources each contained 20 mCi of Cs-137 and 250 mCi of Gd-153. Florida Incident Number: FL08-083 * * * UPDATE FROM STEVE FURNACE TO HOWIE CROUCH @1651 HRS. ON 6/3/08 * * * The State of Florida amended the report to state that the Cs-137 source was 30 mCi in strength as of 1 MAY 1999 and is used as a PET scan source, not a reference source. The Gd-153 source was 250 mCi on 1 DEC 2004. They are encouraging the expedited return of the sources to the licensee. Notified R1DO (Henderson) and FSME EO (Chang). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-06-05
44255 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-06-02 | 2008-06-02 15:01 | 2008-06-02 | MASSACHUSETTS AGREEMENT STATE REPORT - NI-63 SOURCE LEAKAGE The following information was obtained from the State of Massachusetts via facsimile: The licensee reported that two Electron Capture Device (ECD) leak tests were positive for leakage. ECD serial number U0504 had a reading of 0.1 microCuries. ECD serial number U2861 had a reading of 0.06 microCuries. Both units are Agilent model G2397A and contain 15 mCi of Ni-63. The licensee has taken both units out of service and has contacted Agilent for the return of both devices. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-06-05
44254 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2008-05-31 13:30 | 2008-06-02 09:33 | 2008-06-02 | AGREEMENT STATE REPORT INVOLVING A STOLEN MOISTURE DENSITY GAUGE The authorized gauge user for Matrix Engineering Group left a construction site in Paulding County, placing a CPN Model MC-1 Moisture Density Gauge in the camper of his pickup truck. He stopped at a Chevron Station on Goldmine Road in Dallas, GA, leaving his truck for approximately 10-15 minutes, discovering when he returned that the gauge and case were missing. The CPN MC-1 Gauge, S/N M15116482, contains two (2) sources; Cs-137 (10 mCi) and Am-241:Be (50 mCi). A police report was filed with the City of Dallas PD. The licensee will post a reward for return of the stolen gauge. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE FROM KEITH ST. CYR TO HOWIE CROUCH ON 6/2/08 @ 1504 EDT * * * The gauge has been recovered. Apparently, the gauge fell out of the truck when the user was leaving the Paulding County job site. An individual recovered the gauge and returned it to the job site. The gauge is currently in the possession of the licensee and does not appear to be damaged. The State of Georgia will recommend a leak check of the gauge to the licensee. Notified R1DO (Henderson), FSME (Burgess) and ILTAB (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2008-06-05
44253 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-06-01 23:00 | 2008-06-02 02:49 | 2008-06-02 | ENTRY OF UNAUTHORIZED PERSON INTO THE PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee will notify the NRC Resident Inspector. Contact the HOO for additional details. * * * RETRACTION FROM G.L. PLUMLEE TO JOE O'HARA AT 1048 EDT ON 6/2/08 * * * This event has been retracted. The licensee will notify the NRC Resident Inspector. Contact the HOO for additional details. Notified R4DO(Whitten). | 0 | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-06-02
44252 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-06-01 11:48 | 2008-06-01 17:33 | 2008-07-17 | LUBE OIL MOISTURE CONTENT GREATER THAN ACCEPTABLE LIMIT "A sample was taken of the lubrication/control oil from the Unit 1 High Pressure Coolant Injection (HPCI) System for moisture content analysis. The results of this analysis concluded that the moisture content in the oil exceeded acceptable levels. As a result of this condition the Browns Ferry Nuclear Unit 1 HPCI system was declared inoperable at 11:48 on 6/1/08. "This event is reportable within 8 hours in accordance with 10 CFR 50.72 (b)(3)(v) as event or condition that at the time of discovery could have prevented the fulfillment of a safety function. It also requires a 60 day written report in accordance with 10 CFR 50.73 (a)(2)(vii). "Unit 1 remains at 100% power. "Unit 1 has entered Technical Specification LCO 3.5.1 and is performing the required actions. Troubleshooting of the moisture intrusion condition is in progress, and a corrective action plan is being developed. "The NRC Resident inspector has been notified." * * * RETRACTION AT 1239 EDT ON 7/17/08 FROM BAKER TO HUFFMAN * * * "ENS Event Number 44252, made on June 1, 2008, is being retracted. "NRC Notification 44252 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were met when an oil sample indicated the Unit 1 High Pressure Coolant Injection (HPCI) System turbine oil system contained excessive amounts of water. "An evaluation performed in response to this report concluded that the Unit 1 HPCI System was capable of performing its intended safety function with the turbine oil system containing more water than recommended in the TVA Lubrication Oil Analysis and Monitoring Program. TVA found through an engineering evaluation that the amount of water contained in the turbine oil system would not impact the HPCI operation during its mission time for the Design Basis Loss-of-Coolant Accident. "As such, the circumstances discussed in the report did not result in any condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat, or mitigate the consequences of an accident. Thus, there was no impact on nuclear safety. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(B) or 10 CFR 50.72(b)(3)(v)(D). "TVA's evaluation of this issue is documented in the corrective action program (PER 145517). "The licensee has notified the NRC Resident Inspector. " R2DO (Haag) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2008-06-01
44251 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-05-30 15:05 | 2008-05-30 18:05 | 2008-05-31 | PLANNED POWER OUTAGE AT PRIMARY EMERGENCY OPERATIONS FACILITY (EOF) "Southern California Edison has scheduled replacement of the backup diesel generator (DG) for the San Onofre Emergency Operations Facility (EOF), for Saturday May 31, 2008. While the new DG is being installed, the EOF will be inoperable. The EOF outage is expected to begin at about 0700 and last approximately 8 hours. "The alternate EOF located in Irvine, CA, will be available should SONGS need to respond to an Emergency Event. "The Emergency Recall System, which is housed in the EOF, will be out of service while the new DG is being installed. Should recall of the Emergency Response Organization (ERO) be necessary during the EOF outage, SCE will utilize alternate methods (contained in existing site procedures) for activating the ERO. "This planned EOF outage is being reported in accordance with 10 CFR 50.72(b)(3)(xiii). "At the time of this report, Unit 2 and Unit 3 were operating at about 99 percent and 98 percent power, respectively." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2324 ON 5/31/2008 FROM MIKE McBREARTY TO MARK ABRAMOVITZ * * * "The Emergency Operations Facility was returned to service on May 31, 2008 at 1810 PDT. SCE is continuing to troubleshoot problems identified with the transfer switch associated with the new backup diesel generator, and will inform the NRC Resident Inspectors when the backup DG is available." The licensee will notify the NRC Resident Inspector. | 0 | 99 | 98 | 0 | 99 | 98 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-05-30
44250 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-05-15 | 2008-05-30 10:32 | 2008-05-30 | AGREEMENT STATE REPORT INVOLVING RECEIPT OF CONTAMINATED PACKAGES On May 15, 2008, a driver for Cardinal Health Nuclear Pharmacy Services made deliveries of Tc-99 ammo boxes to the Womack Regional Hospital, the Moore Regional Hospital, the Pinehurst Medical and Pinehurst Cardiology followed by a final stop at the Moore Regional Hospital. The driver was notified at the Moore Regional Hospital that his delivery was contaminated. The most probable initial source of the contamination is attributed to his recovery of old boxes picked up at Womack Regional Hospital during his delivery (a later survey confirmed high levels of surface contamination). The State of NC is continuing their investigation. NC Incident No.: 08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-06-04
44249 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-05-30 05:00 | 2008-05-30 07:55 | 2008-05-30 | AGREEMENT STATE REPORT - TRAFFIC ACCIDENT INVOLVING RAM The following was provided by the State via e-mail: "Just after 0500 [EDT] two vans carrying medical RAM collided. There were no injuries. All southbound lanes [of Highway 200 in Marion County] were closed while the vehicles were removed. Hazmat determined that there was no damage or spill from the packages. One van had the packages jammed and they couldn't be removed at the scene. That van and driver were transported to Ocala where the packages can be removed. The other licensee is Cardinal Health 414, 3425 SW 42nd Way, Gainesville, FL 32608; license 3452-3, 3B. The licensees maintain possession of all RAM. No further action will be taken on this incident." The isotope was Tc-99m and Thallium, by-product in a liquid form. The activity level is unknown. "FL Incident Number: FL08-082." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-06-04
44248 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-05-29 20:10 | 2008-05-29 22:26 | 2008-05-29 | MODIFIED SECURITY MEASURES DUE TO SUDDEN INCLEMENT WEATHER At 2010 hours CDT the security measures were modified in accordance with the licensee's physical security plan and severe weather procedures due to severe weather conditions (Tornado Warning). Compensatory measures were instituted during this time. Normal security measures were restored at 2030 hours local time. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW | [5 empty] | 1 | 2008-05-29
44247 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-05-29 11:36 | 2008-05-29 18:06 | 2008-05-29 | OFFSITE POWER BELOW 59.7 HZ "On May 29, 2008, at approximately 1136 PDT, the offsite power grid connected to San Onofre experienced a momentary system disturbance. Control Room indicators alerted Operators that the grid frequency dipped to approximately 59.6 Hz. Because frequency dipped below 59.7 Hz, SCE is reporting this event in accordance with 10CFR50.72(b)(3)(v)(D). "The frequency dip lasted approximately 10 seconds, reportedly due to a loss of generation in the Pacific Northwest. The grid is currently operating at nominal frequency. "At the time of the event, San Onofre Unit 2 was operating in Mode 1 at approximately 99 percent power and Unit 3 was operating in Mode 1 at approximately 80 percent power. The NRC Resident Inspector has been notified of this event and will be provided a copy of this report." | 0 | 99 | 80 | 0 | 99 | 80 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-05-29
44246 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2008-05-28 21:34 | 2008-05-29 02:40 | 2008-05-29 | MANUAL REACTOR TRIP DUE TO IMPROPER MOVEMENT OF CEA'S "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "On May 28, 2008, at approximately 2134 Mountain Standard Time (MST) Palo Verde Unit 2 operators manually tripped the reactor, as directed by procedures, when four Control Element Assembly (CEAs 7, 9, 11 &13) of shutdown bank A slipped to the fully inserted position while conducting low power physics testing following Unit 2's fourteenth refueling outage. Unit 2 was critical [Intermediate Range 5.0E-2]and at normal operating temperature and pressure prior to the trip. Following the manual reactor trip all remaining CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. "Unit 2 is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The cause of the slipped CEAs is not known at this time and is under investigation. "The Senior Resident Inspector was informed of the Unit 2 reactor trip." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-05-29
44245 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2008-05-28 17:30 | 2008-05-28 22:03 | 2008-05-28 | HIGH PRESSURE CORE SPRAY INOPERABLE "On May 28, 2008, at 1730 hours, control room operators determined after testing, that the Emergency Service Water (ESW) Division 3 Subsystem was inoperable due to a condition that will not allow the subsystem to maintain 'keep-fill' pressure in the event of a loss of offsite power. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.2 requires that the High Pressure Core Spray (HPCS) System (a single train safety system) be declared inoperable immediately when the ESW Division 3 Subsystem is inoperable. The plant immediately entered TS LCO 3.5.1 Condition B, HPCS System inoperable. TS LCO 3.5.1, Required Action B.1, verify by administrative means that the Reactor Core Isolation Cooling System is operable within one hour, was completed at 1730 hours. Required Action B.2 requires that the HPCS System be restored to operable status within 14 days. Maintenance/troubleshooting activities are in progress to determine the cause of the ESW Division 3 Subsystem condition. "This event is being reported as a condition that could have prevented the safety function of structures or systems required to mitigate the consequences of an accident. The resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-05-28
44244 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-05-28 16:30 | 2008-05-28 20:02 | 2008-05-28 | TRANSPORTATION ACCIDENT INVOLVING A RADIOACTIVE MATERIAL SHIPMENT "On May 28,2008 at 1630 CDT Browns Ferry was informed that a tractor trailer transporting a shipment of radioactive material from Browns Ferry Nuclear Plant (shipment # 080518) was involved in a 2 car traffic accident near Corinth, Mississippi. Local law enforcement responded to the accident. The Mississippi Emergency Management System was notified as well as the Local EMA in Alcorn County, Mississippi. Investigation into the accident concluded that no personnel injuries occurred and there was no damage to the radioactive material shipment container. Presently another tractor is in route to the area to continue transportation of the shipment. "The licensee notified the NRC Resident Inspector. "This event is reportable as a 4 hour Non-Emergency Notification report in accordance with 10 CFR 50.72(b)(2)(xi), 'Any event or situation, related to the heath and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.'" | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-05-28
44243 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-05-28 | 2008-05-28 18:21 | 2008-05-28 | MASSACHUSETTS AGREEMENT STATE REPORT - SCRAP METAL LOAD SET OFF RADIATION ALARM The following information was received from the State of Massachusetts via facsimile: "A shipment of ferrous scrap metal from a trash to energy generating facility set off the radiation alarms at the entrance to the scrap facility and was immediately rejected. A consultant responded to the facility with an isotope identifier and reported Radium-226 in the load. Insofar as the highest exposure rate on the surface of the trailer was 0.6 millirem/hour, a DOT-E 10656 was issued to permit travel back to the point of origin. The company that originated the shipment has acquired the services of a different consultant to evaluate the situation at their facility, contain the problem and to document the legal disposition of the radioactive material." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-06-02
44242 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-05-01 | 2008-05-27 17:10 | 2009-05-07 | AGREEMENT STATE REPORT - TRITIUM RELEASE FROM EXIT SIGNS "Wal-Mart stores reported to Oklahoma DEQ that they had found three damaged tritium exit signs during an audit of their signage. Two of the signs released tritium, the third did not release tritium. All three signs were at the Wal-Mart in Enid, Oklahoma. It appears that the signs were damaged by a 'walkie stacker' (similar to a fork lift) at an unknown date in 2003. The radioactive content of the signs was not recognized at the time of the damage. All three signs have been sent to Isolite for disposal or recycling. The signs were manufactured by SRB Technologies, Inc. Serial numbers of the leaking signs were 290130 and 290103. "Wipe tests revealed removable contamination of about 800 dpm/100 sq. cm on the wall directly behind one sign, and a maximum removable contamination of 82,800 dpm/100 sq. cm on the cement floor below the other sign. Both leaking signs were in the shipping and receiving area of the store. Wal-Mart has hired Dade Moeller & Associates as consultants, and this company took the measurement and conducted remediation. Dade Moeller states that they will have a technician at the store to remediate the remaining contamination by the end of this week." * * * UPDATE AT 1715 EDT BY HOWIE CROUCH ON 06/04/08 * * * This report is a duplicate of EN# 44225. EN# 44225 will be removed from the database and the public website. * * * UPDATE ON 5/07/2009 AT 1611 EDT BY VINCE KLCO * * * An update was provided from Ralph Johnson to Joe O'Hara at 0914 on 3/19/09. Wal-Mart in Oklahoma performed an inventory of their generally licensed tritium exit signs and confirmed that a total of twelve were broken. This update corrects a previous update to a duplicate event notification. Notified R4DO (Pick) and FSME (Schaffer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2008-05-30
44241 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-05-27 08:15 | 2008-05-27 08:43 | 2008-05-27 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA At 0825 hrs. on 5/27/08, there was an attempted introduction of contraband into the Protected Area. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 1 | 2008-05-27
44240 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-05-25 09:30 | 2008-05-25 09:50 | 2008-05-25 | INVERTER FUSE FAILURE "At 1835 on 5/24/08 CD482 inverter main power fuse failed. This inverter powers various vital ECCS channel 'C' analog instrumentation (including 'C' channel EDG start circuitry). The inverter transferred to the alternate AC power supply as designed with no abnormal plant response or transient. The main power fuse was replaced and attempts were made to place the inverter section back in service and return the inverter to the normal power supply. Logic card checks were performed as part of the normal restoration process prior to transferring to the inverter normal output. These checks could not be completed satisfactorily and indicate that there is an abnormal condition in the inverter section. The inverter, while on alternate AC, is not operable per technical specifications [TS] due to the loss of alternate AC on a LOOP/LOCA, which would prevent the 'C' EDG from starting. Additional safety related equipment that is unavailable include the 'D' Station Service Water Pump for a scheduled maintenance window. All other safety equipment is operable and functioned as required. No personnel were injured. Unit shutdown commenced at 0930 on 5/25/08 in accordance with TS 3.8.3.1. The unit is required to be in hot shutdown by 1435. This four-hour report is bring made in accordance with 10 CFR 50.72(b)(2)(i)." The licensee notified the NRC Resident Inspector. The licensee will notify a local government agency. * * * UPDATE FROM TOM FOWLER TO JOE O'HARA AT 1415 ON 5/25/08 * * * The inverter logic power supply has been replaced, and the inverter has been tested satisfactorily. The inverter has been declared operable, and the licensee exited the technical specification required shutdown at 1217. Power ascension is in progress. The licensee informed the NRC Resident Inspector, and the Lower Alloways Creek Township. Notified R1DO(Gray) | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-05-25
44239 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-05-24 09:38 | 2008-05-24 15:06 | 2008-05-28 | STEAM GENERATOR LEVEL EXCURSION "On 5/24/2008 at 0938, with Beaver Valley Power Station Unit 2 (BVPS U2) in Mode 1 at 15% power during preparations for turbine startup, the unit experienced a steam generator level excursion. Attempts to manually control steam generator water level were unsuccessful. "Steam Generator narrow range levels exceeded the setpoint for P-14, Steam Generator Level High High Turbine Trip. The actuation of P-14 automatically actuated the following: trip of the running Main Feedwater pump, closure of the Main and Bypass Feedwater regulating valves, and closure of the Feedwater Containment isolation valves. In addition to these signals, a turbine trip signal is generated but the turbine was not yet on-line. "The feedwater isolation signal has been reset and normal feedwater flow has been established. Preliminary investigation has revealed that a broken air line caused the 'A' Main Feedwater pump recirculation flow control valve to fail open. This initiated the steam generator level transient. Additional investigation is in progress. "The trip of the Main Feedwater pumps automatically started both Motor Driven Auxiliary Feedwater pumps (MDAFW). The automatic start of the MDAFW pumps from this valid system actuation is reportable under 10CFR50.72(b)(3)(iv)(A). "The plant is currently stable in Mode 1 at 15% reactor power." AFW injected into the core. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MORGAN TO SNYDER ON 5/28/08 * * * The last sentence of the original report text should read "AFW injected into the Steam Generators" since AFW does not inject into the core. | 0 | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-05-24
44238 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2008-05-24 09:54 | 2008-05-24 10:03 | 2008-05-25 | LOSS OF OFFSITE POWER The licensee entered an Unusual Event after an automatic reactor trip due to a loss of offsite power per EAL Designation PU-1. Currently the plant is stable in Mode 3 with power being supplied to the "A" & "B" Emergency Diesel Generators (EDG) running supplying power to the safety buses. Decay heat is being removed by the motor driven Auxiliary Feedwater Pump supplying water to the steam generators exhausting to atmosphere via atmospheric relief valves. There are no primary to secondary tube leaks. NRC Resident Inspector has been notified. * * * UPDATE FROM SKIP JORDAN TO JOHN KNOKE AT1252 EDT ON 05/25/08 * * * At 1252 EDT the licensee terminated from their Unusual Event. After the loss of offsite power due to a failure of the Reserve Station Service Transformer (RSST) the licensee began to troubleshoot the problem as well as beginning to restore offsite power. At 1106 on 5/24/08 a cross-tie from Unit 3 was connected to Unit 2 and "A" EDG was secured. At 0950 on 5/25/08 the RSST was powered up and the non-vital busses were energized. At 1136 the "B" and "D" Reactor Coolant Pumps were started. At 1230 the vital bus was energized and the "A" EDG was secured. The licensee notified the NRC Resident Inspector. Notifications to: R1 (Marc Dupas, David Lew), R1DO (Mel Gray), NRR EO (Fred Brown), IRD MOC (William Gott), DHS (Fred Hill), FEMA (Dan Sullivan), USDA (Amanda Jimenez,), HHS (Mason Pyle), DOE (Julia Muse). The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode2: Startup; FMode2: Hot Standby | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2008-05-24
44237 | 0 | PALISADES | 1 |  |  | [1] CE | 2008-05-23 12:49 | 2008-05-23 16:06 | 2008-05-23 | AUTOMATIC REACTOR TRIP ON POSSIBLE GENERATOR LOCKOUT The reactor automatically tripped at 1249 EDT on 05/23/08. The cause of the reactor trip signal is not positively known, but it is believed to be related to trip of the 346 negative sequence relay which caused a trip of the 386C generator independent trip (coastdown) lockout relay. All plant systems performed as designed with minor deficiencies noted. EOP-1, 'Standard Post Trip Actions', and EOP-2, 'Reactor Trip Recovery', performed. All control rods fully inserted. All atmospheric steam dump valves lifted and reseated. CV-0780 (B Steam Generator ASDV) was identified as leaking and was manually isolated. There is no known primary to secondary leakage. Auxiliary feedwater system actuated automatically as designed in response to low steam generator water levels. AFW actuation consisted on AFW pump P-8A auto start and AFW valve operation. Steam generator water levels were subsequently restored to normal and are being maintained for primary coolant system heat removal via main steam isolation valves to main condenser (via the turbine bypass valves). Plant is at Normal Operating Pressure (2060 psia) and Temperature (533 degrees F). Grid is stable with safety bus station power being provided from Safeguards transformer. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-05-23
44236 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2008-05-23 03:30 | 2008-05-23 08:11 | 2008-07-21 | CHARGING PUMP DECLARED INOPERABLE DUE TO RELIEF VALVE LIFTING BELOW SETPOINT "During normal operation with 23 Charging Pump in service, 21 Charging Pump was placed in service for quarterly testing. Shortly after starting 21 Charging Pump, 23 Charging Pump relief valve lifted below its set point value. CVCS system pressure was approximately 2520 psig. This is the alternate safe shutdown pump responsible for inventory control for remote shutdown. 23 Charging Pump was declared inoperable. Recent NRC guidance indicates that a loss of a single train system not credited in accident analysis is reportable when identified in LCO 3.3.4, Remote Shutdown." The licensee will notify the NRC Resident Inspector. * * * RETRACTION AT 1446 EDT ON 7/21/08 FROM ROKES TO HUFFMAN * * * "Indian Point Unit 2 is withdrawing the 8-hour non-emergency notification made on May 23, 2008, at 08:11 hours (EN #44236). The notification reported a safety system functional failure (SSFF) as a result of the relief valve for the 23 charging pump lifting below its setpoint value. The condition was discovered during Chemical Volume & Control System (CVCS) operation with the 23 charging pump in operation. Shortly after the 21 charging pump was placed in service for quarterly testing, the 23 charging pump relief valve lifted. The operating speed of the charging pumps was reduced and the 23 charging pump relief valve re-seated. The 23 charging pump is the alternate safe shutdown pump responsible for inventory control for remote shutdown from the control room. The relief valve has an active safety function in the open position to provide overpressure protection for the 23 charging pump and associated piping. The relief valve has an active safety function in the closed position to prevent charging pump discharge flow from continuously re-circulating to the pump suction. At the time of the event Operations believed the 23 charging pump relief valve lifted prematurely and declared the 23 charging pump inoperable and made the 8-hour non-emergency notification for loss of remote shutdown capability for a component specified in Technical Specification 3.3.4, 'Remote Shutdown.' The relief valve was subsequently changes out with a spare. "Subsequent investigations determined that the CVCS pressure was set high in the operating band for two pump operation. Engineering determined that when the 21 charging pump was started the pulsation at the discharge of the positive displacement charging pump exceeded the limit of the relief valve pressure setting. Initial header pressure with the 23 charging pump in operation was approximately 2420 psig with typical charging header pressure at approximately 2300 psig. When the 21 charging pump was placed in service, the resultant pressure with consideration for pulsation immediately at the discharge of the charging pump would have been approximately 2701 psig. The charging pump relief valve lift pressure setting is 2735 +/- 3% (2653 psig to 2817 psig). Therefore, the resultant pressure from two pump operation was within the relief valve lifting pressure. An inspection of the removed relief valve showed only minor anticipated seat degradation of the disc ring insert. Further assessment indicated that the 23 charging pump relief valve did lift and also reseated when aligned for parallel pump operation when the CVCS pressure was adjusted. Engineering and Operations concluded that the 23 charging pump and associated relief valve were operable and capable of performing this safety function. The initial condition was determined to have been attributed to elevated initial CVCS pressure that resulted in challenging the relief valve during two pump operation." The licensee will notify the State and the Resident Inspector. R1D0 (Dentel) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2008-05-23
44235 | 0 | DEFENSE LOGISTICS AGENCY |  |  |  |  | 2008-03-11 | 2008-05-22 15:07 | 2008-05-27 | LOST LASER RECEIVER/TRANSMITTERS CONTAINING AM-241 "Two Laser receiver/transmitters were picked from stock for delivery to the Robins AFB Maintenance program. The two items were picked up from location and manifested for local delivery on 21 February 2008. The items were reported missing on customer complaint by the Avionics Repair shop on 11 March 2008. The item was originally marked as missing in the Automated Tracking System on 27 March 2008. Recent extensive searches have not discovered the missing items. "Based on preliminary investigation, the items were manifested for delivery, but the local delivery truck did not show on the day it was ordered. The material remained in the Radioactive Material Shipping area for a couple of days. A hand-receipt transfer document was located but it did not have the driver's signature of receipt. Additionally, the transition of new personnel delayed the reporting of the loss to the DDC Radiation Safety Office. "DDC Radiation Safety Office will work closely with the local Radiation Protection Officer to provide training to emphasis the requirements for timely reporting of incidents involving radioactive material." INCIDENT NO: DDWG-2008-01 Item NSN: 1270-01-365-9471 containing two 8 microCuries Am-241 sources [16 microCuries total]. * * * UPDATE PROVIDED BY NRC R4 (BROWDER) TO J. KOZAL AT 1108 ON 5/27/08 * * * Upon investigation of this event it was determined that the licensee is Defense Logistic Agency and not the US Air Force. The header of the report has been changed accordingly. Notified the R1DO (Rogge) and FSME EO (Bubar) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-05-22
44234 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2008-05-22 14:20 | 2008-05-22 14:35 | 2008-05-23 | REACTOR TRIP DUE TO LIGHTNING STRIKE Lightning struck the main transformer for Millstone Unit 2 and caused actuation of the reactor protection system. The reactor had an uncomplicated trip. Reactor shutdown and all control rods fully inserted. No primary or secondary relief valves lifted. Plant is stable in Hot Standby at NOP and NOT. Level is being maintained with normal feedwater and AFW is available if required. Decay heat is being removed via steam bypass valves. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED AT 2127 EDT ON 05/23/08 FROM MARK STROLLO TO JEFF ROTTON * * * "The purpose of this update is to clarify the stated cause of the reactor trip and plant response. The original title was 'Reactor Trip Due to lightning Strike on Main Transformer'. Although there was a lightning storm in the vicinity of Millstone 2 at the time of the reactor trip, the cause of the reactor trip may be related to a grid disturbance caused by a lightning strike on a transmission line off site. This cause remains under investigation. [Initial] event report states that no primary or secondary relief valves lifted. A steam generator safety relief valve (secondary) lifted for about 34 seconds. "The NRC Sr. Resident Inspector has been notified." Notified R1DO (Gray). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-05-22
44233 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-05-21 | 2008-05-22 13:22 | 2008-05-22 | AGREEMENT STATE REPORT - LEAKING CHECK SOURCE The State provided the following information via email: "Licensee identified a leaking sealed radioactive source. Once identified, the source was taken out of service and placed in the licensee's waste stream and a contamination survey of the area was made. No measurable contamination was identified from this survey. Contamination wipes consisted of area wipes (filter paper) measured in a liquid scintillation counter. "The Cs-137 source was used to test the response and functionality of hand-held radiation detectors. The leaking source, S/N 189-26-5, is a Cs-137 check source with an activity of 100 uCi on 3-1-87 and was manufactured by Isotope Products. The licensee stated the source may not meet the regulatory criteria for a sealed source since the front of the source is electroplated to allow for the detection of Cs-137 betas. As a precaution, the licensee reported it as a leaking source." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-05-27
44232 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-05-21 15:15 | 2008-05-21 21:41 | 2008-05-21 | LOSS OF CONTROL ROOM PHONE COMMUNICATIONS "At 1515 hrs, the control room staff discovered that normal control room phone communications were not working. Additionally, the NRC emergency notification system (red phone) was not functional. "The following communication systems were maintained: Satellite phone system, Chattanooga CECC ring down line, 2 lines in the Technical Support Center, Nextel mobile phone network, and site radio frequencies. "Even though some communications capabilities were maintained, this condition was determined to be reportable as a major loss of communication capability via 10 CFR 50.72(b)(3)(xiii) given that normal control room phone lines and the NRC red phone were not available. "All normal means of communication were returned to service at 1724 hrs by placing a spare battery charger in service to the communications system. "The Browns Ferry NRC Resident Inspector was notified of this occurrence and restoration." | 79 | 100 | 86 | 79 | 100 | 86 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-05-21
44231 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2008-05-21 17:04 | 2008-05-21 21:30 | 2008-05-21 | EMERGENCY DIESEL GENERATOR SHIFTED TO EMERGENCY START DURING POST MAINTENANCE TEST "At 1704, while performing post maintenance testing on the 'A' diesel, the automatic voltage regulator appeared to fail and was swapped from auto to manual. The 1DA bus voltage momentarily decreased causing the undervoltage relays to actuate. This actuation shifted the 'A' diesel to the emergency mode and restored bus voltage. The plant was in mode 5 at the time of the event. The 1DA bus remained energized throughout the event. Subsequently, the 1DA bus was paralleled to offsite power and the 'A' diesel generator was secured. The cause of the voltage regulator failure is being investigated." The licensee notified the NRC Resident Inspector. The licensee will be notifying the State and local emergency response organizations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-05-21
44230 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-05-21 15:00 | 2008-05-21 20:24 | 2008-05-21 | MOBILE CRANE CAUSED DAMAGE TO MET TOWER "During the performance of work activities in the vicinity of the Met Tower at 10 AM, a mobile crane made contact with a support wire causing damage to the tower. All instrumentation on the tower continues to function, but conservatively has been called inoperable. All instrumentation on the back up Met Tower continues to function. The backup Met Tower provides full assessment capability. "Due to the structural damage to the tower, as a precaution the area around the tower including the simulator training building and the maintenance training building have been evacuated. "Experts from Transmission and Distribution are assessing damage to the tower to determine what additional actions may be necessary. "The local media requested information about this event at 1500. Information has been released to the media. "The senior resident inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-05-21
44229 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-05-21 08:05 | 2008-05-21 12:03 | 2008-05-21 | INADVERTENT ACTUATION OF EMERGENCY SIRENS "At approximately 0805 CDT, on May 21, 2008, a Dakota County Communications Center Shift Supervisor inadvertently activated the Dakota County sirens from the primary unit during conduct of a silent siren test. The licensee was notified of the siren activation by the activation signal received on the informer unit in the Technical Support Center (TSC) at 0805. Seven of the 117 sirens in the 10-mile Emergency Planning Zone (EPZ) were activated for less than one minute. No press release is planned by Xcel Energy." The system has been restored to normal. The licensee notified the NRC Resident Inspector. | 99 | 100 | 0 | 99 | 10 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-05-21
44228 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2008-05-20 19:56 | 2008-05-21 02:29 | 2008-05-27 | DECAY HEAT REMOVAL COOLING INTERUPTED DURING CORE RELOAD "At 1956, during reactor core reload with a full refueling cavity, power was lost to the #2 non-vital instrument bus. This power loss resulted in closure of the shutdown cooling temperature control valve, HCV-341. The closure of HCV-341 interrupted the cooling capability of the in service shutdown cooling loop. "While cycling a condenser motor operated valve a 480 volt ground occurred which resulted in tripping the feeder breaker to motor control center MCC-4B2. MCC-4B2 was supplying power to Instrument Bus 2 via the Inverter 2 test transformer. The test transformer was powering Instrument Bus 2 due to Inverter 2 replacement per plant modification. The loss of the #2 Instrument Bus resulted in HCV-341, the shutdown cooling heat exchangers temperature control valve, failing closed. HCV-341 was manually opened to restore cooling at 2019. At 2049 power was restored to Instrument Bus 2 and the shutdown cooling system was returned to automatic operation. Flow through the core was maintained throughout the event, as the shutdown cooling heat exchanger bypass valve responded by opening to maintain flow. At the time shutdown cooling was lost, 44 of 133 assemblies had been loaded into the vessel and shutdown cooling temperature was approximately 88 degrees F. Time to boil was conservatively calculated to be 22.5 hours per plant procedures which assume decay heat from all 133 assemblies. Shutdown cooling temperature rose approximately one degree during this event. "Technical Specification 2.8.1(3)(1) was entered due to no Shutdown Cooling loop in Operation. No reactor coolant boron reductions were in progress. Irradiated fuel assembly loading into the reactor core was secured and actions to restore a Shutdown Cooling loop were being initiated. [Ft. Calhoun] entered] a 4 hour LCO to close all containment penetrations providing direct access from the containment to the outside atmosphere." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ERICK MATZKE TO JOHN KNOKE AT 1416 EDT ON 05/27/08 * * * "Following a detailed review of the event of May 20, 2008, Fort Calhoun station determined that the safety function of removing residual heat from the reactor coolant system was available throughout the entire event. The system is largely manual and the manual functions were not affected by the event. At the time of the loss of power the core was being reloaded. The heat load was very small and the temperature control valve (HCV-341) was closed to allow the system to increase in temperature. When control power to HCV-341 was lost the valve did not change position. "Since the ability of the shutdown cooling system to remove residual heat was not impacted by the loss of power and plant procedures have provisions to control the system locally, the safety function of removing decay heat was not lost. Therefore this notification is being retracted." The licensee notified the NRC Resident Inspector. Notified R4DO (William Jones) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-05-21
44227 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-05-20 13:10 | 2008-05-20 18:44 | 2008-05-20 | OFFSITE POWER GRID DISTURBANCE "On Tuesday, May 20, 2008, at approximately 1310 PDT, the offsite power grid connected to San Onofre experienced a momentary system disturbance. Control Room indicators alerted Operators that the grid frequency dipped to approximately 59.69 Hz. Because frequency dipped below 59.7 Hz, SCE is reporting this event in accordance with 10CFR50.72(b)(3)(v)(D). "The frequency dip lasted approximately 10 seconds, reportedly due to a high voltage DC transmission line disturbance in Oregon. The grid is currently operating at nominal frequency. "At the time of the event, San Onofre Unit 2 was operating in Mode 1 at approximately 99 percent power and Unit 3 was operating in Mode 1 at approximately 80 percent power. The NRC Senior Resident Inspector has been notified of this event and provided a copy of this report." | 0 | 99 | 80 | 0 | 99 | 80 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-05-20
44226 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-05-20 16:00 | 2008-05-20 17:40 | 2008-05-20 | LOSS OF FUNCTIONALITY TO TECHNICAL SUPPORT CENTER "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Action 8.2. The functionality of the Technical Support Center [TSC] has been lost due to the failure of the TSC Chiller to maintain chilled water within the normal control band. Alternate facilities are available to provide emergency response functions and actions are proceeding to return the TSC to FUNCTIONAL status with high priority." The licensee notified the NRC Resident Inspector. | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-05-20
44225 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-06-06 | 2008-05-20 13:54 | 2009-03-19 | THREE BROKEN TRITIUM EXIT SIGNS The Walmart in Enid, Oklahoma performed an inventory of their generally licensed tritium, exit signs and confirmed that three were broken. Walmart suspects that the signs have been broken since sometime in 2003. On May 1, 2008, contractors performed surveys of the area. One wipe was high enough to require remediation (82,000 dpm). The broken exit signs were removed on May 2, 2008. * * * UPDATE PROVIDED FROM RALPH JOHNSON TO JOE O'HARA AT 0914 ON 3/19/09 * * * Walmart in Oklahoma performed an inventory of their generally licensed tritium exit signs and confirmed that a total of twelve were broken. Notified R4DO(Hay) and FSME(McIntosh). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2009-03-19
44224 | -1 | REID HOSPITAL |  |  |  |  | 2008-05-19 09:44 | 2008-05-20 09:44 | 2008-05-21 | NON-PRESCRIBED DOSE GIVEN TO A PATIENT The prescribing physician ordered that a regular treadmill stress test be given to a patient. Instead of the correct test the hospital actually gave the patient a treadmill myocardial perfusion imaging test (MPIT) which uses a dose of Tc-99m. At 9:44 AM on 5/19/08 the patient was given a dose of 16.3 milliCuries of Tc-99m for the resting portion of the MPIT. Then at 10:24 AM on 5/19/08 the patient was given a dose of 35.3 milliCuries of Tc-99m for the stress portion of the MPIT. This resulted in a total dose of 51.6 milliCuries of Tc-99m given to the patient which is typical for a MPIT procedure. The hospital is currently conducting an investigation into this occurrence. The hospital will inform the patient of the error. * * * RETRACTION PROVIDED BY CHARLES NARAYANAN TO J. KOZAL ON 05/21/08 AT 0916 EST * * * Upon investigation the licensee has determined that the event does not meet the reporting requirements of 10 CFR 35.3045(a)(1). Notified the R3DO (Riemer) and FSME EO (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-05-26
44223 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-05-18 17:21 | 2008-05-19 17:20 | 2008-05-19 | VIOLATION OF A NUCLEAR CRITICALITY SAFETY APPROVAL - 24-HOUR REPORT "At 1721 hours on 5-18-08 the Plant Shift Superintendent was notified that violation of a nuclear criticality safety approval (NCSA) had occurred. "At 1720 hours on 5-17-08, the coolant system for [DELETED] was evacuated using an R-114 evacuation pump. The recirculating cooling water (RCW) condenser for that cell had not been disconnected or vented before evacuation of coolant system vapor or air, in violation of NCSA CAS-21 Rev. 01, 'Operation and Shutdown of the Diffusion Cascade,' Control 3.2.3. That control states: 'The RCW condenser shall be disconnected or vented before coolant vapor is evacuated.' "This control minimizes the amount of water that is available to moderate fissile material that might be present in the UF6 region of the process gas cooler. "Coolant system leak rate testing results were logged as of 2100 hours on 5-18-08 showing the coolant system to be evacuated to 30" vacuum and holding. At that pressure the system would be below the vapor pressure of water. Therefore, the coolant system being evacuated to that level and holding would indicate that no liquid water was present in the coolant system. The system being evacuated and holding proves that not only was the condenser free of any significant RCW to coolant leaks, but the process gas cooler was also essentially leak-tight. "The NRC Senior Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-08-1471: PGDP Event Report No. PAD-2008-18; NRC Worksheet No. 44223 "This violation represents a significant breach of NCS administrative controls for this operation: however, the safety significance of the as-found condition was quite low. The worst case enrichment [DELETED] at this location was just above the minimum fissile enrichment, so that a very large mass of optimally moderated uranium (more than [DELETED]) would have been needed for a criticality to be possible. Moderation would have required excessive water intrusion into the coolant system through condenser tube leaks, and subsequent water intrusion into the process gas region of the cooler/converter through a concurrent process gas cooler lube leak. Even though NCS Control 3.2.3 was violated, no significant water intrusion occurred. Although the as-found condition of the coolant system did not contain water, the parameter is considered lost since the typical condition of condenser tubes would be expect to result in water intrusion and would not represent a reliable barrier to in-leakage. "Double contingency was re-established within four hours of discovery by confirming the coolant system was drained of any possible liquid. At 1615 hours on 5-18-08 the air evacuation pumps were isolated from [DELETED] coolant system, which is the last point at which any potential liquid would have been drained from the coolant system. The condenser venting was completed at 2050 hours on 5-18-08. Coolant system leak rate completed at 2100 hours on 5-18-08 confirmed 30" vacuum and holding to show the condenser and process cooler were leak-tight." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-05-19
44222 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-05-16 | 2008-05-19 17:03 | 2008-05-19 | AGREEMENT STATE REPORT - MISADMINISTRATION OF I-131 "A misadministration occurred on 16-May-2008 and this office was notified at 1300 hours. The patient received a prescribed dose of 150 mCi of I-131 on 9-May-2008. Patient returned to hospital on 16- May-2008 for a scan only. Nuclear medicine tech mis-administered 5 mCi of I-131. The patient and doctor have been notified. Any further action is referred to Radioactive Materials. This office will take no further action on this incident." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-05-25
44221 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-05-17 09:04 | 2008-05-17 13:44 | 2008-05-17 | FAILED RELAY CAUSES EMERGENCY DIESEL GENERATOR TO START "At 0904 on 5/17/2008, ' D' and 'E' transfer busses were lost due to a failed relay on a supply breaker in the switchyard. Emergency Diesel Generators #2 and #3 auto-started to re-power the 1J and 2H Emergency Busses. Shutdown cooling on U2 was maintained during the event. U1 remained at 100% power. Offsite power was restored to the 1J and 2H Emergency busses at 1211. "This 8 hour report is being made for Surry Units 1 and 2 in accordance with 10 CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-05-17
44220 | 0 | HUBBELL ROTH AND CLARK |  |  |  |  | 2008-05-17 11:30 | 2008-05-17 13:07 | 2008-05-17 | STOLEN TROXLER MOISTURE DENSITY GAUGE A model 3401 Troxler moisture density gauge was stolen when the 2001 burgundy Ford van it was stored in was stolen while parked at Omego Restaurant, 22501 Eight Mile Road, Detroit, MI. The gauge contains 8 millicuries of Cs-137 and 40 millicuries of Am-241. The gauge was properly stored in its transport case and was chained to the floor in the back of the van. The Detroit police have been notified and have begun their investigation (Report # OCA0805170176). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-05-17
44219 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2008-05-05 09:30 | 2008-05-16 20:30 | 2009-12-07 | POTENTIAL MEDICAL EVENT DUE TO USE OF I-125 SEEDS OF LOWER APPARENT ACTIVITY THAN INTENDED "Notification of a possible medical event per 10 CFR 35.3045 - a brachytherapy procedure in which the administered dose may differ from the prescribed dose by more than 0.5 gray to an organ and the total dose delivered may differ from the prescribed dose by twenty percent or more. "Permittee: VA Medical Center, Philadelphia, PA "Event: The event occurred on May 5, 2008, and was discovered on May 15, 2008. "Description: A permanent implant prostate brachytherapy procedure was performed on May 5, 2008, using I-125 seeds. Seeds of a lower apparent activity than intended were mistakenly ordered and implanted. A CT scan of the patient was performed on May 6, 2008, and a postplan was performed on May 15, 2008. The D90 dose, calculated from the postplan, was less than eighty percent of the prescribed dose. Postplans based on CT scans performed approximately one month after an implant, when swelling from the procedure has partially resolved, are believed to provide more accurate assessment of dose to the prostate. It is intended to obtain another CT scan and postplan at about this time to better assess the prostate dose. The permittee intends to make a determination at that time regarding whether a medical event did occur. The permittee will complete a causal analysis and implement procedural changes to prevent a recurrence before any additional brachytherapy procedures are performed. "Effect on Patients: The VA is continuing to evaluate this event. At this time, adverse effects to the patient are not expected. "Patient notification: The permittee is ensuring that the referring physicians and patients were notified. "Licensee will notify the NRC Project Manager, Cassandra Frasier, of NRC Region III." * * * UPDATE ON 6/06/08 AT 18:16 EDT FROM LEIDHOLDT TO HUFFMAN * * * "This is an amendment to NRC Event Number 44219 and is a notification of possible medical events per 10 CFR 35.3045. "The VHA National Health Physics Program notified the NRC Operations Center on May 16, 2008, of a possible medical event at the VA Medical Center, Philadelphia, Pennsylvania, involving transperineal permanent seed implant prostate brachytherapy. The VHA National Health Physics Program initiated a reactive inspection on May 28, 2008. As part of this reactive inspection, the medical center was requested to review additional brachytherapy procedures. Based on a review of other brachytherapy procedures performed between February 1, 2007, and May 31, 2008, the medical center identified an additional four brachytherapy procedures that may be medical events because the D90 doses, determined from post-implant CT scans, were more than 20 percent less than the prescribed doses. The procedures are still under evaluation and a final determination has not been made. VHA is continuing to evaluate these possible medical events. At this time, adverse effects to the patients are not expected. If these patient procedures are determined to be medical events, the medical center will ensure that the referring physicians and patients are notified. VHA has notified NRC, Region III (NRC Project Manager, Cassandra Frasier). R1DO (Henderson), R3D(Pelke), and FSME (Chang) notified. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM E. LIEDHOLDT TO JOE O'HARA AT 2009 ON 6/12/08 * * * "This is an amendment to NRC Event Number 44219 and is a notification per 10 CFR 35.3045 of additional possible medical events. "VHA notified the NRC Operations Center on May 16, 2008, of a possible medical event at the VA Medical Center, Philadelphia, Pennsylvania, involving transperineal permanent seed implant prostate brachytherapy. "VHA initiated a reactive inspection on May 28, 2008. As part of this reactive inspection, the medical center was requested to review additional brachytherapy procedures. "VHA provided an initial update on June 6, 2008. This update reflects the most current information. "The medical center has identified 45 brachytherapy procedures that could be medical events because the D90 doses, determined from post-implant CT scans, were more than 20 percent less than the prescribed doses. The procedures are still under evaluation and a final determination has not been made. "We note that the medical center prescribes a dose of 160 gray instead of the more common 145 gray and that the number of possible events would be substantially less if the definition of a medical event were based upon the delivered dose instead of a percent of prescribed dose. "Furthermore, the medical center determines D90 doses from post-implant CT scans performed the day after the procedures. Prostate swelling may cause the doses assessed from these scans to underestimate the delivered D90 doses. "The permanent implant brachytherapy program has been suspended by the medical center director and an external review will be performed. "Effect on patients: "VHA is continuing to evaluate these possible medical events. At this time, adverse effects to the patients are not expected. "Patient notification: "If these patient procedures are determined to be medical events, the medical center will ensure that the referring physicians and patients are notified. "Other notification: "VHA has notified NRC, Region III (NRC Project Manager, Cassandra Frasier)." Notified R1DO(Summers), R3DO(Louden), and FSME(Mauer). * * * UPDATE BY E. LEIDTHOLDT TO J. KOZAL ON 6/21/08 AT 1841 * * * "This is an amendment to NRC Event Number 44219, reported on May 16, 2008, and is a notification per 10 CFR 35.3045 of additional possible medical events. VHA provided amendments on June 6 and 12, 2008. This amendment reflects the most current information. "VHA notified the NRC Operations Center on May 16, 2008, of a possible medical event at the VA Medical Center, Philadelphia, Pennsylvania, involving a transperineal permanent seed implant prostate brachytherapy procedure of a patient. This patient procedure is now considered to be a medical event. "VHA initiated a reactive inspection on May 28, 2008. As part of this reactive inspection, the medical center was requested to review additional prostate brachytherapy procedures. "The medical center has identified 63 brachytherapy procedures that could be medical events because the D90 doses, determined from post-implant CT scans, were 80% or less than the prescribed doses. The procedures are still under evaluation and a final determination has not been made for 60 of these procedures. For three of these 63 procedures including the May 5, 2008, procedure, the D90 doses have been confirmed to be 80% or less than the prescribed doses. "We note that the medical center routinely prescribes a dose of 160 gray instead of the more common 145 gray and that the number of possible events would be substantially less if the definition of a medical event were based upon the delivered dose instead of a percent of prescribed dose. "Furthermore, the medical center determines D90 doses from post-implant CT scans performed the day after the procedures. Prostate swelling may cause the doses assessed from these scans to underestimate the delivered D90 doses. "The permanent implant brachytherapy program is suspended and an external review is in progress. "Effect on patients: "VHA is continuing to evaluate these possible medical events. At this time, adverse effects to the patients are not expected. The external review will assess potential medical consequences. "Patient notification: "The three patients whose D90 doses were confirmed to be 80% or less than the prescribed doses and their referring physicians have been notified. If other patient procedures are determined to be medical events, the medical center will ensure that the referring physicians and patients are notified. "Other notification: "VHA will notify NRC, Region III (NRC Project Manager, Cassandra Frasier)." Notified R1DO (Schmidt), R3DO (Kunowski), and FSME (Holonich) * * * UPDATE PROVIDED BY THOMAS HUSTON TO JASON KOZAL AT 1758 ON 6/25/08 * * * "This report is an update to Event Report #44219. As the result of an ongoing review, a medical event was discovered for a fourth patient on June 24, 2008. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of the event will be sent to NRC Region III." Notified R1DO (Grey), R3DO (Burgess), and FSME EO (Camper). * * * UPDATE PROVIDED BY THOMAS HUSTON TO JOHN KNOKE AT 1245 ON 07/02/08 * * * "This report is an update to Event Report #44219. As the result of an ongoing review, medical events were discovered for an additional seven (7) patients on July 2, 2008. This brings the total number of medical events to eleven (11) under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these seven (7) additional medical events will be submitted to NRC Region III." Notified R1DO (Bellamy), R3DO (Kozak), and FSME EO (Zelac). * * * UPDATE FROM HUSTON TO CROUCH ON 07/08/08 AT 1319 EDT * * * "As the result of an ongoing review, medical events were discovered for an additional seven (7) patients on July 7, 2008. This brings the total number of medical events to eighteen (18) under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these seven (7) additional medical events will be submitted to NRC Region III." Notified R1DO (Burritt), R3DO (Duncan) and FSME EO (Burgess). * * * UPDATE PROVIDED BY LYNN MCGUIRE TO JOHN KNOKE AT 1335 ON 07/09/08 * * * A 15-day written report of one of the medical events was submitted to NRC Region III. Notified R1DO (Burritt), R3DO (Duncan) and FSME EO (Burgess). * * * UPDATE FROM THOMAS HUSTON TO JOE O'HARA AT 0943 ON 7/10/09 * * * "This report is an update to Event Report #44219. As the result of an ongoing review, medical events were discovered for an additional two (2) patients on July 9, 2008. This brings the total number of medical events to twenty (20) under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these two (2) additional medical events will be submitted to NRC Region III. "We have notified our NRC Project Manager, Cassandra Frazier (NRC Region III), of these additional events." Notified R1DO(Burritt), R3DO(Duncan), and FSME EO(Burgess) * * * UPDATE ON 7/15/2008 AT 1213 FROM GARY WILLIAMS TO MARK ABRAMOVITZ * * * "This report is an update to Event Report #44219. As the result of an ongoing review, medical events were discovered for an additional nine patients on July 15, 2008. This brings the total number of medical events to 29 under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these nine additional medical events will be submitted to NRC Region III. I will notify our NRC Project Manager, Cassandra Frazier (NRC Region III), of these additional events." Notified R1DO (Dentel), R3DO (Lara), and FSME (Burgess). * * * UPDATE ON 7/18/2008 AT 1313 FROM HUSTON TO HUFFMAN * * * "This report is an update to Event Report #44219. As the result of an ongoing review, medical events were discovered for an additional three patients on July 18, 2008. This brings the total number of medical events to 32 under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these three additional medical events will be submitted to NRC Region III. We will notify our NRC Project Manager, Cassandra Frazier (NRC Region III), of these additional events. " Notified R1DO (Dentel), R3DO (Lara), and FSME (White). * * * UPDATE ON 7/22/2008 AT 1500 EDT FROM WILLIAMS TO HUFFMAN * * * "This report is an update to Event Report #44219. As the result of an ongoing review, medical events were discovered for an additional five patients on July 22, 2008. This brings the total number of medical events to 37 under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these five additional medical events will be submitted to NRC Region III." The licensee will notify NRC Project Manager, Cassandra Frazier (NRC Region III), of these additional events. Notified R1DO (Dentel), R3DO (Riemer), and FSME (Burgess). * * * UPDATE FROM GARY WILLIAMS TO JOE O'HARA 1145 EDT ON 7/25/08 * * * "As the result of an ongoing review, medical events were discovered for an additional two patients on July 25, 2008. This brings the total number of medical events to 39 under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these two additional medical events will be submitted to NRC Region III. Our NRC Project Manager, Cassandra Frazier (NRC Region III), is aware of these additional events." Notified R1DO (W.Cook), R3DO (M.Phillips), and FSME (C.Flannery) * * * UPDATE AT 0805 ON 08/06/08 FROM THOMAS HUSTON TO JEFF ROTTON * * * "As the result of an ongoing review, medical events were discovered for an additional four patients on August 05, 2008. This brings the total number of medical events to 43 under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these five additional medical events will be submitted to NRC Region III. Our NRC Project Manager, Cassandra Frazier (NRC Region III), is aware of these additional events." Notified R1DO (Gray), R3DO (D Hills), and FSME (C. Einberg) * * * UPDATE AT 1002 EDT ON 8/13/08 FROM HUSTON TO SANDIN * * * "This report is an update to Event Report #44219. As the result of an ongoing review, medical events were discovered for an additional four patients on August 12, 2008. This brings the total number of medical events to 47 under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these four additional medical events will be submitted to NRC Region III. I will notify our NRC Project Manager, Cassandra Frazier (NRC Region III), of these additional events." Notified R1DO (Holody), R3DO (Kozak) and FSME (Burgess). * * * UPDATE AT 1422 EDT ON 8/22/08 FROM HUSTON TO KNOKE * * * "This report is an update to Event Report #44219. As the result of an ongoing review, medical events were discovered for an additional eight patients on August 21, 2008. This brings the total number of medical events to 55 under Event Report #44219. The circumstances involved are similar to those previously reported for this event number. A 15-day written report of these four additional medical events will be submitted to NRC Region III. We will notify our NRC Project Manager, Cassandra Frazier (NRC Region III), of these additional events." Notified by email: R1DO (Perry), R3DO (Lipa) and FSME (Burgess). * * * UPDATE AT 1704 ON 10/2/2008 FROM THOMAS HUSTON TO MARK ABRAMOVITZ * * * "As the result of an ongoing reviews, medical events were discovered for an additional 37 patients on October 1, 2008. This brings the total number of medical events to 92 under Event Report #44219. "The circumstances are related to those previously reported for this event number with the following clarifications: - 35 of the additional medical events involve doses to organs or tissues other than the treatment site and are considered to meet medical event criteria described in 10 CFR 35.3045(a)(3). - 2 of the additional medical events involve doses to the treatment site (prostate) that had a D90 dose below 80% of the prescribed dose. - These 37 additional medical events involve different patient cases that have not been previously reported as medical events under this event report. "A 15-day written report of these 37 additional medical events will be submitted to NRC Region III. "We informed our NRC Project Manager, Cassandra Frazier (NRC Region III), of the additional events." Notified R1DO (White), R3DO (Lara), and FSME (Bradford). * * * UPDATE PROVIDED BY EDWIN M. LEIDHOLDT, JR TO JASON KOZAL ON 08/12/09 AT 1820 * * * "Event Report No. 44219 documents the VA's notification of the NRC of medical events involving permanent implant prostate brachytherapy at the Philadelphia VA Medical Center, beginning with a notification on May 16, 2009. As a result of ongoing reviews, the NHPP is notifying NRC of six additional medical events at the Philadelphia VA Medical Center. These events, also involving prostate brachytherapy with I-125 seeds, were discovered on August 12, 2009. These additional six medical events involve D90 doses less than 80% of the prescribed dose. "The D90 doses for all six events reported today were based upon CT scans performed one day after each implant, when the prostate is subject to edema from the procedure which often causes underestimation of the true D90. Furthermore, the prescribed doses were 160 gray, instead of the more common 145 gray. Most if not all of these six patients likely received clinically adequate dose distributions, despite the percent-wise slightly low D90s. Adverse biological effects to these six patients are not expected. We are reporting these six additional events to meet a regulatory requirement, not because of any anticipated harm to these patients. "The facility is aware of the requirement to notify the patients. "A written report on these additional medical events will be submitted to NRC Region III pursuant to 10 CFR 35.3045. We will notify the NRC Project Manager, Cassandra Frazier, of NRC Region III." Notified R1DO (Cook), R3DO (Cameron), and FSME EO (Mauer). * * * UPDATE PROVIDED BY THOMAS HUSTON TO DAN LIVERMORE ON 12/07/09 AT 1649 * * * "NHPP [National Health Physics Program of the U.S. Department of Veterans Affairs] retracts one Medical Event that was reported on October 2, 2008. "The reason is that one of the events reported that date was also reported earlier on July 22, 2008, and is a duplicate report. Only the July 22, 2008 report of this event should stand. "The total number of medical events reported on October 2, 2008, is corrected to be 36 rather than 37. The total number of medical events reported under Event Report No. 44219 is corrected to be 97 rather than 98. "We have communicated this information to our NRC Project Manager, Cassandra Frazier, of NRC Region III." Notified R1DO (Schmidt), R3DO (Phillips), and FSME (Vontill). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-06-17
44218 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-05-15 14:00 | 2008-05-16 09:17 | 2008-05-16 | CONCURRENT REPORT DUE TO RESPONSE TO A PRESS INQUIRY "Below are the responses to questions BWXT received from [deleted] the News & Advance of Lynchburg, VA, regarding NRC Inspection Report No. 70-27/2008-001 and Notice of Violation: "Q: Is Babcock & Wilcox contesting the notice of violation? "A: B&W has 30 days from the notice of the violation, which was issued on April 21, to contest it. A decision has not been made. "Q: Other than losing 'personal effects' and undergoing first aid, has the splashed employee experienced any other consequences from the splashing? "A: We do not comment on the health status of employees. "Q: What happens next in this citation procedure with the NRC? "A: B&W will make the decision to contest the notice or accept the violation. No fine has been charged to the facility. Corrective actions were implemented immediately following this event." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-19
44217 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-05-15 20:00 | 2008-05-15 20:51 | 2008-05-15 | OFFSITE NOTIFICATION TO STATE OF MASSACHUSETTS REGARDING PRESS RELEASE "Entergy Pilgrim Station has reached a tentative 4-year agreement with UWUA Local 369. This notification is in anticipation of media interest and Entergy Press Releases." Licensee notified the NRC Resident Inspector and the Massachusetts Emergency Management Agency. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-05-15
44216 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2008-05-15 14:25 | 2008-05-15 15:01 | 2008-05-15 | ALERT DECLARED DUE TO REQUEST FOR OFFSITE ASSISTANCE CONCERNING LOSS OF PLANT WATER Licensee declared an Alert due to requesting offsite assistance related to loss of plant water service. Water service line break is onsite. Plant water service is used to operate facility process equipment. Licensee is presently shutting down plant facility process equipment. Notified Richland County and State of South Carolina. Local fire department providing temporary water service via fire trucks. Currently there are no releases to the environment and no threat to public health and safety. * * * UPDATE AT 1755 EDT ON 05/15/08 FROM COUTURE TO ROTTON * * * Licensee terminated Alert at 1745 EDT. Plant Water system has been restored. Plant personnel are flushing water system prior to returning to service and starting up plant process systems. Licensee notified state and local agencies. Notified R2DO (Sykes), NMSS EO (Hill), IRD (Gott), DHS (Turner), FEMA (Cannupp), DOE (Yates), USDA (Timmons), and HHS (Howard). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | SC | FUE |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-05-15
44215 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-05-14 06:00 | 2008-05-15 10:51 | 2008-05-15 | CONCURRENT REPORT DUE TO OFFSITE NOTIFICATION TO THE STATE OF VIRGINIA "On May 14, 2008 at approximately 6:00 am, personnel discovered a tote of acid being stored in excess of 90 days allowed by Virginia Department of Environmental Quality (DEQ) regulations. The tote of acid was generated on February 8, 2008 and in order to meet the regulations it should have been shipped on May 8, 2008. An inquiry into the issue was made and the personnel responsible for scheduling shipments believed the generation date was the same as another tote in storage, February 18, 2008. The waste is scheduled to be shipped for disposal on May 16, 2008. A corrective action has been written for this event and an investigation will occur. "This concurrent report is being made because the event was reported to the following government agency, Virginia DEQ" The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-19
44214 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-03-25 | 2008-05-15 09:54 | 2008-05-15 | AGREEMENT STATE - MASSACHUSETTS - LEAKING CS-137 CHECK SOURCE The State provided the following information via facsimile: "This facsimile serves as initial notification of an event of a leaking Cs-137 check source found inside a generally licensed device - Beckman Coulter Model 3801 LSC - at Boston University, Boston, MA. The event was reported by Beckman Coulter to the Massachusetts Radiation via letter dated April 25, 2008. The preliminary information of this event [is as follows:] "On March 25, 2008, a Field Service Engineer (FSE) for Beckman Coulter performed a service call on a Beckman Coulter LS 3801 liquid scintillation counter (LSC) at Boston University in Boston, MA. At the time the service was performed, the FSE discovered an elevated radiation reading inside the LSC. Upon further investigation, the FSE discovered elevated radiation reading originated from a metal base plate used to support lead shielding inside the LSC. A wipe test of this base plate revealed removable contamination of ~ 0.03 microcuries. Upon discovery of the contamination, the FSE immediately notified Beckman Coulter's RSO and Boston University personnel. The contamination was limited to the metal base plate inside the LSC and no personnel were contaminated. Due to the position of the base plate, directly beneath lead shielding, no additional exposure to the user of the LSC would have resulted. The LSC was being decommissioned at the time and it is out of service. The dislodged Cs-137 source (currently 18 microcuries) was recovered from the LSC by the FSE and it is currently being held by Boston University. Beckman Coulter is investigating how the source holder may have been damaged. No contamination was found outside of the LSC, thus no additional decontamination measures were necessary as a result of this event." MA Report 05 - 7780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-05-20
44213 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-03-15 16:35 | 2008-05-14 13:16 | 2008-05-14 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1). "On March 15, 2008, while resetting the main turbine in preparation for performing 1MST-RPS25R, 'RPS Turbine Stop Valve and Control Valve Closure Chan Cal,' a Group 1 isolation was received. Main Steam Lines (MSLs) A and B were isolated for local leak rate testing, however, the MSLs C and D were not. The inboard and outboard Main Steam Isolation Valves (MSIVs) for the C and D MSL closed as a result of this event. "The isolation occurred during work associated with replacement of the main generator output breakers 22A and 22B. In order for the breakers to be removed, wiring that provides breaker position information was disconnected from the turbine control system (EHC). This resulted in a 'breaker closed' input to EHC. When the main turbine was reset, several logic interactions occurred resulting in the Group 1 isolation. No actual plant condition existed which required a Group 1 isolation and, with the Unit in Mode 4, Group 1 isolation is not required to be operable. Therefore, this actuation is considered to be invalid. "The affected MSIVs and PCIS instrumentation operated properly. This was a full Group 1 isolation with only the MSIVs associated with the C and D MSLs closing since the A ad B lines were isolated when the actuation occurred. The invalid PCIS actuation was entered into the corrective action program (i.e., NCR 270475). "The safety significance of this event was minimal. Plant equipment performed as expected. Group 1 isolation was not required to be operable in Mode 4. "The Group 1 isolation was reset and a jumper was installed to prevent a subsequent invalid Group 1 isolation. Procedures will be developed or revised to disable the Group 1 Isolation during modes in which it is not required and to reset the main turbine during outages. "The NRC Resident Inspector has been notified at this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-05-14
44212 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-05-14 10:00 | 2008-05-14 11:32 | 2008-05-14 | TEXAS AGREEMENT STATE REPORT - TWO AM-241 STATIC ELIMINATOR SOURCES MISSING The Solo Cup Company contacted the State of Texas concerning two 20.25 milliCurie Am-241 static eliminator sources that are missing. The Solo Cup company was unable to locate the sources following a request by the manufacturer (NRD) to return them as part of a source recall. The source serial numbers are SA-3232 and SA-3242. Model A-2003. The State investigation of the missing sources is in progress. TX Report I-8511 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-05-19
44211 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2008-04-03 06:25 | 2008-05-13 19:13 | 2008-05-13 | INVALID ACTUATION OF A SBGT DURING ANNUNCIATOR TEST "Monticello Nuclear Generating Plant is making a telephone report in accordance with 10 CFR 50.73(a)(2)(iv)(A) Invalid Partial Actuation of the Standby Gas Treatment and Secondary Containment Isolation Systems due to an inappropriate operator action. This report is being made in lieu of a written Licensee Event Report. "At 0825 on 04/03/2008, an operator was performing an annunciator test of the Control Room panels and inappropriately pushed the 'A' Standby Gas Treatment system 'Test' pushbutton instead of the 'Lamp Test' pushbutton. He then immediately pushed the 'Reset' pushbutton which reset the Standby Gas Treatment train. The inappropriate actuation of the 'A' Standby Gas Treatment System resulted in the 'A' train momentarily starting, causing ventilation fans V-EF-10 and V-MZ-6 to trip. The immediate resetting of the system by depressing the 'Reset' pushbutton prevented a full secondary containment isolation. "All systems started and functioned successfully. "The cause of the invalid signal was the operator actuating the system by depressing the 'Test' pushbutton instead of the 'Lamp Test' pushbutton. "The NRC Resident Inspector was notified of this event report." After the invalid actuation was completed, all systems affected were reset and returned to normal lineup. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-05-13
44210 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-05-13 16:48 | 2008-05-13 17:13 | 2008-05-13 | DAMAGED MOISTURE DENSITY GAUGE At the intersection of Toll Road 528 east of Highway 417 in Orlando a CPN Model MC-3, serial number 8027 moisture density gauge was damaged. "A water truck backed up over the gauge and bent the rod. The rod was later retracted to the shielded condition. The gauge will be returned to CPN for repair. No further action will be taken on incident. " Typically this model gauge contains a 10 milliCuries Cs-137 source and a 50 milliCuries Am-247/Be source. The State of Florida incident number is FL08-075. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-05-16
44209 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-05-13 16:00 | 2008-05-13 16:33 | 2008-05-13 | ACTUAL INTRODUCTION OF CONTRABAND Actual introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2008-05-20
44208 | 0 | VA HOSPITAL OF WEST PALM BEACH FL |  |  |  |  | 2008-05-13 12:15 | 2008-05-13 14:57 | 2008-05-13 | "[The Department of Veterans Affairs called] to report receipt of one package of radioactive material with removable surface contamination on the outside of the package greater than the limits in 10 CFR 71.87(i). "The package was received at approximately 12:15 PM Eastern Time (ET), May 13, 2008 by the VA Medical Center in West Palm Beach, FL. "A wipe test performed on the external surface of the package around 12:30 PM ET indicated a removable contamination level of 42 dpm/cm2 as compared to the regulatory limit of 22 dpm/cm2. "The package contained a PET radioactive drug with Fluorine-18 (F-18) shipped from Cardinal Health of Jupiter, Florida. The vendor/shipper also serves as the delivery carrier. The shipper/delivery carrier was notified of the contaminated package at approximately 12:55 PM ET by the VA Medical Center's Radiation Safety Officer. "Spectral measurements indicated that the contaminant involved is F-18. The package did not appear to be damaged. The package is being held for radiological decay and will be returned to the vendor in a couple of days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2008-05-13
44207 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-05-14 05:00 | 2008-05-13 14:25 | 2008-05-14 | EMERGENCY SIREN OUTAGE FOR UPGRADE "Fort Calhoun Station will be experiencing a partial loss of emergency communications and notification capabilities on Wednesday, May 14, 2008. Omaha Public Power District will be completing an upgrade to the main radio system from approximately 05:00 - 09:00, Wednesday, May 14, 2008. During this time, mobility over the radio system (mostly rural use) and the Fort Calhoun Station Alert and Notification System (ANS) sirens will be out of service. "Emergency Planning will notify the affected counties to have their back-up plan for the [alert and notification system] in place during that time. "Post Maintenance Silent Testing will be performed upon completion of radio maintenance to verify siren communications." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1157 EDT ON 5/14/08 FROM MATZKE TO HUFFMAN * * * The licensee reports that the siren outage commenced at approximately 0400 CDT this morning and is in progress. Currently, the estimated completion time for this activity is now approximately 1300 CDT today (5/14/08). R4DO (Powers) notified. * * * UPDATE PROVIDED AT 1847 EDT ON 05/14/08 FROM GUINN TO JEFF ROTTON * * * "Update to Event Number 44207 - Fort Calhoun Unit 1 - Event Date 05/14/2008 - Emergency Sirens upgrade is complete. Post maintenance silence testing was performed. All sirens are functional. "The NRC Resident Inspector, state, and local officials have been notified." Notified R4DO (Powers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-05-13
44206 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2008-05-13 08:25 | 2008-05-13 08:59 | 2008-05-13 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER At 0806 EDT, a loss of offsite power occurred when the 115 KV line #4 was lost combined with the unavailability of 115 KV line #1 which was out of service at the time for planned maintenance. Both EDGs started and loaded on the safety busses as expected. The licensee declared an Unusual Event at 0825 EDT per EAL 6.1.1 based on loss of offsite power for greater than 15 minutes. The Unit 1 recirc pump #13 tripped as a result of the event and spent fuel pool cooling was also lost. The licensee remained at power and there was no impact on Nine Mile Unit 2. Power for 115 KV line #1 was restored at 0845 EDT. Cause of the loss of Line #4 is still under investigation. The reactor is stable and the safety busses continue to be power by the EDGs. Restoration of a normal electrical power lineup and termination of the UE is still under review. The licensee notified the NRC Resident Inspector, the State, and local authorities. * * * UPDATE AT 10:29 EDT ON 5/13/08 FROM HELKER TO HUFFMAN * * * The licensee terminated the Unusual Event at 10:22 EDT based on restoration of offsite power to safety bus 103 from line #1. Bus 102 still remains energized by the EDG at this time. Investigation into the loss of line #4 continues. The loss of line #4 has been attributed to a Fitzpatrick protective relay 87B actuation for the B phase differential current. Investigation continues. The NRC Resident has been notified by the licensee. NRR EO (Thorp), Rg 1 (Dentel), IRD (McDermott), R1DO (Krohn), DHS (Dwight) and FEMA (McKentry) notified. * * * UPDATE AT 12:53 EDT ON 5/13/08 FROM HELKER TO SNYDER * * * "This condition is also reportable under 10 CFR 50.72(b)(3)(v)(D) 'Any event or condition that at the time of discovery could have prevented fulfillment of a safety function of systems that are needed to mitigate the consequences of an accident.' Specifically, both offsite power 115 KV lines were not available. "The second paragraph which applies is 10 CFR 50.72(b)(3)(iv)(B) 'Any event or condition that results in the valid actuation of the systems listed in paragraph (b)(3)(iv)(B).' Specifically, the auto start of the Emergency Diesel Generators on a valid loss of offsite power signal. "The cause of the loss of line 4 is still being investigated. Offsite power has been restored to onsite buses including PB 102, 103 and 101." The licensee will notify the NRC Resident Inspector of this update. Notified R1DO (Krohn). | 92 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2008-05-13
44205 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-05-12 15:00 | 2008-05-12 20:48 | 2008-05-12 | SHUT DOWN INITIATED DUE TO INOPERABLE STEAM GENERATOR FLOW CHANNELS "This 4-hour notification is being made to report that Salem Unit 2 has initiated a manual reactor shutdown in accordance with [Technical Specification] 3.0.3. The shutdown was initiated due to all eight steam generator steam flow channels being declared inoperable at 1500 on 5/12/08. All eight steam flow channels were indicating lower than actual steam flow such that the high steam flow coincident with low steam pressure or low-low Tave would not occur within the allowable values specified in the technical specifications. Salem Unit 2 is currently in Mode 1. Reactor Coolant System Temperature is 551 degrees Fahrenheit with pressure @ 2235 PSIG. Salem Unit 2 has no other shutdown Tech. Spec. action statements in effect. Prior to the initiating event Salem Unit 2 was raising power at 1/2 % per hour after 2R16 refueling outage. "All ECCS and ESF Systems are available. "No personnel injuries have occurred as a result of the shutdown. "No radiological release due to this event. "21 service water pump is cleared and tagged for strainer replacement. 21A and 23B circulating water pumps are cleared and tagged for maintenance." The licensee notified the NRC Resident Inspector. | 0 | 20 | 0 | 0 | 84 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-05-12
44204 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2008-05-12 14:30 | 2008-05-12 18:54 | 2008-05-12 | ARIZONA AGREEMENT STATE REPORT - CONTAMINATION EVENT DUE TO A BROKEN TRITIUM EXIT SIGN The following information was provided by the Arizona Radiation Regulatory Agency via email on 5/12/08 @ 1854 EST: "By letter dated May 7, 2008, the Licensee reported that their contractor had detected a broken 20 curie tritium exit sign at their Glendale store. A second contractor with a Certified Health Physicist, was called in to decontaminate and investigate the circumstances on April 25, 2008. The second contractor found up to 16,900 dpm/100 cm2 removable contamination on the wall where the sign had been located. On the floor beneath the sign, the contractor reported contamination up to 1,400 dpm/cm2. The date of breakage is unknown and could have actually occurred up to one year prior to discovery. "The device was a SRS Technologies, Inc. Serial number 304150, 20. The sign has been shipped to Canada to Shield Source, Inc., a Canadian licensee. "The Agency is investigating the delay in reporting this event since the report was not made within 24 hours." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2008-05-15
44203 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-05-12 13:45 | 2008-05-12 13:45 | 2008-05-12 | AGREEMENT STATE REPORT - MISSING IRIDIUM-192 SOURCE QSA Global reported to the Commonwealth of Massachusetts that a shipment containing a 149.2 Curie Ir-192 source that was originally shipped on 5/7/08 was missing. The shipment arrived in Miami and was transferred from FedEx to Amerijet. Amerijet reported to an agent of QSA Global, on 5/9/08, that the shipment could not be found at the time of its originally scheduled flight to Trinidad, its final destination. As of 1345 on 5/12/08 Amerijet still could not locate the package. The company initiated a warehouse search. The signature that FedEx had on record as receiver was reported to be "not an eligible" receiver by Amerijet. * * * UPDATE AT 1710 FROM BOB WALKER TO HOWIE CROUCH * * * Amerijet has located the missing shipment in their Miami facility. The package is undamaged and will shortly resume transport to its final destination of Trinidad. Notified ILTAB (Whitney), R1DO (Krohn), FSME (Reis), IRD (McDermott), and DHS (Lee). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-05-15
44202 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-05-12 12:30 | 2008-05-12 15:34 | 2008-05-12 | 24-HR REPORT - UF6 RELEASE DETECTION SYSTEM FAILURE "At 1230 CDST, on 05-12-08 the Plant Shift Superintendent (PSS) was notified that an alarm was received for the C-331 Unit 3 Cell 5 UF6 Release Detection (PGLD) System. Operators responded and found that the READY and MANUAL lights for this system were not illuminated. This PGLD System contains detectors that cover C-331 Unit 3 Cell 5 and Sections 2 and 3 of the cell bypass piping. At the time of this alarm, unit 3 Cell 5 and some areas of Sections 2 and 3 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell and in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 3 Cell 5 PGLD system inoperable, none of the required cell heads and only 2 of the required 3 heads in Sections 2 and 3 of the cell bypass were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.A.1 and 2.4.4.1.C.1 were entered and a continuous smoke watch was put in place within one hour. Engineering has determined that the system would not have been able to perform its intended safety function when this alarm came in. This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATR-08-1412; PGDP Event Report No. PAD-2008-14; Worksheet No. Responsible Division: Operations" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-05-12
44201 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-03-19 | 2008-05-12 10:30 | 2008-05-12 | GENERAL ELECTRIC HITACHI CR120A RELAY/RELAY COIL WIRE CLAMP CRACKING Southern Nuclear Company made this notification of a potential defect in components received by its Edwin I. Hatch Nuclear Plant. The potential defect may exist in ninety-six (96) subject components: ninety-four (94) General Electric Hitachi (GEH) CR120A relays and two (2) GEH CR120A relay coils. The wire clamps supplied with these relays and relay coils may be susceptible to cracking. The wire clamps serve to secure the wire connections to the relays and relay coils. Currently there are thirty-seven (37) CR120A relays and one (1) CR120A relay coil installed. The components not currently installed have been placed on hold. The licensee has followed the recommendations of GEH by visually inspecting all installed components for cracks. No cracks were found. The licensee will replace the clamps on one subject relay installed in the Main Control Room Environmental Control System. The clamps on the components installed in the Source Range Monitoring and Intermediate Range Monitoring instruments show no signs of cracking will be left installed as is. Replacement wire clamps will be ordered from GEH. The licensee plans to replace the clamps on the other stock components. | 92 | 57 | 0 | 92 | 57 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 21.21 |  |  |  | 0 | 2008-05-12
44200 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-05-11 03:00 | 2008-05-11 06:36 | 2008-05-11 | LOSS OF SAFETY FUNCTION DUE TO BOTH RHR TRAINS BEING INOPERABLE DURING MODE 3 "On 05/11/2008, at 0300 CDT, Technical Specification 3.0.3 was entered when excessive leakage was identified on EJ8842 RHR to hot leg injection relief valve. Due to the location in the system this leak adversely affected the operability of both RHR trains. EJHV8716A and EJHV8716B RHR Hot Leg Injection cross tie valves were closed to isolate the leak path. Technical Specification 3.5.2 does not have a CONDITION statement that addresses both RHR trains being out of service in Mode 3. "At the time of discovery the RCS was being heated towards NOP/NOT. RCS pressure was 1340 psig and temperature 504F. "The Unit is being cooled down to reenter Mode 4 at this time. When the Unit enters Mode 4 Technical Specification 3.5.3 will be in effect. Technical Specification 3.5.3 requires one Emergency Core Cooling System (ECCS) Train to be operable while in Mode 4. An operable ECCS train includes both an RHR Subsystem, and a Centrifugal Charging Pump (CCP) subsystem. The requirement to have EJHV8716A and EJHV8716B open is not applicable to Technical Specification 3.5.3. "The Unit will remain in Mode 4 until EJ8842 is restored to Operable status. "The Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-05-11
44199 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-05-09 21:30 | 2008-05-09 23:30 | 2008-05-09 | EMERGENCY SIREN OUT OF SERVICE "On March 9, 2008, Watts Bars Security staff was notified by the Rhea County Sheriff's Department that a single emergency preparedness siren had spuriously activated due to inclement weather and possible lightning strike. The county subsequently notified the Tennessee Emergency Management Agency (TEMA) who, in turn, contacted the Tennessee Valley Authority Operations Duty Specialist in Chattanooga, Tennessee. The siren has been deactivated and repairs will be initiated. Due to the interaction with the county and TEMA (State and local government agencies), this report is being made as a four hour notification under 10 CFR 50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-05-09
44198 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-05-09 14:20 | 2008-05-09 19:12 | 2008-07-01 | BOTH TRAINS OF RHR DECLARED INOPERABLE "On 05/09/2008, at 14:20 CDT, Technical Specification 3.5.3, Condition A, was entered when the 'A' Residual Heat Removal (RHR) Train was declared inoperable due to a gap in one of the 'A' Train Containment Recirculation Sump Strainer modules greater than 1/8 inch. At the time this condition was discovered, the 'B' RHR train was already inoperable for maintenance. "The Unit is in the process of being returned to service following completion of a Refueling Outage. The unit remained stable, in Mode 4, with the 'A' RHR Train inservice providing cooling for decay heat removal. Efforts to correct the gap in the 'A' Train Containment Recirculation Sump Strainer were commenced shortly after identification of this condition, and the condition was corrected and 'A' Train RHR returned to Operable status at 17:45 CDT. 'B' Train RHR is currently being restored following completion of maintenance. The Unit will remain in Mode 4 until the 'B' RHR train is restored to Operable status. "Technical Specification 3.5.3 requires one Emergency Core Cooling System (ECCS) Train to be operable while in Mode 4. An operable ECCS train includes both an RHR Subsystem, and a Centrifugal Charging Pump (CCP) subsystem. The 'A' Train CCP Subsystem remained operable." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 7/1/08 AT 1616 FROM PRESTON LAWSON TO MARK ABRAMOVITZ * * * "Wolf Creek further evaluated this condition and determined that the safety function of the containment sump was maintained under WCGS current licensing basis. Therefore the 'A' Residual Heat Removal (RHR) Train was not inoperable. Wolf Creek is retracting the notification made under 10CFR50.72(b)(3)(v)(B)." The licensee notified the NRC Resident Inspector. Notified the R4DO (Bywater). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-05-09
44197 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2008-05-09 05:25 | 2008-05-09 14:26 | 2008-05-09 | LOSS OF NUCLEAR CRITICALITY DETECTION SYSTEM FOR TWO AREAS CAUSED DURING MAINTENANCE "On 05/09/2008 at 0525 PDT during a maintenance activity, a fuse in a Nuclear Criticality Detection System cabinet failed open which caused two of the nine Nuclear Criticality Accident Alarm system coverage areas to go offline. About 5 minutes later, Security personnel made a plant wide PA announcement to suspend all movement of fissile material. The alarm horns were placed in manual mode and manual monitoring of the NCD comparator panel was established at this time and continued until the system was restored to full operation. "The safety significance is very low. Accidental nuclear criticality is highly unlikely. The system was only degraded for about 5 minutes before Security personnel made a plant wide announcement to suspend all fissile material movement. NCD coverage for the entire plant was reestablished within about 35 minutes. "Corrective Actions to Restore the Safety System and when each was implemented: - Manual monitoring of the NCD comparator panels was established at 0530 - The NCD panel fuse was replaced by 0605 restoring NCD coverage to all areas of the plant. - The alarm horns were placed back in automatic mode at 0720 and the system continued to be monitored by maintenance personnel. - Complete system operability was declared at 0730. - A plant wide PA announcement that the suspension of fissile material movement had been lifted was made at 0745." The licensee will be notifying NRC Region 2 and the State of Washington Department of Health. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-09
44196 | 0 | DOW CHEMICAL COMPANY |  |  |  |  | 2008-04-11 | 2008-05-09 13:23 | 2008-05-09 | LOST C-14 SOURCES While conducting the annual physical inventory of radioactive materials on 04/11/08, 2 samples containing a total of 10.1 milliCuries of C-14 were not able to be located. The samples were: (1) RMR 631- Methylene Bisphenyl Isocyanate (MDI) 1.1 mCi of C-14, and (2) RMR 652 - Dipropylene glycol dimethyl ether, 9.0 mCi of C-14. The samples had been present in their approved storage location during the 2007 physical inventory. All authorized users were interviewed to identify location or usage within the last year. A detailed search of all storage areas and radioisotope-approved labs was performed. Conducted a review of facility waste disposal records, and no information related to the sources location was found. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-05-09
44195 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-05-09 10:59 | 2008-05-09 13:15 | 2008-05-09 | MANUAL REACTOR TRIP DUE TO HIGH STEAM GENERATOR LEVEL "A manual trip of Salem Unit 2 was initiated due to a high water level in 23 Steam Generator. The high water level in 23 Steam Generator occurred while reducing power in accordance with the abnormal operating procedure for loss of circulating water. The operators had entered the abnormal operating procedure for circulating water due to loss of the electrical bus supplying power to the screens. The main supply breaker had tripped open due to the panel being wet from heavy rain. With the screens out of service, TWS [traveling water screen] DP's rose to a value where the circulators were removed from service per procedure. The restoration of the supply breaker is currently in progress. The cause of the high level in 23 Steam Generator during the power reduction is currently under investigation. Following the trip, 2N43, power range nuclear instrumentation channel 3, was declared inoperable due to inaccurate indication and is currently under investigation. "The crew entered EOP-TRIP-1, appropriately transitioned to EOP-TRIP-2 and stabilized the plant at no load conditions. All rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the 21 -24MS10's, the atmosphere relief valves. "The AFW Pumps were manually started as required to maintain steam generator levels. "Salem Unit-2 is currently in mode 3. Reactor Coolant System temperature is 547°F with pressure at 2235 psig. All ECCS and ESF Systems are available. "No personnel injuries have occurred as a result of the Trip. No radiological release due to this event." No Primary relief valves or PORVs lifted during the trip. There are no known fuel or steam generator tube leaks. Unit 2 is in a normal shutdown electrical lineup. Unit 1 was not affected by the transient. The licensee notified the NRC Resident Inspector. The licensee will be notifying the Lower Alloways Township. * * *UPDATE PROVIDED AT 1647 EDT ON 05/09/08 FROM JOHN OSBORNE TO JEFF ROTTON * * * The licensee called to correct the original report that stated the AFW pumps were started manually to maintain SG level. The AFW pumps started automatically due to manually tripping the 21 and 22 SGFPs. The licensee also added notification of the 8 hour Non-Emergency 10CFR50.72(b)(3)(iv)(A)-Specified System Actuation due to the automatic start of the motor driven AFW pumps. The licensee will be notifying the NRC Resident Inspector and the Lower Alloways Creek Township. Notified R1DO (Burritt) | 0 | 0 | 0 | 0 | 47 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-05-09
44194 | 0 | WASHINGTON UNIVERSITY IN ST LOUIS |  |  |  |  | 2008-05-07 16:35 | 2008-05-08 17:30 | 2008-05-08 | LOST I-125 SEEDS RSO reported that two I-125 seeds have been lost following a prostate implant procedure. Seeds have an apparent activity of 0.37 milliCuries each, and actual contained activity of 0.518 milliCuries each. Facility received 15 seeds from the seed manufacturer for a scheduled prostate implant procedure at 0900 CDT on 05/07/08. 13 seeds were implanted successfully by the authorized user. After the procedure was completed, the technologist completed surveys around the patient and in the area of the procedure. At this time, it is believed that the technologist disassembled the MIC applicator improperly and left a part in the MIC that contained the seeds. The technologist did not verify, visually or by survey, that the seeds were contained in the part of the MIC applicator that was going to storage. It is believed that the seeds went with the part of the MIC unit that went into a soap basin for cleaning and that during cycling of the plunger the seeds came out and went into the soap basin and down the drain into the buildings sanitary sewer system. The loss was not identified until 1630 on 05/07/08, when the medical physicist was going to use the two remaining seeds for other testing. Several medical physicists from Radiation/Oncology went to survey the operating room area used for the procedure and were unsuccessful in locating either seed. At 1830, Radiation Safety organization was notified and the facility continued looking for the missing seeds. A survey was performed on the drain trap area of the soap basin and no increased background was identified. The facility does not believe that the seeds will be recovered. The investigation is still ongoing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-05-08
44193 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2008-04-28 | 2008-05-08 15:18 | 2008-05-08 | KENTUCKY AGREEMENT STATE REPORT - MEDICAL EVENT - PATIENT RECEIVED INCORRECT DOSE OF I-131 A patient was prescribed a dosimetric Bexxar I-131 dose of 5 mCuries for a lymphatic cancer uptake study. The patient received an I-131 dose of 44.5 mCuries that was actually intended for another patient. The Doctor has notified the patient. The patient had taken a thyroid block prior to the misadministration. No adverse consequences are expected to the patient. The patient was subsequently given a therapeutic dose of I-131 which was adjusted to account for the misadministration of the dosimetric amount. The State of Kentucky Radiation Health Department investigation is in progress. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2008-05-14
44192 | 0 | BRIDGEPORT HOSPITAL |  |  |  |  | 2008-05-08 | 2008-05-08 09:31 | 2008-05-08 | BRACHYTHERAPY UNDERDOSE TO 2 PATIENTS The licensee discovered that 2 patients received underdoses from brachytherapy in January 2008. The underdoses were discovered May 7, 2008. The cause was related to a change in the input made to the treatment planning computer involving the magnification factor. The prescribed doses were 5500 centigray to the cervix of both patients and delivered dose was 2550 centigray. The patient's prescribing physician and oncologist have been informed and discussions are underway to determine future actions. The patients have not yet been informed. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-05-14
44191 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-05-07 11:00 | 2008-05-07 18:02 | 2008-05-07 | LOSS OF MULTIPLEXER POWER SUPPLY "Plant computer multiplexer power supply has failed resulting in a loss of some monitoring capabilities. Included are: ICRR [Inverse Count Rate Ratio], Digital Reactivity calculations, axial flux difference, meteorological inputs, main steam safety indication, source range, intermediate range, power range, and containment humidity. Control board indications remain available, for assessment of above functions." The licensee is implementing procedural compensatory measures. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-05-07
44190 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-05-06 | 2008-05-06 12:12 | 2008-05-06 | OFFSITE NOTIFICATION TO LAW ENFORCEMENT DUE TO DISCOVERY OF DECEASED INDIVIDUAL ON SHORELINE "The purpose of this report is to notify the NRC of discovery of a deceased individual along the shoreline of Detroit Edison Fermi 2 property. Specifically, at 0900 (EDT), the Fermi Control Room was notified that a deceased individual was discovered along the shore of Fermi property located outside of the Protected Area but in the Owner Controlled Area. The deceased individual is not believed to be a Fermi employee. Local Law Enforcement was notified. Michigan State Police have arrived on site. A press release is not planned at this time. "The NRC Resident Inspector has been notified." At the time of the report, the body had not been moved and the area has been restricted as a crime scene while the investigation is ongoing. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-05-06
44189 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-12-31 | 2008-05-06 11:42 | 2008-05-06 | LOUISIANA AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE The State provided the following information via facsimile: "An overexposure was discovered during a routine compliance inspection of Accurate NDE & Inspection on March 25, 2008. This overexposure was not reported to the Louisiana Department of Environmental Quality. An industrial radiographer received a dose of 7819 mrem for the calendar year 2007. The licensee has been cited for the overexposure and for not reporting the overexposure. This overexposure is being investigated by the LA Department of Environmental Quality." LA Report ID No.: LA08009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-05-09
44188 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-05-05 12:37 | 2008-05-05 17:03 | 2008-05-05 | HIGH HEAD SAFETY INJECTION MANUAL VALVE TO COLD LEG FOUND MISPOSITIONED DURING HEATUP "This is all eight-hour non-emergency reportable event to the NRCOC in accordance with 10 CFR 50.72 (b)(3)(v)(D) for a condition that could have prevented the fulfillment of a safety function. "High Head Safety Injection (HHSI) pump discharge to cold leg injection isolation valve 4-867 was discovered out of position while in a refueling outage (4-24.) The valve was discovered out of position on 5/5/08 at 12:37 and placed in its correct position, locked open and back-seated, at 13:07. Valve 4-867 is required to be locked open and back-seated when the reactor coolant system (RCS) temperature is greater than 380 degrees F, per Technical Specification 3.5.2. Unit 4 was in Technical Specification 3.0.3 (no OPERABLE cold leg injection flowpath for all HHSI pumps to Unit 4) for 30 minutes from time of discovery at 12:37 until correction at 13:07. Valve 4-867 was out of its required position for 5 hours and 26 minutes when the RCS was above 380 degrees F at 07:41 until it was correctly repositioned at 13:07." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-05-05
44187 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-05-05 03:32 | 2008-05-05 12:02 | 2008-05-05 | LOSS OF POWER TO ESF BUSES DURING TRANSFER OF OFFSITE POWER SOURCE "With Unit 3 in a refueling outage and in mode 5, as part of outage activities 4160V unit board transfers were in progress to return Unit 3 to 500KV offsite source, the 3B 4160V Unit Board failed to transfer. The loss of 3B 4160V Unit Board resulted in loss of power to 3EC and 3ED 4160V shutdown boards, 3B 480V shutdown board, 480V SBGT board, and 3B RPS. 3EC and 3ED diesel generators started and tied to the 4160V shutdown boards as required for loss of power. "Unit 3 groups 3 and 6 isolations were received as expected. An unexpected full scram was received. An invalid A IRM actuation occurred (A channel half scram) while RPS 3B bus de-energized resulting in a full scram signal. Previous to this event all control rods were already inserted. "This non-emergency event is reportable under 50.72(b)(3)(iv)(A)(h) - Any event or condition that results in valid actuation of emergency ac electrical power systems. "UNIT 3 remains in Mode 5, flooded up with fuel pool gates removed and all rods are fully inserted. 3A, 3B and 3C 4160V Unit Boards and all four shutdown boards are energized. "Units 1 and 2 were operating at 100% power and were not affected by the incident except for the common refuel zone isolation and temporary loss of control bay ventilation." The EDGs have been restored to standby and the electrical configuration has been returned to normal. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-05-05
44186 | -1 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-05-04 15:30 | 2008-05-04 22:14 | 2008-06-30 | HPCI DECLARED INOPERABLE "During the required quarterly oil sample taken following scheduled flow rate surveillance, the Unit 2 HPCI oil system was found to contain excessive amounts of water. HPCI declared inoperable. "This event is reportable under 10CFR50.72(b)(3)(v)(B), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.' "Unit 2 remains at 100% power "14 day TS LCO 3.5.1 has been entered and troubleshooting is in progress. "NRC Resident has been notified." * * * RETRACTION PROVIDED AT 1648 ON 06/30/08 FROM MICHAEL HUNTER TO JEFF ROTTON * * * "ENS Event Number 44186, made on May 4, 2008, is being retracted." "NRC Notification 44186 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were met when a required quarterly oil sample taken following a flow rate surveillance on the Unit 2 High Pressure Coolant Injection (HPCI) System indicated that the turbine oil system contained excessive amounts of water. "An evaluation performed in response to this report concluded that the HPCI System was capable of performing its intended safety function even though the turbine oil system contained more water than recommended in the TVA Lubrication Oil Analysis and Monitoring Program. TVA found through visual inspection and engineering evaluation that the amount of water contained in the turbine oil system would not impact the HPCI operation during its' mission time for the Design Basis Loss-of-Coolant Accident. "As such, the circumstances discussed in the report did not result in any condition that at the time of discovery could have prevented the fulfillment of the safety function of structures of system that are needed to remove residual heat. Thus, there was no impact on nuclear safety. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(B). "TVA's evaluation of this event notification is documented in the corrective action program. "The licensee has notified the NRC Resident Inspector." The licensee has changed the oil and continues to monitor the oil reservoir monthly until the problem causing the excessive water (Turbine Admission valve) is corrected . Notified R2DO (O'Donohue) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-05-04
44185 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2008-05-02 | 2008-05-02 19:00 | 2008-05-02 | AGREEMENT STATE REPORT - LOSS-OF-CONTROL OF RADIOACTIVE SOURCE BY NEW MEXICO LICENSEE The following information was received from the State of New Mexico via email: "A radioactive gauge was found in a Farmington, NM scrap metal facility and reported to the New Mexico Radiation Control Bureau (Bureau) on Friday, April 18, 2008. An employee at the scrap metal facility reported that a semi-truck delivering scrap metal to a Colorado metal recycler was found to have a 'hot spot'. The radioactive bale was isolated and returned to NM. "Using information from the label on the gauge, the generally licensed source was traced to a NM radioactive material licensee. The Bureau's investigation included a review of Colorado's fax of DOT-SP 10656 Shipment Approval Form (Colorado survey: 1.8 mr/hr on side of trailer), interviews with personnel at the scrap metal facility, radiation surveys of the device, and interviews with licensee personnel. The Bureau's radiation survey of the gauge indicated exposure rates of 7-10 mr/hr at contact with the source housing and 0.3-0.5 mr/hr at one meter from the source. "Discussions with licensee personnel revealed the gauge was listed on the August 20, 2007 physical inventory and the Radiation Safety Officer (RSO) had been laid off on November 7, 2007 in the midst of a scheduled outage of operations that included removal of gauges from service. It appears the gauge was removed from service and discarded with other scrap metal, arriving at the scrap metal facility sometime in late March 2008. "The gauge was retrieved by the licensee and placed in secure storage. The loss of control of the radioactive source is attributed to lack of oversight of the licensee's radiation program during gauge removal operations. Based on scrap metal facility configuration, location of the radioactive bale on the semi trailer during transport, storage of the gauge upon return, and exposure rates from the gauge, it is estimated that public dose limits were not exceeded. The NM Environment Department is evaluating enforcement actions in response to the incident." The gauge was manufactured by Kay-Ray. It has a 50 mCi Cs-137 sealed source, S/N 92B-03016 and was licensed to Public Service of New Mexico. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2008-05-07
44184 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-04-30 11:40 | 2008-05-01 18:59 | 2008-05-01 | AGREEMENT STATE REPORT - TWO ABANDONED ELECTRON CAPTURE DETECTORS The State provided the following information via facsimile: "On April 19, 2008, Urban Ore picked up a load of material from 2151 Berkeley Way, which included a gas chromatograph with an ECD [Electron Capture Detector] containing 300 mCi of Tritium. Prior to this, 2151 Berkeley Way had been sold to the University of California at Berkeley (UCB). On April 26, 2008, Urban Ore returned the gas chromatograph to the loading dock of 2151 Berkeley Way. "On April 28, 2008, the Richmond Regional Office of RHB [Radiological Health Branch] was notified. On April 28, 2008, at 1330 the UCB RSO, and other representatives from UCB met at 2151 Berkeley Way and identified a Largus Applied Technologies gas chromatograph, with an Electron Capture Detector (ECD), Model 200 within the loading dock containing approximately 150 mCi of Tritium. Smears were taken of this ECD and no contamination was found. The group inspected the parking garage inside the building and found another ECD unit, Valco containing approximately 500 mCi of Tritium and a 0.9 uCi Radium-226 button source. Smears of this ECD identified approximately 8000 dpm of contamination at the open end of small bore exhaust tubing. The ECD reportedly came from room 100C. The Largus unit was moved from the loading to the inside of the building and labeled 'do not remove.' At 1600 on April 28, 2008, the RSO asked that all recycling work be stopped in 2151 Berkeley Way. "The RHB was informed of the events of April 28, 2008, at about 1140 on April 29, 2008, which was followed by an email to RHB detailing the above at 1830 on April 29, 2008. On April 30, 2008, RHB has taken custody of the 2 ECDs, and met with the RSOs of UCB and DOL [Department of Labor] and other representatives of CDPH [California Department of Public Health]. A strategy for resolving this incident was worked out, and RHB offered full assistance to DOL." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-05-06
44183 | 0 | W.L. GORE & ASSOCIATES |  |  |  |  | 2008-03-09 | 2008-05-01 09:54 | 2008-05-01 | LOST STATIC ELIMINATOR SEALED SOURCE OF PO-210 "We [licensee] are writing to notify the NRC that W.L. Gore in Wall, NJ has lost a NUCLECEL ion air gun cartridge (P2021- 8000 NIJCLECEL Ionizing cartridge S/N A2FR150) manufactured by NRD, LLC. We [licensee] use these devices to eliminate static from our finished medical product components. The device is a fully contained sealed source alpha emitter sealed in gold and silver for maximum protection and risk minimization. The Source is Po-210 at a 10 milliCuries level. This letter is being written to comply with the requirements of 10 CFR 20.2201. "The static eliminator was lost on approximately March 9, 2008. Theft of the device is highly unlikely with no breaks on record during the period. While associates had been trained on safe care and use of the device, someone accidentally disposed of the device, and it could not be recovered. Follow-up safety training on safe use and return of the devices was conducted again in March 2008. A thorough department-wide search, including trash containers and dumpsters, was coordinated." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-05-01
44182 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-04-30 16:00 | 2008-04-30 22:52 | 2008-05-14 | TWO EMERGENCY DIESEL GENERATORS INOPERABLE "Two emergency diesel generators found inoperable while two trains of residual heat removal are required to be Operable for core cooling. "On 4/30 at 1600 it was discovered that the level in Emergency Diesel Generator Fuel Oil Storage tanks were not trending together. The two underground fuel oil tanks have a capacity of 35,000 gallons each (useable volume of 34,674 gallons). The tanks are connected with a siphon line between the tanks to ensure a passive means of transfer so one emergency diesel can use both tanks. The siphon line does not appear to be transferring fuel oil. "KPS is in a refueling outage and in REFUELING SHUTDOWN mode with the vessel drained to 6" below the flange for reactor vessel reassembly. Both trains of RHR are required to be OPERABLE per TS 3.1.a.2.B. "Technical Specification 3.7.c states that when its normal or emergency power source is inoperable, a system, train or component may be considered OPERABLE for the purpose of satisfying the requirements of its applicable LCO provided: 1. Its corresponding normal and emergency power source is OPERABLE; and 2. Its redundant system, train, or component is OPERABLE. "Kewaunee Power Station (KPS) Technical Specifications Section 3.7.a.7 states that the reactor shall not be made critical unless both diesel generators are operable. The two underground storage tanks combine to supply at least 35000 gallons of fuel oil for either diesel generator and the day tanks for each diesel generator contain at least 1,000 gallons of fuel oil. The current volume is 29,700 gallons in Tank A and 21,500 gallons in Tank B. Based on two trains found inoperable, this is reportable under: 10 CFR 50.72(b)(3)(ii) (8-Hr) 10 CFR 50.72(b)(3)(v)(B) (8-hr) "Per TS 3.1.a.2.B the condition must be fixed immediately. Troubleshooting/investigation is in progress to determine repairs. Cause is being investigated." Condition was found during engineering review of logs taken during operator rounds. The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED AT 1641 EDT ON 05/14/08 FROM JACK GADZALA TO JEFF ROTTON * * * "EN 44182 provided notification that the emergency diesel generator (EDG) fuel oil tanks were not capable of supplying the combined volume of fuel oil (35,000 gallons) from two storage tanks to either EDG as required by Technical Specification (TS) 3.7.a.7 for EDG operability. That notification was based on a conservative determination that a siphon line, which connects the two fuel oil storage tanks, was nonfunctioning. "TS 3.7.a.7 requires both EDGs to be operable when the reactor is critical. Although the reactor was in refueling shutdown mode at the time of this event (i.e., not critical, and therefore not in the mode of applicability for TS 3.7.a.7), the EDGs provide a support function (emergency power) for the Residual Heat Removal (RHR) system; two trains of which were required to be operable for core cooling per TS 3.1.a.2.B. "A subsequent review confirmed that the capability to transfer fuel from either storage tank to either EDG existed independent of the siphon line. The siphon line is not needed for transferring fuel oil from either tank to either EDG. There are alternate means available to transfer fuel oil to the EDGs; sufficient time is available to implement these alternate means of fuel oil transfer within the time available. "Additional fuel oil supply margin existed due to the mode of operation at the time (refueling shutdown). The 35,000 gallon TS requirement is based on the expected fuel consumption of one EDG operating for seven days at continuous rated load, thus ensuring adequate time to restore off-site power or to replenish fuel. The amount of fuel in the storage tanks was sufficient for the EDGs to be capable of performing their support function for RHR in the refueling shutdown mode. As such, both RHR trains remained operable and TS 3.1 a.2.B was satisfied. Consequently, this condition did not meet the reportability criteria in 10 CFR 50.72. "As a result, the notification made on 4/30/2008 (EN 44182) is hereby retracted." The licensee notified the NRC Resident Inspector. Notified the R3DO (Peterson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2008-04-30
44181 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-04-30 15:55 | 2008-04-30 18:41 | 2008-04-30 | CALCIUM CHLORIDE SPILLED ON SITE "Environmental received a call regarding an unknown substance spilled in the south east corner of the site. Environmental personnel responded and discovered approximately 300 pounds of calcium chloride, commonly known as 'Ice Melt.' The Ice Melt was on the side of the road with approximately 25% of the substance in the water of the wetlands. Clean up efforts are underway. The following local government agencies were notified: Michigan Department of Environmental Quality District Office (MDEQ), National Response Center, 911 Local Emergency Planning Committee, Pollution Emergency Alert System (PEAS)." The Ice Melt had been emptied from a facility truck onto the side of the road. The wetland empties into Lake Erie. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-04-30
44180 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-04-30 | 2008-04-30 16:35 | 2008-04-30 | EIGHT LOST PALLADIUM - 103 SEEDS The State provided the following information via facsimile: "[Florida Bureau of Radiation Control was] informed at 1600 hours that (8) Pd-103 seeds and (8) I-125 seeds, all in one box are lost. Box was labeled for a delivery to North American Scientific. Box was left in restricted area over night and was found missing the next day. Housekeeping was suspected of throwing box in the trash. Surveys were performed, dumpster was checked, and North American Scientific was contacted. No further action will be taken on this incident." Activity of Pd-103 seeds 1.2 milliCuries per seed, I-125 seeds 0.381 microCuries per seed. Licensee is retraining staff on proper disposal procedures. FL Incident Number: FL08-066 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-05-05
44179 | -1 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-04-29 23:13 | 2008-04-30 05:21 | 2008-07-31 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE DUE TO SEAL LEAK "On 04/29/08 at approximately 2313 during testing of the Unit 1 HPCI system, a main pump seal developed a leak requiring the HPCI system to be secured. HPCI testing was in progress per OPT 09.2, HPCI System Operability Test, following recent Unit 1 refueling outage. At the time of discovery, the Unit 1 HPCI system had been declared inoperable due to surveillance testing activities which removed HPCI from the standby lineup. When the pump seal leak developed, operators secured HPCI and isolated the leak by closing the pump suction isolation valves and the keep fill supply valves. Investigation into the cause of the pump seal leakage is underway and the Unit 1 HPCI system will be placed under clearance for repair. "The initial safety significance of this condition is considered to be minimal. The Reactor Core Isolation Cooling (RCIC) system as well as the other Unit 1 ECCS systems are operable at this time. Actions have been taken to protect redundant safety systems. "The Unit 1 HPCI system has been removed from service and secured. Investigation is underway to determine the cause of the HPCI main pump leakage. The HPCI system will be placed under clearance for repair." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 7/31/08 AT 1447 EDT FROM TURKAL TO HUFFMAN * * * "The HPCI pump uses seal purge water piping in combination with mechanical seals to limit shaft leakage. Investigation of this event found that inadequate post-maintenance venting of piping between the discharge of the HPCI booster pump and the suction of the HPCI main pump led to the seal faces overheating and subsequent failure. The failure of the seal and the leakage associated with it would not have prevented HPCI from performing its required functions. Water intrusion into the oil system is the limiting impact of the seal failure. The HPCI main pump seal failure event has been evaluated and it was determined that, given a worst-case seal failure, the HPCI pump would be able to operate for greater than the required 4.1 hours and, thereby, satisfy its accident, as well as transient, response requirements. On this basis, the HPCI system was capable of performing its function to mitigate the consequences of an accident and the issue is not reportable under 10 CFR 50.72(b)(3)(v)(D). "Investigation of this condition is documented in the corrective action program in Nuclear Condition Report (NCR) 277188. "The NRC resident was notified of this retraction." The R2DO (Henson) has been notified. | 32 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-04-30
44178 | 0 | FAIRBANKS MORSE |  |  |  |  | 2008-04-29 | 2008-04-29 15:29 | 2008-04-29 | PART 21 NOTIFICATION REGARDING IDENTIFICATION OF DEFECT ALCO SNUBBER VALVE MICRO-CRACKING The reporting organization provided the following information via facsimile: "Name and address the individual or individuals informing the Commission. Mr. Dominic Dedolph, Manager, Quality Assurance, Fairbanks Morse Engine, 701 White Avenue, Beloit, WI 53511. "Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: Facility- Entergy (Indian Point). "Basic component which fails to comply or contains a defect: ALCO Fuel Snubber Valve P/N 2402466-1. The snubber valves in the Emergency Diesel Generator are installed in the high pressure fuel line between the fuel injection pump and the injection nozzle and serve as a pulsation dampener. "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. Nature of defect: Fairbanks Morse Engine (FME) evaluation has determined that a potential safety hazard exists for ALCO fuel injection snubber valves due to micro-cracking in the tip of the snubber valve created during the material surface hardening process when the tips of the snubber valve were quenched in water. "Safety hazard which could be created by such defect: Micro-cracking in the tip of the snubber valve could potentially lead to material flaking . It has been postulated that the flakes (or particles) could be flushed downstream and become lodged in the nozzle, causing excessive fuel to enter the combustion space and wash the cylinder liner dry and lead to a piston seizure. "The date on which the information of such defect or failure to comply was obtained. Deviation discovered on February 29, 2008. Evaluation completed on April 28, 2008. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. Root cause analysis was performed and found that water quenching during the heat treatment process resulted in approximately 40% of the tips of the snubber valves to have micro-cracking present. When oil was substituted for the quenching medium, no snubber valves showed any signs of micro-cracking. The heat treatment process documentation has been updated to specify the quenching medium as oil. Oil has been used exclusively in the heat treatment process of all snubber valves produced by FME since March 1, 2008. "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. FME is notifying Entergy (Indian Point) of the twelve (12) suspect pieces." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2008-04-29
44177 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-04-23 | 2008-04-29 15:03 | 2008-04-29 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE This incident was originally reported in Event Notification #44159 by the licensee due to the uncertainty of the location of the potential overexposure. The State provided the following information via facsimile: "On April 23 2008, [DELETED] (RSO) with Global X-Ray & Testing (GXT) reported an excessive exposure on an industrial radiographer's badge. Landauer contacted GXT and reported that a badge had a reading over 1000 rads. The radiographer in question was interviewed by [DELETED] and a LA Department of Environmental Quality inspector. The radiographer was very shocked to hear of the excessive exposure. He was asked if anything unusual occurred during the month. The radiographer did not think anyone exposed the badge intentionally. The radiographer did state that he could not find his badge one morning on a job that occurred on March 20 - 24, 2008. The radiographer had a physical and blood work performed. The physical included CBC and total Lymphocyte count. The blood work came back within normal limits. This incident is still under investigation by the Louisiana Department of Environmental Quality." Louisiana Report: LA080008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-05-02
44176 | 0 | WALMART |  |  |  |  | 2008-04-25 | 2008-04-29 15:10 | 2008-04-29 | TWO TRITIUM EXIT SIGNS CRUSHED IN TRASH COMPACTOR The licensee reported that one of their employees placed two tritium exit signs in a trash compactor at one of their stores and compacted them. The licensee has tagged out the affected trash compactor and notified representatives of the Commonwealth of Virginia and Region I. The signs are approximately 11.5 Curies each. The Commonwealth is sending representatives to evaluate the radiological condition and assist in the removal and disposal of the devices. The licensee notified Region 1(Joustra). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-04-29
44175 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-04-29 07:50 | 2008-04-29 12:38 | 2008-04-29 | LOSS OF TSC VENTILLATION DURING SCHEDULED MAINTENANCE "This notification is to report a Loss of Emergency Preparedness Capability in accordance with 10 CFR 50.72(b)(3)(xiii). "At 0750 CDT on 4/29/08, the Technical Support Center (TSC) Ventilation System was removed from service for a scheduled surveillance procedure (SP 1738) to replace charcoal filters and measure the cleanup efficiency. It is scheduled to be returned to service on 5/1/08 [at approximately 1500 CST]. The TCS ventilation system is now considered non-functional. The TSC will be staffed in the event it is needed and radiological conditions monitored. If radiological conditions require actions, procedure F3-6, 'Activation and operation of the TSC,' Section 7.6 directs the TSC management to relocate TSC activities to a radiological safe area if necessary." Alternate facilities are available. The Licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-29
44174 | 0 | CHURCH OF JESUS CHRIST LDS |  |  |  |  | 2008-03-07 | 2008-04-29 09:18 | 2008-04-29 | STOLEN TRITIUM EXIT SIGNS The licensee reported that on the night of 3/7/08 the church was broken into and vandalized. As part of the vandalism, 2 self-illuminating exit signs were stolen. The signs were not recovered. The licensee did not discover that the theft of the signs was reportable until 4/29/08. It is not known if the signs were broken during the vandalism. The areas around both signs have been cleaned since the theft. The manufacturer is SRB Technologies (Canada), Inc. Model: BetaLux-E/Luminexit, Activity: 20 Ci each, the serial numbers are not known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-04-29
44173 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-02-07 | 2008-04-28 17:15 | 2008-04-28 | AGREEMENT STATE REPORT - MEDICAL DOSE NOT IN ACCORDANCE WITH WRITTEN DIRECTIVE "On Friday April 25, 2008 at approximately 1700 hrs, the Pennsylvania Bureau of Radiation Protection's Central Office Licensing Section was notified by [REDACTED] of a Medical Reportable Event that occurred on February 7, 2008 at Geisinger's Wyoming Valley Hospital located at 1000 East Mountain Drive in Wilkes Barre, PA. (License #37-01421-01; PA-0006) The event was not discovered until Friday April 25, 2008 during a licensee review of Written Directives administered. "Licensee stated that the written directive for an I-131 treatment of a hyperactive thyroid was incorrectly written as 10 microcuries (0.37 MBq). Licensee stated that the nuclear medicine technician either did not read the directive or misread the directive and administered 10 millicuries. Licensee stated that the dose administered was appropriate for the treatment, however, inconsistent with the written directive. The prescribing physician was notified on the date of discovery. Licensee stated that no adverse health effects are expected as a result of this error. The error most likely occurred because the most common prescriptions for this sort of treatment are 10 - 20 mCi (370 - 740 MBq) I-131 and the technician did not recognize that the written directive stated 10 uCi (0.37 MBq). "Licensee stated that actions taken to prevent recurrence had not been undertaken at the time of report. Licensee will be sending a written report to PA DEP's SCRO. "The above information was reported to [REDACTED] PA DEP BRP Director on 4/28/2008." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2008-05-04
44172 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-04-26 13:18 | 2008-04-26 15:41 | 2008-04-26 | UNANALYZED CONDITION DISCOVERED DUE TO IMPROPERLY INSTALLED FUSE WIRING IN CLASS 1E AIR CONDITIONING UNIT "While trouble shooting, it was discovered that fuses for a remote switch to start the 'B' Class 1E air conditioning unit were installed in series and therefore not installed per design. Drawings show these fuses wired in parallel, rather than in series. In the series configuration, if an electrical short occurs on the Control Room side of the circuit and blew the fuse, the 'isolated' portion of the circuit, fed from the next fuse, would also loose power. Therefore, the circuit could not be re-energized and the unit could not be started in the event of a Control Room Fire. "The Class 1E electrical equipment air conditioning units are included in the post fire safe shutdown design to ensure adequate room cooling for the operating train of safety related electrical equipment. The air conditioning units provide a support function for Class 1E electrical equipment required for safe shutdown. The loss of the Class 1E air conditioning units does not directly result in loss of capability to achieve and maintain safe shutdown in the event of a fire. Rather, room heating beyond design limits could reduce the life of electrical components within the switchgear. "Qualification data exists to show that some components within the switchgear will survive the expected room temperatures and be functional following a loss of room cooling. Data does not exist for each and every component within the switchgear, so a conclusive argument cannot be made regarding equipment functionality following a loss of room cooling. Therefore, this condition resulted in an unanalyzed condition that could potentially affect post-fire safe shutdown equipment availability. "There are no compensatory measures required since the unit is not operating. The configuration will be corrected prior to changing to mode 4." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-04-26
44171 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-04-25 22:10 | 2008-04-26 05:11 | 2008-04-26 | NON-ISOLABLE RCS BOUNDARY LEAKAGE FROM INSTRUMENT LINE "On April 25, 2008, DC Cook Unit 1 was in Mode 4 heating up the RCS after a refueling outage. Personnel were performing a containment walkdown, with the RCS at 1000 psig, looking for leakage. Wisps of steam were seen coming from a 3/4 inch RCS flow instrument line weld, between the RCS loop piping and the instrument isolation valve. The leakage is less than 0.1 gpm. The leakage can not be isolated from the RCS and has been declared to be RCS Pressure Boundary Leakage. Entry into the RCS Operational Leakage Technical Specification, 3.4.13, was made at 2210 on April 25, 2008. This Technical Specification requires being in Mode 5 within 36 hours. "The plant is cooling down and depressurizing as required by Technical Specifications. "The plant is currently evaluating the appropriate repair method for this condition. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-04-26
44170 | 0 | CONSTRUCTION ENGINEERING LABS |  |  |  |  | 2008-04-25 16:00 | 2008-04-25 22:52 | 2008-04-28 | LOST TROXLER DENSITY GAUGE A technician for the licensee was taking asphalt density measurements at the Lua Lua Lei Naval Magazine Base in Hawaii. He was using a Troxler 3450 gauge (nominal 8 mCuries Cs-137 and 40 mCuries Am-241/Be) which was placed in the back of his pickup truck in anticipation of taking additional measurements. He was subsequently informed that no additional density measurements were needed. He completed his paper work and got into his truck and drove off the site. He drove about 1 mile before he realized that he had not secured the gauge in the back of the truck. He stopped and discovered the gauge was missing and had apparently fallen out of the truck bed. He retraced his route but was not able to locate the gauge. The RSO is in the process of requesting assistance from local authorities in helping to locate the missing gauge. * * * UPDATE FROM R. PICKERING TO JOE O'HARA AT 1646 ON 4/28/08 * * * The Troxler gauge was found in a brush area near the side of the road. The case is damaged, and the RSO will be performing a radiological assessment of the damaged case and reporting the results to Troxler for further shipping instructions. Notified R4DO(Pick), FSME(Hsueh), and ILTAB (e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-04-25
44169 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-04-25 17:30 | 2008-04-25 22:55 | 2008-04-25 | EMERGENCY RESPONSE DATA SYSTEM OUTAGE "Limerick Generating Station experienced a loss of the Emergency Response Data System (ERDS), which provides real time plant data to the NRC Operations Center, from approximately 17:30 until 21:30 on 4/25/08. The plant monitoring system (PMS) and Safety Parameter Display System (SPDS) in the main control room were functional for the duration that ERDS was out of service, providing the Limerick Operators with all required data for monitoring the plant had an actual event occurred. In addition, all external phone lines were functioning to allow contact with the NRC Operations Center had an actual event occurred." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-25
44168 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-04-25 11:30 | 2008-04-25 18:29 | 2008-04-25 | NON-CONSERVATIVE CORE SPRAY FLOW IN DRESDEN NUCLEAR POWER STATION LOCA ANALYSIS "Exelon Generation Company, LLC (EGC) has been informed of a change in the vendor calculation of Peak Cladding Temperature (PCT) for Dresden Nuclear Power Station (DNPS) Unit 2. On April 24, 2008, Westinghouse initially notified EGC of a potential non-conservatism with respect to the assumed core spray (CS) flow in the Westinghouse 10 CFR 50, Appendix K LOCA analysis for DNPS Unit 2. Based on further discussions with Westinghouse, EGC confirmed the error on April 25, 2008, at 1130. In selecting the limiting plant configuration for the DNPS Appendix K LOCA model, Westinghouse used the net flow at the CS sparger, instead of the runout flow minus leakage outside the shroud. As a result, Westinghouse used an incorrect input for CS flow for the ECCS LOCA analysis. "Westinghouse has evaluated the impact of correcting the assumed CS flow on the DNPS Unit 2 limiting large break LOCA analysis. Preliminary results indicate an increase of 80 degrees F in the PCT value. This results in a final PCT value of 2230 degrees F, which is in excess of 10 CFR 50.46 (b)(1) limits. However, preliminary calculation results also indicate that a 3 percent reduction in the MAPLGHR limit would offset the 80 degree F increase in the limiting PCT. Dresden Unit 2 has been operating with more than 3 percent margin in MAPLHGR since November 2007 (i.e., the start of the current operating cycle - D2C21). "Administrative limits wilt be established to maintain these margins. "The LOCA analysis of record for DNPS Unit 3 utilizes the correct CS shroud leakage and CS flow delivered to the vessel through the CS sparger. Therefore, this non-conservatism does not affect DNPS Unit 3. "Currently, there is sufficient operating margin for DNPS Unit 2 to ensure the PCT limit would not be exceeded. There are no other 10 CFR 50.46 ECCS criteria for DNPS Unit 2 that are impacted. "This notification is being made as a result of the 10 CFR 50.45 (a)(3)(ii) requirement to report this issue in accordance with 10 CFR 50.72 (i.e., 10 CFR 50.72(b)(3)(ii)(B)). "The licensee notified the NRC Resident Inspector." | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-04-25
44167 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-04-25 | 2008-04-25 10:55 | 2008-05-24 | PENNSYLVANIA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The State provided the following information via email: "The RSO for Applied Testing and Authorities (37-30701-01), Bridgeport, [PA] reported [to the State of PA] that their Troxler Model 3411 portable moisture-density gauge, containing about Cs-137 (44mCi) and Am-241 (9 mCi), was stolen from a street outside an employee's home at 502 Dickinson Street in Philadelphia. It was stolen between 8:30 last night and 6:45 this morning. The RSO indicated that the gauge was stolen from a locked box which was double-chained to a flat-bed truck. It was noticed that the gauge was missing this morning. "The Philadelphia Police Department was notified of the incident by the licensee and has responded to the area. "[State of PA] will be doing an inspection of the licensee this afternoon." ** UPDATE FROM DAVID ALLARD TO JOHN KNOKE AT 10:16 EDT ON 05/23/08 ** State connected with Philadelphia Police detective and licensee's RP Manager. The police have the Troxler gauge. Licensee's staff will go into town to make sure the gauge isn't damaged and leaking, and then take it back to their shop and secure it. Notified R1DO (Mel Gray) FSME DO (Patrice Bubar), ILTAB (Matt Hahn) via email THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2008-04-30
44166 | 0 | HIGH MOUNTAIN INSPECTION SERVICES |  |  |  |  | 2008-04-25 | 2008-04-25 10:54 | 2008-04-25 | POTENTIAL OVEREXPOSURE DURING MONTH OF FEBRUARY 2008 Landauer notified licensee today at 0840 MDT that a dosimetry badge worn by one of their employees in the month of February 2008 read 6429 mR. The employee only worked for 3 days on several jobs where he could have received radiation exposure during the month. The employee has been suspended from any further work that could cause additional exposure until the investigation is completed. The licensee's exposure records show that the employee only received 50 mR from pocket dosimeter. The licensee is launching an investigation as to where the potential overexposure may have occurred and compare to other personnel that worked on the same jobs. The licensee notified NRC Region IV personnel (V. Campbell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2008-04-25
44165 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-04-25 02:56 | 2008-04-25 10:39 | 2008-06-23 | BOTH EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE "On 4/24/2008 at 0110 CDT, a concern with the flexible connection alignment between heat exchangers on the 'A' Emergency Diesel Generator was identified. At the time this condition was identified the 'A' Diesel was out of service for outage maintenance activities. During evaluation of this condition, and discussions with the vendor supplier for this flexible connection, additional questions arose and the condition of the identical connections on the 'B' Emergency Diesel Generator was questioned. Inspection of the 'B' Emergency Diesel Generator identified a similar problem, and at 0256 CDT on 4/25/2008, the 'B' Emergency Diesel Generator was declared inoperable, and the Plant entered TS 3.8.2, Condition B, for one required Diesel Generator being inoperable. All required actions regarding TS 3.8.2 have been complied with. "The 'B' Emergency Diesel Generator is still considered to be functional, and remains aligned for automatic start. The 'A' EDG is currently tagged out and work is ongoing to correct the alignment issue. Upon completion of repair to the 'A' EDG it will be restored to operation and the 'B' EDG will be removed from service to correct the alignment issue. "The plant is currently in Mode 6, with RCS level greater than 23 feet above the Reactor Vessel Flange, and both required Offsite Power Sources remain operable." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY LANCE LANE TO JASON KOZAL AT 1254 ON 6/22/08 * * * "Testing, conducted by the vendor, was performed on the flexible connections in the configuration found at Wolf Creek and in a worst case configuration. The joints were tested, up to design pressure with a joint movement equivalent to a design bases earthquake, without failing. Additionally, the joints were pressurized to burst pressure, which was determined to be greater than 5 times the design pressure of the connection. The testing showed that even though the joints were not installed in accordance with the vendor's recommendation they would have fulfilled their safety function as installed. Therefore, a condition that could have prevented fulfillment of a safety function did not exist. Wolf Creek is retracting the 50.72(b)(3)(v)(B) notification." The licensee notified the NRC Resident Inspector. Notified R4DO (Proulx). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-04-25
44164 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2008-04-24 13:45 | 2008-04-25 10:03 | 2008-04-25 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE "The SC Department of Health and Environmental was notified on Thursday, April 24, 2008, at 1425 hrs, that a Humboldt Model EZ 5001, s/n 1931, containing 10 mCi of Cs-137 and 40 mCi of Am-241:Be, had been damaged at 1345 hrs on April 24, 2008. The Construction Services Manger [licensee] stated that a gauge had been damaged by the authorized user's vehicle. [State] Duty Officer responded to the scene and arrived at 1611 hrs. The area around the gauge had been properly roped off and the source rod was locked in its shielded position. The gauge handle and rod had been snapped off at the top of the gauge. The gauge was secured in the transport container and the inspector advised licensee to return the gauge to the permanent storage location, secure it from further use, and to contact the gauge manufacturer for further instruction regarding disposal. "Licensee was advised by state Duty Officer to submit a written report detailing this event to the Department within 30 days. The event is open and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2008-04-30
44163 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-04-23 23:58 | 2008-04-24 03:15 | 2008-04-24 | HYDRAZINE LEAK INTO STORM DRAIN "At 2340 on 4/23/08 a leak was discovered on a house heating steam boiler that was secured and cooling down. The boiler had been secured at 1930 and there was no leakage noticed at that time. The leak was estimated at 2 gallons per minute. At 2358 it was discovered that this water had reached a storm drain on site. The water contained hydrazine at a concentration of 364 ppb. A 15 minute notification to the state of New Jersey was completed at 0012 in accordance with the plant's Event Classification Guide. Maintenance personnel called to the scene stopped the leak at 0019. Samples are in progress of the sites storm drain outfalls to determine the extent of the discharge. This report is made in accordance with RAL #11.8.2.a." The licensee will notify local township. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-04-24
44162 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2008-04-23 12:08 | 2008-04-23 16:03 | 2008-04-23 | OFFSITE ASSISTANCE REQUESTED DUE TO UTILITY POLE FIRE OUTSIDE THE PROTECTED AREA "On April 23. 2008 at 1150, Clinton Power Station (CPS) Main Control Room received notification from a site employee that a utility pole on the 138 KV line North of the main parking lot was on fire. Ameren/IP was contacted. "At 1155, Ameren/IP de-energized the 138kV line. "Offsite assistance was requested from the Local Fire Department at time 1206. "At time 1256, the offsite Fire Department extinguished the fire. "Clinton Power Station remained online at full electrical load during the event and remains stable. Repairs are in progress, with an expected completion this evening. "The NRC Resident Inspector has been informed." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-04-23
44161 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2008-04-23 10:00 | 2008-04-23 15:46 | 2008-04-23 | NON CRITICAL-SAFE CONTAINER BROUGHT INTO SAFE STORE AREA "A 35 quart mop bucket was brought into a safe store, cleaning area where clean up work is being done to decontaminate old, previously cleaned (safe store), equipment for removal from the facility. This mop bucket is unauthorized for use in this area. "The mop bucket was removed from the area and a review of the facility is being conducted for the presence of additional unauthorized mop buckets. "GNF is making this 24-hour report in accordance with 10 CFR 70, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of § 70.61. "There were no actual or potential safety consequences to workers, the public, or the environment. "[The licensee considers this event is of] minor safety significance. No safety equipment impacted. Investigation of event and implementation of additional corrective actions pending." The licensee plans to notify the State and NRC Regional Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | DEV FROM ISA | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(5) |  |  |  | 0 | 2008-04-23
44160 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-02-23 | 2008-04-23 13:44 | 2008-04-23 | 60-DAY VERBAL NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "On February 23, 2008, a control room operator was aligning the Containment Purge system for Train B operation and triggered an invalid Containment Vent Isolation (CVI) and Auxiliary Building Isolation (ABI). The operator was removing Train A of the system from operation in accordance with system Operating Instruction (SOI) 30.02, 'Containment Purge System'. The operator made an incorrect assumption that a portion of SOI 90.02, 'Gaseous Process Radiation Monitors', that would have properly blocked and aligned power to the Purge Radiation Monitors had been performed. Therefore, when the operator proceeded with the next step in realigning the radiation monitors, a spike occurred on Radiation Monitor 1-RM-90-131. This caused an invalid actuation of Train B of the CVI and ABI systems. Operators verified the isolation and its cause, and suspended movement of irradiated fuel within the Spent Fuel Pool in response to the Train B CVI/ABI signal. The ABI/CVI signal was reset and Auxiliary Building ventilation was restored in accordance with SOI 30.05, 'Auxiliary Bldg HVAC Systems'. "The following information addresses the criteria for a 60 day verbal report defined in Section 3.2.6, 'System Actuation' of NUREG 1022, 'Event Reporting Guidelines 10 CFR 50.72 and 50.73'. This telephone notification is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A). "(a) The specific train(s) and system(s) that were actuated: The spike on the Radiation Monitor initiated an invalid actuation of Train B of the CVI system and ABI system. (b) Whether each train actuation was complete or partial: The Train B CVI and ABI actuation was complete. (c) Whether or not the system started and functioned successfully: The system started and functioned successfully, and all components operated as expected." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-04-23
44159 | 0 | LOUISIANA GLOBAL XRAY AND TESTING |  |  |  |  | 2008-03-01 | 2008-04-23 10:51 | 2008-05-19 | POTENTIAL OVEREXPOSURE GREATER THAN 1000 RADS Louisiana Global X-ray and Testing called to report a potential overexposure after consulting with Region IV. Apparently, Landauer notified them that a dosimetry badge worn by one of their employees in the month of March 2008 read greater than 1000 Rads. The licensee is launching an investigation as to where the potential overexposure may have occurred. The affected employee worked both in the State of Louisiana and offshore. The licensee notified Region IV (Leonard Wert) and the State of Louisiana. * * * UPDATE ON 5/19/2008 AT 1039 FROM W. JOHNSTON TO M. ABRAMOVITZ * * * The State provided the following information via facsimile: "On 4/23/2008, we [Louisiana Global X-ray and Testing] reported an exposure in excess of 1000 rads. Investigation proved that the individual did not receive the exposure, that the TLD received the exposure. This was determined through blood tests to the individual that was assigned the exposed TLD. "The Doctor here [Louisiana Global X-ray and Testing] and a Doctor at ReACT( ORNL) reviewed the lab results and both concurred that the individual did not receive the exposure. "During the investigation it finally came to light that the individual had found his TLD at the end of a work shift in a pipe yard here in south Louisiana. The individual finally confessed that he failed to report the incident to anyone. He figured he had just dropped it when he found it." Notified the R4DO (Proulx) and FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2008-04-23
44158 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-04-22 09:00 | 2008-04-23 08:45 | 2008-05-29 | IMPROPERLY INSTALLED STEEL ANGLE SUPPORTS ON FREEZER SUBLIMER VESSEL "At 0900 CDT on 04-22-08, the Plant Shift Superintendent (PSS) was notified that the weight monitoring systems on vessels 2 on C-333 Unit 1 Cell 9, Unit 2 Cell 2, Unit 4 Cell 2 and Unit 4 Cell 9 freezer-sublimers showed weight changes when improperly installed steel angle supports welded to the vessel inlet piping were cut free. Each freezer sublimer vessel has a weight monitoring and trip system (high-high weight trip system) that prevents the over-filling of UF6 into the vessel. The high-high weight trip system is required by TSR 2.4.3.1 to prevent overfilling the freezer-sublimer vessels when in mode F/S 1 (freeze) or F/S 3 (cold standby). At the time of discovery, each freezer sublimer was in a non-applicable TSR mode F/S 6 (out-of-service). However, each freezer-sublimer has been routinely operated in TSR modes F/S 1 and F/S 3 over several years with the steel angle supports installed. "The steel angle supports were likely installed to facilitate piping alignment during freezer-sublimer construction over fifteen years ago. The steel angle supports were not removed after construction. The presence of the steel angle supports may affect the performance the high-high weight trip system specified in TSR 2.4.3.1. All other installed freezer-sublimers were inspected and no additional steel angle supports were similarly connected. Engineering personnel are conducting a formal stress analysis to determine the stresses the steel supports may have had on the weight monitoring and trip system. There is no evidence that the weight limits specified in TSR 2.4.3.1 have been exceeded as a result of this issue. "Pending further analysis, this event is conservatively being reported as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. " PGDP Assessment and Tracking Report No. ATRC-08-l 183; PGDP Event Report No. PAD-2008-12; Worksheet No. 44158 The NRC Senior Resident Inspector has been notified of this event. * * * RETRACTION ON 5/29/2008 AT 1815 FROM BILLY WALLACE TO MARK ABRAMOVITZ * * * "Retracted on 5/29/08, engineering calculations show that the error from the supports was less than the margin provided in the setpoint calculations." The licensee notified the NRC Resident Inspector. Notified the R2DO (Widman) and NMSS (Stablein). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-04-23
44157 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-04-23 04:10 | 2008-04-23 05:15 | 2008-04-23 | TSC VENTILATION SYSTEM CONSIDERED NON-FUNCTIONAL "At 0410 CDT on 4/23/08 the Technical Support Center (TSC) Ventilation System was removed from service for scheduled maintenance on the Technical Support Center (TSC) cleanup fan. Without adequate flow rates through the TSC cleanup filter, the TSC ventilation system is considered non-functional. Due to the extent of planned work, prompt restoration of the ventilation system will not be available. Contingency plans are in place to utilize the TSC as long as radiological conditions allow. Procedure F3-6, 'Activation and Operation of the TSC', Section 7.6, directs TSC management to relocate TSC activities to a radiological safe area if necessary. The TSC Ventilation system expected return to service is 1200 CDT 4/23/2008." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM WAYNE EPPEN TO HOWIE CROUCH VIA TELECON AT 1538 EDT ON 4/23/08 * * * The TSC ventilation system will remain out of service until approximately Friday, April 25, at 1500 CDT. This is due to unforeseen degradation of the ventilation fan motor. The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Jamnes Cameron) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-23
44156 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-04-17 | 2008-04-22 19:40 | 2008-06-11 | WASHINGTON AGREEMENT STATE REPORT - EXTERNAL CONTAMINATION ON A TRANSPORT TRAILER The following information was received from the State of Washington via e-mail: "Tritium (H-3) contamination was found on a trailer in the outside storage area of Perma-Fix Northwest (PFNW), a radioactive material licensee in Richland Washington on April 17. A DOH inspector noticed liquid dripping from a trailer that had just been unloaded. The trailer had hauled empty radioactive waste drums from Atomic Energy Limited Canada (Chalk River facility in Ontario). The transport vehicle entered the United States at Sault Ste. Marie, Michigan under a Nuclear Regulatory Commission (NRC) import license and entered Washington at Spokane. The shipment had arrived at the PFNW facility in late February. It was manifested as a plastic fiber bag with drums inside. Initial surveys on February 28 noted tritium contamination inside the plastic fiber bag, but no contamination was noted outside the bag or on the trailer. Tritium was a primary radionuclide on the manifest. During off-loading of the drums and plastic liner on April 17, liquid was found in and on the drums (one drum is suspected of being at least partially filled with liquid). After off-loading, standing liquids were noticed by the licensee on the inside trailer bed, but not on the outer trailer floor and skin. After the truck was returned to the storage yard, liquid droplets were found dripping from the front of the trailer by the DOH inspector. Initial contamination levels (up to 1.8 million dpm of tritium) on the trailer front were substantially above the U.S. Dept of Transportation limits; but due to the limited quantity (less than one gallon of liquid), does not pose a health risk. There is no indication of leakage during the actual shipment. "The manifest indicated the total shipment contained H-3 (6.59 mCi) and Cs-137 (7.79 mCi) as the predominant radionuclides. Only tritium contamination has been noted." WA Report # WA-08-025 * * * UPDATE FROM MIKEL ELSEN TO KARL DIEDERICH VIA E-MAIL AT 1538 ON 6/11/08 * * * The trailer was decontaminated and the associated waste will be disposed or processed. The soil under the trailer was removed and packaged for treatment or disposal. The shipper and broker were issued notices of violation. The cause of this incident was poor oversight during packaging. Notified R4DO (G. Miller) and FSME EO (A. Mauer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-04-25
44155 | 0 | NTH CONSULTANTS |  |  |  |  | 2008-04-22 | 2008-04-22 13:27 | 2008-04-22 | LOSS OF CONTROL OF TROXLER MOISTURE DENSITY GAUGE The licensee employee transporting a Troxler moisture density gauge was transiting on DE 896 along Cobbler Creek Curve at approximately 2030 on 4/21/08 and was involved in a severe car accident. The State Police and emergency medical services responded to the scene. The employee was incapacitated and transported to the hospital. The responders were unaware of the presence of the Troxler and had the vehicle towed to a towing yard for storage. The licensee RSO learned of the accident at approximately 1145 and immediately contacted the Delaware State Police and local law enforcement (Newcastle County Sheriff). The licensee was given the contact information of the towing yard and proceeded to contact the towing yard staff. The licensee informed the towing yard of the situation and requested that a visual inspection be performed of the external integrity of the container. The results of the inspection were that the gauge remains chained to the bed of the truck and the container appears to remain secure. The licensee requested that the towing yard keep the area around the vehicle clear of personnel. The company local RSO in Pennsylvania is enroute to the vehicle and will perform a field leak test on the gauge upon arrival. Troxler information (SN 32643 - Source Strength 8 mCi Cs-137 and 40 mCi Am/Be). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2008-04-22
44154 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-04-22 08:41 | 2008-04-22 12:58 | 2008-04-22 | LOSS OF SAFETY FUNCTION DUE TO BLOWN FUSE "At 0841, the Control Room received an alarm indicating an issue with the CD481 1E inverter. Upon walkdown, it was noted that the main power fuse had failed and the inverter channel was powered from a backup non-1E AC source. IAW HCGS procedures, the C EDG was declared inoperable because it would not start in response to a LOCA signal. Electrical output of the CD 481 inverter was available through the event and no transient or actuations occurred. "All require Technical Specification surveillance tests for TS 3.8.1 were completed within the required time-frame. "Additional equipment that was tagged for scheduled maintenance included the D EDG which is currently in an outage window and inoperable. This resulted in 2 of the 4 HCGS EDGs inoperable. With the C and D EDGs inoperable, both Control Room Emergency Filtration Systems (CREF) would be without diesel back-up power supplies in the event of a LOCA and thus inoperable. With no operable CREF systems, Technical specification 3.0.3 applies. A loss of both CREF systems would constitute a loss of function of a safety system designed to mitigate the consequences of an accident (10 CFR50.72(b)(3)(v)(D)). "Replacement of the CD481 1E inverter main power fuse and assessment of inverter function was completed at 10:36. The inverter was placed back in its normal alignment. All related Technical Specification equipment is operable with the exception of the D EDG, which remains in the scheduled maintenance outage. " The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-04-22
44153 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2008-04-21 11:25 | 2008-04-21 14:24 | 2008-04-21 | MANUAL REACTOR TRIP DUE TO LOWERING STEAM GENERATOR WATER LEVEL "On April 21 2008, at approximately 1123 hours, during power ascension from a scheduled refueling outage, Unit 2 experienced an inadvertent main turbine runback. The runback initiated for unknown reasons from an initial reactor power of approximately 37%. As a result of the runback, operators observed decreasing steam generator levels and initiated a manual reactor trip at 1125 hours. As a result of the reactor trip, the auxiliary feedwater pumps actuated on a low steam generator level as designed. Prior to the runback, one of two main feedwater pumps was operating. The unit is stable and in Mode 3. Operators closed the main steam isolation valves as a result of indications of lowering RCS temperature. A 4-hour non-emergency notification is provided for a reactor trip while critical and 8 hour non-emergency notification is provided for a valid actuation of the auxiliary feedwater system." All rods inserted as expected. Decay heat is being removed by AFW through the atmospheric steam dumps. Offsite power is in a normal configuration. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 37 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-04-21
44152 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2008-04-20 22:16 | 2008-04-21 00:37 | 2008-04-21 | UNIT 1 MANUAL REACTOR TRIP DUE TO MAIN TURBINE VIBRATIONS "While ramping the Unit 1 Turbine following a forced unit outage, vibrations on the number 4 bearing increased to 13.9 mils. The ramp was stopped and a rapid load reduction was initiated. Due to sustained vibrations (>14.1 mils) after ramping the turbine down, the Unit 1 reactor was manually tripped. Unit 1 has been stabilized at Hot Shutdown. "All three auxiliary feedwater pumps automatically initiated as designed on low-low steam generator level following the trip. Currently RCS temperature is being maintained stable at 547 degrees. All systems functioned as required following the reactor trip. There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. This event is being reported in accordance with 10 CFR 50.72 (b)(2)(iv) and 10 CFR 50.72 (b)(3)(iv)." Upon exiting the refueling outage in 11/07 the main turbine had a vibration issue of about 11 or 12 mils. Decay heat is being removed via the steam dumps to the condenser. Unit 2 was not affected during this event. Offsite power was lined up normally. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 37 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-04-21
44151 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-04-17 16:44 | 2008-04-18 14:45 | 2008-04-18 | 24-HOUR NRC BULLETIN 91-01 REPORT INVOLVING AN EXCESSIVELY LARGE CONTAINER FOUND IN A FISSILE CONTROL AREA "An open and unattended Rad bag (greater than 5.5 gallon capacity), containing a valve stem fixture, was found in the C-400 G-17 valve disassembly FCA (Fissile Control Area) in violation of NCSA GEN-015. NCSA GEN-015 limits the volume of portable containers taken into an FCA to less than 5.5-gallons. The purpose of the requirement is to limit the accumulation of fissile waste to approved containers. Although NCSA GEN-029 allows the use of larger than 5.5-gallon containers for small equipment items, these containers are required to be fastened or taped closed or attended while open. This bag was not fastened / taped and was unattended. "The valve stem fixture had been placed within the Rad bag for contamination control purposes while being transported into the area. The fixture contained no fissile material; there was no fissile equipment within the FCA; and no fissile work being performed within the FCA. "The NRC Senior Resident Inspector has been notified of this event." "PGDP Problem Report No. ATRC-08-1 147; PGDP Event Report No. PAD-2008-11." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-04-18
44150 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-03-13 | 2008-04-18 11:50 | 2008-04-30 | AGREEMENT STATE - BROKEN TRITIUM EXIT SIGN The State provided the following information via email: "On April 17, 2008, the agency received written notification from the Radiation Safety Officer (RSO), reporting that during their routine inventory check they, accompanied by two of their health physics consultants, found the one tritium (H-3) exit signs in a non-public receiving area in their Cypress, Texas store, had a missing face plate, frame and label, red 'EXIT' cover and several H-3 tubes. The RSO reported that the remaining H-3 tubes were intact. "The RSO reported that they conducted informal interviews with store managers and associates that revealed no additional information as to the date or circumstances of the damage to the sign. The RSO and their consultants stated that because available information does not suggest that the H-3 exit sign (TES) was recently damaged, Wal-Mart believes that no significant contamination currently exists at the site. Additionally, he stated that Wal-Mart reached this conclusion in consultation with consultant Certified Health Physicists (CHPs). "The RSO stated that their long term corrective actions included: implementing protocols, which have been communicated to employees, for the proper handling of TES to ensure public health and safety and the protection of its employees. They report that they are in the process of inventorying all of the TES at its sites across the country to re-establish the accuracy of its records and to track the current locations of the TES, with the intent of ensuring that all TES are accounted for and handled properly. "The RSO stated that the damaged TES will be packaged for shipment according to protocols established by their consultants and consistent with Nuclear Regulatory Commission (NRC) guidelines. Wal-Mart anticipates shipping the remnants of the damaged TES to a specific licensee or arranging for a waste broker to ship the TES to a specific licensee authorized to receive it within thirty-days of their report to the agency, which was dated April 10, 2008." Texas report I-8507 * * * UPDATE PROVIDED BY LATISCHA HANSON VIA E-MAIL TO JASON KOZAL ON 04/23/08 AT 1449 * * * "On 04/22/08: "The agency received written notifications each dated April 17, 2008 that three more exit signs were found damaged at the following locations: "1) 4700 East Palm Valley Blvd., Round Rock, Texas 78665-2580; Store # 5480 - Damaged exit sign discovered on 03/19/08 - approximately 11.5 Ci; Serial # unknown - one damaged exit sign with the tubes in the letter "T" broken. "2) 620 S IH-35, Georgetown, Texas 78628-4157; Store # 1303 - Damaged exit sign discovered on 03/18/08 - 20 Ci; Serial #289930 - one damaged exit sign uninstalled and stored in the manager's office, missing it's face plate, it's red "EXIT" cover and all H-3 tubes. "3) 1030 Norwood Park Blvd., Austin, Texas 78753-6600; Store # 1185 - Damaged exit sign discovered on 03/19/08 - 20.0 Ci; Serial #274828 - one damaged exit sign with broken tubes, installed in the non-public receiving section of the store." Notified R4DO (Cain), FSME EO (Hsueh). * * * UPDATE PROVIDED BY ART TUCKER TO JASON KOZAL ON 4/30/08 AT 1029 * * * The State provided the following information via email: "The State of Texas received notification of nine additional exit signs which had either damaged (4) or missing (5) vials containing tritium (H-3.) The RSO for Wal-Mart stated that the information gather in the inspections conducted throughout the United States was being entered into a database and that they would supply the State of Texas with the results of their inspections conducted in Texas as soon as it was available. No estimate of the number of vials involved or the total activity released has been determined as of today's date. He also stated that he had been in contact with the NRC. " Notified R4DO (Pick), FSME (Burgess). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-04-23
44149 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2008-04-04 | 2008-04-18 11:45 | 2008-04-18 | MISSING DEPLETED URANIUM SOURCE "On April 4, 2008, a condition was identified at the Hematite Decommissioning Project that potentially involves missing licensed material in a quantity greater than 10 times the quantity specified in 10 CFR 20, Appendix C. Specifically, although it cannot yet be determined with certainty, it appears that a small depleted uranium pellet used as a detector source is missing. The radioactive source was one of several installed and used in Eberline, Model DA-1, gamma detectors to provide an indication of continuous operability. From the available documentation, it appears that the detectors were installed in 1993, well before Westinghouse acquired the facility in 2000. "If it is confirmed that the radioactive source indeed is missing and is of the type, quantity, and form of other similar detector sources present at the facility, the source is a depleted uranium pellet in a solid oxide form, with a total mass of approximately 5.5 grams. The total uranium mass of the source is approximately 4.85 grams. The uranium-235 (U-235) activity in the source is approximately 0.037 microcuries, which is a quantity greater than ten (10) times the 10 CFR 20, Appendix C, limit for U-235 of 0.001 microcuries. "For reasons discussed further below, the circumstances under which the apparent loss of licensed material may have occurred cannot be determined with certainty. With the facility in a decommissioning status, it is possible that the source was separated from its detector during decommissioning activities performed since the site ceased fuel fabrication activities in 2001. Subsequently, the probable disposition of the source may have been its having been packaged and shipped either as Special Nuclear Material inventory removed from the site or as radioactive waste. Either situation is credible since significant decommissioning activities in the site Process Buildings has involved the removal of remaining Special Nuclear Material inventory and contaminated process equipment. "As of the date of this report, immediate actions have included the following: "(1) Similar detector sources from gamma detectors that no longer are needed/used have been removed and properly stored. "(2) On April 7, 2008, a physical search and radiological surveys were conducted in an attempt to determine if the potentially missing radioactive source remains in the Process Building area. The source was not found. "(3) An investigation is ongoing to confirm whether the licensed material is indeed missing. This investigation includes searching through Radiation Protection records for additional information regarding the source and any potential evidence of its disposition. It is noted that the ongoing investigation is challenged by: (1) the subject source and similar radioactive sources have not been formally tracked within an inventory and tracking system; (2) a change in facility ownership in 2000; and (3) site management and staff turnover since decommissioning started, such that individuals who may have had first hand knowledge of the cause and/or disposition of the subject radioactive source are no longer at the facility. "The investigation into this event is continuing, and any further details will be provided in the written report that Westinghouse will submit within 30 days of this telephone report pursuant to 10 CFR 20.2201 (b)." The licensee informed NRC Region 3 and the NRC Headquarters Program Manager. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | FUE |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-04-18
44148 | 0 | PALISADES | 1 |  |  | [1] CE | 2008-04-18 06:03 | 2008-04-18 06:23 | 2008-04-18 | UNUSUAL EVENT DUE TO SEISMIC ACTIVITY The earthquake in southeastern Illinois was felt on site. No damage has been reported. All secondary system walkdowns have been completed. Primary system walkdowns are in progress. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM P. PITCHER TO P. SNYDER AT 1144 on 4/18/07 * * * Palisades continues in the Unusual Event after detecting an aftershock from the previous earthquake. Palisades is continuing checks per their procedures for the circumstances at the site. * * * UPDATE FROM TODD PLAUGHER TO JASON KOZAL AT 1438 on 4/18/07 * * * The licensee has exited the Unusual Event at 1431 on 4/18/08. The licensee notified the NRC Resident Inspector. Notified R3DO (Kozak), NRR EO (Ross-Lee), IRD (McDermott), DHS (Gomez), FEMA (Burckhardt) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-04-18
44147 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-04-18 06:02 | 2008-04-18 06:20 | 2008-04-18 | UNUSUAL EVENT DECLARED DUE TO SEISMIC ACTIVITY "At 06:02 on April 18 2008, DC Cook Units 1 and 2 entered the Emergency Plan for a confirmed seismic event based on ground motion felt by plant personnel. An immediate notification to the NRC is required under 10 CFR 50.72(a)(3) for entry into the Emergency Plan. The ground motion sensed by plant personnel was confirmed with the National Earthquake Center. A magnitude 5.4 preliminary (Richter scale) earthquake was confirmed in Southern Illinois at LATITUDE 38.481 North/LONGITUDE 87.826 West. "The Earthquake Abnormal Operating Procedures were entered for both Units. Ground motion was not felt by the control room operating crews, but was noted and reported by other plant personnel. Plant Process Computer trends of Unit 1 RWST level, South Boric Acid Storage Tank Level and North Chemical and Volume Control System Hold Up Tank Level indicated ground motion. No damage to plant equipment was noted during the initial evaluation of plant status. Investigation of the plant impact of the sensed ground motion is in progress. "The NRC Resident Inspectors were notified by phone call. Current Plant status: Unit 1 is shutdown in Mode 6 with Residual Heat Removal Cooling. Unit 2 is operating in Mode 1 at 100% power. AEP system Operations was contacted and the GRID was described as stable and no electrical operations relating to the earthquake event. "The Seismic Monitoring system was INOPERABLE as required by TRO 8.3.2, Cond. B, during the event for routine surveillance. This surveillance has been in progress since 03/26/08. No alarms were generated by the seismic monitoring system during this event." * * * UPDATE AT 0910 EDT ON 04/18/08 FROM CHRIS KELLEY TO S. SANDIN * * * At 0905 EDT on 04/18/08, the licensee terminated the Unusual Event based on completion of system walk downs which confirmed no damage to the facility. The licensee informed the NRC Resident Inspector. Notified R3DO (Kozak), NRR (MJ Ross-Lee), IRD (McDermott), FEMA (Liggett) and DHS (Barnes). * * * UPDATE AT 0958 EDT ON 04/18/08 FROM BRAD LEWIS TO S. SANDIN * * * "A press release regarding the declaration of the emergency was issued and a subsequent press release is planned to address the termination. The offsite notifications are being reported under 10 CFR 50.72(b)(2)(xi)." The licensee informed the NRC Resident Inspector. Notified R3DO (Kozak). * * * UPDATE AT 1203 EDT ON 4/18/08 FROM TIMMOTHY WICE TO JASON KOZAL * * * "At 11:45 on April 18, 2008, D.C. Cook Units 1 and 2 entered the Emergency Plan for a confirmed seismic event based on ground motion felt by plant personnel. An immediate notification to the NRC is required under 10 CFR 50.72(a)(3) for entry into the Emergency Plan. The ground motion sensed by plant personnel was confirmed with the National Earthquake Center. A magnitude 4.6 (preliminary on Richter scale) earthquake-aftershock was confined in Southern Illinois at LATITUDE 38.483 North/LONGITUDE 87.39 West at 10:14 CDT / 11:14 EDT. "The Earthquake Abnormal Operating Procedures were entered for both Units. Ground motion was not felt by the control room Operating crews, but was noted and reported by other plant personnel. No damage to plant equipment was noted during the initial evaluation of plant status. Investigation of the plant impact of the sensed ground motion is in progress. "The NRC Resident Inspectors were notified in person. Current Plant status: Unit 1 is shutdown in Mode 6 with Residual Heat Removal Cooling. Unit 2 is operating in Mode 1 at 100% power. AEP System Operations was contacted and the GRID was described as stable with no electrical operations relating to the earthquake event. "The Seismic Monitoring system was INOPERABLE as required by TRO 8.3.2, Condition B during the event for routine Surveillance. This Surveillance has been in progress since 03/26/08. No alarms were generated by the seismic monitoring system during this event. One of four channels is currently out of service. The three remaining seismic monitor channels indicated no ground acceleration above the lowest instrument activation level of 0.02g. "D.C. Cook intends to issue a press release regarding the declaration of the Notification of Unusual Event emergency classification. The offsite notifications are being reported under 10 CFR 50.72(b)(2)(xi)." * * * UPDATE AT 1616 EDT ON 4/18/08 FROM FRANK BAKER TO JASON KOZAL * * * "At 16:00 on April 18, 2008, DC Cook terminated the Unusual Event specified in EN 44147 for the aftershock response described above. A press release regarding the emergency event termination is anticipated. The offsite notifications are being reported under 10 CFR 50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. Notified R3DO (Kozak), NRR EO (Ross-Lee), IRD (McDermott), DHS (Gomez), FEMA (Burckhardt). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2008-04-18
44146 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-04-17 | 2008-04-17 17:49 | 2008-04-21 | AGREEMENT STATE - LOST TROXLER GAUGE The licensee provided the following information via email: After completing a job a Troxler Moisture Density Gauge (Model number 3430, Serial Number 34618) was loaded into the back of the licensee's truck and not secured. The unsecured gauge fell out of the truck in transit from the job site. The licensee discovered the gauge missing and notified supervision. The licensee notified the local police department and is actively searching for the gauge. The licensee plans to offer a reward for return of the missing gauge. The State of Florida is further investigating the incident. * * * UPDATE FROM ADAMS TO CROUCH (VIA EMAIL) ON 04/21/08 @ 1334 EDT * * * "Florida incident FL08-060 which was reported and occurred on April 17, 2008 involved a lost Troxler gauge. It was recovered today. A gentleman found it at the intersection of 40th St. and 38th Ave. in Coral Gables on Thursday, the day it was lost. He finally called the licensee today and the licensee took possession of it about 10:30 this morning. It is undamaged." Notified R1DO (White) and FSME EO (Burgess). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-04-22
44145 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-04-17 | 2008-04-17 17:27 | 2008-04-17 | RADIOGRAPHY CAMERA MALFUNCTION This "incident occurred on April 15, 2008 at about 8:20 PM at a new [non-nuclear] power plant under construction. Team Industrial Services was performing industrial radiography on Unit 1. The radiography was being performed on elevation 807 on a header approximately 4 foot off of the roof of the boiler. "According to statements from the crew, they had exposed the source on their first shot of the pipe weld, and approximately 15 seconds into the shot they heard what they thought was the guide tube and collimator faillng off the pipe to the roof of the boiler. They then went to retract the source back into the exposure device and encountered an obstruction preventing the source from being retracted into a secured position in the exposure device. They attempted [to retract the source] three times with no success. "The industrial radiographer contacted the facility radiation safety officer and advised him that he had a source he could not retract back into the exposure device. The industrial radiographer extended the radiation safety boundaries above and below the area. The Radiation Safety Officer (RSO) advised [the radiographer] that he was on his way to the site. "The RSO arrived at the site at approximately 9:00 PM. At this time an initial assessment was made and a decision was made to bring in two more trained technicians to assist with boundary control and retrieval of the sealed source. After arrival of the extra technicians, a plan for retrieval was discussed with all technicians, including the Corporate Radiation Safety Officer. "The industrial radiographer stated that his pocket dosimeter had gone 'off scale.' This means that he could have received a dose of at least 200 millirems of radiation. At this time he was advised that he would not be assisting with the retrieval but he continued to assist with boundary control. The licensee has estimated that the industrial radiographer received 630 mR. "At approximately 11:35 PM, the shielding of the source and attempt to repair the guide tube commenced. Four lead shot bags were placed over the end of the guide tube where the sealed source was known to be. The radiation levels were reduced to 15 millirems per hour at five feet from the source under the lead shot bags. The RSO then approached the guide tube with a pair of pliers, located the distortion in the guide tube and rounded it with the pliers. He then returned to the crank assembly and retracted the source successfully back into the exposure device. The RSO is estimated to have received 32 mR from conducting the repair. "A determination was made that there was not an equipment failure, it was a result of the guide tube falling from the pipe to the roof of the boiler that damaged the guide tube resulting in the obstruction. Boundaries were maintained throughout the incident to ensure that at no time any member of the general public could enter the incident area. "DHFS plans to investigate this incident on the next inspection (to be conducted in the near future)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-04-22
44144 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-04-16 14:26 | 2008-04-16 18:08 | 2008-04-16 | TWO GALLONS OF RADIOACTIVE WATER SPILLED IN PROTECTED AREA "A small quantity of radioactive water spilled on the concrete in the Protected Area and is in the process of being cleaned up. Approximately two gallons of water leaked from a shipping container being moved from Containment. The water was contained to the local concrete and tractor trailer receiving the load. The tractor trailer remains in the Protected Area and will be processed for free release. Initial analysis shows the presence of Co-58, Mn-54, Co-60, and Cs-137. Specific activity levels are not available at this time. No individual contaminations occurred during this event. "The licensee has reported this event to the Wisconsin Department of Natural Resources (WDNR) pursuant to WDNR Regulation NR706.03 at 1426 CDT. Subsequent review has determined that this event was not reportable to the WDNR and an update was provided to the WDNR at 1800 CDT. "This event is reportable under 10 CFR 50.72 (b)(2)(xi), 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.'" The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-04-16
44143 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2008-04-16 14:00 | 2008-04-16 16:35 | 2008-04-17 | AGREEMENT STATE REPORT - MEDICAL EVENT A patient at the Oklahoma State University Medical Center in Tulsa, Oklahoma was undergoing prostate treatment. The treatment was to implant 187 Pd-103 seeds (1.5 microCuries each) into the patient. The seeds were injected using a MIC gun which was manufactured by TheraGenics in Buford, Georgia. During the procedure it was observed that one of the seeds was sheared off with only 5% of the seed showing. The patient is believed to have the other 95% of the open seed inside his body. The radiation oncologist was present when this event happened. The patient was surveyed and his radiation levels were 0.46 mr/hr, which is within normal levels. The patient was not informed as yet, but should be by the attending physician. The half life of Pd-103 is 17 days, and most likely will be defused throughout the body. * * * UPDATE ON 4/17/2008 AT 1036 FROM MIKE BRODERICK TO MARK ABRAMOVITZ * * * The State provided the following information via email: "At about 2:00 PM on April 16, a patient was receiving 187 Pd-103 seeds for prostate therapy. The seeds were Theragen Model 200 of 1.5 microCuries each, manufactured by Theragenics, in Buford, Georgia, and purchased from Bard in Georgia. After injecting the seeds, the facility discovered one end of a Pd-103 seed in the 'mic' cartridge that had been used to hold the seeds. Only about 5% of the seed was present, and it is assumed the other 95% was injected into the patient. The piece found was leaking radioactivity. Surveys with a calibrated meter showed that the patient met the criteria for unrestricted release. The licensee plans to ask the referring physician to notify the patient. The licensee speculates that a malfunction in the mic gun caused the seed to be out of alignment when the cartridge was inserted or removed, leading to the clipping of the end, but this is highly preliminary, and the result of speculation rather than definite findings. The licensee will do an investigation. The licensee has temporarily stopped doing prostate implants. DEQ will send investigators to the site." Notified FSME (Burgess) and the R4DO (Clark). * * * UPDATE ON 4/17/2008 AT 1536 FROM MIKE BRODERICK TO JASON KOZAL * * * The State provided the following information via email: "There was a miscommunication between the state and the facilities, average strength for the Pd-103 sources involved in this event is 1.5 milliCuries, rather than 1.5 microCuries. The licensee has informed the patient of the event. The mic gun involved has been taken out of service. It is also considered possible the cartridge holding the sources was flawed, but the cartridges were disposed of as biomedical waste immediately after the surgery and will not be available to be checked. The licensee informs [the state] that the cartridges are generally covered in blood after one of these procedures, and such cartridge disposal is typical. The licensees are holding the mic gun until a state inspector arrives for an investigation, after which it will be returned to the manufacturer for evaluation." Notified FSME (Von Till) and R4DO (Miller). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2008-04-22
44142 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-04-15 08:49 | 2008-04-15 17:13 | 2008-04-15 | RESIDUAL HEAT REMOVAL SYSTEM DECLARED INOPERABLE "At 0849 the B train of service water (SW) AC and DC power distribution systems [were] declared inoperable due to voltage fluctuations below the Tech Spec minimum. During this time the A train of RHR for Unit 1 was inoperable due to an equipment outage. LCO 3.0.3 [was] entered due to both trains [of] RHR inoperable on Unit 1. At 1029 Unit 1 exited LCO 3.0.3 when the A train of RHR was restored. Currently ground isolation efforts are in progress on the B train SW power distribution system." The licensee notified the NRC Resident Inspector. | 100 | 61 | 0 | 100 | 61 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-04-15
44141 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-04-14 12:00 | 2008-04-15 14:46 | 2008-04-15 | LOSS OF SIREN ALERT NOTIFICATION SYSTEM DUE TO SYSTEM MODIFICATIONS "On April 14, 2008 during activities being performed by a Berrien County (BC) vendor associated with relocation of the BC 911 Dispatch Center, a microwave line was wired in parallel with the transceiver used to activate the Alert and Notification System (ANS) sirens. Following completion of the installation of the parallel microwave circuit, station personnel were informed and a poll was conducted at approximately 1633 hours on April 14, 2008, to verify no loss of capability of the ANS. This poll was unsuccessful. Immediate corrective actions included removal of the parallel microwave circuit and performance of an additional siren poll. The subsequent siren poll was completed successfully at approximately 1739 hours on April 14, 2008. A silent testing performed at 1000 hours on April 15, 2008, confirmed that all sirens are operational. An investigation has been initiated to evaluate the exact nature of the intended change, and to examine the processes used to control activities that may impact ANS operation. The ANS may not have been available on April 14, 2008, from approximately 1200 hours when the parallel circuit was installed, until the configuration was restored and successfully polled at 1739 hours." The licensee has notified the NRC Resident Inspector. They are working with Berrien County during the investigation. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-15
44140 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-04-15 07:00 | 2008-04-15 12:50 | 2008-04-15 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "Unit 2 HPCI (High Pressure Coolant Injection) System was declared inoperable due to discovery of a failed flow controller. The controller failure would prevent HPCI from achieving rated flow (safety function). Investigation into cause of failure and preparation for controller replacement are in progress. This event is being reported under 10CFR50.72(b)(3)(v)(B & D)." The licensee notified the NRC Resident Inspector. The licensee indicated the Isolation Condenser is operable. A 14 day LCO is in effect. | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2008-04-15
44139 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-03-19 | 2008-04-15 11:26 | 2008-04-15 | AGREEMENT STATE - FLORIDA - MISSING DOSE OF TC-99M The State provided the following information via facsimile: "Cardinal Health reported that they are missing a single dose of Tech-99m (25 mCi) since 19 March 2008. Customer reported item was not in ammo box upon receipt. Cardinal Health has searched premises with no indication. Procedures were reviewed and found to be correct. Corrective action consisted of a staff meeting to reiterate the requirement to follow proper procedure when packaging and shipping radioactive material. Incident referred to materials office for further investigation. This office will take no further action." FL Rpt No: FL08-056 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-04-18
44138 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2008-04-14 12:45 | 2008-04-14 16:05 | 2008-05-05 | HIGH ENERGY LINE BREAK ANALYSIS REVEALED POTENTIAL ACCIDENT MITIGATION DEFICIENCY "During review of a High Energy Line Break (HELB) analysis a condition was discovered where a break in the auxiliary steam system could result in a loss of all the containment fans and coolers, which are required to be maintained operable due to procedural restrictions to mitigate a design basis accident. "The plant entered Technical Specification (T.S.) 2.0.1 at 1245 CDT. This specification requires a plant shutdown within 6 hours. Operations personnel isolated auxiliary steam to the affected areas of the Auxiliary Building at 1305 CDT. With auxiliary steam isolated to the Auxiliary Building, containment fans and associated coolers were restored to an operable status. Plant exited T.S. 2.0.1 at 1305 CDT." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1224 EDT ON 5/5/08 FROM MATZKE TO HUFFMAN * * * "An exhaustive review of the high energy line break licensing and design basis for the auxiliary steam system as it impacts the safety functions or the containment coolers has determined that the required safety functions are met for the licensed and designed basis of the plant. Therefore the previous notification (EN 44138) of April 14 is being withdrawn." The licensee notified the NRC Resident Inspector. R4DO (Pick) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-04-14
44137 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2007-12-11 | 2008-04-14 11:22 | 2008-04-14 | AGREEMENT STATE REPORT - MISSISSIPPI - MISADMINISTRATION INVOLVING AN HDR TREATMENT The State provided the following information via email: "On 3-26-08, licensee's RSO notified DRH [Mississippi Division of Radiation Health] of a Iridium-192 HDR treatment misadministration. The reportable event involves the administration of 3 separate fractions for one (1) patient over a six (6) day period. The misadministration was caused by not measuring the catheters. Measurements taken on 3-25-08 of the tandem and ovoid applicators connected to the Varion Varisource HDR indicated that the length of the source wire entered in the treatment planning system should be 128 cm instead of 120 cm. Further inspection of the catheters revealed that the ovoid catheters were correct but the tandem catheter should have been used with a different applicator. The error resulted in the dose being delivered approximately 86 mm inferior to the desired location. The prescribed treatment was for 5 fractional treatments for 600 cGy each (3000 cGy total); however, due to the error only 470 cGy was administered in 3 treatments (26% of the prescribed dose). It was noted during the investigation by DRH that for other problems not associated with the HDR treatments, the patient did not return for the final 2 fractional doses. The dose to the vaginal region inferior to the treatment area received a 1300 cGy overexposure as a result of the error. The Radiation Oncologist does not foresee this patient experiencing adverse health effects as a result of this misadministration. The referring physician and the patient have been notified. " MS Report No. MS-08004 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2008-04-17
44136 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2008-04-09 07:00 | 2008-04-14 10:02 | 2008-04-14 | AGREEMENT STATE - MISSISSIPPI - TRAFFIC ACCIDENT INVOLVING TRUCK CARRYING TC-99M The State provided the following information via email: "DRH [Mississippi Division of Radiological Health] received a phone call from Cardinal Health RSO on 4-9-08 about a transportation accident involving one of their transport vehicles and an 18 wheeler on Hwy 49 South near Tchula, MS. The accident happened around 7:00 AM. The Cardinal driver had already made his deliveries to the facilities and only had the return packages (used doses) from the day before. According to RSO, driver hit the rear of the 18 wheeler after he made a sudden stop on the highway. According to RSO, all packages stayed secured and braced and their was no contamination or contents spilled out of the packages. Another driver was in route to location to pick up the other driver and the radioactive packages to return them to the Flowood facility." The material being transported was used doses of Tc-99m and there was no spillage or cleanup required. MS Report No. MS-493-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2008-04-17
44135 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2008-04-12 15:00 | 2008-04-12 15:12 | 2008-11-14 | MODIFICATION TO PROCESS COMPUTER THAT WILL IMPACT ERDS "The Unit 3 Plant Process Computer System (Emergency Response and Data Acquisition System, ERDADS) ERDS link will be out of service to install phone cables for the unit 4 ERDS link and cyber security equipment cabling. Additionally we are performing several software upgrades on the unit 3 ERDADS system. These upgrades will require several computer backup operations and several interruptions to the unit 3 ERDS link capability. "These activities will render the Unit 3 ERDS link out of service for several hours per day over the course of 3 to 5 days. In case of a plant emergency that would necessitate the activation of the unit 3 ERDS link, it can be placed in service within one (1) hour. The unit 3 SPDS functions are unaffected by this work. "This is an 8-hour reportable event per 10 CFR 50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of plant systems will not be affected due to this planned action. "The licensee has informed the NRC Resident Inspector." * * * UPDATE ON 11/14/2008 AT 1155 FROM BOB BONONTO TO MARK ABRAMOVITZ * * * ERDS was returned to service on October 31, 2008. The licensee notified the NRC Resident Inspector. Notified the R2DO (Bonser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-12
44134 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-04-10 19:03 | 2008-04-11 16:32 | 2008-06-04 | FAILED DETECTOR HEADS "At 1903 CST, on 04-10-08 the Plant Shift Superintendent (PSS) was notified that an alarm was received in the C-335 Area Control Room for the C-335 Unit 2 Cell 7 UF6 Release Detection (PGLD) System. Operators responded to the local panel and found all detector heads in alarm. Operators attempted to reset the system and the system would not reset, all heads remained in alarm. Operators then responded to the Unit 2 Cell 7 cell floor with the proper PPE and confirmed there was not a UF6 release. This PGLD System contains detectors that cover the C-335 Unit 2 Cell 7 cell housing roof and cell exhaust duct and sections 3 & 4 of the cell bypass housing. At the time of this alarm, C-335 Unit 2 Cell 7 and sections 3 & 4 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell housing roof, cell exhaust duct, and cell bypass housing are operable during steady state operations above atmospheric pressure. With all the Unit 2 Cell 7 PGLD system heads locked in alarm, none of the required 3 heads in the cell housing roof and cell exhaust duct were operable and less of the required 3 heads in the cell bypass housing sections were operable. This PGLD System was declared inoperable, TSR LCOs 2.4.4.1.A.1 and 2.4.4.1.C.1 were entered and a continuous smoke watch was put in place within one hour. An investigation is ongoing to attempt to determine the cause of the failure. This event is being reported as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATRC-08-1089; PGDP Event Report No. PAD-2008-10; Worksheet No. 44134 Responsible Division: Operations" * * * UPDATE FROM B. WALLACE TO J. KNOKE AT 1021 EDT ON 6/4/08 * * * The update is a retraction. Investigation has attributed the false alarm to a moisture problem and not a loss of power. The system did not fail. The licensee notified the NRC Resident Inspector. Notified R2 (Robert Haag) and NMSS (Jack Guttmann) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-04-11
44133 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-04-11 | 2008-04-11 13:00 | 2008-04-11 | AGREEMENT STATE REPORT - MISSING STRONTIUM-90 BETA APPLICATOR The State of Texas reported that a 55 milliCuries strontium-90 beta applicator, Amersham Model SIA.20, is currently missing. The device was formally used at a cancer treatment facility in Plano, Texas, which has since filed for bankruptcy protection. The device was not returned to the authorized user upon sale of the property. The state believes the device is locked and stored in the building and is attempting to gain access through the bankruptcy trustee. The state is investigating and will provide further details at a later date. * * * UPDATE FROM RAY JISHA TO JOE O'HARA AT 1730 0N 4/11/08 * * * The State of Texas has inspected the business and accounted for the missing beta applicator. Additionally, they have discovered some other nuclear source material. The state has served an impoundment order on the business and has secured all of the sources in the building pending additional investigation and follow-up. Texas Incident No. I-8500 Notified R4DO(Deese) and FSME(Kock). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-04-16
44132 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-04-10 10:56 | 2008-04-10 16:28 | 2008-04-10 | FITNESS FOR DUTY NON-LICENSED SUPERVISOR "A non-licensed employee supervisor had a confirmed positive for alcohol during a for cause fitness for duty test. The employees access to the plant has been terminated." Contact the HOO for additional details. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 26.73 |  |  |  | 0 | 2008-04-10
44131 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-04-10 10:15 | 2008-04-10 16:22 | 2008-06-20 | "ANALYSIS INDICATES CONTAINMENT COOLERS MAY NOT HAVE AUTOMATICALLY STARTED IN SLOW SPEED FOLLOWING POSTULATED MAIN STEAM LINE BREAK" "Information provided by another plant identified a condition where Containment Fan Coolers may trip if running in fast speed and not start automatically in slow speed, following a Loss of Coolant (LOCA) or Main Steam Line Break (MSLB). Wolf Creek commenced evaluation to determine if our Containment Coolers were susceptible to this condition. "Investigation and analysis as of this date indicate that in the case of a Main Steam Line Break, the coolers could trip while running in fast speed and not be able to be automatically started by the sequencer in slow speed due to present electrical design configuration. The peak containment pressure in this case would exceed the analysis of record by approximately 5 psig. "For the spectrum of the smaller break LOCA's, where actuation is delayed until pressurizer low pressure Safety Injection or the Containment Hi 1 pressure signal, analysis shows that the Containment Pressures would not be exceeded if the Containment Fan Coolers did not automatically start in slow speed. For a Large Break LOCA, analysis shows that the Containment Cooler Fans would be shed prior to tripping, and would be automatically started in slow speed by the sequencer. "Wolf Creek is currently in a defueled condition, for Refueling Outage 16. Continued evaluation and analysis of this issue is ongoing. This issue will be resolved prior to the plant entering Mode 4, where Technical Specification 3.6.6 requires Containment Fan Coolers be operable." The information was originally received from Callaway. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1245EDT ON 06/20/08 FROM LANCE LANE TO S. SANDIN * * * The licensee is retracting this event based on the following: "Wolf Creek evaluated this concern and concluded that the condition did not exist at Wolf Creek. Further analysis of the Main Steam Line Break, if this concern had existed, showed that the calculated post-accident pressure and temperature peak values would not exceed the peak accident values in the Final Safety Analysis Report. Therefore, an unanalyzed condition did not exist and Wolf Creek is retracting the 50.72(b)(3)(ii)(B) notification." The licensee informed the NRC Resident Inspector. Notified R4DO (Farnholtz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-04-10
44130 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2008-04-09 16:15 | 2008-04-09 18:46 | 2008-04-09 | LOSS OF ALL ENS TELEPHONE LINES ON SITE AFTER MAINTENANCE "Following maintenance on the FTS phone system and a successful test of the ENS phone, the ENS phone system failed. Normal commercial phone lines are still functioning and will be used for any required notifications. Repair personnel have been contacted and are expediting repairs." The maintenance performed earlier affected the FTS lines inside the licensee's area of responsibility and the 942 commercial exchange. The licensee notified the NRC Resident Inspector. The licensee will be notifying the state of Illinois. | 0 | 98 | 98 | 0 | 98 | 98 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-09
44129 | 0 | UNDERWATER ENGINEERING SERVICES, IN |  |  |  |  | 2008-04-08 | 2008-04-09 11:59 | 2008-04-09 | POTENTIAL PART 21 NOTIFICATION REGARDING TORUS IMMERSION/VAPOR PHASE COATINGS The reporting organization provided the following information via facsimile: "NUPIC identified that a potential problem of unqualified coatings exists with results of the 1996 DBA/Irradiation Test on February 29, 2008. UESI initiated Nonconformance Report NCR # 2008-01, insured that no coating applications were scheduled in Nuclear facilities requiring adherence to ANSI N101.2-1972, notified parent company President of potential Part 21 and under his directive began investigation. "Based on NUPIC Audit No. 08.03SPAFL.08. 1, Finding No. 1, a review of Historical Design Basis Accident (DBA) / Irradiation Test Results dated 12/16/1996, and subsequent internal investigation and evaluation, it has been determined that UESI Proprietary Underwater Coating Picco UT-15, when applied over the substrate Carboline CZ-11 only, does not meet all acceptance criteria of ANSI N101.2-1972 and ANSI N5.12-1974 for DBA qualified Coating Service Level I repair material. "The evaluation concluded, that while Picco UT-15 is fully qualified to ASTM D-3911-95 for all Service Level I and Torus/Immersion Area coating repairs on all substrates tested, use of the product should have been limited to ANSI N101.2-1972 qualified on all substrates tested with the exception of CZ-11. "Beginning immediately, UESI will cease to market and install its product as ANSI N101 .2-1972 / N5.12-1974 irradiation and DBA qualified when applied as a repair material over Carboline CZ-11 substrate. "Identification of the facility the activity or the basic component supplied for such facility or such activity within the United States which fails to comply or contains the defect." Duane Arnold Energy Center - DAEC has been contacted. Facilities with CZ-11 substrate and repairs performed with Picco UT-15, but may be exempt from Part 21 impacts are as noted: Cooper Nuclear Station- NPPD has been advised of the finding as a courtesy. Pilgrim Nuclear Station - PNS has been advised of the finding as a courtesy. Peach Bottom - PBAPS has been advised of the finding as a courtesy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21 |  |  |  | 0 | 2008-04-09
44128 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-04-08 23:50 | 2008-04-09 07:31 | 2008-04-09 | OFFSITE NOTIFICATION TO OSHA FOR FATALITY ONSITE DUE TO AN APPARENT HEART ATTACK "At 2100 on 4/8/2008, off-site medical assistance was requested for a Turkey Point Nuclear Power Plant Station contract employee experiencing an apparent heart attack. Miami-Dade County Fire and Rescue responded to the emergency. The patient was transported to the hospital by air rescue at 2132 on 4/8/2008. The contract employee was later pronounced dead at the hospital. "At 2350 on 4/8/2008, the Occupational Safety and Health Administration (OSHA) was notified of the on-site fatality of a contract employee. The Turkey Point Unit 3/4 control room was notified of the OSHA notification at 0620 on 4/9/2008. "Unit 3 remains in Mode 1 at 100% power with GREEN (Acceptable) risk. "Unit 4 is defueled during a planned refueling outage with GREEN (Acceptable levels of key safe shutdown functions are being maintained) risk. "This notification is a 4-hour notification being performed in accordance with 10CFR50.72(b)(2)(xi) for notification to an off-site government agency." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-04-09
44127 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2008-04-08 11:00 | 2008-04-08 19:10 | 2008-04-08 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR "At approximately 1100 Mountain Standard Time on April 8, 2008 at the Palo Verde Nuclear Generating Station, a non-licensed supervisor tested positive for alcohol during a random 'Fitness for Duty' test. The person's access authorization has been placed on hold in accordance with station procedures. This event is being reported pursuant to 10 CFR 26.73(a)(2)(ii). The NRC resident inspector has been notified of the event." | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.73 |  |  |  | 0 | 2008-04-08
44126 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-04-08 08:16 | 2008-04-08 09:22 | 2008-04-08 | CREDIBLE SECURITY THREAT RECEIVED FROM LOCAL LAW ENFORCEMENT Site is taking appropriate actions per the security plan concerning a credible site specific threat. Site declared a Notice of Unusual Event at 0816 CDT. There is no effect on plant conditions. The site will exit this event when security determines that there is no threat. * * * UPDATE AT 1418 EDT ON 04/08/08 FROM DAN WEBER TO JEFF ROTTON * * * " Unusual Event HU 4-2 was terminated at 1226 [CDT] hours. Site security threat procedure has been exited. This notification also provides, notification of completion of immediate reporting requirements of 10 CFR 73.71 Appendix G as well as 4-hour notification of communications to and from off-site agencies. A press release associated with the UE will be made. This notification satisfies reporting requirement of 10 CFR 50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector and state and local emergency response organizations. Notified R3DO(Stone), R3 RA (Shear), NRR (Wiggins), NRREO (Ross-Lee), ILTAB (Whitney), IRD (Blount), DHS (Akers), FEMA (Canupp) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) | 73.71(b)(1) | 50.72(b)(2)(xi) |  | 1 | 2008-04-08
44125 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2008-04-07 13:45 | 2008-04-07 20:44 | 2008-04-07 | CORE ELEMENT ASSEMBLY CALCULATORS DECLARED INOPERABLE "On 4/7/2008, at approximately 1345 CDT, with ANO-2 in Mode 3 (Hot Shutdown) at normal operating temperature and pressure, and with all control element assemblies (CEAs) withdrawn approximately 2 stops, the Control Room was notified by the Computer Support Group (CSG) that the software verification for CEAC1 and CEAC2 (Core Element Assembly Calculators) had not been verified. Both CEAC's were declared inoperable. The Reed Switch Position Indicators (CEA positions) are considered inoperable if the CEAC's are inoperable. Tech Spec 3.1.3.3 requires at least one of these position indicators be operable in Modes 3 through 5 for each CEA not fully inserted. All CEAs were approximately 2 steps withdrawn from fully inserted during plant heatup to clear the rod bottom indications in preparations for CEA Drop Time Testing. At 1350 the reactor trip breakers were opened and CEA's were verified to be fully inserted to meet the Action Statement for Tech Spec 3.1.3.3. Note that no actual position indication was lost, nor did the CEAC show any signs of malfunction. The software verifications have been completed by the CSG." The licensee notified the NRC Resident Inspector. The licensee also notified the state. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-04-07
44124 | 0 | RANCHO SECO | 1 |  |  | [1] B&W-L-LP | 2008-04-05 11:40 | 2008-04-07 18:41 | 2008-04-07 | UNUSUAL EVENT REPORTED AFTER-THE- FACT DUE TO A FIRE ONSITE "Rancho Seco is a defueled reactor. All fuel is in the Rancho Seco ISFSI. "During decommissioning operations in the reactor building, a debris fire occurred while the contractor was cutting rebar during the removal of interior concrete. Assorted trash and combustible materials were ignited. "The building was evacuated per procedures and onsite SMUD staff and contractors brought the fire under control utilizing available fire suppression equipment after several minutes and the fire was deemed extinguished at 1340 hours, 4/5/08. "No injuries occurred. "All weekend work operations were ceased and a fire watch was established. A review of the incident occurred and measures to prevent future fires were employed. "Decommissioning work resumed Monday, 4/7/08. As part of the After Action Review it was determined official notification to response and regulatory agencies still needed to be made. "No detectable airborne contamination occurred. "No contaminated personnel occurred." The fire was detected in destruction debris under a pile of concrete rubble in the reactor building. The fire was initially extinguished at 1045 PDT by onsite personnel. The fire reflashed two additional times and was extinguished until it was determined to by completely extinguished at 1340 PDT on 04/05/08 and the licensee terminated the Unusual Event. The event was declared and logged by the ISFSI Technician on 04/05/08, who is also the onsite Emergency Coordinator when an emergency is declared. It was discovered on the morning of 04/07/08 that the emergency declaration was made and logged on 04/05/08 at 1140 PDT, but no offsite regulatory notifications had been made. The licensee notified the local NRC Inspector (Garcia) and Region 4 (Keller). The licensee will be notifying the state and local emergency response organizations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-04-07
44123 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-04-07 10:33 | 2008-04-07 12:06 | 2008-04-07 | UNUSUAL EVENT - LOSS OF OFF-SITE POWER WHILE DEFUELED At 1020 CDT on 4/7/08 a loss of off-site power was experienced due to maintenance work in the switch yard. At 1033 CDT the licensee declared an Unusual Event. Presently, off-site power is in the process of being restored . The "B" Emergency Diesel Generator is running and loaded, while the "A" Emergency Diesel Generator and "A" bus is tagged out of service for maintenance. The Essential Service Water system developed a leak in the end bell of a cooling unit, which in turn caused licensee to secure control room cooling. This put the licensee in LCO 3.7. The plant is currently defueled. Spent fuel pool cooling has been reestablished. The licensee notified the NRC Resident Inspector. Licensee will be contacting other state, local, and government agencies, and will be issuing a press release. * * * UPDATE PROVIDED AT 1406 EDT ON 04/07/08 FROM JEFF ISCH TO JEFF ROTTON * * * At 1250 CDT, normal off-site power was restored to NB02 and the Unusual Event was terminated. The "B" Emergency Diesel Generator was secured and placed in standby. The licensee has notified the state and local emergency response organizations and will be notifying the NRC Resident Inspector. Notified R4DO(Lantz), NRREO (Ross-Lee), IRD (Cruz), DHS (Akers), and FEMA (Biscoe). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 4 | KS | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-04-07
44122 | -1 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-04-07 04:30 | 2008-04-07 05:11 | 2008-04-07 | TECHNICAL SUPPORT CENTER MAY BECOME UNINHABITABLE DUE TO SCHEDULED MAINTENANCE "At 04:30 hours on Monday, April 7, 2008, the Cook Nuclear Plant (CNP) removed the Technical Support Center [TSC] Heating Ventilation Air Conditioning [HVAC] System from service for planned maintenance. The TSC HVAC system will remain out of service for a period of approximately three days. "Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "This notification is being made in accordance with NUREG 1022 as a potential unavailability of an emergency response facility in accordance with 10 CFR 50.72 (b)(3)(xiii). "The licensee notified the NRC Resident Inspector. The licensee will supplement this notification upon returning the TSC HVAC system to normal operational status." * * * UPDATE PROVIDED AT 1329 ON 04/07/08 BY RICHARD HACKMAN TO JEFF ROTTON * * * The following information was provided by the licensee to RETRACT the event: "Upon additional evaluation CNP determined that the planned maintenance reported above was limited in scope and did not remove the entire TSC HVAC system from service. The planned maintenance resulted in two of three fully redundant air chillers (air conditioners) being removed from service for maintenance. The third chiller and the TSC HVAC system is operable and remains in service. Therefore, the CNP TSC has been maintained in a configuration that ensures habitability. "The NRC Resident Inspector has been notified of the retraction." Notified R3DO (Skokowski). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-07
44121 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2008-04-06 13:17 | 2008-04-06 14:13 | 2008-04-07 | UNUSUAL EVENT FROM REACTOR COOLANT SYSTEM LEAKAGE Millstone unit 2 entered a refueling outage on 4/6/2008. The plant was in the process of placing shutdown cooling in service when at 1236 a 10-15 gpm leak was detected by decreasing pressurizer level. The release path was determined to be from the Reactor Coolant System (RCS) to the Refueling Water Storage Tank (RWST). Pressurizer level is stable and RWST level is rising slowly. Two charging pumps are available for RCS makeup. Decay heat is being removed with Atmospheric Dump Valves. The vent line on the RWST does not contain a radiation monitor and this is an potential unmonitored radiation release path. The Unusual Event was declared at 1317. The leak was terminated at 1320. Monitoring of the potential release path commenced at 1610. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 4/6/2008 AT 1910 FROM WAYNE GAMMON TO MARK ABRAMOVITZ * * * "The leak path has been isolated by closing the two air operated ECCS recirc header stops 2-SI-659/660." The Unusual Event was terminated at 1856 and the NRC exited "monitoring mode" at 1920. Notified IRD (Cruz), NRR EO (Quay), and R1DO (Hansell). EPA Incident Report Number: 867171 The licensee notified the NRC Resident Inspector. * * * UPDATE ON 4/07/08 @ 1110 EDT FROM JIM KUNZE TO HOWIE CROUCH * * * "Upon further review, the times that the RCS leak occurred and was isolated require correction. The RCS leak occurred at 1243 when valve 2-SI-651 was opened to place shutdown cooling in service. The leak was terminated at 1356 when valve 2-Sl-659 was closed. "The NRC Sr. Resident Inspector has been notified." Notified R1DO (Conte). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-04-06
44120 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-04-04 12:59 | 2008-04-04 17:39 | 2008-04-17 | ACCIDENT MITIGATION - COMMON CONTROL ROOM EMERGENCY AIR CONDITIONING SYSTEM "Salem Unit 1 was placed in a configuration that affected the ability to mitigate the consequences of an accident due to an inadvertent actuation of the common control room emergency air conditioning system (CREACS). CREACS was actuated as a result of an invalid Control Room air intake duct radiation monitor initiated on April 4, 2008 at 1259 hours. Salem Unit-2 is currently defueled. Salem Unit 1 is in Mode 1 at 100% power. Unit 1 has two shutdown LCOs in effect. The first is for the CREACS system, which is shared between Unit 1 & 2, being aligned for single train operation with the Unit 2 CREACS train out of service per LCO 3.7.6. The second shutdown LCO is for two outside air intake dampers being inoperable for scheduled maintenance. With Unit 2 having an invalid Radiation Monitor signal, the CREACS system actuates in accident pressurized mode. This mode of actuation starts the CREACS fans, isolates the Control Room Envelope from the normal control room ventilation system and aligns the two sets of CREACS outside air intake dampers. With a Unit 2 Radiation Monitor signal, the Unit 2 CREACS intake dampers close and the Unit 1 CREACS intake dampers open. These damper positions are locked in until manually reset. With only one train of CREACS operable, the dose analysis indicates that the requirements of General Design Criterion (GDC) 19 can only be met during the worst case design basis accident if the Unit 1 CREACS intake dampers are closed and the Unit 2 CREACS intake dampers open. Therefore, until the CREACS intake dampers were reset and realigned, Salem Unit 1 would not have been able to mitigate the consequences of an accident and is reportable in accordance with 10CFR50.72(b)(3)(v)(D). The CREACS system actuation was reset after the failed radiation monitor (1R1B ch II) was removed from service and the dampers were re-aligned to their pre actuation alignment at 1316 hours, restoring Salem Unit 1 to within the assumptions of the dose analysis. Total duration in the condition was 17 minutes. "The only piece of major equipment out of service on Salem Unit 1 is the 15 Service water pump which is out of service for scheduled maintenance." The Licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY ERIC POWELL TO JASON KOZAL ON 04/17/08 AT 2113 * * * "On April 4, 2008 Salem Unit 1 was placed in a configuration that was contrary to the current dose analysis of record due to an inadvertent actuation of the common control room emergency air conditioning system (CREACS). CREACS was initiated as a result of an invalid actuation of a Control Room air intake duct radiation monitoring channel (1R1B ch II). At the time of the actuation, the Unit 2 train of CREACS was out of service due to scheduled maintenance leaving only the Unit 1 CREACS train operable. Unit 1 was at 100% power and Unit 2 was defueled. With one train of CREACS out of service at the start of an accident the dose analysis of record requires that the CREACS emergency intake dampers for the unit having the accident to close and for the opposite units emergency intake dampers to open. The actuation of the radiation monitoring channel 1R1B channel II caused the Unit 1 emergency intake dampers to open which was contrary to the dose analysis of record. "Subsequent to this event, an evaluation was performed utilizing the assumptions of the dose analysis of record with the exception of the actual measured engineered safety feature system leakage outside containment and the atmospheric dispersion factors (x/Q) associated with the Unit 1 CREACS intake. Based upon this evaluation, the CREACS system with one filtration train operable and the emergency intakes open on Unit 1 would have been able to maintain doses to the Control Room operators below the limits of GDC-19 and the dose analysis of record. Since the CREACS system was capable of performing its accident mitigation function, this event is being retracted." The licensee will notify the NRC Resident Inspector. Notified R1DO (Schmidt) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-04-04
44119 | 0 | SHAW AREVA MOX SERVICES, LLC |  |  |  |  | 2008-02-06 | 2008-04-04 14:30 | 2008-04-04 | PART 21 - REINFORCING BARS BELOW ACI STANDARDS "The purpose of this letter is to inform the NRC Operations Center that Shaw AREVA MOX Services, LLC (MOX Services) has identified a deviation associated with reinforcing bar supplied by Energy and Process Corporation (E&P). "The condition involves reinforcing bars (rebar) supplied by E&P that have a bend radius below the minimum specified by ACI Standard 315-99 and ACI Standard 349-97. The condition was initially observed on 06 February 2008. The extent of condition determination found that a significant portion of bent rebar in all sizes failed to meet the minimum bend radius specified by ACI Standard 315-99 and ACI Standard 349-97. Based on this finding, it was concluded that a similar nonconforming population could be present embedded in those areas of the plant where concrete had already been poured. "MOX Services has determined that the IROFS [Item Relied On For Safety] function of the BMF structure was not diminished by the rebar installed in concrete poured to date and that a substantial safety hazard would not result in the MFFF [Mixed Oxide Fuel Fabrication Facility] if the deviation had not been discovered. For industry awareness, we have conservatively chosen to report this deviation under the provisions of 10 CFR 21.21(d)(3)(i)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2008-04-04
44118 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2008-04-03 14:00 | 2008-04-03 14:57 | 2008-04-03 | LOSS OF ABILITY TO TELEPHONE OUT OF STATE "When it was discovered that numerous plant personnel could not make telephone calls out of state, attempts were made to contact the states of Vermont, New Hampshire, and Massachusetts, as well as the NRC through the FTS phone. The NRC, as well as the state of Vermont were contacted but the NAS phone system was inoperable as well as the land lines to the states of NH and MA. Alternate means to contact the states were available via the microwave system." At 1430 all communications that were lost were restored. At 1445 all testing of communications were completed. The licensee notified the NRC Resident Inspector. | 50 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-04-03
44117 | 0 | PONZE I&M ENGINEERING LAB, INC. |  |  |  |  | 2008-04-03 | 2008-04-03 08:23 | 2008-04-05 | STOLEN CPN MOISTURE DENSITY GAUGE The licensee Radiation Safety Officer reported that a company pick-up truck, that had a moisture density gauge stored in the bed, was stolen from in front of the apartment complex of the Authorized User. The apartment was located in Guaynabo, Puerto Rico, which is remotely located from the licensee home office located in Coto Laurel, Puerto Rico. The gauge is a CPN Model MC-1DRP, S/N 60703285, which contains 10 mCi of Cs-137 and 50 mCi of Am: Be. The gauge was last leak checked on October 15, 2007. The gauge was secured to the truck in a metal case mounted to the chassis of the truck and secured with the gauge lock, the gauge case lock and two locks on the metal storage case. The stolen truck was a white 1996 Ford Ranger pick-up with Puerto Rican tag number 557-167. The licensee notified the Puerto Rico State Police of the theft of the truck and gauge. * * * UPDATE FROM JOSE IRIZARRY TO HOWIE CROUCH ON 04/05/08 @ 0809 HRS EDT * * * Mr. Jose Irizarry, RSO for Ponze, reported that at 0430 EDT he was notified by Puerto Rico State Police that they had recovered the moisture density gauge in San Juan, Puerto Rico. The gauge was still locked in its storage container and was returned to the Authorized User. Notified R1DO (Hansell), FSME (White) and ILTAB (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-04-03
44116 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2008-04-02 04:30 | 2008-04-02 15:21 | 2008-04-02 | AGREEMENT STATE REPORT INVOLVING STOLEN TROXLER MOISTURE DENSITY GAUGE On 04/02/08 at 0400 PDT, the Authorized Gauge User checked out a Troxler Model #3440, S/N 30441, from his company and was enroute to the jobsite when he received a call that the job was cancelled. He went home to have breakfast at 0430 PDT. At 0500 PDT, he found that the chains securing the device for transport had been cut and the gauge was missing from the transport vehicle parked at the users home. The gauge contains two sources: 9 mCi Cs-137 and 44 mCi Am-241:Be. The last leak test was performed on 03/04/08. The licensee notified the Nevada Highway Patrol and Las Vegas Metro Police of the theft. A contributing factor to the theft may have been the lack of two tangible barriers securing the gauge. NV Event Report ID No.: NV-NV080002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2008-04-07
44115 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2008-04-01 11:26 | 2008-04-01 14:51 | 2008-04-01 | OFFSITE NOTIFICATION TO STATE OF FLORIDA DUE TO CHROMATE SPILL "During a scheduled run of the 3A Emergency Diesel Generator for surveillance, an active engine coolant leak was discovered on the diesel engine radiator while pressurized. 3A Emergency Diesel Generator was shutdown to depressurize the radiator leakage path. The leak caused a spill of 55 gallons of chromated engine cooling water into the Emergency Diesel Generator building. The leakage rate has decreased to approximately 1 drop per minute after depressurization and is contained within a berm. "There was no release to the environment and therefore there was no ground water intrusion. "Notification to State of Florida Department of Environmental Resources Management was completed at 1350 on 4/1/2008. "3A Emergency Diesel Generator remains inoperable at this time pending repairs to the radiator. Unit 3 is currently in a 72-hour Technical Specification Action Statement. This Technical Specification Action Statement is extendable to 14 days with proceduralized compensatory actions. "Unit 4 is currently in Mode 5 for refueling. 4A and 4B Emergency Diesel Generators remain operable, and Unit 4 shutdown risk remains GREEN (acceptable levels of performance of key safe shutdown functions). "This notification is being conducted in accordance with 10CFR50.72(b)(2)(xi)." The licensee informed the State of Florida and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-04-01
44114 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2008-04-01 07:10 | 2008-04-01 11:16 | 2008-04-01 | CONTAMINATED INJURED WORKER TRANSPORTED OFFSITE "Medical event requiring the transport of a radioactively contaminated person to an offsite medical facility for treatment. Initial onsite survey for radioactive contamination was unable to be performed before transport of the person offsite for medical treatment. Ambulance left site at 08:02 EDT. Surveys completed at hospital found low levels of radioactive contamination on individual's clothing and skin. This is determined to be a level 1 contamination event (0 - 5000 counts per minute above background). Maximum reading of 600 counts per minute above background located on right hand. Remaining locations 20 to 100 counts per minute above background. Individual has been decontaminated with no remaining contamination above background. Radiation protection personnel have taken control of radioactive material and returned it to Nine Mile Point in accordance with D.O.T. guidelines." Licensee Radiation Protection personnel surveyed the ambulance and the emergency room for contamination per plant procedures. No spread of contamination was found. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2008-04-01
44113 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-03-31 15:30 | 2008-04-01 10:52 | 2008-04-25 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the State of Arkansas via email (quotations omitted for readability): The Arkansas Department of Health, Radioactive Materials Program, is reporting that one of their licensees, Tigue Construction Company, Inc., has a Troxler moisture/density gauge that is stolen/missing from a pickup truck some time during the day in or near Brinkley, Arkansas. The licensee became aware of the missing gauge at 15:30 on March 31, 2008 after loading the gauge in the truck at the office in Glenwood, Arkansas that morning. The licensee has stated that the gauge, transport case and chains are missing. The licensee made one stop in Little Rock and observed that gauge in the truck during that stop. The licensee has filed a police report with the Brinkley Police Department. The Troxler gauge is a Model 3440, S/N 27381, and contains 40 milliCuries of Am-241:Be and 8 milliCuries of Cesium-137. The Arkansas Department of Health prepared a press release on the event. The licensee verbally indicated that the gauge was properly secured in the truck at the time. The Arkansas Department of Health is investigating the circumstances surrounding this event. Arkansas Department of Health notified Brinkley Police Department, Monroe County Sheriff's Office, Arkansas Department of Emergency Management (Arkansas State Police, Arkansas Highway Patrol), State of Mississippi, State of Tennessee [and] NRC Region IV. Arkansas has assigned Event Report ID No: AR-03-08-01 * * * UPDATE AT 1250 EDT ON 4/25/08 FROM MACK TO HUFFMAN VIA E-MAIL * * * "On April 17, 2008, the stolen Troxler Model 3440, Serial Number 27381, belonging to Tigue Construction, Inc., was retrieved from the Van Buren County Courthouse in Clinton, AR. "The gauge had been found in a ditch, by a citizen, approximately 2 weeks prior to April 17, 2008, and retrieved by the County Emergency Management Staff. Due to significant storms and flooding in the county the notification to Arkansas Dept. of Health was delayed. The gauge and transport case were found without any locks. "It is unclear how the gauge arrived in Clinton, AR. After being stolen in Brinkley, AR. The distance is 140 miles. "Health Physicists from the Arkansas Department of Health retrieved the gauge and stored it in the Department's Radioactive Material storage area. Field analysis indicated the gauge was not leaking. "On April 21, 2008, a representative from Tigue Construction, Inc., retrieved the gauge from the Arkansas Department of Health and will conduct a leak test prior to returning the gauge to service. The Department considers this event closed." R4DO (Cain), FSME (Zelac) and ILTAB (via e-mail) were notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2008-04-04
44112 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-04-01 05:30 | 2008-04-01 10:28 | 2008-04-01 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED OFFSITE "A potentially contaminated individual was transported to the Salem County Memorial Hospital by the on-site Fire Protection personnel due to a non-industrial medical emergency. The individual had been working in unit two containment as a Foreign Material Exclusion Area watch. The individual was surveyed en-route to the hospital and was determined to be not contaminated. The individual remains at the hospital and is undergoing testing and evaluation. Salem unit two remains defueled with spent fuel cooling in-service." Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2008-04-01
44111 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2008-03-31 15:50 | 2008-03-31 19:18 | 2008-06-03 | OFFSITE NOTIFICATION TO OHIO EPA CONCERNING NON-COMPLIANCE WITH HAZARDOUS WASTE REMOVAL REQUIREMENTS "At 1550 hours, a self identification call was made to the State of Ohio Environmental Protection Agency (EPA), offices in Columbus, Ohio to inform them of the recent discovery of non-compliance issues relating to the accumulation, storage, and shipment (i.e., 90 days to ship) of hazardous waste (reference 40 CFR 261, 'Identification and Listing of Hazardous Waste'). Guidance was requested from the state EPA for remediation and reporting of the condition. The Perry Nuclear Power Plant personnel were advised by the Ohio EPA to properly identify, package and ship the waste as soon as possible. The waste consists of three drums of floor grinding waste generated during the resurfacing of the Auxiliary Building floor in 2005, and approximately 100 bags of miscellaneous trash generated during disassembly of plant equipment in 2007. This issue was discovered during activities to prepare the waste for shipment off site. The waste will be shipped per the direction of the Ohio EPA and an out-of-cycle hazardous waste annual report will be made to the Ohio EPA. "This report is being made in accordance with 10 CFR 50.72(b)(2)(xi) as an event or situation related to the protection of the environment for which a notification to another government agency has been made. The resident inspector has been notified." The hazardous material contains low level rad waste. * * * UPDATE FROM RICHARD O'CONNOR TO HOWIE CROUCH @ 1334 HRS EDT ON 6/03/08 * * * "On March 31, 2008, in accordance with 10 CFR 50.72(b)(2)(xi), notification was made for an event or situation related to the protection of the environment for which a notification to another government agency was made. This report was made when a self-identification call was made to the State of Ohio Environmental Protection Agency (EPA) offices in Columbus, Ohio, for the discovery of potential non-compliance issues with 40 CFR 261 requirements for the accumulation, storage, and shipment of hazardous waste. Based on further investigation using a Toxicity Characterization Leachate Procedure analysis of the waste, it was determined that the waste was, in fact, non-hazardous and could be shipped for off-site disposal. The requirements of 40 CFR 261 had been and continue to be met." The licensee has notified the NRC Resident Inspector and the State of Ohio. Notified R3DO ( Pelke). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-31
44110 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-03-28 | 2008-03-31 18:19 | 2008-04-18 | AGREEMENT STATE REPORT INVOLVING A PARTIAL EQUIPMENT FAILURE OF AN HDR UNIT DURING A SOURCE EXCHANGE The following information was received from the State of Washington via email (quotations omitted for ease of reading): STATUS: New Licensee: Providence Everett Medical Center City and State: Everett, WA License Number: WN-M0135-1 Type of License: Medical Date and time of Event: 28 March 2008 Location of Event: Everett, WA ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): A Varian Medical Systems (varian) representative was attempting a routine source exchange at the licensee's facility. There were no patients or Medical Center staff involved in the source exchange process. The varian rep noted some trouble with making the "old" source enter the exchange container. After several attempts the rep realized the transfer was not proceeding as expected. The rep telephoned staff at Varian Corporate headquarters for assistance. The decision was made to cut the source wire near the source and place the source assembly into the emergency shielded source container (emergency pig). After the wire was snipped and the cut piece placed into the emergency pig, the rep performed a survey and noticed that the radiation levels were less than expected. At this time the licensee and the Varian rep both notified the Office of Radiation Protection of the event by telephone. The room was locked and barrier tape placed across the door. A Varian recovery team was called for and arrived at the Medical Center, with the source designer, on Saturday, 29 March 2008. An Office of Radiation Protection investigator also joined the team on Saturday to direct the onsite investigation and recovery. The investigation determined that both the dummy wire and the source wire had tried to exit the HDR unit simultaneously. The wires become stuck in the "home switch" part of the HDR. When a wire was cut it had been the dummy wire and not the source assembly wire. The cutoff dummy wire had been placed into the emergency pig which had given lower then the expected dose rate readings. On Saturday, the recovery team successfully retracted the source into the HDR. Testing is underway to determine why the HDR source exchange process had allowed both wires to be sent out at once. A comprehensive written report is expected from the manufacturer within the next few days. Notification Reporting Criteria: WAC 246-220-250 Equipment Failure. Isotope and Activity involved: HDR Sealed Source: Ir-192, approximately 185 GBq (5 Curies). Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None Lost, Stolen or Damaged? (mfg., model, serial number): Varian HDR source model VS2000 (not lost, not stolen, possibly damaged). Disposition/recovery: Source recovered 29 March 2008 by Varian recovery team. Leak test? No "official" leak test yet but several contamination wipe surveys were performed during the course of the recovery. All of these were negative. Vehicle: N/A Release of activity? None Activity and pharmaceutical compound intended: N/A Misadministered activity and/or compound received: N/A Device (HDR, etc.) Mfg., Model; Varian VariSource Ix (Trademark) HDR Exposure (intended/actual); consequences: None to patients and the public. The highest exposure received by a recovery team member was 87 mRem. Was patient or responsible relative notified? N/A Was written report provided to patient? N/A Was referring physician notified? N/A Consultant used? No Event Report # WA-08-020. * * * UPDATE VIA E-MAIL FROM ARDEN SCROGGS TO JASON KOZAL ON 04/18/08 AT 1836 * * * "A written report was received [by the state] from the manufacturer. "The Varian report concluded the cause of the incident was 'the service engineer mistakenly extending the active source wire while the dummy wire was already in the same pathway. This action jammed the dummy and source wires at the home switch and prevented the active wire from properly retracting to the tungsten safe when commanded.' "[The manufacturer] also concluded the likelihood of a licensee / operator recreating this type of event was nil, since the conditions which allowed this to happen are only present when the factory service engineer is working on the unit. "This was originally reported as an equipment failure but now appears to be an error by the manufacturer's representative." Notified R4DO (Clark) and FSME (Von Till). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-04-03
44109 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2008-03-31 13:52 | 2008-03-31 17:11 | 2008-04-02 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP DURING MAINTENANCE ACTIVITIES "Event: At 1352 hours, Unit 2 experienced a Reactor Trip due to a turbine trip. The indicated cause was low condenser vacuum. The exact cause is still under investigation but is believed to be related to a maintenance procedure in progress on the condenser vacuum instrumentation. Post-trip response was normal. Auxiliary power transferred to the start-up source (switchyard) as expected. Main Feedwater was not affected so there was no demand for Emergency Feedwater. A second High Pressure Injection pump was manually started per procedure to maintain Pressurizer level indication on scale. This is a routine action to compensate for post-trip RCS temperature and volume changes. "In an apparently unrelated event, Keowee Hydro Units (KHU) 1 and 2 were shutdown from commercial operation at approximately 1425 hours. During the shutdown, the KHU 1 output breaker failed to open as expected and KHU 1 was manually locked out. The lockout removed both the Overhead and Underground Power Paths from service, making on-site emergency power unavailable to all three Oconee units. Per Tech Specs, a gas turbine unit at Lee Steam Station was started and used to energize the Oconee Standby Bus at 1518 hours. "Initial Safety Significance: There is little or no safety significance to the Unit trip. The subsequent KHU 1 lockout removed both the Overhead and Underground Power Paths from service, making on-site emergency power unavailable until the Lee gas turbine was aligned. There was no demand for the Keowee emergency power function during either event. "Corrective Action(s): Investigations are in progress as to the cause of the Reactor Trip and the KHU 1 lock out. Alignment of KHU 2 to the underground is currently on hold, pending evaluation of the problem which led to the KHU 1 lockout." All control rods fully inserted with decay heat being removed via the turbine bypass valves. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1055 EDT ON 04/02/08 FROM COREY GRAY TO HOWIE CROUCH * * * The licensee is retracting a portion of the original report identified under 10CFR50.72(b)(3)(v)(D) based on the following: "Event: UPDATE: "At 1352 hours, Unit 2 experienced a Reactor Trip due to a turbine trip. The indicated cause was low condenser vacuum. The exact cause is still under investigation but is believed to be related to a maintenance procedure in progress on the condenser vacuum instrumentation. Post-trip response was normal. Auxiliary power transferred to the start-up source (switchyard) as expected. Main Feedwater was not affected so there was no demand for Emergency Feedwater. A second High Pressure Injection pump was manually started per procedure to maintain Pressurizer level indication on scale. This is a routine action to compensate for post-trip RCS temperature and volume changes. "In an unrelated event, Keowee Hydro Units (KHU) 1 and 2 were shutdown from commercial operation at approximately 1425 hours. During the shutdown, the KHU 1 output breaker, ACB-1, failed to open as expected and KHU 1 was manually locked out. The lockout removed KHU 1 and the Overhead Power Path from service due to the failed ACB. Because KHU 1 was the unit aligned to the Underground Power Path, Operations declared that path inoperable also. "This condition was initially reported as making on-site emergency power unavailable to all three Oconee units. Per Tech Specs, a gas turbine unit at Lee Steam Station was started and used to energize the Oconee Standby Bus at 1518 hours. In this alignment, the Lee gas turbine provides the on-site emergency power function. "A design feature allows a KHU to automatically align to the Underground Path when the unit originally aligned to that path has been locked out, the overhead path is locked out and an emergency start signal exists. Keowee Operations confirmed that during the lockout event the required lockout signals were present on KHU 1 such that KHU 2 would have aligned to the Underground Power Path if an emergency start demand had occurred. As a result, the Underground Power Path remained available during this event and there was no loss of safety function. Therefore the portion of the event related to 10CFR50.72(b)(3)(v)(D) is RETRACTED. "The Underground Power Path was administratively inoperable because a surveillance (SR 3.8.1.3) to verify operability of KHU 2 to the underground path, required per TS 3.8.1 Condition C.1, could not be performed. The surveillance procedure utilizes a normal start signal, which was inhibited by the lockout on the overhead path. The surveillance procedure does not include provisions for using an emergency start signal. At 1906 hours, after the overhead lockout had been reset, KHU 2 successfully completed an Operability test aligned to the Underground Power Path. "Investigation determined that the failure of ACB-1, the output breaker for KHU 1, was due to a terminal strip sliding link in the trip circuit being in an intermediate position. It was damaged during repair so the entire sliding link block was replaced. The unit was successfully tested connected to each power path and was declared Operable on 4-1-08 at approximately 0600 hours. At 0930 hours on 4-1-08 the standby bus was disconnected from Lee. "Initial Safety Significance: "There is little or no safety significance to the Unit trip. The subsequent KHU 1 lockout removed the Overhead Power Path from service. The Lee gas turbine was aligned to energize the standby bus. Operations and Engineering subsequently confirmed that on-site emergency power remained available via KHU 2 and the Underground Power Path. There was no demand for the Keowee emergency power function during either event. "Corrective Action(s): "Investigation as to the cause of the Reactor Trip continues. Unit 2 is now on-line at low power and is in the process of returning to full power. "ACB-1, the output breaker for KHU 1, terminal strip sliding link has been repaired/replaced; both KHUs have been tested and declared operable; the Lee gas turbine has been secured." The licensee informed the NRC Resident Inspector. Notified R2DO (Evans). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-03-31
44108 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2008-03-31 08:00 | 2008-03-31 10:50 | 2008-03-31 | OFFSITE NOTIFICATION DUE TO MINOR GAS SPILL "At or about 0800 on 3/31/08 it was reported that a petroleum sheen was observed in the parking lot headed for the creek. Upon investigation from the responding spill team and Maintenance, the source of the sheen was found to be coming from an employee's vehicle. It was a very minor drip of petroleum (less than 1/2 cup) that was pushed by the rain to the soil and storm catch basin. A boom was put in place to avoid the sheen from entering the creek. The parking lot and soil were cleaned and a catch device was placed under the vehicle. New York State Department of Environmental Conservation (DEC) - Avon Spill Unit- was notified and assigned spill number 0751599 to the event. No further action is required." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-31
44107 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-03-29 10:00 | 2008-03-29 17:59 | 2008-03-29 | OIL WASTE DISCHARGE INTO STORM DRAIN ONSITE "On 3/29/08 at approximately 1100, oil waste was discharged from Units 1 and 2 into a storm drain which discharges into the cooling canal system. The discharge created an oil sheen approximately 10 feet in diameter. The oil slick is currently contained within an oil boom. The Department of Environmental Resource Management for Miami-Dade County was notified of the event at 1715." This was a minor leak contained entirely within the owner controlled area with no path to major waterways. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-29
44106 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-03-29 06:49 | 2008-03-29 09:49 | 2008-03-29 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED OFFSITE "While in Mode 6 / refueling, a contract scaffold builder received a cut to the leg while working in the containment building and was transported to Coffey County Hospital prior to the area under the pressure bandage having the radiological survey completed. This report is being submitted per the requirements of 10 CFR 50.72(b)(3)(xii). "Upon arrival at the hospital the radiological survey was completed and no contamination identified." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2008-03-29
44105 | 0 | WILLIAMSPORT HOSPITAL |  |  |  |  | 2008-03-28 13:00 | 2008-03-28 15:35 | 2008-03-28 | UNPLANNED DOSE TO FETUS "A written directive was completed on 3/18/08 prescribing 18 mCi of I-131 (capsule) for the treatment of hyperthyroidism on 3/28/08. The [prescribing physician] indicated on the form that pregnancy test was negative and she was not breastfeeding. The pregnancy test result was attached to the directive. "Upon arrival the patient completed an assessment form and consent form and she indicated in writing that she was not pregnant or breastfeeding. Staff and authorized user verified patient identity (name and birth date), dose, dose calibrator setting, and route of administration. The patient received the dose as prescribed. "Nuclear Medicine was contacted by the lab shortly after the administration with a positive pregnancy result that was done on the day of the therapy. The patient's physician was notified. The patient was notified to increase fluids and void frequently and advised to make an appointment with her OBGYN physician. [A] Health Physicist Consultant was also notified and [the hospital] is awaiting the dose calculation to the embryo." At the time of the report, the hospital had not calculated a dose to the unborn child. The hospital will provide the calculated dose when it is available but the Radiation Safety Officer believes that the result will be less than 50 milliSieverts (< 5 rem). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | HOS | [5 empty] | 0 | 2008-04-03
44104 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-03-28 10:00 | 2008-03-28 15:25 | 2008-04-02 | FILTERS NOT SCANNED PROPERLY FOR ACTIVITY PRIOR TO PACKAGING "Some contaminated cartridge filters were placed/packaged in two (2) 55-gallon drums based on nominal values of U-235 content as opposed to measured values (i.e., some filters were not measured by the segmented scanning system). "The control system is the scanning of the contaminated filters [individually]. The deficiency was the failure to scan the filters [individually] prior to placing the filters into drums. [Filters packaged in drums are required to be NDA scanned prior to packaging. This is an item relied on for safety (IROFS). Not scanning some filters was a degradation of an IROFS.] "Written instructions were issued to operations personnel to package contaminated processing cartridge filters. The instructions indicated that the filters had been previously scanned and the U mass values were listed in an attachment to the instructions. However, some of the filters were not scanned, and instead were assigned nominal U-235 mass values. Nominal values are based on process history. Nuclear Criticality Safety required each filter to be scanned prior to being loaded/packaged into drums. Approval of the instructions was based on the implication that all of the cartridge filters had been scanned. "The two (2) drums were scanned to confirm the total U-235 mass in each drum. The activity to package the filters has been suspended until additional corrective actions can be completed. "The criticality safety significance is low due to the low U-235 mass values for each filter in addition to the low total U-235 mass for each drum [less than 350 grams U-235 process limit]. In addition, the nominal U-235 values are based on historical records and provide a good estimate of the U-235 content. "Initial activities to inspect the filters and the use of nominal values prevented the drum limits from being exceeded. "There were no actual or potential safety consequences to workers, the public, or the environment." The licensee notified the NRC Resident Inspector. * * *UPDATE ON 4/2/2008 AT 1615 FROM R. SHAKELFORD TO M. ABRAMOVITZ * * * NFS is preparing a press release in anticipation of inquiries from the media. The licensee will notify the NRC Resident Inspector. Notified R2DO (Evans), NMSS (Whaley) and Fuel Cycle OUO (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-03-31
44103 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2008-03-27 19:07 | 2008-03-27 21:38 | 2008-03-27 | FATALITY OF LICENSEE EMPLOYEE "OSHA was notified at 2055 on 3/17/08, under 29 CFR 1904, of the fatality of an employee caused by an apparent heart attack while at work." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-27
44102 | -1 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-03-27 16:45 | 2008-03-27 20:27 | 2008-05-23 | UNACCEPTABLE FLAW FOUND IN RPV CAP TO PIPE WELD "At 1645 EDT, it was determined that an unacceptable flaw existed in reactor pressure vessel penetration N9. This penetration leads to a capped line and the flaw is in the cap-to-pipe weld. Based on manual ultrasonic examination, the flaw is 6.2 inches in length on a 5.5 inch OD pipe. Using non-qualified ultrasonic sizing techniques, the flaw is estimated to have a maximum depth of 30 percent through-wall. The flaw was discovered during in-service inspection examination of this penetration, using an improved technique compared to the technique used during a 2004 inspection. The flaw has been found unacceptable per paragraph IWB-3514.4 of the 1989 Edition of ASME Section XI Code and is therefore reportable. A weld overlay repair is being planned. "The safety significance of this is minimal. Unit 1 is currently in a refueling outage. Repairs of the affected weld will be completed prior to startup." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY BILL MURRAY TO JASON KOZAL AT 0946 ON 5/23/08 * * * "On March 27,2008, at 2027 hours, the Control Room Supervisor made a notification (Event Number 44102) to the NRC Operations Center in Accordance with 10 CFR 50.72(b)(3)(ii)(A) (i.e., any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded). The notification was made as a result of determining that an unacceptable flaw existed in the reactor pressure vessel penetration N9 (control rod drive system return line) nozzle-to-pipe cap weld. At the time of discovery, based on manual ultrasonic examination, the flaw was determined to be 6.2 inches in length on a 5.5-inch OD pipe. Using non-qualified ultrasonic depth sizing techniques, the flaw was estimated to have a maximum depth of 30 percent through-wall. The flaw was found unacceptable in accordance with paragraph IWB-3514.4 of the 1989 Edition of ASME Code, Section XI and therefore was reportable. "Basis for Retraction "On March 30, 2008, manually indexed phased-array ultrasonic examination of the CRD return line nozzle-to-array caw weld was preformed. Based on these inspections, it was determined that the indication does not exhibit stress corrosion cracking characteristics and is not consistent with ultrasonic responses associated with inside diameter (ID) connected geometry. Therefore, the CRD return line nozzle-to-pipe cap weld is acceptable from an ASME Code Section XI perspective. On this basis, the indication did not result in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded and the issue is not reportable under 10 CFR 50,72(b)(3)(ii)(A). "Investigation of this condition is documented in the corrective action program in Nuclear Condition Report (NCR) 272454. "The NRC resident was notified of this retraction." Notified R2DO (Vias). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-03-27
44101 | 0 | HIRO MAKINO |  |  |  |  | 2008-03-27 10:00 | 2008-03-27 17:58 | 2008-03-27 | PACKAGE EXTERNAL CONTAMINATION ABOVE LIMITS At 1000 HST on 03/27/08 a package containing 3 unit doses of Tech 99 (M) was delivered by Pacific Radiopharmacy to the licensee. Wipe survey of shipping bag handle revealed 20000 dpm on a 300 square centimeter wipe. A single wipe of all three unit dose pigs revealed 14000 dpm. The delivery carrier was notified and reported that no contamination was found on the transport vehicle or the driver. The unit dose pigs were decontaminated and the shipping bag was stored for decay. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2008-03-27
44100 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-03-26 14:57 | 2008-03-26 23:04 | 2008-03-26 | 24 HOUR REPORT OF DEGRADED CRITICALITY CONTROL "At 1410, on 3/26/08 the Plant Shift Superintendent was notified that a violation of a nuclear criticality safety approval (NCSA) had occurred. During a review of pre-removal NDA [Non destructive assessment] inspection in C-337 for the unit 3 cell 10 stage 2 converter inspection port, it was discovered that the NDA was performed on the wrong side of the converter (measurement taken on the east side of the converter, and the access hole was cut in the west side). The pre-removal NDA inspection was improperly performed resulting in a violation of NCSA GEN-10. The purpose of the requirement is to determine the initial handling category of the equipment. "Two independent post removal NDA measurements were performed on the adjacent system and two independent visual inspections were performed on the removed item that demonstrated the item and adjacent system were each UH [uncomplicated handling]. The results indicate the equipment was properly classified as UH based on the resulting mass. "SAFETY SIGNIFICANCE OF EVENTS: Although a leg for double contingency was lost, the correct equipment handling category was used. Additionally, an independent verification of no visible uranium present on the removed item has been successfully performed in accordance with applicable procedures to NCS Exempt the item. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRIT!CALITY COULD OCCUR): The equipment contained less than a safe mass of uranium and the equipment was covered to prevent exposure to a moderator. The uranium mass would have had to exceed a critical mass. The equipment would then need to be exposed to sufficient moderator in order for a criticality to be possible. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY CONCENTRATION, ETC.): The process condition relied on for double contingency for this scenario is mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The NDA measurement indicated less than 674 grams at 1.6679 wt% U-235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on mass. Prior to opening the system a pre-removal NDA is required to be performed to initially classify the handling category of the equipment. Since the pre-removal NDA was performed on the wrong side of the equipment potentially resulting in an improper handling categorization, this control was violated. The second leg of double contingency is based on mass by performing a post-removal NDA of the removed equipment and adjacent system within 24 hours to verify the handling category. This control was not violated. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: On 3/26/08, a second post removal NDA was completed on the adjacent system and a second visual inspection was performed on the removed item in order to verify the handling category is UH and re-establish double contingency. "The NRC Senior Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-08-0906; PGDP Event Report No. PAD-2008-08" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-03-26
44099 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-03-26 10:45 | 2008-03-26 15:45 | 2008-03-26 | CONTROL ROOM PRESSURE BOUNDARY DOOR BLOCKED OPEN "At 1045 EDT, it was recognized that Auxiliary Building Door R5-6 is a Control Center Pressure Boundary door. The door was blocked open at approximately 1400 on 3/24/2008 to support draining for on going maintenance on Division 1 CCHVAC Chiller. Upon recognizing this condition, Tech Spec 3.7.3 Action B.1 was entered for an inoperable Control Center Pressure Boundary at 1045 EDT [03/26/2008], with a 24 hour action to restore the boundary to operable status. Actions were taken to close Door R5-6 at 1120 hours [03/26/2008], and Tech Spec 3.7.3 Action B.1 was exited. This event is being reported per 10CFR50.72(b)(3)(v) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of the Control Room Emergency Filtration (CREF) system. The accident mitigation function of CREF could not be assured during the time Door R5-6 was open without administrative controls to close it, if necessary." The licensee notified the site NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-03-26
44098 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-03-25 | 2008-03-26 14:48 | 2008-03-26 | AGREEMENT STATE - CALIFORNIA - STOLEN TROXLER GAUGE The State provided the following information via email: "On March 25, 2008, a Troxler M/D gauge, Model 3411, Serial Number 6520 was stolen from a URS company pick up truck during the evening. According to the RSO, the gauge was stolen from inside a locked container, which was stored in a locked camper shell, within a locked gated garage at the employees residence. The employee had taken the gauge to his residence in preparation for an early morning job. The density gauge was stated to contain approximately 9 mCi of Cesium 137 and 44 mCi of Americium 241. " CA Report #032608 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-03-31
44097 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-03-26 07:22 | 2008-03-26 14:30 | 2008-03-26 | FITNESS FOR DUTY - NON-LICENSED CONTRACT SUPERVISOR "At 0722 on March 26, 2008 at the Beaver Valley Power Station, a contract non-licensed supervisor tested positive for a controlled substance during a pre-access test. This person's access authorization has been denied and is not currently on site. This is being reported pursuant to 10 CFR 26.73(a)(2)(ii). The NRC resident inspector has been notified of the event." Contact the Headquarters Operations Officer for additional Information | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2008-03-26
44096 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-03-26 11:07 | 2008-03-26 13:54 | 2008-03-26 | OFFSITE NOTIFICATION DUE TO MINOR OIL SPILL "On March 26, 2008, at approximately 11:07 hours, an oil sheen was discovered outside the Indian Point cooling water discharge canal in the Hudson River. In accordance with the Indian Point Spill/Release plan, a spill or leak causing a visible sheen in the river as a result of the release of a petroleum product requires a notification to the New York State Department of Environmental Conservation (NYS DEC) and the National Response Center (U.S. Coast Guard). The National Response Center was notified at 11:16 hours and the NYS DEC was notified at 11:38 hours. The source and cause of the petroleum product spill/leak is under investigation. An environmental cleanup vendor was contacted and is scheduled to be on site the afternoon of March 26, 2008, for assessment and cleanup." The licensee notified the site resident inspector. R1DO notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-26
44095 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-03-26 07:58 | 2008-03-26 10:50 | 2008-03-26 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF EMERGENCY SIRENS "At 0758 CDT, on March 26, 2008, the Goodhue County dispatcher inadvertently activated the Goodhue County sirens from the primary unit during the conduct of a silent siren test. As per procedure they were to send out two silent signals; however the first was the silent and the second signal was the activation. Upon selecting the alert, they immediately sent out a signal to cancel the activation. Thirty-two of the 117 sirens in the 10-mile Emergency Planning Zone (EPZ) were activated for approximately 14 seconds. The licensee was notified of the siren activation by the activation signal received on the informer unit in the Technical Support Center (TSC) as well as hearing the sirens being activated. Goodhue County Emergency Management contacted the local radio station at 0805 [hrs. CDT] to notify the public of the false activation. No press release is planned by Xcel Energy. No other press release is planned by Goodhue County." The licensee notified the NRC Resident Inspector. | 76 | 100 | 0 | 76 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-26
44094 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-03-25 18:49 | 2008-03-25 20:24 | 2008-03-28 | LOSS OF OFFSITE POWER DUE TO STATION AUXILIARY TRANSFORMER FAULT "At 1835 on March 25, 2008, Unit 2 experienced a Loss of Offsite Power. At 1849, an Unusual Event was declared. Station Auxiliary Transformer (SAT) 242-2, Phase C, experienced a Phase Overcurrent. This resulted in an isolation of the SAT, a loss of offsite power, and an automatic Fire Protection deluge of the SAT. No fire was confirmed. All equipment responded as required. The appropriate abnormal operating procedure was entered for event mitigation and is in progress. The Unit 2 Emergency Diesel Generators are supplying required safety-related power. Unit 2 remains at power." The plant is stable and all equipment is functioning as required. The licensee is assessing a cross-tie to Unit 1 which is unaffected by this event and in the refueling mode. The licensee notified the State and local authorities and the NRC Resident Inspector. Notified DHS (Greg Ray), FEMA (Erwin Casto), DOE (Sal Morrone), USDA (Timmons), HHS (Rick Turner), EPA/NRC (Petty Officer Thompson Report #866038). * * * UPDATE BY SCOTT PURIN TO NRC AT 2230 EDT ON 3/25/08 * * * The emergency buses on Unit 2 have been re-energized by offsite power supply sources via Unit 1 SAT. The Unit 2 EDGs have been secured and placed back in standby. The licensee is developing a recovery plan to restore a Unit 2 SAT to supply offsite power to Unit 2 loads. This will require such things as analyzing chemistry samples of the affected SAT transformers and assessing the protective relaying. In addition, some switchyard realignment will be necessary. The licensee is currently in a 72 hour LCO under Tech Spec 3.8.1 for the current electrical alignment. The NRC Resident Inspector is onsite and the NRC Region continues to monitor the situation. * * * UPDATE FROM STEVE WIDOLFF TO HOWIE CROUCH AT 0022 EDT ON 3/28/08 * * * "At 2309 [hrs. CDT] on 3/27/08, Byron Unit 2 terminated an Unusual Event that was declared at 18:49 on 3/25/08, in accordance with EAL M.U.1 due to a loss of offsite power to transformers 242-1 and 242-2. "Transformer 242-1has been energized from offsite power and is supplying Unit 2 ESF busses 241 and 242. The entry conditions for M.U.1 are no longer met. A press release will be issued." Transformer 242-2 is out of service and isolated for repairs. The licensee notified the NRC Resident Inspector. Notified R3DO (Hills), NRR EO (Ross-Lee), IRD (McDermott), DHS SWO (Doyle), FEMA (Liggett), DOE (Morrone), EPA (Allison), USDA (Timmon) and HHS (Dalziel). | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-03-25
44093 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-03-25 15:22 | 2008-03-25 17:06 | 2008-03-25 | LOSS OF HEALTH PHYSICS VENTILATION SYSTEM USED FOR EMERGENCY RESPONSE "Shift received alarms which lead to the discovery of MCC 1 R24-S030 being de-energized. This MCC supplies power to the Health Physics emergency HVAC air handling unit (1Z41-B100). Maintenance has been notified and is currently working to restore the system to OPERABLE status. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, rev. 2 as an emergency facility (Plant Hatch Operational Support Center) affected due to the Health Physics emergency HVAC out of service." The licensee notified the NRC Resident Inspector. | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-25
44092 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2008-03-25 08:40 | 2008-03-25 15:26 | 2008-03-25 | PLANT SHUTDOWN INITIATED DUE TO DEGRADED BATTERY VOLTAGE "On March 25, 2008 at approximately 0640 PDT, SCE discovered a battery with voltage slightly below Technical Specification limits. At approximately 0840 PDT, plant operators began cooling Moisture Separator Reheaters (MSR) in preparation for a Shutdown as required by TS 3.8.4. Initiating MSR cooldown reduced reactor power by 0.1%. Although plant operators had not initiated boration or control rod insertion, SCE is, nevertheless, reporting this occurrence in accordance with 10CFR50.72(b)(2)(i). "At approximately 0850 PDT, the battery was restored to Operable status and MSR cooldown was suspended. At approximately 1112 PDT, the Unit was returned to full power. SCE is continuing to assess if additional actions are required. "At the time the shutdown was initiated, Unit 2 was operating at about 100% power. Unit 3 continues to operate at about 100% power. The NRC Resident Inspectors have been briefed on the shutdown plans and will be provided with a copy of this report." Preliminary information indicates that the degraded voltage was due to loose terminal bolts. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-03-25
44091 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-03-25 11:18 | 2008-03-25 14:38 | 2008-03-25 | INADVERTENT ACTUATION OF EMERGENCY DIESEL GENERATOR DURING SURVEILLANCE TESTING "On March 25, 2008, during scheduled monthly testing per surveillance procedure M628, '480 Volt Undervoltage Degraded Grid Protection System Bus 5A Functional', an Instrumentation & Control technician conducting the test inadvertently caused an undervoltage condition on 480 volt AC safeguards Bus 5A, resulting in the automatic actuation of the associated Emergency Diesel Generator (EDG)-33. In accordance with design EDG-33 started and loads on Bus 5A were stripped and required loads were sequenced back onto Bus 5A. All equipment performed as designed. Normal power for Bus 5A has been restored and all equipment returned to pre-event condition. Investigation into the cause of the event is in progress. Unit 2 is currently in a refueling outage and was unaffected. Licensee has notified the NRC Resident Inspector and the State Public Service Commission." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-03-25
44090 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2008-03-24 22:48 | 2008-03-24 23:48 | 2008-03-25 | SPDS OOS FOR PLANNED MAINTENANCE "Arkansas Nuclear One, Unit 2 is removing power from the Safety Parameters Display System (SPDS) for 18 month preventative maintenance and scheduled corrective maintenance. SPDS is a computer based system that is utilized by both Unit I and Unit 2 to provide critical information during an emergency. Unit 2 is currently performing a refueling outage. Compensatory measures are being taken to ensure necessary backup monitoring is established on Unit 1, the operating unit. The duration of the maintenance is scheduled for approximately 24 hours." The licensee notified the NRC Resident Inspector, and the Arkansas Department of Health. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-25
44089 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2008-03-23 22:16 | 2008-03-24 01:56 | 2008-03-24 | MANUAL REACTOR TRIP - LOSS OF SPEED ON MBFP "The Indian Point Unit 2 reactor was manually tripped from 94% power at 2216 on 3/23/08 due to a loss of speed on 22 main boiler feed pump (MBFP). Indian Point Unit 2 is currently in mode 3 with all automatic actions for a manual reactor trip occurring as required. Indian Point Unit 2 was in a coast down in advance of a scheduled refueling outage. "The reactor was manually tripped as required by abnormal operating procedure 2-AOP-FW-001. All control rods inserted on the trip. No safety or relief valves lifted due to the trip. The motor driven aux feedwater pumps automatically started on low steam generator level and are being used to maintain steam generator level. Condenser steam dumps are maintaining reactor temperature. The Unit 2 electrical lineup is the normal shutdown electrical lineup. The licensee has notified the state Public Service Commission. "Unit 3 was unaffected and remains in mode 1 at 100% power." The licensee has notified the NRC Resident Inspector. The licensee expects to issue a media release. | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-03-24
44088 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-03-22 19:39 | 2008-03-22 20:50 | 2008-03-22 | TURBINE TRIP RESULTING IN A REACTOR SCRAM "Limerick Unit 1 automatically shutdown from a turbine trip at 1939 hrs on 03/22/08. The cause of the turbine trip is under investigation at this time. All control rods inserted as required. No ECCS [Emergency Core Cooling System] and no RCIC [Reactor Core Isolation Cooling] initiation occurred. No primary or secondary containment isolations were received. "The plant is currently in Hot Shutdown maintaining normal reactor level with feedwater in service." Minimum water level after the scram was 5 inches. Level 3 had been reached however all level 3 isolation valves were already shut. No SRVs lifted after the scram. Decay heat is being removed by steam loads with the turbine bypass valves available if needed. The plant is in its normal shutdown electrical lineup. The licensee will issue a press release and has informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-03-22
44087 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-03-22 10:35 | 2008-03-22 11:01 | 2008-03-23 | LOSS OF SPDS/ERDS COMPUTER SYSTEM GREATER THAN 8 HOURS "At 1035 hours, on 03/22/2008, the Unit 1 SPDS and ERDS system was removed from service to disconnect and remove a temporary power supply to support a planned maintenance outage on the PICSY computer normal power supply. The disconnection and removal of temporary power is expected to have a duration greater than 8 hours, but less than 24. During this time, control room hardwire indications will be available. An update will be provided when SPDS/ERDS becomes available. "Since the Unit 1 SPDS/ERDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10 CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * UPDATE FROM JIM HUFFORD TO JOHN KNOKE AT 0423 EDT ON 3/23/08 * * "This is a follow-up courtesy notification to EN# 44087. As of 0213 EDT, on 03/23/08, Unit 1 ERDS and PICSY are now fully restored. The planned outage activities are now complete. No further maintenance scheduled." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-22
44086 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-03-21 15:25 | 2008-03-21 17:59 | 2008-03-21 | AUTOMATIC REACTOR SCRAM FROM A MAIN TURBINE TRIP "Actuation of an RPS signal while the reactor was critical. "At 1525 a generator trip signal on the main transformers initiated a reactor scram due to Turbine Stop and Control Valve fast closure. Safety relief valves operated initially to lower reactor pressure. Turbine bypass valves operated initially to lower reactor pressure. Turbine bypass valves are maintaining pressure control currently. Reactor recirc pumps A and B transferred to slow speed operation as expected. No ECCS initiations were received. Reactor level is being controlled with normal systems condensate and feedwater. Lowest level indicated was approximately -6" wide range. Level 3 initiations occurred to group 3 isolation valves. No valves operated, they are normally closed." The site is investigating the cause of the trip. A probable cause is the "C" phase differential trip which was received from the main transformer. All control rods fully inserted during the scram. The plant is on its normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-03-21
44085 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-03-21 09:13 | 2008-03-21 16:40 | 2008-03-22 | SYSTEM INJECTION DETERMINED INOPERABLE BY FAILURE TO REMOVE ELECTRICAL JUMPER PRIOR TO MODE CHANGE "In accordance with Instrument Maintenance Instruction (IMI) 99.040, 'Auto Safety Injection (SI) Block, Feedwater Isolation Block, and Maintain Source Range In Service Jumpers,' jumpers were placed to block the SI automatic actuation logic and actuation relays during WBNs [Watts Bar Nuclear] Cycle 8 refueling outage. The automatic actuation function for SI is required in Modes 1, 2, 3, and 4 per Function 1.b of Table 3.3.2-1 of Technical Specification (TS) 3.3.2, 'ESFAS Instrumentation.' WBN entered Mode 4 at 0020 EDT on March 20, 2008 and Mode 3 at 0100 EDT on March 21, 2008. On March 21, 2008, it was discovered that the jumpers installed per IMI-99.040 had not been removed. Due to this, Limiting Condition for Operation (LCO) 3.0.3, was entered at 0913 EDT and exited at 0958 EDT when the system was restored. The jumpers being in place in Mode 4 and 3 rendered both trains of SI automatic actuation inoperable for approximately 33 hours and 38 minutes. This event is being reported under 10 CFR 50.72(b)(3)(v)(D), 'Event or Condition that could have Prevented Fulfillment of a Safety Function.'" The licensee attributes the error to a combination of both procedural inadequacy (i.e., the step removing the jumper did not require verification) and personnel error. The licensee informed the NRC Resident Inspector. * * * UPDATE PROVIDED BY DOUGLAS HOLT TO JOE O'HARA AT 0213 ON 03/22/08 * * * "This is a follow-up notification to EN#44085 to amend reported information. At 2133 on 3/21/08 when permissive P-11(Low Pressure and Low Steamline Pressure) blocks were cleared, the on-shift crew questioned the presence of the 'AUTO SI Blocked' alarm and determined that it should have been cleared when the SI automatic logic jumper was removed earlier in the day. The crew utilized the procedural guidance of GO-1 to cycle the reactor trip breakers and reinstate the automatic safety injection logic at 2206 on 3/21/08. The previous report that identified that LC0 3.0,3 was exited at 0958 EDT is to be amended. LCO 3.0.3 was exited at 2206 when SI automatic logic was completely reinstated by cycling the reactor trip breakers." The licensee notified the NRC Resident Inspector. Notified R2DO(Ernstes) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-03-21
44084 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-03-20 08:13 | 2008-03-20 15:48 | 2008-03-20 | TRAFFIC ACCIDENT CAUSES LOSS OF POWER TO TEN EMERGENCY SIRENS "On March 20, 2008, between 0813 and 0818 power to 10 of the 78 sirens in Washington County was lost. They lost power due to a vehicle hitting a power pole. None of the 10 have battery back up power. The sirens are located south of the city of Fort Calhoun, in southeast Washington County. By 1200 power had been restored to 8 of the 10 sirens. The remaining sirens are awaiting replacement of power poles supporting supply lines to restore power. Pole replacement is in progress." The licensee notified the NRC Resident Inspector, state, and local officials. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-20
44083 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2007-12-15 | 2008-03-20 13:45 | 2008-03-27 | AGREEMENT STATE REPORT INVOLVING IMPROPER DISPOSAL OF TRITIUM EXIT SIGNS In December, 2007, the Regal Cinemas complex was sold and underwent renovation by a contracting company, PM Renovations. The contractor removed and disposed of fifty (50) general licensed tritium exits signs. The signs were manufactured by Best Lighting Products, Model # SLXTU1GB20, serial #'s 115741 through 115790. Each sign contained 11.47 Curies of tritium. The State of Maine during an inspection on 03/11/08 noticed that the signs had been removed and is pursuing discussions with PM Renovations as to their final disposition. The signs may have been taken to one of two landfills located in Norridgewock, ME or Hampden, ME or incinerated. If the signs were disposed of in a landfill, the State will perform an assessment to determine potential impact on water supply. * * * UPDATE FROM S. SEELEY TO P. SNYDER ON 3/27/08 AT 1443 * * * The following information was received from the State of Maine via facsimile: "The event is not yet closed by the State. We are still trying to locate the final resting place of the missing signs. We are also working with our Dept. of Environmental Protection for further action." Additional information received by the State from PM Renovations suggests that the signs could have gone to the Juniper Ridge landfill facility in Old Town, ME. Notified R1DO (Bellamy) and FSME (McConnell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2008-03-25
44082 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC. |  |  |  |  | 2008-03-20 | 2008-03-20 12:32 | 2008-03-20 | PART 21 REPORT INVOLVING POTENTIAL FAILURE OF CERTAIN ROSEMOUNT PRESSURE TRANSMITTERS The following information was received via fax: "Re: Notification under 10 CFR Part 21 for certain Model 3051N Pressure transmitters "Pursuant to 10 CFR Part 21, section 21.21(b) Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you that a limited number of Model 3051N pressure transmitters listed in the attachment may exhibit erratic, unstable output prior to an off-scale failure. The affected transmitters were shipped from RNII between March 31, 2002 and November 20, 2002. "1.0 Name and address of the individual providing the information: "Mr. Marc D. Bumgarner Vice President & General Manager Rosemount Nuclear Instruments, Inc. 8200 Market Boulevard Chanhassen, MN 55317 "2.0 Identification of items supplied: "Certain Model 3051N pressure transmitters identified in the attachment. "3.0 Identification of the firm supplying the item: "Rosemount Nuclear Instruments, Inc. 8200 Market Boulevard Chanhassen, MN 55317 "4.0 Nature of the failure and potential safety hazard: "The Model 3051N Smart Pressure Transmitter is dedicated for nuclear use consistent with the requirements of 10 CFR Part 21. It is qualified for use in safety related applications per IEEE 323-1983 (mild environment) and IEEE 344-1987 for seismic applications as documented in its associated qualification reports. "The Model 3051N pressure transmitter contains an application-specific integrated circuit (ASIC) which performs the Digital to Analog Conversion (DAC). Procurement and production records indicate that a limited number of Model 3051N pressure transmitters manufactured between January 2002 and October 2002 have DAC ASICs which may contain phosphorus as the encapsulation material. "ASIC industry experts have since determined that under certain conditions the phosphorus compound can lead to reduced insulation resistance of the integrated circuit, with potentially adverse impact on performance. As a result, ASIC and IC manufacturers eliminated the use of phosphorus in their products. Industry experts have examined the performance of phosphorus materials in electronic circuits under various conditions and estimated a potential ASIC failure rate of approximately 1% for the general population of phosphorus-containing electronic circuits. "Three Model 3051N transmitters have recently been returned to RNII due to erratic, unstable, or off-scale output. Failure analysis identified the phosphorus-containing encapsulation material of the DAC ASIC as the cause of failure for these transmitters. These transmitters were installed and performing properly for 3-5 years before failure. "Failure of the DAC ASIC depends on several factors, including: "Phosphorus concentration "Spacing of ASIC leads "Voltage driving the ASIC (which affects operating temperature) "Ambient temperature "The observed failure rate of the DAC ASIC in Model 3051N pressure transmitters indicates a potential reliability concern. As a result, notification is being made in accordance with 10 CFR Part 21 to customers that purchased a transmitter from the potentially affected population. A transmitter with a failing DAC ASIC will annunciate itself by erratic or unstable output, followed by off-scale output (high or low). "5.0 The corrective action which is taken, the name of the individual or organization responsible for that action, and the length of time taken to complete that action: "The use of phosphorus in the DAC ASIC was eliminated in October 2002. "Model 3051N pressure transmitters affected by this notification may be returned to RNII for replacement at no charge. "6.0 Any advice related to the potential failure of the item: "The end user is advised to determine the impact of this potential reliability issue upon its plant's operation and safety, and take action as deemed necessary. Affected transmitters may be returned to RNII for replacement at no charge. "Rosemount Nuclear Instruments, Inc. is committed to the nuclear industry and: remains dedicated to the supply of high quality products to our customers. If you have any questions, or require additional information related to this issue, please contact: Mike Dougherty (205) 865-1112, Gerard Hanson (952) 949-5233, Bob Cleveland (952) 949-5206, or Matt Doyle (952) 949-5204." Facilities affected which were identified in the referenced attachments: Cook Nuclear Plant, Vermont Yankee, Quad Cities Nuclear Station, and Robinson. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2008-03-20
44081 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-03-19 13:40 | 2008-03-20 12:09 | 2008-03-20 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR A non licensed supervisor had a confirmed positive for illegal drugs during a pre-access fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2008-03-20
44080 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-03-18 | 2008-03-20 11:45 | 2008-03-20 | AGREEMENT STATE REPORT INVOLVING LOSS OF GENERAL LICENSED MATERIAL The following report was received via email: "N.C. Radiation Protection Section was notified 19 March 2008 of two (2) missing polonium-210 static elimination devices. Information on the devices is as follows: "1) NRC Model P-2021-8201, serial no. A2FC364, initially distributed on 22 Jun 2006, initial activity was 10 millicuries, decay-corrected activity (as of 18 March 2008) 0.415 millicuries "2) NRC Model P-2021-8201, serial no. A2FK529, initially distributed on 01 Dec 2006, initial activity was 10 millicuries, decay-corrected activity (as of 18 March 2008) 0.935 millicuries "The information will be turned over to the General License Coordinator for further investigation. "N.C. Radiation Protection has not received any media attention as of this report. No press release has been issued." Event Report ID No.: NC-08-13 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-03-25
44079 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-03-20 05:30 | 2008-03-20 07:37 | 2008-04-08 | AGREEMENT STATE REPORT - STOLEN NEUTRON GENERATORS AND LOGGING TOOL A representative of Baker Atlas, a fishing and well-logging company, reported that a F-250 pick-up truck was stolen this morning between midnight and 5:30 a.m. central time. Contained in the truck were 4 neutron generators with a source strength of less than 1 curie each and one well logging source with a source strength of 100 milliCuries of Cs-137. The State of Texas is following up on the report with more details to follow. * * * UPDATE AT 1435 EDT ON 03/20/08 FROM LATISCHA HANSON TO S. SANDIN * * * The following additional details were provided by the State of Texas via email: "Event Description: On March 20, 2008, at 6:25 a.m., the agency received a telephone call from the licensee, reporting the theft of one of the company's vehicles, a Ford F-250 pick-up truck (licensee will find license plate number and submit later) from a hotel in Pharr, Texas, which had four neutron generators and one logging tool that contained a 100 milliCuries (mCi) radioactive material (RAM) stored on the truck. The licensee reported that the crew was from their Pearland, Texas site. The licensee stated the vehicle containing the sources was stolen from the LaQuinta hotel in Pharr, Texas between the hours of 12:30 and 5:00 A.M. on Thursday, March 20, 2008. The licensee immediately contacted the Pharr Police Department and filed a theft report. The licensee further reported that the initial police investigation shows that the vehicle has not crossed into Mexico. "The licensee submitted the following information regarding the stolen equipment: "A. The Cesium source is a Gulf Nuclear CS-2 with an original capsule number of CS2-985. This source was shipped with a tracking ID of S3H01 12. The activity is 3.7 GBq (100 mCi). "B. The Pulsed Neutron Generators (SSDR, along with a section of our Transport Manual showing the container that the tools are carried in and a drawing of the tool section sent to Incident Investigation Program (IIP)). The tools in question are: "1. Generator 370457 mounted in tool 8283PA-10041239 and containing tube 327. "2. Generator 370453 mounted in tool 8283PA-370403 and containing tube 321. "3. Generator 189707 mounted in tool 8283PA-190149 and containing tube 340. "4. Generator 189496 mounted in tool 8283PA-370249 and containing tube 271. "Each of these generators contains less than 37 GBq of H-3. "The licensee stated that their company uses a tracking number system in place of the traditional model/serial numbers. The licensee will try to research the traditional numbers to submit later. "Texas Incident #: I-8496 Notified R4DO (Whitten) and FSME (Burgess). * * * UPDATE AT 1800 EDT ON 04/01/08 FROM LATISCHA HANSON TO S. SANDIN * * * The truck was recovered early morning on Saturday, March 30, 2008 just south of Falfurrias, TX. The search is on-going for the missing rad material. Notified R4DO (Lantz) and FSME (White). * * * UPDATE AT 1923 EDT ON 04/08/08 FROM LATISCHA HANSON TO J. KNOKE * * * The State provided the following information via email: "On April 6, 2008, [licensee] received a call from [their] security consultant stating that the Mission Texas Police Department (PD) had contacted him that a radioactive source had been located near the intersection of Bensen Palms Road and Orange Grove Drive. At 1:08 PM, Officer [delete] of the Mission PD contacted [licensee] and confirmed that the device appeared to be our stolen Cesium Source and that the padlock was intact. [Licensee] dispatched our local District Manager (DM) and an engineer to the location to take possession of the source and transport it to our storage location in Edinburg, Texas. The local DM confirmed that the source was intact and conducted an area survey to ascertain that no contamination had occurred. "The local DM and the engineer will drive the area around the recovery, but at this time there is no sign of the missing Neutron Generators and associated tools." Notified R4DO (Deese), FSME (Kock), ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-03-25
44078 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2008-03-18 | 2008-03-19 16:08 | 2008-03-19 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The licensee provided the following information via facsimile: "The South Carolina Department of Health and Environmental Control was notified at 9:00 a.m. on March 19, 2008 by the licensee that one of their moisture density gauges had been damaged at a work site near Lancaster, South Carolina. According to the licensee, the gauge was damaged after being struck by a large truck at a work location. The licensee reported moderate damage to the gauge and source rod but indicated that the source was in the shielded and locked position. The licensee placed the damaged gauge in its transportation case and transported it back to their business location. The gauge is a Troxler 3400 series containing 9 mCi of Cs-137 and 44 mCi of Am-241 :Be. [The state Duty Officer] is responding to this incident to perform surveys of the gauging device and any other necessary actions. This event is open pending the results of the licensee's and Department's [state] investigation. Notifications and updates will be made through the NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2008-03-24
44077 | -1 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-03-19 11:40 | 2008-03-19 12:32 | 2008-03-25 | POTENTIAL COMPROMISE OF SAFEGUARDS INFORMATION "On 3/19/08 at 1140 EDT, Security determined a potential compromise of safeguards information existed. The information was communicated via email. An investigation has been initiated. This event is conservatively being reported in accordance with 10CFR 73, Appendix G, Section I,(c)." The licensee notified the NRC Resident Inspector. * * * UPDATED AT 12:30 EDT ON 03/25/2008 FROM MARK RAGSDALE TO S. SANDIN * * * After further evaluation, the licensee has determined that this event is a 24 hour loggable event and not a 1 hour report. Contact the Headquarters Operation Officer for further details. The licensee notified the NRC resident inspector. Notified R2DO (Jay Henson) and 73.71 GP via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-03-19
44076 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2008-03-18 12:00 | 2008-03-19 10:24 | 2008-03-19 | RECEIPT OF PACKAGE WITH SURFACE CONTAMINATION The following script was provided in a telephone call to the NRC Operations Center: "My name is Thomas Huston with the Department of Veterans Affairs, VHA National Health Physics Program. This report involves NRC master materials license No. 03-23853-01VA. "I am calling to report receipt of three packages of radioactive material with removable surface contamination on the outside of the package greater than the limits in 10 CFR 71.87(i). "The three packages were received at approximately 1:00 PM ET, March 18, 2008 by the VA Medical Center in West Palm Beach, FL. "Wipe tests performed on the three packages indicated the following removable contamination levels: 24700 dpm/cm2, 12880 dpm/cm2, and 35570 dpm/cm2 as compared to the regulatory limit of 22 dpm/cm2. "The three packages contained Co-57 flood sources and were received from a commercial vendor, Eckert & Ziegler (Isotope Products Laboratories), of Valencia, CA. The final delivery was by common carrier. The final delivery carrier was notified of the contaminated packages at approximately 1630 hrs ET on March 18, 2008 by the VA Medical Center's Radiation Safety Officer. The vendor was notified of the contamination at approximately 1730 hr on March 18, 2008 by the VA Medical Center's Radiation Safety Officer. "The radionuclide involved is believed to be Co-57; however, additional confirmatory measurements are being made. "Additional information: The Department of Veterans Affairs coordinates all reports to the NRC from the NHPP Director's Office located in North Little Rock, AR. NRC oversight for the VA Master Materials licensee is assigned to NRC Region 3. Address of permittee involved in this event: "VA Medical Center, 7305 North Military Trail, West Palm Beach, Florida 33410, VHA Permit Number 09-25328-01." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2008-03-19
44075 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-03-17 | 2008-03-18 18:17 | 2008-03-18 | AGREEMENT STATE REPORT - SHIPPING CONTAINER ARRIVED DAMAGED WITH SOURCE OUTSIDE OF PIG AND CONTAINER The State of California Radiologic Health Branch provided the following information via email: "The licensee shipped a nominal 123 mCi Co-60 source via FedEx in a Type A package from a temporary job site in the State of Washington to their office in Paramount, CA. Upon arrival at the Paramount office, the Type A shipping container was observed to have been damaged, and the Co-60 source was found out of its shielded pig, and outside of the Type A container. Calculation assuming a point source shows that the radiation levels would have been ~170 mr/hr at one meter, ~1.8 R/hr at one foot, and ~1700 R/hr at one centimeter from the source. "The Type A container is constructed of steel, with an inner lead storage pig, and was secured to a wooden shipping pallet. The Type A container has a collar that extends above the lead pig. The cover for the lead pig is secured by a rod that fits through the steel collar. The rod is secured in place by a lock on the rod. Upon receipt of the Type A container at the Paramount, CA facility, the wooden pallet was missing, the lock on the securing rod was missing, the securing rod was not inserted in the holes in the steel collar (therefore it was not securing the cover to the lead pig), and although the inner lead pig cover was in place, the source was found lying on top of the lead pig within the steel collar portion of the Type A container. It is surmised that the Type A container was dropped on the lock during transportation, such that the lock broke, the securing rod was displaced, the cover came off the lead pig, and the source came out of the lead pig. Either the Co-60 source lodged in the steel collar at that time, or the source fell out and someone picked it up and placed it on top of the lead pig within the steel collar of the Type A container (the latter appears more likely). The source is located at one end of an ~3 inch long rod. "The licensee notified FedEx of the event. FedEx's consultant is investigating to determine where and how the damage to the Type A container occurred, and to evaluate the exposures to FedEx personnel. Transportation occurred exclusively on FedEx conveyances, so no significant non-FedEx personnel exposure is expected to have resulted during transportation. A licensee employee reinserted the source in the lead pig before removing the Type A container from the FedEx delivery truck. In doing so he handled the non-source end of the source rod with his bare fingers, while wearing extremity dosimetry. Calculated extremity dose is 100 to 200 mrem based on a 5-10 second handling time." CA Report Number 031708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-03-21
44074 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2008-03-17 19:29 | 2008-03-18 00:09 | 2008-03-18 | UNAUTHORIZED ENTRY Actual entry of an unauthorized person into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operation Officer for additional details. * * * RETRACTION AT 1035 ON 3/18/2008 FROM JIM TURKETT TO MARK ABRAMOVITZ * * * "At 0009 on 3/18/2008 SCE&G reported a potentially reportable security event. After further evaluation SCE&G has determined that this event is a 24 hour loggable event and not a one hour report. The unbadged individual had undergone the appropriate search processes, and was under escort for the duration of the entry into the protected area. A confirmatory search in PADS has verified that this individual met the requirements for access. Therefore SCE&G Is retracting this notification." The licensee notified the NRC Resident Inspector. Notified the R2DO (Lesser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-03-18
44073 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-03-13 | 2008-03-17 18:00 | 2008-03-21 | AGREEMENT STATE REPORT OF LEAKING IODINE-125 SEED The State of Washington Department of Health, Office of Radiation Protection, provided the following information via e-mail: "On 10 March 2008 a patient was implanted with approximately 80 I-125 seeds. On 12 March 2008 (or 13 March 2008, it remains unclear as of this writing), the patient complained of pain and difficulty urinating. A cauterization was performed via the urethra. Upon removal of the cauterization equipment, some seeds also exited via the urethra. One seed, in particular, was visibly different from the rest. This seed was, upon closer observation, noted to be shorter than the others and, in fact, had been damaged. Cause of the damage (shear force during insertion or perhaps a result of the cauterization) has yet to be determined. "A survey of the area including the patient using a Technical Associates TBM-3 showed contamination of the equipment and bodily fluids, while an external reading directly over the thyroid showed levels above background." The activity of the damaged I-125 seed was less than 300 microcuries. Licensee is assessing possible overexposure to the patient, organ dose calculations underway by licensee consultant. * * * UPDATE ON 3/21/2008 FROM ARDEN SCROGGS TO MARK ABRAMOVITZ * * * The State provided the following information via email: "On 10 March 2008 a patient was implanted with 102 I-125 seeds. On 13 March 2008 the patient complained of pain and difficulty urinating. A cauterization was performed via the urethra. Upon removal of the cauterization equipment, 'some' seeds also exited via the urethra. One seed, in particular, was visibly different from the rest. This seed was, upon closer observation, noted to perhaps be shorter than the others and, in fact, had been damaged. Cause of the damage (shear force during insertion or perhaps a result of the cauterization) has yet to be determined, although as of this writing the most logical conclusion would be over-heating from the cauterization procedure. "A survey by the licensee of the area including the patient using a Technical Associates TBM-3 showed contamination of the equipment and bodily fluids, while an external reading directly over the thyroid showed levels above background. "A CT scan was performed on 19 March 2008 to determine the number of seeds remaining in the patient. Results of that scan show the proper number, 92 seeds, remain in the patient of the total 102 implanted. "Seed was damaged, probably from heat, but if not, then from some other mechanism. These were seeds from Best Medical International, Model 2301. "Wipes of the remaining seeds showed contamination levels up to 500 nCi. While all seeds exhibited some detectable counts from the wipes, it is thought that one was actually leaking and had cross-contaminated the others while in storage together. "Bioassay of the patient on 19 March 2008 showed a thyroid burden of 0.8 microcuries, a dose less than 1 Rem to the organ itself." Notified the R4DO (Whitten) and FSME (Delligatti). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-03-20
44072 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-03-17 13:00 | 2008-03-17 16:30 | 2008-03-17 | MANUAL REACTOR TRIP DUE TO LOWERING STEAM GENERATOR LEVEL DUE TO THE LOSS OF 'B' MAIN FEED WATER PUMP "While operating at 100% rated thermal power in Mode 1, a Manual Reactor Trip was initiated due to the lowering of Steam Generator (S/G) level due to the loss of 'B' Main Feed Water Pump. Initial investigation indicates that the loss of XPB03 transformer caused the loss of Non-Class 1E 4160VAC PB03 and PB04. At the time of the event, bus PB04 was cross-tied with bus PB03 for scheduled maintenance of transformer XPB04. This caused loss of all condensate and heater drain pumps. A manual reactor trip was actuated in anticipation of an automatic reactor trip. Aux Feed auto actuation did occur as required. The Non-Safety Related Charging pump was lost due to the loss of PB03 and charging flow was re-established to the Reactor Coolant System by starting 'A' Charging pump. All other plant equipment functioned as required. The plant is currently stable in Mode 3 at 560 degrees F and 2235 psig. Continuing to investigate. "At 15:03 CDT, plant experienced an auto Feed Water Isolation signal due to Low-Low S/G level. Feed Water Isolation had already occurred with the initial event but the signal had been previously been reset. Manual feed water flow control has been established from Aux Feed Water." All control rods inserted into the core during the trip. Decay heat is being removed via the steam dumps to condenser using AFW to feed the steam generators. No primary or secondary relief valves lifted during the transient. The electrical grid is stable and supplying plant safety loads via the normal path. NRC Resident has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-03-17
44071 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-03-17 08:00 | 2008-03-17 15:27 | 2008-03-17 | TECHNICAL SUPPORT CENTER DEGRADED HABITABILITY CONTROL "At approximately 0800 CDT on 3/17/08, operations personnel identified and investigated an issue with excessive noise/vibration of the Technical Support Center (TSC) cleanup fan. Investigation revealed that the TSC cleanup fan exhaust damper set screws, which attach the positioner to the damper shaft, had become loose and were slipping on the damper shaft. With this damper not adequately attached to the positioner the damper cannot be controlled and therefore flow through the cleanup filter cannot be controlled. Without adequate flow rates through the TSC cleanup filter, the TSC ventilation system is considered non-functional. "As of 1400 CDT, repair and testing of the damper has been completed and the TSC ventilation is now functional. Had an emergency condition occurred during the time the repairs took place, contingency plans were in place to utilize the TSC as long as radiological conditions allowed. Procedure F3-6, 'Activation and Operation of the TSC,' Section 7.6, directs TSC management to relocate TSC activities to a radiological safe area if necessary." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-17
44070 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-03-17 11:50 | 2008-03-17 11:50 | 2008-03-21 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) AND EMERGENCY RESPONSE DATA SYSTEM (ERDS) UNAVAILABLE DUE TO PLANNED MAINTENANCE "At approximately 1200 hours, on 03/17/2008, the Unit 1 SPDS and ERDS system will be removed from service to connect a temporary power supply to support a planned maintenance outage on the PICSY [Plant Indication Computer System] computer normal power supply. The installation of temporary power is expected to have a duration greater than 8 hours, but less than 24. During this time, control room hardwire indications will be available. An update will be provided when SPDS/ERDS becomes available. "Since the Unit 1 SPDS/ERDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM RICH KLINEFELTER TO HOWIE CROUCH @ 1222 HRS. EDT ON 03/18/08 * * * "This is a follow-up courtesy notification to EN# 44070. Unit 1 ERDS has been restored as PICSY is now on temporary power. Restoration to normal power is expected to occur on 3/21/08. SPDS remains out of service due to other planned outage activities." The licensee has notified the NRC Resident Inspector. Notified R1DO (Perry). * * * UPDATE FROM JIM HUFFORD TO JOHN KNOKE @ 0530 HRS. EDT ON 03/21/08 * * * "This is a follow-up courtesy notification to EN# 44070. As at 0513, on 03/21/08, Unit I ERDS and PICSY are now fully restored. The planned outage activities are now complete." The licensee will notify the NRC Resident Inspector. Notified R1DO (Neil Perry) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-17
44069 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-03-14 | 2008-03-17 10:46 | 2008-03-20 | AGREEMENT STATE - LEAKING IODINE- 125 PROSTATE SEEDS "Licensee identified 7 leaking Iodine-125 leftover prostate seeds from two patient doses: 3/11/08, 4 seeds. 3/12/08, 3 seeds. Patients were recalled, but showed no iodine uptake. Licensee phoned [state radiation protection officials]." Seeds are approximately 0.3 micro Curies each. Mills Pharmaceuticals (Core oncology-Oklahoma City) manufactures the seed sources. They are then sent to Medtech Diagnostic Services, Ft Meyers, Florida. Medtech loads the seeds into cartridges and sterilizes order. Medtech then sends the loaded cartridges to Carolinas Medical Center. The state, licensee, and manufacturer are working together to determine where the seeds got damaged, whether at manufacturing, loading, or unloading. "Incident Number 08-12." * * * UPDATE FROM GERALD SPATE TO JOE O'HARA AT 1055 ON 3/20/08 * * * The state called to correct an editorial error on the original report. The seed activity is 0.36 milli Curies vice 0.3 micro Curies. Notified R1DO(Perry) and FSME(Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-03-20
44068 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-03-16 14:30 | 2008-03-16 16:52 | 2008-11-14 | LOSS OF PLANT PROCESS COMPUTER SYSTEM ERDADS "The Plant Process Computer System (Emergency Response and Data Acquisition System, 'ERDADS') OPCONs for Unit 4 failed causing the NRC Emergency Response Data System Link to be non-functional. "This is an eight hour NRC Notification for an ERDADS failure which is not corrected in 30 minutes and a loss of ability to supply ERDS data for greater than 30 minutes per 1OCFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 4/12/2008 AT 1512 FROM JIM RUSSELL TO MARK ABRAMOVITZ * * * "The Unit 4 Plant process Computer System (Emergency Response and Data Acquisition System, 'ERDADS') is out of service for an approximate 4 week period to implement a planned modification which replaces the current ERDADS system. During this time period the Unit 4 ERDS and SPDS functions will not be available. Also, Unit 4 Regulatory Guide 1.97 Category 2D Containment Temperature and power system indicators for motor control centers, batteries and inverters is unavailable in the Control Room, although other instrumentation is available to monitor these parameters." The reactor is currently defueled. Notified the R2DO (Musser). The licensee notified the NRC Resident Inspector. * * * UPDATE ON 11/14/2008 AT 1155 FROM BOB BONONTO TO MARK ABRAMOVITZ * * * ERDS was returned to service on October 31, 2008. The licensee notified the NRC Resident Inspector. Notified the R2DO (Bonser). | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-16
44067 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-03-16 11:37 | 2008-03-16 14:12 | 2008-03-16 | REACTOR TRIP DUE TO BROKEN SENSING LINE "At 1137 CDT, Comanche Peak NPP, Unit 2 reactor tripped due to a broken sensing line feeding the vacuum inputs to the 2/3 low vacuum turbine trip. With the reactor power steady at 100%, the turbine trip signal generated a valid RPS reactor trip signal. All control rods fully inserted. Both motor driven AFW pumps and the turbine driven AFW pump started as a result of low steam generator level following the trip. "Currently Unit 2 is in Mode 3, stable with RCS temperature at no-load program temperature of 557 degree F being maintained on the steam dumps. All 4 steam generators are at program level, being maintained by the motor driven AFW pumps. The turbine driven AFW pump has been returned to standby." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-03-16
44066 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-03-15 09:33 | 2008-03-15 11:19 | 2008-03-17 | REACTOR TRIP DUE TO TURBINE TRIP "At 09:33 EDT the plant experienced a turbine trip which resulted in a reactor trip from 85%. Plant power was less than 100% due to a [turbine] control valve oscillating problem identified on 3/13/08. "Post-trip [complications]: one of the four 4160 V busses, Bus 1A1, did not fast transfer from 22 KV to the 161 KV system as expected. This buss loss caused Reactor Coolant Pump RC-3A [to] trip off. Seals on RC-3A appear to be failed. The other 3 RC pumps remained in service for forced circulation through the Steam Generators "Steam Generator levels are being maintained by Main Feedwater Pump FW-4C. Steaming is through the steam dump and bypass valves to the condensers. "No primary or secondary relief valves lifted during this event. "Standard post-trip actions were taken per EOP-00 , followed by a transition to EOP-2. Loss of Off-Site Power. During EOP-00 the plant computer indicated 8 rods not inserted into the reactor core. Secondary and primary rod indication showed all control rods inserted. In response to the difference of rod position indication, emergency boration was implemented. Emergency boration was secured after shutdown margin was verified. "4160 V buss 1A was reenergized on the 161kv system at 10:31 EDT. "A transition to plant procedure OP-3A, plant shutdown was made at 10:58 EDT. "Reactor Coolant Pump RC-3A seal evaluation is in progress. The plant will remain in Mode 3." The licensee notified the NRC Resident Inspector and plans a press release. While RCP RC-3A seals indicate the same pressure across them there were no accompanying indications of containment sump water level increasing or high radiation levels in containment. Decay heat is being removed by normal feedwater feeding the steam generators steaming to the condenser steam dumps. Nuclear Instruments indicated plant shutdown throughout the trip. Safety buses are powered by offsite power and emergency diesel generators are in standby. * * * UPDATE FROM ERICK MATZKE TO PETE SNYDER AT 1033 ON 3/17/08 * * * "None of the reactor coolant pump seals at [Fort Calhoun Station] (FCS) were failed. There were abnormal indications on the A reactor coolant pump seal. The A reactor coolant pump seal is now working normally." Notified R4DO (Whitten). | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-03-15
44065 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2008-03-14 08:00 | 2008-03-15 00:07 | 2008-03-15 | POSSIBLE MEDICAL EVENT - LEAKING BRACHYTHERAPY SEEDS "Description: Three patients were scheduled for transperineal permanent prostate seed brachytherapy implantations on March 14, 2008. Three separate packages of seeds in preloaded needles were received; surveys showed no surface contamination or contamination outside the inner sterile containers. On March 14, 2006, after 12 of 106 seeds were implanted in the first patient, a survey meter showed a small amount of radioactive contamination on the inside of the sterile packaging. This implantation was stopped. The survey meter showed contamination on the tips of three of the four needles that had been used, the greatest being 5000 cpm (420 Bq if an efficiency of 20% is assumed). This patient was administered stable iodine to block his thyroid in case of a leaking seed. The seed vendor was notified by telephone. "To determine if the remaining patients should be implanted, the remaining two packages of seeds were opened and the interiors of the sterile packaging were surveyed. No contamination was found. An implant procedure was performed on the second patient. At the end of the procedure, the used needles were surveyed. A survey meter showed contamination on the tips of two of the needles; it was about 1000 cpm (83 Bq if an efficiency of 20% is assumed) on each. The seed vendor was again notified by telephone. A urine bioassay of this patient showed no radioactivity. "Implantation of the third patient was cancelled. "The needles of preloaded seeds were supplied by Best Medical International. The seeds contained I-125 and were Best Model 2301. The three batches of seeds were Lot Numbers 23017, 23019, and 23018 (not implanted). "At this time, it is uncertain whether any seeds were leaking. A possibility is that the contents of the sterile packages were contaminated by the vendor, but no seeds were leaking. "Effect on Patients: The VA is still evaluating this event. At this time, no adverse effects to the patients are expected. "Patient notification: The permittee is in the process of ensuring that the referring physicians and patients were notified. "We will notify the NRC Project Manager, Cassandra Frasier, of NRC Region III. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 4 | CA | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2008-03-20
44064 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-03-14 10:27 | 2008-03-14 18:06 | 2008-03-14 | FITNESS FOR DUTY REPORT A non-licensed employee supervisor had a confirmed positive for an illegal substance during a random fitness-for-duty test. The employee's access to the protected areas was suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector and Greg Hansen in Region III. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2008-03-14
44063 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2008-03-13 19:00 | 2008-03-13 19:18 | 2008-03-13 | SAFEGUARDS REPORT INVOLVING POTENTIAL LOSS OF SGI The licensee determined that the loss of controlled Safeguards Information (SGI) was significant. Compensatory measures are not in effect. Contact the Headquarters Operations Officer for details. The licensee informed the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-03-13
44062 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-03-13 14:45 | 2008-03-13 18:24 | 2008-03-13 | REACTOR BUILDING TO TORUS VACUUM BREAKER PRESSURE SWITCHES MAY NOT PERFORM DESIGN FUNCTION "March 13, 2008 at 1445 hours, engineering analysis identified that the pressure switches that operate to open the Reactor Building (RB) to Suppression Chamber (Torus) vacuum breaker isolation valves would not perform their design function. The condition impacted the function of both RB to Torus vacuum breaker isolation valves. One vacuum breaker isolation valve has been opened to maintain the function of the vacuum breaker in that line. A plan is being implemented to correct the deficiency and is expected to be completed within the required 72 hour Limiting Condition for Operation expiration time for the current condition. This is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-03-13
44061 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-02-29 11:00 | 2008-03-13 17:05 | 2008-03-13 | AGREEMENT STATE REPORT INVOLVING A SPILL OF Tc-99m DURING ADMINISTRATION OF A DIAGNOSTIC DOSE The following report was received via email: "The Colorado Radiation Control Program (RAM Unit) received a call from the licensee on February 29, 2008 at approximately 13:15 that a small spill had occurred as part of a cardiac treadmill test. We [Colorado Rad Control Program] received written communication on February 29, 2008. "The diagnostic dose prescribed for the patient was 31.4 mCi of Tc-99m (Cardiolite). The patient was walking on the treadmill. During the initial attempt of injection of the nuclide into the patient via the catheter, part of the dose (~2 mCi) spilled out at the juncture of the catheter and the needle into the patient resulting in a small spill onto the patient and down onto the treadmill. The test was stopped at that point and the patient was cleaned where the spill had occurred. There was no clothing contaminated. The attending staff was surveyed and none of the staff was contaminated. "The area was monitored, ambient gamma exposure rates were about 50 uR/h, with the highest exposure rate on the impacted area of the treadmill reading ~3.5 mR/h. Readings returned to background within three feet of the spilled material. Due to the rough surface of the treadmill, remediation was not performed, rather the spill areas was covered with plastic sheeting and marked as a contaminated area. The treadmill was out of service until 3/3/08, which was longer than 10 half lives (they took advantage of the weekend). However, since the device was out of service for longer than 24 hours, this is reportable under Colorado Regulations Part 4.52.2.2, which are equivalent to NRC 10 CFR 30.50 (b)(1). The licensee has followed up with retraining of the nuclear medicine technician by reviewing the procedures for checking the IV tubing and making sure the proper connections are intact." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-03-18
44060 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2008-03-13 16:44 | 2008-03-13 18:36 | 2008-03-13 | ALERT DECLARED DUE TO TOXIC GAS DISCHARGE INTO THE 1B EMERGENCY DIESEL GENERATOR BUILDING "During the 1B diesel generator surveillance run, the control room received fire alarms for the 1B diesel generator room. The system operator reported the room was full of smoke and the CO2 system had discharged. The control room manually shutdown the 1B diesel generator due to the event. An Alert classification was declared based on EAL #HA3 - Report or Detection of Toxic or Asphyxiant Gas within the Vital Area in Concentration that May Result in an Atmosphere Immediately Dangerous to Life or Health. No Radiological Release has occurred or is in progress." The licensee stated that all personnel were accounted for and that no injuries had occurred. The 1B emergency diesel generator building is being ventilated to re-establish habitability. The licensee stated that there is no fire. During discussions between NRC management and the licensee it was noted that the exhaust header on the 1B EDG had been recently replaced and that a failure of this exhaust header introduced smoke and exhaust gas into the building which actuated the CO2. The licensee notified State and local agencies and the NRC Resident Inspector. A press release will also be issued. * * * UPDATE FROM McCORY TO HUFFMAN AT 1945 EDT ON 3/13/08 * * * The Alert was terminated at 1836 CDT based on ventilation of the room and re-establishment of habitability. The licensee notified State and local agencies and the NRC Resident Inspector. R2 (McCree), R2DO (Lesser), NRR (Wiggins), NRR EO (Haney) and IRD (Cruz) notified. Notifications to DHS, FEMA, DOE, EPA, USDA, HHS were also made by the NRC Operations Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-03-13
44059 | 0 | PALISADES | 1 |  |  | [1] CE | 2008-03-13 | 2008-03-13 12:38 | 2008-03-13 | POTENTIAL DEFECT IN FAIRBANKS MORSE EMERGENCY DIESEL GENERATOR SNUBBER VALVE MATERIAL AND HEAT TREATMENT Abstract: "Palisades has experienced failures of two snubber valves on an emergency diesel generator since November 2005. These valves were made from AISI E 52100 material. Entergy has determined through destructive metallurgical analysis that the material was incorrectly heat-treated. Not all of the install snubber valves were constructed of this material. The defect in the material of the snubber valves may allow the snubber valves to crack under operation, resulting in fuel oil leakage and loss of fuel oil supply to the affected cylinder on the engine. Component information: "Manufacturer: Fairbanks Morse Model: ALCO Model 251F ALCO Part Number: 2402466 Description: "Palisades has experienced failures of two snubber valves on the 1-2 emergency diesel generator since November 2005 due to incorrectly heat treated material of the snubber valves. Both snubber valves failed soon after being initially installed in the engine or after being re-installed in the engine after maintenance. The first snubber valve failed after operating for approximately 10 hours of operation. The second snubber valve was installed in the engine and had approximately 135 hours of run time on it before it was removed, inspected and re-installed in the engine. After reinstallation into the engine, the snubber valve failed after approximately 2 hours of operation. Review of the purchasing history of the snubber valves could not identify when these failed snubber valves were originally purchased. "On February 27, 2008, Entergy determined, through destructive metallurgical analysis, that the material that was incorrectly heat-treated was AISI E52100 material. Not all snubber valves were constructed of this material. Subsequently, the receipt inspection practices were revised to include testing of the snubber valves for the suspect material. This is accomplished by using a Niton XLT 800 chemical analyzer to identify (non-destructively) the chemical content of the snubber valves. Snubber valves with manganese contents <0.5% are rejected as they are most likely to be constructed of E52100 material. "In January 2008, five snubber valves were rejected due to not meeting Palisades material requirements. Subsequently, one of the snubber valves was destructively tested and confirmed to have been incorrectly heat treated. These snubber valves were identified to have been purchased in 2004. "A Part 21 evaluation was performed and it was concluded that this is a substantial safety hazard because the defect may allow the snubber valves to crack under operation, resulting in fuel oil leakage and loss of fuel oil supply to the affected cylinder on the engine. The loss of fuel oil supply to a cylinder may affect the ability of the emergency diesel generator to meet its design basis load rating; the external leakage of fuel may result in the potential for a fire to develop and render the diesel generator inoperable; and the leakage of fuel may affect the ability of the fuel oil system to supply adequate fuel oil to the diesel generator throughout its mission time. Causes: "Snubber valves constructed from AISI E52100 material may be incorrectly heat-treated. The cause of this is not known. Corrective Actions: "Palisades experienced two failures, which were reported in Licensee Event Reports 2005-007 and 2007-006. Entergy identified the improper heat treatment following the second failure. Entergy has subsequently replaced all snubber valves on the 1-1 emergency diesel generator. Entergy replaced the defective snubber valve and the remaining snubber valves on the 1-2 emergency diesel generator that had been replaced at the same time the defective snubber was installed. Since the replacement snubber valves on 1-2 emergency diesel generator did not have their material composition verified, eight additional snubber valves were sub replaced after verifying E52100 was not present. Entergy plans to replace the remaining 10 snubber valves on 1-2 emergency diesel generator. Based on the amount of in-service time of these snubber valves and verification of 26 acceptable snubber valves, there is reasonable expectation of operability." The licensee notified the NRC Resident Inspector. Palisades has been in contact with Fairbanks Morse concerning this issue. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 21.21 |  |  |  | 0 | 2008-03-13
44058 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2008-03-12 11:30 | 2008-03-12 18:22 | 2008-03-13 | AGREEMENT STATE - UNIDENTIFIED RADIOACTIVE MATERIAL RECEIVED AT METAL RECYCLING FACILITY The State of Oregon Radiation Services Section reported that they had sent an inspector to Schnitzer Steel in Portland, Oregon due to unidentified radioactive material that had been received by the facility. A barge of metal for recycling had been received from Amix Recycling of Vancouver, British Columbia that set off a radioactive portal alarm. The radioactive material has not yet been specifically identified. The State inspectors have determined that one of the radioactive sources appears to be a process gauge with a Cesium source. There is also indication of a Radium or Cesium source in a scrap metal pipe. The State will ensure that the sources are adequately secured and will be following the licensees interactions with the originator of the shipment in terms of long term disposition of the sources. Oregon Report Number 08-0025 * * * UPDATE AT 1921EDT ON 03/13/08 FROM STATE OF OREGON (TERRY LINDSEY) TO STEVE SANDIN VIA EMAIL * * * "Oregon Radiation Protection Services personnel have completed an initial survey of the empty barge that contained two radiation gauges with Cesium-137. One gauge (mat scanner) was sheared apart with scrap steel equipment and was leaking along both shear points. Both gauges have been secured and contamination has been contained at this time. "The Oregon 102nd Civil Support Team also assisted with the final survey and decontamination evaluation onsite and the site has been secured for today. "A U.S. EPA Region X team has been activated by U.S. EPA Duty Officer and is enroute to Oregon to assist with further site evaluation and investigation. Oregon RPS personnel will be coordinating with the U.S. EPA team tomorrow morning for any final survey work and evaluation of potential enforcement concerns related to removal of radiation warning labels from these gauges." Notified R4DO (Pruett) and FSME (Bradford). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2008-03-17
44057 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-03-12 14:30 | 2008-03-12 17:33 | 2008-03-12 | LONG TERM HABITABILITY OF TECHNICAL SUPPORT CENTER UNDER ACCIDENT DOSE ANALYSIS EXCEEDS ACCEPTANCE CRITERIA "At approximately 1430 CDT on 3/12/08 Prairie Island staff completed a preliminary review of a revised dose analysis for the Prairie Island Technical Support Center (TSC) that called into question the long term habitability of the TSC under bounding accident conditions. The preliminary calculation result exceeds the 30-day 5 rem whole body dose acceptance criteria of NUREG-0696 and is based on bounding case assumptions consistent with Regulatory Guide 1.4 (including fuel melt, highest allowable containment leakage and bounding atmospheric dispersion factors). The primary contributor is an approximately 25 square foot window in the north wall of the TSC. Compensatory measures are being established to provide shielding over the window in the TSC." The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-12
44056 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-03-11 14:57 | 2008-03-12 13:44 | 2008-03-12 | TWO CYLINDERS IDENTIFIED WITH WEIGHT CHANGE PRIOR TO WASH "Between 1979 and 1985, approximately 960 thin-walled cylinders were obtained by Paducah Gaseous Diffusion Plant (PGDP), transferred to Allied Chemical, and filled with near-normal assay material as part of a strategic feed reserve. These cylinders were transferred to Oak Ridge Gaseous Diffusion Plant (ORGDP) for storage. They were shipped back to PGDP beginning in the early 1990s. All but three of these cylinders have been fed. In early 2003, the Nuclear Criticality Safety Evaluation (NCSE) was revised to evaluate the washing of the heeled cylinders. "At 1457 hours on 3/11/2008, the Plant Shift Superintendent was notified that two non-fissile cylinders were identified in the ORGDP strategic reserve category that had a weight change while stored at ORGDP in violation of the NCSE for the C-400 cylinder wash operation. One leg of double contingency is based on it being unlikely that cylinders in this category would be introduced into the process while stored at ORGDP. The weight change indicated that these cylinders were introduced into the process at ORGDP. The other leg of double contingency is based on two individuals independently verifying that the cylinder had no weight change while it was stored at ORGDP. This control was not violated. The NCSE concern associated with these cylinders entering the process is the potential to introduce fissile material into the cylinder while stored at ORGDP and subsequent washing at the non-fissile C-400 cylinder wash. Even though one leg of double contingency was lost, these cylinders were not washed. "The cylinder heel of one cylinder is approximately 11 lbs. at 0.711 wt% U-235 in solid form and the other cylinder is approximately 39 lbs. at 0.7 wt% U-235 in solid form. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-08-0730; PGDP Event Report No. PAD-2008-06." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2008-03-12
44055 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2008-03-12 08:15 | 2008-03-12 13:07 | 2008-03-12 | ACCIDENTAL EMERGENCY SIREN ACTIVATION "At approximately 0815 CDT, on March 12, 2008, a Dakota County corrections officer inadvertently activated the Dakota County sirens from the backup unit during the conduct of a silent siren test. The licensee was notified of the siren activation by the activation signal received on the informer unit in the Technical Support Center (TSC) at 0815, as well as a subsequent phone call from the siren contractor. Seven of the 117 sirens in the 10-mile Emergency Planning Zone (EPZ) were activated for approximately 3 minutes. No press release is planned by Xcel Energy. Dakota Communications Center received a call from a local radio station asking why the sirens were activated. No other press release is planned by Dakota County. "The NRC Senior Resident Inspector was notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-12
44054 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-03-12 05:00 | 2008-03-12 10:01 | 2008-03-12 | INTERRUPTION TO ENS TELEPHONE SERVICE "At 05:00 hours on 3/12/2008, it was discovered that the Surry Power Station Emergency Notification System (ENS) phone was nonfunctional. This was discovered when the NRC attempted to contact the Surry Main Control Room, and no response was obtained. The ENS phones in the Main Control Room and the Technical Support Center cannot dial out. Telecommunications has been contacted to investigate the problem. "This event is reportable in accordance with 10CFR50.72(b)(3)(xiii), any event that results in a major loss of offsite communications capability. (e.g., Emergency Notification System). "At 08:00 the NRC ENS phone was tested and it was determined to be functional from the Main Control Room to the NRC. The NRC Resident was notified that the ENS phone was returned to service at 09:20." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-12
44053 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2008-03-11 | 2008-03-11 16:16 | 2008-03-11 | GEORGIA AGREEMENT STATE REPORT The State of Georgia reported that one of their licensees, Applied Technical Services, was conducting radiography at the Rayonier Paper Mill in Jessup, GA. While filming a tank weld, the radiography camera fell approximately 24 feet to the ground. The licensee was unable to retract the source back into the camera. The licensee isolated the area and covered the source with temporary lead shielding. Additionally, they established a 2 mR/hr boundary around the source which will be continuously manned until the manufacturer (QSA Global) representative arrives to secure the source and camera. The licensee reports that no overexposures occurred during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2008-03-14
44052 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-03-10 | 2008-03-11 14:21 | 2008-04-11 | NEBRASKA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The State of Nebraska Department of Health & Human Services, Radiation Control Program, Radioactive Materials Branch reported that a radiographer employed by Team Industrial Services, Inc. was potentially overexposed while performing radiography at a Nebraska City, NE facility. Team Industrial Services, Inc. is performing work in Nebraska under reciprocity of their Illinois license. On March 7, 2008, while at the job site, the radiographer noticed that his direct-reading pocket dosimeter was off-scale. He reported this to the regional Team Industrial Services RSO and stated that he believed he just bumped the dosimeter to cause the off-scale condition. The RSO directed him to send his TLD to Landauer Laboratories for processing. On March 10, 2008, Landauer informed the RSO that the TLD indicated that the radiographer received 7.753 REM Deep Dose Equivalent. The Team Industrial RSO notified his corporate RSO, who then notified the State of Nebraska. The radiographer has been restricted from radiation areas while Team Industrial and the State of Nebraska investigates this incident. * * * UPDATE RECEIVED VIA E-MAIL FROM HOWARD SHUMAN TO JOE O'HARA AT 1530 ON 4/11//08 * * * "On March 11, 2008, the Corporate RSO for Team Industrial Services, Inc. called to report that one of their industrial radiographers had received an exposure of 7.753 rems to their dosimetry badge while conducting radiographic operations, under reciprocity, at a construction site in Nebraska City, NE. "The dates that the radiographer had performed radiography were the evening of March 4, 2008 and the early morning of March 5, 2008. At the time the radiographer noted that his pencil dosimeter had gone off-scale. He did not notify the FRSO in the licensee's Illinois office until March 7, 2008 at which time his dosimetry badge was sent off to Landauer for emergency processing. Landauer verbally reported the findings to Team Industrial on March 10, 2008. "During the subsequent investigation of the incident, the radiographer admitted that he had performed radiography alone at the temporary jobsite alone. Four possible scenarios were developed during the investigation. First, he had received the exposure because the confined space in which the exposures were made caused the radiographer and assistant to be in a 200-300 Mr/hr field. This was discounted because the assistant only had 30 mrem on her pencil dosimeter and badge readings were 137 mrem for February and 4 mrem for March (both sent in for emergency processing). "The second scenario involved the statement by the radiographer that he had dropped his dosimetry badge near the camera and guide tube and that he may have "bumped" his pencil dosimeter. Calculations could not substantiate the exposure to the badge. In addition, it was too coincidental that both the dropped badge and "bumped" pencil dosimeter happened at the same time. "The third scenario was that this was an intentional exposure of the badge. Intensive questioning by the State of Nebraska inspectors and Team management could not substantiate this scenario. "The last and most probable scenario was that the radiographer did not fully retract the source following a radiography shot and failed to properly conduct a complete survey around the camera and guide tube before repositioning the guide tube for the next radiography shot. "There is no evidence to discount any of the above scenarios so the investigation is considered to be inconclusive. "A complete investigation report is in process. Violations have been identified and will be included in the final report with the response from the licensee." Notified R4DO(Deese) and FSME(Kock) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-03-14
44051 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-01-24 03:35 | 2008-03-11 11:06 | 2008-03-11 | 60 DAY REPORT - INVALID ACTUATION OF THE NUCLEAR SERVICE WATER SYSTEM "This 60-day optional report as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73 (a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Nuclear Service Water System (NSWS). "While performing changeout of a Nuclear Service Water (RN) current module, there was an unexpected auto swap from the normal heat sink (Lake Wylie) to the ultimate heat sink {Standby Nuclear Service Water Pond (SNSWP)} occurred and the system responded as designed. Work was stopped when notified by Operations. "This event occurred when technicians attempted to isolate power to the module prior to replacing. Unable to do so, they decided to perform a changeout under hot conditions. While tracing power utilizing wire tabs, the technicians did not identify that removing wire from terminal 12 of the module disturbs the power path to other channels. The channel associated with the bad module remained in the trip condition throughout, and when power to other channels was disturbed, the logic for a swap from the normal heat sink to the ultimate heat sink was completed and the automatic swap occurred as designed. This event was entered into the site corrective action program for evaluation." The licensee will inform local and state agencies and has informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-03-11
44050 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2008-03-10 18:13 | 2008-03-10 23:59 | 2008-04-22 | HPCI INOPERABLE "During performance of the quarterly high pressure coolant injection (HPCI) Surveillance Test, a technical specification step could not be completed due to observed system water flow and discharge pressure oscillations. These oscillations are presently under investigation. The tech spec step involved establishing flow conditions at a certain discharge pressure. The problem is either with the test return system or the control system. A formal troubleshooting plan is being developed to determine the root cause and corrective action required to re-establish operability of the HPCI system. The system remains inoperable due to the problem found during testing. If the problem is found to be caused by the control system, then it could have potentially impacted the ability of the HPCI system to mitigate the consequences of an accident." HPCI is currently in a 14 day Tech Spec 3.5.1.h LCO. The licensee notified the NRC Resident Inspector. The licensee will be notifying the Minnesota Duty Officer. * * * UPDATE FROM MARK KRUSE TO JASON KOZAL ON 4/22/08 AT 1631 * * * "Monticello is retracting the event reported based on further reviews of the event which found that the issue did not impact HPCI operability. A problem was identified with the test return valve CV-3503 which is not a safety-related component. The stations formal troubleshooting team has identified the cause for the degradation and corrective actions will be tracked in the station's corrective action program." The licensee will notify the NRC Resident Inspector. Notified R3DO (Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-03-11
44049 | 0 | DELVAL SOIL & ENV. CONSULTANTS |  |  |  |  | 2008-03-10 13:45 | 2008-03-10 14:09 | 2008-03-10 | DAMAGED TROXLER MOISTURE DENSITY GAUGE The RSO reported that while the technician was performing a soil test, a piece of construction equipment backed over the gauge. The incident occurred at the "Bodo tract" on the corner of Station Rd. and Con-Chester Pike (Rt. 322). The current status of the gauge is that the source rod is still in the test position. The technician has cordoned off the area awaiting the arrival of the RSO. The extent of damage to the gauge is unknown at this time. The gauge is a Troxler model 3440 containing 40 mCi of Am-Be and 8 mCi Cs-137. The RSO has notified Region 1 NRC (Gordon) and will be updating this report once the event is assessed. * * * UPDATE FROM MICHAEL SOWERS TO HOWIE CROUCH @ 1752 EDT ON 03/10/08 * * * The licensee RSO was able to retract the source back into the shield, however the shield has broken away from the gauge. Area radiation surveys did not indicate any contamination in the incident area. The licensee has transported the gauge back to their facility and will be conducting a leak test sample to send to Troxler. Notified R1DO (Lorson) and FSME EO (Flanders). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-03-10
44048 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-03-08 19:37 | 2008-03-08 21:23 | 2008-03-08 | LOSS OF POWER TO OFF-SITE EMERGENCY SIRENS "On March 8, 2008, at 1937 hours, Emergency Planning determined that 17 of a total of 156 sirens were reported as unavailable due to weather related loss of power as a result of high winds. In accordance with the Indian Point reporting procedure, the loss of 16 or more sirens that can not be returned to service in one hour, constitutes a major loss of the offsite notification capability that requires an 8-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(xiii). Actions are underway to restore all of the sirens to service. "As of 2043 EST on 03/08/08 there were 16 of 156 sirens out of service. "The licensee notified the NRC Resident Inspector, as well as the Counties of Westchester, Putnam, Rockland, and Orange." The licensee also notified the Public Service Commission. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-08
44047 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-03-07 19:14 | 2008-03-07 22:49 | 2008-03-12 | INTERMITTENT OPERATION OF EMERGENCY RESPONSE DATA SYSTEM "At 1914 on 3/07/08, the Unit 4 RCO noted that the ERDADS OPCON displays in control room and computer room stopped updating. This rendered the Unit 4 ERDS link to the Nuclear Regulatory Commission Operations Center (NRCOC) to be inoperable for greater than 30 minutes, as the link can not be initialized if required. "Attempts to reboot the OPCON displays and the PEDS Computers were initially performed per plant procedure, but did not correct the issue. Troubleshooting is in progress at this time. No estimated return to service is available at this time. "8-hour notification being performed to NRCOC under event classification 10 CFR 50.72 (b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MARK JONES TO PETE SNYDER ON 3/12/08 @ 1431 hrs. * * * A CPU board had been replaced. At 1420 the ERDS link to the NRC has been restored and is considered operable. The licensee notified the NRC Resident Inspector. Notified R2DO (Lesser). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-07
44046 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-03-07 14:46 | 2008-03-07 17:21 | 2008-03-07 | AUTOMATIC REACTOR SCRAM WITH HPCI/RCIC ACTUATION DUE TO LOSS OF CONDENSATE FEEDWATER "Unit 2 RPS actuation / unplanned scram with subsequent ECCS discharge to the RCS at 1446 hrs. on 3/07/08. Unit 2 scrammed on Low RPV water level of 3 inches above instrument zero as a result of a loss of condensate feedwater. Water level decreased to approximately 60 inches below instrument zero as a result of the loss of feedwater. [Top of active fuel is approximately 150 inches below instrument zero.] The cause of the loss of feedwater is presently under investigation. At 35 inches below instrument zero, HPCI and RCIC actuated and restored water level. HPCI oscillations were experienced and the system was taken to manual control, at which time the flow oscillations abated. All other systems functioned as required. "A team has been assembled to investigate and determine the cause of the initiating event of the loss of feedwater." During the scram, all rods inserted into the core. There were no safety relief valve actuations as a result of the transient. RPV level was restored and is being maintained using control rod drive flow. The electrical grid is stable with normal offsite power supplying safety loads. Decay heat is being removed using the turbine bypass valves to condenser. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2008-03-07
44045 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-03-06 | 2008-03-07 16:32 | 2008-03-07 | AGREEMENT STATE REPORT - POSSIBLE PATIENT UNDERDOSES "The Department of Health and Family Services (DHFS) was notified on March 6, 2008, of possible underdoses to up to eight patients treated with Samarium-153 since late 2006. "When the licensee was preparing a recent dose of Samarium-153, the activity measured in the dose calibrator did not read as expected. After review, the licensee determined that the dose calibrator was calibrated to measure Samarium-153 in a vial, but the nuclear medicine technologist had measured the activity of Samarium-153 in a syringe instead. For this particular case, the dosage was remeasured properly prior to administration, but further review of cases identified up to eight additional instances when the nuclear medicine technologists may have measured the activity of Sarnarium-153 in a syringe instead of in a vial. Samarium-153 has a combined beta and gamma decay spectrum, and when the activity is measured in a syringe, the attenuation and volume geometry is estimated to lead to administered activities of approximately 30% less than prescribed in the written directives. "DHPS will investigate this incident next week." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-03-13
44044 | 0 | KENNEDY HEALTH SYSTEM |  |  |  |  | 2008-03-07 | 2008-03-07 15:15 | 2008-03-07 | NUCLEAR POWERED PACEMAKER POTENTIALLY UNACCOUNTED FOR After recently determining that an individual with a nuclear powered pacemaker was due for a six month check-up, the licensee attempted to reach the individual on March 5, 2008. Later the licensee determined that the individual was deceased. The licensee contacted the funeral director in an attempt to recover the pacemaker. The licensee also contacted Medtronic Corp. in an attempt to determine if the funeral director had returned the pacemaker to Medtronic but the licensee has still been unable to account for the pacemaker. On March 7, 2008, after attempts to locate the device, an official from Kennedy Health System determined that a Coreatomic Inc. nuclear powered pacemaker is missing and perhaps lost. The pacemaker is a Coreatomic model C-101-P nuclear powered cardiac pacemaker serial number 1168. Typically these pacemakers contain 2 to 4 curies of Pu-238 which is about 250 milligrams of material or less. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-03-07
44043 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-03-06 09:30 | 2008-03-07 14:03 | 2008-03-07 | CALIFORNIA AGREEMENT STATE REPORT - LOST LICENSED MATERIAL Received the following information from the State of California via fax: "A person contacted the California Radiologic Health Branch (RHB) on 03/06/08 to report that the radiation detector at the Compton Transfer Station had alarmed from a bin that had come from FedEx at 5927 W. Imperial, [Los Angeles] (near LAX); the reading was 22.8 kcpm, with a background of [approximately] 3.4 kcpm. [A RHB Investigator] went that afternoon, and after sorting through the bin contents, found an [approximately] 13 mCi Cs-137 source. The source is [about] 1/4 inch long and 1/8 inch in diameter. The radiation measurement was about 50 mrem/hr at one foot (measured using a Bicron microrem meter and a Keithley 36150). [The RHB Investigator] placed the source in a lead pig and secured it in the trunk of his car. "On 3/7/08, [RHB Investigators] discussed the incident with the Manager at the Fed Ex Imperial location, [the Manager of] FedEx Dangerous Goods, and other FedEx employees in Dangerous Goods. [An RHB Investigator] advised them that [RHB Investigators] would be there later today (03/07/08) to survey the facility to make sure there aren't any other sources, and that Fed Ex is to interview their employees to try and determine how the source came to be in the bin, and from whom it had come." California RHB will continue to investigate this incident and has assigned incident report number 5010-030608 to this event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-03-12
44042 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2008-03-07 10:45 | 2008-03-07 13:00 | 2008-03-07 | TELEPHONE OUTAGE ONSITE "On 3/7/08, at 1045, Vermont Yankee experienced a telephone service interruption that resulted in a loss of the dedicated phone line used to contact the NRC Operations Center via the Emergency Notification System (ENS) - FTS phone as well as a loss of the Nuclear Alert System (NAS) from the control room. "Alternate phone communications remain available from the control room to both the NRC Operations Center as well as the states of Vermont, Massachusetts, and New Hampshire. "The Emergency Planning organization has verified proper ENS - FTS and NAS communications from the Emergency Operations Facility (EOF)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM KRITZER TO SNYDER ON 3/7/08 AT 1552 * * * Vermont Yankee's ENS and other phone lines are back in service. The licensee notified the NRC Resident Inspector. Notified R1DO (Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-07
44041 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-03-07 10:30 | 2008-03-07 11:25 | 2008-03-07 | OFFSITE NOTIFICATION DUE TO TRITIUM IN ONSITE WATER SAMPLES "Brunswick previously reported detection of tritium in excess of Nuclear Energy Institute (NEI) reporting criteria on June 13, 2007, i.e., EN 43420, as a result of water samples taken from an onsite shallow groundwater well (i.e., ESS 1BC) near the Storm Drain Stabilization Pond (SDSP). As previously indicated in EN 43420, the storm drain system routes tritiated water into the SDSP. Overflow from the Turbine Building air-wash system was identified as the primary contributor to the effluent of the storm drain system. The air-wash is no longer routed into the storm drains, which eliminated the main source of the tritium into the storm drain system. "On March 6, 2008, an ongoing investigation determined that tritium levels in excess of NEI voluntary reporting criteria present in an onsite shallow groundwater well (i.e., ESS-2C), resulted from a condition not previously reported. Though elevated levels of tritium for each incident are most likely a result of the same source (i.e., effluent routed in the storm drain system,) subsequent investigations indicate that the storm drain piping may allow an inadvertent pathway to groundwater in close proximity to ESS-2C. "The monitoring well ESS-2C is well within the boundaries of the site owner controlled area and there is no indication that tritium has migrated into any drinking water. "The following agencies will be updated on the status of the onsite tritium samples and informed of the pending press release: State Officials, City of Southport, Brunswick County, NEI, INPO, and ANI. "The Licensee notified the NRC Senior Resident Inspector." | 93 | 77 | 0 | 93 | 77 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-07
44040 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-03-05 | 2008-03-06 15:29 | 2008-03-06 | LOUISIANA AGREEMENT STATE REPORT - PERSONNEL ANNUAL OVEREXPOSURE Received the following information from the State of Louisiana via facsimile: The licensee, Louisiana Heart Hospital in LaCome, LA., submitted a High Exposure Report to the State concerning one of their physicians. The physician's exposure by badge was 5,244 mrem for the 2007 calendar year. The cause of the overexposure was attributed to high workloads in the Cardiac Catherization Labs during the period. Corrective actions taken include double badging the individual, including the addition of a waist badge beneath his lead apron, using additional shielding/distance and using special equipment such as pull-down lead shields. Additionally, the licensee will review the individual's exposure quarterly to adjust workload and/or corrective actions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-03-11
44039 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-03-05 | 2008-03-06 12:30 | 2008-03-07 | TEXAS AGREEMENT STATE REPORT - SAFETY EQUIPMENT FAILURE "On March 5, 2008 at 3:43 p.m., the agency [Texas Department of State Health Services] received a telephone call from the licensee reporting that the manufacturer was performing a gauge update replacement change on their level gauges when he discovered the shutter was stuck in the open position for this particular gauge. The manufacturer representative quickly removed the level gauge and took it to a remote area for closer examination. "The initial thought was that the shutter was just stuck open, but upon closer examination, the manufacturer representative discovered that the shutter door was badly damaged by severe heat from the weather and could not be fixed on-site. "The manufacturer representative then constructed and installed a temporary shield for the gauge and reported readings at 12 inches away of 4-7 Mr/hour. The licensee reports that the gauge has been placed in a sequestered area, with area caution signs and a 24-hour person surveillance while they await the Type A transport container ordered by the manufacturer representative for safe transport back to his company for repair or replacement. "The licensee reports that the leak test performed was negative. The licensee also stated that this gauge has been in service for approximately 11 years without any problems. Since the licensee had the manufacturer out at their facility taking their 5010 series gauges out and replacing them with new series, the gauge is now in the possession/ownership of the gauge manufacturer. "Gauge information: Texas Nuclear - Manufacturer, Model# - 5010A, Serial #- B-405, 1000 mCi in 1997 "Source information: Am-241 1000 mCi in 1997, Serial # - AO366, Mfg: Texas Nuclear "Call to licensee's RSO for clarification on gauge information. He reported that the gauge is locked inside the Type A container and the Type A container is locked inside a caged storage area. The manufacturer will ship it out to their Sugar Land, Texas facility sometime today." Texas Incident#: I-8489 * * * UPDATE FROM LATISCHA HANSON TO HOWIE CROUCH @ 1315 EST ON 03/07/08 * * * "On 03/07/08 at 10:48 a.m., Incident Investigation Program (IIP) called the gauge manufacturer representative back and was able to speak with him. He stated the damage was from heat, but not from the weather; it was from the extreme heat of the coke vessel the gauge was attached to, which can reach temperatures up to ~900°F. He told IIP that the shutter carousel has plastic which can change forms and melt within a couple of hours. He cannot estimate when this could have occurred between 11/20/07 and 03/5/08. He stated that he was still at the location, waiting for the transport truck to load the gauge and send it to his facility, Thermo Measuretech. "On 03/07/08 at 11:00 am., II [Incident Investigator] placed a telephone call to the licensee's Radiation Safety Officer (RSO) to clarify when the gauge was last checked and if there was any possibility of public exposure between the time they last checked it and the gauge change on 03/05/08. He stated that there was absolutely no possibility of public exposure, due to the following facts: "1) The coke drum vessel has extreme heat and the gauge housing is mounted in a wire cage within four inches of the vessel and also has a rain cover. He stated no one goes up there unless they are performing the gauge check. "Besides the extreme heat of the vessel, there is an air gap that someone would have to stick their hand through to get to the gauge housing and he can't think of a situation where someone would want to reach through the heat and air gap to get to the gauge. "2) He told us the last gauge check was on 11/20/07 and it was noted that the shutter door was hard to close, but that is not unusual due to the extreme vessel heat, dirt and grime that collect on it while there. He told us they perform this check every 3-5 years and this is the only time someone is in contact with the gauge. "IIP asked him if he would fax us a copy of the November 2007 check. He affirmed he would. He stated that there were 5 other gauges that were exchanged, so we asked if he would include those gauges serial numbers for us as well. "He reminded us that the normal operating position for the shutter is in the open position. "3) The RSO updated us with the gauge transport process. He stated the truck was delayed yesterday due to their area experiencing high winds and hail storms and was expected in sometime today. "IIP will continue to update this report with any additional information as it becomes available." Notified R4DO (Cain) and FSME (Flannery). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-03-11
44038 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-03-06 04:00 | 2008-03-06 05:45 | 2008-03-06 | PIN HOLE LEAK DISCOVERED IN 1 INCH INSTRUMENT LINE DURING RPV PRESSURE TEST "With Unit 1 in Mode 4 for a planned refueling outage, a pin hole leak was discovered on a 1 inch line between the 'A' Main Steam Line (MSL) and MSL flow instrument condensing chamber (1B21-D006B) in a weld at a 45 degree elbow. Leakage was identified as approximately 2 gallons per hour (GPH). This leakage was identified during RPV pressure test while test pressure was 1050 psig. "This elbow is near the 1B21-D006B condensing chamber and is located in the Unit 1 drywell (primary containment). "This item constitutes a primary coolant boundary leak discovered while shutdown." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-03-06
44037 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2008-03-05 21:00 | 2008-03-05 22:20 | 2008-03-10 | CIRCUMFERENTIAL PIPING CRACK "On March 5, 2008, a volumetric ultrasonic examination of a Reactor Coolant to Decay Heat System pipe weld was analyzed and determined to identify an unacceptable indication. This dissimilar metal weld is located on the nozzle to the Decay Heat System drop line piping, which is the common suction line from the Reactor Coolant System and is a 12 inch outer diameter pipe. The indication is circumferential, is 15 inches in length, and reaches a maximum localized depth of 65 percent through-wall in one location. The weld was previously partially inspected during the November 2007 refueling outage using manual ultrasonic examination and no indications were identified. The current inspection was done using newly qualified phased array ultrasonic examination techniques in response to industry operating experience regarding dissimilar metal weld flaws. The indication has been found unacceptable per paragraph IWB 3514.4 of the 1989 Addenda of ASME Section XI without further fracture mechanics analysis and is therefore considered reportable. "Preparations for a weld overlay repair and further confirmatory manual ultrasonic testing examinations are in progress. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM J. TAYLOR TO JOE O'HARA AT 1730 ON 3/10/08 * * * "On March 8, 2008, further fracture mechanics evaluation of the circumferential indication on the Decay Heat System Drop Line determined that the requirements of the ASME Section Xl pipe code were maintained. Specifically, the acceptance criteria of the 1989 Edition Section XI, Table IWB-3641-1, -2, were met with an allowable value for flaw depth / wall thickness (a/t) of 0.75. Consequently, the 65% through wall indication would be considered acceptable for operation and the Degraded Condition Reporting Criteria would not be exceeded. Therefore, this event is not reportable under any 10CFR50.72 criterion. However, due to industry operating experience with dissimilar metals welds, this notification is being made voluntarily. Confirmatory manual ultrasonic testing examinations were completed which validated the presence of the indication originally found via phased array UT examination techniques. A full structural weld overlay repair is in progress which will be completed before returning Crystal River 3 to power operation. The repair effort has already successfully deposited the first weld layer over the location of the flaw. No Licensee Event Report will be submitted for this event." The licensee notified the NRC Resident Inspector. Notified R2DO(Hopper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-03-05
44036 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-03-05 | 2008-03-05 20:15 | 2008-03-05 | FIFTEEN EMERGENCY SIRENS INOPERABLE FOR A TIME "On March 5, 2008, at 1312 CST, fifteen (15) emergency notification system sirens in the Fort Calhoun Station Emergency Planning Zone (eleven in Harrison County, Iowa, four in Pottawattamie County, Iowa) were de-energized due to a un-planned power outage. The loss of AC Power to these emergency notification sirens impacted 15 of 101 total sirens; 8 of which had DC Battery Backup Power. As a result, this event is being reported under 10 CFR 50.72 (b)(3)(xiii) and guidance in NUREG-1022 as a major loss of off-site communications capability (e.g. offsite notification system). "Power was restored to 8 sirens, 4 in Harrison County and all 4 from Pottawattamie County on March 5, 2008 at 1413 hours. One siren in Harrison County was restored at 1417 hours. The remaining 6 sirens were restored at 1529 hours. The power loss was determined to be due to a farm equipment malfunction." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-05
44035 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-03-05 08:00 | 2008-03-05 19:10 | 2008-03-07 | VACUUM DAILY INSPECTIONS NOT COMPLETED "Raschig Ring Vacuum Cleaners (RRVCs) are used within BWXT's Research and Test Reactors and Targets (RTRT) radiologically controlled area to collect floor scrubbing solutions. There are no fissile solutions present in the area. The RRVCs are checked daily to ensure the vessels are adequately filled with Raschig rings. According to the form used to document the inspection, the last time the level was verified it was noted as 'good.' However, the inspection was last performed on January 28, 2008. The RTRT foreman had recently been assigned to the area and was not aware of the requirement to perform the daily check. On the morning of March 5, 2008 the foreman realized the check had not been performed and proceeded to inspect the RRVC. The level of the rings within the vacuum cleaner was judged to be inadequate (the form does not contain specific acceptance criteria). The rings were approximately 5 inches below the level of the hose intake. There was a minimal amount of contaminated floor scrubbing solution in the vacuum cleaner at the time of discovery. Only solutions from floor scrubbing are collected with RRVCs in RTRT. Fissile solutions are not generated in the area. The RRVC was immediately removed from service pending the results of an investigation. "The initial filling of the vacuum cleaner with Raschig rings by an operator is an Item Relied on for Safety (IROFS). The vacuum cleaner was adequately filled with Raschig rings in September of last year during the semi-annual inventory. However, at the time of event the ring level was less than adequate, resulting in a degraded IROFS. The daily inspection of the Raschig ring level is a second IROFS to ensure an adequate ring level on an ongoing basis. The failure to perform this inspection is a failure of this IROFS. The remaining IROFS is the operator controls what is collected (and therefore the U235 concentration) with the RRVC. Only contaminated floor scrubbing solutions are vacuumed within in RTRT, not fissile solutions. "There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. There was a portion of the RRVC that contained no rings, but there was only a minimal amount solution in the vacuum cleaner. However, with the degradation of one IROFS and the loss of a second, double contingency could no longer be assured. "BWXT is making this 24 hour report in accordance with 10 CFR 70, Appendix A (b)(2), 'Loss or degradation of items relied on for safety that results in failure to meet the performance requirements of § 70.61.' "The use of the RRVC in the RTRT area was immediately suspended by Nuclear Criticality Safety pending further investigation." The Licensee notified the NRC Resident Inspector. * * * UPDATE FROM C. YATES TO P. SNYDER ON 3/6/08 AT 1426 * * * "As a result of the ongoing investigation supplemental information to this notification is being provided. "The investigation identified that two other vacuum cleaners were not adequately filled with Raschig rings. One of these RRVCs is used within the Chemistry Lab. The ring level in this vacuum cleaner was approximately 3 inches below the level of the hose intake. The vacuum is used in the Chemistry Lab for floor scrubbing purposes. Although there are no fissile solutions in the lab, the NCS posting on the RRVC allows concentrations of up to 400 grams 235 to be collected. This is the same NCS posting on RRVCs in BWXT's Uranium Recovery facility. "Although unlikely, it is possible that the Chem Lab RRVC could be transferred to Uranium Recovery and used to collect high concentration fissile solutions. The ring level of RRVCs used in Uranium Recovery is checked daily. Should the Chem Lab RRVC be moved to Uranium Recovery there are no documented controls to check the ring level before its use. Potentially, the Chem Lab RRVC containing an inadequate level of Raschig rings could have been used to collect a high concentration fissile solution. "The filling of the vacuum cleaner with Raschig rings in accordance with American Nuclear Society Standard 8.5 is an Item Relied on for Safety (IROFS). The standard states, 'The level of the solution shall not exceed the level of uniformly packed rings.' The Chem Lab vacuum cleaner was not adequately filled with Raschig rings according to the standard. This IROFS was degraded. A second IROFS for the RRVC is the operator inspects the Raschig ring level according to ANS 8.5. The standard states, 'Raschig rings shall be inspected periodically to demonstrate their continued criticality control properties.' One of the required tests accounts for settling over time. The standard further states, 'If settling is detected, rings meeting specifications of this standard shall be added to restore full packing.' This second IROFS had failed given the level of the rings in the Chem Lab RRVC at the time of discovery. As such, no IROFS as documented in the Integrated Safety Analysis Summary remained. Double contingency had been lost. "There was no immediate risk of a criticality or threat to the safety of workers or the public as a result of this event. There was a portion of the RRVC that contained no rings, but there was only a minimal amount of solution in the vacuum cleaner. However, with the degradation of one IROFS and the loss of a second, double contingency could no longer be assured. "BWXT is making this 1 hour report in accordance with 10 CFR 70, Appendix A, (a)(4)(ii) - An event or condition such that no items relied on for safety, as documented in the Integrated Safety Analysis summary, remain available and reliable in an accident sequence evaluated in the Integrated Safety Analysis, to perform their function: Prevent a nuclear criticality accident." Notified R2DO (Hopper), NMSS (Easton) and Fuels OUO Group (e-mail). * * * UPDATE FROM B. COLE TO P. SNYDER ON 3/7/08 AT 1752 * * * The following "additional supplemental information is being provided to Event Notification #44035 as a result of the ongoing investigation. "During the investigation of Event Notification #44035, a concern was expressed about the ability of a RRVC to suction solution above the level of the Raschig rings. It is BWXT's opinion that it is possible to collect solution above the level of the Raschig rings in the vacuum cleaner. "The criticality safety of the RRVCs is based on American Nuclear Society Standard 8.5, 'Use of Borosilicate-glass Raschig Rings as a Neutron Absorber in Solutions of Fissile Material.' The standard states, 'The level of the solution shall not exceed the level of uniformly packed rings.' It is BWXT's opinion that it is credible for the solution to exceed the level of the Raschig rings in the RRVC. "There is no immediate risk of a criticality or threat to the safety of workers or the public. It is BWXT's opinion that under certain conditions there is a potential for high concentration SNM bearing solutions to be collected above the level of the Raschig rings. According to internal spill procedures this condition is not likely, but is credible. As such, this potential condition is an unanalyzed condition where double contingency is lost. "BWXT is making this 24 hour report in accordance with 10 CFR 70, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of §70.61. "The use of all RRVCs at the BWXT facility was immediately suspended by Nuclear Criticality Safety pending further investigation." Notified R2DO (Hopper), NMSS (Easton), and Fuels OUO Group (E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-03-11
44034 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-03-05 14:43 | 2008-03-05 17:44 | 2008-03-05 | AUTOMATIC SCRAM DUE TO APPARENT MALFUNCTION IN TURBINE CONTROL SYSTEM "At 2:43 p.m. CST, an unplanned automatic reactor scram occurred. The initial investigation determined that the event resulted from an apparent malfunction in the main turbine control system. This had the effect of causing reactor steam pressure to exceed the trip set point for the reactor protection system, initiating the reactor scram signal. All reactor control rods inserted, and the main feedwater system remained in service. Reactor safety-relief valves initially lifted as a result of the pressure transient. Reactor pressure is now being controlled by steam line drains with turbine bypass valves as a backup. There was no condition requiring the actuation of emergency diesel generators or emergency core cooling systems." "NRC Resident Inspector has been notified." | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-03-05
44033 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2008-03-05 | 2008-03-05 16:14 | 2008-03-07 | AGREEMENT STATE REPORT - MISADMINISTRATION OF Y-90 MICROSPHERES The State provided the following information via facsimile: "A medical licensee notified the Department of a misadministration during a Y-90 microsphere procedure, The problem was identified at the conclusion of the procedure when staff noted that 50% of the Y-90 microspheres were still in the application kit, resulting in a 50% underdose to the patient. The licensee's medical physicist, who is investigating the incident, was unsure if the problem was caused by a faulty injection valve or human error (e.g.. The valve was turned to the wrong position during the procedure). The licensee is Skyridge Medical Center Denver, CO, License 1053-01. "No other details are available at this time. "The Department has initiated an investigation of this incident." * * * UPDATE ON 03/08/2008 AT 0847 EST FROM FSME (FLANNERY) TO ALEXANDER * * * The NRC has reviewed this event and determined it to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-03-10
44032 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-03-05 | 2008-03-05 16:21 | 2008-03-05 | AGREEMENT STATE REPORT - ABANDONMENT OF MATERIALS MANUFACTURING FACILITY The Commonwealth of Massachusetts called to report that one of their materials licensees has ceased business and terminated or dismissed a majority of their employees. The licensee is under an M&D order, and a review of an inventory of materials on the site indicates there are materials at the site which exceed the allowable quantities in Table 1 of the M&D order. Since the business is no longer staffed, the Commonwealth of Massachusetts has expressed concerns with security at the facility. The issue was discussed in detail on a conference bridge with NRC Headquarters, Region 1, and Commonwealth of Massachusetts representatives. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-03-10
44031 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-01-10 | 2008-03-05 14:53 | 2008-03-05 | AGREEMENT STATE REPORT - LOST IODINE-125 BRACHYTHERAPY SEEDS "A permanent prostate seed implant was performed on 12/21/07. Following this case there were 18 unused seeds remaining. Unused seeds are kept in the original shielded container provided by the vendor and stored in the nuclear medicine hot lab until returned by the Radiation Safety Officer (RSO) to the vendor for ultimate storage and disposal. Unused seeds are normally returned once each quarter by the RSO. "In this case, however, the nuclear medicine technologist transferred the 18 seeds from the shielded container to a lead-lined radioactive waster bin for the storage of dry-solid active waste such as gloves, absorbent pads, etc. potentially contaminated with Tc-99m. This waste bin is not used for medical waste such as syringes, sharps, etc. "The dry-solid radioactive waste bins are held for decay-in-storage. Based on the preliminary information and a review of the radioactive waste disposal log, this particular bag was surveyed and disposed of on either 1/10/08 or 2/6/08. Since they use two bins and hold for radioactive decay until the other is full, it is not clear at this time as to which bag was disposed in the regular trash. Discovery of the lost material was through inquiries by the RSO concerning how many unused seeds were available this quarter for return. If the seeds were disposed of in the regular trash on 1/10/08, the activity lost would be 5.03 milliCuries; if disposed of in the regular trash on 2/6/08, the activity lost would be 3.68 milliCuries. "The possible disposition of the licensed radioactive material at this time is the landfill. A detailed written description of the incident will be submitted within 30 days. "The State of Wisconsin plans to investigate this incident on an upcoming inspection." Wisconsin Event Report ID: WI080004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-03-10
44030 | 0 | PACIFICORP ENERGY |  |  |  |  | 2007-02-16 | 2008-03-05 11:47 | 2008-03-05 | TWELVE LOST TRITIUM EXIT SIGNS The licensee provided the following information via email: "In February of 2007 PacifiCorp Energy received the NRC letter (NRC Regulatory Issue Summary 2006-25) regarding Tritium exit signs. The receipt of the NRC 2006-25 instruction letter prompted Wyodak plant to do an inventory of Tritium exit signs and review the NRC standards and rules. When reviewing the 10CFR20.2201 rules in regards to missing sources, Wyodak plant subsequently started an investigation and discovery of the now missing Tritium exit signs. "The following is a brief description of our investigation of missing Tritium exit signs: "In 1993 a contractor (Montague) was hired to build a new coal handling facility at Wyodak plant that is owned by Black Hills Power and PacifiCorp Energy. An assumption is made that the contractor ordered 22 Tritium self luminating exit signs from Isolite and installed them in the new coal facility. The contractor (Montague) who built the Secondary Crusher Facility is no longer in business to verify any of the assumptions. "During the facility construction most of the new coal handling facility was being handled by Black Hills Corporation. Later owner / operator lines were finalized and PacifiCorp Energy took over operation of the facility. "In about 1999 the coal handling operator's control building which was a part of the 1993 facility was torn down. It is believed that two of the 1993 Tritium exit signs were destroyed with the demolition of this building. "In 2003 Isolite notified PacifiCorp that the 22 self luminating Tritium exit signs purchased in 1993 were about to come to the end of their effective life. This call is what leads us to the assumption that 22 Tritium signs were purchased and installed in 1993. From the Isolite telephone call in 2003 PacifiCorp Energy's Wyodak plant purchased 22 new Tritium exit signs to replace the original 1993 signs. A work order was written to change out the old signs. The work order was never completed. "From the ongoing investigation we now believe that only 16 of the original 22 Tritium exit signs were installed by the contractor (14 in the coal handling facility and 2 in its control building). It is assumed that 6 of the Tritium exit signs left the plant at the end of the 1993 construction with the contractor. "We are currently working with Isolite to identify the serial numbers of the missing Tritium exit signs. "Disposition of the radioactive material: "6 - Tritium exit signs with 7.5 curries each are assumed to have been taken by the contractor (Montague) in 1993 - lost and not recoverable. "2 - Tritium exit signs with 7.5 curries each were hauled to trash with the demolition of the coal operators control building in 1999 assumed lost and not recoverable. "2 - Tritium exit signs with 7.5 curries lost by plant in 2003 assumed to be in a landfill and not recoverable. "2 - Tritium exit signs with 11.5 curries, S/N's 224944 and 224947 lost by plant somewhere between 1993 and 2007 assumed to be in a landfill and not recoverable.. "Radiation exposure to individuals: "It is believed that no individual exposure took place or any individual risk was involved. "Actions taken to recover the material: "Plant personnel have made a comprehensive search throughout the plant, plant storage and shop areas, plant warehouses, and coal facilities. Plant tried to make contact with the original installation contractor (Montague) but the company has gone out of business. Interviewed employees that might have had any knowledge of the Tritium exit signs. The results of the plant investigation are reported above. "Actions taken to prevent recurrence. "Wyodak Plant has completed an inventory of the 1993 and 2003 signs. Maps have been made of Tritium exit signs in use. "A corporate policy has been initiated on the use and handling of Tritium exit signs. An annual inventory list with model and serial numbers has been created for tracking and inventory purpose. Employees responsible for the ordering, disposal, and installation of Tritium signs will receive annual training on the corporate policy." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-03-05
44029 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-02-18 10:00 | 2008-03-04 17:18 | 2008-03-04 | AGREEMENT STATE REPORT - DENSITY GAUGE CONTAINING CS-137 INADVERTENTLY THROWN AWAY AS SCRAP WAS LATER RECOVERED "Brief Description of Incident "Railroad [RR] car arrived at Nucor Steel [in South Carolina] at 10AM on February 18, 2008. The RR car set off the exploranium detection equipment, so to ensure accuracy the RR car was passed through 4 times. Radiation measurement of RR car #JOSX 1771 was 25 microR/hr [which is] five times background (5 microR/hr). Notified SC-DHEC -Radiation Waste [DELETED] who further contacted NC DENR. [DELETED] from SC Nucor Steel was given CRCPD approval (see SC-NC 08-01) for return trip of rail car to point of origin, Iron & Metal Goldsboro, N.C. "The Rail Car numbered JOSX 1771 returned from Nucor Steel Darlington, SC on February 28, 2008. [NC-DENR] arrived at their location in Goldsboro on February 29, 2008 in the AM, as requested and took reading from the rail car and found only one hot spot (35 microR/hr - Ludlum 19) that was located on the left side of the railcar toward the upper middle portion of container. The item in question was located. "I annotated what was legible and it is the following: Model number 7062 BP; Serial Number 18317; Manufacturing Date 1984; Type and Amount of Isotope Cs-137, 100 mCi. Highest Readings 10.5 mR/hr on contact with Ludlum 19 and Identifinder. "Gauge SN 18317 was retrieved from Iron & Metal Goldsboro with chain of custody letter signed by all parties, then taken to storage room at the GAF Materials Corp. where three other gauges are now kept. GAF Materials has custody of the damaged gauge and will package it and ship it to a suitable vendor for repair. N.C. Incident Number 08-09. The State of North Carolina informed Region 1(Jim Cotton). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-03-07
44028 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-03-04 08:16 | 2008-03-04 11:19 | 2008-03-04 | ERDS LINK DETERMINED INOPERABLE FOR 3 HOUR PERIOD "On 3/04/08 at 0816 EST, the Control Room was notified that the ERDS Link was inoperable from 1815 to 2115 EST on 3/03/08. "During the troubleshooting it was discovered that a fuse was blown on the ERDADS I/O Subsystem Chassis. The ability to activate the ERDS Link is done by the Tesselators which were locked up due to the blown fuse. Removing power fuse for inspection and replacing was completed, chassis resumed normal functions. The ERDS link was returned to operable 3/03/08 at 2115 EST. "Initial determination did not correctly identify the loss of ERDS Link functions. Upon later review by Engineering, it was determined that the link was inoperable during the 3 hour period." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-04
44027 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2008-03-04 01:00 | 2008-03-04 02:16 | 2008-03-04 | PLANNED MAINTENANCE ON MlSHlCOT SUBSTATION BY WPS RESULTS IN GREATER THAN 50% SIREN COVERAGE LOSS "On March 4, 2008, at 0100 CST, ten emergency notification system sirens in the Kewaunee Power Station Emergency Planning Zone (one in Kewaunee County, nine in Manitowoc County) were de-energized due to a planned power outage. The loss of power to these emergency notification sirens resulted in a lost population coverage of 51.2%. As a result, this event is being reported under 10 CFR 50.72(b)(3)(xiii) and guidance in NUREG-1022 as a major loss of off-site communications capability. "The expected duration of the planned power outage is 2 hours. Kewaunee and Manitowoc County Emergency Management agencies have already established appropriate contingency measures for the planned loss of the emergency notification system. Contingency measures include route alerting and an available plane with loud speaker for the areas affected by the power outage. The State of Wisconsin and the Federal Emergency Management Agency were previously informed of this planned outage. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-03-04
44026 | 0 | AREVA NP INC |  |  |  |  | 2008-03-03 11:26 | 2008-03-03 11:45 | 2008-03-03 | EXTERNAL CONTACT RADIATION READING EXCEEDED ALLOWABLE LIMITS "On March 3, 2008 at approximately 1126 EST, the Radiation Protection organization at AREVA NP Inc. Lynchburg, determined that a shipment of fuel services equipment (Box 0454) exceeded the 200 mrem/hour dose rate specified in 10 CFR 71.47 (b)(1). The equipment was being returned after use during a refueling outage. Radiation Protection surveyed the shipping container and obtained a reading of approximately 340 mrem/hour. In accordance with 10 CFR 20.1906(d)(2) the final delivery carrier has also been notified. This immediate notification is being made in accordance with the requirements of 10 CFR 20.1906(d)(2) and 10CFR 71.47(b)(1)." The fuel cleaning equipment had been recently used during a refueling outage at Watts Bar. * * * UPDATE FROM GEOFF WERTZ TO JOE O'HARA AT 1447 ON 3/3/08 * * * Mr. Wertz reported that area around the hot spot on the container was smeared, and no evidence of loose surface contamination exists. Notified R1DO(Caruso), FSME(Morell), and NMSS(Giitter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | VA | TRA |  | 20.1906(d)(2) |  |  |  | 0 | 2008-03-03
44025 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2008-03-01 13:15 | 2008-03-01 14:34 | 2008-03-01 | OFFSITE NOTIFICATION DUE TO STEAM LEAK AFFECTING ASBESTOS LAGGING "An emergency asbestos project notification was made to NYS [New York State] Department of Labor in accordance with NYS Code Rule 56. The amount of damaged insulation has been identified as a minor project. The emergency asbestos project is a result of a Moisture Separator Reheater 1A level control system steam leak, which occurred at 0535 3/1/08. No visible damage to permanent structures or equipment, beyond the steam leak, is evident." A cap blew off a level transmitter which wetted and dislodged the surrounding asbestos insulation which subsequently fell to the floor below. The steam leak has been isolated. There were no injuries or adverse impacts on plant operations. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-03-01
44024 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2008-03-01 04:27 | 2008-03-01 09:52 | 2008-03-01 | EMERGENCY FEEDWATER ACTUATION WHILE SHUTTING DOWN "On 03/01/2008 a pre-planned unit shutdown was in progress to repair a reactor coolant pump seal. At approximately 20% reactor power, a main feedwater flow perturbation occurred. This flow perturbation resulted in an Emergency Feedwater actuation at 0427 [EST]. Both Emergency Feedwater system trains started automatically on low levels in the Once Through Steam Generators as designed. Main feedwater system recovered and continued to supply inventory with levels stabilized at the required low level setpoint. Following plant stabilization, Emergency Feedwater was secured and the pre-planned unit shutdown was resumed. This event is reportable under the requirements of 10 CFR 50.72 (b)(3)(iv)(A)." The cause of the feedwater flow perturbation is still under investigation. The licensee notified the NRC Resident Inspector. | 20 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-03-01
44023 | 0 | SABIA CORPORATION |  |  |  |  | 2008-02-29 | 2008-02-29 17:52 | 2008-02-29 | STRONTIUM-90 SOURCE LEAKAGE LEADS TO UNPLANNED CONTAMINATION OF WORKER While disassembling industrial gauges for source disposal, a Sr-90 source was breached causing contamination of the work area and one worker performing the task. Prior to disassembly, the source was leak tested with no leakage found. The size of the source is unknown at this time. The licensee contacted Region IV materials personnel to discuss this event and it was suggested by the region that the contaminated individual undergo urine bioassay. Region IV has an inspector in the area who will be at the Sabia facility in the morning. Notified R4DO (Campbell) and FSME EO (Bubar). * * * UPDATE FROM J. MILLER TO HOWIE CROUCH ON 02/29/08 @ 1956 HRS. * * * The licensee reports that the source came from a NER 592 gauge, source S/N 1265 manufactured on 8/9/84. The original strength was 100 mCi. Current source strength is 57 mCi. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EXCESSIVE RELEASE | UNPLANNED CONTAMINATION | [8 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2202(a)(2) | 30.50(b)(1) |  |  | 0 | 2008-02-29
44022 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-07-01 | 2008-02-29 16:39 | 2008-02-29 | AGREEMENT STATE REPORT - MISSING RADIOACTIVE MATERIAL "Avery Dennison, a General Licensee, reported to the Agency [MA Bureau of Environmental Health] via telephone at 10:15 a.m. on February 26, 2008 that two static eliminator devices are believed to be missing. Avery Dennison reported that one device was sent to the manufacturer in July, 2007 but that the manufacturer never received it. Avery Dennison reported that another device was in a box and it was tossed. "The Agency followed up with the Licensee and the Manufacturer (NRD, LLC) of the devices and confirmed that the following two devices are believed to be missing: "Device 1: NRD, LLC Model P-2001-080, s/n A2EV025, containing 181.1 millicuries of Po-210 "Device 2: NRD, LLC Model P-2001-080, s/n A2FM086, containing 181.1 millicuries of Po-210 "Device 1 has an approximate assay date of January 3, 2006. "Device 2 has an approximate assay date of January 12, 2007. "The Agency has scheduled a site visit with cognizant individuals to investigate the matter." Notified R1DO (Doerflein), FSME EO (Bubar) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-03-05
44021 | 0 | REID HOSPITAL & HEALTH CARE SERVICE |  |  |  |  | 2008-02-27 11:00 | 2008-02-29 14:50 | 2008-03-03 | PROSTATE TREATMENT SEEDS IMPLANTED IN UNINTENDED LOCATION Sixty-two I-125 seeds were to be implanted in a patient's prostate. After 37 seeds were implanted, surgery was halted and the location verified as being 1-2 cm below the prostate. The hospital is evaluating the medical implications of this event. The physicians and patient were notified. Seeds: 0.315 milliCuries each * * * UPDATE FROM FLANNERY TO ALEXANDER AT 0713 EST ON 03/03/2008 (VIA E-MAIL) * * * The NRC's medical events review committee has determined that is report is a medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2008-03-03
44020 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-02-28 16:56 | 2008-02-29 13:15 | 2008-02-29 | MEDIA/PRESS RELEASE CONCERNING BWXT ACTIVITIES "In response to additional media inquiries regarding the NRC News Release No. II-08-002, BWXT will provide the attached information to media representatives contacting BWXT for additional information. In response to media inquiries concerning the possible use of Lynchburg city wastewater treatment plant to treat water from BWXT, BWXT will provide the attached information to media representatives contacting BWXT for additional information: "Regarding NRC News Release No. II-08-002: "Q: What are some of the corrective actions taken by the company? One NRC document I read referred to a corrective action of installing brackets onto the raschig ring vacuum cleaners for transport. Is that one of the corrective actions, and has it been completed? What other corrective actions have been taken? "A: We developed a comprehensive list of corrective actions in response to last year incident. Currently, we are in the process of completing all corrective actions, and are on schedule to meet our commitments to the NRC. "Q: The Company was given 30 days to pay the fine or appeal it. Which action was taken? "A; The company paid the fine. "Regarding Wastewater Treatment inquiry: "Q: I just learned that the city's wastewater treatment plant is studying the idea of treating water from the B&W facility, and that B&W is paying for the study. Could you provide information, or connect me with someone in the company who can offer a comment on this study? Has B&W been treating its own water before? Why is the company interested in possibly having the city treat the water instead? "A: A number of new regulations have been issued in recent years to address discharges of nutrients to the Chesapeake Bay and its tributaries. To meet the new requirements, B&W is studying a variety of options, including the possibility of constructing a new pipeline to allow us to discharge a portion of our wastewater into the city's waste water treatment plant. We are working with the Lynchburg Regional Wastewater Treatment Facility and Campbell County to perform a feasibility study for this option to ensure that the city's treatment plant can handle our flow without impacting their current treatment parameters. It's important to note that these wastewaters are non-radioactive. However, the project is still very much in the preliminary stages and a decision on whether or not to pursue this option wont be made for some time." The licensee will be notifying the NRC Resident Inspector. Notified R2DO (Munday), NMSS EO (Giitter) and Fuels OUO via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-02-29
44019 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-02-28 | 2008-02-29 11:09 | 2008-02-29 | AGREEMENT STATE REPORT - OVEREXPOSED PERSONNEL MONITORING BADGE The following information was received from the State of Louisiana via fax: "On February 28, 2008, TEAM Industrial Services reported that an industrial radiographer's personnel monitoring badge received an excessive exposure of 10 rem. The industrial radiographer left his badge in the work truck while he was not performing radiography for a few days. The truck was parked next to a tank that was being x-rayed. According to TEAM, this exposure was just to the badge and not to the radiographer. According to TEAM, the actual exposure to the radiographer is 67 mrem. This incident is under investigation and further information will be forwarded once available." LA Event Report ID: LA 080006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-03-05
44018 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-02-22 | 2008-02-29 10:39 | 2008-02-29 | AGREEMENT STATE REPORT INVOLVING POTENTIAL DAMAGE TO A MOISTURE DENSITY GAUGE The following report was received via email: "A Louisiana Department of Transportation and Development (DOTD) van was involved, in an accident while carrying a Humboldt 5001 soil moisture density gauge. The gauge contained 10 mCi of Cs-137 (s/n9733GQ) and 40 mCi of Am-241 (s/nNJ03934). The Louisiana State Police notified LA DEQ of the accident and stated that the overpack was not breached and that readings at the surface were 0.9 mR/hr. The gauge and overpack were inspected at the DOTD district laboratory that was 0.5 miles from the accident. The overpack was in overall excellent condition except for a small hole (approximately 1 inch in circumference) which had been punched through the exterior wall but did not puncture the interior wall of the overpack. The overpack and gauge were surveyed by a DEQ inspector and recorded readings of 0.2 mR/hr at 1 meter which, correspond to the transportation index. A leak test has been sent off for the gauge and the results are pending. Will update with further information when it becomes available." LA Event Report ID No.: LA080005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-03-05
44017 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2008-02-29 10:40 | 2008-02-29 11:05 | 2008-02-29 | OFFSITE NOTIFICATION OF A SMALL OIL SPILL "At approximately 1040 EST, a spill of approximately 4.5 gallons of hydraulic fluid from a small dry cask storage utility vehicle occurred. Approximately half the fluid spilled onto the asphalt roadway and half onto the soil. This is not a de-minimis spill and New York State Department of Environmental Conservation and the Westchester County Department of Health will be contacted. Clean-up of the spilled fluid is in progress and the leaking vehicle has a containment device under the leak. There is no impact to sewers or waterways. No operating equipment on Unit 2 or Unit 3 is affected." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-02-29
44016 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-02-29 04:51 | 2008-02-29 05:40 | 2008-02-29 | MANUAL REACTOR TRIP DUE TO HIGH STEAM GENERATOR WATER LEVEL "With the Unit 4 reactor in Mode 1 at approximately 10% power and immediately following main turbine start-up and synchronizing the main generator to the grid, the reactor and turbine were manually tripped due to 4A steam generator water level rising uncontrollably. The reactor was manually tripped prior to reaching the reactor protection trip point for high steam generator water level. An investigation is in progress to determine the cause of the high water level in the 4A steam generator." All rods fully inserted upon the trip and all systems functioned as required. There were no complications and the 4A steam generator water level is currently within the normal water level band. The licensee will be notifying the Resident Inspector. | 0 | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-02-29
44015 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-02-28 | 2008-02-28 19:16 | 2008-02-28 | AGREEMENT STATE REPORT - SOURCE DISCOVERED The State provided the following information via email: "The Licensee reports that they have 'discovered' residual radiation left in a Nuclear Systems irradiator model 'U' following the removal of the original 5000 Ci of Co-60 by a contractor of the OSRP last summer. The licensee thinks that one of the original 40 capsules that comprised the 8 rods (5 sources/rod) that contained the original 5000 Ci of cobalt 60 in 1958 may have remained in the device following source removal. The sources were removed for disposal last summer as part of the OSRP program to remove old unneeded sources of radiation." CA Report: 022808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-03-04
44014 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-02-28 | 2008-02-28 14:05 | 2008-02-28 | AGREEMENT STATE REPORT - MISSING / BROKEN TRITIUM EXIT SIGNS "On January 30, 2008, the RHB South ICE office received information regarding a broken exit sign containing approximately 11 Ci of H-3 (as of 2006). The sign was broken in a dormitory room at Biola University in La Mirada, California (later discovered to have occurred around December 13, 2007). This is a generally licensed device. This incident was investigated and handled under the 011308 Investigation by this office. On February 13, 2008 we were notified of a second H-3 exit sign that had been found broken (3 tubes of approximately 1 Ci each) on February 8, 2008. This broken H-3 sign was found during the inventory process of H-3 signs possessed by Biola requested by this office. Biola had never registered these GL devices to the State. During the inventory process Biola discovered that several of these H-3 exit signs were missing. For several weeks Biola searched dormitory rooms and other campus locations in performing the inventory of these devices. On February 27, 2008, I received an email from [a lady] stating that of they could only account for 79 of the 83 signs originally received for installation in Horton Hall, meaning that they do not know the location of four of the signs (77 physically present and 2 disposed account for the 79). The total remaining H-3 activity of the four signs is approximately 44 Curies. "Biola will register the remaining signs with the State, and send a copy to this office." CA Number: 022708 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-03-04
44013 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-02-28 12:38 | 2008-02-28 13:46 | 2008-02-28 | "PLANNED MAINTENANCE ON SAFETY PARAMETER DISPLAY SYSTEM (SPDS) AND EMERGENCY RESPONSE DATA SYSTEM (ERDS) "At 1238 CST hours on 2/28/2008, the SPDS and ERDS were removed from service to support maintenance at River Bend Station. The work is expected to be completed in approximately 8 hours. "During this time, other Main Control Room indications and alternate methods will be available to implement the Emergency Plan. Since the SPDS computer system will be unavailable for greater than two hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10 CFR 50.72 (b) (3) (xiii). "A follow-up notification will be made to the NRC after the SPDS and ERDS are returned to service. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM T. SHENK TO P. SNYDER AT 1750 ON 2/28/08 * * * SPDS and ERDS were placed back into service as of 1748 local time. The licensee will notify the NRC Resident Inspector. Notified R4DO (Campbell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-28
44012 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-27 | 2008-02-27 18:27 | 2008-02-27 | DISCOVERY OF INAPPROPRIATE UNESCORTED ACCESS GRANTED TO CONTRACT EMPLOYEE Actual entry into a protected area of an individual that had gained unescorted access through withholding information during the badging process. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-02-27
44011 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-02-27 | 2008-02-27 16:15 | 2008-02-27 | AGREEMENT STATE REPORT - MISSING MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "On February 27, 2008, Circle Inc. discovered that a Troxler nuclear gauge with a 9 mCi source of Cs-137 (s/n 50-9134) and a 44 mCi source of Am-241 (s/n 47-14943) was missing from a construction site on the levee near Nicole and Lapalco in Westwego, LA. The incident is under investigation and additional information will be forwarded once it is received." Louisiana Event Report: LA080004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-03-03
44010 | 0 | ADVANCED CARE MEDICAL |  |  |  |  | 2008-02-27 10:45 | 2008-02-27 15:50 | 2008-02-27 | UNPLANNED CONTAMINATION CAUSED BY DAMAGED I-125 SEED During assembly of a brachytherapy seed strand in the production lab, one seed was damaged and contaminated the working tool. The seed was I-125 containing 0.399 millicuries. Contamination levels of the working tool was determined to be 17,224 dpm. Decontamination of the working tool was completed and restored working tool to normal background levels. The other 82 seeds that were in the vicinity of the working tool have been quarantined. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2008-02-27
44009 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-02-26 13:09 | 2008-02-26 14:38 | 2008-02-26 | UNITS 3 AND 4 TRIPPED DUE TO GRID FLUCTUATIONS "At 1309 both U-3 and U-4 tripped from 100% power due to a momentary power fluctuation caused by grid instabilities. All systems responded normally with the exception of the 4C non-vital 4KV bus which deenergized. All vital 4KV busses on both units are supplied from offsite power and both units are stable with Auxiliary Feed Water supplying feed to all steam generators. Current information from system indicates the grid is stable. 4C non-vital 4KV bus restoration is complete." No relief valves or safeties lifted. Decay heat path is AFW to S/G's with normal heat sink to the condenser and canal. All safety related equipment is operable and in standby. No ECCS actuation. FPL has not given a cause of the grid disturbance. The licensee is investigating the cause of the non-vital bus deenergizing. The Florida State Warning Point has been notified. The licensee notified the NRC Resident Inspector. * * *UPDATE PROVIDED BY MARK JONES TO JEFF ROTTON AT 1732 EST ON 02/26/08 * * * The licensee provided the following update to report a valid specified System actuation per 10CFR50.72(b)(3)(iv)(A) that occurred at 1614 EST on 02/26/08. "At 1614, an inadvertent initiation of the Auxiliary Feedwater (AFW) System occurred on Unit 4. "During the Unit 4 reactor trip, the 4C 4KV bus de-energized due to grid transient. This caused the 4B Steam Generator Feed Pump (SGFP) breaker to trip with control switch in 'mid after start' position. Later, with the control switch for the 4B SGFP still in 'mid after start' position, operators performed a procedure to swap feed source for the steam generators from SGFP to Standby SGFP. As part of this procedure, the 4A SGFP was secured. When the control switch for the 4A SGFP was taken to stop, the logic for start of the Auxiliary Feedwater System was met due to loss of last running SGFP. "The AFW system responded as expected for an auto initiation. Initiation of the AFW system was noted by the operators, and actions were taken to control feed flow rate and Reactor Coolant System temperature, pressure and inventory. The AFW system has been restored to standby status." The licensee has notified the NRC Resident Inspector. Notified the R2DO (Munday). | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-02-26
44008 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2008-02-22 | 2008-02-25 10:00 | 2008-02-27 | OHIO AGREEMENT STATE REPORT - TWO CONTAMINATED INDIVIDUALS The following information was obtained from the Ohio Department of Health via email: "Initial Notification: The Bureau [Ohio Department of Health Bureau of Radiation Health] was notified via e-mail at approximately 4:00 PM on Friday, 2/22/08 that the licensee experienced a contamination incident in their source handling facilities. The e-mail was sent to a Bureau staff member who was out of the office until Monday, 2/25/08. The e-mail was retrieved by the Bureau staff member at approximately 6:00 AM on Monday, 2/25/08. "The contamination incident involved two (2) employees who were working in the source disposal room. One employee was attempting to retrieve a source from one of the licensee's own SR-1 source holders (vintage 1972) using the saw. In doing so, he breached the 300 mCi Cs-137 source and contaminated the area with microspheres. The licensee's emergency procedures were immediately activated. Employees verified that there was no floor contamination outside of the disposal room through use of a pancake probe and then maslin wipes. The ventilation system was turned off. No activity was found outside the doors to the disposal room. A third employee went into the disposal room to do surveys and wipes and confirmed that contamination is present in the room. "The first employee involved in the contamination incident was removed from the disposal room, dressed in two Tyvek suits, and moved from the disposal room to the enclosed area outside that room where he could be frisked. He exhibited contamination on one hand and on one leg. The second employee, having taken additional wipes and surveys to determine the locations of contamination, was then removed. Contamination was detected on his hands as well as his shirt and pants. Decontamination commenced on both individuals. This information was contained in the initial e-mail notification from the licensee and was current as of 2/22/08. "Follow-up: The Bureau initiated a phone call with licensee management at approximately 8:15 AM on Monday, 2/25/08. During this call the licensee stated that the facility contamination is limited to the source handling room, which has been isolated and sealed with tape. The licensee further stated that no further decontamination work was done over the weekend once the individuals involved were decontaminated and the source handling room was secured. The licensee stated that the determination was made that the contamination on the two individuals involved was limited primarily to the clothing worn. This clothing was removed, and any areas of their body showing contamination were successfully decontaminated. One of the individuals had shown contamination near his nose. Surveys of tissues used by him to blow his nose during decontamination indicated no contamination, but nasal swabs of this individual were not done by the licensee. The licensee stated that bioassays of the contaminated individuals were not planned at this time. The Bureau informed the licensee that bioassays would be necessary for these individuals. "The Bureau has dispatched two inspectors to the licensee's facility in Cincinnati, Ohio, to arrive there late morning Monday, 2/25/08. The licensee has been instructed not to take any further actions regarding clean-up of the contaminated areas until the Bureau inspectors arrive. The Bureau will require a written action plan from the licensee for the decontamination process, which the licensee stated will be performed by an outside contractor." * * * UPDATE PROVIDED BY STATE OF OHIO VIA EMAIL (STEPHEN JAMES) TO JEFF ROTTON AT 1207 EST ON 02/27/08 * * * The following information was provided by the state via email: "UPDATE TO INITIAL REPORT: Two inspectors from the Bureau visited the licensee's facilities on Monday, 2/25/08. The inspectors verified that the licensee had secured ventilation and sealed off the sealed source disposal room where the incident occurred to prevent the spread of contamination. The licensee sealed off the room using duct tape around the doors and along the floor of the doorways. The inspectors also interviewed the individuals involved in the operations that resulted in the breaching of the source to determine the steps taken once the individuals became aware that the source had been cut into. The Bureau inspectors conducted confirmatory surveys, including wipe tests, of the area around the contaminated room and of the ventilation system discharges. These surveys indicated no evidence of contamination outside of the source disposal room. The Bureau also issued an order to the licensee on Monday, 2/25/08, prohibiting any additional sealed source removal operations by the licensee until further notice. "The Bureau contacted the licensee via telephone on Tuesday, 2/26/08, to discuss ongoing dose reconstruction efforts and the licensee's plans for decontamination of the sealed source disposal room. The licensee stated that the two individuals involved were scheduled for whole-body counting at the University of Cincinnati later in the week, which was the first available time this could be done. The licensee is also working on dose estimates from the incident, which will be provided to the Bureau as soon as they are completed. The licensee is in the process of selecting a contractor to perform the clean-up activities and will inform the Bureau once a contractor has been selected and a start date established. The licensee was informed that the Bureau will send representatives to attend the initial meeting with the licensee and the clean-up contractor to discuss the plan of action and timeline. The licensee was also informed that the Bureau would send inspectors to the facility periodically during the clean-up to perform confirmatory measurements and review the progress to date. The licensee was reminded that they were subject to the NRC M&D security orders and may need to address those as it related to the escorting of contractor personnel." Ohio Incident Reference number: OH2008-011 Notified R3DO (Kozak) and FSME EO (Michele Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2008-02-28
44007 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-25 05:40 | 2008-02-25 09:44 | 2008-02-25 | OPERATIONS SUPPORT CENTER RENDERED NON-FUNCTIONAL DURING PLANNED MAINTENANCE "Planned preventive and corrective maintenance activities are being performed today (2/25/08) on the Hatch Nuclear Plant's HP/Chemistry area emergency air handling unit. The HP/Chemistry area emergency HVAC is required for functionality of the Operations Support Center (OSC), as this area may be utilized during declared emergencies. These planned work activities are to be completed today within (15) hours. During the time these activities are being performed, the HP office emergency HVAC will not be available for operation and will be rendered non-functional during the performance of the work activities. "If an emergency condition requiring activation of the OSC occurs during the time these work activities are being performed, then contingency plans call for continued utilization of the HP/Chemistry areas as long as radiological conditions allow. Habitability surveys will be performed more frequently in the areas while they are being utilized. If required, respiratory protection equipment will be utilized, as appropriate, for emergency responders utilizing this area until such time as the power is restored to allow the HP/Chemistry emergency HVAC to be returned to service. "This event is reportable per 10 CFR 50.72 (b)(3)(xiii) as described in NUREG-1022. Rev. 2, since this work activity affects an emergency response facility for the duration of the evolutions." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-25
44006 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2008-02-25 01:40 | 2008-02-25 08:13 | 2008-02-25 | DEGRADED CONDITION DUE TO LEAKAGE ON A PRESSURIZER HEATER SLEEVE During in-service inspection VT-2 visual inspection, the licensee discovered dried boric acid on pressurizer heater sleeve C-3. All other pressurizer sleeves were inspected with no additional findings. The licensee will not increase coolant temperature until the repair is made to the sleeve. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-02-25
44005 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-02-23 16:00 | 2008-02-23 17:46 | 2008-03-20 | UNACCEPTABLE FLAW IN RPV CAP-TO-PIPE WELD "At 1600 EST, it was determined by a phased array ultrasonic examination that an unacceptable flaw existed in reactor pressure vessel penetration N9. This penetration leads to a capped line and the flaw is in the cap-to-pipe weld. The flaw is 2.3 inches in length and reaches a maximum depth of 43.6 percent through-wall on a 5.75 inch OD pipe. The flaw was discovered during the routine ISI [In-service Inspection] examination of this penetration. The flaw has been found unacceptable per paragraph IWB-3514.4 of the 2003 Addenda of ASME Section XI and is therefore reportable. Upon discovery of the flaw, all penetrations of this type were examined with no further findings. "A weld overlay repair is planned and should be completed by 3/6/08." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM J. ANDERSON TO P. SNYDER ON 3/20/08 AT 0943 * * * "On 2/23/2008 event number 44005 was made to report an unacceptable flaw in reactor pressure vessel penetration N9. The assumption made at that time was that the flaw seriously degraded the affected control rod drive (CRD) return line that was capped. This was based on the fact that the flaw was unacceptable from an ASME Section XI perspective and therefore reportable. Based on this assumption the event was reported in accordance with the following reporting requirement. "'10 CFR 50.72 (b)(3)(ii)(A) Any event or condition that results in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded;' "The depth of the flaw was initially reported to be 43.6% through wall and the thickness of the wall was measured to be 0.75 inches. Phased array ultrasonic examinations in accordance with Appendix VIII of Section XI were used to fully interrogate and characterize the circumferentially oriented flaw. The final dimensions were 2.3 inches in length on the inner diameter and a maximum depth of 60% through wall. A flaw evaluation of the Unit 1 CRD return line nozzle cap weld was subsequently performed by Structural Integrity Associates, Inc., to evaluate the 'as-found' condition and to determine the implications of the flaw on the affected system at the time of shutdown. The evaluation considered the flaw size and the appropriate stresses for operation. No crack growth was required to be assumed since the 'as-found' flaw was compared against the allowable flaw size which was used to determine the acceptability of the flaw during plant operation. Since the weld is associated with the capped CRD return line nozzle, the applied stress at the affected location was due to pressure loading only. "The flaw evaluation concluded that the requirements of Section IWB-3640 were satisfied for a flaw less than 75% through-wall. The 'as-found' depth of 60% through wall is less than the allowable depth of 75%. Based on this information, the Structural Integrity Associates, Inc. evaluation demonstrated that the flaw was acceptable per the ASME Code Section Xl, 2001 Edition through 2003 Addenda requirements. Since the as- found flaw depth at the N9 weld is less than the allowable flaw depth, the required safety factors were met at all times during plant operation. "Based on this updated information the conclusion has been reached that this flaw did not seriously degrade the plant or its principal safety barriers. Since the condition does not meet a reporting requirement, this notification serves to retract Notification # 44005 made on 2/23/2008." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-02-23
44004 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2008-02-23 03:14 | 2008-02-23 04:02 | 2008-02-23 | UNUSUAL EVENT DECLARED DUE TO HIGH DOSE EQUIVALENT IODINE GREATER THAN TECH SPEC REQUIREMENT Unit 1 was performing a plant shutdown in preparation for a refueling outage. RCS sampling indicated a dose equivalent Iodine-131 reading of 1.41 microCurie/gram with a Technical Specification limit of 1.0 microCurie/gram. As a result, the licensee declared an Notification of Unusual Event (NOUE) under EAL AU121. To reduce the dose equivalent iodine, the licensee placed maximum purification into service. Actions required to exit the NOUE include reducing dose equivalent iodine to below Technical Specification limits. The licensee has notified the NRC Resident Inspector. Notified R1 (Collins), R1DO (Powell), IRD (Cruz), NRREO (Batemen), NRR (Dyer), DHS (Doyle), and FEMA (Fuller). * * * UPDATE FROM AMY CORDENER TO HOWIE CROUCH @ 0612 EST ON 02/23/08 * * * The licensee is still in the NOUE. As of 0600, the last RCS sample indicated 1.15 microCurie/gm. NOUE exit criteria will be met when two successive samples indicate less than 1.0 microCurie/gm. Notified R1DO (Powell) * * * UPDATE FROM MICHAEL SAUL TO HOWIE CROUCH @ 0927 EST ON 02/23/08 * * * At 0908 EST, three consecutive Reactor Coolant System I-131 activity samples indicated approximately 0.9 microCuries/gm which is less than the Technical Specification limit. The licensee is still in the NOUE and will exit when at least one more sample indicates less than the Technical Specification limit. The licensee will be notifying the NRC Resident Inspector. Notified R1DO (Powell). * * * UPDATE FROM MICHAEL SAUL TO PETE SNYDER @ 1043 EST ON 02/23/08 * * * At 1035 EST, the licensee exited the NOUE based on four consecutive samples at less than 1.0 microCuries/gm of I-131. Notified R1DO (Powell), NRREO (Bateman), IRD (Cruz), DHS (Inzer) and FEMA (Sweetser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 1 | MD | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-02-23
44003 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-02-07 | 2008-02-22 15:32 | 2008-02-22 | AGREEMENT STATE REPORT - LOST ELECTRON CAPTURE CELL CONTAINING NICKEL - 63 SOURCE "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "The Boeing Company reported February 7th they are unable to find one gas chromatograph electron capture cell that contains 555 MBq (15 millicuries) of nickel-63. The Licensee became aware of the missing source on January 7, 2008, during a routine survey and inventory of their radioactive waste area. Based on their investigation, the licensee thinks the source was disposed of as radioactive waste in a shipment sent to the Low Level Radioactive Waste site in December 2007. The licensee attributes this to staff not following the established procedures for the transfer and disposal of the source. The person assigned waste area duties in December has subsequently left employment with Boeing. Confirming this directly is unlikely to happen. The Boeing RSO has reviewed the procedures and believes that when they are followed they are adequate to prevent loss of a source. However, the RSO will now require two people to be involved in the radioactive waste packaging process with both signing shipment documents before they are complete. The Boeing RSO reviewed the new procedure with the radiation safety staff. We are told, the discussion emphasized the importance of following the procedures. The RSO will have the waste manifest changed to show addition of the source. "Event Report #WA-08-011." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-02-27
44002 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2008-02-22 05:30 | 2008-02-22 09:10 | 2008-02-23 | LOSS OF COMMERCIAL AND EMERGENCY PHONE SYSTEMS The licensee experienced a loss of the onsite phone systems including ENS phones at 0530 EST. Offsite communications capability was maintained with the "Omni" phone circuit. The ENS and onsite phone system were restored at 0821 EST. It appears that the onsite phone system computer locked up. When the computer was rebooted, phone systems returned to normal. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JOHN POPIELARSKI TO JOHN KNOKE AT 1602 EST ON 02/22/08 * * * At 1430 EST the licensee determined the ENS line is inoperable but the commercial line is operable. At 1602, the ENS line is operable. The licensee, however, is still troubleshooting system. The licensee notified the NRC Resident Inspector. Notified R1DO (Powell). * * * UPDATE FROM BARRY HEDRICK TO JOHN KNOKE AT 2045 EST ON 02/22/08 * * * Licensee stated the computer system was found to have a corrupted hard drive, and that has been replaced. The main computer is now back in operation. The backup computer was found to have outdated hardware and that will be addressed at a later date. The licensee notified the NRC Resident Inspector. Notified R1DO (Powell). * * * UPDATE FROM JIM VASH TO JOE O'HARA AT 2130 EST ON 02/23/08 * * * All repairs to both computers are complete and the phone line has been tested SAT. The licensee will notify the NRC Resident Inspector. Notified R1DO (Powell). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-22
44001 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2008-01-29 | 2008-02-21 16:21 | 2008-02-21 | AGREEMENT STATE REPORT - MISSING TRITIUM SIGN The State provided the following information via email: "The general licensee reported a possible missing tritium sign on January 29, 2008. The sign (NRD, Inc, Model #3 T-4001, Serial # 91355) had been purchased in September of 1993. The licensee did a search for the missing sign. The search included questioning the electrical working crew leader and crew, electrical maintenance supervisor and a communication to the entire plant requesting information on the status of the sign. They also checked the area where bulbs and electrical material await recycling. The licensee believes the sign had been disposed of in the common trash." Report NE080001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2008-02-26
44000 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-02-12 | 2008-02-21 13:50 | 2008-02-21 | AGREEMENT STATE REPORT - BROKEN TRITIUM SIGNS The State provided the following information via email: "On February 12, 2008, the maintenance engineer from the Residence Inn in Corona, CA contacted RHB headquarters and left a message regarding two broken tritium exit signs. The message was not referred to the South RM ICE office until February 21, 2008. On February 21, 2008, [the State] dispatched an inspector to assess the situation, and ensure the signs are isolated and contained, until disposal can be arranged. The general licensee will also be requested to obtain a health physics consultant to assess potential exposures." CA NMED # 022108 * * * UPDATE FROM DONELLE KRAJEWSKI TO JOE O'HARA VIA E-MAIL AT 1704 ON 02/21/08 * * * "There were 2 tritium exit signs whose plexi-glass fronts were cracked. The H-3 tubes do appear to be ruptured since the letters are not completely and evenly lighted when you view the signs in a darkened room. "Each exit sign contained 0.426 TBq (11.5 Curies) H-3. Manufacturer - Shield Source Inc, Petersbourgh, Canada, Model 101, Distributed by - Safety Light Corp, Bloomsburg, PA 17815. The serial numbers are #U9453 and T7844. "Wipes were taken from the face of the signs and in the surrounding area, but it will be a couple of weeks before we get the results. The signs were individually packaged in plastic and were placed in a 5 gallon pail which will remain in a secure area until disposal by an authorized waste broker." Notified R4DO (Howell, L.) and FSME (Suber). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-02-26
43999 | 0 | VIRGINIA COMMONWEALTH UNIVERSITY |  |  |  |  | 2008-02-20 12:40 | 2008-02-21 13:22 | 2008-02-21 | POTENTIAL MEDICAL EVENT - UNDERDOSE OF Y-90 MICROSPHERES The licensee reported that a patient being treated for liver cancer received approximately half of the prescribed dose of Y-90 microspheres. The licensee calculates the patient received 16 Grays instead of the prescribed 38 Grays. The treatment is performed in three flushes. The patient receives 50% of the medication in the first flush and the remaining 50% in the second flush. The third flush is performed to ensure all the prescribed medication has been applied to the patient. In this case, the patient received the first flush but the second flush wouldn't go through the line. The licensee is investigating a problem with the three-way valve used in the treatment or potentially a crimp in the line which caused a blockage. Both the patient and prescribing physician are aware of this problem, and the other half of the patient's therapy is planned for a future time period. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-02-27
43998 | 0 | MID-ATLANTIC LLC |  |  |  |  | 2008-02-20 16:00 | 2008-02-21 09:20 | 2008-02-21 | VEHICLE TRANSPORTING SOIL DENSITY GAUGE INVOLVED IN ACCIDENT An employee for Mid-Atlantic LLC transporting a soil density gauge was involved in an accident at 1600 EST on Route 30 near Columbia, PA. The gauge is a CPN-MC1 with approximately 50mCuries Am-241/Be and 10mCuries Cs-137. The gauge was thrown from the vehicle during the accident. Local emergency response and hazmat team cordoned off the area and determined that there were no significant radiation levels. The RSO responded to the scene and noted that the gauge was still in its shipping container. The container had only minimal damage. When the container was opened, the gauge itself appeared to be undamaged. The RSO performed surveys and swipes confirming that there was no likely damage. The RSO has taken possession of the gauge and returned to the company offices. He plans on conducting a leak and functionality test to confirm the gauge was not impacted by the accident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2008-02-21
43997 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2008-02-20 11:00 | 2008-02-20 17:48 | 2008-02-20 | FITNESS FOR DUTY REPORT INVOLVING A CONTRACTOR SUPERVISOR A non-licensed contract employee supervisor tested positive for alcohol during a random fitness-for-duty test. The contractor's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the State of New York and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2008-02-20
43996 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-20 15:05 | 2008-02-20 16:30 | 2008-02-20 | RHR SERVICE WATER SYSTEM DECLARED INOPERABLE DUE TO INABILITY TO MEET FSAR REQUIREMENT "At 1505 EST, it was determined by an engineering analysis that a leak on a 3/4 inch vent line of the Residual Heat Removal Service Water (RHRSW) System common discharge line would prevent continuous operation of the system for 30 days as required by the Unit 2 FSAR. "Specifically, if the line were to completely shear, the resulting leak would have exceeded the capacity of the building sumps and over a prolonged period of operation would have resulted in the excessive water levels in the Reactor Building Torus room area. In order to mitigate the condition, supplemental pumping capacity would be needed in the building sumps or the RHRSW system would have to be temporarily secured. "The RHRSW system has been tagged out for repair of the line. The appropriate 8-hour RAS in Tech Spec has been entered. The line will be repaired and the system returned to service." The licensee identified the crack in the socket weld during a system walkdown and anticipates completion of repairs in approximately 6 hours. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 2140 EST ON 02/20/08 FROM BILL DUVALL TO S. SANDIN * * * At 2120 EST on 02/20/08 the RHR SW System was declared OPERABLE after completion of repairs and testing. The failure of the socket weld at 2E11-FV001 is preliminarily attributed to fatigue cracking caused by vibration. A root cause investigation is ongoing. A system walkdown did not identify any additional deficiencies. The licensee informed the NRC Resident Inspector. Notified R2DO(Robert Haag). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-02-20
43995 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-02-19 | 2008-02-20 10:11 | 2008-02-21 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL SHIPMENT MISSING The Commonwealth of Massachusetts confirmed receipt of the following email notification (no additional comments) made by the shipper (QSA Global) to both them and the NRC Operations Center at 0955 EST: "Please be advised that QSA Global, Inc. has been notified that a shipment of radioactive material bound for Hong Kong has been declared missing. Details follow: "Customer: ETS Testconsult Ltd. In Hong Kong, PRC "Carrier: Fed Ex "One 650L transport container containing (2) Ir-192 sources: (1) 2.9 TBq (77.5 Ci) and (1) 2.1 TBq (57.2 Ci) "It is believed that the material is not in the US as it had cleared the Anchorage, AK facility. A trace has been initiated, but due to the wide variation in time zones, not all intermediate locations in Asia have been checked as of this notification." The airway bill confirms the shipment arrived in Hong Kong on 2/18/08 at 4:54 pm local time. * * * UPDATE AT 1152 ON 2/20/2008 FROM MARIO IANNACCONE TO MARK ABRAMOVITZ * * * The shipment has been found at the Fed Ex facility in Newark, NJ. Notified FSME (Burgess), R1DO (Powell), and IP (Ramsey). * * * UPDATE FROM CHARLES ELLARS (QSA GLOBAL) TO HOWIE CROUCH ON 02/21/08 @ 1015 EST * * * In a correction to the previous update, FedEx informed the QSA Global broker that the shipment was NOT physically located in Newark, NJ. What was located in Newark was the FedEx container the freight was manifested on. It is now believed that the shipment was sent unmanifested to Hong Kong. QSA Global representatives in Hong Kong will be contacting the FedEx facility in Hong Kong to determine the status of the shipment. Additionally, QSA Global has contacted the FedEx RSO on the matter. * * * UPDATE FROM CHARLES ELLARS (QSA GLOBAL) TO JOE O'HARA ON 02/21/08 AT 1546 * * * The licensee provided the following information via email: "Please be advised that QSA Global, Inc. is in receipt of the serial number for the transport container that was declared missing yesterday from our broker. He [QSA] received the number from FedEx staff in Newark. This number is not on the paperwork they [FedEx] have and gives us confidence that they [FedEx] have visually inspected the package. The shipment is expected to be put on a plane tonight to start for its final destination in Hong Kong." Notified R1DO (Powell), FSME (Morell), and IP (Ramsey). * * * UPDATE FROM THE COMMONWEALTH OF MASSACHUSETTS TO HOWIE CROUCH ON 02/22/08 @ 0910 EST VIA FAX * * * "Package has been found. "QSA Global, Inc. submitted at approximately 1:10 p on February 21 that the package is no longer missing and has been physically located at FedEx's facility in Newark, NJ. QSA Global indicated at 3:47 p.m. on February 21 that FedEx staff in Newark, NJ have confirmed the identity of the package and will continue shipment of the package to its final destination in Hong Kong. "QSA Global, Inc. submitted that they will provide verification of receipt of the package when it is received by the customer in Hong Kong and will also provide a 30 day written report about this event." Notified R1DO (Powell) and FSME (Flannery). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-02-25
43994 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2007-12-19 16:00 | 2008-02-19 17:56 | 2008-02-19 | AGREEMENT STATE REPORT INVOLVING A DAMAGED CPN PORTABLE GAUGE The following report was received via email: "This is the initial notification for an incident that was reported to this Department on 12/19/2007 at approximately 4:00PM. At that time the Department was notified by telephone of an accident involving a CPN model MC1 DR portable gauge. The gauge is owned and operated by Kleinfelder, Inc., Colorado Radioactive Materials License Number 958-01. The incident occurred at a temporary jobsite just outside of Pueblo, Colorado. The individual notifying the Department was . . . the company RSO. The licensee reported that while at the jobsite the operator backed his vehicle over the gauge. At the time of the accident, the Cs-137 source was in its shielded position. The result of the accident was that the handle/source rod was snapped off above the gauge case approximately 6 inches from the top of the handle. The source remained in the shielded position and the body of the gauge remained intact with no apparent damage. The gauge was inspected by Department personnel on 02/04/2008 and was found to be in the condition previously described by the RSO. The department had directed the Licensee to leak test the gauge at the time the report was initially made and the results are pending. Once the leak test results are received by the Department the licensee will be directed to provide details on repair or disposal of the gauge. No other details are available at this time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2008-02-22
43993 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2008-02-18 19:30 | 2008-02-19 12:22 | 2008-02-19 | AGREEMENT STATE REPORT INVOLVING A VEHICLE ACCIDENT WHILE TRANSPORTING A RADIOGRAPHY CAMERA The following report was received via email from the State of Texas: "At 8:04 p.m., Radiation Control (RC) was contacted through the 24-hour Radiological Emergency Assistance telephone number by San Jacinto Emergency Management, reporting a car accident in San Jacinto County, on Highway 59, north of Houston, where a company was transporting a radioactive camera which was thrown from the truck onto the roadside. The Emergency Management representative reported that there was no leakage from the camera and that the driver sustained minor injuries. They did not have the company's name or any additional information on the radioactive source and was following instructions to make the initial notification to the State. The Emergency Management representative said they would call back with additional information. "The Emergency Management representative called back and relayed the following information: "Company/Licensee: National Inspection Services - out of Crowley, TX "The Emergency Management representative reported that the Cleveland Haz-Mat team was handling the incident, but did not have any contact information for them. "RC placed a call to the company contact, who informed RC that he was enroute from Sulphur, LA and would be on-site in 2 hours. He gave me the name and the telephone number of the Haz-Mat chief on-site. He also said another company supervisor was enroute from Lafayette, LA and would be there ~1 hour. "RC then called the Haz-Mat chief on-site, who reported that they surveyed with a Victoreen 6A series survey meter on the x100, x10 and x1 scales and got no readings of any radiation leakage. He said the camera was intact but out of its transport container. He informed RC that they were going to transport it back to the station. RC asked him for the manufacturer's information on the camera. The chief said he had it an ice cooler, with styrofoam overpack in the back of his truck and to call him back ~ 3 minutes for the information. "Meanwhile RC called the company representative from Lafayette, had the camera information: "Mfg.: SPEC 150 Ir-192 camera with ~ 30 Ci source. "He said that a Level II Radiographer was also in the company vehicle and was on the accident scene with the chief and could answer any questions. He also said the Texas Radiation Safety Officer (RSO) was contacted and would get with RC. He said the truck was a complete loss, the darkroom broke apart off of the truck and the camera was thrown out of the darkroom. He said the Level II Radiographer followed their O&E procedures for handling the recovery and securing of the camera. He said the camera would be picked up tonight by the company representative from Sulphur and would be sent off to SPEC in the morning for leak testing. I reminded him of the written notification as a follow-up to the telephone notification. He did not know off-hand their Texas Radioactive Materials License (RAML) number. "RC called the chief back right away, whose information concurred with the company representative's. RC then asked to speak with the Radiographer, who confirmed that he oversaw the camera recovery, examination and radiation surveying and concurred that the camera was neither damaged nor leaking. RC told him and the chief that in keeping with Increased Controls (IC), to have the Radiographer travel with the camera when it is transported back to the fire station, so that visual control of the camera is maintained by the licensee. RC also asked that the company representative from Sulphur, LA contact RC when they picked up the camera and the employee. "RC placed a call back to the other company representative from Lafayette and relayed the same information to him. He agreed to call me back as soon as he had secured them both. "RC followed up with a resolution summation call to San Jacinto Emergency Management. "I will await the camera secured-confirmation call from Joe. At 11:04 p.m. (CST) RC received the telephone call from the Haz-Mat employee that the camera and company employee were both picked up. "02/19/08, camera verification information from licensee @ 9:49 a.m.: "Mfg: SPEC Model: 150 Serial No.: 875 or 820 "Source: Ir-192 25 Ci Mfg.: SPEC Serial No.: OH2913 "Last leak test: 01/31/08" Texas Incident #: I-8484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2008-02-22
43992 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-18 01:20 | 2008-02-18 05:08 | 2008-03-20 | UNANALYZED CONDITION DUE TO #2 TURBINE BYPASS VALVE FAILURE "Unit two reduced power to 90% to perform monthly turbine testing surveillance on 2/18/08. All tests were completed satisfactorily with the exception of the main turbine #2 Bypass Valve (BPV). At 0120 hours, the #2 BPV stroked fully open per procedure, but the last 10% of travel to full open did not yield the expected response of BPV fast open from 90% to 100%. The fast acting solenoid did indicate expected state change to 'energized' at 90% valve open, but the BPV did not indicate fast open. Therefore the Main Turbine Bypass System has been declared inoperable and associated actions of Tech Spec 3.7.7 have been invoked. This spec requires compliance with LCO 3 .2.2 MINIMUM CRITICAL POWER RATIO (MCPR) limits for an inoperable main turbine bypass system as specified in the COLR (Core Operating Limit Report), are made applicable (within 2 hours) or reduce THERMAL POWER to <24% RTP within the following 4 hours. The MCPR limits were calculated by reactor engineering and installed in the process computer at 0347 hours. A decrease in reactor power was not required once the MCPR limit was installed. "The COLR (ref.: TRM Appendix A) states Unit Two can be operated with EITHER the End- of- Cycle Recirc Pump Trips (EOC-RPTs) out of service OR the Turbine Bypass Valves inoperable, but not both. The EOC-RPTs were already out of service as allowed for current conditions of the operating cycle. Upon discovery of the inoperable Bypass Valve, it was recognized that this placed Unit Two in an unanalyzed condition for fuel thermal limit. The shift crew took immediate actions to confirm the surveillance was current for EOC-RPTs and placed them in service per approved plant procedures. This was accomplished at 0315 hours, which returned the unit to an analyzed condition." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM J. ANDERSON TO P. SNYDER ON 3/20/08 AT 0943 * * * "During the surveillance testing of the main turbine bypass valves, one of the three main turbine bypass valves did not function as expected. The function of the main turbine bypass system was degraded but not lost. Upon discovery the required action statement (RAS) in Technical Specifications 3.7.7 and 3.2.2 were properly entered, and the required actions were taken within the allowed out of service time of two hours. Based on the initial review of the condition and the fact that the core operating limits report (COLR) described operation in the condition with the EOC-RPT out of service concurrent with loss of the main turbine bypass capability as an unanalyzed condition, a notification was made in accordance with the following reporting requirement: "'10 CFR 50.72 (b)(3)(ii)(B) The nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "The initial notification was a conservative action taken shortly after the condition was discovered. The condition was immediately identified during surveillance testing of the main turbine bypass valves, the required Technical Specifications RAS was entered and the actions completed within the allowed two hour time frame of 0120 - 0315 EST on 2/28/08. This prompt action prevented continued operation with EOC-RPT out of service and main turbine bypass inoperable and eliminated this potential to be in a condition where the design basis may not have been met. "A more detailed review was subsequently performed which determined that the minimum critical power ratio thermal limit for having EOC-RPT out of service and main turbine bypass inoperable as calculated during the reload analysis was 1.42. At the time of the event the actual MCPR at that point in core life was 1.57. Even though prompt actions were taken as required, there was actual margin to the calculated MCPR limit of 1.42. Had a design basis transient occurred, the MCPR Safety Limit would not have been exceeded. "Based on this information the determination has been made that the unit was not in an unanalyzed condition that significantly degraded plant safety. This notification serves to retract the previous event notification # 43992 made on 2/18/2008 at 0508 EST." The licensee notified the NRC Resident Inspector. | 0 | 89 | 0 | 0 | 89 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-02-18
43991 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-17 09:00 | 2008-02-17 08:31 | 2008-02-17 | PLANNED PHONE OUTAGE "The Emergency Notification System (ENS), Health Physics Network (HPN), site commercial telephone lines and Emergency Response Data System (ERDS) have been taken out of service for a planned maintenance outage. The outage is scheduled for a duration of six hours. The plant radio system, plant page system, and Prelude phone system are unaffected by the maintenance." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1534 ON 2/17/08 FROM NED DENNIN TO JEFF ROTTON * * * All phones are back in service and operable. The licensee will notify the NRC Resident Inspector. Notified R1DO (Dentel). | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-17
43990 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2008-02-15 19:02 | 2008-02-16 02:45 | 2008-04-12 | POTENTIAL INOPERABILITY OF EMERGENCY CORE COOLING SYSTEMS DUE TO AN UNALALYZED CONDITION "This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii) which states in part Any event or condition that results in (A) the condition of the nuclear power plant, including its principle safety barriers, being seriously degraded; or (B) the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety and 10 CFR 50.72(b)(3)(v) which states in part Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. This notification describes a licensee identification of a condition where the low pressure emergency core cooling systems (ECCS) may not have been able to perform their safety functions of removing residual heat and significantly degrades plant safety. The condition has been corrected. "At 2152 on 15 February 2008, while operating at 100% power, Nine Mile Point Unit 2 completed evaluating a 10 CFR 21 communication from General Electric on ECCS suction strainers, and concluded that the calculation on debris head loss was non conservative. The original design basis net positive suction head calculations assumed a suppression pool water level of 199.5 feet. Based upon the General Electric notification, at this suppression pool water level, the low pressure core spray and all three residual heat removal systems might not have been able to perform their safety functions. Further engineering evaluation determined that if the suppression pool level was [greater than or equal to] 200.3 feet then the suction strainers debris head loss could be met and the low pressure ECCS would be able to perform their safety functions. "At 1902 the control room operators took action to raise suppression pool water level while engineering completed their evaluation based on the expectation that suppression pool water would have to be raised. At 1910 on 15 February 2008, suppression pool water level was raised to 200.3 feet, which resulted in the low pressure core spray and residual heat removal systems being able to perform their safety function." The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 4/12/08 AT 1001 EDT FROM PETRELLI TO HUFFMAN * * * "After further review, this event notification report is being retracted based on the following: "The notification was initiated due to a 10 CFR 21 communication from General Electric on ECCS suction strainers, indicating that the calculation of suction strainer head loss was non-conservative. As a result, at the assumed suppression pool water level of 199.5 feet, adequate net positive suction head may not be available for the low-pressure ECCS pumps. Suppression pool water level was raised 9.8 inches, to 200.3 feet, which provided assurance that the low pressure ECCS pumps were capable of performing their specified safety functions. "Further evaluation by plant staff has determined that there are margins available in the suction strainer head loss calculations and in the design basis ECCS pump net positive suction head calculations that, when combined, exceed the increase in suction strainer debris head loss identified in the General Electric communication. Based on these available margins, there was adequate net positive suction head for the low pressure ECCS pumps at the originally assumed suppression pool water level of 199.5 feet. In addition, the as-found quantity of corrosion products and debris removed from the suppression pool during the current refueling outage was significantly less than the quantity assumed in the design basis suction strainer head loss calculations, indicating that additional analytical margin existed. Thus, the low pressure ECCS pumps were operable and capable of performing their specified safety functions without reliance on the 9.8 inches of water level added to the Suppression pool. Raising the suppression pool water level was a conservative action but was not necessary to maintain operability of the low pressure ECCS pumps. Therefore, this event is not reportable under either 10 CFR 50.72(b)(3)(ii) or 10 CFR 50.72(b)(3)(v)." The licensee notified the NRC Resident Inspector. R1DO (Conte) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2008-02-16
43989 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2008-02-14 16:04 | 2008-02-14 18:39 | 2008-02-14 | OFFSITE NOTIFICATION TO STATE OF NEW JERSEY "Notified [New Jersey Department Environmental Protection] NJDEP of a discharge of less than one gallon of a 15% sodium hypochlorite solution which contacted the soils of the state of New Jersey. The sodium hypochlorite was contained and has been cleaned up. "Notification will also be made to the Ocean County, New Jersey Board of Health." The cause of the spill was due to the deliveryman having trouble with the hose connection on the truck. The licensee notified the NRC Resident Inspector. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-02-14
43988 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-02-14 | 2008-02-14 15:36 | 2008-02-14 | AGREEMENT STATE REPORT - TRACTOR TRAILER SET OFF RADIATION ALARM "On 2/13/08 RHB was notified of a tractor trailer from the Turlock transfer station (municipal trash) that set off the radiation alarms at Covanta Energy. The truck was returned to the Turlock transfer station and arrangements were made to survey the vehicle to determine the reason for the alarm. On 2/14/08 an RHB inspector visited the transfer station to survey the truck to determine the radionuclide and quantity. Readings on the truck were stated to be 5 mr/hr at surface. Cesium 137 was identified. The cesium source measured 260 mr/hr using an Ion Chamber at about a foot. This would be approximately 85 mCi. The source was located and placed in properly shielded lead pig. The source will be stored at Thomas Gray and Associates and will be examined for serial numbers and to accurately determine the activity at a later date. The source appeared rusty and was very small and was similar to a brachytherapy source. Following the examination additional information will be provided." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-02-19
43987 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-02-14 02:07 | 2008-02-14 14:10 | 2008-02-14 | ALARM RECEIVED FROM UF6 RELEASE DETECTION SYSTEM "At 0207 CST, on 02-14-08 the Plant Shift Superintendent (PSS) was notified that an alarm was received in the C-333 Area Control Room for the C-333 Unit 5 Cell 8 UF6 Release Detection (PGLD) System. Operators responded to the local panel and verified the alarm was not due to a UF6 release, but local panel lights were flickering. Operators attempted to test the system and the system would not test fire. This PGLD System contains detectors that cover the C-333 Unit 5 Cell 8 cell housing roof and inter-cell housing and section 4 of the cell bypass housing. At the time of this alarm, C-333 Unit 5 Cell 8 and section 4 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell housing roof, inter-cell housing, and section 4 of the cell bypass housing are operable during steady state operations above atmospheric pressure. With the Unit 5 Cell 8 PGLD System inoperable, none of the required 3 heads in the cell housing roof and inter-cell housing were operable and only two of the required 3 heads in the cell bypass housing were operable. This PGLD System was declared inoperable. TSR LCOs 2.4.4.1.B.1 and 2.4.4.1.C.1 were entered and a continuous smoke watch was put in place within one hour. An investigation is ongoing to attempt to determine the cause of the failure. This event is being reported as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-02-14
43986 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2008-02-14 06:47 | 2008-02-14 11:56 | 2008-02-14 | TSC POWER OUTAGE "At 0647 hours, a fault at the Conowingo Hydroelectric station resulted in the loss of the 191-00 line to Peach Bottom Atomic Power Station (PBAPS). This condition resulted in a loss of the Station Blackout (SBO) power supply for PBAPS. The Technical Support Center (TSC) facility for PBAPS is powered from the SBO power supply. Therefore, power was lost to the TSC resulting in a degradation of the emergency assessment capability at PBAPS. "Efforts were promptly initiated to restore power to the TSC. Power was restored to the TSC at 0959 hours. The TSC Ventilation system restoration is in progress at this time. "The NRC resident has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-14
43985 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-02-13 18:50 | 2008-02-13 22:24 | 2008-02-13 | TECHNICAL SPECIFICATION 3.0.3 REQUIRED SHUTDOWN "With the 'B' Emergency Diesel Generator out of service for 7 day LCO, the 'A' [Centrifugal Charging Pump] (CCP) was declared inoperable due to associated room cooler tube leak. TS 3.0.3 was entered at 1820 hours with plant shutdown commencing at 1850 hours. At 1950 hours, the NRC granted a 19-hour Notice Of Enforcement Discretion (NOED) from the initial CCP 'A' inoperability time of 1420 hours until entry into TS 3.0.3 is required. Time when Wolf Creek will be required to enter TS 3.0.3 for the 'A' CCP inoperable due to room cooler leakage is now 0920 hours on 2/14/08. Power reduction was stopped at 1950 hours. Currently making preparations to return the unit to 100% power." Repairs to the 'A' CCP are expected to be complete before 2400 CST 2/13/08. The Licensee has notified the NRC Resident Inspector. | 88 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-02-13
43984 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2008-01-30 05:13 | 2008-02-13 17:28 | 2008-02-13 | LOSS OF ALL 81 OFFSITE SIRENS FOR APPROXIMATELY 80 MINUTES "On 1/30/08 at approximately 0617 Eastern Standard Time, while conducting a routine public warning siren interrogation test, the Harris Nuclear Plant (HNP) determined that the offsite emergency sirens were not capable of being activated. Initial investigations revealed that HNP lost power to the sirens due to a failure of the control module in the Uninterruptible Power Supply (UPS) of the siren system. At approximately 0644, an interrogation test of the system was completed and the sirens were verified to be operating normally. This event was initially viewed as not reportable. Subsequent investigation conducted between 1/31/08 and 2/13/08 revealed that other equipment supplied by the UPS was lost for between 70 and 80 minutes. As there is no direct monitoring capability for siren power supplies, it is reasonable to conclude that the sirens had been lost for a period of time between 70 and 80 minutes. This event should have been reported under 10 CFR 50.72(b)(3)(xiii) on 1/30/08. A completely new UPS system has been installed, and [the] siren systems are fully functional at this time." The UPS was replaced on 2/7/08. Its loss on 1/30/08 affected all 81 sirens. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-13
43983 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-02-13 09:30 | 2008-02-13 17:01 | 2008-02-13 | 24 HOUR REPORT CONCERNING IMPROPERLY ANALYZED CONDITION RELATED TO INTEGRATED SAFETY ANALYSIS "During a routine internal audit of the Uranium Recovery 3-inch Extraction System on February 13 at 0930, a Nuclear Criticality Safety (NCS) engineer observed several inconsistencies between the documented limits and controls in the Integrated Safety Analysis summary and those derived in the associated NCS evaluations. These anomalies were non-conservative in nature and included items such as the inside diameters of the columns, column wall thickness, and limits on the number of stainless steel columns in the system. In addition, the most recent NCS evaluation of the system employed a different analytical methodology than earlier evaluations. The evaluation employed the solid angle methodology, which had not been previously utilized to evaluate the 3-inch Extraction System. In past evaluations, the system was modeled using the law of substitution as a 7 x 2 array of 4-inch columns, mirrored in the x and y faces to form an infinite planar array. This change in methodology was incorrect. Based on these uncertainties in the safety basis, the engineer was unable to determine if double contingency was maintained. "An evaluation is currently being performed. "BWXT is making this 24-hour report in accordance with 10 CFR 70.61, Appendix A, (b)(1) - Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of § 70.61. "The operation was immediately shutdown by Nuclear Criticality Safety pending further investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-02-15
43982 | 0 | AREVA NP, INC. |  |  |  |  | 2007-12-27 | 2008-02-13 15:26 | 2008-02-13 | PART 21 INVOLVING POTENTIALLY DAMAGED FUEL ASSEMBLY SPACER SIDE PLATES The following information was received via facsimile: "Reportable Defect "(i) Name and address tithe individual informing the Commission: Gayle Elliott, 3315 Old Forest Road, Lynchburg, VA 24501 "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: Susquehanna Steam Electric Station, Units 1 and 2, potentially may contain ATRIUM- fuel assemblies with damaged spacer side plates. "(iii) Identification of the firm constructing the facility or supplying the basic component which falls to comply or contains a defect: AREVA NP Inc. (AREVA NP) supplied the ATRIUM-10 fuel assemblies to the Susquehanna units. The spacer side plates were damaged during recent re-channeling campaigns at the reactor site. "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such a defect or failure to comply: The damaged (missing) spacer side plates could impact the critical power performance of the fuel assemblies and the local power peaking distribution within the fuel assembly. "(v) The date on which the information of such a defect or failure to comply was obtained: This issue was determined to be a deviation on December 27, 2007. "(vi) In the case of a basic component which fails to comply, the number and the location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: The known defect has occurred at Susquehanna Unit 1. Based on the number of spacer pieces found, four (4) fuel assemblies could be damaged. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for this action; and the length of time that has been or will be taken to complete the action: AREVA NP recommended and PPL Implemented Operating Limit penalties for the potentially damaged fuel assemblies to protect the MCPR Safety Limit and LHGR SAFDL. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: See (vii) above." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2008-02-13
43981 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2008-02-12 19:45 | 2008-02-12 19:58 | 2008-02-12 | LOSS OF ENRICHED URANIUM HEXAFLUORIDE IN SAMPLE VIALS "Reason for Notification: During preparation of receipt transaction documentation (NRC 741) it was discovered that results of laboratory analysis for two [shipping] containers containing 16, P-10 sample tubes of UF6 [uranium hexafluoride] could not be located. Upon further investigation, neither the vials nor [shipping] containers could be located in the laboratory or on site. The vials contain a total of 128 Grams Uranium (6 grams Uranium 235) enriched to 4.95 wt%. This is approximately 409.4 micro-curies. It was determined that on 02/04/2008, 2 metal pails each containing (8) UF6 P-10 sample tubes were received in the Shipping & Receiving (S/R) department. One of the containers was dented upon receipt. S/R notified Health Physics to have the containers surveyed; they were cleared to the lab. However, the lab could not confirm that the P-10 vials containing uranium had been unloaded from the containers. One employee recalls surveying at least one of the containers, removing the labels and placing the containers out on Dock #11 for disposal. "Notification is being made based on [10 CFR 20.2201] (a) Telephone reports. (1) Each licensee shall report by telephone as follows: (i) Immediately after its occurrence becomes known to the licensee, any lost, stolen, or missing licensed material in an aggregate quantity equal to or greater than 1,000 times the quantity specified in Appendix C to Part 20 under such circumstances that it appears to the licensee that an exposure could result to persons in unrestricted areas. "Safety Basis: These vials were secured in containers authorized for shipment, which were surveyed by Health Physics upon receipt with no indication of leakage. It is postulated these [shipping] containers [with the sample vials still in the containers] have been inadvertently sent to either a waste landfill or scrap metal dealer. "Summary of Activity: - Columbia Fuel Site laboratories and waste processing facilities have been searched. - Interviews with affiliated staff have confirmed packages were staged for waste disposal. - Westinghouse notification to Richland County South Carolina, and South Carolina Department of Health and Environmental Control will follow immediately. - Event entered into Corrective Action Process (CAPS# 08-043-C004)" The licensee stated that the vials are approximately 2 inches long and between 1/8 to 1/4 inch in diameter. The vials were made of plastic with metal end caps. These vials are typically packed in Styrofoam in the shipping containers and their presence in the shipping containers may not be readily determined by just looking into the containers. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-02-14
43980 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-02-06 | 2008-02-12 16:15 | 2008-02-12 | AGREEMENT STATE REPORT - LOUISIANA - LEAKING CHECK SOURCE The State provided the following information via facsimile: "On February 8, 2008, Waste Management reported a leaking source. On February 7, 2008, an e-mail from Suntrac was opened. This e-mail contained information on two leak tests that were performed on two sealed radioactive check sources. One of the sealed sources had removable activity that was above 0.005 uCi. A 5 mCi source of Cs-137 had a removable activity of 0.0084 uCi. This source has been taken out of service. Waste Management will contact Suntrac for disposal of the source. The source was identified as 'Orange #2' and a serial number was not known." LA Report ID LA080003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-02-15
43979 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-02-09 09:00 | 2008-02-11 16:44 | 2008-05-15 | AGREEMENT STATE REPORT INVOLVING FAILURE OF HDR SOURCE TO RETRACT DURING TESTING The following information was provided by the State of Louisiana via email: "On February 9, 2008 at around 9:00 am, a Model Number AccuSource 1000, with a Model M-19 Iridium-192 High Dose Rate Brachytherapy Source failed to retract automatically while pre-operational acceptance testing was being performed at New York Radiation Oncology Associates, Queens, New York City, New York. The AccuSource 1000 is manufactured by Oncology Systems, Inc. Their license number is LA-11598-L01, amendment# - initial, with an expiration date of July 31, 2012. Agency Interest Number is 147139. "Model M-19 Iridium-192 source SSD number is LA-0612-S-115-S. The sources maximum quantity is 12 curies of Iridium-192. "Oncology Systems, Inc. according to their license condition number eight, states that 'The licensee shall report to the Department, immediately by phone and written notice with ten (10) days of occurrence of any irregularities pertaining to inability to retract the source to its fully shielded [position], and failure of any component or software (critical to safe operation of the device) to properly perform its intended function under the authority of this license.' "This was reported by SPEC who is the manufacturer of the Model M-19 Iridium-192 source. Talking with SPEC, it does not seem that Oncology Systems, Inc. have any personnel located at the 119 Teal Street, St. Rose, LA 70087 location." The source, which was extended approximately 10 cm when it stuck, was manually retracted. There was no reported personnel overexposures, however, the individual's film badges involved in returning the source to the shielded position have been sent out for processing. The City of NY Rad Health Department was notified by the State of Louisiana of this incident. * * * UPDATE PROVIDED AT 1512 EDT ON 05/15/08 FROM PENROD TO ROTTON * * * The State provided the following information via facsimile: "The incident involved an OSI AccuSource 1000, lr-192 HDR Brachytherapy unit. The unit malfunctioned, during an initial systems check, resulting in the source disconnecting from the source cable and the source capsule. The source strength was 8.62 curies. The source remained in a shielded position and was shipped back to Source Production & Equipment Company (SPEC), RAM License # LA- 2966-L01, the source manufacturer. No patients were involved and no overexposures were noted. This investigation is still in progress. One area of concern was noted. "On February 9, 2008, an Oncology Systems. Inc. (OSI) Field Engineer, was performing quality assurance testing on the AccuSource 1000, lr-192 Brachytherapy High Dose Rate Remote Afterloader (HDR), at the new York Radiology Associates, located in Queens, New York (RAM License # 91-3338-01). Field Engineer first performed a systems and software check on the HDR using a nonradioactivce source. All quality assurance tests passed during this time. He then loaded the HDR with the inner vault/spool cartridge assembly, which had an 8.62 Curie lr-192 sealed source. Field Engineer performed several tests on the HDR unit before running the source cable out, to insure that the inner vault was installed correctly to the outer vault (which is part of the HDR unit). The tests passed. He then extended the source out of vault when a force error sensor was triggered between the vault and the turret. When the force error was triggered this triggered an emergency retraction of the source. During the emergency retraction of the Ir-192 source, the vault door closed on the source tip resulting in a source disconnect and the loss of the top part of the source capsule. The source did retract to the inner vault where it was shielded and did not leave the AccuSource unit. The inner vault/spool cartridge, with the Ir-192 source was packaged in a Type A shipping container, provided by SPEC, held at the facility in a locked room until it could be shipped to SPEC. SPEC received the container on 2/26/2008. The source capsule tip loss was not known until the inner-vault was inspected by SPEC on 03/18/08. "Surface readings were 19mR/hr and 0.7mR/hr at one foot away. Survey readings of the package, before it was sent to SPEC, highest survey reading at one foot away from the package was 1.4mR/hr. This was taken at the bottom of the package. The highest reading taken from its side at one foot away was 0.51 mR/hr, similar to the reading at SPEC. "Once the package was open, several wipes were performed by SPEC. Two areas above background were noted. The wipe from the tip of the cap/wire where the source capsule was missing (the lr-192 source would have direct contact with this piece) had a wipe count of 327cpm and back end of the cable had a wipe count of 101cpm. Background was 37cpm. Survey readings of the vault were done by SPEC and the department at the time of this investigation. Survey readings on the side of the vault were 200 mR/hr and 100 mR/hr at the end of the vault. The source was located in the inner vault, but the inner vault was not opened at the time of this inspection. The facility wanted the lr-192 source to decay before opening the inner vault. "The inner vault was disassembled by SPEC on 03/18/2008. They found the bare lr-192 pellet in the straight exit channel of the front vault slug. The source capsule was not in the inner vault. The shipping package was re-surveyed and the capsule was not found. SPEC immediately notified the department and OSI. Wipe tests of the inside of the vault was performed by SPEC. The highest reading was taken from the center vault slug which was 33,000 nanoCuries. OSI field Engineer was going to the New York Facility during the week of 04/15/2008 to do a survey of the AccuSource and the therapy room to see if the missing capsule can be located. The results have not been received by the department as of 04/23/2008. "OSI states that the force error could have been triggered by many reasons and that the cause is unknown. The source became 'stuck' due to the vault door closing partially on the capsule. OSI is in the process of making design and software changes to prevent this problem from occurring in the future." Notified R4DO (Powers) and FSME EO (Tadessee). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-02-14
43978 | 0 | SCI ENGINEERING INC |  |  |  |  | 2008-02-11 14:30 | 2008-02-11 16:41 | 2008-02-11 | DAMAGED MOISTURE DENSITY GAUGE At approximately 1430 CST, a moisture density gauge was damaged when it was run over by construction equipment at the Riverport 7 construction site, near the cross roads of Riverport Drive and Riverport Lane, in Maryland Heights, Saint Louis County, MO. Make: Humboldt; Model: 5001; Serial Number: 1654C; Source: 10 millicuries Cs-137 and 40 millicuries Am-241:Be. Consultants, RM Wester, have been contacted, and are in the process of taking surveys and taking possession of the gauge. There does not appear to be any damage to the source. The source is believed to be retracted and shielded. The rod on the top of the gauge was broken, and the source can not be readily moved in the normal manner. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2008-02-11
43977 | 0 | USAF SURGEON GENERAL |  |  |  |  | 2008-02-11 07:48 | 2008-02-11 08:15 | 2008-02-11 | POTENTIALLY LOST IMPROVED CHEMICAL AGENT MONITOR The Radiation Protection Office of the U.S. Air Force Surgeon General was informed this morning that an improved chemical agent detector was lost at the Moody AFB in Georgia. The device is identified as a DuPont-Merck, model #NER004R, serial number 18465. The device contains 15 milliCuries Ni-63. It is also identified as a SSDR NR-1129-D-103-S. The permit number GA-00653-01/00AFP docket number 030-00653. The device was in the custody of the 820th Security Forces Group Commander and appears that the equipment was misplaced following a training exercise that was conducted on base. The USAF is investigating by conducting a search of all the gear associated with the exercise, and does not believe the device is in the custody of the general public. Licensee is going to contact Rachel Browder in Region IV. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-02-11
43976 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2008-02-10 22:07 | 2008-02-11 01:48 | 2008-02-13 | MANUAL REACTOR SCRAM DUE TO INCREASING REACTOR VESSEL LEVEL "On February 10, 2008, at approximately 2207 hours CST, the 'B' Reactor Recirculation pump tripped from fast speed to off. The resultant reactor pressure vessel level swell resulted in reactor pressure vessel level being greater than 48 inches and rising. Per Clinton Power Station operating procedures, the 'A' Reactor Operator placed the mode switch to the 'shutdown' position initiating a manual reactor scram. All control rods inserted [fully]. CPS is currently stable in Mode 3." Decay heat is being removed to the main condenser via the turbine bypass valves. Reactor level is being maintained using the motor driven reactor feedpump. No SRVs lifted during the transient. Licensee is in progress of restoring the electrical plant to a normal shutdown lineup. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2226 ON 2/13/08 FROM M. EVANS TO P. SNYDER * * * "After further analysis of the scram, it was determined that an automatic level 8, high reactor water level, scram occurred approximately one second prior to the reactor operator placing the mode switch to the 'shutdown' position." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-02-11
43975 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-02-02 09:00 | 2008-02-09 22:23 | 2008-02-09 | AGREEMENT STATE REPORT INVOLVING FAILURE OF RADIOGRAPHY CAMERA TO LOCK SOURCE IN THE SHIELDED POSITION The following information was received via email: "On Saturday, February 2, 2008, at approximately 9:00 A.M., a CONAM radiographer was performing radiography at Conoco Phillips in Signal Hill, CA, when he found he was unable to lock the device after retracting the source to the fully shielded position. The source was fully shielded throughout the incident, and remained under the constant surveillance of the radiographer. The Assistant RSO arrived on site at approximately 10:00 am, determined there was dirt in the locking [pin] that prevented it from popping up. He cleaned the dirt, and the locking [pin] engaged, locking the source in place. The device was transported back to the licensee's laboratory, tagged as out of service, and will be sent to INC for inspection and maintenance. The device involved is an INC IR 100 camera (S/N 4160), containing 80 Ci of Ir-192. There were no significant exposures from this event. RHB will follow up with the licensee to determine the root cause of the event, and any necessary corrective actions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-02-13
43974 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-02-09 13:20 | 2008-02-09 19:00 | 2008-02-09 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) REMOVED FROM SERVICE FOR SCHEDULED MAINTENANCE "On 02/09/08 at 05:20 CST, the Wolf Creek Nuclear Plant Information System (NPIS) was removed from service for a planned electrical bus maintenance, which results in the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) being inoperable. At 13:20 CST the maintenance exceed 8 hours as determined by WCNOC for meeting this reporting criteria. "Wolf Creek Nuclear Operating Corporation is making this ENS notification pursuant to the criteria of 10 CFR 50.72(b)(3)(x)(xiii). There is no other loss of emergency assessment capability concurrent with the removal of the NPIS from service. Plant personnel entered the appropriate Off-Normal procedure and have obtained local readings for the equipment that is normally monitored by SPDS and NPIS during the planned maintenance. "Nuclear Plant Information System was returned to service on 02/09/08 at 17:52 CST. "The Senior NRC Resident has been briefed on this evolution and the planned return to service of the system." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-09
43973 | -1 | NUTHERM INTERNATIONAL, INC |  |  |  |  | 2008-02-09 | 2008-02-09 09:11 | 2008-04-09 | PART 21 NOTIFICATION - POWER SUPPLY UNIT IS LIMITED AT ELEVATED TEMPERATURES "In accordance with 10CFR Part 21, Nutherm International, Inc. has opened an evaluation for a potential reportable condition. "Based on testing results of a production unit of a Nutherm Power Supply, part number 55320, the unit may not perform at elevated temperatures (at or above 120 °F) at its rated nameplate output rating of 20 Amps indefinitely. Preliminary reviews indicate that at ambient air temperatures of 120 °F or greater, the rectifier employed in the design may be limited to output currents of 15 Amps or less. "There have been no reports from customers concerning failures of these units as a direct result of this issue. If a reportable condition exists TVA (Browns Ferry) and Exelon (Quad Cities, Dresden, Peach Bottom) will be contacted." * * * RETRACTED ON 04/09/2008 AT 1835 EDT BY LEONARD HINSON TO FANGIE JONES * * * The reporting organization provided the following information via facsimile: "Nutherm has completed its investigation and concluded that all units supplied to customers meet the requirements of the Nutherm environmental qualification reports. Review of the qualification reports for these units indicates that the units were to operate at a maximum of 15.1 Amperes at temperatures up to 120°F. Some of the qualification reports also require that the units operate up to 15.1 Amperes at 160°F for 15 minutes. The results of our investigation indicate that the units supplied will meet the operating and accident requirements as stated in the qualification reports. "Based on the results of this investigation, Nutherm International, Inc. has concluded that a reportable condition does not exist." Notified R1DO (Richard Conte), R2DO (Randy Musser), R3DO (Anne Marie Stone), NRR Part 21 Group ( by email: Vern Hodge and John Thorp), and NRO (Omid Tabatabai). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21 |  |  |  | 0 | 2008-02-09
43972 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2008-02-08 18:12 | 2008-02-08 19:59 | 2008-02-08 | CONTROL ROD POSITION DEVIATION "While withdrawing shutdown bank rods in preparation for a North Anna Unit 2 startup, a Rod Control system Urgent Failure alarm was received in the main control room. Further investigation revealed group step counters for Shutdown Bank 'A' deviated by 3 steps from demand. TRM 3.1.3 was entered and the Reactor Trip breakers were opened within the 15 minute requirement." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-02-08
43971 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-02-08 14:02 | 2008-02-08 14:02 | 2008-02-08 | PH MONITORING PROBE EFFLUENT BYPASSES THE WASTE HOLDUP POND "As part of the on going investigation of the final holdup pond (NRC Notification #43958), McGuire has identified a discharge path from the pH monitoring and adjustment system that has existed since plant startup. This discharge path has been secured. The North Carolina Department of Environmental and Natural Resources will be notified." The effluent from the pH monitoring probe had been routed to a pit which drains into the river i.e. bypassing the holdup pond. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-02-08
43970 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-08-09 | 2008-02-07 19:47 | 2008-02-07 | AGREEMENT STATE - LEAKING GENERAL LICENSED SOURCE FROM A GAS CHROMATOGRAPH The State provided the following information via email: "On August 9, 2007, a dry smear of an ECD at UC Berkeley indicated a gross count rate of 5171 cpm. It was determined that this count rate indicated an activity of 0.03 uCi of Nickel-63. The ECD was returned to Varian on August 21, 2007, who determined that the leakage was less than the reportable limit of 0.005 uCi. Varian returned the ECD with the original Nickel-63 foil to UC Berkeley on August 28, 2007. "On October 16, 2007, the same 15 mCi Nickel-63 foil in the same Electron Capture Detector (ECD) in the Varian gas chromatograph was again found to be leaking. The activity of the leakage was determined to be 0.06 uCi. On October 17, 2007, the use of the gas chromatograph was immediately suspended, and a follow-up survey found that the contamination was limited to the top of the ECD, the exhaust funnel and a section of the exhaust tubing. On October 19, 2007, Varian representatives removed the ECD and transported it to their facility for analysis and repair. No adverse health effects resulted from this incident. UC Berkeley notified the RHB [Radiologic Health Branch] of this matter on November 9, 2007." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-02-12
43969 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-02-07 02:30 | 2008-02-07 08:16 | 2008-02-07 | INJURED CARPENTER TRANSPORTED TO APPLING COUNTY HOSPITAL "At 0230 EST an injured contract worker who was potentially contaminated was transported by ambulance to an offsite medical facility. The contract employee fell approximately 15 feet from a scaffold in the Unit 1 condenser bay. Unit 1 is presently shutdown (Mode 5) for a refueling outage. The worker was placed on a stretcher for transport and was partially frisked prior to release. However, due to concerns for a potential back injury, the worker was not removed from the stretcher for a back survey and was transported, with HP escort, as a contaminated person. After arriving at the hospital, a complete survey was performed and the worker was found to be free of contamination." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2008-02-07
43968 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-07 03:40 | 2008-02-07 05:16 | 2008-02-07 | OSC HVAC SYSTEM DID NOT START AS REQUIRED "In preparation for scheduled Motor Control Center (MCC) cleaning activities, the Health Physics normal HVAC system had to be shutdown and the Health Physics emergency HVAC was to be started while the MCC that supplies power to the normal HVAC would be out of service. When the emergency HVAC system was started per the system operating procedure (34S0-Z41-006-0), the air handling unit (1Z41-B100) started, but neither compressor units (1Z41-B101) started. Maintenance has been notified and is currently working to restore the system to operable status. "This event is reportable per 10CFR50,72 (b)(3)(xiii) as described in NUREG-1022, rev. 2 as an emergency facility (Plant Hatch Operational Support Center) is affected with the Health Physics emergency HVAC out of service. "Update: maintenance cleaned electrical contactors and have both compressors running at 0436 hours." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-07
43967 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-02-06 19:20 | 2008-02-06 20:19 | 2008-02-06 | TRAIN "A" 250 VDC CABLE PASSES THROUGH TRAIN "B" SWITCHGEAR ROOM "On February 6, 2008 at 1920 hours, Cook Nuclear Plant Engineering personnel identified an unanalyzed condition that has the potential to degrade plant safety. Specifically, a cable routing error in the original design for safety related Train 'A' 250 VDC was discovered. A short section of Train 'A' 250 VDC was found to pass through the Train 'B' 4kV switchgear room. This routing was discovered to exist in both units. The routing of the cabling presents the possibility that a fire could disable the remote control to both 4kV switchgear trains. "Local inspection identified no additional or supplementary fire barrier such as fire retardant wrapping. "Compensatory measures (fire watch) have been established. "In accordance with 10 CFR 50.72(b)(3)(ii) this condition is reportable as a condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2008-02-06
43966 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2008-02-06 | 2008-02-06 14:58 | 2008-02-06 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE GREATER THAN 25 REM The 4Q07 dosimetry badge reading results indicated an exposure of 261,067 mrem shallow dose, beta, probably from P-32. It is believed that this reading may be a result of leaving a contaminated glove in a lab coat pocket following work, and then placing the badge in the same pocket, and the two remaining together for a period of over a month. The worker has been withdrawn from all radiation work. An investigation is in progress. "02/06/08 - Radiation Safety Officer [REDACTED] of OHSU (License #OR-90731) notified [OREGON PUBLIC HEALTH] at the Agency that while reviewing dosimetry reports from Global Dosimetry Co., he discovered one user who had a 261,067 mrem shallow dose. [OREGON PUBLIC HEALTH] contacted [RSO] regarding the high dose and found that the dose was reported on a whole body badge for 4Q07. Further, it was found through this discussion that the isotope was P-32 and the user told [RSO] that he placed a contaminated glove in the pocket of his lab jacket and later placed his whole-body badge in the pocket with the glove. This was done approximately after 1 month into 4Q07 and the dosimetry and jacket were not used for 2 months. Unknown dose to the user during the first month from the glove. The glove was checked when found in the pocket and found to have 1100cpm (3400dpm) at that time. The user has been suspended from using radioactive material until an investigation (both OHSU and State Radiation Protection Services) can be performed and results determined. [RSO] is writing a preliminary report to be sent to [OREGON PUBLIC HEALTH] and [OREGON PUBLIC HEALTH] this afternoon or tomorrow. "02/06/08: SA-300 consulted, potential dose exceeds 250 rem shallow dose level. Notified NRC Operations Center by phone per significant reportable event requirements at 1458 EST (11:58 PST) and received Event number 43966. Relayed preliminary information as acquired so far, will follow with fax of this information as well. Licensee to issue preliminary investigative report sometime this afternoon or early tomorrow." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2008-02-11
43965 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-02-06 | 2008-02-06 13:09 | 2008-02-07 | AGREEMENT STATE REPORT - EXTREMITY OVEREXPOSURE TO TWO INDIVIDUALS "Anazao Health contacted [the Florida Bureau of Radiation Control] Licensing and Materials Office by fax concerning an over exposure to two individuals on 28 January 2008. Initial determination was on 27 December 2008. During routine facility audit on 6 February 2008 inspector found documentation concerning over exposure. No verbal communication was sent by Anazao Health to state officials. One individual received 105.3 [REM] to right extremity TLD finger ring, and 82.3 [REM] to his left extremity TLD finger ring. Both are shallow dose equivalent for calendar year 2007. Second individual received 53.186 [REM] to right extremity TLD finger ring, and 80.066 [REM] to his left extremity TLD finger ring. Florida is investigating." Florida Incident number FL08-018 * * * UPDATE AT 1423 EST ON 02/07/08 FROM STEVE FURNACE TO S. SANDIN * * * The following information was received as an update via email: "Anazao Health compounds radiopharmaceutical drugs. The company makes capsules of concentrated doses normally one quarter the size of standard capsules. The company primarily accomplishes these tasks by hand. "Both employees worked with I-131 liquid in the preparation of nuclear medicine capsules. The I-131 stock contained up to 3 Curies and the individuals removed stock liquid into other vials for diagnostic or therapy capsule production. Operations were conducted within a fume hood. A buffer solution was added to vials in order to dilute the I-131 to required activity levels. The individuals removed liquid from these vials to make capsules. "The individuals stood outside the flume hood behind lead shielding, while the forearms and hands were placed inside the fume hood in order to manually work with I-131 liquid vials and to prepare capsules of required activity. Employees wore double latex gloves, plastic sleeves and a disposable lab coat. "Manually working with significant amounts of I-131 in the preparation of diagnostic and therapy capsules from liquid inside a fume hood caused both employees extremity finger rings to exceed State of Florida limits. Syringe shields were not used by the individual when extracting liquid I-131 from vials. There are no written procedures for this operation for the individual to follow. No remote tools were used during the preparation process. "Florida is investigation this incident." Notified R1DO (Cahill) and FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-02-11
43964 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2008-02-06 11:33 | 2008-02-06 12:56 | 2008-02-09 | FLOOD WATCH DUE TO SNOW MELT AND HEAVY RAIN "On February 6, 2008 at 1119 hours, Clinton Lake level reached 694 feet 0 inches (mean sea level). Normal lake level is 690 feet 0 inches. Per Clinton Power Station (CPS) procedure 4303.02, 'Abnormal Lake Level,' the CPS Main Dam - Emergency Action Plan requires that a 'Flood Watch' be declared. This resulted in a notification to the DeWitt County Sheriff's Department that occurred at 1133 hours. Lake level continues to slowly rise due to the melting snow and heavy rains received in the area for the past several days. Expected peak is approximately 694 feet 6 inches. Mitigating measures are currently being instituted as a precautionary measure in the screen house, per CPS procedures. "The NRC Resident has been notified." High lake level only affects the plant intake structure. * * * UPDATE AT 1248 EST ON 02/09/08 FROM DALE SHELTON TO S. SANDIN * * * "On February 8, 2008 at 1655 hours, Clinton Lake level reached 693 ft-0 inches (mean sea level). Clinton Power Station (CPS) Procedure 4303.02, 'Abnormal Lake Level', and the CPS Main Dam - Emergency Action Plan allow termination of the 'Flood Watch.' This resulted in a notification to the DeWitt County Sheriff's Department that occurred on February 8, 2008 at 2043 hours when the Offnormal procedure was exited. Maximum lake level observed was 694 ft-4 inches (mean sea level). Lake level is currently 692 ft-6 inches (mean sea level) and lowering. Inspections have identified no damage due to the heavy rainfall or associated elevated lake level." The licensee informed the NRC Resident Inspector. Notified R3DO (Tom Kozak). | 27 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-02-06
43963 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-05 18:45 | 2008-02-05 21:07 | 2008-02-05 | IRRADIATED FUEL MOVEMENT PERFORMED WITH A REQUIRED ACCIDENT MITIGATION/RADIATION RELEASE SYSTEM BYPASSED "On February 5, 2008 EST at 1845 hours it was discovered that irradiated fuel moves had been performed during the previous shift with both Unit 1 and Unit 2 refuel floor high exhaust radiation monitors bypassed. The condition affected both Susquehanna Units. The radiation monitors are required to be operable for conditions noted in footnotes (a) and (b) in Technical Specification Tables 3.3.6.2-1 and 3.3.7.1-1 (i.e. operations with a potential for draining the reactor vessel, and during CORE ALTERATIONS and during movement of irradiated fuel assemblies in the secondary containment). The function of these instruments is to initiate systems that limit fission product release during and following certain postulated fuel handling accidents and to minimize the consequences of radioactive material in the control room environment. "No movement of irradiated fuel assemblies was in progress when the issue was discovered. The event has been determined to be reportable within 8 hours under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D)." The radiation monitors were bypassed on 1/31/08, as allowed, during a fuel pool activity NOT involving fuel movement. Approximately one hour of fuel movement occurred during the time the radiation monitors were bypassed. The oncoming shift manager identified the discrepancy during the shift turnover prior to assuming the shift. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2008-02-05
43962 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2008-02-05 16:43 | 2008-02-05 19:20 | 2008-02-05 | SAFEGUARDS DEGRADATION DUE TO WEATHER CONDITIONS The licensee reported adverse weather conditions including reports of a possible tornado in the county. The licensee took actions that resulted in a vulnerability in the safeguards system for which compensatory measures were not employed. At 1747 CST, after weather conditions improved, normal safeguards systems were re-established. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional information. The reduction in power on Unit 1 was in accordance to a transmission system operations request due to local grid conditions. Offsite power to the site is normal. | 26 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-02-05
43961 | -1 | BOSTON VA HOSPITAL |  |  |  |  | 2008-02-04 17:45 | 2008-02-05 15:39 | 2008-03-06 | POTENTIAL OVER-EXPOSURE OF WORKER WHO OPERATES A FLUOROSCOPY MACHINE Radiation Safety Officer of Boston VA Hospital made a 24-hour report that that a worker who operates a fluoroscopy machine, which produces x-rays from an accelerator and is used in cardiology, may have received exposure greater than allowed limits. The worker's radiation badge is normally read monthly, with a typical exposure of 80-200 mrem. However, his badge from July 2007 was not read until December 2007. Landauer read the badge on December 23, 2007, and reported a reading of 5,700 mrem, which they reported by letter dated January 23, 2008, to the Radiation Safety Officer, who received the information February 5, 2008. An investigation has commenced to determine whether some of the badge reading may have been when the worker was not wearing the badge, or due to other sources. * * * RETRACTION FROM T. HUSTON TO P. SNYDER ON 3/6/08 AT 1510 * * * This report is retracted based on the fact that "the reported exposure was to a dosimeter and not to an individual. In addition, the exposure did not involve byproduct materials." Notified R3DO (P. Pelke), R1DO (J. Caruso), and FSME (S. Wastler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | MA | HOS |  | 20.2202(b)(1) |  |  |  | 0 | 2008-02-05
43960 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-01-31 | 2008-02-04 16:03 | 2008-02-04 | AGREEMENT STATE REPORT - MEDICAL EVENT RADIATION TREATMENT NOT ADMINISTERED PER INTENTION The following report was made by e-mail: "In Radiation Oncology, a treatment was ordered for an HDR cylinder gynecological treatment of 2 fractions of 600 cGy to 5 mm past the surface of the cylinder. The treatment form was most likely filled out by a resident and was signed by both the resident and the attending radiation oncologist as stated by Environmental Health & Safety staff. When the radiation oncologist typed the official written directive into the IMPAC system, (Information for Management, Planning, Analysis and Coordination System), her intention was to treat 2 fractions of 600 cGy to the surface of the cylinder. The treatment was planned according to the written form to 5 mm past the surface of the cylinder. This plan was checked and signed off by the treating physician and was the treatment given to the patient. The radiation oncologist states that there should be no medical impact to the patient, as prescription to 5 mm past the surface of the cylinder is also an acceptable and standard treatment. The radiation oncologist has changed the prescription in IMPAC to reflect the dose that was given. The treating physician has notified both the referring physician and the patient." A 'medical event' indicates potential problems in a medical facility's use of radioactive materials. It does not result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-02-09
43959 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-04 11:59 | 2008-02-04 12:50 | 2008-02-25 | SAFEGUARD SYSTEM DEGRADATION WITH OFF-SITE NOTIFICATION Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have been employed. Off-site notification made to PA State Police. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION OF EVENT FROM DAVE BORGER TO JOE O'HARA AT 1735 ON 02/25/08 * * * The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R1DO (Doerflein). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 1 | 2008-02-04
43958 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-02-04 09:15 | 2008-02-04 11:44 | 2008-02-04 | OFFSITE NOTIFICATION TO THE NORTH CAROLINA DEPARTMENT OF ENVIRONMENT AND NATURAL RESOURCES "A leak in the final holdup pond has resulted in a release of treated wastewater to the environment. North Carolina Department of Environment and Natural Resources [has] been notified." The volume of the leak was approximately 100,000 gallons and the leak was to groundwater. The licensee has sampled the wastewater for tritium and determined that the activity was below reporting limits. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-02-04
43957 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-02-04 10:20 | 2008-02-04 11:18 | 2008-02-04 | EXTERNAL READINGS EXCEEDED ALLOWABLE DOSE RATE "On February 4, 2008 at approximately 10:20 EST, the Radiation Protection organization at Watts Bar Nuclear Plant (WBN), notified the Shift Manager (Licensed SRO) that a shipment of miscellaneous equipment exceeded the 200 mrem/hour dose rate specified in 10 CFR 71.47. The equipment was being received for use in an upcoming refueling outage. Radiation Protection surveyed the shipping container and obtained a reading of approximately 2000 mrem/hour. In accordance with 10 CFR 10.1906(d) the final delivery carrier has also been notified. This immediate notification is being made in accordance with the requirements of 10 CFR 20.1906(d)(2) and 10 CFR 71.47." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2008-02-04
43956 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-02-02 05:30 | 2008-02-02 07:44 | 2008-02-02 | MANUAL REACTOR TRIP DUE TO HIGH TURBINE VIBRATIONS "The DC Cook Unit 1 Reactor was manually tripped from 93% power due to high vibrations on main turbine bearings #5 and 6. "This event is reportable under 10CFR50.72(b)(2)(iv)(B), RPS actuation, as a four (4) hour report and under 10CFR50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. "Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 1 remains stable in Mode 3 while conducting the post Trip Review. No radioactive release is in progress as a result of this event. "The DC Cook Resident NRC Inspector was notified 02/02/08 at approximately 0535 EST. "The electrical grid is stable and Unit 1 is being supplied by offsite power. Unit 2 is not affected. All control rods fully inserted. Decay heat is being removed via steam dumps to the main condenser." | 0 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-02-02
43955 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2008-02-01 | 2008-02-01 19:20 | 2008-02-11 | AGREEMENT STATE REPORT - DEPLETED CESIUM-131 SEEDS LOST FROM DAMAGED PACKAGE DURING SHIPMENT The State provided the following information via email: "The Licensee reported by phone that at 2:30 PST today a package of returned and depleted implant seeds containing Cs-131 with a 9.7 day half-life was found damaged upon receipt with some of the contents missing. The package was to have contained 15 seeds that were returned from a customer on the east coast. When the package arrived, the licensee upon receipt inspection noted the package had a hole in it that had been repaired with tape. The receipt inspection also detected higher than expected dose rates at slightly less than 1 mr/hr contact with the package. The package was taken to a controlled area suitable for bio-hazard work and opened by the RSO. The package was opened and discovered with loose seeds in the box. 11 seeds were recovered, 4 seeds are missing. An Isoray facility survey was performed between the receiving area and the controlled area where the package was opened. No additional seeds were located. The sender of the package is being contacted as well as the RSO for FedEx. Highest dose rate on contact with a single seed was 1 mr/hr. The seeds were reported to have aged seven half-lives as of this day and at 1/100th of original strength. The Licensee will update our office [the State of Washington] with additional information when it comes available." The State does not know who originated the shipment or the initial strength of the CS-131 before the seven half-life decay. Washington State Report Number: WA-08-007 * * * UPDATE FROM ARDEN SCROOGS TO BILL HUFFMAN ON 2/4/08 AT 1504 EST VIA E-MAIL * * * The shipment originated from Geisenger Health in Danville, PA, and was shipped by FedEx. The original strength of the seeds was nominally 4 to 5 millicuries each, or 14 to 20 for the four missing seeds. At seven half-lives, the strength would be approximately 1/100th of the original strength, or 40 to 50 microcuries. R4DO (Mike Shannon), FSME EO (Larry Camper), ILTAB (Matt Hahn), and R1DO (Christopher Cahill) informed. * * * UPDATE FROM ARDEN SCROOGS TO KARL DIEDERICH ON 2/11/08 AT 1134 EST VIA E-MAIL * * * "The receipt inspection detected higher than expected dose rates at ~1.7 mR/hr contact with the package. "Detailed Carrier Information from with delivery route and timeframe. Jan 29, 2008: 4:15 PM - Picked up in Montoursville, PA. 7:51 PM - left Montoursville, PA. 11:46PM - Arrived FedEx location in Newark, NJ. Jan 30, 2008: 8:38 AM - Departed FedEx location in Newark, NJ. 10:41AM - Arrived FedEx location in Memphis, TN. 3:36 PM - Departed FedEx location in Memphis, TN. 6:35 PM - At sort facility in Spokane, WA. 8:49 PM - At local FedEx facility in Spokane, WA. Jan 31, 2008: 9:52 AM - On FedEx vehicle for delivery Pasco, WA. 11:46AM - Delivered." R4DO (Dale Powers), FSME EO (Michelle Burgess), ILTAB (Jim Whitney), and R1DO (Glenn Dentel) informed. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2008-02-06
43954 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-02-01 13:00 | 2008-02-01 15:49 | 2008-02-01 | AGREEMENT STATE REPORT OF METAL THICKNESS GAUGE MALFUNCTION The Massachusetts Radiation Control Program (MRCP) reported that a licensee, Allegheny Rodney (metal foil manufacturer), informed the MRCP of a malfunction in a metal thickness measuring gauge. The process gauge is supplied by Integrated Industrial Systems and contains a 1000 milliCurie Am-241source (Serial #1225). The licensee stated that the gauge is not functioning for unknown reasons and a technician from Integrated Industrial Systems will be responding to investigate the problem. There is no evidence at this time of a missing or leaking source. MRCP intends to follow-up with the licensee early next week after the cause of the gauge malfunction has been determined. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-02-06
43953 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-01-31 14:06 | 2008-02-01 14:48 | 2008-02-01 | 24 HOUR REPORT OF RELEASE DETECTION SYSTEM FAILURE "At 1406 CST, on 01-31-08 the Plant Shift Superintendent (PSS) was notified that an alarm was received for the C-333 Unit 3 Cell 5 UF6 Release Detection (PGLD) System. Operators responded to the panel and verified the alarm was false but when they attempted to test the system it failed. Preliminary troubleshooting indicates that the cause of the alarm may have been a momentary loss of power. This PGLD System contains detectors that cover the C-333 Unit 3 Cell 5 cell housing roof and inter-cell housing. At the time of this alarm, C-333 Unit 3 Cell 5 was operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell housing roof and inter-cell housing are operable during steady state operations above atmospheric pressure. With the Unit 3 Cell 5 PGLD system inoperable, none of the required 3 heads in the cell housing roof and inter-cell housing were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.B.1 was entered and a continuous smoke watch was put in place within one hour. An investigation is ongoing to attempt to conclusively and accurately determine the cause of the alarm. "This event is being reported as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-02-01
43952 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-02-01 13:45 | 2008-02-01 14:47 | 2008-02-01 | SCHEDULED LOSS OF ALL MAIN CONTROL ROOM ANNUNCIATORS TO SUPPORT PLANT MAINTENANCE "At 01:45 PM CST on 2/1/2008, the Main Control Room annunciator system has been removed from service to support maintenance at River Bend Station. The duration of the work is expected to be completed in less than one (1) hour. "During this time, other Main Control Room indications and alternate methods will be available to implement the Emergency Plan. Since the Main Control Room annunciator system will be unavailable, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii). "A follow-up notification will be made to the NRC after the Main Control Room annunciator system is returned to service. "The licensee notified the NRC Resident Inspector." The reactor is defueled and there are no major evolutions scheduled to occur during this period. * * * UPDATE PROVIDED BY TIM SCHENK TO JEFF ROTTON AT 1530 EST ON 02/01/08 * * * "Main Control Room annunciator system has been restored to service at 1528 EST." The licensee notified the NRC Resident Inspector. Notified the R4DO (Hay). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-02-01
43951 | 0 | MILLSTONE | 1 |  |  | [1] GE-3,[2] CE,[3] W-4-LP | 2008-02-01 10:24 | 2008-02-01 13:47 | 2008-02-01 | LOSS OF SPENT FUEL POOL COOLING Millstone Unit 1 is in a decommissioning status but still maintains spent fuel in the spent fuel pool. On January 30, 2008, the normal power to the Unit 1 spent fuel pool was lost due to a fault (overcurrent trip) in the "Trayer Switch" (an auto disconnect switch) in the electrical supply line to the spent fuel pool cooling bus. A backup diesel generator was started and was being used to power the spent fuel pool cooling system until the "Trayer Switch" was repaired. At approximately 0840 EST today (2/01/08), alarms were received indicating low decay heat pump low flow and low spent fuel pool cooling pump low flow and discharge pressure. Investigation revealed that the backup diesel generator was operating at a frequency of 57.5 Hz rather than the normal 60 Hz. The technical staff was unable to get the diesel generator to maintain the normal 60 Hz output frequency. The licensee elected to secure the spent fuel pool cooling system pumps at 1024 EST based on concerns that the pumps could be damaged if operated at under frequency for an extended period of time. Licensee technicians are currently engaged in repairing the diesel generator frequency controls and estimate that it could be returned to service this afternoon. The licensee has also ordered a temporary skid mounted diesel generator which should also arrive this afternoon. The repairs to the normal power source are not anticipated to be completed until Monday (2/04/08). The spent fuel pool temperature has increased 1 degree to 86 F in approximately 4 hours. The tech spec limit on spent fuel pool temperature is 150 F. The licensee states that other unit electrical systems powered off the diesel, such as lighting and rad monitors, continue to operate normally at the reduced output frequency of the diesel. One security tower has been slightly impacted but appropriate compensatory measures were implemented. A Millstone Unit 2/3 Resident Inspector has been notified. The licensee has attempted to contact the Regional Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW | [5 empty] | 0 | 2008-02-01
43950 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2008-01-31 12:30 | 2008-02-01 11:11 | 2008-02-01 | AGREEMENT STATE REPORT - EQUIPMENT SAFETY FAILURE "On Thursday, January 31, 2008 during a treatment of a patient an event occurred with the licensee's Leksell Gamma Knife Stereotactic teletherapy treatment unit (Model 24001 Type C). "The patient treatment plan called for three exposure fractions. The first fraction was initiated at 10:25 a.m., without incident. After the normal termination time of treatment, the couch retracted fully and the patient's head was withdrawn from the unit. However, the shielding doors on the unit did not close. An Authorized Medical Physicist (AMP) then entered the treatment room, walked behind the unit, and closed the shielding doors manually. The licensee estimates that the AMP received an exposure of no more than 0.0083 mrem while closing the shielding doors. The patient was removed from the treatment room and a radiation survey was conducted to verify that the shielding doors had closed completely. "Elekta was contacted (12:30 p.m. 01/31/08) and a service representative arrived and completed an evaluation of the Gamma Knife and could find no faults in any aspect of the Gamma Knife system operation. A decision was made by the Authorized User to complete the last two exposure factions. The remaining shots were successfully completed. "The patient did not receive a radiation dose deviating from the written directive from the shielding doors not closing. The licensee was in constant contact with DHFS throughout this incident. This event will be followed up by DHFS on the next scheduled inspection (02/19/08). "Event Report ID No WI-08-01 "License No.: 79-1281-01 "Event Type: HFS 157.13(17)(b)2.a - 'Equipment is disabled or thus to function as designed'" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2008-02-07
43949 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-02-01 04:45 | 2008-02-01 05:45 | 2008-02-01 | AUTOMATIC SCRAM AS A RESULT OF TURBINE TRIP "Unit 2 automatically scrammed [at] 0445 as a result of an RPS actuation due to a turbine trip. All rods inserted. The plant is stable. No ECCS or SRV actuation occurred. This report is made pursuant to 50.72(B)(iv)(B). An investigation into the cause is currently in progress. " Primary plant pressure is 900 psig. with the decay heat path to the condenser via turbine bypass valves. All safety related systems are operable, and the licensee is investigating a potential issue with the EHC system. The NRC Resident Inspector has been informed. The Commonwealth of Pennsylvania and local government agency will be informed. The licensee will issue a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-02-01
43948 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2008-01-31 15:44 | 2008-01-31 18:06 | 2008-01-31 | MANUAL REACTOR SCRAM IN RESPONSE TO TRIP OF BOTH REACTOR RECIRC PUMPS "At 1544 EST 01/31/2008, the reactor mode switch was taken to shutdown in response to the trip of both reactor recirc pumps. All control rods fully inserted into the core. The lowest reactor vessel water level reached was 157 inches. Reactor water level is being controlled in the normal band using CRD. "The cause of the reactor recirc pump trips are under investigation at this time. There was no maintenance or testing in progress that would explain the pump trips. "At the time of the scram all ECCS systems and Emergency Diesel Generators were operable with the exception of Division 1 RHR. Division 1 RHR Surveillance testing was in progress. Surveillance testing is complete. Division 1 RHR is available with administrative activities remaining before it will be declared operable. Isolations and actuations occurred as expected. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Any event that results in actuation of the reactor protection system (RPS) when the reactor is critical." Decay heat is being removed to the main condenser via the turbine bypass valves. The electric plant is a normal shutdown lineup. No SRVs lifted during the reactor scram. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2008-01-31
43947 | -1 | BRIDGEPORT HOSPITAL |  |  |  |  | 2008-01-30 | 2008-01-31 10:46 | 2008-03-13 | POTENTIAL INOPERABLE SAFETY FUNCTION "In regard to Part 21.21 Notification of failure to comply or existence of a defect and its evaluation, [the licensee notified] the NRC of a defect that was detected on the Varian, Mammosource unit, Gammamed Plus (M1), ID#H64E168. "The defect noted was the following: "A daily check is performed to verify when the source guide tube is disconnected from the unit head, the source will not extend. This test is performed as recommended on p. 73 of the ESTRO Booklet No.8, ' A Practical Guide to Quality Control of Brachytherapy Equipment'. Disconnecting the tube (i.e. the lock that connects the source guide tube to the turret of the Mammosource) the dummy wire or the source wire should have been prevented from extending out. If the disconnect is within 2 mm of being connected the wire does extend out. This was documented on a check film using the Mick PerinaDoc phantom. As recommended in the Varian GammaMed HDR User Manual, P. 6-20, Varian BrachTherapy service was called. "Notification: "Varian Corp. was notified of this problem on 1/30/08 and a service engineer will be sent to the site to adjust the light sensor that communicates whether the source guide tube is connected. We are continuing treatment with two independent physicists verifying before treatment that the source guide tube is connected properly and securely." * * * RETRACTION FROM WISHKO TO HUFFMAN VIA E-MAIL AT 1431 EDT ON 3/13/08 * * * "Verbal communication with an engineer from Varian Corporation stated that when the source guide tube is disconnected within 2 mm from the turret of the Mammosource, the source can extend. Since this is a design feature and accepted by Varian Corporation, I wish to withdraw my report of notification on a discovered defect." R1DO (Lorson) and FSME (Wastler) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21 |  |  |  | 0 | 2008-01-31
43946 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2008-01-30 18:40 | 2008-01-30 19:00 | 2008-01-30 | ALERT DUE TO MOISTURE CONTACT WITH A URANIUM DIOXIDE MIXTURE OF UNFAVORABLE GEOMETRY An uranium dioxide powder mixture was contained in a hopper of unfavorable geometry with moisture prevention criticality protection measures. After starting a process stream, moisture was unintentionally introduced into the hopper containing the uranium dioxide powder. At 1840 Global Nuclear Fuels declared an Alert condition onsite as a result of this introduction of moisture to the uranium dioxide powder. The process stream was secured which stopped the introduction of moisture. No criticality occurred. * * * UPDATE FROM S. MURRAY TO P. SNYDER AT 2110 ON 1/30/08 * * * The uranium dioxide powder in the hopper was successfully discharged into a hybrid container of favorable geometry. At 2107 the licensee exited the Alert condition. Notified R2DO (Bonser), NMSS (Weber, Mamish), IRD (Cruz), DHS (Haselton), FEMA (Sweetser), DOE (Smith), USDA (Timmons), HHS (Turner) and EPA (National Response Center) (Snowden). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | NC | FUE |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-01-30
43945 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-01-30 12:20 | 2008-01-30 17:52 | 2008-01-30 | AUXILIARY FEEDWATER PUMPS DECLARED INOPERABLE BASED ON POSTULATED MAIN FEEDWATER LINE BREAK SCENARIO "On 01/30/08, it was discovered that restrictor plates were not installed as required in the Unit 1 and Unit 2 interior doghouse floor drains. The restrictor plates are indicated as required on applicable flow diagrams. The purpose of the plates is to limit the amount of flow into the interior doghouse floor drains following a Main Feedwater (MFW) line break event in the doghouse. Without the restrictor plates installed, the amount of flow into the floor drains following a MFW line break could overwhelm the capability of the floor drain pump. Water could then flood into the AFW pump rooms and could render all three AFW pumps on the affected unit inoperable. Operations declared the 3 AFW pumps on both Units inoperable at 1220 today. TS 3.7.5.D states that with 3 AFW trains inoperable, LCO 3.0.3 and all other LCO required actions requiring Mode changes are suspended until on AFW train is restored to operable status. Both Units will remain at 100% power until repairs are complete. This condition does not prevent the AFW pumps from starting on an automatic or manual signal for any required plant events. "An investigation into how this condition occurred is underway. As a result of this discovery, all three AFW pumps on each unit have been declared inoperable. "Plant personnel are currently in the process of fabricating the required restrictor plates or blind flanges as necessary and installing them to conform to the drawing requirements. The restrictor plates/blind flanges are being installed and upon completion the affected AFW pumps will be considered operable." The licensee notified the NRC Resident Inspector. State and local government agencies will also be notified by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2008-01-30
43944 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2008-01-30 12:30 | 2008-01-30 13:22 | 2008-01-30 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE NOTIFICATION CAPABILITIES At 1230 EST, the licensee discovered that offsite notification capabilities were lost. Upon discovery, they declared a Notification Of Unusual Event (NOUE) under EAL 7.3.2. At the time of discovery, the licensee was in their adverse weather procedure due to winds exceeding 55 mph on site. The high winds caused a loss of electrical power to non-vital power block facilities, including the site PBX (Private Branch Exchange). The backup diesel generator for PBX power initially failed to start but was manually started at 1300 EST, and PBX functions were restored. No other vital equipment was adversely affected by the loss of non-vital power. The licensee will remain in the NOUE until normal power is restored to the power block. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM HARDING TO HUFFMAN AT 2017 EST ON 1/30/08 * * * The licensee terminated the Unusual Event at 2015 EST on 1/30/08 based on restoration of normal offsite power to the PBX. In addition, the backup diesel power supply to the PBX has been verified to be functional and available. The licensee has also stationed a spare backup diesel if needed. All phone lines have been tested and confirmed to be back in service with the exception to the RECS line (dedicated line to State and County Officials). Backup commercial lines to the State and County Officials are available. The licensee will be notifying the NRC Resident Inspector. R1DO (Perry), FEMA and DHS notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-01-30
43943 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2008-01-30 03:35 | 2008-01-30 12:20 | 2008-01-30 | MULTIPLE EMERGENCY SIRENS LOST POWER DUE TO SEVERE WEATHER "Due to severe weather (wind storm) in the area, a total of 8 of 78 sirens were reported out of service (loss of power) in Washington County, NE. An additional 6 sirens were running on their battery backup power supplies. The sirens have been returned to service. A large segment of the population was NOT affected." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-30
43942 | -1 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2008-01-29 14:41 | 2008-01-29 21:50 | 2008-03-27 | HIGH PRESSURE COOLANT INJECTION SYSTEM NOT AVAILABLE FOR SAFE SHUTDOWN CAPABILITY "The D/C power supply for the Unit 1 High Pressure Coolant Injection (HPCI) system instrumentation has failed resulting in the inability of HPCI to meet its requirement to support safely shutting down the reactor during a Station Blackout (Complete Loss of A/C Power) situation. The Emergency Core Cooling System (ECCS) function of HPCI is still available with the alternate A/C power supply." The licensee is actively troubleshooting the power supply. The HPCI unavailability places the licensee in a 14-day Limiting Condition for Operation action statement. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM D. SEMETER TO P. SNYDER ON 3/27/08 AT 1300 * * * "This is a retraction of the event notification made on 1/29/08 at 21:50 EST hours. This event (#43942) was initially reported as a safety system functional failure under the requirement of 10 CFR 50.72(b)(3)(v)(A). The notification stated that the D.C. power supply for the Unit 1 High Pressure Coolant Injection (HPCI) system instrumentation failed resulting in the inability of HPCI to meet its requirement to support safely shutting down the reactor during a Station Blackout (SBO) (Complete Loss of A/C Power) situation. The Emergency Core Cooling System (ECCS) function of HPCI is still available with the alternate A/C power supply. "A review of the station's current licensing basis determined that HPCI is not credited with a safety function during a Station Blackout (SBO) event. Operating procedures direct securing HPCI early in an SBO event to minimize the discharge rate on the Class 1E batteries. The Reactor Core Isolation Cooling (RCIC) system is credited with maintaining reactor inventory during a SBO event. HPCI remained capable of completing its safety function to inject coolant into the reactor pressure vessel during a loss of coolant accident (LOCA) concurrent with loss of offsite power (LOOP) event. The Division 2 automatic initiation logic was inoperable but the Division 4 automatic initiation logic was unaffected by the Division 2 instrument power supply failure. Division 2 instrument power is required for HPCI automatic flow control and would not have been initially available during a LOOP event. However, the Division 2 instrument power would have been restored when the 480 VAC load center is re-energized approximately 13 seconds into the event. The 13 second delay in HPCl injection is offset by existing margin in HPCI's capability to meet the Technical Specification response time of 60 seconds. "Therefore, a condition did not exist at the time of discovery that could have prevented the fulfillment of the HPCI safety function." The licensee notified the NRC Resident Inspector. Notified R1DO (Bellamy). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2008-01-29
43941 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2008-01-29 05:31 | 2008-01-29 06:30 | 2008-01-29 | MANUAL REACTOR TRIP TO REPAIR RCP "2B1" SEAL PACKAGE "St Lucie Plant, Unit 2, manually tripped the reactor at 0531 hrs. EST, as part of a controlled reactor plant shutdown, in response to an RCS leak rate of 0.28 gpm, indicated to be associated with the 2B1 Reactor Coolant Pump seal package. All systems functioned as expected, satisfactorily. All CEAs fully inserted. Decay Heat removal is with Steam Generators and Main Feedwater. This report is made pursuant to 10 CFR 50.72(b)(2)(iv)(B)." Unit 2 will cooldown to Mode 5 for repairs. The licensee informed the NRC Resident Inspector. * * * UPDATE FROM ALAN HALL TO HOWIE CROUCH @ 1218 EST ON 1/29/08 * * * "St. Lucie Plant, Unit 2, reported their manual reactor trip of 0531 hrs. EST, at 0630 hrs. EST, for an unidentified leak associated with the 2B1 RCP seal package (EN 43941). Subsequent investigation, reported to the STA [Shift Technical Advisor] at 1015 hrs. EST, determined that this leak constitutes an RCS Pressure Boundary Leak. This leak is at a pipe-to-flange weld on the outboard side of the first flanged coupling of the 2B1 RCP Upper Cavity Seal pressure sensing line. Investigation is in progress to determine the detailed configuration at the leak and root cause. There were NO ESFAS signals or actuations. Decay Heat Removal continues on Steam Generators, with MFW [Main Feedwater] and SBCS [Steam Bypass Control System]; Off-Site power continues [to be] available and stable; Unit 1 at 100% power with operations and conditions normal. This report is made pursuant to 10 CFR 50.72(b)(3)(ii)(A)." The licensee informed the NRC Resident Inspector of this update. Notified R2DO (Bonser). | 0 | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | DEGRADED CONDITION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2008-01-29
43940 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-01-28 18:43 | 2008-01-29 00:51 | 2008-03-17 | HIGH PRESSURE CORE INJECTION (HPCI) INOPERABLE "On 1/28/08 at 1843 CST, Browns Ferry Unit 1 was performing 1-SR-3.3.5.1.3(D) HPCI System Condensate Header Low Level Switch Calibration and Functional Test when 1-LS-73-56A failed to actuate. Per TS 3.3.5.1, 1-LS-73-56A is inoperable. 1-SR-3.3.5.1.3(D) defeats the logic relay normally actuated by 73-56A & B. This causes HPCI to be inoperable per TS 3.3.5.1.D if the relay is defeated for greater than 1 hour. Failure of the 73-56A switch prevented restoration of the relay within the 1 hour time frame. "This event is reportable under 10CFR 50.72(b)(3)(v)(B) 'any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to: Remove Residual Heat' and 10CFR 50.72(b)(3)(v)(D) 'any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to: mitigate the consequences of an accident.' "This event also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(v)(B) and 10CFR 50.73(a)(2)(v)(D). "The defeated relay was restored to normal and the HPCI system returned to operable status at 2330 CST on 1/28/08." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1359 EDT ON 3/17/08 FROM RASMUSSEN TO HUFFMAN * * * "On January 28, 2008, Browns Ferry Unit 1 entered an LCO to perform a planned maintenance activity, High Pressure Coolant Injection System Condensate Header Low Level Switch Calibration and Functional Test, 1-SR-3.5.5.1.3(D). During the calibration of 1-LS-073-0056A and 1-LS-073- 0056B, 1-LS-073-0056A was found inoperable. The removal of both level switches from service (and as a result the HPCI transfer on low condensate header level function) was a planned maintenance activity, performed in accordance with an approved procedure and in accordance with the plants TSs. During this time no condition was discovered that could have prevented HPCI from performing its intended function because 1-LS-073-056B was considered OPERABLE. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(B) or 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. R2DO(Lesser) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2008-01-29
43939 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2008-01-28 06:51 | 2008-01-28 15:53 | 2008-01-28 | AGREEMENT STATE NOTIFICATION - STOLEN MOISTURE/DENSITY GAUGE "At 0651 on January 28, 2008, the licensee contacted the State of California Warning Center /OES to report that a nuclear density gauge (CPN, model MC1, serial number MD40807529 - containing [10] milliCuries Cesium 137 and [50] milliCuries Americium 241:Beryllium) was stolen along with the company vehicle that the gauge was secured within (2005 Toyota Tacoma - CA license 7W04195). The gauge was inside the locked transport case. The transportation case was locked and secured to the bed of the vehicle with chains and two independent locks. The gauge handle was also locked. This was reported to the Palm Desert Police Department (T08028025). The last leak test was performed on December 17, 2007 and was negative for removable contamination." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2008-01-31
43938 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2008-01-28 12:00 | 2008-01-28 15:09 | 2008-01-28 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE "N.C. Radiation Protection Section was notified on 28 January 2008 by the RSO for ECS Carolinas, LLP Charlotte office that one of their portable moisture/density gauges (Humboldt Model 5001) was damaged at a construction site in Charlotte, NC. The gauge contains two sealed sources: (1) Cesium-137, 10 milliCuries (nominal) and (2) Americium-241:Beryllium, 50 milliCuries (nominal). Serial numbers for the gauge and the sources were not immediately available. "The RSO responded and performed confirmatory measurements on the device using a hand-held GM survey instrument. The gauge handle was detached from the source rod and index rod and the case has some minor damage. The index remained attached to the gauge and the source rod remained within the shield. The RSO's survey confirmed that the Cesium-137 source is still contained within the shield. The licensee also performed a survey of the area where the gauge was initially struck and readings were at background levels (approx. 0.05 mR/hr). The readings at one meter from the gauge were approx. 0.4 mR/hr (consistent with the TI [Transportation Index]) and at one foot were approx. 2-3 mR/hr. "The licensee has been in contact with the manufacturer and has received instructions on packaging and returning the device to Humboldt Scientific (Raleigh, NC). The device has been transported back to the licensee's storage facility and will be returned to Humboldt's Raleigh facility later this week." North Carolina has assigned Event Report ID No. NC-08-03. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2008-01-31
43937 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-01-15 16:21 | 2008-01-28 15:15 | 2008-01-28 | INADEQUATE INSPECTIONS ON THRU-WALL PIPING PENETRATION SLEEVES "The issue is associated with sleeved line penetrations thru walls [in the 300 Complex]. The documented periodic inspection was not adequate to verify the continued reliability and availability of the sleeve. In addition, the discussion in the supporting safety analysis was insufficient. "During the two (2) year review of the safely-related equipment (SRE) test, it was determined that the test could not be performed as written and that the test did not verify the continued reliability and availability of the sleeve. In addition, after a review of the discussion in the supporting safety analysis, the discussion was determined to be insufficient. "There were no actual safety consequences to workers, the public, or the environment. Although determined to be extremely remote because of the nature of the pipe and sleeve, the potential criticality consequences include a leak of uranium-bearing solution from the pipe and sleeve and into the wall. "The safety significance is determined to be low due to the following: - the solution lines and sleeves are compatible with the associated uranium-bearing solutions (stainless steel); - the sections of lines and sleeves thru the walls are straight pipe with no connections; and, - leaks have not been observed in straight pipe and sleeve sections. "Additional actions taken in response to the event: "The number and locations of the sleeved line penetrations are being investigated. The grout/caulk may be removed to facilitate inspections of the sleeves. Safety-related equipment (SRE) tests and safety analyses are being revised to better describe the accident sequence/barriers and periodic inspections." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-01-30
43936 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-01-27 15:17 | 2008-01-27 20:24 | 2008-02-07 | EMERGENCY RESPONSE DATA SYSTEM LINK TO NRC UNAVAILABLE "At 1517 [hrs. EST] on 1/27/08, it was determined [that] the Emergency Response Data System (ERDS) link to the NRC was unavailable from Unit 4. ERDS link remains unreliable at this time. "Notification is based on 'A major loss of emergency assessment capability' per 10CFR50.72(b)(3)(xiii), specifically a loss of the ability to supply ERDS data for greater than 30 minutes" The licensee will be notifying the NRC Resident Inspector. This is a recurring event. See Event Numbers 43877, 43902, and 43924. * * * UPDATE AT 1900 EST ON 02/07/08 FROM MARK JONES TO S. SANDIN * * * The licensee provided the following information as an update: "At 1517 on 1/27/2008 it was determined that the Emergency Response Data System (ERDS) link to the NRC was unavailable from Turkey Point Unit #4. An emergency notification based on 'A major loss of emergency assessment capability' per 10CFR50.72(b)(3)(xiii) was made at 2024 EST on 1/27/2008. Refer to EN#43936. "The Unit 4 Emergency Response Data System (ERDS) link to the NRC was returned to operable status at 1800 EST on 2/7/2008." The licensee informed the NRC Resident Inspector. Notified R2DO (Musser). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-27
43935 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-01-25 13:00 | 2008-01-25 18:42 | 2008-01-25 | TECHNICAL SUPPORT CENTER MAY BECOME UNINHABITABLE "At approximately 1300 hours Eastern Standard Time on Friday, January 25, 2008, the Cook Nuclear Plant (CNP) determined that under certain accident conditions, the Technical Support Center (TSC) may become uninhabitable due to the inability to switch to the emergency ventilation mode. "Compensatory measures exist to relocate TSC personnel to the unaffected unit's control room if necessary based upon results of procedurally required monitoring of TSC radiological conditions. "Parts are available and repairs are expected to be completed during the current shift. "This event is reportable as specified in NUREG 1022 as a loss of an emergency response facility in accordance with 10 CFR 50.72 (b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-25
43934 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-01-25 17:00 | 2008-01-25 17:23 | 2008-01-25 | STATEMENT FOR INQUIRIES BY MEDIA CONCERNING IMPOSED CIVIL PENALTY BWX Technologies, Inc. will issue the following statement for media inquiries into the NRC imposed civil penalties for an event that occurred at the facility in July, 2007: "On July 26, 2007, BWXT in Lynchburg, Va., reported an unusual event at its Mount Athos plant to the Nuclear Regulatory Commission (NRC). A vacuum cleaner containing uranium-bearing wastewater tipped over while being moved from one location to another. Fewer than 22 liters of wastewater spilled from the container; a negligible amount of uranium was present in the wastewater. "The incident did not result in a release of radioactive material to employees or the environment, and there was no possibility of a criticality due to the small amount of material being transported. Additionally, no employees were injured as a result of the incident, and manufacturing operations at the facility were not impacted. In accordance with its operating license, BWXT immediately notified the NRC following the incident. "As a result of the event, the NRC imposed a civil penalty in the amount of $32,500 on the facility. The NRC has given BWXT 30 days to pay the fine or protest its imposition. Following the incident, BWXT implemented corrective actions related to the process." The licensee has notified the NRC Resident Inspector of this notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-01-29
43933 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2008-01-25 09:00 | 2008-01-25 14:43 | 2008-01-25 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF EMERGENCY SIREN "On January 25, 2008, at about 0902 PST, SCE notified the City of Dana Point Emergency and Support Services of a spurious actuation of a SONGS [San Onofre Nuclear Generating Station] emergency response siren located in the City of Dana Point. "The actuation occurred on January 25, 2008 at about 0900 PST with a duration of approximately ten seconds. The cause of the actuation appears to be due to SCE [Southern California Edison] maintenance being performed at the time. "SCE personnel notified Orange County and the State of California Office of Emergency Services regarding the inadvertent actuation of part of the public notification system. "In compliance with 10CFR50.72(b)(2)(xi), requiring licensees to report any event that results in notification to other government agencies, SCE is providing this notification to the NRC. "At the time of this occurrence, Unit 2 was operating at about 96 percent power and Unit 3 was operating at about 100 percent power. SCE has notified the NRC resident inspectors about this occurrence and will provide them with a copy of this report." | 0 | 96 | 100 | 0 | 96 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-01-25
43932 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2008-01-24 16:04 | 2008-01-24 18:59 | 2008-01-24 | MANUAL REACTOR TRIP DUE TO FAILURE OF THE "C" FEEDWATER FLOW CONTROL VALVE "At 1604 [EST], VC Summer Nuclear Station was manually tripped due to rapidly decreasing level in 'C' Steam Generator. The decreasing Steam Generator level was due to a failure of the 'C' Feedwater Flow Control Valve. All systems responded as required. All Emergency Feedwater Pumps automatically started on Lo-Lo Steam Generator level. The Steam Generator levels recovered quickly. The Pressurizer Level Control System cycling resulted in lifting the Letdown System Relief Valve due to high temperature and pressure. The Letdown Relief Valve reseated with no further problems. One Moisture Separator Reheater Relief Valve lifted momentarily and reseated. "Presently, the plant is in Mode 3 with normal RCS pressure and temperature. Decay heat is being removed by dumping steam to the condenser. The plant will remain in Mode 3 until repairs are completed on the 'C' Feedwater Flow Control Valve." During the trip, all control rods fully inserted into the core. The electrical grid is stable and emergency power is being supplied from offsite via the station start-up transformer. There is no known primary to secondary leakage. The licensee has notified the NRC Resident Inspector and will be notifying State and local agencies. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-01-24
43931 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2008-01-24 12:45 | 2008-01-24 17:45 | 2008-01-24 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST ON A CONTRACT SUPERVISOR A non-licensed contract employee supervisor had a confirmed positive for illegal drugs during a fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. | 79 | 100 | 0 | 79 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2008-01-24
43930 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2008-01-24 | 2008-01-24 15:29 | 2008-01-24 | AGREEMENT STATE REPORT - WRONG ISOTOPE ADMINISTERED "On January 14, [2008], a physician gave a verbal order for a I-123 [Iodine-123] uptake scan. But instead, the patient was given a I-131 uptake scan. On January 16, the physician reviewed the results and realized the wrong isotope had been used. The patient has been notified. No adverse health effects are expected. Florida is investigating." The amount of I-131 delivered to the patient was 4.7 milliCuries. This event was assigned Incident Number FL08-012 by the State of Florida. A 'medical event' indicates potential problems in a medical facility's use of radioactive materials. It does not result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-01-30
43929 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2008-01-23 22:15 | 2008-01-23 23:05 | 2008-01-23 | UNUSUAL EVENT - UNCONTROLLED HYDROGEN LEAK "St. Lucie Plant made an Unusual Event notification to the Florida State Warning Point @ 2228 EST, 01/23/08 based on a Hydrogen Tube Trailer fitting failure, and subsequent leak of hydrogen gas. The emergency classification was Emergency Action Level #20. A., per St. Lucie Plant EPIP-01, 'Classification of Emergencies'. The hydrogen leak was terminated upon discovery, with no subsequent fire and no personnel injuries. The event (and declaration) was terminated @ 2228 EST, on 01/23/08." The licensee notified the NRC Resident Inspector, and the Commonwealth of Florida Warning Point. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-01-23
43928 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2008-01-23 14:15 | 2008-01-23 21:34 | 2008-01-23 | ONE OF TWO MAIN FEEDWATER PUMPS TRIP "On January 23, 2008, at about 1415 PST, SONGS Unit 2 was operating at approximately 95 percent power when one of two main feed water pumps (P063/K005), tripped on low oil pressure while an adjustment was being made to the pump's lubricating oil pressure regulator. Control room operators manually actuated the emergency feedwater system in accordance with Abnormal Operating Instructions. Control room operators reduced reactor power level to about 65 percent which can be sustained with one normal feedwater pump in operation. The cause of this event is currently under investigation. "In compliance with 10CFR50.72(b)(3)(iv)(A), requiring licensees to report any event or condition that results in valid actuation of the emergency feedwater system, SCE is providing this notification to the NRC. "At the time of this occurrence, Unit 3 was operating at about 100 percent power. SCE has notified the NRC resident inspectors about this occurrence and will provide them with a copy of this report." | 0 | 65 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-01-23
43927 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-01-23 17:05 | 2008-01-23 18:31 | 2008-01-24 | UNUSUAL EVENT - TOXIC GASES IN THE TURBINE BUILDING "Detection of toxic gases (CO) inside the turbine building. "Source not identified. "Initial Readings were greater than 50 parts per million in turbine building lower elevations. "EALHU5.1 "Detected by safety department random sampling. "Turbine building has been evacuated, all personnel have been accounted for with no injures. "Follow-up notification will be made with determination of cause of event. "The unit is currently defueled. The carbon monoxide source is being investigated." The NRC Resident Inspector as well as state and local authorities were notified. * * * UPDATE FROM ERIC PICKRELL TO JOE O'HARA AT 1932 EST ON 1/23/08 * * * "Notified J. O'Hara of termination of the declared NOUE. Termination is based on subsequent air monitoring sampling revealing normal Oxygen levels and no detectable Carbon Monoxide levels. "(unknown) Source of abnormal sample readings is not yet determined. Believed to be result of Hydrogen Water Chemistry system purge which was in progress at the time of sampling." Licensee terminated the declaration of notification of unusual event at 1827 CST following two subsequently satisfactory air samples. Notified R4DO(Johnson), NRR(Case), and IRD(Blount) * * UPDATE FROM TIM SCHENK TO JOHN KNOKE AT 1515 EST ON 01/24/08 * * "It has been determined that hazardous levels of toxic gases (Carbon Monoxide) inside the turbine building did not exist at the time of emergency declaration. Actual carbon monoxide levels were less than detectable. Gas sensor cross contamination led to false readings of high carbon monoxide level (60 ppm), when actual gas measurements were reading hydrogen levels of 20 ppm. This level of hydrogen is well below the 40,000 ppm Lower Explosive Limit for hydrogen. The source of the hydrogen readings was attributed to a leaking ventilation rig for the Hydrogen Water Chemistry system during system purge with Nitrogen." The licensee notified the NRC Resident Inspector. Notified R4DO (C. Johnson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 4 | LA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2008-01-23
43926 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2008-01-23 11:30 | 2008-01-23 17:50 | 2008-02-19 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The State provided the following information via email: "At approximately 11:30 AM January 23, 2008, the Agency was informed that the Licensee had a Instro Tek Model 3500, SN 599, portable moisture/density gauge stolen from the back of a truck. The theft occurred at approximately 6:00 AM . The gauge was locked with a chain in the bed of the truck which was parked unattended at an employee's residence. The gauge contains 11 mCi (408 MBq) of Cesium-137 and 44 mCi (1.63 GBq) Am:Be-241. The Licensee is offering a $500.00 reward for the recovery of the source. A press release will be made. "Glendale PD is investigating and has issued report number 08-8332. "The Agency [State] continues to investigate the circumstances regarding this theft for the source. The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." * * * UPDATE BY AUBREY GODWIN TO JASON KOZAL ON 02/19/08 AT 1103 EST * * * "The device was recovered from a Pawn Shop in Phoenix, AZ after being advertised on e-Bay. The Pawn Shop Owner indicated the device was not opened but it was not secured. The investigation continues." Notified R4DO (Miller), FSME (Burgess), ILTAB (e-mail), Mexico (Fax) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2008-01-28
43925 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2008-01-23 09:00 | 2008-01-23 14:08 | 2008-01-23 | AGREEMENT STATE REPORT - THREE PATIENTS POSSIBLY EXPOSED TO ALPHA EMITTER "Licensee notified state that Tuality Community Hospital had 3 patients with possible exposure through inhalation of Thorium, Selenium, Zinc Oxide, Zinc Hydrate, Hydrogen Seleniate. [Licensee is] concerned about potential for Alpha particle exposure and requested assistance contact information. [State] provided REAC/TS contact information." The state will be providing additional information when licensee provides it. Oregon Incident Report #08-0005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2008-01-28
43924 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-01-23 00:10 | 2008-01-23 01:42 | 2008-01-23 | EMERGENCY RESPONSE DATA SYSTEM UNAVAILABLE "On 1/23/08 at 0010 the Unit 4 Emergency Response Data Acquisition and Display System (ERDADS) was noted to be not functioning. Reboot was attempted several times prior to achieving success. During this timeframe a loss of the ability to supply Emergency Response Data System (ERDS) data existed for greater than 30 minutes. This is also an ERDADS failure that was not corrected within 30 minutes. These fall into a 'major loss of emergency assessment capability' 10 CFR 50.72 (b) (3) (xiii). The system was restored 1/23/08 at 0045." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-23
43923 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2008-01-14 13:41 | 2008-01-22 20:16 | 2008-01-22 | INVALID ACTUATION OF GROUP 5 AND GROUP 10 PRIMARY CONTAINMENT VALVES DURING SURVEILLANCE TESTING "This is not an LER. The reports being made to the NRC under 10 CFR 50.73(a)(2)(iv)(A), and the 60 day telephone notification option under 10 CFR 50.73(a)(1). The event included invalid '. . .general isolation signals affecting containment isolation valves in more than one system. . .' as discussed in 10 CFR 50.73(a)(2)(iv)(B). "The following information is provided as requested in NUREG-1022: "(a) The specific train(s) and systems that were actuated? "On January 14, 2008 at 13:41 hours. Unit 2 received invalid Division 1 Primary Containment isolation signals to both Group 5 (RHR Shutdown Cooling Isolation valves) and Group 10 (Reactor Core Isolation Cooling [RCIC] system isolation valves) during Division 1 instrumentation surveillance testing. While performing testing, an incorrect lead was lifted causing this invalid actuation. "(b) Whether each train actuation was complete or partial. "The event resulted in closure of the RCIC steam supply header outboard containment isolation valve. The Division 1 RHR Shutdown Cooling System isolation valves were already closed at the time of the isolation signal. "(b) Whether or not the system started and functioned as designed. "The Primary Containment isolation instrumentation logic and associated valve closure function (for RCIC) actuated as designed." The licensee took prompt actions to recover the RCIC and RHR systems. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-01-22
43922 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-01-21 09:52 | 2008-01-21 12:26 | 2008-01-21 | ON-SITE FATALITY "A supplemental employee associated with the Salem Steam Generator Replacement Project died this morning from an apparent heart attack. The death was not the result of any industrial safety issue and did not occur in a contaminated area. The individual was treated by the onsite EMI's who administered CPR and AED (automatic external defibrillator). He was transported via ambulance to Salem Memorial hospital where he was pronounced dead. This is considered to be a common report for both Salem and Hope Creek Generating Stations." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-01-21
43921 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2008-01-19 23:02 | 2008-01-20 02:55 | 2008-01-20 | AUTOMATIC REACTOR TRIP FOLLOWING TURBINE TRIP "Initiating alarm received was a Turbine Trip. All on site buses 1, 2, 4, 5 and 6 swapped to the Reserve Auxiliary Transformer power supplies. Bus 3 did not swap as expected. The station has entered a Technical Specification 3.8.1.1 (a) 72 hour action statement for offsite power distribution with 345 kV Bus 3 unavailable. "All safety systems operated correctly. The station continues to troubleshoot the initiating cause of the Turbine Trip. The plant is stable in Mode 3." During the swap of non safety buses to the Reserve Auxiliary Transformer the Reactor Coolant Pumps (RCP) tripped. Following the loss of power to the RCPs the reactor stabilized in natural circulation. A Pressurizer PORV cycled following the trip. One RCP was restarted to restore forced circulation. Auxiliary Feedwater Pumps started as expected on the trip and were subsequently secured. All control rods fully inserted on the trip. The current decay heat removal path is Start-up Feedwater supplying water to the Steam Generators steaming to the Condenser Steam Dumps. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0348 ON 1/20/08 FROM FORREST TO HUFFMAN * * * The licensee has indication of a differential voltage fault on the C phase of the 345 kV line that feeds the Unit Auxiliary Transformer and the generator step-up transformers. The licensee also wanted to ensure that the report reflected the specified system actuation of Auxiliary Feedwater. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-01-20
43920 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2008-01-19 11:52 | 2008-01-19 16:13 | 2008-01-19 | 'A' AND 'B' RECIRCULATION PUMP MOTOR GENERATOR OVERSPEED STOPS FOUND SET HIGH (NON-CONSERVATIVE) DURING SURVEILLANCE TESTING "During the Performance of the 18 month surveillance requirement to demonstrate operability of the reactor recirc pump motor set scoop tube mechanical and electrical stop over-speed set points to be less than or equal to 109 percent and 107 percent, respectively, the 'A' and 'B' MG set stops were found non-conservatively high. The electrical and mechanical stops have been adjusted to meet surveillance requirements as of 1538 [on] 1/19/2008. "The potential impact of this condition would be a function of the reactor recirc 'run-out' transient. If that analyzed transient were to have occurred, the potential existed for the flow dependent Minimum Critical Power Ratio to have been exceeded. This could result in exceeding the safety limit (MCPR) under the most limiting postulated conditions. "Evaluation of the potential cause of the improper settings is underway. "The 'A' Recirc Pump and Motor were replaced during the last refueling outage. [November 2007]" The licensee notified the NRC Resident Inspector. The licensee will notify Lower Alloways Creek Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-01-19
43919 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2008-01-18 17:44 | 2008-01-18 18:44 | 2008-01-18 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO TWO INOPERABLE ROD POSITION INDICATORS IN THE SAME ROD GROUP "At 1744 [EST] on 1/18/08, [the licensee] entered Technical Specification (TS) 3.0.3 on Unit 3 due to observed Rod Position lndicator (RPI) F-14 dropping from 228 steps to 135-145 steps and behaving erratically. This RPI is in the same bank as currently inoperable RPI F-2. TS 3.1.3.2 has actions for a maximum of one RPI per bank inoperable. Since there are two inoperable in one bank, an entry into TS 3.0.3 is required. "Power reduction [was] initiated at 1835 [hrs.]. "Repairs [are] currently in progress [and the licensee] anticipate[s] correction prior to completion of power reduction." If the RPI is not corrected, the licensee will be required to be in Mode 3 by 0044 hrs. EST on 01/19/08. This is an ongoing issue. See Event Notifications 43896 and 43888. The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY DAVE FUNK TO JASON KOZAL AT 2041 0N 1/18/07 * * * "Repairs are complete. RPI F-14 has been restored to service on Unit 3, exited Technical Specification 3.0.3 at 2027. Return to 100% power on Unit 3 [is] in progress." The licensee will notify the NRC Resident Inspector. Notified R2DO (Moorman). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-01-18
43918 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2008-01-18 17:03 | 2008-01-18 17:54 | 2008-01-18 | OFFSITE NOTIFICATION DUE TO RECEIPT OF PACKAGE THAT EXCEEDED ALLOWABLE CONTACT DOSE RATE "At 1703 EST on 1/18/2008, Susquehanna LLC personnel became aware that a shipment received from GE Hitachi Nuclear Energy exceeded the allowable limit of 200 mr/hr contact dose rate. The external radiation limit of 200 mrem/hr was exceeded on one of the two boxes comprising the shipment. The limit per NDAP-QA-0648 is 200 mrem/hr on contact for a shipment type for a transport vehicle which is not designated exclusive use. The actual value was determined to be 350 mrem/hr, therefore reportable per the requirements of 10CFR20.1906(d)(2). "The NRC Resident Inspector and the Shipper (GE Hitachi Nuclear Energy) were notified. The transport vehicle left Wilmington NC on 1/17/2008 at 1435 and was received by SSES [Susquehanna Steam Electric Station] on 1/18/2008 at 0800. There was no surface contamination noted on the shipment. The original survey completed prior to shipment noted the highest on contact dose rate was 170 mr/hr. "This item is reportable under 50.72(b)(2)(xi) for offsite notification of an event of public interest." The boxes contained various pieces of equipment that GE uses to support refueling. The licensee has notified the NRC Resident Inspector and will be notifying the Pennsylvania Emergency Management Agency. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | EXTERNAL RAD LEVELS > LIMITS |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) | 20.1906(d)(2) |  |  | 0 | 2008-01-18
43917 | -1 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2008-01-17 | 2008-01-18 15:20 | 2008-03-12 | POTENTIAL OVEREXPOSURE "The possible medical event occurred at a broad-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. The permittee is VA Boston Healthcare System, Boston, Massachusetts. "The possible medical event occurred on January 17, 2008, and was discovered the same day. The basis for the possible medical event is under 10 CFR 35.3045(a)(2) and involved administration of radiopharmaceutical that might have resulted in more than 50 rem to tissue and involved a wrong route of administration. "Specifically, a F-18 FDG injection of approximately 3.6 millicuries was infiltrated into a patient's arm. "The Department of Veterans Affairs and permittee are reviewing the possible medical event circumstances and the dose calculation methods. "The permittee informed the patient and referring physician." * * * RETRACTION FROM THOMAS HUSTON TO HOWIE CROUCH ON 3/12/08 @ 1430 HRS. * * * "The basis for retracting the event is that infiltration is not considered to be a wrong route of administration. This basis was communicated to NHPP [National Health Physics Program] in a phone call received from our NRC Region III Project Manager (Cassandra Frazier) on March 7, 2008 at 4:40 pm." Notified R1DO (Lorson), R3DO (Ring), and FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 1 | MA | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2008-01-24
43916 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-01-18 10:15 | 2008-01-18 11:53 | 2008-01-18 | OFFSITE NOTIFICATION OF TRITIUM IDENTIFIED IN WATER SAMPLES FROM PIPING LEAK "This is a report of a situation, related to the protection of the environment, for which a notification to other government agencies is being made, as described in 10CFR50.72(b)(2)(xi). "On January 17, 2008, at approximately 1300 hours, site environmental monitoring personnel at River Bend Station completed analysis which confirmed the presence of tritium in water samples taken from a piping leak that occurred on January 16, 2008, on plant property. The source of the tritium was from water that had been treated in the liquid radwaste system and was suitable for release. The Louisiana Department of Environmental Quality and other state and local officials are being notified in accordance with the voluntary NEI groundwater protection initiative. "The following is a summary of the events that led up to the identification of tritium in the water sample. "On January 16, 2008, at approximately 1750 hours with the plant shutdown in Mode 5 (Refueling), River Bend Station personnel identified a water leak from a cooling tower blowdown line. The design of this system takes water from the plant's cooling tower basin. This water mixes with treated water being discharged from the liquid radwaste system. The diluted blowdown is then discharged to the Mississippi River. "Plant operators received a low blowdown line flow alarm and immediately terminated the discharge of water from the liquid radwaste system. The cooling tower blowdown pumps were also subsequently stopped. The leak was caused by a failure of the blowdown piping. "The leak was located inside the owner controlled area near the plant's cooling towers. Based on the location of the leak, the water drained to a nearby storm drain and into East Creek (Outfall 3). East Creek exits the plant site and discharges to the Mississippi River. The volume of the spill as been estimated to be less than 720 gallons of water from the radwaste system. This water had been treated and was suitable for release. Additional clean water from the cooling tower basin mixed with the water from the liquid radwaste system and was released. The analysis of a water sample, taken at the discharge point to East Creek determined that the samples contained 28,042 Pico Curies per liter (pCi/I) tritium. The NRC reporting level for a non-drinking water pathway is 30,000 pCi/I. Samples taken directly at the location of the leak contained 129,456 pCi/I tritium. The release has no potential to impact the health and safety of the public. RBS personnel are investigating the cause of the leak and will not restore blowdown until action is taken to prevent further occurrence." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-01-18
43915 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2008-01-16 12:30 | 2008-01-18 10:32 | 2008-01-18 | AGREEMENT STATE REPORT INVOLVING A LEAKING SEALED SOURCE WITH CONTAMINATION The following information was provided via fax: "Duratek called DRH at approx. 1430 EST Jan. 17, 2008 to report a contamination event which required control of an area of their building for greater than 24 hours. While unpackaging a sealed source that was sent to them for processing for disposal, the container which the source was in was found to be contaminated. An area of about 10' by 10', covered with herculite, was contaminated and an area of 20' by 50' is being access controlled. Three personnel working at the scene were contaminated with the maximum contamination found on the personnel being 300 cpm alpha. The source was a 140 µCi U-232 solid source from the Portsmouth Facility in Ohio. The source was re-secured in containers and the contaminated area is being decontaminated. Max contamination levels on container were 400,000 dpm/100 cm2 beta/gamma and 100,000 dpm/100 cm2 alpha. The personnel were decontaminated and had lung counts. Lung counts for all were negative for elevated intake. Fecal bioassays were initiated and are ongoing. "Media attention: None at this time. "Event Report ID No.: TN-08-005" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2008-01-23
43914 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-01-17 18:00 | 2008-01-17 23:48 | 2008-01-18 | CONTROLLED SUBSTANCE FOUND IN LOCATION OUTSIDE PROTECTED AREA "At approximately 1800 EST, a controlled substance and paraphernalia were discovered by a supplemental employee, who then reported the discovery to his supervision. Plant Security was contacted, who then notified Local Law Enforcement. All supplemental personnel who were in-processing in the area at the time of discovery were interviewed and sent for FFD testing. All immediate results were negative; lab results are still pending. A drug detection dog was brought in by the Local Law Enforcement Agency to clear the area where the substance was found and nothing additional was found. This notification is being made as a courtesy as a result of the potential newsworthiness of the event." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (POPE) TO NRC (HUFFMAN) AT 0925 EST ON 01/18/08 * * * "The building in which the substance was found was located outside the Plant Vogtle Protected Area." The licensee notified the NRC Resident Inspector. R2DO (Moorman) notified. | 97 | 98 | 0 | 97 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW | [5 empty] | 0 | 2008-01-18
43913 | 0 | APL LIGHTING COMPONENTS |  |  |  |  | 2007-09-18 | 2008-01-17 13:17 | 2008-01-17 | LOST STATIC ELIMINATOR The licensee reported they lost a static eliminator manufactured by NRD, Model #P202108181 with 2 milliCuries of Polonium 210. The device was last seen in June 2007 and was used to remove plastic particles from manufactured plastic parts. The licensee believes that the device became dislodged in the manufacturing plant, fell onto the shop floor, and was swept up with debris. The licensee was collecting and accounting for the devices in September 2007 when they noticed it was missing. As a result of this event, the licensee has since incorporated training into the workforce so that the employees can identify and account for the devices. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2008-01-17
43912 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-01-17 13:04 | 2008-01-17 14:00 | 2008-01-17 | DISCOVERED VULNERABILITY IN A SAFEGUARD SYSTEM "The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details." * * * UPDATE FROM DAVE FUNK TO JOE O'HARA AT 2128 AT 1/17/08 * * * The licensee provided additional information regarding the safeguards system vulnerability. Contact the Headquarters Operations Officer for additional details. Notified R2DO(Moorman) and 73.71 E-Mail Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2008-01-17
43911 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-01-17 09:17 | 2008-01-17 10:21 | 2008-01-17 | CONTROL ROOM ANNUNCIATORS REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "At 0917 CST on 1/17/2008, the Main Control Room annunciator system has been removed from service to support maintenance at River Bend Station. The duration of the work is expected to be completed in less than one (1) hour. "During this time, other Main Control Room indications and alternate methods will be available to implement the Emergency Plan. Since the Main Control Room annunciator system will be unavailable, this is considered a Loss of Emergency Assessment Capability and is reportable under 10CFR50.72(b)(3)(xiii). "A follow-up notification will be made to the NRC after the Main Control Room annunciator system is returned to service. "The licensee notified the NRC Resident Inspector." * * * UPDATE FROM SCHENK TO SANDIN AT 1120 EST ON 01/17/08 * * * At 1015 CST on 1/17/08, the licensee restored the main control room annunciator system to service. The NRC Resident has been notified. R4DO (Spitzberg) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-17
43910 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2007-12-11 16:45 | 2008-01-17 10:10 | 2008-01-17 | 60-DAY NOTIFICATION OF AN INVALID ACTUATION OF UNITS 2 AND 3 PRIMARY CONTAINMENT ISOLATION SYSTEMS "This 60-day report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of specified systems, specifically the Units 2 and 3 Primary Containment Isolation Systems (PCIS). "On 12/11/07, at approximately 1645 hours, the 13 Kv non-safety related AS4 feeder breaker tripped as a result of an electrical fault downstream of the breaker. The electrical fault resulted in a momentary voltage dip on the offsite power source (3SU). The momentary voltage dip resulted in PCIS Group II and III isolations on Units 2 and 3. Unit 2 experienced inboard PCIS isolations, while Unit 3 experienced outboard PCIS isolations. The isolations involved various process lines including Reactor Water Cleanup (RWCU), Containment Atmospheric Control (CAC) / Containment Atmospheric Dilution (CAD), Drywell Sumps, and Containment Instrument Nitrogen. The Units 2 and 3 PCIS isolations were reset by approximately 1715 hours in accordance with procedures. All required isolation valves operated as designed. "The AS4 breaker trip has been preliminarily determined to be an electrical fault of a fuse clip associated with a non-safety related transformer (00X029). This transformer provides power to equipment at the discharge canal control structure. This issue has been entered into the site Corrective Action Program (CRs 710316, 711652, 710769) for evaluation and implementation of further corrective actions. "The NRC resident has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-01-17
43909 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-01-16 19:25 | 2008-01-16 21:15 | 2008-01-16 | MANUAL REACTOR TRIP DUE TO LOWERING STEAM GENERATOR LEVEL During a surveillance test on the Loop 3 Steam Generator pressure channel, the loop 3 Steam Generator main feedwater regulating valve went closed. The unit was manually tripped on lowering steam generator level. All control rods fully inserted on the reactor trip. Both motor driven and the turbine driven AFW pumps started successfully. The turbine driven AFW pump was secured and the motor driven AFW pumps are providing feedwater to the steam generators. Decay heat is being removed to the main condenser via the turbine steam dump valves. No PORV, safety relief valves, or atmospheric dump valves opened on the reactor trip. Unit 1 is in a normal shutdown electrical lineup. There was no effect on Unit 2 during this event. The licensee is investigating the unexpected closure of the Loop 3 Steam Generator main feedwater regulating valve. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-01-16
43908 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2008-01-15 | 2008-01-16 16:47 | 2008-01-16 | MASSACHUSETTS AGREEMENT STATE REPORT - MISSING BRACHYTHERAPY SEEDS "The Licensee's RSO reports that a total of five (5) I-125 brachytherapy seeds, each containing 0.395 millicuries (assayed January 15, 2008) (total activity of 1.975 millicuries) are missing. The Licensee's RSO reports that the seeds were likely lost during or after a procedure performed in the Licensee's operating room on January 15, 2008. The seeds were discovered to be missing on January 16, 2008 and the seeds likely were disposed of in regular trash. "The Licensee's RSO reports that the missing seeds are Oncura Echo seed Model 6733 seeds. "The Licensee continues to search and survey for the seeds." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2008-01-21
43907 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2008-01-15 14:15 | 2008-01-15 16:14 | 2008-01-17 | UNUSUAL EVENT - LOSS OF OFFSITE POWER "At 1404 1/15/2008, Central time, Point Beach experienced a loss of Unit 1X-04, Low Voltage Station Auxiliary Transformer. This loss has caused Point Beach to declare an Unusual Event (SU 1.1, Loss of all Offsite Power to essential busses for greater than 15 minutes.) "The loss of Unit 1X-04 transformer is under investigation. "All equipment operated properly with the exception of 1B-04, 'B' train 480 VAC Safeguards Bus, supply breaker opened for unknown reasons. "The licensee notified the NRC Resident Inspector. "Preparations are underway for a Unit 1 shutdown." Both Unit 1 EDGs are running and supplying Unit 1 safeguard buses. Non-safety buses are powered from an auto transfer that occurred after the loss of 1X-04. No impact on Unit 2 due to the Unit 1 electrical transient. Licensee notified state and local emergency management agencies. * * * UPDATE FROM DENNY SMITH TO JEFF ROTTON AT 2300 ON 1/15/08 * * * "On 1/15/08 at 1941 central time, FPL Energy Point Beach, LLC issued a press release concerning the Unusual Event at Point Beach that was declared on 1/15/08 at 1415 central time. The Unusual Event was reported under EN# 43907 and occurred due to the loss of all offsite power to essential busses for greater than 15 minutes from the failure of the Unit 1 X-04, Low Voltage Station Auxiliary Transformer. "The NRC Resident Inspector has been informed of the press release and this subsequent notification." * * * UPDATE FROM RICK ROBBINS TO JOE O'HARA AT 1816 EST ON 1/16/08 * * * "At 1404 on 1/15/08 central time, Point Beach experienced a loss of Unit 1 X-04, Low Voltage Station Auxiliary Transformer. This loss caused Point Beach to declare an Unusual Event and that was reported under EN# 43907. Technical Specification 3.8.1.B, Associated unit's 13.8/4.16 kv (X04) transformer inoperable, was not met as of 1404 on 1/15/08 and this LCO has a Required Action to restore the (X04) transformer to Operable status with a Completion time of 24 hours. "At 1404 1/16/08 the LCO was still not met and Unit 1 entered Technical Specification 3.8.1.H Required Action and associated Completion Time Not met, with a required action to be in Mode 3 in 6 hours and Mode 5 in 36 hours. "This Event Notification Worksheet is for the initiation of the Technical Specification Required reactor shutdown that commenced at 1549 on 1/16/08, per 10 CFR 50.72(b)(2)(i)." The licensee notified the NRC Resident Inspector. Notified R3DO(Stone), NRR EO(Evans), and IRD(Blount). * * * UPDATE FROM RICK ROBBINS TO JOE O'HARA AT 2222 EST ON 1/16/08 * * * "Update: At 1947 CST on 01/16/08, the Unit 1 reactor reached MODE 3, completing the required Technical Specification Shutdown. Offsite power has been restored to the essential busses by paralleling from Unit 2 4160 V buses and the Emergency Diesel Generators G-01 and G-03 have been placed back to a normal standby alignment. The unit is being taken to MODE 5 in accordance with plant TS requirements. "This update to EN #43907 also reports the termination of the Unusual Event [AT 2035 CST] SU1.1, Loss of all offsite power to essential buses for greater than 15 minutes initially reported via EN #43907. The State of Wisconsin and the counties of Kewaunee and Manitowoc were notified of the termination via the Nuclear Accident Reporting System (NARS) at 2041 on 1/16/08." The licensee notified the NRC Resident Inspector. Notified R3DO(Stone), NRR EO(Evans), NRR ET(Dyer), DHS(Gray), FEMA(Dunker), and IRD(Blount). * * * UPDATE FROM KILE HESS TO BILL HUFFMAN AT 1019 EST ON 1/17/08 * * * "Update: At 0702 CST on 01/17/08, FPL Energy Point Beach, LLC issued a press release regarding the termination of the Unusual Event and the shutdown of Unit 1 for repair of 1- X04 transformer. "The NRC resident inspector was notified of the press release." R3DO (Stone) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION | PLANT S/D REQD BY TS |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) | 50.72(b)(2)(i) |  | 0 | 2008-01-15
43906 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2008-01-15 13:30 | 2008-01-15 15:42 | 2008-01-15 | DAMAGED FIBER OPTIC CABLE AFFECTED COMMUNICATIONS "At approximately 1:30 PM Eastern Standard Time, the Harris Nuclear Plant (HNP) identified the inability for the NRC to contact the plant using the telecommunications system. The dedicated phone line to the State and County Warning Points and Emergency Operating Centers was maintained and verified. This condition was the result of a damaged fiber optics cable remote from the plant site. The cable was damaged during construction in Apex, NC. The ability for HNP to contact offsite agencies and HNP Emergency Response Organization was maintained at all times. Alternate methods for the NRC to contact HNP were established at 2:45 PM. The telecommunication capabilities were restored at 3:04 PM Eastern Standard Time." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-15
43905 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2007-12-20 | 2008-01-15 11:35 | 2008-01-16 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT - MISPLACED SEEDS DURING PROSTATE TREATMENT The State provided the following information via facsimile: "On January 10, 2008, a 4-week follow up CT-based post prostate seed implant plan was created and reviewed by the prescribing physician. Upon completion of the review it was determined that the seeds had been implanted approximately 2.5cm interior to the base of the prostate. The prescription dose was for 145 Gy to be implanted into the prostate gland using 74 lodine -125 seeds with an average activity of 0.300 milliCuries "The post plan dosimetry showed that prostate was under-dosed by greater than 20% from the prescription dose of 145 Gy. The nearby organs at risk, namely the bladder and rectum, were not affected by the misplacement of the seeds. "On January 11, 2008, the prescribing physician, [DELETED], notified the attending urologist, [DELETED] of this medical event. The urologist has requested that he notify the patient himself." Item Number: KY082 * * * UPDATE FROM CYNTHIA FLANNERY TO JOE O'HARA VIA E-MAIL AT 0651 ON 1/16/08 * * * "EN43905 has been reviewed and determined to be a reportable medical event." Notified R1DO(Cobey) and FSME(Flannery) A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2008-01-19
43904 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-01-14 16:10 | 2008-01-14 17:05 | 2008-01-14 | PLANNED LOSS OF MAIN CONTROL ROOM ANNUNCIATOR SYSTEM "At 1610 hours, on 1/14/2008, the Main Control Room annunciator system will be removed from service to support activities for a planned maintenance outage at River Bend Station. The duration of the work is expected to be completed in less than 1 hour. "During this time, other Control Room indications and alternate methods will be available to implement the Emergency Plan. Since the Main Control Room annunciator System will be unavailable, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii). "A follow-up notification will be made to the NRC after the Main Control Room annunciator system is returned to service. "The licensee notified the NRC Resident Inspector." No major systems in LCOs at this time and the only major ongoing activity is Fuel Handling. * * * UPDATE PROVIDED BY GARY HUSTON TO JEFF ROTTON AT 1809 ON 01/14/08 * * * "Main control room annunciator system has been restored to service at 1708 CST." The licensee notified the NRC Resident Inspector. Notified R4DO (Spitzberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-14
43903 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2008-01-13 15:12 | 2008-01-14 15:36 | 2008-01-18 | FAILURE OF UF6 RELEASE DETECTION SYSTEM "At 1512 CST, on 01-13-08 the Plant Shift Superintendent (PSS) was notified that the C-333 Unit 6 Cell 7 UF6 Release Detection (PGLD) System failed to function when performing the twice per shift test firing. Test firing of the PGLD detector heads is required per TSR SR 2.4.4.1-1. TSR 2.4.4.1 also requires that at least the minimum number (three) of detector heads in the cell and in each defined section of the cell bypass are operable where UF6 systems are above atmospheric pressure. The C-333 Unit 6 Cell 7 PGLD System contains detectors that covers the cell and Sections 3 and 4 of the cell bypass piping. At the time of this failure some areas of Section 3 of the cell bypass were operating above atmospheric pressure. Since Unit 6 Cell 7 was operating below atmosphere, the cell was not in an applicable TSR mode. However, Section 3 of the cell bypass was above atmosphere and in an applicable TSR mode which required at least three operable PGLD heads. With the Unit 6 Cell 7 PGLD system inoperable only two of the required three heads in Section 3 of the cell bypass were operable. This PGLD System was declared inoperable, and system pressure in the affected operating area was reduced to less than atmospheric pressure within one hour, thus placing the operating system in a non-applicable TSR mode. This event is being reported as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATR-08-0122; PGDP Event Report No. PAD-2008-01; Worksheet No. 43903 "Responsible Division: Operations" The licensee is investigating the cause of the event, and will make appropriate notifications to the Department of Energy. * * * RETRACTION PROVIDED BY TONY HUDSON TO JASON KOZAL AT 1403 ON 1/18/08 * * * "On January 13, 2008 the C-333 U/6 C/7 PGLD system failed during testing. This affected all the PGLD heads in the cell area and two of the four heads in section 3 of the cell by-pass. A review of operating pressures in the affected area determined that the cell was operating below atmospheric pressure, but that piping in section 3 of the cell by-pass was operating above atmosphere. Thus, three of four heads in section 3 of the Cell by-pass were required by the TSR to be operable. Given the recent failure in November and indications that the failure modes may be similar, the PSS reported the event to the NRC per 10CFR 76.120(c)(2)(i), In-Service Safety System Failure. Subsequent to the event, the pressures in C-333 U/6 CR, section 3 in the cell by-pass area associated with the event were reviewed. Using Engineering Notice EN-C-821-05-090, Rev, 3, it was determined that section 3 of the cell by-pass was actually not operating above atmosphere and thus, the PGLD system was not required to be operable at the time of the failure. Since the failure only affected detectors in an area operating in a non-TSR mode, the PGLD system is not required to be operable and reporting under 10 CFR 76.120(C)(2) is not required." The licensee notified the NRC Resident Inspector. The licensee made appropriate notifications to the Department of Energy. R2DO (Moorman) and NMSS EO (Kokajko) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2008-01-14
43902 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2008-01-13 09:44 | 2008-01-13 13:56 | 2008-01-13 | INTERMITTENT PLANT COMPUTER FAILURES "At 0944, the Plant Computer (ERDADS) failed. Investigation revealed the ERDS link was also INOPERABLE due to the failure of the plant computer due [to] data corruption due to train failovers. Engineering has restored the plant computer by 1300. Called the plant computer and ERDS link OPERABLE at time 1330." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-13
43901 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2008-01-13 10:36 | 2008-01-13 11:36 | 2008-01-13 | LOSS OF EMERGENCY ASSESSMENT CAPABILITIES DUE TO PLANNED MAINTENANCE ACTIVITIES "Planned Maintenance on Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS). "At 1036 CST hours, on 1/13/2008, the SPDS and ERDS system will be removed from service to support activities for a planned maintenance outage at River Bend Station. The duration of work is expected to be approximately 8 hours. "During this time, Control Room indications and alternate methods will be available to implement the Emergency Plan. Since the SPDS computer system will be unavailable for greater than 2 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii). "A follow-up notification will be made to the NRC after the SPDS and ERDS are returned to service. "The licensee notified the NRC Resident Inspector." * * * UPDATE AT 1844 ON 1/13/08 FROM HUSTON TO SNYDER * * * "The SPDS and ERDS systems have been returned to service at 1745." The licensee will notify the NRC Resident Inspector. Notified R4DO (Bywater). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-13
43900 | 0 | PALISADES | 1 |  |  | [1] CE | 2008-01-13 05:21 | 2008-01-13 09:11 | 2008-01-13 | MANUAL REACTOR TRIP AFTER LOSS OF MAIN FEEDWATER PUMP Palisades Operations staff manually tripped the reactor in accordance with their station's Off-Normal Operating Procedure, after an automatic trip of the "B" Main Feedwater Pump (MFP). The cause of the MFP auto-trip is unknown and being investigated. During the trip, all systems performed as designed. During the transient resulting from the trip, the atmospheric steam dump valves did open momentarily and properly reseated. There is no known primary-to-secondary leakage therefore no release was known to have occurred. All control rods inserted fully as a result of the trip. Auxiliary feedwater pump [AFW] 8A started, as expected, in response to low steam generator water levels experienced during the transient and supplied both steam generators. Decay heat is being removed via the main steam isolation valves to the condenser with the 8A AFW pump supplying feedwater to the steam generators. The plant is at normal temperatures and pressures for this mode. The electrical grid is stable with the station start-up transformer supplying station loads. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-01-13
43899 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2008-01-12 16:26 | 2008-01-12 20:57 | 2008-01-12 | MANUAL REACTOR SCRAM DUE TO DEGRADED COOLING TO MAIN TRANSFORMERS "On 1/12/08 at 1626 hours a manual scram was inserted due to degraded cooling on the main transformers. All control rods fully inserted and all systems actuated and/or operated as designed. No safety relief valves opened during the event and reactor pressure is currently being controlled within normal bands with bypass valves. Reactor water level is also being controlled within normal bands with the condensate and feedwater system. Group 2 and 3 isolation signals were received however, no valve movement occurred since these valves are normally closed." The licensee is investigating a potential electrical fault which may have caused the event, but it appears that there was an electrical fault in the transformer cooling system. The grid is normal with no transmission system warnings in effect. All feeds are available. Reactor vessel level is 32.6 inches stable with normal condensate system feeding the vessel. Primary plant pressure is 815 psig. All safety and BOP electrical buses are energized normally. No bus power was lost. Decay heat path is via bypass valves to the main condenser. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-01-12
43898 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-01-12 09:04 | 2008-01-12 19:09 | 2008-01-12 | VALID SPECIFIED SYSTEM ACTUATION DURING EDG GOVERNOR TESTING "An overvoltage condition occurred on the D23 Safeguards 4kv bus during planned system outage window EDG governor testing. The EDG output breaker was immediately opened and the engine secured per test direction. Due to the output breaker being opened, the D23 bus then experienced an undervoltage condition. Bus voltage monitoring instrumentation automatically initiated automatic closure of the 201-D23 Bus Offsite Supply Feed Breaker after a 1 second time delay and re-energized the D23 Safeguards Bus per design. "The remaining three 4kv buses and Emergency Diesel Generators were unaffected and remain operable." The voltage regulation circuit is being investigated at this time to assist in determining the cause of the overvoltage condition. The EDG was out of service and inoperable during the testing. The EDG governor was replaced during the outage window and was being fine tuned when the event occurred. The licensee is currently in day 6 of a 30 day LCO (3.8.1.1). The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2008-01-12
43897 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2008-01-12 | 2008-01-12 11:10 | 2008-01-12 | BULLETIN 91-01 LOSS OF DOUBLE CONTINGENCY CRITICALITY SAFETY CONTROLS "During a project review for the recovery of uranium generated by the chemical laboratory in the Fuel Manufacturing/Operations (FMO) complex, it was discovered that ten (10) laboratory generated cans of material had been improperly stored on a conveyor system. The cans of material came from the FMO chemical laboratory that generated them from its process. The material consisted of both dry uranium powder/pellets and wet ammonium diurinate (ADU). Each can contained approximately 16kg of uranium. "After the material was placed in the cans, it was given an incorrect material type indicating it contained only dry material. When the material was moved from the chemical lab to a storage area in preparation for processing, it was improperly stored on a conveyor which was only authorized for dry material. The second controlled parameter (mass of uranium in each can) was maintained at all times. "Upon discovery of this condition, the ten (10) cans were immediately placed on skids on the conveyor to provide the necessary spacing between each can. "While this did not result in an unsafe condition, this event is being reported pursuant to NRC Bulletin 91-01 within 24 hours of discovery. "NUMBER AND TYPES OF CONTROLS NECESSARY UNDER NORMAL OPERATING CONDITIONS: "The basis of criticality safety relies on spacing of cans (geometry) and mass as independent criticality safety controls. "NUMBER AND TYPES OF CONTROLS WHICH FUNCTIONED PROPERLY UNDER UPSET CONDITIONS: "1 - Mass control remained intact, thus no unsafe condition existed. "NUMBER AND TYPES OF CONTROLS NECESSARY TO RESTORE A SAFE SITUATION: "1 - Control on can spacing was lost since skids were not used to separate moderated cans on the conveyor. "SAFETY SIGNIFICANCE OF EVENTS: "Low Safety Significance - independent control on mass remained intact - additional failure modes required before a criticality accident could occur. The as-found condition was analyzed and demonstrated to be safe. "SAFETY EOUIPMENT STATUS: "All ten (10) cans were placed on skids on the conveyor system and will await further processing. "STATUS OF CORRECTIVE ACTIONS: "Corrective and preventative actions will be identified as part of the incident investigation." The cans were improperly stored for several weeks. The licensee will be making notifications to NRC Region 2, the State of North Carolina and the New Hanover County Emergency Management Agency. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2008-01-12
43896 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2008-01-12 05:41 | 2008-01-12 07:37 | 2008-01-12 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO TWO ROD POSITION INDICATORS (RPIs) OUT IN ONE ROD BANK "At 0451 [EST, the licensee] entered into [Technical Specification (TS)] 3.0.3 due to observed RPI B-10 erratic indication. This RPI is in the same bank as currently inoperable F-2 RPI. TS 3.1.3.2 has actions for a maximum of one RPI per bank inoperable. Since there are two [RPIs inoperable] in one bank, an entry into TS 3.0.3 is required. "Power reduction was initiated at 0541. "Repairs are currently in progress and [the licensee] anticipates correction prior to completion of the power reduction." The licensee notified the NRC Resident Inspector. See event notification #43888 for similar report. * * * UPDATE FROM DAVID FUNK TO HOWIE CROUCH ON 01/12/08 AT 1049 EST * * * Repairs have been completed and B-10 Rod Position Indicator has been returned to service. At 1010 EST, the licensee exited TS 3.0.3 and power ascension to 100% is in progress. The licensee has notified the NRC Resident Inspector. Notified R2DO (Widmann). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-01-12
43895 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-01-11 16:22 | 2008-01-11 17:53 | 2008-01-14 | TECH. SPEC. REQUIRED SHUTDOWN DUE TO GAS VOIDING IN DISCHARGE PIPING "Gas intrusion into ECCS piping required entry into Technical Specification (TS) 3.0.3. "Wolf Creek was operating at 100% power when gas voiding was discovered in RHR discharge piping common to both trains of ECCS. Due to void reoccurring in excess of predetermined limits both trains of ECCS were declared inoperable at 1525 CST. A TS required shutdown was commenced at 1622. "Engineering is researching the composition of the gas and possible sources." The licensee must determine that the line is solid with fluid without any gas voiding before exiting the TS required shutdown. All normal and emergency power supplies are available. All EDG's are operable. Reactor power is being reduced one-half a percent per minute. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY DIANE HOOPER TO JEFF ROTTON AT 1932 ON 01/14/08 * * * "At 1550 [CST] on 1/14/2008, Engineering notified control room that the A RHR pump suction from the recirc sump has a void in excess of the allowable limit. Due to the isolation of the 'piggyback' line from the A RHR to the suction of the CCPs, [Wolf Creek] no longer has 'at least the ECCS flow equivalent to a single OPERABLE ECCS train available.' [Wolf Creek] has already entered condition B of 3.5.2 and the cooldown requirement from action B of 3.5.2 is more restrictive than the cooldown requirement of 3.0.3. No additional actions need to be taken to comply with Tech Specs. "At 1700 [CST] on 1/14, Engineering reports that the voids in the 'piggyback' line has been filled to within acceptable limits." The licensee will notify the NRC Resident Inspector. Notified the R4DO (Spitzberg) | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-01-11
43894 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2008-01-11 15:10 | 2008-01-11 15:46 | 2008-02-08 | DISCOVERY OF AN AFTER THE FACT UNUSUAL EVENT At 1510, "[Watts Bar Nuclear (WBN)] had identified RCS leakage in excess of 25 gallons per minute (gpm). The leakage was estimated at 105 gpm. This is a report notification only and not a declaration. The EAL that was exceeded was 2.6, RCS identified leakage. While placing a mixed bed demineralizer in service VCT level was observed to have dropped 10%. The demineralizer was immediately removed from service. This terminated the drop in VCT level. In accordance with WBN EPIP-1 Emergency Classification Flowchart, section 3.0 step 3.3.7, if an EAL was exceeded but the emergency has been totally resolved (prior to declaration), the emergency condition that was appropriate shall not be declared but reported only. The duration of the leakage was approximately 15 minutes. The unit remains at mode 1 and 100% power. The cause for the unexpected level decrease is under investigation at this time. There were no radiological releases associated." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM MICHAEL BRANDON TO JOE O'HARA AT 1327 ON 1/15/08 * * * The original report contains a typographical error. The leak duration was reported as 15 minutes. The correct time period is 1.5 minutes. Notified R2DO(Moorman) * * * RETRACTION ON 2/8/2008 AT 1710 FROM MICHAEL BRANDON TO MARK ABRAMOVITZ * * * "On January 11, 2008, TVA notified the NRC of the discovery of an after the fact unusual event. The reported event described potential RCS leakage in excess of 25 GPM that was approximately 1 and 1/2 minutes in duration. The estimated magnitude of this leak was based on a step change in Volume Control Tank (VCT) level that occurred when placing the 1A Mixed Bed Demineralizer in service. TVA's post-event investigation concluded the cause of the VCT level change was the filling of a void in the 1A Mixed Bed Demineralizer. The cause of the void was a procedural deficiency in the flush methodology used when returning the demineralizer to service. Based on the evaluation of this event, TVA has concluded that no actual RCS leakage occurred. The RCS pressure boundary remained intact throughout this evolution. "Based on the result of this evaluation and the subsequent successful alignment of the demineralizer without incident, TVA is retracting this event. "The licensee has notified the NRC Resident of this retraction." Notified the R2DO (Munday) and NRR EO (Brown). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | TN | POW |  | 76.120(a)(4) |  |  |  | 0 | 2008-01-11
43893 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-01-10 16:00 | 2008-01-10 20:41 | 2008-01-10 | INADVERTENT ACTUATION OF OFFSITE EMERGENCY SIREN "At 1600 on 1/10/2008 the Control Room was notified by [Offsite Duty System engineer] (ODS) that at 1515, one offsite emergency siren (siren # 54) inadvertently actuated for approximately 3 minutes in Tanner. This required ODS to notify the Alabama Emergency Management Agency. The siren is located within the 10 mile EPZ for BFNP. Due to inclement weather a Tornado Watch was in effect at the time. The siren is currently operable. "The licensee notified the NRC Resident Inspector. "This event is reportable as a 4 hour Non-Emergency Notification report in accordance with 10 CFR 50.72(b)(2)(xi); 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." . | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-01-10
43892 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2008-01-10 18:12 | 2008-01-10 20:34 | 2008-03-07 | VOIDING DISCOVERED IN HIGH HEAD AND INTERMEDIATE HEAD SI COMMON SUCTION "Both centrifugal charging pumps and both safety injection pumps [were] declared inoperable due to 5% to 7% voiding identified in a portion of common suction piping. [The] pumps were inoperable for 27 minutes. [The] line was vented to remove [the] void and [the] pumps restored to operable. (These pumps are the High Head and Intermediate Head Emergency Core Cooling Pumps.)" The source of the voiding is not understood and is under investigation. All systems functioned as required. R4DO (Bywater) notified. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM PRESTON LAWSON TO P. SNYDER AT 1733 ON 3/7/08 * * * Wolf Creek engineering evaluated the effects of the voids found in the common suction piping for the high head and the intermediate head emergency core cooling pumps. The pumps and their systems would have been able to perform their intended safety functions. The licensee will notify the NRC Resident Inspector. Notified R4DO (Cain). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2008-01-10
43891 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2008-01-10 12:21 | 2008-01-10 15:08 | 2008-01-10 | OFFSITE NOTIFICATION - SPILL OF WATER CONTAINING TRITIUM "This is a voluntary notification for a spill of water containing tritium as specified in section 2.2.a.iii, of Nuclear Energy Institute document NEI 07- 07 entitled 'Industry Groundwater Protection Initiative.' On January 5, 2008 at 13:55, Browns Ferry Nuclear (BFN) Plant operations personnel received a high water level alarm on a sump located within the plant, at the Condensate Piping Tunnel. The high water level was corrected within 3 hours of the alarm. Investigation into this condition determined that the water came from an overflow of the Unit 3 Condensate Storage Tank into the tunnel as a result of failed tank level instrumentation. The water was immediately transferred to the plant radioactive waste system for processing. Laboratory analysis results received on January 9, 2008 indicated this water contained 2.2 E-03 uCi/ml tritium. Based on the tunnel construction, there is a potential for a small amount of this water to permeate into the ground. Subsequent to the spill, a sample obtained from the ground water sampling well adjacent to the tunnel showed no detectable level of tritium. BFN routinely monitors the ground water for radioactivity in accordance with the NEI Groundwater Protection Initiative. Tritium levels at BFN have never reached or exceeded the Environmental Protection Agency drinking water limit. This spill was contained within the plant structure and will not increase the dose to the public. As such, this event poses no threat to public health or safety. "The licensee notified the NRC Resident Inspector. "This event is reportable as a 4-hour Non-Emergency Notification report in accordance with 10CFR50.72(b)(2)(xi) Any event or situation, related to the heath and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2008-01-10
43890 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2008-01-10 | 2008-01-10 12:44 | 2008-01-10 | AGREEMENT STATE REPORT - POTENTIAL EXCESSIVE EXPOSURE The agreement state submitted the following information via e-mail: "On January 10, 2008, CONAM reported an accidental, excessive exposure to an industrial radiographers badge. The badge reading for the month of November 2007 was 11,592 millirem. At the end of his shift, the radiographer put his personnel monitor in his work bag. The shift that came in after him used his work bag and had the bag next to the radiography camera during exposures. "The licensee believes that this exposure was to the badge and not to the radiographer. The licensee will be sending a written report within 30 days. [The State of Louisiana] will forward new information when it is received." Louisiana Event Report ID: LA070032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2008-01-15
43889 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-10-13 10:13 | 2008-01-10 12:22 | 2008-01-10 | 60 DAY LER REPORT - 1C EDG INVALID START "This 60-day telephone notification is being made in accordance with the reporting requirements of 10CFR50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) for an invalid actuation (start) of the 1C Emergency Diesel Generator (EDG). "On November 13, 2007, at 1013 hours, while performing the replacement of an indicating bulb on the 1C EDG local start/stop CMC switch (a turn to stop/start switch) the switch was pushed inward making up the start contact and causing an inadvertent start of the 1C EDG. The EDG started but did not load since this was not a valid demand for operation of the 1C EDG. The 1C EDG was shutdown in accordance with operating procedures and returned to its normal standby status. The local start/stop switch was replaced and the removed switch was examined. The removed switch was determined to be missing a cardboard collar on the shaft of the switch that prevents inward movement. Lack of the cardboard collar did not inhibit the turn to start/stop function of the switch." The licensee will notify the NRC Resident Inspector, State of New Jersey, State of Delaware, and local government agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2008-01-10
43888 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2008-01-10 05:02 | 2008-01-10 05:37 | 2008-01-10 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO TWO ROD POSITION INDICATORS (RPIs) OUT IN ONE ROD BANK "At 0408 EST [the licensee] entered into TS 3.0.3 due to an observed RPI B-10 erratic indication. This RPI is in the same bank as currently inoperable F-2 RPI. TS 3.1.3.2 has actions for a maximum of one RPI per bank inoperable. Since there are two [RPIs inoperable] in one bank, an entry into TS 3.0.3 is required. "Power reduction was initiated at 0502. "Repairs are currently in progress and [the licensee] anticipates correction prior to completion of the power reduction." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM NIELSEN TO HUFFMAN AT 0755 EDT ON 01/10/08 * * * The licensee reports that repairs have been completed to RPI B-10 and it has been returned to service. Technical Specification 3.0.3 was exited at 0625. Reactor power has been returned to 100%. The NRC Resident Inspector will be notified. The R2DO (Ayres) has been informed. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2008-01-10
43887 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2008-01-09 16:30 | 2008-01-09 18:43 | 2008-01-09 | ERDS FAILED TO DISCONNECT DURING TEST "Unit 3 was conducting a communication test of the Emergency Data Response System (ERDS). Following the test of the ERDS system, the ERDS modem would not disconnect with the NRC. The ERDS modem was disconnected in an effort to not overload the NRC communication system. The modem was disconnected at 16:30 EST on 1/9/2008. This constitutes a major loss of emergency assessment capability in accordance with 10 CFR 50.72 (b) (3) (xiii). The cause for the ERDS modem to auto-redial is not known. The ERDS link will be disconnected until the cause for the modem to auto-redial is determined and corrected. Follow-up NRC OC notification will be made when the ERDS link is re-established." The vendor is on site. The licensee has notified the resident inspector. *** UPDATED ON 1/9/08 AT 2122 EST BY EDDIE NEVILLE TO KARL DIEDERICH *** The ERDS modem has been repaired, tested satisfactorily, and returned to service. The licensee will notify the resident inspector. R2DO (Ayres) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-09
43886 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2008-01-08 11:42 | 2008-01-08 20:33 | 2008-02-20 | POTENTIAL LOCA INJECTION FLOW RATE ISSUE "At 11:42 CST, a condition report was initiated that questioned the specified flow path for simultaneous hot and cold leg injection following a large break loss of coolant accident (LOCA). When an unisolated LOCA event exists, simultaneous hot leg and cold leg injection should be implemented if the plant cannot be placed on shutdown cooling within six hours of the LOCA initiation and RCS pressure is less than 120 psia. The procedure is implemented at five and one-half hours to provide adequate time to align simultaneous hot/cold leg injection before the six hour time limit. Injecting to each side of the reactor vessel at an injection rate greater than 165 gpm, ensures that fluid from the reactor vessel (where the boric acid is being concentrated) flows out of the break regardless of the break location and is replenished with a dilute solution of borated water from the other side of the reactor vessel. The action is taken between 5.5 and 6 hours after the LOCA in order to ensure that the buildup of boric acid is terminated well before the potential for boric acid precipitation occurs which could restrict coolant flow through the core. Once the RCS is refilled, the boric acid is dispersed throughout the RCS via natural circulation. If entry into shutdown cooling system operation is anticipated before the 5.5 hour limit, then the realignment to hot/cold leg injection is unnecessary. "The potential concern is associated with a charging line thermal relief valve CH-202 bypassing flow from hot leg injection and preventing the required flow rate needed to prevent boron precipitation from occurring. A minimum injection rate of 147 gpm to the cold legs and 159 gpm to the hot legs is required to prevent boric acid precipitation. Total hot leg injection flow is measured at FIA-236. Cold leg injection flow is the total of the four HPSI flow instruments, FI-313, FI-316, FI-319, and FI-322 with 50 gpm the minimum flow indication. A total cold leg injection flow of at least 200 gpm ensures at least 150 pm flow into the core, assuming 25% spillage out the break. This meets the required minimum of 147 gpm. It could not be determined through a review of the design basis documents and associated calculations what, if any, bypass flow is assumed through CH-202. "Current procedural guidance in the emergency operating procedures is to align a high pressure safety injection pump to the charging header and provide hot leg injection from auxiliary pressurizer spray valves attached to the charging headers through the pressurizer and into the hot leg. The current procedural guidance does not isolate CH-202 and due to the location of flow instrument FIA-236, it cannot be guaranteed that all the flow through the charging system is being injected into the hot leg or being diverted through the normal charging line. As a result the potential existed which could have prevented the fulfillment of the safety function of a system needed to remove residual heat. Therefore this report is being made in reference to 10 CFR 50.72 (b) (3) (v) (B). "Efforts are continuing to review design basis documents and calculations to determine if bypass flow was assumed past CH-202 when determining the minimum hot leg injection rate. As a compensatory measure, Operations management has restricted the use of hot and cold leg injection via the charging header until the design basis review confirms the adequacy of the current procedural guidance or the procedural guidance is revised. Pre-approved alternative methods will be utilized via the emergency operating procedures to perform simultaneous hot and cold leg injection if required." No LCO condition exists. The licensee notified the NRC Resident Inspector. * * UPDATE FROM ERICK MATZKE TO JOHN KNOKE AT 1619 EST ON 02/20/08 * * "On January 8, 2008, (Event Number 43886) Fort Calhoun Station reported that there could be a potential reduction of injection flow to the hot leg during Long Term Core Cooling (LTCC) simultaneous hot and cold leg injection. The charging line thermal relief valve/check valve CH-202 could potentially divert flow from hot leg injection and reduce hot leg flow below the required flow rate needed to prevent boron precipitation from occurring. On January 8, 2008 it could not be determined through a review of design basis documents and associated calculations if bypass flow has been assumed through CH-202. "Divergence of flow through CH-202 would result if a valve failure occurred. Assuming flow is diverted through CH-202, the operators would not realize that flow was going through the wrong flow path (cold leg) as their flow indication (FE-326) is located upstream of where the flow path to the hot leg and cold legs branch off. Therefore, there was nothing to alert the operator to isolate CH-202 or go to alternate hot leg injection. Previous procedural guidance was not adequate to address this condition. Current procedural guidance is adequate to address this condition as the procedures now require isolating CH-202 for LTCC. "A reanalysis was performed to evaluate the required flow rate needed to prevent boron precipitation and ensure adequate LTCC. Calculations performed assumed full flow (failure) through CH-202. Under postulated design scenarios it was determined that adequate flow would have been provided to the hot legs during simultaneous hot and cold leg injection during LTCC. The calculations determined that under the evaluated scenarios, divergence of flow through CH-202 was acceptable, and that the requirements to maintain adequate flow to the core for LTCC decay heat removal and boron flushing would have been met. "As a result of the analysis that were performed, it has been determined that the system was capable of performing its design function even under bypass flow conditions through CH-202. Therefore, this event is NOT reportable under 10 CFR 50.72( b) (3) (v) (B) as previously reported." The licensee notified the NRC Resident Inspector. Notified R4 DO (Miller) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2008-01-08
43885 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2008-01-08 10:40 | 2008-01-08 16:47 | 2008-03-06 | RCIC INOPERABLE DUE TO MIN FLOW VALVE INABILITY TO REPOSITION "This report is being made in accordance with 10 CFR 50.72 (b) (3) (v) due to the Reactor Core Injection Cooling (RCIC) system being determined to be inoperable on 01/08/08 at 1040 EST. During a planned RCIC system outage, an instrument calibration surveillance identified a flow switch failure that would have prevented automatic closure of the pump minimum flow valve. Insufficient data is immediately available to assess the ability to achieve design basis flow rates with the minimum flow valve open. This event is an eight-hour notification. The RCIC instrument is currently under repair and will be completed prior to return to service. "Plant is in a stable condition. Investigation is continuing. "The resident NRC inspector has been notified of this event." This event places them in a 14-day LCO per ACT-1-08-002. HPCI verified operable. * * * UPDATE FROM RICHARD PROBASCO TO HOWIE CROUCH ON 03/06/08 @ 1656 EST * * * BASIS FOR RETRACTION: "Event Notification 43885 was conservatively made to ensure that the Eight-Hour Non Emergency reporting requirements of 10 CFR 50.72 were satisfied pending the evaluation of RCIC System operability. "On 1/8/08, during performance of Attachment 5 to 8.E.13, 'RCIC System Instruments Calibration', RCIC flow switch FS-1360-7, contact number 2 failed to close as expected on increasing test pressure. This switch is expected to close while increasing test pressure between 13.7 to 14.3 inWC [inches of Water Column]. Contact number 2 closes when RCIC flow exceeds 100 gpm signaling [minimum] flow valve MO-1301-60 to close. Failure of the switch to close prevents automatic closure of the [minimum] flow valve on a system flow of 100 gpm increasing. Failure of the [minimum] flow valve to close during RCIC system operation would allow about 70 gpm to 170 gpm of RCIC pump discharge flow to go directly to the torus bypassing the reactor vessel. "The switch was replaced and the flow switch was returned to service. The defective switch was evaluated and the cause of the failure was determined to be carbon buildup on the switch contacts. "A functional failure review was performed to assess the impact of the flow switch failure on the RCIC System design basis functions. The RCIC System is required to automatically provide makeup water to the reactor vessel following vessel isolation. This review identifies that 400 gpm is adequate to meet reactor vessel makeup requirements. With the flow controller in 'AUTO' and the minimum flow valve open, the flow controller would increase turbine speed until the flow rate setpoint of 400 gpm is achieved. Based on evaluation of the RCIC System flow controller configuration, turbine speed limits, and hydraulic modeling, it was determined that the required 400 gpm flow rate could have been delivered under worst case conditions with a failed open minimum flow valve. "These evaluations concluded that the RCIC System was capable of performing its intended safety functions during the time when FS-1360-7 failure prevented automatic closure of the pump minimum flow valve. The RCIC System would have started and supplied design basis flow to reactor vessel under design basis conditions. Thus there would have [been] no impact on nuclear safety. Therefore, this event was not reportable pursuant to 10 CFR 50.72(b)(3)(v). "Event Number 43885, made on 01/08/2008, is being retracted." The licensee will be notifying the NRC Resident Inspector. Notified R1DO (Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-01-08
43884 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2008-01-06 11:00 | 2008-01-06 15:22 | 2008-03-04 | HPCI DECLARED INOPERABLE DUE TO FAILED SURVEILLANCE TEST "During HPCI pump operability surveillance in preparation for a system outage, the system failed to achieve rated flow and pressure in the time required by procedure and Tech Specs. The procedural requirement is <49 seconds and the Tech Spec requirement is < 50 seconds. The system achieved rated flow and pressure in 54 seconds. The system outage has been delayed until troubleshooting plans can be developed and implemented." The licensee notified the NRC Resident Inspector. * * * RETRACTION BY K. LONG TO R. ALEXANDER AT 1109 EST ON 03/04/2008 * * * "The initial notification was made as a result of the failure of HPCI to meet its response time of 50 seconds as defined in the Technical Requirements Manual (TRM) due to a degraded component. Failure to meet the operability procedure requirements resulted in the high pressure coolant injection (HPCI) system being considered inoperable. Since HPCl is a single train system, its inoperability was the event that warranted a notification to meet the following reporting requirement: "10 CFR 50.72(b)(1)(v) Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems needed to: (D) Mitigate the consequences of an accident. "An additional review and evaluation of the licensing basis was performed and demonstrated that the procedural required response time was set conservatively. As expected, the licensing basis does not require or assume any specific start time and HPCl is not credited in the accident analyses. The acceptance criterion contained in the TRM is within licensee control via the 10 CFR 50.59 process. Consequently, the TRM criterion was revised to 75 seconds to retain a value to assure continued monitoring and trending of HPCl performance in order to recognize and prevent continued performance degradation. Additionally, it is reasonable to conclude that HPCl would have completed its mission time of 4 hours despite the degraded condition of the EGR [Electronic Governor Remote] that caused the initial slower response time. This is based on the fact that HPCl started and ran at rated flow and pressure for approximately 39 minutes prior to shutdown with no problems identified. This removes any questions regarding its ability to restart and run based on demand during its mission time of 4 hours. An industry expert on this system and the engineer from the vendor that supports this system concurred with that conclusion. "Since this subsequent review and evaluation determined that the slower response time did not render HPCl inoperable, no single train failure of HPCl occurred. The system was fully capable of performing its intended safety functions during the event timeline. Based on this information this notification serves to retract notification # 43884 made on 1/06/08." The licensee notified the Resident Inspector of this retraction. Notified the R2DO (Musser). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2008-01-06
43883 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2008-01-05 09:00 | 2008-01-05 17:03 | 2008-01-05 | SAFETY EQUIPMENT FAILURE OF THE CRITICALITY ALARM SYSTEM "SNM-124 Section 12.6.4 requires that criticality alarm system detector pairs must generate an alarm signal when both detectors in a pair exceed their trip point, or when one detector is in a fault condition while the other exceeds the alarm trip point. "During testing, 2 of 18 detector pairs did not generate an alarm signal in all modes as discussed above. "In the event of a criticality, 2 detector pairs may not have generated an alarm signal. "During 27 December 2007 through 29 December 2007, a programmable logic controller (PLC) monitoring system was attached to the critical alarm system components. On 29 December 2007, all detector pairs were satisfactorily tested that they would generate an alarm signal when required. "During 31 December 2007 until 5 January 2008, limited SNM operations were conducted at the plant. Suspect equipment faults occurred during the time frame from 29 December 2007 to 5 January 2008 due to unknown cause. "Troubleshooting revealed an equipment fault in each detector pair that failed during testing. These faults have been corrected and the detector pairs satisfactorily retested." The two (2) affected detector pairs are located in the NDA North & South and Building 311 North & South. There were no recorded trouble alarms generated by the operable detector in the affected areas during the week when the system was not functioning properly. Also, there is no indication of tampering in that the fault was identified as loose wiring/connections inside locked cabinets accessible to authorized personnel only. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-01-07
43882 | 0 | HACKLEY HOSPITAL |  |  |  |  | 2007-12-13 | 2008-01-04 15:20 | 2008-01-04 | PATIENT RECEIVED LESS THAT PRESCRIBED DOSE "On 12/13/07, a patient was scheduled for a thyroid ablation with 100 mCi of NaI-131. The dose arrived with 3 capsules totaling 95.5 mCi. The nuc med tech was unaware that the package contained 3 capsules due to lack of visualization. The nuc med tech administered 1 capsule with the activity of 21.39 mCi of NaI-131. The package was sent back to the pharmacy with the remaining 2 capsules of approximately 70 mCi of NaI-131. "The mistake was recognized the next morning. The radiologist was made aware of the situation and the patient notified immediately. The patient returned the morning of 12/14/07 and was administered the remaining 2 capsules totaling 69.7 mCi of NaI-131. "Overall, the patient received a total of 91.09 mCi of Nal-131 over the course of 17 hours." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2008-01-10
43880 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2008-01-04 02:50 | 2008-01-04 08:05 | 2008-01-04 | PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING REFUELING "While in Mode 6 with the Reactor Head in place and fuel in the Reactor Vessel, weld overlay was in progress on the common Decay Heat Suction line from the Reactor Coolant System. The Reactor Coolant System is in a drained condition with RCS level approximately 24 inches above the Hot Leg Centerline. During the first weld pass on the suction line weld located in Containment, the welding operator noticed water seeping from the weld. Visual inspection revealed a small leak. The leakage is too small to quantify the leakrate. Surface examinations prior to welding revealed no abnormal conditions or leakage. Welding operations on this weld have been suspended. Planned Refueling activities continue to defuel the reactor vessel. "One train of Decay Heat Removal remains in service providing core cooling. The second train is aligned in standby for Decay Heat Removal. Both Trains of Decay Heat Removal have been declared inoperable due to this leak, however both trains of Decay Heat Removal remain functional." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2008-01-04
43879 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2008-01-02 03:31 | 2008-01-02 10:45 | 2008-01-02 | LOSS OF TSC RADIO SYSTEM DUE TO BATTERY BACKUP DEPLETION DURING POWER SUPPLY CHANGEOUT "A condition is being reported per Technical Requirements Manual 13.13.1 Emergency Response Facilities Required Action B.2. The functionality of the TSC was lost due to inadvertent removal of electrical power from the radio system that provides the communication function between the TSC and Field Monitoring Teams. Normal power supply was authorized to be removed at 0331 on 01/02/2008 and condition was discovered when battery power depleted. Electrical power has been restored as of 0956 on 01/02/2008 and operability of communication capability has been verified. " NRC Resident Inspector has been notified." | 97 | 98 | 0 | 97 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-02
43878 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-12-31 21:40 | 2008-01-01 01:58 | 2008-01-01 | UNIT 3 AUTOMATIC SCRAM DUE TO MAIN GENERATOR LOAD REJECT SIGNAL "On 12/31/07 at 2140 the Unit 3 reactor scrammed due to turbine generator load reject signal on the Main Generator. The cause of the load reject signal is unknown and the investigation is continuing. All systems responded as expected to the load reject signal. Six Main Steam Relief valves (MSRVs) opened momentarily and then reclosed. Subsequently, reactor pressure was automatically controlled by the Main Turbine Bypass valves. No Emergency Core Cooling System (ECCS), nor Reactor Core Isolation Cooling (RCIC) reactor water level initiation setpoints were reached, and reactor water level is being automatically controlled by the Feedwater system. This report is being made as required by 10CFR 50.72(b)(2) due to the actuation of the Reactor protection System. "Refer to BFN PER number 135878." All control rods fully inserted into the core, and all safety systems are operable. PCIS group isolations were received for groups 2, 3, 6, and 8. There were no grid abnormalities at the time of the load reject, and the event had no effect on Unit 1 or 2. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2008-01-01
43877 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-12-31 21:10 | 2008-01-01 01:15 | 2008-01-01 | ERDADS FAILURE FOR SEVENTY MINUTES "This is an eight hour non-emergency notification to the NRCOC due to a major loss of emergency assessment capability (10CFR50.72(b)(3)(xiii)). "At approximately 2110 on 12/31/07 it was discovered that the Unit 4 ERDADS [Emergency Response Data Acquisition Display System] failed. This impacted the ability of the ERDS link to transmit valid data. The U4 ERDADS was restored at 2220 on 12/31/07. The system was unavailable for 70 minutes. The ERDS link to the NRC and U4 ERDADS are now fully Operable. "U4 ERDADS failed due to corrupted shared memory on both PEDS (Plant and Environmental Data System). The PEDS units were de-energized to clear the corrupted shared memory and then reset successfully." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2008-01-01
43876 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2007-12-31 08:40 | 2007-12-31 13:38 | 2007-12-31 | DEATH OF AN EMPLOYEE OUTSIDE THE PROTECTED AREA "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "At approximately 06:40 MST on December 31, 2007, at the water reclamation facility for the Palo Verde Nuclear Generating Station, an employee died. The death was not related to activities impacting or related to the safety of the public or other onsite personnel. Specifically, an individual collapsed and was promptly examined by a Palo Verde Emergency Medical Technician (EMT). An air evacuation was ordered however, prior to air evacuation the individual expired. The death does not appear to be work-related nor the result of an accident. "The individual was outside of the Radiological Controlled Area and no radioactive material or contamination was involved. "Palo Verde has not observed any heightened public or media concern as a result of the death. Since the death is apparently unrelated to Palo Verde's industrial or radiological health and safety, no news release is planned. "The individual's name has not yet been released, pending notification of next-of-kin. "The Arizona Division of Occupational Safety and Health was notified of the death at 0840 MST. "The Maricopa County Sheriff's Office is conducting a routine investigation into the death." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-12-31
43875 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-12-31 05:49 | 2007-12-31 09:28 | 2008-02-29 | SAFEGUARDS REPORT - POTENTIAL VULNERABILITY TO A SAFEGUARD SYSTEM "Safeguards system degradation related to the monitoring and detection of a PA boundary. Compensatory actions taken upon discovery. Contact the Headquarters Operations Officer for details." The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 2/29/2008 AT 1226 FROM BRUCE FRANZEN TO MARK ABRAMOVITZ * * * "DNPS implemented compensatory measures in accordance with the Security Plan and determined that this event is not a 1 Hour Reportable event but is a 24 Hour Loggable Event." The licensee notified the NRC Resident Inspector. Notified the R3DO (Passehl) and 73.71 group (e-mail). | 0 | 97 | 99 | 0 | 97 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-12-31
43874 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2007-12-29 01:31 | 2007-12-29 07:54 | 2007-12-29 | MANUAL REACTOR TRIP WHEN FIVE CONTROL RODS UNEXPECTEDLY DROPPED 20 INCHES "At 2320, on 12/28/07, a Reactor Startup was commenced. At 0025, on 12/29/07 Subgroup #15, of Regulating Group #3, was placed on the hold bus. Placing the Subgroup on the hold bus was a pre-planned action that was briefed prior to the reactor startup, in accordance with an approved interim engineering disposition. The interim engineering disposition was written and approved on 12/28/07 for concerns over CEA #1, of Subgroup #15, dropping into the core unexpectedly. Subgroup #15, of Regulating Group #3, contains five CEA's [CEA # 60, 62, 64, 66 and 1]. At 0047, all Regulating Group CEA's, with the exception of Regulating Group #5, were placed at the Upper Electrical Limit [136 inches withdrawn]. Regulating Group #5 was at 120 inches withdrawn in preparation for diluting to criticality. At 0107, the dilution to criticality was commenced. At 0131, all 5 CEA's in Subgroup #15 slipped into the core approximately 20 inches. A manual reactor trip was then ordered by the unit supervisor. 2-EOP-1, 'Standard Post Trip Actions' was then performed. The unit was borated to shutdown boron concentration. All Safety Functions were met satisfactorily and 2-EOP-1 was exited. The unit was in Mode 3 approaching Mode 2 at the time of the trip. The unit is currently stable in Mode 3, Hot Standby." Reactor coolant pump heat is being removed using the atmospheric steam dumps. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-12-29
43873 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-12-28 17:54 | 2007-12-28 19:58 | 2007-12-28 | AUTOMATIC TRIP ON FAILURE OF STATION POWER TRANSFORMER "This 4 hour notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) to report that Salem Unit 1 has experienced an automatic reactor trip. The trip was initiated by failure of 12 Station Power Transformer (SPT). The cause of the trip was the loss of two Reactor Coolant Pumps (RCP) (13 and 14). These RCPs were powered from 'F' and 'G' group busses (non safeguards), which were powered by 12 SPT. "Post trip the following occurred: 11, 12 & 13 Auxiliary Feed Water (AFW) Pumps [automatically] started after the trip due to valid steam generator low levels (14%) as expected. The automatic start of the Auxiliary Feedwater System due to a valid steam generator low level is an ESF actuation and is an 8 hour report in accordance with 10 CFR 50.72 (b)(3)(iv)(B). 13 AFW pump was tripped [in accordance with] the Emergency Operating Procedure and will be returned to an operable condition following recovery of steam generator levels. "All control rods fully inserted following the trip. No ECCS actuation occurred. There was no major equipment out of service prior to the event. No injuries resulted from this event. "Salem Unit 1 is currently in Mode 3. Reactor Coolant System pressure is at 2235 PSIG and temperature is at 547 degrees with decay heat removal via the Main Steam Dump System. Unit 1 has no active shutdown [Technical Specification] action statements in effect. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-12-28
43872 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-12-28 | 2007-12-28 11:34 | 2007-12-28 | MEDICAL EVENT - INCORRECT ISOTOPE ADMINISTERED "Doctor ordered iodine (didn't specify isotope) thyroid uptake & scan for a patient. This licensee uses I-123 for this purpose. Patient was incorrectly scheduled for a I-131 (2.2mCi) whole body scan and that was done on 12/17/07. Error was discovered 12/25. Patient & doctor have been notified and no adverse health effects are expected. Licensee will submit a written report. Scheduling personnel will be re-educated to verify an order before scheduling patients for a procedure. The tech will be re-educated to read the script before dosing a patient. Any further action on this incident is referred to Radioactive Materials." Incident Number FL07-205 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2008-01-03
43871 | -1 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2007-12-28 04:50 | 2007-12-28 06:46 | 2008-03-26 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN - DROPPED CEA "At 0347 on 12/28/07, during plant start up from a refueling outage while In Mode 2, one control element assembly (CEA) dropped to the bottom of the core from the upper electrical limit. The reactor was not critical at the time. Technical Specification LCO 3.1.3.1 action (e) was initiated to proceed to Mode 3 at 0450 while actions are taken to repair and retrieve the CEA. This four hour non-emergency report is being made pursuant to 10 CFR 50.72(b)(2)(i), the 'Initiation of any nuclear plant shutdown required by Technical Specifications'." The licensee notified the NRC Resident Inspector. * * * RETRACTED ON 03/26/2008 AT 1433 EDT BY JACK BREEN TO DAN LIVERMORE * * * The licensee is retracting this report based on the following: "At 03:47 on 12/28/07, during plant start up from a refueling outage while in Mode 2, one control element assembly (CEA) dropped to the bottom of the core from the upper electrical limit. The reactor was not critical at the time. Technical Specification LCO 3.1.3.1 [Action E] was initiated to proceed to Mode 3 at 0450 while actions were taken to repair and retrieve the CEA. This event was reported as a four hour non-emergency report pursuant to 10CFR 50.72(b)(2)(i), 'The initiation of any nuclear plant shutdown required by Technical Specifications.' Upon further review of the event, and since the Unit was not critical in mode 2 at the time of the event, this event is not considered reportable in accordance with the guidance provide in NUREG-1022, Rev. 2, 'Event Reporting Guidelines 10CFR50.72 and 50.73,' in which 'The initiation of any plant shutdown' does not include mode changes required by TS if initiated after the plant is already in a shutdown condition. As such this notification is being retracted. The Site Resident has been notified of this retraction." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-12-28
43870 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-12-27 20:04 | 2007-12-28 02:24 | 2007-12-28 | LOSS OF SPDS CAPABILITY FOR GREATER THAN ONE HOUR "At 2004, while performing a routine surveillance (Manual Scram Functional Test) the operator performing the surveillance identified that the Plant Management Information System (PMIS) terminals in the control room did not respond as expected to the surveillance. The expected response would have displayed an 'RPS channel trip' message. "PMIS is the computer system which implements the Safety Parameter Display System [SPDS] and dose determination. Dose determination was available using manual calculations. This system also supports the ERDS (Emergency Response Data System) and the core monitoring system. "Additional investigation found that the PMIS displays had stopped updating at 1950. Attempts to cause the system to fail over to the backup computer (the 'A' computer) thus restoring functionality were unsuccessful. Information Technology (IT) personnel were called and responded to the plant. IT personnel manually restarted the 'A' computer and switched the input/output (I/O) devices to the 'A' computer. Personnel have verified the Technical Support Center and Emergency Offsite Facility systems are also functional. Functionality of the SPDS system and its related systems was verified to be restored at 2330. The backup system ('B') remains out of service and will be addressed tomorrow. "This event is reported under 50.72(b)(3)xiii, Any event which results in a major loss of emergency assessment capability." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-12-28
43869 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2007-12-06 | 2007-12-27 19:23 | 2007-12-28 | AGREEMENT STATE REPORT - MARYLAND - MISSING COBALT-57 CALIBRATION SOURCES The State of Maryland was notified on 12/27/07 by one of its licensees that two Co-57 calibration sources were missing. The two sources were 0.9 mCi and 1.3 mCi (2.2 mCi total) and were used by a mobile nuclear medicine service licensee, DigiRad, to calibrate nuclear imaging cameras before use. The sources were lost in the process of returning them to the manufacturer, International Isotopes, in International Falls, Idaho. The DigiRad RSO stated that the two Co-57 sources were packaged and shipped via FedEx ground out of Linthicum Heights, Maryland on December 6, 2007. The package arrived at International Isotopes on December 10. For reasons unknown at this time, the package was not opened at International Isotopes until December 21. It was reported by DigiRad that when the package was opened at International Isotopes, the shielded shipping container was inside but no sources were found. Again, for reasons unknown at this time, International Isotopes did not contact DigiRad to report that there were no sources in the shipping container. DigiRad contacted International Isotopes to follow-up on the shipment on December 26 and was informed that the sources were not in the shipping container when it was opened at International Isotopes. The shipping package was reported to have been intact and undamaged and there was no evidence that the package had been opened or tampered with during shipment. DigiRad informed the State that it has interviewed the individual who packaged the sources and there is no indication that he may have inadvertently left them out of the shipping container. A search of the area at DigiRad has not turned up the sources. DigiRad has no information on what International Isotopes has done to confirm that the sources were not actually in the container at the receiving end. * * *UPDATE FROM THE STATE (MANLEY) TO HUFFMAN AT 1320 EST ON 12/28/07 * * * The RSO from DigiRad notified the State of Maryland that the sources have been located at International Isotopes and confirmed by serial numbers. It appears that the sources were actually shipped to DigiRad in November of 2007. The employee that shipped the sources in November is no longer employed at DigiRad and has not been interviewed. It is suspected that the DigiRad employee that shipped what he thought were the sources on December 6 did not actually open the shielded source container to confirm that the sources were present. The DigiRad RSO now believes that the source container shipped to International Isotopes on December 6 was empty. Therefore, based on confirmation between DigiRad and International Isotopes, the two Co-57 calibration sources are no longer missing and have been confirmed (via serial number) to be present at International Isotopes. Investigation into the source tracking and accountability issues will be followed up on by the State. Notified R1DO (Perry), R4DO (Pruett), and FSME (Wastler) have been notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2008-01-01
43868 | -1 | R. M. WESTER CONSULTANTS |  |  |  |  | 2007-12-26 10:00 | 2007-12-27 12:27 | 2008-01-10 | DAMAGED MOISTURE DENSITY GAUGE Radiation Health Physics consultants, R.M. Wester, notified the NRC of an event in the State of Missouri that resulted in damage to a Humboldt Soil Density Gauge (Model EZ 5001, S/N 693) containing 40 mCi Am-241/Be and 10 mCi Cs-137. The gauge is licensed to Jacobi Geotechnical Engineering. The consultant stated that the event took place at a construction site in Pezley, MO. The gauge was run over by a backhoe. There was some damage to the plastic housing of the gauge. The source rod was undamaged. The source rod was wipe tested with negative results. In addition, soil samples at the incident location also tested negative. R.M. Wester has taken possession of the gauge and will ship it to Humboldt for repairs. The licensee notified the NRC Resident Inspector. * * * RETRACTION BY JAMES PYATT TO KARL DIEDERICH ON 1/10/08 AT 1630 * * * "Wester responded to the site at the time of the accident, and found no indication of leakage. The gauge was shipped to the manufacturer, Humboldt. Humboldt reports there is no leakage, and there is no indication of loss of safety function." R3DO (Hills) and FSME (Bubar) informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-12-27
43867 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2007-12-26 15:22 | 2007-12-26 21:10 | 2007-12-26 | MINOR FIRE ON COOLING TOWER FAN SHROUD "On Wednesday, December 26, 2007, at approximately 15:22 MST, a fire occurred in a fan shroud for Palo Verde Nuclear Generation Station Unit 3 cooling tower number 3. The fire was knocked down by the on site fire department using the fire truck water cannon. Smoldering continued between fan shroud segments. "Offsite assistance was requested in the event a pumper truck was needed due to the elevation of the cooling tower fan area. While the pumper truck was not needed, offsite personnel did assist in getting a fire hose to the top of the cooling tower. "No press release is planned, but media attention has already been observed in response to media monitoring communications on local police/fire scanners. "Palo Verde Unit 3 is shutdown and in Mode 5 in its thirteenth refueling outage. The cause of the fire is under investigation. Maintenance activities were in progress on the cooling tower at the time of the fire. The fire was completely extinguished at 16:45 hours and no emergency plan classification was declared or required as a result of the fire. The cooling towers are located on the owner control area outside of the protected area. "The NRC Resident Inspector has been notified of the event and this ENS informational notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW | [5 empty] | 0 | 2007-12-26
43866 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-12-25 21:10 | 2007-12-25 23:22 | 2007-12-25 | AUTOMATIC REACTOR TRIP DUE TO TRIP OF "B" REACTOR COOLANT PUMP "On 12/25/07 at 2110 hours EST, Unit 2 tripped from 100% power due to a trip of the 'B' Reactor Coolant Pump. The reactor trip 1st out annunciator was 'Loss of flow, power >30%'. All control rods fully inserted. This event is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater [AFW] pumps auto started due to the event and the steam driven AFW pump subsequently tripped on overspeed. The steam driven AFW pump was reset and placed in service. The ESF [Engineered Safety Function] actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). The unit is currently in mode 3 and [the licensee is] investigating the cause of the ground on the 'B' reactor coolant pump." The plant is at normal operating pressure and temperature. The electrical grid is stable and supplying plant loads through the startup transformer. Decay heat is being removed via the steam dumps to the condenser with feedwater being supplied via the normal path. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-12-25
43865 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2007-12-24 11:00 | 2007-12-24 15:40 | 2007-12-24 | LOSS OF TELECOMMUNICATIONS CAPABILITY DUE TO DAMAGED FIBER OPTIC CABLE "At approximately 11:00 AM Eastern Standard Time, the Harris Nuclear Plant (HNP) identified the inability for offsite agencies to contact the plant using the telecommunications systems. This condition was the result of a damaged fiber optics cable remote from the plant site. No information is available regarding the cause of the damaged cable. The ability for HNP to contact offsite agencies and HNP Emergency Response Organization was maintained at all times. Alternate methods to contact HNP were established for selected agencies. The telecommunication capabilities were restored at 2:11 PM Eastern Standard Time." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-12-24
43864 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-12-23 03:58 | 2007-12-23 19:02 | 2007-12-23 | SMALL UF6 PROCESS LEAK "On 12/23/2007 at 0358 the C-333 unit 3 cell 1 PGLD (process gas leak detection) head (YE-5) at stage 5 actuated. Along with the PGLD actuation a seal alarm and a vibration alarm on stage 7 were received. A nearby operator on the cell floor responded to the alarm and observed a small UF6 release from the stage 7A seal cavity. To stop the release the cell was immediately shut down from the ACR which lowered the cell's pressure to below atmospheric pressure. The exact amount of material released has not been determined. Checks by health physics personnel found the actual amount of UF6 released was not significant and resulted in a relatively small area of contamination on the end of the compressor near the seal that failed and on the floor immediately around the end of the compressor. "The actuated PGLD head is a Q safety system component. At the time of the incident the cell was operating in a mode which required the system to be operational. This is being reported based on SAR 6.9 Table 1, J2 (unplanned actuation of a Q safety system) and 10 CFR 76.120(c)(1)(i) (unplanned contamination event). "The NRC Resident Inspector has been notified of this event. "PGLD Problem Report Nos. ATRC-07-3433; PGLD Event Report No. PAD-2007-022; NRC Event Number 43864" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | OTHER UNSPEC REQMNT | [8 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2007-12-23
43863 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2007-12-21 14:45 | 2007-12-21 16:57 | 2007-12-21 | RCS PRESSURE BOUNDARY LEAKAGE ON RCP SEAL INJECTION LINE "With unit shut down in Mode 3 with all CEAs inserted preparing for startup, RCS Pressure Boundary leakage was identified. Leakage appears to be from a weld to Reactor Coolant Pump Seal Injection Line. Leakage is much less than one gallon per minute. Implementing Technical Specification LCO 3.4.6.2 Reactor Coolant System Operational Leakage Action (a) to place the unit in Cold Shutdown within the following 30 hours. Commencing plant cooldown for repair." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-12-21
43862 | 0 | KEY TECH |  |  |  |  | 2007-12-19 10:00 | 2007-12-21 16:07 | 2007-12-27 | DAMAGED MOISTURE DENSITY GAUGE The Troxler moisture density gauge was being used at a construction site in Newark, New Jersey near Jackson Street. The gauge was not in use and the source rod was in the safety position when a roller rolled over part of the gauge. The area around the gauge was cordoned off until the RSO performed radiation surveys and performed a wipe test. The survey indicated no contamination or leakage. The wipe test was shipped to Troxler and verified no radioactive material leakage. The gauge is currently in the licensee's gauge storage room awaiting disposition. Troxler Moisture Density gauge Model 3440 Serial Number 16356 One Cs-137 source (typically 8 milliCuries) * * * UPDATE FROM FONG CHEN TO HOWIE CROUCH @ 1430 EST ON 12/27/07 VIA TELEPHONE * * * The licensee wanted to clarify some statements made in the original report. The gauge was in use at the time of the incident with the source rod in the testing position. After the gauge was hit, the licensee was able to retract the source into the shielded (safe) position. A leak test swipe was performed and the swipe was overnighted to Troxler. Troxler reported that sample results were negative for leakage. Notified R1DO (Perry) and FSME (Wassler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-12-21
43861 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-12-11 | 2007-12-21 14:49 | 2007-12-23 | MASSACHUSETTS AGREEMENT STATE REPORT - LOST SHIPMENT OF IRIDIUM-192 SOURCES "The RSO for QSA Global called to report a missing shipment. The shipment was dispatched from QSA on 12/5/07 via Roadway. Roadway has a signed receipt (dated 12/11/07) from LAN Cargo in Miami, FL. LAN Cargo cannot locate the shipment in Miami. The initial notification was made to QSA on Tuesday morning, 12/18/07, and there was some initial confusion as Roadway said that it was delivered [LAN Cargo], and LAN Cargo said they did not know where it was. Official notification of the missing shipment was not made to QSA until yesterday, 12/20/07. As of today, the shipment is still missing and QSA notified MA RCP. "The shipment contains 4 sources containing a total of just under 800 curies of Ir-192. The investigation is on-going and more details will follow as they are received." The following additional information was obtained from QSA Global's RSO: Date Shipped: Dispatched from QSA on 12/5/07 via Roadway, PRO #100-971702-4, for LAN Cargo in Miami. Roadway has a signed receipt for the shipment from LAN Cargo, but LAN Cargo cannot locate the shipment in Miami. Customer: Caefe NDT, Rioja 4855, 2000 Rosairo (SF) Argentina RAM: Seven (7) IR-192 sources in four containers on a skid: 4066.3 GBq, 8572.9 GBq, 8025.3 GBq, and 8162.3 GBq. Status: The initial notification was made to QSA Tuesday morning and there was some initial confusion as Roadway said that it was delivered, and LAN said they didn't know where it was. It is a skid that weighs over 400 lbs, so it is not something that can be easily moved. Because of the initial confusion over the actual status, official notification of the missing shipment wasn't made to QSA until yesterday morning. As of today, it is still missing and therefore, QSA is making the formal notification to MRCP per 105 CMR 120.281. A second shipment bound for Lima, Peru was consigned to LAN Cargo on the same day and we are investigating whether the missing shipment went to Lima instead of Argentina. The licensee has also contacted the State of Florida. ILTAB (Sandler) and R2DO (Shaeffer) notified. * * * UPDATE PROVIDED BY STATE OF MASSACHUSETTS (BOB WALKER) TO JEFF ROTTON AT 1542 ON 12/23/07 * * * The shipment has been located at the Miami Roadway Express Terminal Dock. Notified R1DO (Henderson), FSME (Mohseni, Pangburn), IRD (Cruz), R2DO (Shaeffer), ILTAB (Sandler). Notified DHS (Steve York), DOE(Sal Morrone), FEMA (Erwin Casto), USDA (Amanda Jimenez), HHS (Jamie Whitt). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-12-26
43860 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-12-21 08:25 | 2007-12-21 12:31 | 2007-12-21 | SECONDARY CONTAINMENT BYPASSED FOR SHORT PERIOD "Annulus Exhaust Gas Treatment System (AEGTS) 'A' was removed from service (INOPERABLE) to obtain a charcoal sample. AECTS 'B' Train was the OPERABLE Train. At 0825 hours, the charcoal plenum for the 'A' train was opened to obtain a charcoal sample resulting in alarms for AECTS 'B' low flow and Annulus low differential pressure. Based on this indication AEGTS 'B' and secondary containment were INOPERABLE. AEGTS 'B' flow was restored to normal following closure of the charcoal plenum and annulus differential pressure was restored to normal at 0833 hours, restoring secondary containment. "AEGTS 'B' was declared operable at 0845 hours. Early indication is that a discharge damper in the AEGTS 'A' train had not operated properly. This condition was determined to be reportable in accordance with 10 CFR 50.72(b)(3)(V)(C) and (D), as condition that could have prevented the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the Consequences of an accident." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-12-21
43859 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2007-12-21 04:13 | 2007-12-21 07:14 | 2007-12-21 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO BOTH EDG'S BEING DECLARED INOPERABLE "This notification is being made to report a Technical Specification required shutdown due to Prairie Island Nuclear Generating Plant (PINGP) Train B Unit 1 emergency diesel generator (D2) being out of service for maintenance and Prairie Island Nuclear Generating Plant (PINGP) Train A Unit 1 emergency diesel generator (D1) being declared inoperable as a result of the Bus 15 load sequencer failure. "On 12/20/07, at approximately 2355 hours (CST), with PINGP Unit 1 in MODE 1, D2 out of service for maintenance activities, SP 1306, D2 Diesel Generator Relay Functional Test, was being performed. This surveillance test requires the performance of SP 1094; Bus 15 Load Sequencer Test which failed during the test. This resulted in the Bus 15 Load Sequencer being declared inoperable per T.S. 3.3.4 and D1 Diesel Generator being declared inoperable. With D2 and D1 EDG's inoperable entered TS 3.8.1.F which requires Unit 1 to be in Mode 3 within 6 hours. Unit 1 shutdown commenced at 0413. "Corrective actions for this event are in progress and are being tracked via the corrective action program." The NRC Resident Inspector was notified of this event by the licensee. | 35 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-12-21
43858 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-12-12 | 2007-12-20 19:03 | 2007-12-20 | CALIFORNIA AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The State provided the following information via email: [Deleted] of the City of Santa Rosa City Hall, Facilities Maintenance reported that a single tritium exit sign that was used at the facility located at 520 3rd Street, Santa Rosa, formerly owned by AT&T, and later sold to the City of Santa Rosa, was missing. The single Isolite Tritium Exit sign (S/N A3N1685) was listed on the inventory list but was not located when they took over the facility. [Deleted], the representative of AT&T acknowledged the loss and reported it to RHB on December 12, 2007. The inspector assigned to this issue will visit the facility in the very near future to investigate and determine if any of the Santa Rosa personnel are aware of the location of missing H-3 exit sign. CA Incident Number: 121207 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-12-25
43857 | -1 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-12-05 | 2007-12-20 16:45 | 2008-03-07 | WISCONSIN AGREEMENT STATE REPORT - LEAKING TRITIUM EXIT SIGN The State provided the following information via facsimile: "The licensee reported the discovery of a broken tritium exit sign on December 5, 2007, during an inspection. The sign had been damaged at some unknown previous date. The licensee had collected exit signs for disposal. A worker recalled having difficulty removing a sign and prying it off the wall. The frame broke and pieces fell to the floor. He also recalls sweeping up the pieces, including broken tubes and placing in normal trash. The unbroken tubes were collected, and the sign reassembled. The sign is currently bagged and stored in a secured storage area, pending disposal by a contractor. "DHFS intends to investigate. Staff will be present when the contractor arrives to wipe test and package all the exit signs for disposition." The licensee notified the state on December 19, 2007 via telephone and facsimile. WI Event Report ID No.: 070030 * * * UPDATE FROM RASHID SALIKHDJANOV TO HOWIE CROUCH @ 1637 EST ON 03/07/08 * * * "On December 20, 2007, Kimberly-Clark Corporation notified the DHFS [Department of Health and Family Services] of a damaged tritium exit sign. According to the licensee, the damage occurred on an unknown previous date during a collection of exit signs with tritium and the damage was not discovered until December 05, 2007. All collected exit signs were placed in secure locked storage room pending disposal. Licensee arranged with a contracted waste disposal company for disposal of the signs. "During an investigation of the event on January 15-16, 2008, a DHFS inspector reconstructed the event and interviewed the worker who damaged the tritium exit sign. The employee indicated that the damage happened in August 2006. He recalled having difficulty removing the sign and eventually had to pry it off the wall. When this was done the sign frame broke and various pieces fell to the ground. The pieces, including broken tubes, were swept up and placed in the normal trash. The broken tubes were collected and the sign reassembled. The damaged sign was placed in a plastic bag and turned in with the remaining signs that had been removed that day. The employee did not report the incident other than the frame was damaged during removal. A dose assessment performed by DHFS, indicated that the maximum uptake to the worker was 68 mCi of tritium (less than required 5 times the ALI of 80 mCi). DHFS wipe tests were performed at 3 points on the floor, where pieces of the exit sign, including broken tubes, would have fallen and one area ~20 feet above the floor. Results of the survey indicated that maximum contamination was 3970 dpm/100 cm [squared] on the floor. "The contracted waste disposal company wipe tested all signs and storage area contamination prior to disposal. Results of survey indicated that maximum contamination did not exceed 40dpm/100 cm [squared]. All exit signs, including the broken item, were shipped out on January 16, 2008. Licensee intends to contract with a consultant company to perform additional wipe tests of the accident area and to clean up the area if it is necessary. DHFS will close this event once the area has been decontaminated. Since the dose estimate was less than the 5 times the ALI, DHFS retracts the report to NRC Operations Center." Notified R3DO (Pelke) and FSME EO (Flanders). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-12-25
43856 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-12-20 07:00 | 2007-12-20 14:50 | 2007-12-20 | LOSS OF VARIOUS SYSTEMS AT EOF DUE TO LOCAL TELEPHONE SYSTEM PARTIAL T1 FAILURE "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) as an event that resulted in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g. significant portion of control room indication, Emergency Notification System or offsite notification system.) "At 0700 on 12/20/07, one of the five T-1 data lines to the Emergency Offsite Facility (EOF) was discovered to be out of service. This caused a loss of Safety Parameter Display System capability, the FTS 2001 system, Alternate Intercom system, and Low Band base radio (the primary Downwind Survey team radio) at the EOF. Computer terminals remained functional for calculating CNS Dose. All other Emergency Response Facilities were unaffected. "At 0826, the T-1 line was restored by repairing a line repeater. At 0948, all EOF equipment affected by the T-1 line were satisfactorily tested and verified to be operational. "The NRC Resident Inspector was notified of the loss and restoration of the T-1 line." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-12-20
43855 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2007-11-08 10:21 | 2007-12-20 13:35 | 2007-12-20 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of the containment isolation signals affecting more than one system. "On November 8, 2007, at 1021 hours, with Unit 2 shutdown for a planned mid-cycle outage to remove a defective fuel bundle and conduct other maintenance activities, two primary containment isolation valves in different systems closed unexpectedly. The valves closed during application of a clearance section that inadvertently created a false primary containment isolation signal. "None of the plant conditions which require PCIS Group 5 or 7 actuation (low reactor water level, high reactor pressure, high area temperature, etc.) existed; therefore, these actuations are considered invalid. "The following two primary containment isolation valve isolations/actuations occurred: - Residual Heat Removal shutdown cooling supply inside isolation valve (2RHS*MOV112, Group 5) - Reactor Water Cleanup supply from Reactor Coolant System and Reactor Pressure Vessel inside isolation valve (2WCS*MOV102, Group 7) "The valves functioned successfully as they cycled completely from full open to full closed. "The event was entered into NMP's corrective action program for evaluation and resolution. "The NRC Senior Resident Inspector has been notified of this report. "Reference corrective action document CR 2007-6769." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-12-20
43854 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2007-12-19 11:45 | 2007-12-19 14:57 | 2007-12-19 | MANUAL REACTOR SCRAM DUE TO LOWERING REACTOR LEVEL At 1145 EST, operators inserted a manual reactor scram due to lowering reactor water level after the 'A' main feedwater pump tripped. Prior to the scram, the plant was operating at reduced power due to removing the 'B' main feedwater pump from service for planned maintenance. Reactor water level was at 155" when the scram was initiated and lowered to 100" during the transient. Currently, reactor water level is at the normal operating band and is being maintained by the feedwater system. After the scram, all safety systems functioned as expected. There were no system isolations due to the transient. Electrical power is being provided by normal offsite sources via the startup transformer. Decay heat is being removed via the normal path through bypasses to the main condensers. Additionally, the licensee made an offsite notification to the New Jersey Department of Environmental Protection due to approximately 300 dead or distressed fish in the discharge canal. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 55 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) |  |  | 0 | 2007-12-19
43853 | 0 | INVENSYS PROCESS SYSTEMS |  |  |  |  | 2007-11-02 | 2007-12-19 14:41 | 2008-04-04 | PART 21 NOTIFICATION - FAILURE TO FULLY COMPLY WITH THE REQUIREMENTS FOR DEDICATION OF COMMERCIAL GRADE ITEMS "In accordance with 10CFR21, this letter is to inform you that Invensys Systems, Inc. (d/b/a Invensys Process Systems (IPS)) has identified a failure to fully comply with the requirements for Dedication of Commercial Grade Items (e.g. fuses, resistors, capacitors, etc.) provided to some of our nuclear customers. These parts, certified as safety-related basic components, were not subject to verification of functional performance characteristics as part of the Dedication process and therefore if not installed and tested in their intended application could represent a potential safety hazard. "This condition was identified during the NUPIC (Nuclear Procurement Issues Committee) joint audit of our Foxboro, Massachusetts facility and immediate notification was provided to the member utilities through their web-based system. This Failure to Comply was confirmed on 11/2/07 and, based on our records, has been determined to be limited to the customers, orders and parts identified in [the report]. "Invensys has taken immediate corrective action to rectify the situation in that these parts are no longer provided as safety-related and we will be providing separate notification to each of the nuclear customers listed in [the report]. It should be noted that the subject materials were all controlled and provided in accordance with the approved IPS procedures which include requirements for inspections verifying the appropriate manufacturer, part number, markings and other physical characteristics. If these items have been properly installed in the intended Foxboro equipment, functional performance is typically verified through subsequent component or system-level testing." The following customers are effected by this issue: American Electric Power, Arizona Public Service, Dominion Nuclear, Entergy, Exelon, First Energy, Indiana Michigan Power Co., NPPD, OPPD, Constellation, Union Electric, and Wolf Creek. * * * UPDATE ON 4/4/2008 AT 1633 FROM DAVID GOLDEN TO MARK ABRAMOVITZ * * * An updated list of parts and affected utilities was distributed. The affected utilities will be notified next week. The affected utilities are: Ameren UE American Electric Power Amergen Energy Co LLC Arizona Public Service Arkansas Power & Light Baltimore Gas & Electric Commonwealth Edison Connecticut Yankee Atomic Consolidated Edison Company of New York Detroit Edison Dominion Nuclear Duquesne Light Edison Material Supply LLC Entergy (Operations & Vermont Yankee) Exelon Nuclear Nine Mile Point Nuclear Station First Energy Corp Florida Power & Light (and FPL Seabrook) Georgia Power Gina Nuclear Power Plant GPU Nuclear Indiana Michigan Power Company Iowa Public Power District Maine Yankee Atomic Power Nebraska Public Power District New York Power Authority Northern States Power Company Nuclear Management Company Omaha Public Power District Pacific Gas & Electric Company PECO Energy Company Philadelphia Electric Company Portland General Electric Company Progress Energy (Carolinas & Florida) Southern California Edison Toledo Edison TVA Virginia Power Company Westinghouse Electric Wisconsin Public Service Corp. Wolf Creek Nuclear Operating Notified the R1DO (Hansell), R2DO (Evans), R3DO (Skokowski), R4DO (Lantz), NRR (Hodge and Thorpe via e-mail), and FSME (Jankovich via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-12-19
43852 | 0 | TURKEY HILL DAIRY |  |  |  |  | 2007-12-17 | 2007-12-17 17:45 | 2007-12-18 | BROKEN TRITIUM EXIT SIGN The licensee called to report that they discovered a broken tritium exit sign in a storage locker in their parts room. They contacted a contractor who did the site characterization and cleanup. Currently, the sign is stored on site in the safety storage room, doubled bagged and labeled. No over exposure or personnel contamination was indicated. The only data for the sign is it was manufactured in 1999. There was no damage to any additional exit signs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EXCESSIVE RELEASE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2202(b)(2) |  |  |  | 0 | 2007-12-18
43851 | -1 | DEFENSE LOGISTICS AGENCY |  |  |  |  | 2007-12-15 | 2007-12-18 13:54 | 2008-01-17 | TRITIUM AIMING POST LIGHTS MISSING The Defense Distribution Center Defense Depot in Anniston, AL reported a shortage of 7 aiming post lights, each containing 9 Ci of tritium. The shortage was discovered during a shipment pick denial process. A physical inventory conducted at the time of denial confirmed that the lights were not at the designated storage location. The lights were last accounted for during a September, 2007 inventory. It was noted, however, that 88 Material Release Orders were processed for the lights on the same date that the inventory was conducted. No reported overages by receiving agencies were identified. The Defense Depot will contact each recent recipient to determine quantities received in an attempt to reclaim the devices. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * RETRACTION FROM DAVE MACK TO JOE O'HARA AT 1404 ON 1/17/08 * * * The depot determined that they did not have a loss of 7 aiming post lights. A database error recorded 50 lights being received at the facility. However, after reviewing shipping documentation and packaging, the depot determined that they only received 43 lights, which resulted in a 7 light discrepancy. The depot notified Region 2 (Parker). Notified R1DO(Cobey) and FSME(McConnell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | AL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-12-18
43850 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-10-22 18:30 | 2007-12-18 10:43 | 2007-12-18 | INVALID SYSTEM ACTUATION "The following information is provided as a 60 day telephone notification under 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of a 10 CFR 50.73(a)(2)(iv)(B) system. NUREG 1022, Revision 2, identifies the information that is to be reported as discussed below. "On October 22. 2007, at 1830 hours, Division 2 of Residual Heat Removal (RHR) was being placed in Shutdown Cooling (SDC) following completion of a SDC outage. The plant was in Mode 5, Refueling. Reactor Protection System (RPS) A was deenergized for maintenance. RPS B was being supplied by the alternate supply because the B RPS Motor Generator was removed from service for maintenance. Upon start of the RHR D pump motor the RPS B Alternate Supply Electrical Protection Assembly (EPA) breakers tripped due to sensed undervoltage. The loss of the power supply to RPS B resulted in the following: A reactor scram (all rods were already fully inserted), RHR SDC outboard valve isolation, trip of the Reactor Water Cleanup System (RWCU), outboard valve isolation of the Torus Water Management System (TWMS). "A secondary containment isolation also occurred resulting in a trip of Reactor Building Heating Ventilation and Air Conditioning (HVAC), auto start of Division 2 of Standby Gas Treatment System (SGTS), and shift of the Control Center HVAC system to recirculation mode. All actuations and isolations were as expected for existing plant conditions. The initiation signal was invalid because it did not result in response to an actual plant parameter, nor did it trip as a result of any other requirement for initiation of a safety function. Due to the actuation of equipment in multiple systems that were not removed from service or otherwise prevented from changing states, this event is reportable under 50.73(a)(2)(iv) as an invalid actuation of one of the specified systems. "The reactor scram actuation was complete because a half scram was already present due to RPS A being deenergized for maintenance. The Division 2 SGTS system automatically started, secondary containment fully isolated, Reactor Building HVAC system tripped, and the Control Center HVAC fully shifted into the recirculation mode. The following were partial isolations due to loss of RPS B, Division 2: RHR SDC isolation and TWMS isolation. "All systems functioned properly in response to the RPS power loss based on refuel outage system configurations." The licensee believes that the cause of the undervoltage was a result of the start of the RHR pump which caused an in-rush current. The licensee is considering a design change, and captured this event in their corrective action program system as CARD 07-26537. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-12-18
43849 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2007-12-18 07:39 | 2007-12-18 09:49 | 2007-12-18 | HYDRAULIC FLUID SPILL ONSITE "On 12/18/07 at 0739, the Control Room was notified of an approximate 50 gallon oil spill onsite. The spill appears to have originated from a broken hydraulic fluid line on a nearby crane. The spill is contained and did not reach any storm drain or body of water. The spill is reportable to the State of New Hampshire Department of Environmental Services in accordance with State regulation. The NRC Resident has been notified of the event." This incident did not impact plant operations and there were no radiological materials involved. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-12-18
43848 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-12-07 | 2007-12-17 14:25 | 2007-12-20 | MISSING THALLIUM-201 SHIPMENT The State of Massachusetts was notified of a missing shipment of approximately 185 millicuries of Thallium-201. The shipment originated at the licensee, Bristol Meyers Squibb, on December 8, 2007. The shipment had not arrived at its destination, Pharmaceutical and Diagnostic Services, Inc., as of December 17, 2007. Shipment tracking has determined that the package was scanned by FedEx in Boston on December 9, 2007, and no other scans had been recorded. The licensee is working with the shipper to locate the package. The State will provide more information to NRC as it becomes available. As of December 17, 2007 the package activity is approximately 24 millicuries. * * * UPDATE FROM SUMARES TO HUFFMAN AT 1410 EST ON 12/20/07 * * * Bristol Meyers Squibb has informed the State of Massachusetts that the missing Thallium shipment has been located at its own facility as of December 18, 2007. The shipment was apparently inadvertently routed to a Fed Ex facility in Colorado on December 11, 2007. Fed Ex assigned a new tracking number and returned the shipment to Bristol Meyers Squibb. Because the shipment was assigned a new tracking number, it was not immediately recognized that the material had been returned to the shipment originator. The shipment is undamaged and all material has been accounted for. R1DO (Henderson) and FSME (Burgess) have been notified. ILTAB notified via e-mail THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-12-20
43847 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-12-17 02:03 | 2007-12-17 10:37 | 2007-12-17 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY (SPDS) "At 0203 CST, the plant experienced a loss of the Safety Parameter Display System (SPDS) and other computer systems used for emergency assessment in the Control Room, Technical Support Center (TSC) and Emergency Operating Facility. This capability was fully restored at 0600 CST. The cause of the loss was an electrical fault in an intercom box in the TSC." The licensee will notify the NRC Resident Inspector. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-12-17
43846 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2007-12-17 00:30 | 2007-12-17 10:33 | 2008-02-05 | SAFEGUARDS EVENT Safeguards system degradation related to monitoring and detection of PA boundary. Compensatory actions taken. Call the Headquarters Operations Officer for details. The licensee will notify the NRC Resident Inspector. * * * RETRACTION RECEIVED FROM TOM STEC TO JOE O'HARA AT 1033 ON 2/5/08 * * * "Update to Event Notification (ENF 43846) Retraction: "Event Notification ENF 43846 documented an event on December 16, 2007, at 2230 hours, in accordance with 10CFR73.71 (b)(1) 'Physical Security.' In accordance with 10CFR73.71, Security recorded the event in the Reportable Events Log. Based upon further investigation, it was determined that the event was not a Reportable Safeguards Event in accordance with Appendix C to Part 73. "This event has been determined to not be reportable in accordance with 10CFR73.71(b)(1) and ENF 43846 is retracted. "The [NRC] Resident Inspector has been notified of this retraction." Notified R3DO(Kozak) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-12-17
43845 | 0 | JANX INTEGRITY GROUP |  |  |  |  | 2007-12-13 20:00 | 2007-12-14 16:33 | 2007-12-14 | SAFETY EQUIPMENT FAILURE In a remote area in Missouri, radiography personnel were x-raying welds on a pipe that was placed in a trench. Away from the radiographers, the pipeline contractors moved another pipe in the trench which caused the trench to collapse, allowing water into the trench. The radiography saw it happening and immediately cranked the source into the shielded position. The water submerged the SPEC-150 radiography camera and equipment. Using the same camera, the radiographer set up for a shot in a different location. When exposing the source, it became stuck in the unshielded position. The radiographer immediately notified the RSO and marked off the area with boundary tape while he awaited assistance from the vendor. When the vendor could not immediately respond due to weather related travel issues, the radiography personnel procured a heater to thaw the camera as they suspected the camera was frozen from the earlier water intrusion. Surrounding temperatures were in the twenties. After warming the camera, they were able to successfully retrieve the source to the shielded position. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-12-14
43844 | 0 | JANX INTEGRITY GROUP |  |  |  |  | 2007-12-13 20:00 | 2007-12-14 16:22 | 2007-12-14 | POTENTIAL OVEREXPOSURE The licensee reported that two personnel, a radiography technician and assistant, were performing radiography shots at a fabrication shop in Detroit, MI. After completion of a shot, the technician cranked the SPEC-150 camera source into the shielded position. The assistant then surveyed the camera and got a background reading, indicating the source was, indeed, shielded. The survey was verified by the technician. The assistant then removed the camera from a hook that it was hanging on and set it on the ground. He then started preps for the next shot and set the survey meter down on the ground. After completing the preps, the assistant noticed that the survey meter was pegged high on the X10 scale. He immediately moved away from in front of the camera and notified the technician. The source was again verified in the shielded position after the technician locked the camera. No rate alarm occurred on the assistant's rate device but his pocket dosimeter indicated off-scale. The Radiation Safety Officer was immediately notified. The assistance estimated he was in front of camera for approximately two to five minutes. The estimated dose received by the assistant was calculated to be between one and five REM. This will be confirmed when the assistant's TLD is read. The RSO has overnighted the TLD to a lab for processing. The camera was removed from service and will be evaluated by the vendor for suspected failure of an internal safety mechanism. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2007-12-14
43843 | 0 | AREVA FUEL MANUFACTURING |  |  |  |  | 2007-12-14 | 2007-12-14 14:29 | 2007-12-17 | PART 21 REPORT - RASCAL SOFTWARE CODE VERSION 3.0.5 RASCAL is a software code used to estimate projected dose as a result of a radioactive release. AREVA reported that the software underestimates the dose in its calculation of a uranium release using the enrichment option. This underestimate is reported to be on the order of a factor of 0 to 8.6 times when the enrichment is in a range of 0 to 5 percent. AREVA is recalculating the doses in their Radiation Hazards Analysis. Specifically, the licensee indicated that it will apply a factor to correct for the "enrichment" option of the code if a real or potential emergency release needs to be assessed. Other facilities that use RASCAL are not known. * * * UPDATE FROM NRC TO R. ALEXANDER AT 1036 EST ON 12/17/07 * * * On Friday, December 14, 2007, the Areva fuel manufacturing facility of Richland, Washington, notified NRC regarding an error in the RASCAL computer code. The reported issue involves a code option that would be used primarily by fuel cycle facilities. Specifically, the issue involves use of an option in the code that allows users to select a uranium enrichment percentage instead of entering the activity of each uranium nuclide separately (U-234, U-235, and U-238). This error is not present for uranium hexafluoride releases. Doses from the release of enriched uranium hexafluoride are calculated correctly. The NRC is currently evaluating the RASCAL computer code issue reported by Areva. Until the computer code is updated, fuel cycle facilities should not use the uranium enrichment percentage option for releases other than uranium hexafluoride. As an alternative, users should enter the activity of each uranium nuclide separately (U-234, U-235, and U-238) in order to insure correct dose projections from the code. All registered RASCAL code users and the RASCAL Users Group have been notified by email regarding this issue. Any RASCAL user seeking additional information on this issue can contact the NRC via email at sam2@nrc.gov. Notified R1DO (Trapp), R2DO (Seymour), R3DO (Duncan), R4DO (Farnholtz), and NRR (Kuo and Hodge). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-12-17
43842 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-11-15 08:00 | 2007-12-14 10:49 | 2007-12-14 | LOUISIANA AGREEMENT STATE REPORT - TROXLER MOISTURE DENSITY GAUGE HIT BY A BULLDOZER This information was received via email "Eustis Engineering reported an incident that occurred on November 15, 2007. At 8:00AM on this date a Troxler gauge model number 3440 with serial number 25934 was hit by a bulldozer. This gauge has a 8.0 mCi source Cs-137 and a 20 mCi source of Am241:Be. The bulldozer that hit the gauge was operated by James Construction at the Marathon GME Refinery construction site. The technician called the Eustis Engineering office immediately after it occurred. Mr. (deleted), the Eustis RSO, was dispatched to the site. The RSO arrived at 9:30AM and conducted a survey using a Trox Alert survey meter. At 30 feet away the meter reading was 0.1 mR. At 2 feet away the meter reading was 0.2 mR. A leak test was conducted by Gamma Tron on November 15, 2007 after the incident with the results being less than 0.005 uCi (microCuries) of removable contamination." Event Report ID No.: LA070031. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-12-19
43841 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-11-19 09:13 | 2007-12-14 08:36 | 2007-12-14 | AGREEMENT STATE REPORT - MEDICAL DOSE TO WRONG ORGANS The Agreement State of Louisiana submitted the following information: "On Monday November 19, 2007, Cardinal Health Nuclear Pharmacy delivered an isotope dose labeled incorrectly. The dose delivered, was labeled Tc-99m Mertiatide (Mag-3) assayed at 5.1 milliCuries at 9:13 AM. The dose ordered was for a Renal Scan scheduled for 9:30 AM. After injection of the ordered dose, subsequent imaging revealed accumulation of radiopharmaceutical in the liver and spleen. The target organ for Mag-3 is the kidneys. The images would suggest Tc-99m Sulfur Colloid as the agent delivered. This information was reported by the facility that received the dose. The facility also notified Cardinal Health. "This matter is under investigation by Louisiana DEQ." This report refers to Louisiana event identification number: LA070030. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-12-20
43840 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-10-14 02:00 | 2007-12-12 17:02 | 2007-12-12 | INADVERTENT ACTUATION OF EMERGENCY DIESEL GENERATOR "This 60-day optional telephone notification as allowed by 10 CFR 50.73(a)(1) is being made in lieu of an LER submittal. This notification is made pursuant to the reporting requirements specified in 10 CFR50.73(a)(2)(iv)(A) for an invalid actuation of one of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). "On October 14, 2007, at approximately 0200 hours EST with the plant in Mode 5, Refueling, while performing ECCS Start and Load Reject surveillance testing on Emergency Diesel Generator (EDG) 14, the EDG unexpectedly auto-started. Investigation revealed that the auto-start was caused by a faulty test switch. The test switch had been tested multiple times prior to performing the surveillance with no abnormalities noted. "EDG 14 is one of two EDG's in Division II of the Onsite Emergency Power system. The EDG responded properly to the auto-start signal. The actuation was complete, in that the EDG started and ran unloaded. The surveillance testing was immediately stopped upon receipt of the inadvertent actuation. In accordance with the EDG operating procedure, the EDG was synchronized, loaded for about an hour, shut down and returned to standby status. "Since no actual plant condition existed that required the EDG to auto-start, the actuation was invalid. There were no safety consequences or impact on the health and safety of the public. The event was entered in the corrective action program for evaluation and resolution. "The NRC Resident Inspector will be notified of this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-12-12
43839 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-12-12 09:00 | 2007-12-12 10:54 | 2007-12-12 | FLORIDA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE "Troxler gauge stolen from storage facility. Incident discovered at 0900 12-Dec-07; this office notified at 1015 same day. Police on scene. Owner will offer reward. No further action will be taken by this office." Isotopes: Cs-137 & Am-241 Activities: 8 mCi's & 40 mCi's Material Form: By-product; Special Form Probable Disposition of Material: Material stolen and not recovered Model Number: Troxler 3430, Serial Number 32900 Organizations Notified: HSER, HSERE, St. Augustine Police Dept. Case #021610 Incident Location: 150 St. Johns Business Place Suite 303, St. Augustine, FL 32095 Location Classification: Controlled Area FL Incident Number: FL07-194 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-12-17
43838 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-12-11 15:20 | 2007-12-12 10:53 | 2007-12-12 | FLORIDA AGREEMENT STATE REPORT "A misadministration occurred on 11-Dec-2007 this office notified at 1520 hours. The prostate was to receive 140 Gy, but received only 100 Gy. This incident referred to Radioactive Materials for Investigation. This office will take no further action on this incident." Isotope: I-125 Activity: 92 seeds at 0.295 millicuries per seed Material Form: Interstitial Brachytherapy Seeds Incident Number: FL07-193 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * *UPDATE BY FSME (FLANNERY) TO MACKINNON AT 1105 ON 12/13/07* * * "This event (EN43838) has been reviewed and determined to be a reportable medical event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-12-15
43837 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2007-12-11 11:05 | 2007-12-11 17:53 | 2007-12-11 | MAJOR LOSS OF COMMUNICATIONS CAPABILITY "On Tuesday, December 11, 2007, at approximately 1105 PST, the San Onofre Nuclear Generating Station Control Room Red Phone and commercial telephone systems became inoperable for approximately 10 minutes. Control Room Red Phone operability was confirmed by a successful call to NRC Headquarters Operation Office about 1115 PST. "Southern California Edison is reporting this event in accordance with 10CFR50.72(b)(3)(xiii) for a condition that resulted in a major loss of offsite communications capability (Emergency Notification System and offsite notification system). "As part of the problem solving efforts, the Red Phone may become inoperable for brief periods of time. "At the time of this report, Unit 2 is in Mode 6 in a refueling outage and Unit 3 is in Mode 1 at 100 percent power. The NRC Senior Resident Inspector has been notified of this event and provided a copy of this report." The licensee still had satellite phone communications capability. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-12-11
43836 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-12-11 08:55 | 2007-12-11 17:28 | 2008-02-08 | LOSS OF RHR ROOM COOLER "At 08:55 on 12/11/07 the division 1 RHR room cooler, V-AC-5 would not start. At approximately 10:00, troubleshooting determined that the cause of the failure was a blown line fuse on the B phase of the 480 VAC supply breaker. In accordance with plant procedures, a loss of this room cooler requires that the associated division 1 core spray pump and both division 1 LPCI pumps be declared inoperable. The result is entry into Technical Specification 3.5.1 Condition M due to having two or more ECCS injection/spray subsystems inoperable. This requires entry into LCO 3.0.3. At 10:53 on 12/11/07 the blown line fuse was replaced, the unit was tested and operability was restored. LCO 3.0.3 was exited at this time. "The Technical Specification bases for Technical Specification 3.5.1 Condition M states that when multiple ECCS subsystems are inoperable, as stated in Condition M, the Plant is in a condition outside of the accident analyses. As described in this bases section the plant is in an unanalyzed condition and pursuant to 10 CFR 50.72(b)(3)(ii) an 8 hour report is being made. "At this time, the station believes there was no loss of safety function. Further review of the event is in progress at the station. "The station has informed the NRC resident inspector of this event." * * * UPDATE AT 1710 EST ON 02/08/08 FROM RANDY SAND TO S. SANDIN * * * After further review, the licensee is retracting this report based on the following: "The notification was initiated due a TS Bases that stated the plant was outside of its accident analyses with multiple ECCS subsystems are inoperable. This was considered an unanalyzed condition. "Further evaluation by plant staff has determined that for the conditions present at the time of the event the station was bounded by the accident analysis and therefore the event was not an unanalyzed condition. A review of Section 14 of the Updated Safety Analysis Report (USAR) determined that with one low-pressure ECCS division inoperable, the plant was not outside the ECCS accident analysis as described in the SAFER GESTR ECCS licensing topical report for Monticello and reflected in Chapter 14 of the USAR." The licensee informed the NRC Resident Inspector. Notified R3DO (Tom Kozak). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-12-11
43835 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-12-11 10:19 | 2007-12-11 16:20 | 2007-12-12 | LOSS OF 11 ALERT AND NOTIFICATION SIRENS DUE TO SEVERE ICE STORM "Due to a severe winter ice storm in the area surrounding Cooper Nuclear Station, 11 of 24 Alert and Notification System Sirens were discovered to be out of service as of 1019 hours on 12/11/07. This event impacts the ability to readily notify a portion of the 10 Mile Emergency Planning Zone (EPZ) Population for Cooper Nuclear Station. This event also meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii), major loss of the off-site emergency notification system. "Eight of the failed sirens are located in Atchison County, MO (Seven have failed directly due to loss of AC power and one has partially failed due to other aspects of the storm). One of the failed sirens is located in Richardson County, NE (due to direct loss of AC Power). The other two sirens are located in Nemaha County, NE (One has failed directly due to loss of AC power and one has partially failed due to other aspects of the storm). "Atchison, Richardson, and Nemaha County Authorities have been notified and compensatory emergency route alerting has been discussed as an alternate means of public notification. NOAA/EAS Tone Alert Radios issued for notification of rural residents within the 10-mile emergency planning zone are available and the local NOAA radio transmitter is operable. Contact of the local power utilities has been initiated so that power restoration efforts can be monitored. The licensee also notified the NRC Resident Inspector, FEMA Region 7, Missouri State Emergency Management Agency, and the Nebraska Emergency Management Agency." ** UPDATE FROM BRAD BARE TO J. KNOKE AT 2207 ON 12/12/07 ** "As of 1702 on 12/12/07, the number of inoperable Alert and Notification System (ANS) sirens fell below 25% of the total number of sirens (24) which was the basis for reporting the major loss of the off-site emergency notification system. Currently there are 4 sirens still inoperable in Atchison County, MO. Power restoration activities by local power companies are still in progress in Atchison County. All ANS Sirens located in the Nebraska side of Cooper Nuclear Station 10-Mile EPZ have been returned to service. The licensee has notified the NRC Resident Inspector, and authorities in Atchison County and State of Missouri." Notified R4DO (Bywater) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-12-11
43834 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2007-10-15 14:02 | 2007-12-11 13:57 | 2007-12-11 | INADVERTENT START OF EMERGENCY DIESEL GENERATOR D2 "This notification is being made to report an invalid system actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A). Prairie Island Nuclear Generating Plant (PINGP) Train B Unit 1 emergency diesel generator (D2) started due to an invalid system actuation. "On 10/15/07, at approximately 1402 hours (CDT), with PINGP Unit 1 in MODE 1, D2 started inadvertently during an air roll. "The inadvertent start of D2 Diesel Generator occurred while the diesel was declared inoperable (Technical Specification LCO 3.8.1 CONDITION B was entered at 0916 10/15/07 and exited at 1433 10/15/07). Normally, an air roll uses starting air to turn the engine one revolution to clear oil from the top piston of the D2 opposed piston diesel engine. The D2 control switch is to be in pullout per procedure. However, due to operator error, the D2 control switch was not in pullout during the air roll and D2 started during the attempted air roll. D2 did not automatically connect to the associated emergency bus (Bus 16), because no bus undervoltage signal was present and the supply breaker was open. "The Train A diesel generator (D1) remained operable during this event and the Train A EDG was able to provide power to the Train A emergency bus (Bus 15), if necessary. The invalid start was entered into the PINGP corrective action program. The preliminary investigation of this event determined that the D2 start was caused by operator error - the outplant operators performing the air roll missed a step in the procedure that directed calling the control room to verify the D2 control switch in pullout prior to conducting the air roll. "Corrective actions for this event are in progress and are being tracked via the corrective action program." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-12-11
43833 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2007-12-10 15:45 | 2007-12-11 09:17 | 2008-01-03 | AGREEMENT STATE REPORT FROM NORTH DAKOTA OF A POSSIBLE OVEREXPOSURE A physician researcher at the University of North Dakota received a report from Landauer of a radiation exposure reading on his badge of 74 Rem deep dose and 69 Rem shallow dose. The monitoring period for the badge (monthly or quarterly) was not known to the State. Investigation has determined that the researcher is believed to have worked only with P-32 and has done nothing out of the ordinary. The lab area where the researcher worked has been surveyed and there is no indication of contamination. The researcher is currently having blood work done to determine if there is any indication of radiation damage. The licensee is also working with Landauer focusing on the discrepancy between the deep dose and shallow dose readings on the badge. For an overexposure of this magnitude, it would be expected that the shallow dose would be much greater than the deep dose. The University Radiation Committee is leading the investigation for the licensee. The State plans to evaluate the results of the licensee's investigation findings before considering what actions it will take . * * * UPDATE FROM CHRIS SCHMALTZ TO RYAN ALEXANDER AT 0931 EST ON 12/19/2007 * * * The North Dakota Department of Health was informed from Landauer that the physician researcher's ring badge from the time period had been processed and showed no remarkable dose above normal doses seen for those conducting activities similar to that of the researcher. Additionally, Landauer identified residual contamination (not quantified) on the researcher's primary dosimetry badge that showed the excessive deep dose and shallow dose. It appears at this time that the majority of the dose delivered to the primary badge may have been due to the contamination on the badge. Results of the blood work have not been completed the time of the update. The researcher is currently restricted from working in radiation areas and using radioactive materials, pending the completion of the investigation. Notified R4DO (Farnholtz) and FSME EO (Morell). * * * UPDATE FROM CHRIS SCHMALTZ TO JOE O'HARA AT 1421 EST ON 01/03/2008 * * * The North Dakota Department of Health was informed by the University of North Dakota via letter that the university received a report from Landauer that indicates the contamination was limited to the physician's badge and that the dose was to the badge and not to the individual. Blood work and a medical exam conclude that the physician was not overexposed. The dose in question was limited to the badge. Based upon the reported results, the State does not consider this to be an overexposure event. Notified R4DO(Lantz) and FSME EO (Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2007-12-14
43832 | 0 | PALISADES | 1 |  |  | [1] CE | 2007-12-10 18:30 | 2007-12-10 22:21 | 2007-12-10 | NOTIFICATION TO OFFSITE AGENCIES DUE TO ELEVATED TRITIUM LEVELS "Five new ground water monitoring wells were recently installed at Palisades Nuclear Plant in support of the Nuclear Energy institute (NEI) ground water initiative. The initial sampling of one of these wells displayed a level of tritium that triggered the communication protocol of the NEI initiative on ground water protection. On December 10, 2007, at 1830 hours, Entergy confirmed that the tritium concentration for this well was 22,000 picoCuries per liter (pCi/l). The threshold for initiating the communication protocol is 20,000 pCi/l (Offsite Dose Calculation Manual limit for drinking water). This well is located inside the owner controlled area and inside the protected area. This well is not a drinking water source. Entergy is continuing to investigate the source of tritium identified in this well. Samples from the remaining four wells are below minimum detectable activity levels. There is no indication that tritium has migrated off the Palisades site. The licensee plans to notify the State of Michigan, Van Buren County Office of Domestic Preparedness, City of South Haven, Covert Township, and the South Haven Charter Township. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-12-10
43831 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-12-03 14:30 | 2007-12-10 16:36 | 2007-12-10 | AGREEMENT STATE - LEAKING CESIUM-131 SOURCE The State provided the following information via email: "At approximately 2:30 PM on December 3, 2007 the Agency was notified that a Cesium 131 seed was found to be leaking. The source was an IsoRay Medical, Inc., Model CS-1, 3.12 milliCuries. The seed became jammed in the Mick applicator cartridge. The patient bed, the OR [Operating Room], and trash all surveyed clean. Upon opening the cartridge, contamination was discovered. One person received some contamination of their hands which was removed within 15 minutes. The licensee estimates the exposure to the hands of that individual as less than 50 rems. "The source has been secured for decay and ultimate disposal. The Agency [Arizona Radiation Regulatory Agency] continues to investigate this event. The U.S. NRC is being notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-12-16
43830 | -1 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2007-12-08 00:50 | 2007-12-08 07:54 | 2007-12-27 | REACTOR POWER INADVERTENTLY INCREASED ABOVE ACCIDENT ANALYSIS LIMIT "On December 8, 2007 at 0050, during plant maneuvers to return Unit Two from 84% to 100% reactor power following main turbine control valve testing, the two-minute instantaneous thermal power was inadvertently increased above the accident analysis thermal power limit of 2735.1 thermal megawatts while adjusting main turbine load to maintain Reactor Coolant temperature on program. The maximum power level attained was 2741 thermal megawatts. This is a potentially unanalyzed condition. Prompt operator action was taken to restore reactor power to within limits. Reactor thermal power was restored to within limits [below 2735.1 thermal megawatts] eight minutes later at 0058." The two-minute instantaneous thermal power was restored to below 2700 thermal megawatts (100% rated thermal power) at 0105. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DAVID SUPANICH TO HOWIE CROUCH ON 12/27/07 @ 1243 EST VIA EMAIL * * * "Based on the results of an evaluation of the event, the licensee concluded that Unit 2 operated at a maximum power level of 2741 MWth [101.5 percent rated thermal power (RTP)]. The maximum analyzed steady-state reactor core power levels, including uncertainties, are 102 percent of RTP or 2754 MWth. The unit was not in an unanalyzed condition. Therefore, this event is not reportable. "Based on this evaluation, the associated non-emergency notification made on December 8, 2007, is retracted." Licensee has notified the NRC Resident Inspector. Notified R1DO (Perry). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-12-08
43829 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-12-06 20:44 | 2007-12-07 15:47 | 2007-12-07 | UNPLANNED SAFETY SYSTEM ACTUATION AND CONTAMINATION EVENT "On 12/06/2007 at 2042 [CST] C-337 unit 5 cell 5 was being charged and placed on stream and had just gone above atmospheric pressure. At 2044 hours two PGLD (process gas leak detection) heads in the C-337 unit 5 cell 5 actuated and would not clear indicating a potential UF6 release. To stop the release the cell was immediately taken back below atmospheric pressure. Investigation revealed that a UF6 release had occurred causing the PGLD actuation. The amount of material released has not yet been determined. "The PGLD heads are Q safety system components. At the time of the incident the cell was operating in a mode which required the system to be operational. This is being reported based on SAR 6.9 Table 1, J2 (unplanned actuation of a Q safety system) and 10 CFR 76.120 (c) (1) (i) (unplanned contamination event). "The NRC Resident Inspector has been notified of this event." There was no release to the environment and no personnel contaminations reported. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | OTHER UNSPEC REQMNT | [8 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2007-12-07
43828 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-12-06 15:50 | 2007-12-07 15:42 | 2007-12-07 | UNPLANNED SAFETY SYSTEM ACTUATION AND CONTAMINATION EVENT "On 12/06/2007 at 1550 [CST] the C-337 unit 5 cell 3 PGLD (process gas leak detection) head in the C-337 unit 5 cell 3 housing actuated and would not clear. Response to the alarm by operators revealed a haze above the cell indicating a UF6 release inside the cell housing. While the operators were responding to the unit 5 Cell 3 alarm, two other PGLD heads actuated in C-337 unit 5 cell 5. To stop the release both cells 3 and 5 were taken below atmospheric pressure. Investigation indicated that a UF6 release had occurred. The amount of material released has not been determined. "The actuated PGLD heads are Q safety system components. At the time of the incident the cell was operating in a mode which required the system to be operational. This is being reported based on SAR 6.9 Table 1, J2 (unplanned actuation of a Q safety system) and 10 CFR 76.120 (c) (1) (i) (unplanned contamination event). "The NRC Resident Inspector has been notified of this event." There was no release to the environment and no personnel contaminations reported. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | OTHER UNSPEC REQMNT | [8 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(1) |  |  |  | 0 | 2007-12-07
43827 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-12-03 | 2007-12-07 15:32 | 2007-12-07 | ARIZONA AGREEMENT STATE REPORT - LEAKING SEALED SOURCE "A leaking sealed source discovered on Monday, December 3rd 2007, at the Scottsdale Radiation Oncology Center in our hot lab. "This seed is listed as a sealed source containing Cs-131, from the company IsoRay Medical, Inc. The activity contained inside this seed was 3.12 mCi [milli-Curies] of Cs-131. The incident occurred following a patient prostate implant. This seed had become jammed in a Mick Applicator cartridge. After the patient procedure in the hospital had finished, surveys of linen, OR [Operating Room], patient bed, and trash showed readings of background with the GM [Geiger-Mueller] survey meter. The seed, still in the cartridge, was packaged inside the container it had originally arrived in and shipped to the [Scottsdale Radiation Oncology Center]. "Upon its arrival in Scottsdale, the package was surveyed externally with a wipe test which showed no contamination on the external package. It was at [Scottsdale Radiation Oncology Center] that we ascertained that the seed had leaked into its internal container and contaminated the Mick cartridge it resided in. Our personnel that regularly loads seeds was removing it with bare hands since the outside container had been surveyed and showed no contamination. The seed was dislodged into a lead container behind a leaded shield, and the cartridge was surveyed by a GM tube. Since the GM tube responded, our personnel then placed the cartridge into a lead container and then surveyed her fingers. Upon realizing she was contaminated she informed the ARSO [Assistant Radiation Safety Officer]. She was directed to wash with soap and water. After about 15 minutes her hands showed no residual contamination with a GM and pancake probe with open face. The seeds were then placed into a capped glass container and into a marked leaded container. The original shipping box was surveyed, and the decision was to bag the entire box, and store in locked cabinet for 70 days (10 half lives). A survey will be performed to prove that the container is background before it is put back into service. "All areas and personnel were surveyed with the GM and pancake probe open faced, to confirm no residual contamination. The area and personnel were clean and further wipe tests showed only background. "The physician was informed of incident as well as ARRA [Arizona Radiation Regulatory Agency], and IsoRay's health physicist. A calculation showed that the 15 minutes of exposure to the personnel extremities did not exceed the regulation AAC R12-1-445 of 50 rads that is reportable. "As a corrective action, personnel will now wear rubber gloves until all cartridges are examined following the return of any seeds." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-12-12
43826 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2007-11-15 | 2007-12-06 14:03 | 2007-12-06 | PART 21 - POTENTIAL INSUFFICIENT THREAD ENGAGEMENT FOR CERTAIN PRESSURE TRANSMITTERS Rosemount Nuclear Instruments, Inc. (RNII) reported that certain Model 1152, 1153 Series B and D, and 1154, and 1154 Series H Pressure Transmitters may have inadequate thread engagement between the electronics housing and sensor module. Transmitters affected by this notification may not confirm to RNII specifications under accident conditions. Supplier testing has determined that no immediate risk exists, however it is RNII's opinion that two threads of engagement may not be sufficient to assure that the product will perform its intended safety function over the qualified life of the transmitter. The following are the potentially affected licensees: Oyster Creek, Calvert Cliffs, Kewaunee, North Anna, Millstone, Surry, Turkey Point, Vogtle, Diablo Canyon, Shearon Harris, South Texas Project, Browns Ferry, and Wolf Creek. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2007-12-06
43825 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-12-05 06:55 | 2007-12-05 07:23 | 2008-01-28 | ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA At 0655 on 12/5/07 there was an attempted introduction of contraband into the Protected Area. The licensee notified the NRC Resident Inspector and the Lake County Sheriff's Department. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 1545 ON 1/28/08 FROM T. STEC TO P. SNYDER * * * "A 1-hour Physical Security Notification was made on December 5, 2007, in accordance with 10CFR73, Appendix G, 'Reportable Safeguards Events.' This report was made when a Perry Plant employee was found to be in possession of contraband. The contraband was detected prior to the contraband being allowed into the protected area. In accordance with 10 CFR 73.71, Security recorded the event in the Reportable Events Log. Based on further investigation, it was determined that the employee had no malevolent intention and did not attempt to introduce contraband into the protected area. "This event has been determined not to be reportable under 10 CFR 73, Appendix G, and this portion of [Event Report] 43825 is retracted. "[Event Report] 43825 also reported, under 10 CFR 50.72 (b)(2)(xi), a 4-hour 'Offsite Notification' for notifying the Lake County Sheriff's Department about the contraband incident. This portion of Event Report 43825 is not retracted." Notified R3DO (Lipa). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 1 | 2007-12-05
43824 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2007-12-04 07:00 | 2007-12-04 16:06 | 2007-12-04 | OFFSITE NOTIFICATION DUE TO POTENTIAL LOSS OF THREE SIRENS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On December 04, 2007 at approximately 07:00 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Department discovered sirens 17, 18 and 23 out of service. Siren #23 was restored to service at 09:34 and siren 18 was restored to service at 10:32. Siren 17 remains out of service and is estimated to impact approximately 206 members of population in the emergency planning zone (EPZ) within 5 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles. This call is being placed due to the relatively large segment of the population affected [10 CFR 50.72(b)(3)(xiii)]. During an event, the Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected areas when sirens are inoperable. In order to activate this contingency, Maricopa County Department of Emergency Management was notified of the failed siren at 12:58 [10 CFR 50.72(b)(2)(xi)]. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren 17 being out of service and this ENS call." The utility received a pulse check report at 0700 this morning which indicated that three sirens failed the initial pulse check. After the second pulse check, two of the three sirens responded correctly. However, the third siren (No. 17) remained OSS, and the licensee has dispatched a crew to repair it. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2007-12-04
43823 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-12-03 20:51 | 2007-12-03 23:31 | 2007-12-03 | ACCIDENT MITIGATION - CREFS INOPERABLE "On 03 DEC 07 at 2051, following a review of notification CR-CNS-2007-08237 [written for a degraded condition on the field wiring on the motor for HV-FAN-BF-C-1B - the control room HVAC exhaust booster fan, and a physical inspection of the motor itself], it was determined that reasonable assurance that CREFS would fulfill its safety function could not be established. "The CREFS system was inoperable at the time for the purpose of planned maintenance and the condition was discovered during the performance of that planned maintenance. "HV-FAN-BF-C-1B is normally in operation at all times and was operating prior to being secured for the planned CREFS maintenance window. "This fan is a required support feature for the control room emergency filtration system (CREFS) at CNS. This is a single train system and per 10CFR50.72(b)(3)(v)(D) an 8 hour report is required due to the fact that at the time of discovery this condition could have prevented the fulfillment of the safety function of an SSC that is required to mitigate the consequences of an accident." The licensee is in a 7 day shutdown LCO 3.7.4 Condition A. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-12-03
43822 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-12-03 21:00 | 2007-12-03 23:13 | 2007-12-04 | AGREEMENT STATE REPORT - LOST RADIOGRAPHY CAMERA The licensee's radiography team left the temporary jobsite with their SPEC 150 radiography camera on the tailgate. The camera contained a 24 Curie Ir-192 source. The licensee drove approximately 15 miles down the road prior to remembering the gauge was on the tailgate. It was then noticed that the camera was no longer in the truck. The licensee team is retracing their route in search of the camera and will be contacting the Tarrant County Sheriff's Department to aid in the search. The licensee is not sure if the camera had been secured properly prior to driving down the highway. The route taken was from Tinsley Lane to North Business 287 in Saginaw, TX towards Justin, TX in Tarrant County. Notified NORTHCOM and Mexico via email. Texas Report TX-07-43822 *** UPDATE FROM TEXAS DEPARTMENT OF HEALTH (JISHA) TO HOWIE CROUCH AT 0743 ON 12/04/07 *** The SPEC 150 radiography camera was recovered at 0633 CST. A member of the public found the camera and placed it in the back of his private vehicle. Upon hearing about the lost source on the local news this morning, the citizen turned the camera over to the Fort Worth Fire Department. The camera appears intact and undamaged. Texas Department of Health is responding to the fire department to conduct a survey and inspection of the camera. No overexposures are expected. Notified DHS (Haselton), DOE (Parsons), FEMA (Burckart), USDA (Watts), HHS (Garcia), EPA (Johnson), Mexico (via email), NORTHCOM (via email), R4DO (Hay), FSME EO (Burgess) and ILTAB (Sandler). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-12-06
43821 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-12-03 12:00 | 2007-12-03 17:58 | 2007-12-03 | FITNESS FOR DUTY - POSITIVE TEST FOR ALCOHOL DURING RANDOM EXAMINATION A non-licensed supervisor in the corporate office had a confirmed positive test for alcohol during a random examination. The employee's access to the plant has been restricted. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2007-12-03
43820 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-12-03 11:45 | 2007-12-03 15:58 | 2007-12-03 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTUATION "At approximately 1145 CST, on December 3, 2007, the Dakota County Sheriff's office inadvertently activated the Dakota County sirens during the conduct of a silent siren test. The licensee was notified of the siren activation by the siren contractor for the county. Seven of the 117 sirens in the 10-mile Emergency Planning Zone (EPZ) were activated for approximately one to one and one-half minutes. No press release is planned by Xcel Energy or the Dakota County Sheriff's office. The NRC Senior Resident Inspector was notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-12-03
43819 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2007-08-08 08:00 | 2007-12-03 15:21 | 2007-12-03 | AGREEMENT STATE NOTIFICATION - MEDICAL EVENT INVOLVING IODINE 125 SEEDS The State provided the following information via facsimile: "On August 8, 2007 a patient presented to Longmont United Hospital, Colorado Radioactive Materials license #73-01, for implantation of I-125 seeds into the prostate for treatment of adenocarcinoma of the prostate. The Authorized User was Radiation Oncologist [DELETED], MD; the surgeon was [DELETED], MD; the Authorized Medical Physicist was [DELETED], MS. "In the course of the operative procedure, some seeds were placed inferior to the prostate rather than into the gland itself. Due to the misplacement of the seeds, the total dose to the prostate differed from the prescribed dose by more than 20%. "The prescribed dose to the prostate was 160 Gy. A total of 63 0.476U Bard Model STM 1251 [seeds] were implanted. [Total activity 0.3 milliCurie per seed]. Post-implant dosimetry was performed, based on a CT scan of pelvic region. The mean dose to the prostate was 14.4 Gy, the mean dose to the rectum was 44.7 Gy, and the mean dose to the urethra was 73.4 Gy. No other critical structures were substantially irradiated. "At the root of this event was displacement of the prostate gland that was not detected by image guidance caused by substantial peri-prostatic bleeding and hematoma formation. The tissues adjacent to the prostate provided an image with features mimicking the appearance of the prostate, though with non-distinct borders. Due to the bleeding, even these non-distinct borders were expected. In short, enough plausible indicators of correct positioning were present that the surgical team proceeded with the implant until the misplacement of the seeds was discovered. "Due to the unusual circumstances of this specific procedure, no underlying deficiency in the prostate brachytherapy program of this licensee is indicated. The program has since implemented the use of stabilization needles at initiation of the implantation procedure. The primary element deserving of attention lies in the inherent dependence upon the ultrasound image. In such rare cases as this of limited visualization, it may behoove all users to use alternative methods to verify position, such as the digital exam performed on this patient or fluoroscopic visualization of the anatomy. It might be recommended to perform the verification in such circumstances prior to the implantation of any seeds. "The spouse of the patient was informed immediately after the surgical procedure, and the patient was informed when he regained his faculties after anesthesia. The CT scan was performed later that day for dosimetric purposes. "It is understood that the notification provided in this report to your Agency [State of Colorado] should have occurred within 15 days of the event. However, there was miscommunication between the Licensee and the QMP, each thinking that the other had made the report. [Licensee] apologizes for this delay. In the future if such an event should occur, a single person will be appointed to submit a report so that this confusion will not occur again." A total of 23 milliCuries from 63 seeds were implemented during this procedure. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2007-12-06
43818 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2007-11-27 13:30 | 2007-12-03 12:56 | 2007-12-03 | NEVADA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE "At approximately 1330 [PST] on Tuesday November 27, 2007, a technician and asst. RSO for the City of Henderson NV, drove away from a jobsite where he had been taking a backscatter density measurement with a Troxler 3440 Nuclear Density Gauge. He left the gauge sitting on the side of the road with the probe unlocked and not in a safe mode. At 1333, he returned to the site to find that the gauge had been removed. The RSO filed a report with Henderson PD [on 11/27/07] and phoned in a report to Nevada Radiological Health Section the following day [11/28/07] at 1010. The gauge [Serial #26655] contains [2] sealed sources: 8 milliCuries Cs-137, and 40 milliCuries Am-241/Be ." The licensee issued a press release (print, radio, and TV) to notify the public of the incident, warn them of the potential danger and ask for the return of the gauge. Nevada Item Number: NV070009 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2007-12-06
43817 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-12-01 14:35 | 2007-12-01 18:25 | 2007-12-01 | AUTOMATIC EDG STARTS ON 161 KV LINE TRANSIENT "This report is being made under 10CFR50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section' due to the Auto Start of the 'A' and 'B' Standby Diesel Generators. "The Auto start of the 'A' and 'B' Standby Diesel Generators occurred on a valid bus undervoltage condition caused by a transient on the 161 kV Fairfax line. The Standby Diesel Generator Feeder Breakers did not close onto their respective Essential buses. The Essential buses were not required to load onto either diesel as they remained powered from the 1X003 Start-up Transformer during and after the event. Offsite power remained fully operable during and following the event. The Standby Diesel Generators have been returned to the standby/ready condition. "The RWCU pump tripped which removed RWCU from service. The system has been returned to service. The 'D' Well Water Pump also tripped and auto restarted." The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-12-01
43816 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-12-01 08:45 | 2007-12-01 12:43 | 2007-12-01 | TEXAS AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "On Saturday, 12/01/07 at 10:45 a.m., the agency was contacted through the 24-hour emergency answering service by the licensee's RSO, reporting the theft of their Troxler, Model 3430 moisture/density (m/d) [gauge]. The RSO reported that the employee was enroute to a job site and stopped at a Valero gas station on Tidwell Road in Houston, TX at approximately 8:45 a.m. to get gas. The employee finished pumping the gas, returned the nozzle to its hook and walked to the back of the bed of his Silver Dodge F1500 pickup truck to check the bracing of the gauge, when he noticed that a vagrant from the bus stop jumped in the truck and began to drive off. The employee banged on the window of the driver side and was subsequently drug alongside the truck for a distance, while the perpetrator sped off, jumped a median and eventually escaped. The RSO reported that the gauge was in its transport case, triple locked, and securely braced in the bed of the truck, but the [keys for the gauge locks] were on the same ring as the truck keys. "The Houston local law enforcement (LLE) were immediately notified and a police report was filed and assigned case # 175693707-U. [Incident Investigation Program (IIP)] instructed the RSO to submit a picture of the gauge to the LLE to assist them in locating the gauge. The RSO was also asked to consider placing an advertisement in the local newspaper offering a reward. IIP informed the RSO that TDSH would submit an email notification to Texas Association of Pawn Brokers (TAPS) with a description of the gauge to possibly assist in its location. Gauge Information: Mfg: Troxler, Model #: 3430, Serial #: 026027 Source information: 1) Cesium-137; 8 milliCuries, Serial #: 75-9095 2) Am-241:Be 40 milliCuries, Serial#: 47-22446 Last Leak lest: Monitoring Services on 08/14/07 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-12-05
43815 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-11-30 10:52 | 2007-11-30 17:50 | 2007-11-30 | MANUAL HPCI ISOLATION DUE TO STEAM LEAK INCREASE "At 1052 on 11/30/2007 while in Mode 3 for a maintenance outage, a previously identified steam leak on the packing of valve 3-FCV-073-0006A, HPCI Steam Line Condensate Inboard Drain Valve, increased. The room temperatures were not rising at the time of the increased leakage, alleviating the potential automatic isolation of the system. Upon review of the condition, the Operations staff closed the steam isolation valves and declared HPCI INOPERABLE to minimize the spread of contamination in the area. After HPCI was isolated, inspection of the valve identified a Code Class 2 piping through wall leak on a tee upstream of 3-FCV-073-0006A which contributed to the increased leakage observed prior to isolation of the system. "This event is reportable as an 8-hour Non-Emergency Notification in accordance with 10CFR50.72 (b)(3)(v)(B) as; 'Any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to: Remove Residual Heat'; and 10CFR50.72(b)(3)(v)(D), 'any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to: mitigate the consequences of an accident.' "This event also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(v)(B) and 10CFR 50.73(a)(2)(v)(D)." The Code Class 2 piping leak was on a tee for the steam trap bypass valve upstream of the HPCI Steam Line Condensate Inboard Drain Valve. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-11-30
43814 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2007-11-30 11:00 | 2007-11-30 14:20 | 2007-11-30 | POTENTIAL LOSS OF ITEM RELIED ON FOR SAFETY (IROFS) "Reason for Notification: On 11/30/07, during a routine NCS facility walkthrough assessment performed by a qualified NCS Engineer, it was discovered that the SNM mass balance maintained for the Chemical Process Development Laboratory (CPD Lab) had been performed incorrectly. Specifically, although the applicable inventory form and associated mass limit for the lab was in terms of grams of SNM (i.e., grams of UO2), cans of archive pellets brought into the lab had been recorded in terms of grams of 235U (underestimating the total lab mass). "As a result, the total inventory of the lab was actually at approximately 39 kg UO2 (assuming the 2007 annual nominal plant enrichment of 4.38 wt%). This value exceeds the lab mass limit of 15.9 kg UO2, designated an Item Relied on for Safety (IROFS) in the Laboratory ISA Summary (CHMDEV-101). "Notification is being made based on the potential for Loss or degradation of IROFS that result in failure to meet the performance requirements of 10CFR70.61, reference Appendix A, Section (b)(2) to Part 70 of 10CFR70. "Safety Basis: The total inventory of the lab was at approximately 39 kg UO2 (assuming the 2007 annual nominal plant enrichment of 4.38 wt%). This value exceeds the lab mass balance limit of 15.9 kg UO2 (based on the single parameter mass limit for UO2 and water). Although criticality in the lab is judged to be incredible, a mass limit was established for the lab, and a mass balance was initiated to enforce it. This mass balance was designated an IROFS in the Laboratory ISA Summary (CHMDEV-101). "Criticality in the CPD Lab is judged to be an incredible event because no routine process operations are performed in the lab, and special evolutions (for testing or product development) require explicit Criticality Safety Evaluations. The vast majority of SNM currently in the lab is in the form of mounted archive pellets in small (~1 gallon) metals cans stored on the floor of the lab. These cans are being stored there temporarily until a new grinder can be installed to dispose of them. "Although the mass limit was exceeded in the lab, no potential for criticality existed, as the SNM was stored in sealed metal cans with limited moderation (provided by plastic mounting material). In addition, per CN-CRI-06-30, it requires more than 27 fully loaded and optimally moderated pellet cans to challenge the CFFF acceptance criterion of 0.98, even with multiple stacked cans and optimal spacing. In reality, there are only 15 pellet cans in the lab, and these are stored in a single planar array with 12 inch surface-to-surface spacing. "Summary of Activity: The archive pellet cans have been removed from the lab, such that the total mass balance in the lab is now below the mass limit for the lab. The event was documented in the plant Corrective Action Process (CAPs #07-334-C025). A new Criticality Safety Evaluation for the CPD Lab (CSE-18-D) was issued on October 16, 2007, and is scheduled for implementation during December 2007. Although this new CSE still concludes that criticality in the lab is incredible, it established additional controls on maintaining the mass balance and special periodic Assessments of the mass balance by the NCS Function. "Conclusions: Problem was self identified by Westinghouse personnel during a scheduled NCS Facility Walkthrough Assessment. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. A causal analysis will be performed. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2007-11-30
43813 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2007-11-28 17:24 | 2007-11-29 16:31 | 2007-11-29 | OFFSITE NOTIFICATION OF HIGH TRITIUM LEVELS IN SUMP "This communication is being made in accordance with 50.72(b)(2)(xi) and the Nuclear Energy Institute (NEI) Industry Ground Water Protection Initiative. Millstone Power Station and other nuclear power stations across the country are participating in this voluntary initiative to develop and improve ground water protection programs at nuclear power stations. This communication provides notification of preliminary sample analysis of water that seeped into the foundation drain sump outside of the Millstone Unit 3 engineered safety features building. This water is pumped to the station yard drain system and discharged to Long Island Sound via a permitted and monitored pathway for the station. Tritium was detected at a concentration of approximately 34,000 picoCuries per liter in a sample of the water from the sump. The NEI reporting threshold for tritium concentrations is 20,000 picoCuries per liter. "Investigation into the source of the tritium is underway and at the present time the source has not been determined. "The presence of tritium at this location does not present a health hazard to plant employees or the general public. Samples from several wells closest to the affected sump show no detectable concentrations of tritium. Additional sampling is underway. Based on the known hydrology of the site, public drinking water supplies are not affected. "The licensee notified the following agencies: CT Department of Environmental Protection, CT Department of Emergency Management and Homeland Security, CT Department of Public Utilities Control, The Town of Waterford, and The Town of East Lyme." The licensee performed pump maintenance in the sump. At the same time, they performed samples of the water in the sump and found the high tritium concentration in the samples taken. The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-11-29
43812 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-11-29 | 2007-11-29 16:13 | 2007-11-29 | FLORIDA AGREEMENT STATE REPORT - RECOVERED SEALED SOURCES "[CVG Inc. employee] states that a crate with radioactive symbology is in a warehouse [rented by his company]. [CVG Inc. employee] wants to dispose of it and has asked the state for assistance. He suspects the crate has been there since 1995. Miami inspection office will investigate. A Venezuela company (CVG Inc.) ordered the two sources from Ronan Inc. out of Florence, Ky in 1995. Ronan was contacted and will arrange pick up and return to Kentucky after satisfactory wipe tests and updating paper work. No further action will be taken on this incident." Investigation determined that the crate contained two RONAN Inc. Cs-137 sources, 300 millicuries each, serial numbers 1535 GK and 1536 GK. The sources were scheduled to be shipped to Venezuela in 1995, but the Captain of the shipping vessel in 1995 refused to accept the radioactive material shipment. FL Incident Number: FL07-184 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-12-04
43811 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-11-27 18:11 | 2007-11-28 15:22 | 2007-11-28 | AGREEMENT STATE REPORT - NATURALLY OCCURRING RADIOACTIVE MATERIAL FOUND AT A SCHOOL The Agreement State submitted the following information via e-mail: "At approximately 6:11 PM November 27, 2007, the Agency was informed that the Washington Elementary School District had found some radioactive material and had called the Glendale Fire Department. The material was found when the District was cleaning out some chemicals. The Glendale and Phoenix Fire Departments responded and they detected radiation with their instrumentation. At that point the Agency was contacted. "The radioactive material was identified as radium 226 and read 220 microrad at 3 inches from the container. Wipes and alpha surveys checks made in field were negative. Laboratory results pending. Based on the radiation reading at 3 inches, we estimate that a total of between 0.5 to 5 microcuries of radium may be present. The material was secured until a waste broker can remove it. The form of the radium was not determined. "The [Arizona Regulatory] Agency continues to investigate this event." Arizona Report First Notice Number: 07-013 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-12-03
43810 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2007-11-28 | 2007-11-28 16:55 | 2007-11-28 | POTENTIAL UNAUTHORIZED ACCESS TO SAFEGUARDS INFORMATION Potential unauthorized access and transfer of Safeguards Information. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-11-28
43809 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-11-28 02:30 | 2007-11-28 11:22 | 2008-01-25 | HPCI INOPERABLE DUE TO LEVEL SWITCH FAILURE "On 11/28/2007 at 0230 CST, Browns Ferry Unit 1 received a 'HPCI PUMP SUCT HDR LEVEL LOW' alarm and HPCI automatically transferred its suction from the Condensate Storage Tank (CST) to the Suppression Pool. With the HPCI suction not aligned to its normal source, the HPCI system was declared inoperable. At 0710 CST, trouble shooting identified a level switch malfunction. This switch was removed from service allowing HPCl to be returned to the normal Standby Readiness configuration. The System was declared Operable at 0710 when the system was aligned back to normal suction source. "This event is reportable under 10CFR 50.72(b)(3)(v)(B) 'any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to: Remove Residual Heat' and 10CFR 50.72(b)(3)(v)(D) 'any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to: mitigate the consequences of an accident.' "This event also requires a 60 day written report in accordance with 10CFR 50.73(a)(2)(v)(B) and 10CFR 50.73(a)(2)(v)(D)." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM TODD BOHANAN TO HOWIE CROUCH AT 1311 HRS. EST ON 01/25/08 * * * "ENS Event Number 43809, made on 11/28/2007, is being retracted. "NRC Notification 43809 was conservatively made to ensure that the eight-hour non-emergency reporting requirements of 10 CFR 50.72 were met pending the evaluation of an atypical system alignment with the High Pressure Coolant Injection (HPCI) [system]. "An evaluation has been performed in response to this event. The evaluation concluded that the HPCI system was capable of performing its intended safety function in this atypical configuration. As such, the circumstances discussed in the report did not result in any condition that could have prevented the fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident. Thus there would have no impact on nuclear safety. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(B) or 10 CFR 50.72(b)(3)(v)(D). "TVA's evaluation of this event is documented in the corrective action program. "The licensee has notified the NRC Resident Inspector." Notified R2DO (Desai). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | POT RHR INOP |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(v)(B) |  |  | 0 | 2007-11-28
43808 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-11-28 07:32 | 2007-11-28 08:39 | 2007-11-28 | REACTOR SCRAM AND ECCS INJECTION A reactor scram occurred at full power due to either a main turbine trip or loss of feedwater (cause is still under investigation). All rods fully inserted. RCIC started as expected but tripped shortly thereafter on a preliminary indication of low suction pressure. The Digital Feedwater System backup motor driven feedwater pump did not function as required and reactor water level decreased to level 2 (130 inches). High Pressure Core Spray (HPCS) started automatically at level 2 and restored water level. Currently reactor water level is at 188 inches and reactor pressure is at 927 PSI. Decay heat is being removed via the turbine bypass valves. No other significant equipment was out of service at the time of the scram. The scram had no impact on offsite or onsite power availability. The licensee attempted to restore RCIC a second time and experienced another trip. In addition, the licensee attempted to restore the digital feedwater and was unsuccessful. Feedwater continues to be supplied as needed via the HPCS while the licensee attempts to restore RCIC and Digital Feedwater System. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2007-11-28
43807 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-11-27 09:15 | 2007-11-27 10:30 | 2007-11-27 | ALERT DECLARED DUE TO OXYGEN DEFICIENT ATMOSPHERE An ALERT was declared at 0915 CST. A nitrogen freeze seal was being used on a 3 inch pipe in the 1B RHR and 1B Containment Spray pump room. A leak developed on the freeze seal jacket. This created an oxygen deficient atmosphere (less than 19.5 percent oxygen). The nitrogen supply was isolated. And the room was evacuated. The alert was declared in accordance with Emergency Action Level (EAL) "hazard alert #7 (HA7)." Additional ventilation was being placed in the area to restore normal oxygen levels. EAL table entry HA7 is for "Release of toxic or flammable gases within or restricting access to a vital area which jeopardizes operation of systems required to maintain safe operations or establish or maintain safe shutdown." No personnel injuries occurred. Oxygen levels were returned to acceptable levels at 0933 CST. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1205 ON 11/27/2007 FROM PAUL CANTWELL TO MARK ABRAMOVITZ * * * The ALERT was terminated at 1103 CST. Notified IRD (McDermott), R3DO (Lipa), DHS SWO (Mary Anne), FEMA (Dan Sullivan), DOE (Anthony Parsons), EPA (Ms Ross), USDA (Andrew Watts), and USDA (Rick Turner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-11-27
43806 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-11-22 15:47 | 2007-11-26 14:31 | 2007-11-26 | OFFSITE NEWS PRESS RELEASE "This concurrent report is being made to the NRC as a result of a media inquiry from [a reporter] of the Virginian Pilot for an article concerning the closure of Barnwell and its impact on the BWXT operations. The Virginian Pilot is a newspaper in the Hampton Roads, Virginian area. The information was provided to [the reporter] by [Deleted], BWXT's Communications Specialist." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2007-12-03
43805 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2007-11-19 | 2007-11-26 10:18 | 2007-11-26 | AGREEMENT STATE - PATIENT RECEIVED 10% OF PRESCRIBED DOSE "Medical physicist for the licensee called to advise that on Wednesday November 21, it had come to his attention that a medical event had occurred at their Winfield, IL facility. He reported that on beginning Monday November 19, the delivered dose per fraction was only one tenth that which was originally prescribed by the oncologist. The original written directive was to have a post surgical total dose of 3400 cGy delivered in 10 fractions over the course of 5 days (2 per day). However when reviewed by the medical physicist, the treatment protocol instead indicated that each fraction was 34 cGy instead of the 340 cGy per fraction. The attending oncologist we immediately notified and treatments suspended. As a result the dose administered was well below 20% of the intended dose as well as less than 50% per each fraction. "At the time of the assessment only 6 fractions had been conducted and a total dose of 192 cGy had been delivered. After notifying the oncologist and the patient the same day the error was noted, it was determined that the treatment provided to date was an ineffective post surgical procedure and the patient should be retreated. A revised treatment plan was prepared and the first six fractions of a revised 10 fraction treatment have been completed at this time. The oncologist believes there is no end medical effect that will be noticed from this event. "Upon review, the treatment team determined that the dosimetrist who entered the data for the treatment plan had failed to enter the proper dose per fraction after applying a dose optimization plan. Nor was the error caught during a routine review of the plan by the treatment team prior to loading the plan from the planning system. The confusion may have arisen from the fact that this was the first multi-fractionated treatment that the dosimetrist had prepared as all previous treatments they had been involved with were all single fractions. "Due to the nature of this event it will be reported to the U.S. Nuclear Regulatory Commission Operations Center. The licensee is aware of the requirement to file a written report within the next 15 days. This item will remain open an under investigation until receipt of that report. "Corrective Actions: 1 New procedure written 2 Personnel received additional training" The patient has been informed of the incident and has re-commenced radiation treatment. The state has no follow-up intentions for this event. Illinois event number: IL070062 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * *UPDATE BY FSME (FLANNERY) TO KOZAL AT 0950 ON 11/27/07* * * "This event (EN43805) has been reviewed and determined to be a reportable medical event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-12-02
43804 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2007-11-23 22:26 | 2007-11-24 01:08 | 2007-11-24 | TECHNICAL SPECIFICATION REQUIRED PLANT SHUTDOWN DUE TO INOPERABLE LOAD SEQUENCER "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On Friday, November 23, 2007, at 22:26 Mountain Standard Time (MST) Palo Verde Nuclear Station Unit 1 initiated a normal reactor shutdown to comply with Condition H of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.8.1. "TS LCO 3.8.1 requires that automatic load sequencers for train A and B be operable in Modes 1, 2, 3 and 4. The shutdown is necessary due to an inoperable automatic load sequencer for train A in Unit 1. The train A automatic load sequencer was declared inoperable on November 22, 2007, at 19:30 MST and was not restored to operable status within the TS required 24 hour completion time of Condition F of TS 3.8.1. TS 3.8.1 Condition H requires the plant to be placed in MODE 3 within 6 hours and MODE 5 within 36 hours if the required actions and associated completion time of TS Condition F are not met. Efforts are in progress to correct the condition. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." The licensee is taking measures to evaluating the extent of this condition from the remaining automatic load sequencers for Units 1, 2 and 3. The inoperability was discovered due to an invalid actuation of the A train load sequencer that resulted in a pond spray pump initiation. The licensee notified the NRC Resident Inspector. | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-11-24
43803 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2007-11-21 11:15 | 2007-11-21 19:00 | 2007-11-21 | ERDADS LONG TERM HISTORIAN DATA STREAM WAS NOT UPDATING "At approximately 1115 on 11/21/07 it was discovered that the Unit 3 ERDADS long term historian data stream was not updating. This impacted the ability of the ERDS link to transmit valid data. The modem was functional, but did not appear to be receiving data from the ERDADS computers. The long term historian appears to have gone offline at 1441 on 11/12/07. The probable cause of the malfunction appears to be a post installation modification to the system. The ERDS link was restored at 1130 11/21/07 and testing has confirmed it operable. No evidence of tampering has been discovered and this failure affects Unit 3 only." The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-11-21
43802 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2007-11-21 14:08 | 2007-11-21 18:55 | 2008-03-14 | SAFETY PARAMETER DISPLAY SYSTEM DEGRADATION "On 11/21/2007 at 1408 hours, the Clinton Power Station lost a portion of the Safety Parameter Display System in support of Process Computer replacement. These portions are not expected to be restored to service until Process Computer replacement activities are completed. The Plant Process Computer is expected to be fully operational by February 1, 2008. "This event is reportable due to the major loss of emergency assessment capability per 10CFR50.72 (b)(3)(xiii) (when the SPDS has been unavailable for 8 hours or greater). "The NRC Resident Inspector has been notified." The alarm for secondary containment sump level has been lost to the SPDS. Compensatory measures are in effect. * * * UPDATE ON 3/14/08 AT 1526 EDT FROM KISS TO HUFFMAN * * * The system upgrade has been completed along with full confidence run testing. The SPDS is now considered operational and emergency assessment capability restored. The licensee notified the NRC Resident Inspector and State authorities. R3DO (Ring) was notified. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-11-21
43801 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-11-20 20:28 | 2007-11-21 17:42 | 2007-11-21 | FAILURE OF UF6 RELEASE DETECTION SYSTEM "At 2028 CDST, on 11-20-07 the Plant Shift Superintendent (PSS) was notified that the C-333 Unit 6 Cell 7 UF6 Release Detection (PGLD) System failed to function when performing the twice per shift test firing. The test firing of the PGLD detector heads is required per TSR-SR 2.4.4.1-1. This PGLD System contains detectors that cover C-333 Unit 6 Cell 7, Section 3, and Section 4 of the cell bypass piping. At the time of this failure, unit 6 cell 7 and some areas of Section 3 and Section 4 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in the cell and in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 6 Cell 7 PGLD system inoperable, none of the required cell heads and only 2 of the required 3 heads in Section 3 and Section 4 of the cell bypass were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.B.1 and 2.4.4.1.C.1 was entered and a continuous smoke watch was put in place within one hour. Troubleshooting indicated the failure was not similar to writing failures recently experienced on other PGLD systems. The two components most susceptible to failure have been replaced and investigations continue into root cause. The system had functioned correctly when the previous test firing was performed at 1430 hours on 11-20-07. However, since the failure potentially occurred prior to the test firing at 2028 hours the event is being reported as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when (a) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; (b) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and (c) no redundant equipment is available and operable to perform the required safety function." The NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-11-21
43800 | 0 | EMERSON PROCESS MANAGEMENT, FISHER |  |  |  |  | 2007-11-16 | 2007-11-21 12:46 | 2007-11-21 | PART 21 REPORT ON WELDING OF SAFETY RELATED COMPONENTS "SUBJECT: Welder Qualification "PURPOSE: The purpose of this Fisher Information Notice (FIN) is to alert customers that as of November 16, 2007, Fisher Controls International LLC became aware of the possibility of a situation related to welding of safety-related components at the Fisher Controls Marshalltown facility. "We are informing our customers of record of this circumstance in accordance with Section 21.21 (b) of 10 CFR 21 because Fisher Controls International LLC is not aware of each and every application or system design utilized by our customers therefore cannot determine whether an anomaly could cause a defect or 'failure to comply', relating to a substantial safety hazard. "Receipt of this notice does not necessarily mean that the recipient has been shipped any of the subject equipment. It is expected that the recipients of this notice will review the information for applicability to their facilities, and if required, take the appropriate action as described in the section at the end of this notice. "APPLICABILITY: This notice applies only to the subject equipment supplied by Fisher Controls International LLC identified [below]. "DISCUSSION: During an internal audit, it was determined that one welder was missing the necessary qualification documentation to weld repair ASME SA351-CF8M or ASME SA479-S31600 (P-No 8) material using ASME SFA-5.4 Grade E316L filler (categorized as an F-No. 5 filler in ASME Section IX), using the shielded metal arc welding (SMAW) process. Fisher has conducted a review of all applicable weld records and compiled a list of all applicable orders, based on a June 2005, date of hire. "A Corrective Action Request (CAR) has been initiated to determine root cause and appropriate corrective actions. "Fisher has not, as of the date of this notice, found any indication that the valves will not continue to function as designed. In order to support this position. Fisher submits the following facts: "- Fisher has determined that all filler material used for these weld repairs were the correct ASME code material. "- For pressure boundary parts, weld repaired material successfully completed a production hydro. "- Once the issue was discovered, the welder successfully qualified for the missing process and filler combination. "Note: Fisher is continuing to investigate. If necessary, updates will be made when more information becomes available. "ACTIONS REQURED: No action is required for plants that do not have the subject equipment. If your plant has installed any of the equipment identified by this notice, based on the information gathered to date, Fisher has no reason to believe that the affected parts will not perform their intended valve function. If your plant has not installed any of the equipment identified by this notice, contact your local Fisher Representative Sales Office regarding appropriate corrective action. "IMPLICATIONS: The recipient of this notice is requested to review the information contained in this notice to determine its applicability to his/her facility. If no equipment meeting the applicability requirements listed above have been provided by Fisher Controls International LLC, then no further action is required. If equipment meeting the applicability requirements listed above have been supplied and used in a safety-related application, Fisher Controls requests that the recipient of this notice review it and take appropriate action in accordance with 10 CFR 21." The following are the plant sites to which this notice applies: Catawba, Davis-Besse, Oconee, Salem, St. Lucie. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-11-21
43799 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2007-11-20 15:00 | 2007-11-21 11:42 | 2007-11-21 | TAMPER SEALS BROKEN ON UF6 SHIPPING CANISTER "A regularly scheduled shipment of Uranium Hexaflouride from an overseas supplier arrived at the Columbia site. During routine inspection for receipt it was noted that one of the overpacks had both tamper indicating devices compromised. The shipment was not accepted. On November 20 at approximately 1130 Westinghouse notified Law Enforcement and South Carolina Department of Health and Environmental Control. "Notification is being made based on the potential for 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made, shall be reported to the NRC Operations Center concurrent to the news release or other notification', reference Appendix A, Section (c) to Part 70 of 10CFR70. "At no time has the integrity of the overpack or container been challenged, nor has it been removed from the conveyance. The loaded trailer is located where plant security personnel can maintain visual and video surveillance. "Cylinder remains in the overpack, which is located on the transport conveyance in a secure location at the entrance to the Site Property. "The Columbia Site, the shipper and transport company are evaluating the appropriate path forward for disposition." * * * UPDATE FROM G. COUTURE TO P. SNYDER AT 1514 ON 11/21/07 * * * Local law enforcement came to the site and surveyed the overpack with an explosive detection canine unit. The surveys were clean. Notified R2DO (Henson), ILTAB (Hahn) and NSIR (Giantelli), FSME EO (Mohseni). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2007-11-21
43798 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-11-21 03:30 | 2007-11-21 09:15 | 2007-12-07 | ERDADS COMPUTER SYSTEM FAILURE "At 0330 on 11/21/07, Unit 4 ERDADS computer system failed and subsequently would not display any data. The plant's other Computer display system continues to show data. However, it has been determined the Emergency Response Data System (ERDS) link from Unit 4 is inoperable. Troubleshooting is in progress and a follow up notification will be made when the Unit 4 Emergency Response Data System is operable. "The Unit 3 Emergency Response Data System remains operable." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1145 ON 12/7/2007 FROM EDWARD NIELSEN TO JEFF ROTTON * * * "Repairs are complete and the Unit 4 ERDS link was available at 2321 on 12/1/2007. Subsequent testing and evaluation is complete and the ERDS link has been declared operable at 0800 on 12/7/2007." The licensee notified the NRC Resident Inspector. Notified the R2DO (Musser). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-11-21
43797 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2007-06-14 | 2007-11-20 16:56 | 2007-11-20 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via email: "The Licensee reported this event in June and filed a report in a letter that was misfiled causing a delay in this notification. "A gauge user in the employ of the licensee was using a Troxler model 3440 moisture density gauge serial number 31185 at a temporary jobsite in Issaquah. The employee placed the gauge in an area staked to exclude construction traffic. The employee left the gauge unattended to retrieve an item from the user's vehicle. While away from the gauge, a pickup backed towards the gauge in the staked area. Workers in the area attempted to get the driver's attention and stop the pickup but failed. The pickup struck the gauge and caught the handle under the hitch of the truck, breaking the stationary rod and bending the source rod. The source appeared to have remained in its shielded position. The gauge was dislodged from the pickup by moving the pickup forward. The gauge user cleared personnel within a 50 foot area around the gauge and contacted the RSO. The RSO went to the jobsite with a survey meter and performed surveys. Survey readings indicated the source had remained in its shielded position. The damaged gauge rods were secured with cloth tape. The gauge was place in the transport box and returned to its licensed storage location. A leak test was taken at that time and the results returned were normal. "The gauge user's employment with the licensee was terminated for violating the licensee's Operating and Emergency Procedures by leaving the gauge unattended at the jobsite. "The licensee currently reports they are still in possession of the damaged gauge and presently storing it in that condition. The licensee is working with a carrier to get it shipped properly to Troxler in North Carolina. "Notification Reporting Criteria: WAC 246-221-250 Notification of Incidents. "Isotope and Activity involved: 8 mCi of Cesium 137, and 40 mCi of Americium 241 Beryllium. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None known. "Lost, Stolen or Damaged? (mfg., model, serial number): Damaged Troxler, model 3440, Serial Number 31185. "Disposition/recovery: The damaged gauge was placed in the manufactures transport, stored at the licensed storage location and held for pick up and repair or disposal by the manufacturer. "Leak test? Results of the leak test taken at time of the incident were normal." Washington Event #WA-07-059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2007-11-23
43796 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2007-09-27 05:12 | 2007-11-20 16:16 | 2007-11-20 | INVALID EMERGENCY DIESEL GENERATOR START "This telephone notification is being made under 10 CFR 50.73(a)(2)(iv)(A) in lieu of an LER submittal, pursuant to NUREG-1022, Section 3.2.6. "At 0512 on 09/27/07 the 'A' Diesel Generator (DG) was being restored to its normal lineup following a maintenance run. During restoration per Station Operating Procedure SOP-306, an under instruction Operations trainee inadvertently pressed the 'Emergency Start' pushbutton instead of verifying the 'Emergency Start' status light was clear as required by Step 2.4.b of the procedure. This resulted in a start of the 'A' DG in the emergency mode. Following an equipment walk down, the 'A' DG was then secured at 0518. "This inadvertent start of the 'A' DG was determined to be an invalid actuation since it was not the result of a valid signal nor an intentional manual actuation. This inadvertent start was complete, in that the DG started and ran, however; the bus was not required to be loaded and the output breaker did not close. Although inadvertently actuated, the 'A' DG started successfully and would have been able to function in the emergency mode if it had been required." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-11-20
43795 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-11-19 21:00 | 2007-11-20 16:00 | 2007-11-20 | SPILL OF SEWAGE SLUDGE "At approximately 1100 hours on November 19, 2007, waste treatment operators noticed that the sewage sludge pump transferring material to the LLR press, located at the Waste Treatment Facility, had split and that sludge material had been released. The volume of sludge material that was released is estimated to be less than 150 gallons. The material was released in the pump house and flowed to a gravel area north of the pump house and extended into a storm water drainage ditch. A small quantity of material appeared to collect in the ditch, but did not flow off-site. Operators contained the spilled material and cleaned the affected areas in less than 24 hours. "Facility sewage is of low activity due to natural content and the possible presence of trace material due to trace contamination in the associated piping system. The material is known to be << [much less than] 30 pCi/g [picoCuries per gram]. The total activity spilled including natural background is estimated to be less than 6 uCi [microCuries] using a maximum concentration of 10 pCi/g and 150 gallons of material. Both values are conservative. A study is in progress to determine if licensed material was actually present. "On November 20,2007, as required by our VPDES Permit Number 0003697, the Virginia Department of Environmental Quality was notified of this non-permitted release to the environment. "BWXT is making this concurrent notification in accordance with 10 CFR 70 Appendix A(c)." There was no other potentially hazardous material released. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2007-11-28
43794 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2007-11-20 06:30 | 2007-11-20 14:15 | 2008-01-14 | HIGH PRESSURE COOLANT INJECT INOPERABLE "On November 20, 2007 at 0630 hours, with the reactor at 100% core thermal power, a power supply failure was discovered in the high pressure coolant injection (HPCI) flow controller circuitry that may have precluded the system from performing its design basis function. Therefore, in accordance with 10 CFR Part 50.72(b)(3)(v) an eight-hour notification is being made. "As background, on November 18, 2007, at 2145 hours, the high pressure coolant injection (HPCI) system was removed from service for planned maintenance. The required risk analysis was performed and the appropriate 14 day limiting condition for operation (LCO) was entered in accordance with Technical Specification (TS) 3.5.C. Later on November 19, 2007 at approximately 2100 hours the planned maintenance had been completed and HPCI was restored to the normal standby line-up in preparation for post maintenance testing (PMT). The HPCI valve quarterly operability and HPCI pump and valve quarterly operability tests were performed as the prescribed PMT. Upon initiation, the HPCI turbine was observed to come up to expected rated speed (~4,200 rpm) and expected HPCI pump discharge pressure (~1,300 psig). However HPCI pump indicated discharge flow was observed to be ~2,300 gpm, which is less than the Technical Specification requirement of 4,250 gpm. The HPCI system was secured and remained in the original TS 3.5.C LCO and a troubleshooting plan was initiated. "On November 20, 2007, at 0630 hours, troubleshooting identified a power supply failure in the HPCI flow control circuitry. A replacement flow controller was identified and installed and it is anticipated that appropriate PMT will be initiated by 1600 hours. The impact of the power supply failure for the design basis operability for HPCl could not be definitively established before the eight-hour notification requirement of 10 CFR Part 50.72(b)(3)(v) was exceeded." The licensee notified the NRC Resident Inspector and the Commonwealth of Massachusetts. * * * RETRACTION FROM DAVE NOYES TO JOE O'HARA AT 1751 ON 1/14/08 * * * "NRC Notification 43794 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were met pending the evaluation of an atypical condition (low reading) observed with the High Pressure Coolant Injection (HPCI) Flow Controller while performing scheduled surveillance testing for the HPCI System. "During surveillance testing on 11/18/07, the HPCI System was started and met or exceeded the Technical Specification minimum requirements designed to demonstrate HPCI System Operability. While testing the specific components of the system, the HPCI Flow Controller was observed to be behaving erratically. Although the HPCI System was still capable of performing its required design safety function, the Shift Manager declared the system inoperable since he did not have definitive indication that the turbine was providing the required flow. "Troubleshooting of the flow controller determined that the low flow indication was due to a degraded transmitter power supply located internal to flow controller FIC-2340-1. FIC-2340-1 is located in the main control room and is used to control HPCI system flow rate, and provide power to flow transmitter FT-2358. Although indicated flow rate was only 2300 gpm due to the degraded power supply, actual flow rate was approximately 5400 gpm based on pump hydraulic curves. "The power supply in question only supplies power to FT-2358. Normal required supply voltage from this power supply is 28VDC to 36VDC. The degraded power supply could only supply 22.4VDC at the transmitter FT-2358 terminals. The degraded power supply voltage caused transmitter to output a lower than normal current for the actual measured flow rate giving a false low flow rate to FIC-2340-1. "An Apparent Cause Evaluation and Past Operability Evaluation were performed in response to this event. These evaluations concluded that HPCI System was capable of performing its intended safety functions with the transmitter power supply degraded. HPCI system was capable of performing its intended safety functions during the time when FIC-2340-1 transmitter power supply exhibited low output voltage. HPCI would have started and supplied design basis flow to reactor vessel under design basis conditions. Thus there would have no impact on nuclear safety. Therefore, this event was not reportable pursuant to 10 CFR 50.72(b)(3)(v)(D). "ENS Event Number 43794, made on 11/20/2007, is being retracted." The licensee will notify the NRC Resident Inspector and the Massachusetts Civil Defense Authority. Notified R1DO(Cobey) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-11-20
43793 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2007-11-20 05:05 | 2007-11-20 11:29 | 2007-11-20 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "On November 20, 2007, at 0505 hours, the Control Room Emergency Ventilation (CREV) system was declared inoperable due to an inoperable Air Filtration Unit (AFU). During monthly testing it was discovered that the AFU heater failed to operate as required. Technical Specification 3.7.4, Condition A, was entered which requires the CREV system to be restored to an operable status in seven days. This notification is being made in accordance with I0CFR50.72(b)(3)(v)(D), Event or Condition That Could Have Prevented Fulfillment of a Safety Function, because the CREV system is a single train system required to mitigate the consequences of an accident. "Troubleshooting is in progress to determine the cause of the AFU heater failure to start." The licensee notified the NRC Resident Inspector and the Illinois Emergency Management Agency (IEMA). | 97 | 96 | 0 | 97 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-11-20
43792 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2007-11-19 15:29 | 2007-11-19 21:17 | 2007-11-19 | SAFEGUARDS REPORT INVOLVING A PROTECTED AREA VULNERABILITY The licensee discovered a vulnerability in a safeguard system that could have allowed unauthorized or undetected access to a protected area for which compensatory measures have not been deployed. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-11-19
43791 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2007-09-21 13:10 | 2007-11-19 10:38 | 2007-11-19 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATORS "This telephone notification is being made in accordance with 10CFR50.73(a)(1) to report an invalid actuation of the Emergency Diesel Generators (EDGs) reportable under 10CFR50.73(a)(2)(iv)(A). "On September 21, 2007, at approximately 1310 EDT, while Operators were in the process of synchronizing the main turbine generator, a Generator Field Overexcitation trip occurred due to a failed transistor on the manual voltage regulator circuit board. This resulted in a primary and backup generator lockout and turbine trip. All four EDG's started and operated as expected. Because electrical power was never lost to the emergency buses and none of the EDGs loaded onto their respective emergency buses, the actuations were considered to be partial. The EDGs were returned to their standby line-up by 1615 on September 21, 2007. Since no actual bus undervoltage condition existed which required the EDG's to start and the start occurred inadvertently as a result of a single component failure, this event has been classified as an invalid actuation. "This invalid EDG start event was entered into the corrective action program (i.e., NCR 247573) "Initial Safety Significance Evaluation - The safety significance is considered to be minimal. The EDGs started and operated normally. Offsite electrical power to the Emergency buses was never lost. "Corrective Actions - The main turbine generator manual voltage regulator circuit board was replaced." The licensee notified the NRC Resident Inspector. | 23 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-11-19
43790 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-11-18 | 2007-11-18 14:40 | 2007-11-18 | AGREEMENT STATE REPORT - BRACHYTHERAPY SOURCE LOST IN LAUNDRY The State of Florida received a report from Shands Hospital that a 6 millicurie Ir-192 brachytherapy ribbon was lost in the laundry. Apparently, the ribbon was noticed missing following a brachytherapy treatment. Following the treatment, only 9 of 10 ribbons used were accounted for. The licensee said that a warning alarm sounded when laundry was put down the laundry chute, however; the licensee was unable to retrieve the material from the laundry prior to it being shipped off-site to the hospital's laundry facility in Lakeland, FL. The licensee will continue to try to retrieve the material from the laundry. The State of Florida is following-up on this incident. * * * UPDATE FROM D. FERGUSON TO P. SNYDER AT 1629 ON 11/18/07 * * * The licensee retrieved the source from the laundry. The State of Florida is following-up on this incident. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-11-21
43789 | 0 | CRAIG TESTING LABORATORYS |  |  |  |  | 2007-11-16 18:30 | 2007-11-17 09:33 | 2011-04-27 | LOST TROXLER GAUGE MODEL 3430; S/N 33784 On 11/16/07 at 1830, an employee of Craig Testing Laboratory was traveling from a McDonald's restaurant to a Wawa convenience store. When the employee reached the convenience store, he noticed the tailgate of his truck was down, and the Troxler moisture density gauge model 3430; serial number 33784 was missing. The employee notified the company RSO and the Hamilton Township Police Department (Case No. 07-63766). A search of the traveled route near the intersection of route 40 and route 50 was conducted without success. The employee stated that when he was at the restaurant the gauge was present in the back of the pickup truck but not properly secured under lock and key. However, when the employee reached the convenience store (which was about a mile away) the gauge and other items were missing. Those other items included a box of concrete cylinder molds and a concrete pressure meter. The licensee does not believe the items were stolen. The licensee believes the gauge and items fell out of the truck. The activity of the sources are: Am-241 (40 millicuries) and Cs-137 (8 millicuries). The licensee has searched e-Bay and Craig's List and is placing reward ads in the local area and ads in the local newspaper. * * * UPDATE FROM IAN CRAIG TO HOWIE CROUCH AT 1416 EDT ON 4/27/11 * * * This morning, the licensee recovered the gauge from a private citizen. The citizen stated that he received the gauge from an acquaintance. The gauge was intact and in pristine condition. Radiation surveys were normal and the source was secure and shielded. The licensee is awaiting leak test results before placing the gauge back in service. The State of New Jersey will be notified by the licensee as it is now an Agreement State. The licensee's New Jersey license is RAD110001-507930. Notified R1DO (Schmidt), FSME EO (McIntosh) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-11-17
43788 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-11-16 11:00 | 2007-11-16 17:32 | 2007-11-17 | DEGREDATION OF EMERGENCY PREPAREDNESS RESPONSE CAPABILITIES "At approximately 1100 CST on Friday November 16, 2007, Monticello Nuclear Generating Plant determined that there had been a degradation of the Emergency Preparedness response capabilities when the Emergency Response Data System, Offsite Dose Projection (MIDAS), Safety Data Parameter System, selected telephones, and site computer terminals became inoperable in the Technical Support Center (TSC). The loss of these systems is associated with a partial loss of power to the TSC. As a result of these conditions, the TSC was declared non-functional. Emergency Communications remain available with the Emergency Telecommunication System, and Health Physics Network being operable. "Monticello has verified operability of the ERO notification system (pagers), and the communication circuit used to notify the state and local counties. The siren system for local counties was unaffected by loss of site systems. Plant page and radio systems remain operable. Adequate communications capabilities are operable at this time to implement the emergency plan. "The site's Emergency Operations Facility (EOF), which is the back-up facility for the TSC, is fully operational and measures are being implemented to direct TSC personnel to the near site EOF in the event of an actual emergency condition. "The station has informed Wright and Sherburne counties and the Minnesota State Duty Officer of this condition. "Troubleshooting efforts are in progress. A return to service time for all systems is to be determined. Monticello has determined that this event is reportable to the NRC as an 8-hour non-emergency report in accordance with 10 CFR 50.72 (b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM K. HAUGEN TO P. SNYDER AT 1253 ON 11/17/07 * * * The TSC has been restored to an operable configuration. The licensee notified the NRC Resident Inspector. Notified R3DO (Passehl). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-11-16
43787 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-11-15 09:15 | 2007-11-16 10:14 | 2007-11-16 | SAFETY SYSTEM ACTUATION DUE TO INCIDENTAL UF6 RELEASE "On 11/15/2007 at 0915 instrument mechanics were performing a cell datum calibration in the C-333 Unit 4 Cell 2 cell panel when a strong odor assumed to be HF was noticed after the stage 1 high side pressure valve was opened. The 1/4" valve is on a manifold which accesses pressure taps in various locations in the cell. When the odor was detected a UF6 leak detection head located in the cell panel ducting also actuated. The mechanic opening the valve, immediately closed the valve when the odor was detected and they immediately left the area. HF samples taken a few minutes later in the area around the cell panel were all negative. Precautionary urine samples have been taken from the individuals involved and analysis are being run on the samples. "It is believed a small incidental UF6 release occurred when the small high side valve was momentarily opened and actuated the UF6 detection system head which is a Q safety system component. At the time of the incident the cell was in operation in a mode which required the system to be operational. This is being reported based on SAR 6.9 Table 1, J2. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2007-11-16
43786 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2007-11-14 | 2007-11-16 09:15 | 2007-11-23 | AGREEMENT STATE REPORT - LOST Cs-137 SOURCE HOLDER "Ohmart-VEGA RSO was informed on 11/14/07 that a shipment of SR-1A source holders sent to Gibraltar Mines in McLeese Lake, BC, Canada has been lost in transit. The missing consignment consists of 5 devices, each containing 100 mCi of Cs-137. The shipment left the Ohmart facility on 10/25/07. The Ohmart representative in Canada [DELETED] is leading the effort to locate the missing shipment. [DELETED] of the CNSC was notified by Canadian Freightways personnel on 11/14/07. "TST Overland confirms turning over (2) skids to Canadian Freightways on Oct 29, 2007 in Burnaby, BC for furtherance to McLeese Lake, BC. One skid containing detectors was delivered to the customer in McLeese Lake. [DELETED] was unaware of this missing item until he received a phone call from the customer. He is pressing the trucking company to locate the equipment. "Timeline as currently known: TST-Overland picked up two skids at Ohmart-Vega in Cincinnati, OH on 10/25/07; TST signed for them on waybill 766-4148797. TST-Overland moved the shipment through Sarnia, ON for delivery to TST-Porter Burnaby, BC. TST-Porter in Burnaby verified receipt of two skids. CFL was called to pick up 2 skids from TST-Porter in Burnaby on waybill 354-982526 per the attached copy. CFL delivered the shipment of one pallet only to Williams Lake November 2. Trace started with CFL November 9." Devices are five Sealed Source Fixed Gauges activity of 100 mCi each Serial Numbers (5943CN, 5950CN, 6157CN, 6160CN, 6165CN). Ohio report number: OH070006 * * * UPDATE AT 0845 ON 11/23/07 FROM B. BEAUDIN TO P. SNYDER * * * Mr. Beaudin from the Canadian Nuclear Safety Commission called with information that the missing sources were found intact in Burnaby, B.C. The sources were never lost. They were misplaced and located in a warehouse at a different location than expected. Notified Ohio (S. James), R3DO (M. Ring) and FSME EO (A. Mohseni). Notified via email R4DO (J. Clark), FSME NMED PM (Burgess), R3 SLO (via M. Ring), R4 SLO (McLean, Erickson), OIP (Baker, Dembeck) and ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2007-11-21
43785 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-11-06 | 2007-11-15 13:27 | 2007-11-15 | AGREEMENT STATE REPORT - DISCONNECTED RADIOGRAPHY CAMERA SOURCE On November 6, 2007, a radiography camera source was found by licensee personnel to be disconnected from the camera. The Assistant Radiation Safety Officer was notified, reported to the site and retrieved the source into a source changer for safe transport back to the licensee's facility. The camera contained a 69 curie Ir-192 source. The State of California is following up on this incident. CA identification number: 110807. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-11-20
43784 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-11-15 03:13 | 2007-11-15 06:34 | 2007-11-15 | REACTOR SCRAM - INITIATION OF ARI CAUSED BY LEVEL 2 SIGNAL "At 03:13 EST 11/15/2007, a reactor scram occurred due to initiation of ARI caused by a Level 2 signal from Div 1 level instrumentation. The reactor mode switch was taken to shutdown in response to the trip of the recirc pumps initiated by ARI as directed by our Abnormal Operating procedures. All control rods fully inserted into the core. The lowest reactor vessel water level reached was 183 inches. The MSIV's were manually closed to control cooldown rate. Reactor water level is being controlled by CRD and reactor water cleanup blowdown. "At the time of the scram, protective tagging was being hung on the Division I Reference Leg Backfill system. "At the time of the scram all ECCS systems and Emergency Diesel Generators were operable. This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), any event that results in actuation of the reactor protection system (RPS) when the reactor is critical." The licensee is investigating the cause of the scram. There was no ECCS injection. Primary plant pressure is 400 psig, and primary plant temperature is 335 degrees Fahrenheit. The scram is uncomplicated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 9 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-11-15
43783 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-11-14 08:30 | 2007-11-14 21:04 | 2007-11-20 | 24-HR INCIDENT REPORT - SAFETY SYSTEM ACTUATION "At 0830 hours, Autoclave #5 in the X-343 Facility experienced a Steam Shutdown due to high condensate level alarm (B) actuating. The autoclave was in TSR applicable Mode IV 'Feeding, Transfer or Sampling' when the actuation occurred. This is considered a valid actuation of a 'Q' Safety System. The autoclave was placed in Mode VII 'Shutdown' and declared inoperable by the Plant Shift Superintendent (PSS). An investigation is underway to determine the cause of the actuation. No release of radioactive material occurred as a result of the incident. This is being reported in accordance with UE-RA-RE1030 Appendix D.J.2. 'Safety Equipment Actuations.'" The licensee notified the NRC Program Manager and will notify the DOE site representative. * * * RETRACTION FROM G. SALYERS TO P. SNYDER AT 1553 ON 11/20/07 * * * "Following an investigation into the circumstances surrounding this incident by PORTS Nuclear Regulatory Affairs and Engineering, a recommendation was made to the PSS Office that this event be retracted. The recommendation was based upon the determination that 'Steam Shutdown' occurred as a result of an invalid signal to 'B' condensate level alarm. The follow-up testing of the redundant 'A' condensate level probe and condensate drain system confirmed a high condensate level condition was not present when 'B' condensate level alarm actuated. Per the reporting criteria as stated in PORTS SAR section 6.9, Table 1, criteria J.2, this is not a reportable event due to the 'Q' system actuation being caused by an invalid signal. Based upon the information provided, the PORTS PSS Office is retracting this event." Notified R2DO (Henson) and FSME EO (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2007-11-14
43782 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-11-14 13:00 | 2007-11-14 15:34 | 2007-11-14 | PART 21 NOTIFICATION - AREVA 4kV CUTLER HAMMER BREAKERS The licensee provided the following information via facsimile: "In accordance with 10CFR21.21(d)(3), Southern Nuclear Operating Company (SNC) is making notification of a defect in a basic component supplied to Joseph M. Farley Nuclear Plant (Farley). A 10CFR21 report regarding a defect associated with Model MA-VR-350 4160 V circuit breakers supplied by AREVA was made by AREVA to SNC on October 3, 2007. The breaker design incorporates the use of a C-clip which may not have been properly installed or that can become dislodged from its groove on the Main Link Assembly pin which holds the Banana Link in place. If the Banana Link becomes disengaged from the Main link Assembly pin, the breaker will charge, but not close or it will leave the breaker in a 'trip-free' condition. "The Model MA-VR-350 4160 V circuit breakers are used in the plant safety related 4160 V switchgear and serve as pump motor supply breakers for multiple safety related applications, e.g., component cooling water, low-head and high-head safety injection, containment spray, auxiliary feedwater, as well as the emergency diesel generator output breakers. Currently, there are breakers in stock and installed. Consequentially, their postulated failure in these critical applications could create a substantial safety hazard. "Existing plant procedures already included pre-installation inspection steps for the Model MA-VCR-350 4160 V circuit breakers to identify loose nuts, bolts, retaining rings, or other hardware. In response to this concern, SNC revised plant procedures to add the C-clips to the inspection list to verify they are properly seated on the main link. Given the multiple examinations that were being conducted on the breakers in accordance with existing procedures, and the subsequent procedure enhancements that have been made to examine the C-clips, SNC determined that the installed breakers would continue to operate as designed on demand. "As recommended by AREVA, a visual inspection, of the Model MA-VR-350 4160 V circuit breakers should be performed at regular maintenance intervals to insure proper installation of the C-clip on the main link assembly." SNC has been in contact with NRC Region II (Scott Shaffer, Chuck Casto) and has notified the NRC Resident Inspector. | 30 | 100 | 0 | 30 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 21.21 |  |  |  | 0 | 2007-11-14
43781 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2007-11-14 12:20 | 2007-11-14 15:15 | 2007-11-14 | OFFSITE NOTIFICATION OF CHEMICAL SPILL ONSITE "During Construction Activities for a new Security Training facility, an earth mover overturned resulting in a spill of diesel fuel, hydraulic fluid, and engine coolant. The magnitude of the spill is not positively known at this time, but is believed to be less than 50 gallons. The event occurred outside the Protected Area. No personnel were injured during the event. The New York State Department of Environment Conservation (NY DEC) has been notified per plant procedures (Avon Office DEC Spill #75111)." At the time of this report, the earth mover was still overturned and the licensee is taking actions to resolve. No media interest is anticipated as a result of this incident. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-11-14
43780 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2007-11-13 06:32 | 2007-11-13 07:08 | 2007-11-13 | UNUSUAL EVENT DECLARED DUE TO UNEXPECTED REACTOR VESSEL WATER LEVEL CHANGE DURING A REFUELING OUTAGE WITH IRRADIATED FUEL IN THE CORE While in a drained down condition the reactor vessel experienced an unexplained loss of reactor coolant system inventory with irradiated fuel within the vessel. Licensee entered Emergency Action Level MU-9, Unusual Event at 0632 EST. Within a few minutes after entering EAL MU-9 reactor vessel water level returned to its initial water level of 13.7 inches above the centerline of the Hot Legs of the Reactor vessel. Licensee is investigating why reactor vessel water level changed. Chairman Klein's Comm. Assist. (Bill Orders), Comm. Jaczko's Assist (T. Hipschman), Comm. Lyons Assist (S. Baggett), R1DO (M. Miller), R2DO (M. Lesser), R3DO (M. Phillips), R4DO (V. Campbell) , DHS (A. Ackers), FEMA (Sullivan), DOE (S. Bailey), USDA (Watts), HHS (C. Harper) , EPA (NRC) Chief Brown were notified. * * * UPDATE ON 11/13/07 AT 1025 EST FROM J. BOYD TO MACKINNON * * * Termination of Unusual Event. "EAL classification of MU9 is no longer applicable. Investigation of the unplanned Reactor vessel level showed no indication of leakage into any building containing RCS piping. The apparent cause of the event is due to a slight negative pressure in the RCS. When the OTSG lower manways were installed with HEPA filters fan units running, the indicated RCS level lowered and stabilized due to the HEPA units drawing air from the RCS. No actual RCS inventory loss occurred. When the HEPA units were turned off the RCS level returned to the indicated Reactor vessel level prior to the event. In accordance with station procedures this EAL event was terminated at 0929 on 11/13/07." The licensee notified the Resident Inspector, State and Local Officials of this event update R1DO (D. Holody), NRR EO (J. Dozier), IRD (B. McDermott) , DHS ASWO (Ed Hoisinton) and FEMA (D. Sullivan) were notified of the termination of the Unusual Event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-11-13
43779 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-11-11 16:39 | 2007-11-11 20:06 | 2007-12-04 | HPCI INOPERABLE DUE TO VALVE FAILURE DURING QUARTERLY SURVEILLANCE "On 11/11/07 at 1639, the High Pressure Coolant Injection (HPCI) system was declared inoperable. The quarterly HPCI System Valve In-Service Surveillance was in progress. During the performance of the surveillance, the Suppression Chamber supply check valve was unable to be cycled open in accordance with the surveillance procedure. "Loss of the HPCI system is reportable under 10CFR50.72(b)(3)(v) as loss of a single train safety system required to mitigate the consequences of an accident. The plant is stable in Operational Condition 2, no other Emergency Core Cooling or Safety Related systems are inoperable and plant start-up activities are in progress." The licensee notified the NRC Resident Inspector and the Lower Alloways Creek Township. * * * RETRACTION AT 1532 ON 12/4/2007 FROM MICHAEL REED TO MARK ABRAMOVITZ * * * "Further investigation revealed that the existing steps of the controlling surveillance procedure did not consistently equalize pressure across the HPCI suction check valve and therefore did not establish adequate test conditions. The surveillance procedure was revised to ensure adequate test conditions were established and the valve was successfully stroked. Evaluation of the initial assessment of operability determined that the suction check valve was not inoperable. Therefore the HPCI system was also not inoperable as initially declared and continued to be able to perform its safety function. "Based on this additional information, the associated non-emergency 8-hour notification made on November 11, 2007, is retracted." The licensee notified the NRC Resident Inspector and the Lower Alloways Creek Township. Notified the R1DO (Barkley). | 8 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-11-11
43778 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2007-11-09 | 2007-11-10 11:45 | 2007-11-10 | AGREEMENT STATE REPORT - HIGH EXTERNAL RADIATION LEVELS ON I-125 MEDICAL SEED SHIPMENT The State provided the following information via email: "Bard Brachytherapy, a vendor of I-125 prostate seeds based in Carol Stream Illinois, notified the Illinois Radiation Control Program that they had received a shipment of seeds from a state of Washington licensee, Virginia Mason Medical Center, which had excessive external radiation levels. The Illinois, Division of Nuclear Safety promptly notified the state of Washington, Department of Health via phone and email. "At the surface the package was reported to be reading 600 mR/hr while readings at a meter were 1.4 mR/hr. It was determined the lid of the pig which contained the returned seeds (51 seeds total from an original shipment of 90, with an activity of 1406 MBq [38 mCi]) had shifted during transport allowing a beam of radiation to penetrate the external surface of the transport package. "Immediately upon notification from Illinois, the shipper (Virginia Mason Medical Center) was contacted. Washington DOH staff spoke with the Authorized Medical Physicist who provided this information: This was the remainder of a shipment originally received by the licensee on 5 November 2007. It arrived with a total of 90, I-125 seeds with an average activity of 0.4 mCi/seed. Thirty-nine of the original 90 seeds were implanted and the remaining 51 were repackaged according to the manufacturer's (Bard's) instructions. "At the time of shipment, licensee records show a dose rate at the surface of the package of 0.14 mR/hr, and a reading at one meter of 15 microR/hr. "The licensee, upon questioning, acknowledged this shipment differed from all prior shipments from this vendor because it was a sterile shipment (all prior shipments had been non-sterile) and thus came in new/different packaging with different packaging instructions. "The licensee firmly believes the lid of the pig was dislodged due to abuse during shipment. "The licensee stated they had been in contact with Bard concerning this incident. Bard has agreed that on all future such shipments for clients in the state of Washington (it was unclear if corrective action would be extended to clients in other states as well) Bard will include more tape, for sealing the 'lid' of the pig, and that repackaging shipping instructions would also include steps for taping the pig closed prior to shipment." See also EN #43775, Illinois Agreement State report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2007-11-14
43777 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-11-09 15:30 | 2007-11-09 17:56 | 2007-11-09 | AGREEMENT STATE REPORT - TRUCK TRANSPORTING A RADIOGRAPHY CAMERA OVERTURNED The State provided the following information via facsimile: "At approximately 1530 hours the left rear tire of the pickup truck transporting the camera blew out. Truck rolled on its side [just West of I-4/I-95 intersection on I-4]. There were no injuries and no damage to the camera. Company personnel have custody of camera and a truck is being dispatched to retrieve it. Camera will be tested for leakage and functionality before being placed back into service. No further action will be taken in this incident." Camera: Sential Model 424-9 S/N 3688 Source: 29 Curies Ir-192 Florida Incident: FL07-174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-11-14
43776 | 0 | CONVAL INC |  |  |  |  | 2007-11-09 | 2007-11-09 15:30 | 2007-11-09 | PART 21 NOTIFICATION - CONVAL VALVES WELD QUALIFICATIONS The manufacturer provided the following information via facsimile: "This letter serves to notify the Commission of two (2) potential safety-related, non-compliances as defined in 10CFR-Part 21. These non-compliances involve Electron Beam (EB) weld qualifications for welds performed on pressure boundary and safety related components of Conval valves; and Electron Beam (EB) welding of cobalt alloy types 6 and 21 to pressure boundary parts of Conval valves. "Possibly as high as 2,000 forged-body, globe valves generally for use on high temperature steam and hot water in sizes ranging from, 1/2" to 4", possibly involving one or more of these non-compliances, have been supplied by Conval to approximately 25 nuclear power plants over an estimated time period extending from the 1980's to the present. Probably over half of the valves suspected of nonconformances were procured as Commercial Grade valves." Potentially affected plants are: Region 1: Fitzpatrick, Indian Point, Pilgrim, Vermont Yankee, Nine Mile Point Region 2: North Anna, Surry, Oconee, Brunswick, Crystal River, Harris Region 3: Cook, Palisades, Quad Cities, Point Beach Region 4: Arkansas Nuclear One, Fort Calhoun, Palo Verde, Grand Gulf, Waterford, Cooper, South Texas Foreign Plants: Laguna Verde (Mexico), Keoberg (South Africa) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | OTH | PAR | 21.21 |  |  |  | 0 | 2007-11-09
43775 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2007-11-09 11:00 | 2007-11-09 15:14 | 2007-11-09 | ILLINOIS AGREEMENT STATE REPORT - HIGH EXTERNAL RADIATION LEVELS ON I-125 MEDICAL SEED SHIPMENT "This afternoon [at 1330 CST, the State of Illinois] received a call from the [Deleted], the Radiation Safety Officer [RSO] for Bard Brachytherapy located in Carol Stream, IL. The RSO advised that a package of fifty one, I-125 seeds with a total activity of 38 milliCuries, had been returned to them from a client that had abnormal radiation levels associated with the package. Surface readings showed 600 mr/hr and readings at 1 meter showed 1.4 mr/hr. Their investigation quickly showed that all sources identified in the shipping papers were accounted for. However, the lid to the pig which shielded the contents had become askew during transit due to failure to secure it properly resulting in the elevated readings. The vial within the leaded container was intact with no signs of external radioactive contamination or loss of integrity. The RSO promptly notified the shipper, Virginia Mason Medical Center of Seattle, Washington as well as the courier's (Federal Express) radiation safety officer. There is no reason to suspect that there were any overexposures to transportation personnel as a result of the event considering the low level gamma radiation associated with I-125. This event has no media attention associated with it at this time, nor are there any security concerns associated with it. Given the improper preparation of the package by the shipper, no further action is expected from Bard Brachytherapy at this time save for filing the appropriate written report." IL Event No: IL070058 See also EN #43778, Washington State Agreement State report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-11-14
43774 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2007-11-01 | 2007-11-08 14:55 | 2007-11-09 | ILLINOIS AGREEMENT STATE REPORT - MISSING SHIPMENT OF I-125 TO SPAIN On 7 November 2007 at 1500 CST, the licensee notified the State of Illinois of a single package of medical therapy isotopes (I-125, 97.5 millicuries total) that was scheduled for delivery to a customer in Madrid, Spain on 1 November 2007 was missing in transit. The shipment was delivered by Medi-Physics personnel to the Iberia Airlines Cargo freight office for booking on Iberia Airlines Flight 6274, nonstop from O'Hare, IL to Madrid, Spain. The licensee has information that the shipment had not cleared customs and the shipment did not get to the freight forwarder that was contracted to deliver the shipment to a hospital in Spain. The licensee is actively trying to locate the shipment. * * * UPDATE PROVIDED BY STATE (DAREN PERRERO) TO JEFF ROTTON VIA EMAIL AT 1703 EST ON 11/09/07 * * * The State provided the following information via email: "[The State of Illinois] has been notified by [Deleted], radiation safety officer, of GE Healthcare/Medi-Physics (IL-01109-01) in Arlington Heights, IL. [The licensee RSO reported that they] have been advised as of 1545 CST that their package of thirteen missing I-125 seeds totaling 95 millicuries has been located by the carrier, Iberia Cargo. The package was found intact, with no apparent damage or loss at the airport in Madrid, Spain. The package will be released from customs and sent on to the intended recipient (Hospital la FE. Servicio de Braquiterapia). Written confirmation will be provided later by Iberia Cargo." Notified R3DO (M. Phillips) and FSME (R. Lewis). Notified ILTAB (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-11-13
43773 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-11-07 03:06 | 2007-11-07 07:58 | 2007-11-07 | REACTOR SCRAM AS A RESULT OF LOSS OF NORMAL POWER 13.8 KV BUS "With the plant in Mode 1 at [approximately] 75% power, the Auxiliary boiler and water treatment building 480 volt switchgear (NJS-SWG1J) faulted. The fault resulted in the loss of the NPS A bus (13.8 Kv normal supply), causing condensate and feed pumps to trip. Operators in the control room immediately responded and the plant was manually scrammed at 0306. Both the high pressure core spray (HPCS) and the reactor core isolation cooling (RCIC) systems responded automatically and injected into the vessel (valid ECCS signal). Safety systems responded as expected, including level 2 isolations." The licensee believes a transformer fault may have transferred up the line and caused the loss of normal power supply. RCIC is controlling reactor water level with primary plant pressure approximately 325 psia. Decay heat is being controlled through modulating the SRV's. The licensee has all systems available to place the unit in safe shutdown and cooldown. The licensee has one inoperable EDG and is not in any technical specification action statement at this time. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2214 ON 11/7/2007 FROM BRYAN KELLEY TO MARK ABRAMOVITZ * * * "The high pressure core spray system was returned to its standby lineup at 0318 (all times are CST). Standby service water was being placed in service at 0701 to raise service water header pressure when standby service water pump 'C' started automatically. NPS 13.8kv switchgear 'A' was restored to service at 1245. The reactor core isolation cooling system, which automatically started at the time of the event, was shutdown at 1645. The Division 3 diesel generator, which automatically started at the time of the event, was restored to its standby lineup at 1429. Shutdown cooling was placed in service with residual heat removal pump 'A', at 1626. The plant entered Mode 4 (cold shutdown) at 1942. "The electrical fault that initiated the event has been isolated to a 13.8kv/480v transformer in the turbine building. An investigation is ongoing." The licensee notified the NRC Resident Inspector. Notified the R4DO (Spitzberg) and NRR (Lubinski). | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2007-11-07
43772 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2007-11-05 16:49 | 2007-11-05 21:22 | 2007-11-06 | SPDS OUT OF SERVICE FOR PLANNED MAINTENANCE "At 16:49 hours, on 11/05 the Unit 1 SPDS and ERDS systems were removed from service to support restoration activities from a planned maintenance outage on the power supply. The duration of work is expected to be approximately 10 hours. (Scheduled for completion at 03:00 on 11/06/2007). During this time, Control Room indications and alternate methods will be available. "Since the SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10 CFR 50.72(b)(3)(xiii). "A follow-up notification will be made to the NRC after the SPDS and ERDS system are returned to service." The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 0315 ON 11/6/07 FROM J. PAULES TO P. SNYDER * * * At 0314 on 11/6/07 the SPDS and ERDS systems were returned to service. The licensee will notify the NRC Resident Inspector. Notified R1DO (M. Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-11-05
43771 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2007-11-05 | 2007-11-05 14:11 | 2007-11-05 | TRANSPORTATION OF RADIOACTIVE MATERIAL WITHOUT PROPER LABELING "Pursuant to 10 CFR 50.72(b)(2)(xi), Energy Northwest hereby informs the Nuclear Regulatory Commission (NRC) of an intent to report a undeclared shipment of hazardous material to the Department of Transportation (DOT). "Energy Northwest recently discovered that on January 23, 2007 an NCS Model LMP-10 Freon monitor, containing a 300 mCi Tritium source, was transferred to NCS Corporation for calibration without designating the shipment as Radioactive Material, Excepted Package, Limited Quantity of Material, 7, UN2910 as required by 49 CFR 173.421(a). The monitor was shipped from Richland, WA on January 23, 2007 via UPS and received in Columbus, OH on January 24, 2007. The return shipment of the instrument to Energy Northwest was received on February 12, 2007 and was designated as containing radioactive material. "There were no consequences associated with this incident and the potential for radioactive exposure of any individual as a result of this shipment was negligible." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-11-05
43770 | -1 | ENGINEERING & TESTING SERVICES |  |  |  |  | 2007-11-04 09:00 | 2007-11-05 11:38 | 2007-12-05 | TROXLER GAUGE DAMAGE BY BACKHOE On 11/4/07 at around 8:45 a.m. to 9 a.m. a Troxler (Model 3430, S/N 33496) moisture density gauge was being used at a construction site when a backhoe suddenly reversed direction and backed over it. The sealed source in the gauge is in the stored and shielded position. The licensee plans to return the gauge to the manufacturer to determine the extent of the damage and for repair. * * * RETRACTION PROVIDED BY C. NABHAN TO J. KOZAL ON 12/05/07 AT 1325 * * * Upon inspection by the Troxler Corporation the gauge was found in the normal condition with only cosmetic damage. No safety equipment was damaged or found inoperable. Troxler performed a microscopic inspection of the source rod and the neutron source cavity, as well as the plug that secures the source. No defects were found. Therefore, no failure of safety equipment existed at any time. Notified R1DO (Barkley), FSME EO (Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-11-05
43769 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2007-11-03 15:00 | 2007-11-04 16:10 | 2007-11-04 | RADIOGRAPHY CAMERA SOURCE FAILS TO FULLY RETRACT INTO CAMERA The licensee was using a radiography camera on the Alaska pipeline approximately 50 miles North of Fairbanks (near pump station 7). The temperature was approximately 5 to 8 degrees F. Moisture entered into the locking mechanism causing the latch to trip prematurely i.e. the source was not fully retracted into the camera. The RSO took the latching mechanism apart and fully retracted the source. The RSO and assistant each received a dose of 30 millirem during this repair. Radiography camera: Industrial Nuclear Corporation model IR-100 Source: 72 Curie Ir-192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-11-04
43768 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-11-03 17:22 | 2007-11-03 17:26 | 2007-11-08 | LOSS OF SPDS AND ERDS DUE TO PLANNED MAINTENANCE "At 1722 hours, on 11/3/2007, the SPDS and ERDS system was removed from service to support activities for a planned maintenance outage on the UPS vital bus power supply. The duration of work is expected to be approximately 48 hours. During this time, Control Room indications and alternate methods will be available. Since the SPDS computer system will he unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii). The licensee will notify the NRC Resident Inspector." * * * UPDATE AT 1715 ON 11/7/2007 FROM SUE REITH TO MARK ABRAMOVITZ * * * "Maintenance activities are continuing on the power supply for the SPDS and ERDS systems. Current estimate will restore the computer systems by 2000 on 11/08/07. An update will be provided once SPDS and ERDS are restored." R3DO (M. Phillips) notified. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1234 ON 11/8/2007 FROM DAVID HEMMELE TO MARK ABRAMOVITZ * * * "Planned work which resulted in the removal from service of SPDS and ERDS has been completed. SPDS and ERDS have been restored to service as of 1115 11/8/2007." The licensee notified the NRC Resident Inspector. Notified the R3DO (Phillips). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-11-03
43767 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-10-29 | 2007-11-02 14:34 | 2007-11-02 | LOSS OF CONTROL OF AM-241 SOURCES IN STATIC ELIMINATOR BARS The State provided the following information via facsimile: "On October 29, 2007, the Agency received notification from a metal recycling facility that unexpected radioactive material had been detected in an incoming load of scrap. Agency representatives responded to the site and determined, by using a radioisotope identifier, the presence of Americium-241. The load was returned to its originator under DOT SP 10656, MA-MA-07-01, where an investigation into the type, quantity and form of Am-241 could be performed under controlled conditions. Telephone interviews with the scrap recycler indicated the scrap had originally come from two facilities, one that had already been contacted by him, and had acknowledged possession and use of process gauges at their facility. The Agency contacted the responsible individual and requested an inventory of their sources be performed to determine whether any were lost or missing. "On October 30, the general licensee reported none of their sources were unaccounted for. Consequently, an agency responder met with the scrap recycler later that day, and on separating the device from other materials, identified the source was a static eliminator bar. The licensee representative was contacted again, and he and another individual responded to the site, where on visual inspection they promptly took responsibility for disposing of the bar from their facility. "The Agency's investigation to date indicates the initial bar found was one of 12 that had been transferred to the North Andover facility from another of the company's facilities located in Somerville, MA. An additional five bars were discovered the following day in a pile of aluminum scrap at the recycler's yard, where they have been temporarily secured. Six bars were found installed in process equipment at the North Andover facility. The static eliminator bars are not registered with the Agency, and current facility management claims no knowledge that these bars, originally distributed to Sweetheart Cup between 1993 and 1995 by NRD, Grand Island, NY, are required to be registered and controlled under equivalent general license regulations to other devices currently registered with the Agency. "Sweetheart Cup was purchased by the Solo Cup Company approximately four years ago, and further investigation is necessary before determinations may be made on where, and how, the breakdown in communication regarding these devices occurred, and on the scope of the problem in Massachusetts, or in other jurisdiction where Solo Cup has had, or maintains, manufacturing facilities. The static eliminator bars are NRD Model No. A-2003 and contain up to 20.25 mCi Am-241 each. The licensee has committed to hiring a qualified consultant to assist them with fully characterizing the scope of this event, establishing a plan of correction, and implementing corrective actions if needed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-11-07
43766 | 0 | PENN STATE HERSHEY MEDICAL CENTER |  |  |  |  | 2007-10-10 09:30 | 2007-11-02 13:13 | 2007-11-02 | MISSING I-131 GEL CAPSULE "To assist the Hot Lab Tech, at 9:20 AM on October 10, 2007, another Nuclear Medicine Technologist placed a gel capsule containing 55 microCuries of I-131 into a Leucite thyroid neck phantom and oriented the phantom for an anterior projection to calibrate the thyroid uptake counting system for dosimetry measurements needed on a thyroid treatment patient . After setting the counter for a ten-minute count she informed the Hot Lab Tech that the sample was counting. She did not stay with the thyroid neck phantom and counting system which was located in an alcove approximately twenty feet from the door to the Hot Lab. While the neck phantom was visible from the doorway of the Hot Lab, the Hot Lab Tech did not have it under constant observation. However, there were Nuclear Medicine personnel in the corridor between the Hot Lab and this alcove almost continuously during the counting procedure. "At 9:38 AM, the Hot Lab Tech oriented the neck phantom for a posterior projection and set the system for a second ten-minute count. When the Hot Lab Tech returned to the Thyroid counter at 10:15 AM, she discovered that only background counts had been recorded for the ten-minute counting period. A check of the neck phantom revealed that it contained no radioiodine capsule. "After an extensive but unsuccessful search by Nuclear Medicine personnel, Health Physics was called for assistance at 11:30 AM. A Health Physics team spent several hours searching all conceivable areas but, no capsule was found. "Security was notified along with the local police. The local police responded, took fingerprints but, as of yet, have not responded further. "A review of the DVD from the security camera located outside the Hot Lab and Injections rooms failed to determine the fate of the radioiodine capsule but did confirm that there were Nuclear Medicine personnel in sight of the neck phantom for essentially the entire procedure and especially for the 18 minute window (from the end of the first count to the beginning of the second count) when the capsule went missing. "An investigative Committee was formed to query all Nuclear Medicine Technical personnel and Nuclear Medicine nurses and to determine the fate of the lost capsule and/or the root cause of the event. This committee was chaired by the Radiation Safety Officer and included the Assistant Manager of Radiology, the Chief of Nuclear Medicine, the Operations Director for Radiology, the Associate RSO and the Director of Human Resources. "The investigation failed to determine the fate of the missing radioiodine capsule. "The investigation revealed that the Chief Technologist had approved the calibration of the thyroid uptake counting system in the alcove rather than a locked room because he considered the capsule in the neck phantom to constitute 'secure.' "The investigation revealed some attitude problems on the part of the technical staff and some deviations from required 'good radiation safety practices' unrelated to the missing capsule. "Corrective actions implemented include: "1. Dismissal of the Chief technologist. 2. Dismissal of the Hot Lab technologist responsible for the calibration of the thyroid uptake counting system. 3. Year long probation for all remaining Nuclear Medicine Technologists. 4. Increased training sessions for all Nuclear Medicine technologists. 5. Relocation of the office of the Assistant Manager of Radiology to the Nuclear Medicine area. 6. Additional security cameras ordered for other areas of Nuclear Medicine. 7. Random review of recordings from security cameras by Health Physics to verify adherence to good radiation safety practices. 8. Changes to the door locks to severely restrict traffic flow in and access to the Nuclear Medicine areas. 9. Increase observation of Nuclear Medicine activities by Health Physics. 10. Increased observation of Nuclear Medicine activities by physicians and residents. 11. Relocation of the Thyroid uptake counting system to a room that can be locked when no-one is in attendance during a calibration procedure. 12. Requiring that sources being used outside of the Hot Lab will be under the control and responsibility of a single individual for the entire time that the source is out of the Hot Lab. "This incident has been thoroughly reviewed with our Radiation Safety Committee and our Subcommittee on Human Use of Radioisotopes. "The licensee will continue to search for the missing source and will continue close scrutiny of all Nuclear Medicine operations. As of this date, the fate of the capsule is still unknown. The current activity, due to decay, would be approximately 8 microcuries." The licensee notified NRC Region I (Pam Henderson), Dairy Township Police Department, and Director, PA Bureau of Radiation Protection. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-11-02
43765 | 0 | ENGINEERING CONSULTING SERVICES |  |  |  |  | 2007-11-02 10:00 | 2007-11-02 10:53 | 2007-11-05 | MOISTURE DENSITY GAUGE RUN OVER BY PAVER At a construction site in Park Plaza (133 - 143 Park Street in Vienna, Virginia 22180) a paver ran over a CPN model MC1DR moisture density gauge. The paver dragged the device 6 to 8 feet before stopping. The device was found to be in the shielded position. The Radiation Safety Officer verified this with a meter that read 0.4 millirem per hour at 1 meter which was expected for a shielded device. The licensee plans to return the gauge to the manufacturer for a damage assessment . * * * UPDATE FROM O. DUZYOL TO P. SNYDER AT 0949 ON 11/5/07 * * * The serial number of the gauge in the original notification is MD50702756. Notified R1DO (Miller) and FSME EO (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-11-02
43764 | -1 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2007-11-02 07:44 | 2007-11-02 10:55 | 2007-12-19 | SUSPICIOUS EXPLOSIVE DEVICE DISCOVERED IN VEHICLE AT OCA ACCESS CHECKPOINT "On November 2, 2007 at 0744 [MST], Palo Verde Nuclear Generating Station Units 1, 2 and 3 declared a Notification of an Unusual Event as specified in the Emergency Plan. The basis for the Emergency Class declaration was detection of a credible threat: an explosive device was detected during a vehicle search at the site access check point. The site has entered its Deliberate Acts procedure. The device was discovered in a contract employee's vehicle at 0525 MST. It was confirmed to be an explosive device at 0730 MST by the Maricopa County Sheriff's Office (MCSO). The explosive device was removed from the site by MCSO and Federal Bureau of Investigation (FBI) at 0852. The individual driving the vehicle has been detained by MCSO. No other individuals were in the vehicle at the time. "Palo Verde Unit 1 is in Mode 2 at approximately 2% power. Unit 2 is in Mode 1 at 100% power. Unit 3 is defueled undergoing steam generator replacement. No reactor protection system or engineered safety feature system actuations have occurred and none are required. No major structures, systems, or components are inoperable impacting the continued safe operation of the units. Plans are to continue Mode 2 operations in Unit 1 and Mode 1 full power operation in Unit 2. "Further investigation is ongoing in cooperation with MCSO and the FBI. Security is conducting searches of the site. No additional concerns have been identified at this time. The security event has not resulted in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of the security event declaration. A news release was made at 11:10 a.m." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DON VOGT TO J. KNOKE AT 1809 EDT ON 11/02/07 * * * At 1447 MST site security posture has changed from Code Red to Code Yellow Heightened Awareness, and at 1504 MST licensee exited the Unusual Event,. The licensee has notified the NRC Resident Inspector, state and local agencies, and will be issuing a press release this evening. Notifications were given to the following: R4 (Art Howell), R4DO(Powers), NRR EO (Bateman), IRD Manager (Blount), ILTAB (Sandler), DHS (York), FEMA (Dunker), DOE (Wyatt), FBI-SIOC (Curry), HHS (White), USDA (Phillip). * * * UPDATE FROM WAREN HENDRIX TO J. KNOKE AT 1416 EDT ON 11/03/07 * * * The licensee downgraded the security posture at the site from Code Yellow Heightened Awareness to Code Yellow. The licensee notified the NRC Resident Inspector. Notified R4DO (Powers) and ILTAB (Sandler). * * * UPDATE FROM DAN HAUTALA TO W. HUFFMAN AT 1600 EST ON 12/19/07 * * * "Arizona Public Service Company (APS) is retracting security-related Event Notification #43764 and notification of unusual event (NUE) reported on November 2, 2007. Based upon investigations performed by the Federal Bureau of Investigation (FBI), Maricopa County Sheriff's Office (MCSO) and Palo Verde Security department, APS has determined that there was no explicit nor credible threatened action as described in 10 CFR 73.71, Appendix G, Paragraph I. These investigations revealed that the previously reported explosive device was placed in the owner's truck bed without his knowledge. Therefore, there is no reason to believe that a person has committed or caused, or attempted to commit or cause, or has made a credible threat to commit or cause: theft or unlawful diversion of special nuclear material; or significant physical damage to a power reactor; or interruption of normal operation of a licensed nuclear power reactor." The licensee notified the NRC Resident Inspector. R4DO (Farnholtz) has been notified and an e-mail sent to ILTAB and the 73.71 group. | 2 | 100 | 0 | 2 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Startup | Power Operation | Refueling | Startup | Power Operation | Refueling | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2007-11-02
43763 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2007-11-01 17:00 | 2007-11-02 10:33 | 2007-11-02 | NON-LICENSED EMPLOYEE TESTED POSITIVE FOR ALCOHOL DURING RANDOM TESTING A non-licensed employee supervisor, not involved in plant operations, had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's unescorted access to the plant has been denied. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2007-11-02
43762 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-10-31 | 2007-10-31 13:33 | 2007-10-31 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "Received initial notification from [the RSO] that a Troxler gauge was stolen. Gauge was in a conex box at job site. Miami office will investigate. No further action will be taken on this incident." Location of job site: 13th Ave & Martin L King Blvd, Pompano Beach, FL Troxler Model number: 3430 Serial Number: 37992 Sources: Cs-137 (8 milliCuries), Am-241:Be (40 milliCuries) This incident was reported to the Broward County Police. Florida Incident Number: FL07-170 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-11-05
43761 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2007-10-29 23:00 | 2007-10-31 10:55 | 2007-10-31 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE UNATTENDED FOR SIX HOURS The State provided the following information via facsimile: "This is the initial notification for an incident that was reported to this Department on this date. Conam Inspection & Engineering Services, Inc., 6900 East 47th Ave. Unit 200 Denver, CO 80216, a Radiography Licensee (Colorado License # 963-01) provided the Department with the attached Preliminary Incident Investigation report (two pages). Initial details indicate that a radiography source was left unattended and improperly secured on a jobsite for approximately six hours. A member of the job site staff identified the problem and notified the licensee. It appears that this was a result of an ill employee leaving the job site without properly securing the source. An investigation has been initiated by the Colorado Department of Public Health and Environment. No other details are available at this time." The Conam Preliminary Incident Investigation Report follows: "Date and time of incident: October 29, 2007 at 11:00 p.m. Location of the incident: Suncor USA in Commerce City, CO. Date and time investigation began: October 30, 2007 at approximately 4:30 a.m. "Description of the Incident/Chronology of Verifiable Events: Conam I&ES performed radiography services at Suncor Refinery in Commerce City, CO on October 29, 2007. These services were being performed on a 24 hour basis. An exposure device was maintained on site and transferred from day shift personnel to night shift personnel. On October 29, 2007 the exposure device was not stored properly in the transport vehicle by the day shift radiographer. The day shift radiographer neglected to lock the outer door to the darkroom and the tailgate on the transport vehicle prior to leaving visual surveillance of the transport vehicle. The vehicle was parked on Suncor property approximately 40 feet from the Conam office. The day shift radiographer departed the job site at approximately 6:45 p.m. The night shift radiographer was on site prior to the departure of the day shift radiographer. The night shift radiographer became ill, and left the lob site at approximately 11:30 p.m. The night shift radiographer left the exposure device on site unattended by any approved Conam I&ES personnel. The night shift radiographer did not access the darkroom at any time on site prior to his departure since the radiography assistant was not present that evening. A Suncor representative noticed the darkroom on site without any Conam representation at approximately 4:30 a.m. The Suncor representative locked the darkroom and removed the keys to the vehicle then notified Conam management. Conam management responded at approximately 5:15 a.m. and representation was on site to properly secure the exposure device at 6:15 a.m. There were no exposures to the Public during this time period. "List of Contributing Factors: Radiographers failed to follow proper security procedures for securing radioactive materials with IC orders. "Proposed Corrective Actions: Conam management had a safety stand down for all radiographic personnel at Suncor. All additional radiographic personnel will have a safety stand down this week. The staff will be reinstructed as to the proper protocol for securing radioactive materials with the IC order. The two radiographers have been suspended from radiographic services at this time. "Corrective Action Plan Complete? No "If Not, Reason: Corrective action will be completed upon the final outcome of the investigation and the completion of reinstruction to radiographic personnel." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2007-11-05
43760 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2007-10-30 23:30 | 2007-10-30 23:57 | 2007-11-01 | OUTAGE OF SAFETY PARAMETER DISPLAY SYSTEM (SPDS) AND EMERGENCY RESPONSE DATA SYSTEM (ERDS) "At 2330 hours, on 10/30/2007, the SPDS and ERDS system was removed from service to support activities from a planned maintenance outage on the 'C' vital bus power supply. The duration of work is expected to be approximately 12 hours. (Scheduled for completion at 11:30 hours on 10/31/2007). During this time, Control Room indications and alternate methods will be available. "Since the SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The licensee will notify the NRC Resident Inspector. Notified R1DO (Dental). * * * UPDATE FROM JAMES PAULES VIA TELEPHONE TO K. DIEDERICH AT 0330 ON 11/1/07 * * * At 0230 hours, on 11/1/2007, the SPDS and ERDS system were returned to service. The licensee will notify the NRC Resident Inspector. Notified R1DO (Dental). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-31
43759 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-10-30 13:42 | 2007-10-30 17:36 | 2007-10-30 | INADVERTENT ACTIVATION OF OFFSITE EMERGENCY SIRENS "River Bend Station is making a 4 hour report in accordance with 10 CFR 50.72 (b)(2)(xi) of an event that occurred at approximately 1342 hours on October 30, 2007 when the offsite emergency sirens for River Bend located in West Feliciana Parish were inadvertently activated. The siren activation was not related to any condition or event at River Bend. The sirens sounded for approximately 1 minute. River Bend has notified West Feliciana Parish and the Governors Office of Homeland Security and Emergency Preparedness of the inadvertent siren activation. "The site NRC resident inspector's office has been informed of the inadvertent activation and that a 4 hour notification is being made. "The cause of the inadvertent activation is not precisely known at this time, but occurred in conjunction with vendor testing of a new siren control system. This activation of the sirens has been entered into the site corrective action program to determine the cause and the actions necessary to prevent recurrence. "There was no impact on River Bend due to the activation of the offsite sirens located in West Feliciana Parish, Louisiana. The River Bend alert and notification system remained operable for the duration of the event. "The Governors Office of Homeland Security and Emergency Preparedness is making notification to the public of the inadvertent siren activation using the emergency alert system. A press release from Entergy is not planned at this time." | 75 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-30
43758 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2007-10-25 08:00 | 2007-10-30 11:48 | 2007-10-30 | AGREEMENT STATE - ACCIDENT INVOLVING TRUCK CARRYING RADIOPHARMACEUTICALS The State provided the following information via email: "DRH notified by NuMedRx Nuclear Pharmacy RSO that one of their delivery vehicles had been involved in an accident on Highway 49 North at the Highway 16 intersection. Apparently, the vehicle was struck by a school bus while it was en route to making a delivery to a Greenville, MS facility. No students were on the bus at the time of the collision. Apparently, law enforcement personnel did not realize the vehicle was transporting radioactive materials and no notifications were made to MEMA. DRH was not notified until after the vehicle was removed by the wrecker service. DRH responded to the wrecker service facility to survey and retrieve the transport container. The transport container was not ejected from the vehicle; however, the package was turned over and was not secured by the straps anymore. The package was labeled 'Yellow II' and still secured by the tamper seal. No leakage was detected [levels were 0.4 mR/hr at the surface of transport container] and radioactive doses/package were returned to RSO at the Jackson, MS nuclear pharmacy." The delivery vehicle was carrying Thallium-201 and Technetium-99m totaling 13 millicuries. Mississippi report number: MS 07007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2007-11-02
43757 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-10-29 19:30 | 2007-10-30 01:44 | 2007-10-30 | LOSS OF POWER TO TECHNICAL SUPPORT CENTER (TSC) "On 10/29/07 at 1930 hours, it was determined that the Hope Creek TSC has been unavailable for greater than 8 hours as a result of a scheduled electrical bus outage. Although SPDS, the radiation monitoring system, and communications capabilities remain unaffected, and adequate contingency measures are in place to utilize the Salem Generating Station TSC if required, the loss of normal lighting, computers, CRIDS [Control Room Integrated Display System] and dose assessment capabilities have impaired the effective and efficient use of the Hope Creek TSC. A causal investigation to determine why the impact of the electrical bus outage was not pre-identified has been directed. The plant is currently stable in Operational Condition 5. This report is being made pursuant to 10CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector and the Lower Alloways Creek Township government. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-30
43756 | 0 | NTH CONSULTANTS |  |  |  |  | 2007-10-29 12:45 | 2007-10-29 13:46 | 2007-10-29 | STOLEN TROXLER GAUGE An authorized user (AU) of the licensee called the RSO at 12:45 on 10/29/07 indicating a 3401 Troxler gauge (s/n 12664) in his possession was stolen. "The gauge was last seen at the authorized user's (AU) residence in Livonia, MI between 4:00 and 5:00 p.m. on 10/28/07. The gauge was secured to the truck bed with two cables that were threaded through the gauge case handle to prevent the gauge case from being opened. Each cable had its own lock. The gauge case lid was also locked. The source rod was locked in the shielded position. On 10/29/07, the AU drove to a secured temporary job site in Detroit, MI and stayed in or near the open bed pickup truck containing the gauge at all times. The AU identified that the gauge as missing at about noon on 10/29/07. All other equipment in the truck bed remained. The cables were not cut. All of the locks were taken. The licensee suspects that the thief cut the cable locks to steal the gauge. The licensee searched the area near the AU's residence and did not find the gauge. In addition, the licensee filed a report with its LLEA. The licensee is contemplating whether or not to notify the local media as a means of finding the gauge. The licensee is in the process of deciding what actions to take to prevent a similar event, with a focus on enhancing security, including making the gauges less visible when they are in open bed trucks." The activity of the sources are: Am-241/Be (40 millicuries) and Cs-137 (8 millicuries). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-10-29
43755 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2007-10-29 09:35 | 2007-10-29 12:03 | 2007-10-29 | PLANNED OUTAGE OF ERDADS "This notification is being made due to a planned loss of [Emergency Response Data Acquisition Display System] (ERDADS). Maintenance will be replacing a bad disc drive for the 'B' Plant Environmental Data System (PEDS) and utilizing the 'A' PEDS for restoration of software. Estimated [time for] return to service is by the end of the business day (1700) [10/29/07]." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-29
43754 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2007-10-29 | 2007-10-29 11:39 | 2007-10-30 | TRANSPORTATION ACCIDENT INVOLVING Tc-99m "A nuclear pharmacy delivery vehicle has been in an accident. The accident took place on the Chickasaw Turnpike, south of Ada, in Pontotoc County. It is at Mile Marker 14, two miles south of highway 1 and the turnpike junction. "The vehicle was a nuclear pharmacy delivery vehicle from Nutech, a nuclear pharmacy, in Wichita Falls, TX. He was returning to Wichita Falls (Nutech headquarters is in Tyler, TX, but they have a pharmacy in Wichita Falls). He was returning from making deliveries, and is believed to have had only empty containers of radioactive materials. The radioisotope involved is believed to be Technicium-99m, used in diagnostic nuclear medicine. The doses are believed to have been administered last Friday, which would mean only a slight residue would be in the containers. If the doses involved were in fact from last Friday, the radioactive component should have decayed away by now, and be non-radioactive. The pharmacy reports that the driver had new doses with him for delivery this morning, but he is believed to have delivered those before the accident. "The delivery vehicle is reported to have swerved across the median of the turnpike and struck an oncoming semi head-on. The driver was killed. Emergency responders removed the driver's body from the vehicle, but no other contact with the vehicle has been made. OHP reports that the ammunition cans used for transport of these doses are outside the vehicles, and at least one has ruptured. There is no evidence of radioactive material on the road, and OHP has left the highway open. This should be safe, even if there is full-strength Tc-99m present. "OHP and the Ada Fire Department have requested DEQ assistance in verifying the presence or absence of contamination, and a team is on their way there now. If contamination is found, it is likely that DEQ will recommend that the accident area be cordoned off until the material has decayed. "It is possible there is no hazard at all remaining here, and in any case, there is no hazard except to people in intimate contact with the wreck debris. Keep in mind that these isotopes are intended to be administered to patients, so there is nothing 'lethal' here. DEQ takes any prospect of significant radiation contamination seriously, of course. I am about to inform the NRC of the incident. "The above is based entirely on reports from OHP, Ada Fire Dept., and NUTECH. It is preliminary and may change as we get more information. There is no known media interest yet, but media interest is likely." Both the licensee RSO and Oklahoma DEQ are sending teams to investigate possible radiation at the site. It is suspected that the ammo cans are empty since the accident occurred after making deliveries. * * * UPDATE AT 10:28 ON 10/29/2007 FROM MIKE BRODERICK TO MARK ABRAMOVITZ * * * The State provided the following information via email: "DEQ inspectors [DELETED] have been to the accident scene and done surveys. The driver's body and all people who handled the driver's body were surveyed and showed no signs of radiation. They found no evidence of loose radiation contamination, but did find some intact pigs that showed some evidence of still containing radioactivity inside. They worked with the pharmacy owner to confirm that all pigs had been recovered. All syringes except two empty ones have been recovered. They were unable to find the two empty syringes despite repeated surveys of the crash area, which is covered in tall grass. The pharmacy is taking custody of all pigs and syringes, and packaging them to return them to the licensee facility. Vehicles and the body of the pharmacy driver have been removed from the accident scene. The inspectors are returning to the office. "The above is a preliminary notification based on a telephonic report from the inspectors in the field. "The pharmacy license number is Texas license L04274." Notified R4DO (Powers) and FSME EO (Kokajko). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-11-01
43753 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-10-28 22:03 | 2007-10-29 02:12 | 2007-11-13 | REFUEL FLOOR EXHAUST HI-HI RADIATION ALARMS DURING REACTOR REASSEMBLY "On 10/28/07 at 2203 in Operational Condition 5, two of three Refuel Floor Exhaust Radiation Monitors actuated on HI-HI Radiation during the Moisture Separator lift for Reactor Pressure Vessel Reassembly. Reactor Building Ventilation was procedurally secured at the time of the actuation to minimize the potential for airborne contamination. The cause of the elevated radiation levels at the Refuel Floor Exhaust Radiation Monitors is currently attributed to the lifting of the Moisture Separator closer to the surface of the water to obtain an unobstructed underwater path to the Reactor Pressure Vessel. The resulting ESF signal yielded an automatic start of the 'A' and 'D' Station Service Water Pumps, the Filtration Recirculation and Ventilation System, and load-shed of non-1E breaker loads. All systems responded as expected. Systems and components actuated by the condition have been restored to a normal stand-by alignment as required. No other systems were affected and the plant is stable in Operational Condition 5." The licensee will notify the NRC Resident Inspector. The licensee notified the Lower Alloways Creek Township. * * * RETRACTION AT 1554 ON 11/13/2007 FROM MICHAEL REED TO MARK ABRAMOVITZ * * * "Follow up investigation has revealed that the initiation of the signals was the result of radiation levels outside of the Refuel Floor Exhaust duct, and not from the in-duct activity. This would not be considered the parameter satisfying the requirements for initiation of the safety function of the system. The actual plant condition that satisfies the requirements for initiation of the safety function of the system is to detect conditions and initiate protective actions due to a release of steam or radioactive material internal to the duct that could result in the release of fission products to the environment. As a result, this is not considered a 'valid actuation' and is being retracted. Also, upon review of the refuel floor camera system, the reason for the HI-HI actuation was that during the Moisture Separator lift, the Moisture Separator broke the surface of the water by approximately 24 inches. This caused the radiation monitors to alarm on radiation shine from the moisture separator rather than airborne activity in the exhaust duct. "This notification also provides telephone notification of an invalid actuation other than actuation of the reactor protection system instead of submitting a written LER 1. This is not considered an LER 2. This report is being made under 10 CFR 50.73(a)(2)(iv)(A). 3. The resulting ESF signal yielded an automatic start of the 'A' and 'D' Station Service Water Pumps, the Filtration, Recirculation and Ventilation System (FRVS), and load-shed of non-1E breaker loads: all systems responded as expected. This was a complete actuation. All required systems started and functioned successfully." The licensee notified the NRC Resident Inspector. Notified the R1DO (Holody). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-10-29
43752 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2007-10-28 00:59 | 2007-10-28 03:24 | 2007-10-28 | MANUAL SCRAM DUE TO LOWERING INTAKE LEVEL "High winds (in excess of 40 MPH) resulted in significant debris at the plant intake. Traveling screens had been placed in 'Fast' speed and continuous wash on the previous shift in anticipation of predicted high wind conditions. As the debris entered the intake, high traveling screen differential pressure and lowering intake level prompted the operating crew to enter the appropriate Abnormal Operating Procedure (AOP). "Efforts to manually clean the screens were ineffective, and at 0059 hours, the crew inserted a manual scram as directed by procedure at 240 foot intake level. "On scram, as expected, reactor vessel level lowered to the low level scram setpoint (177 inches above top of active fuel). At this point, as expected, an automatic Reactor Protection System (RPS) actuation, and a Group 2 Primary Containment Isolation System (PCIS) isolation occurred with no anomalies noted. "During plant cooldown reactor level lowered to 177 inches above TAF. This resulted in a valid RPS actuation and a PCIS Group 2 isolation signal. All systems responded as expected. "Operators were able to maintain reactor vessel level above the actuation setpoint for High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems, and these systems were not required to operate. "The cause of the failure of the traveling screens to maintain intake level is under investigation. "All control rods are fully inserted and the plant is stable in Mode 3, Hot Shutdown." Decay heat is being removed via the turbine bypass valves to the main condenser. No SRVs lifted during the transient. The plant is in a normal shutdown electric plant lineup. The licensee notified the NRC Resident Inspector and the New York Public Service Commission. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-10-28
43751 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2007-10-23 | 2007-10-26 16:37 | 2007-10-26 | AGREEMENT STATE REPORT INVOLVING AN IMPROPERLY CONNECTED CAMERA SOURCE The following information was received via fax: "Tulsa Gamma Ray was doing some radiography work at the Coffeyville refinery and had a source hang-up on October 23. The Tulsa Gamma Ray RSO was called. He came up from Tulsa and was able to return the source to the shield after about 10 minutes using a rod to push the source. "Tulsa Gamma Ray RSO performed an investigation and discovered the radiographer did not properly attach the drive cable to the source assembly. The source was able to be pushed out but did not allow the source to be retracted. The equipment did not fail. The event occurred [due] to human error. "The personnel were instructed to properly connect the drive cable to the source assembly and verify the connection by attempting to pull the connection apart. The personnel have been given additional radiation safety training." The camera is an Amersham Model 880B (S/N 1568) containing a 73 Curie Ir-192 source. The RSO received a dose of approximately 150 mrem while reattaching the source. Tulsa Gamma Ray is an Oklahoma licensee (License No. OK-17178-02) performing work in Kansas under reciprocity permit No. 2007-013. The Coffeyville Refinery is located in Coffeyville, KS. Kansas Reference No.: KS070009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-10-31
43750 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-10-25 19:30 | 2007-10-26 14:19 | 2007-10-26 | BOTH LOW TEMPERATURE OVERPRESSURE PROTECTION SYSTEMS OUT OF SERVICE "This 8 hour report is being made pursuant to 10 CFR 50.72(b)(3)(v). On 10/25/2007 at 1930 CDT Point Beach Nuclear Plant (PBNP) Unit 1 and Unit 2 low temperature overpressure protection systems (LTOP) were declared inoperable as a result of the determination that the current LTOP actuation setpoint was non-conservative based on updated calculations. Specifically, "1) The mass input from the Safety Injection Pumps has significantly increased based on the use of a Point Beach Nuclear Plant specific system flow model. "2) The setpoint calculation does not consider instrument delay times during (PORV) Pilot Operated Relief Valve actuation. "3) The updated Calculation changes instrument uncertainties. "LCO 3.4.12 for the LTOP system is not applicable at this time for either unit (both units in Mode 1/100% power). LCO 3.4.12 is only applicable in Mode 5, Mode 6 when the reactor vessel head is on, and Mode 4 when any cold leg temperature is at or below the temperature specified in the Pressure Temperature Limits Report (270 deg F). "Changes to operating procedures to delineate operation of reactor coolant pumps and charging pumps during low temperature conditions are in progress. Implementation of these procedure changes will permit LTOP to be returned to service." The licensee stated that this issue was discovered as part of the on going calculation reconstitution initiative at the plant. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY RYAN RODE TO JASON KOZAL AT 2135 ON 10/26/07 * * * "The following is an update to the 8 hr report made to the NRC via EN#43750: "On 10/26/07 at 17:51 procedure changes which identify requirements for operation of reactor coolant pumps and charging pumps during low temperature conditions have been made. These procedures provide the guidance required to ensure that the current LTOP setpoints remain conservative. Based on the issuance of these procedures with the required guidance, LTOP is returned to service for both Unit-1 and Unit-2." The licensee notified the NRC Resident Inspector. Notified R3DO (Hills). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-10-26
43749 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2007-10-26 11:49 | 2007-10-26 12:06 | 2007-10-26 | PRESS RELEASE ISSUED DUE TO TRAIN DERAILMENT "Harris Nuclear Plant has issued a press release at 1149 EDT today related to the events previously reported to the NRC on 10/25/07. Plant operation has not been affected." The following is the content of the licensee's press release: "Rail incident on Harris Plant property reported. "The wheels of a caboose and part of an empty flatbed car came off the train tracks while accompanying a spent fuel shipping container on Harris Plant property. No injuries occurred and all rail cars remained upright and sustained no damage. "The wheels of the rail car carrying the shipping container remained on the tracks, fully upright and fully intact the entire time. There was no damage or impact to the shipping container, and there was no danger to the health and safety of the plant or the public. The rail car was moved safely into its storage location and the shipping container was not affected. "This occurred on Harris Plant property. According to procedure, the NRC and local law enforcement were immediately notified. "Plant officials report that the rail cars came off the tracks when individuals inaccurately communicated about whether the tracks were prepared for the train's movement." The licensee notified the NRC Resident Inspector. | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-26
43748 | 0 | ENERTECH |  |  |  |  | 2007-10-25 | 2007-10-25 19:10 | 2007-12-21 | POTENTIAL 10CFR PART 21 REPORTABLE CONDITION FOR ENERTECH CARTRIDGE SOLENOID VALVE The following notification was received via fax: "This submittal provides initial notification to your office that we have opened an evaluation for a potential reportable condition under 10CFR Part 21. Based on technical data provided by the San Onofre Power Plant, two (2) Enertech normally energized, normally open, cartridge solenoid valves, part number C9113S, installed on PME dump valves have not operated within the closure time design parameters. Upon investigation SCE determined higher than expected levels of contamination, internal oxidation and pitting collectively effected the valves response time. This valve was introduced to the industry in Dec 2004. Enertech is working closely with plant personnel to determine the cause of this condition, determine a resolution, and prepare a formal Evaluation Report within the next 50 days. If at any time during the evaluation process, a defect is discovered, we will provide an amended notification to this communication. "No other Power Plants have reported similar problems to Enertech. The solenoid valve under evaluation has multiple safety related applications. The following plants will be contacted if a reportable condition exists: SCE, STP, KHNP, Entergy (Waterford), and Dominion (Surry)." * * * UPDATE FROM ENERTECH (MCKOWN) TO HUFFMAN VIA FAX AT 1845 EST ON 12/21/07 * * * "Our 60 day evaluation has concluded that a 10 CFR Part 21 reportable condition does not exist regarding this issue. We have reached this conclusion on the following basis: "Our evaluation could not establish our valve has a defect, a deviation, or a departure from a technical requirement. "Enertech worked with SCE plant personnel to determine the cause of the 2 solenoid valves condition. The root cause of the failure of the inlet solenoid valve cartridges to operate was corrosion buildup at poppet flow orifice. "Enertech was unable to duplicate the SONGS Unit 3 experience using valves that had been exposed to trapped hydraulic fluid with high water content for periods of 20-26 months. We inspected and tested valves in our inventory and valves previously shipped to other sites, resulting in no observed corrosion. Concluding the event did not have a common mode failure. "The solenoid valve cartridge has been used by a significant number of nuclear utilities, including SONGS Unit 2, without identifying similar situations to those experienced at SONGS Unit 3." R4DO (Pruett), R2DO (Shaeffer) and the Part 21 Coordinators (Hodge and Thorp via e-mail) have been notified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-10-25
43747 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-10-25 14:10 | 2007-10-25 16:46 | 2007-10-25 | SAFEGUARDS EVENT - ACCESS GRANTED TO UNAUTHORIZED INDIVIDUAL Access was granted to vital areas to an unauthorized individual. Immediate compensatory measures taken upon discovery. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-10-25
43746 | 0 | KARMANOS CANCER CENTER |  |  |  |  | 2007-10-24 14:00 | 2007-10-25 11:40 | 2007-10-26 | GAMMA KNIFE TREATMENT TO WRONG SIDE OF BRAIN "On October 24, 2007, a medical event occurred at Leksel Gamma Knife facility which resulted in the total dose delivered differing from the prescribed dose by more than20%. "1. Licensee's name: Karmanos Cancer Center. "2. Name of prescribing physician: [DELETED] "3. Brief description of the event: "Due to a left - right reversal of the treatment planning MRI images, the patient's left side was targeted and treated rather than the right side. The error resulted in an 18 mm shift of isocenter across midline of the brain. The collimator diameter selected for the treatment was 18 mm, thus resulting in some overlap of the delivered 50% isodose volume with the correct intended target lesion volume. The event resulted in approximately 7% of the lesion volume receiving the prescribed dose of 18 Gy to the 50% isodose, rather than the preferred 95% of the lesion volume. "4. Why the event occurred: "During the pre-treatment setup and simulation MRI imaging, a 'feet first' scan technique was used with the patient positioned in the MRI scanner head first. This had the effect of reversing the axial images left to right. The standard of practice in gamma knife radiosurgery is to position the patient in the MRI scanner head first, and to use the 'head first' scan technique. The gamma knife authorized medical physicist (AMP) failed to recognize the scanning error when importing the MRI images into the Gamma Knife treatment planning computer, and subsequently registered them as head first. This resulted in the wrong side of the patient being targeted and treated, i.e. the left cerebellum was targeted and treated rather than the right cerebellar lesion. "5. The effect on the individual who received the administration: "To be determined. "6. What actions have been taken or are planned to prevent recurrence: "For all future gamma knife cases, left/right alignment of the MRI images will be inspected by the AMP by using the Leksel anterior face plate with fiducial markers visible in the MRI images. A Gamma Knife MRI protocol will be written and posted in the MRI department and in the Gamma Knife suite. The protocol will clearly indicate the patient and scan orientation required for Gamma Knife planning and delivery, which are patient on table head first, with head first scanning protocol. "7. Certification that the licensee notified the individual, and if not, why not: "The referring neurosurgeon will be notified this evening after he finishes with surgery." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE AT 08:13 ON 10/26/2007 FROM GREG MORELL TO MARK ABRAMOVITZ * * * This event has been reviewed and determined to be a reportable medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-10-27
43745 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2007-10-25 10:00 | 2007-10-25 11:20 | 2007-10-25 | AGREEMENT STATE REPORT - STOLEN SOIL DENSITY GAUGE State called indicating licensee reported a Humboldt soil density gauge, Model 5001B (s/n 2978) was stolen from the back of an employee's pickup truck sometime during the night of 10/24/07. The gauge was chained down (but was cut) while parked at the employee's personal residence. The source activity is 44 mCi of Am-241/Be and 11 mCi of Cs-137. A police report was filed with the Tulsa police department, Report # 2007-074-103. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-10-30
43744 | 0 | MEAD JOHNSON & COMPANY |  |  |  |  | 2007-10-11 | 2007-10-25 10:25 | 2007-10-25 | MISSING N-63 FOIL SOURCE DETECTORS Back in 1992 licensee had four detectors stored at their facility in Evansville, IN. These 4 detectors had Ni-63 foil sources with activity of 15 milliCuries each. The model/serial number of these detector are 18803-60520/C2141; 18803-60520/C0844; 18713A/83047; and 19312/S11091. About September 2007 the licensee went to retrieve these electron capture detectors, however, they could not find them. The licensee contacted Hewlett Packard (HP) and asked if they had the missing detectors. HP said they did not. After several weeks of searching , the Licensee believed that the missing detectors are a result of inventory accountability, rather than an actual theft. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-10-25
43743 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-10-24 15:30 | 2007-10-24 16:48 | 2007-10-25 | FLORIDA AGREEMENT STATE REPORT - STOLEN/LOST TROXLER MOISTURE DENSITY GAUGE "Licensee called 10/24/07 at 1640 hours and reported that a Troxler gauge is missing. It was last seen on 10/24/07. Troxler gauge was sitting on tailgate while operator was writing paperwork in vehicle cab. Operator drove off with gauge on tailgate. Wingerter employees searching area for gauge. It was reported missing to the North Miami PD. The Radioactive Materials Office is investigating. No further action will be taken by this office." Incident Location: Intersection of Curtiss Drive and Pervis Avenue Opalocka, FL Isotope(s) Cs-137; Be:Am-241 Activity(s): 8mCi; 40mCi Material Form: Chemical Form; Physical Form: By-product; Special Form Probable Disposition of Material: Material stolen and not recovered. Emergency Groups at Scene: North Miami PD Incident Number: FL07-163 * * * UPDATE PROVIDED BY STEVE FURNACE TO JASON KOZAL ON 10/25/07 AT 1308 * * * The lost Troxler was recovered by the licensee at the intersection of NW 103rd St and NW 27th Ave Opalocka, FL. The device appears to have fallen off the vehicle tailgate at this location. The case was damaged but the source remained unharmed and locked in the shielded position. Surveys taken revealed no external contamination or indication of leakage. The device will be returned to the manufacturer for repair. Notified R1DO (Caruso), ILTAB (Via E-mail) and NMSS EO (Morell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-10-29
43742 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2007-10-23 23:05 | 2007-10-24 00:21 | 2007-10-24 | ALERT DECLARED DUE TO ELECTRICAL FIRE IN THE AUXILIARY BUILDING At 2305 an Alert condition was declared based on Emergency Action Level (EAL) 7.6, "Fire or Explosion Onsite Affecting One Train of ESF Systems." The fire was out at the time of the notification. There was no gaseous radiological release. There were no injuries. The plant continues to operate at full power. The licensee is still assessing the full impact of any damage. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0044 ON 10/24/07 FROM JEFF GERARD TO PETE SNYDER * * * "Smoke is dissipating." The Alert condition is still in effect. There is no radiological release. There was no explosion. * * * UPDATE AT 0256 ON 10/24/07 FROM FRED VAN BUSKIRK TO PETE SNYDER * * * The Alert condition was terminated at 0133 CDT since inspections of the local area confirmed that the fire had been extinguished. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 4 | AR | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-10-24
43741 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2007-10-23 14:37 | 2007-10-23 16:20 | 2007-10-23 | OFFSITE NOTIFICATIONS MADE DUE TO OIL SHEEN SEEN IN HUDSON RIVER "This afternoon, an intermittent oil sheen was observed in the discharge canal and ultimately it reached the Hudson River. Efforts to find and secure the source of the oil are on-going. The NYSDEC (New York State Department of Environmental Conservation) , WCDOH (Westchester County Department of Health) , and US Coast Guard have been notified. "Immediate Action Description: Attempted to determine source of the oil. Initiated regulatory notification "Suggested Action Description: Continue with efforts to determine the source of the oil and secure it." NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-23
43740 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 1976-10-22 14:00 | 2007-10-22 16:19 | 2007-10-22 | OFFSITE NOTIFICATION DUE TO A SMALL LEAK - TRITIUM "On October 20, 2007, Surry Power Station workers detected a minor water leak from an underground concrete storm drain pipe inside the station's protected area. This storm drain line flows into the station discharge canal and is monitored by station personnel. Workers had excavated this pipe to conduct inspection activities when they noticed water leaking at a rate of 1 to 2 drips per minute from a pipe joint. The leak rate was estimated at one-half a gallon per day. "A sample of the leaking water was evaluated for tritium as part of an industry ground water protection initiative and determined to have a concentration of 31,900 picoCuries per liter. This tritium leak poses no threat to employees or the public. There is no indication that tritium has migrated off the Surry site undetected. Monitoring wells on the perimeter of the Surry site and on-site drinking water well samples have not shown any indication of tritium. Leakage from this section in the storm drain line is ultimately recaptured by the building foundation dewatering system surrounding adjacent site structures and returned to the storm drain line. "This leak has been contained and maintenance activities are under way to repair the storm drain line. "This notification is being transmitted due to Notification of Other Government Agencies under 10CFR50 72(b)(2)(xi) The Surry County Administrator was notified. The Senior NRC Resident, Virginia Department of Health, Virginia Department of Emergency Management and Virginia Department of Environmental Quality will be notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-22
43739 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-10-15 17:30 | 2007-10-22 14:21 | 2007-10-22 | CALIFORNIA AGREEMENT STATE REPORT Received the following information via e-mail: "On October 22, 2007, a letter, dated 10/17/07, was received from Haytham (deleted), RSO, reporting a stolen nuclear gauge (Troxler 3400 Series, S/N 14411). The incident happened on 10/15/07 at San Bernardino County. According to the incident report, the nuclear gauge was taken to Southwest Calibration in San Bernardino for repair. After the repair, at about 5:30 pm, the field technician stopped at an automobile garage in San Bernardino to have the company truck tail light repaired. The nuclear gauge metal box was bolted close to the tail light access location and was asked by the shop technician to remove the box so they can repair the tail light. The metal box was placed on the side near the waiting room. Then, the technician went inside the waiting room. After the tail light was repaired, the technician went outside and did not find the nuclear gauge. "The technician called the RSO and left a message. The incident was reported to San Bernardino County Sheriff's Office (Police Report # 030705898) and an ad was placed in the 'SUN', San Bernardino newspaper for seven days. "RHB - South RAM office will investigate this incident." 5010 Number (Date Notified): 102207 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-10-25
43738 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-10-22 11:20 | 2007-10-22 13:18 | 2007-10-25 | DISCOVERED DEGRADATION IN SAFEGUARD SYSTEM Discovered a vulnerability in a safeguards system that could have potentially allowed access into a controlled access area. Compensatory measures were immediately taken upon discovery. Contact HOO for further details. The NRC Resident Inspector will be informed of this notification by the licensee. * * * RETRACTION PROVIDED BY JOHN FEIGL TO JASON KOZAL AT 1824 ON 10/25/07 * * * After further evaluation the vulnerability in a safeguards system that could have potentially allowed access into a controlled access area did not exist. Contact HOO for further details. The NRC Resident Inspector will be informed of this notification by the licensee. Notified R2DO (Hills) and 73.71 Group | 0 | 98 | 99 | 0 | 98 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-10-22
43737 | 0 | AGILENT TECHNOLOGIES |  |  |  |  | 2007-09-27 12:00 | 2007-10-22 10:16 | 2007-10-22 | LOST ELECTRON CAPTURE DETECTOR On 6/20/07, a previously manufactured electron capture detector was returned to the New Castle, DE facility because it was not able to reach its final shipment destination. The detector was stored in an area for returned shipments containing radioactive materials. On 9/27/07 the licensee attempted to locate the device for proper dispositioning but could not find it. The licensee ensured that employees knew the description and labeling of the box. The licensee then conducted a search of the entire building but was unable to locate the device. The device contained a 15 millicurie Ni-63 source. As part of their corrective actions the licensee ensured that the employees were trained in their responsibilities concerning this type of material. In the future the licensee plans to increase the frequency of periodic training. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-10-22
43736 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2007-10-22 03:11 | 2007-10-22 09:27 | 2007-10-22 | SHUTDOWN DUE TO INOPERABLE STEAM DRIVEN AUXILIARY FEEDWATER PUMP "The following report is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "On Monday October 22, 2007, at 0311 Mountain Standard Time (MST) Palo Verde Nuclear Station Unit 1 initiated a normal reactor shutdown to comply with condition C of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.7.5. At 0504 MST Mode 3 was entered. "LCO 3.7.5 requires that three auxiliary feedwater (AF) pumps be operable in Modes 1, 2, and 3. The shutdown was necessary due to an inoperable steam supply for the essential steam driven AF pump turbine. The steam supply had been declared inoperable on October 15, 2007, at 0904 MST and will not be restored to operable status within the TS required 7 day completion time. Efforts are in progress to correct the condition. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-10-22
43735 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-10-19 18:30 | 2007-10-19 19:55 | 2007-10-19 | TECH SPEC REQUIRED SHUTDOWN DUE TO ULTIMATE HEAT SINK INOPERABILITY "lnitiated Unit 1 and Unit 2 plant shutdown due to inoperability of ultimate heat sink system. The inoperability is due to structural integrity failure of ASME Class 3 piping through wall leakage of the 0C Essential Service Water riser piping of the mechanical draft cooling tower." Licensee is in Technical Specification 3.7.9 which requires the units be in Mode 3 in 6 hours and Mode 5 in 36 hours. The licensee has notified the NRC Resident Inspector. | 75 | 75 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-10-19
43734 | -1 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2007-10-19 04:00 | 2007-10-19 18:43 | 2008-01-02 | AGREEMENT STATE REPORT - PATIENT OVEREXPOSURE GREATER THAN 50 REM A patient intervened during a vaginal iridium seed implant treatment by removing one of the needles from her body. The needle was found by a nurse approximately 30 minutes after it had been removed by the patient. The needle was located at the foot of the bed near the patients right foot and ankle. The doctor directed the nurse to place the source back into the pig. There were six sources in the needle. Total activity is 7 milliCuries of Ir-192. The estimated dose to the nurses hand was 13 milliRem, and she was wearing a whole body dosimeter, which is being examined. The estimated dose to the patients right ankle is 4.6 to 165 Rem. The patient will be monitored for acute radiation signs. The patient is in the process of receiving the planned dose. * * * UPDATE PROVIDED BY MELANIE RASMUSSON TO JEFF ROTTON AT 1123 EST ON 01/02/08 * * * The State of Iowa received a recent update stating that the licensee concluded that the patient's intended dose with IMRT (external beam Intensity Modulated Radiation Therapy) and the dose to the exposed areas of the patients' legs and ankles from the removed source showed no signs of skin reaction as of December 5, 2007 and was due to patient intervention. They are going to continue to follow the patient and said that they would keep the State of Iowa informed. Notified R3DO (Louden) and FSME (Flannery) A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2007-10-25
43733 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-10-19 | 2007-10-19 18:10 | 2007-10-19 | POTENTIAL RECOVERY OF LOST OR STOLEN TROXLER MOISTURE DENSITY GAUGE A local citizen contacted the State of Florida to report that he had a Troxler moisture density gauge Model 3440, S/N 22605 in his possession for a year. The individual stated that he took the gauge from his deceased neighbors home, and that the neighbor had told him he found the gauge in a field. The state representative was informed by the NRC Operations Center that this device was reported stolen from the U.S. Army Corps of Engineers in FT. Polk, LA in March 2002 and documented on NRC Event Report #38806. The state is going to retrieve the gauge this evening. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-10-24
43732 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2007-10-17 18:30 | 2007-10-19 15:21 | 2007-10-19 | OFFSITE NOTIFICATION DUE TO TRANSPORTATION PACKAGE REQUIREMENTS NOT BEING PROPERLY MET On October 17, 2007 at 1830, a regularly scheduled shipment of four UF6 cylinders from URENCO in Almelo, Netherlands did not have tamper proof seals on the outer overpack. This is a violation of the Certificate of Compliance for the package shipping requirements. The shipment was prevented from entering the site and is currently in a secure location under guard view and video surveillance at the site's entry control point. The licensee made a courtesy call to the Richland County Emergency Agency, and the South Carolina Department of Health and Environmental Control. The licensee also intends to formally notify the DOT of this event. The licensee is in contact with the manufacturer of the shipment and is working to resolve the issue. The licensee has notified NRC Region 2 Fuel Cycle Branch personnel. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2007-10-19
43731 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-09-24 | 2007-10-19 09:55 | 2007-10-20 | AGREEMENT STATE REPORT INVOLVING AN IMPROPER INJECTION The following information was received from the Louisiana Department of Environmental Quality via fax: "On September 24, 2007, a customer called the pharmacy to inform them that a Tc-99m mertiatide prescription for renal imaging showed no renal distribution and instead showed only liver distribution. After an investigation by the licensee, it was determined that the error occurred in the pharmacy and all customers who could have been affected by the event were notified. Only one of the patients was injected. The radiation dose to the patient involved was minimal. Procedures not followed is the root cause of this incident. The corrective actions for this incident include retraining on policy and procedures regarding compounding doses. "Event Report ID No.: LA070028" * * * UPDATE PROVIDED BY CINDY FLANNERY (FSME) TO JEFF ROTTON AT 1243 ON 10/19/07 * * * This event (EN43731) has been reviewed and determined to not meet the definition of a medical event. Notified R4DO (Proulx) and FSME EO (Flannery). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-10-25
43730 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-10-18 12:15 | 2007-10-18 14:53 | 2007-10-18 | AGREEMENT STATE REPORT - LOST AM241/BE SOURCE FROM DAMAGED TROXLER GAUGE MODEL 3430 The State provided the following information via email: "On October 18, 2007, the agency was contacted at 12:49 p.m. by their emergency answering service, reporting that a licensee had lost a gauge in Houston and was requesting Incident Investigation Program (IIP) to call them back to assist them with [the lost gauge]. "IIP called the licensee back and talked with [DELETED], Site RSO for their LaPorte, TX location. [RSO] reported that his technician was driving down the highway in Houston and discovered that the gauge had fallen out of his truck around 12:15 -12:30 p.m. on 10/18/07. The RSO stated that the tailgate was up, but the gauge may not have been braced down. "The technician immediately called the RSO, who drove down the highway and found pieces of the gauge, the handle, and the Cs-137 source. The RSO stated the Cs-137 source is intact. He remains on location with the agency's investigator. The agency's investigator has surveyed the area and the gauge pieces that were recovered with a NaI detector and was not able to locate the AmBe source. "The gauge specifications are: Mfg: Troxler Model 3430, Serial #: 29328, Last Leak test: 10/11/07 "Source Information: 1) Cs-137 Serial #: 750-2544; 8 mCi 2) AmBe Serial #: 47-26370; 40 mCi. The source is double-encapsulated in stainless steel, with dimensions of: .4 in.x.3 in. and is less than 1/2 in. long and 1/4 in. in diameter. "Mfg states that the chance of the source encapsulation being broken and breached is remote. "The agency has notified local law enforcement (LLE) to shut down the 3-lane highway (so that) safe surveying for the AmBe source can be accomplished. The agency has asked LLE to contact and coordinate with the local HAZMAT team. IIP will continue to investigate and assist with locating the lost AmBe source. Additionally, the licensee was given contact information for two consultants to assist with this incident and location of the lost source. Incident Investigations will continue to update this incident as current information is received. "Disposition/Action Taken: 1) Report to NRC and NMED, 2) Contacted local law enforcement (LLE) and local HAZMAT. "Texas Incident Number: I - 8449, Event Report: TX-07-43606" * * * UPDATE FROM ART TUCKER TO JOE O'HARA AT 2125 ON 10/18/07 * * * The state along with DOD personnel performed a search of highway 225 for the missing source. However, the search was unsuccessful. The highway has been reopened, and the state will meet tomorrow to discuss further follow-up actions. Notified R4DO(Proulx), FSME EO(Tschiltz), ILTAB(e-mail), and Mexico(fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-10-23
43729 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2007-09-15 | 2007-10-18 12:36 | 2007-10-18 | INVALID PRIMARY CONTAINMENT ISOLATION "This notification is being made in accordance with 10CFR50.73(a)(2)(iv)(A) to provide information pertaining to an invalid Primary Containment Isolation System (PCIS) Group 3 actuation signal that affected containment isolation valves in more than one system. "On 09/15/07, with the reactor at 100% power, an invalid PCIS Group 3 actuation occurred from a momentary spike of the 'A' Refuel Floor radiation monitor which reached the instrument's high radiation trip setpoint. Radiation protection technicians dispatched to the refuel floor verified dose rates in the vicinity of the 'A' radiation monitors detector to be normal and below the alarm set points. The radiation monitor was verified to be indicating normally to expected radiation levels. Subsequent visual inspection and functional checks of the radiation monitor were completed satisfactory and the instrument channel was returned to service. The cause of the spurious spike is attributed to an unknown source of electrical noise. "Both trains of the Standby Gas Treatment System started as designed and Reactor Building ventilation isolated. The train actuation was complete. "The PCIS functioned successfully providing a complete Group 3 isolation. The PCIS Group 3 isolation involves the following systems and isolation valves: Drywell and Suppression Chamber air purge and vent: V16-19-6, 6A, 6B, 7, 7A, 7B, 8, 9, 10, 23 Containment Makeup: V16-20-20, 22A, 22B Containment Air Sampling: VG-23, 26, V109-76A, 76B Containment Air compressor suction: V72-38A, 38B Containment Air Dilution: VG-9A, 9B, 22A, 22B, NG-11A, 11B, 12A, 12B, 13A, 13B "In accordance with 10CFR50.73(a)(i) a telephone notification is being made instead of submitting a written Licensee Event Report." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-10-18
43728 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-10-16 22:30 | 2007-10-17 13:53 | 2008-05-11 | REPORTABLE QUANTITY OF WASTE ACID RELEASED ONSITE "A second-shift Waste Treatment operator discovered acidic wastewater (a mixture of nitric acid, hydrofluoric acid and water) discharging from a sump on the Bay 5A Pickle Acid Scrubber pad at approximately 10:30 PM on 10/16/2007. The acidic wastewater ran downhill onto the roadway to the north and eventually onto a concrete pad near the bottom of the hill. By the time of the discovery, or very shortly thereafter, the overflow stopped. The operator notified area supervision and verified that all valves and pumps at the Waste Treatment facility were functioning normally and wastewater was being received in the equalization tanks. "Estimates on 10/17/2007 by Environmental Engineering of the amount of flow discharged to the line versus the amount received at Waste Treatment, combined with visual observation of the spill area, suggest that approximately 275 gallons of acidic wastewater were released from the trench, of this amount, approximately 25 gallons potentially reached uncovered surfaces adjacent to the road (gravel/grass). This was deemed to be a Reportable Quantity of a hazardous substance and appropriate notifications were made to the National Response Center (Notification #851841), the EPA Region 11 Consent Order Coordinator and the Virginia Department of Environmental Quality. "The spill area was neutralized with soda ash and thoroughly rinsed. The small gravel/grass areas that may have been impacted are being assessed for additional remediation as necessary." BWXT will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2007-10-22
43727 | 0 | ONCOLOGY INSTITUTE OF GREATER LAFAY |  |  |  |  | 2007-08-14 | 2007-10-17 11:39 | 2007-10-17 | POTENTIAL MEDICAL EVENT A patient received a series of 3 vaginal cylinder HDR treatments on 08/14/07, 08/28/07, and 09/11/07 at the Arnett Cancer Care Center [also known as the Oncology Institute of Greater Lafayette which is the name on their license]. The treatment was planned with a source spacing of 5 millimeters. The electronic transfer of source spacing from the planned console to the treatment console did not function properly and the source spacing information was entered into the treatment console manually and inadvertently a source spacing of 2.5 millimeters was used. The dose distribution was different than planned due to the spacing difference, but the overall dose was correct. The prescribed dose per fraction was 700 cGray using an Ir-192 source with 13 dwell positions spaced 5 millimeters apart. The physician has been notified and does not believe that there will be any adverse effects to the patient. At this time the patient has not been notified, but the licensee is attempting to contact her to inform her that the overall dose was delivered differently that planned. The licensee has taken corrective action to set the device default spacing at 5 millimeters and they will be revising their procedures to prevent reoccurrence. An inspection by the NRC Region 3 Inspector (Bob Gattone) on 10/16/07 discovered the source spacing error. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-10-23
43726 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-10-12 | 2007-10-17 09:13 | 2007-10-17 | AGREEMENT STATE REPORT - LEAKING I-125 PROSTATE BRACHYTHERAPY SEED "Patient was implanted with 100 Iodine 125 seeds (0.36 milliCuries per seed) on Friday October 12, 2007. Five (5) seeds were left over. The 5 leftover seeds were emptied from the loading cartridge into a lead pig. The cartridge was deposited in the regular trash. The leftover seeds were assayed by [DELETED], Rad Safety Tech on October 16, 2007. After assaying the seeds, [DELETED] surveyed the lead pig, and discovered elevated exposure rates of the empty pig. Further surveys and wipes indicated removable contamination of the lead pig. "The five Iodine 125 seeds were leak/wipe tested, and one seed showed 0.02 microCuries of removable contamination (29,000 dpm). The loading cartridge was tracked down in the regular trash, and showed removable contamination. The patient was recalled, and a thyroid scan of the patient on 10/16/07 showed no elevated thyroid uptake. The surgeon [DELETED] and all surgical staff showed no removable contamination. The surgery suite and all adjacent/pertinent areas showed no removable contamination. "The leaking source has been packaged, and is ready to be shipped back to Core Oncology, Oklahoma City for evaluation. Mills Pharmaceuticals (Core Oncology) manufactures sources. "North Carolina Incident No. 07-52" A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-10-23
43725 | 0 | CTI & ASSOC. INC. |  |  |  |  | 2007-10-16 11:00 | 2007-10-16 16:05 | 2007-10-16 | DAMAGED TROXLER MOISTURE DENSITY GAUGE 10/16/07 at 1100 EDT a Troxler 3401; 8 millicuries Cs-137 and 40 millicuries Am-241/Be, was run over by a bulldozer while the gauge operator was driving the drive rod into the ground (was going to test the compaction of the soil). The gauge operator was about 15 to 20 feet away from the gauge when it was run over. The top handle and the top of the source rod were sheared off. The Radiation Safety Officer came to the site and took surveys. Surveys found no contamination and the gauge is presently in its locked position on the tail of a truck. The survey readings of the gauge from 2 feet away ranged from 0.06 to 0.1 millirems per hour (survey readings were taken using a TroxAlert meter). The RSO will have the gauge leaked tested and then he plans to ship the gauge back to Troxler for repairs/disposal. Serial number of the gauge is 5323. This incident occurred at 6825 West Jefferson Ave., Detroit, MI at a basement excavation site. NRC Region 3, Darrel Wiedeman, was notified of this incident by Jim Meehle. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-10-16
43724 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-10-15 12:00 | 2007-10-15 18:29 | 2007-10-15 | MASSACHUSETTS AGREEMENT STATE REPORT The following agreement state report information was faxed to the NRC Operation Center. "Description: Thickness gauge "Investigation Pending: No "Consultant Hired: Yes "Corrective Action: Licensed Contractor fixed the gauge "SUBJECT: A gauge on the Z-25 press is sometimes stuck closed. The equipment is out of use. "Equipment problem : Shutter was not working properly. Equipment problem, capacitor fell off." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-10-18
43723 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2007-10-15 09:50 | 2007-10-15 13:16 | 2007-10-15 | OFFSITE NOTIFICATION TO FLORIDA DEPARTMENT IF ENVIRONMENTAL PROTECTION (FEDP) "At 0950, the Florida Department of Environmental Protection (FDEP) was notified in regards to a Turbine Lube Oil spill of approximately 350 gallons. The notification, to the FDEP, was required due to the inability to reach clean-up target levels within 30 days. In addition, the State Warning Point was notified at 1010. This non-emergency notification is being made, pursuant to 10 CFR 50.72(b)(2)(xi), due to the notification of outside government agencies in response to this environmental event. The cause of the oil spill is still under investigation." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-15
43722 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2007-10-13 02:20 | 2007-10-13 05:15 | 2007-11-07 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE CONTROL RODS "Susquehanna Unit 1 was being manually shutdown on 10/13/2007 for a planned maintenance outage to address control cell friction. Prior to the shutdown five control rods had been declared inoperable due to control cell friction. When reactor power was lowered to 10% at 0220, entry into Tech Spec 3.1.3 was required for 'One or more BPWS groups with four inoperable control rods'. The completion time for this specification is 4 hours. The inoperability of the control rods condition cannot be cleared in the specified time. This condition results in the unit being in a 'Shutdown Required By Technical Specifications'. The required action is to be in Mode 3 within 12 hours. The Shutdown required by Technical Specifications is reportable as a 4 hour Non-Emergency report under 10 CFR 50.72(b)(2)(i). "Manual insertion of control rods will continue until all rods are fully inserted. Hot Shutdown is expected by 0800, 10/13/07. "Shutdown activities will continue to place the unit in cold shutdown. "A Press Release will be made concerning the planned maintenance outage." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1438 ON 11/7/2007 FROM TODD CREASY TO MARK ABRAMOVITZ * * * "On October 13, 2007, Susquehanna operators began the process of shutting down Unit 1 for a planned maintenance outage to address known control cell friction issues. Because four of five control rods declared inoperable during the operating cycle were located in the same Banked Position Withdrawal Sequence (BPWS) group, station personnel realized that conditions for entry into Technical Specification (TS) 3.1.3 'Control Rod Operability' Condition E would already be met when thermal power reached 10% rated thermal power during the shutdown. (NOTE: TS 3.1.3 Condition E is not applicable when thermal power is > 10%). With power less than or equal to 10%, TS 3.1.3 Condition E mandates restoration of control rods to operable status within 4 hours. If this 4 hour completion time is not met, TS 3.1.3 Condition F mandates that the plant enter Mode 3 (Hot Shutdown) within the next 12 hours. At 0220 hours on October 13, power was lowered to 10% power and TS 3.1.3 Condition E was entered. Control Room personnel, anticipating that the 4 hour restoration window allowed by Condition E would expire before the LCO could be cleared, reported the shutdown as a shutdown required by Tech Specs per 10 CFR 50.72(b)(2)(i). The ENS report was made proactively before the 4 hour restoration window had expired. Subsequently, the Unit 1 mode switch was placed to Shutdown (Mode 3) at 0610 hours on October 13. Because the timing of this mode change was within the 4 hour restoration window provided by TS 3.1.3 Condition E and because TS 3.1.3 is no longer applicable once Mode 3 is attained, the Condition requiring shutdown (Condition F) was never entered as a result of the inoperable BPWS rods as was initially reported via EN #43722. "However, TS 3.1.3 Condition F can also be directly entered if nine or more control rods become inoperable. As the controlled shutdown Progressed, four additional control rods had been conservatively declared inoperable because they failed to settle at latched position '00' in a reasonable period of time. (Note: LER reports 50-387/2005-002-00 and 50-387/2006-001-00 have previously discussed control rod friction experienced at Susquehanna.) Accordingly, TS 3.1.3 Condition F was entered at 0343 hours on October 13, 2007. This TS entry constitutes the initiation of a nuclear plant shutdown required by the plant's Technical Specifications and is thus reportable per 10CFR50.72(b)(2)(i). "Sufficient compensatory measures had been enacted such that TS 3.1.3 Condition F was no longer applicable by the time the controlled plant shutdown was completed. Therefore, the 60-day reporting that is necessary when a nuclear plant shutdown is completed per a plant's Tech Specs does not apply. (Reference: 10 CFR 50.73(a)(2)(i)(A)) The licensee notified the NRC Resident Inspector. Notified the R1DO (Miller). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-10-13
43721 | 0 | THOMAS, DEAN, & HOSKINGS |  |  |  |  | 2007-10-12 | 2007-10-12 18:07 | 2007-10-12 | DAMAGED TROXLER MOISTURE DENSITY GAUGE A Troxler moisture density gauge was damaged by construction equipment that backed up over the gauge after it had been placed on the ground in preparation for taking soil density measurements. The incident occurred at a Great Falls MT construction site. The source rod was still in the safe shielded position when run over. The gauge housing was damaged but there was no apparent damage to the gauge sources. The rod source was confirmed to still be present in the gauge. There was no contamination found. The damaged gauge was placed into its shipping container. The sources will be leaked tested prior to shipment to Troxler for repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-10-12
43720 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2007-10-12 16:04 | 2007-10-12 18:02 | 2007-10-12 | OFFSITE NOTIFICATION MADE DUE TO ELEVATED LEVELS OF TRITIUM "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to the fact that Exelon Nuclear has informed the Illinois Emergency Management Agency and Illinois Environmental Protection Agency of recent groundwater monitoring results at Quad Cities Station. This notification was made at 16:04 hours CDST on October 12, 2007. "As part of the Station's continuing environmental monitoring and sampling program, new wells were recently installed on Station property to better characterize the known, on-site tritium plume previously identified during Exelon's fleetwide tritium study conducted in 2006. Samples from some of the new wells have indicated elevated levels of tritium requiring notification of the State of Illinois. "Based on well data to date, the tritium in the groundwater is confined to Exelon property and poses no threat to public health or safety. "The Station continues to track this issue by monitoring the existing wells, installing new wells for further assessment, and pursuing underground pipe integrity testing." The NRC Resident Inspector was notified of this event by the licensee. | 97 | 96 | 0 | 97 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-12
43719 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2007-10-12 13:30 | 2007-10-12 14:52 | 2007-10-12 | UNANALYZED CONDITION AFFECTING FIRE SAFE SHUTDOWN "During an engineering review it was discovered that for certain fire scenarios affecting the auxiliary building west motor control center - rod control room, the previously established fire safe shutdown strategy might not be successful. Specifically, for a fire in the west motor control center - rod control room, fire safe shutdown would be accomplished utilizing an unaffected charging pump. During an engineering review, a vulnerability was identified in which under certain circumstances the spurious closure of a charging pump suction valve could result in a loss of the running charging pump and the unavailability of the remaining charging pumps due to potential fire damage. The result is that all charging pumps could be affected by the fire and be unavailable to support fire safe shutdown in accordance with established procedures. "Compensatory actions to minimize risk of fire in areas of concern are being implemented. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." The licensee has also notified appropriate State and local authorities. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-10-12
43718 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-10-12 08:02 | 2007-10-12 11:07 | 2007-10-12 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "At 0802 [CDT] on 10/12/2007 with Unit 1 at 100% power, an automatic reactor scram was received due to a turbine trip. Unit 2 and 3 were also at 100% power and were unaffected by the event. All expected PClS isolations, Group 2 (RHR Shutdown Cooling), Group 3 (RWCU), Group 6 (Ventilation), and Group 8 (TIP) were received along with the auto start of CREVs and 3 SBGT trains. "This event is reportable as a 4-hour and 8-hour non-emergency notification along with a 60-day written report in accordance with 10 CFR50.72(b)(2)(iv)(B), 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(A) as 'any event or condition that results in valid actuation of RPS or PCIS'. "All control rods fully inserted, the electrical grid is stable, the EDGs and ESF systems remain available, and decay heat is being removed via the Turbine Bypass Valves. The licensee notified the NRC Resident Inspector. "The cause of the turbine trip is under investigation." The 1D RHR pump is OOS for planned maintenance. Isolations occurred as a result of low reactor water level +2 inches. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-10-12
43717 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2007-10-11 21:47 | 2007-10-12 04:34 | 2007-10-12 | LOSS OF ERDADS/SPDS DISPLAY "On 10/11/2007 at 2147, the ERDADS SPDS displays for Unit 1 were discovered out of service, rendering the majority of process parameters and trends unreadable from the display screens in the control room, TSC, and EOF. This information was also not available to the NRC via the ERDS. However, the process parameters and alarm capabilities are available to operating personnel via redundant control room and plant instrumentation. Information regarding main steam line radiation monitoring, meteorological data, and information provided by the Qualified Safety Parameter Display System (QSPDS) (i.e. RCS sub cooling, reactor vessel level, and core exit temperature) is available on the ERDADS terminals and is also available to the NRC via the ERDS. The ERDS Link to the NRC from both Unit 1 and Unit 2 remains functional. Troubleshooting by the site maintenance and engineering personnel is ongoing. This Non-Emergency Notification is being made pursuant to 10CFR50.72(b)(3)(xiii) regarding loss of emergency assessment capability." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-12
43716 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-10-11 13:34 | 2007-10-11 21:37 | 2007-10-11 | POSITIVE FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2007-10-11
43715 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-10-11 05:40 | 2007-10-11 17:03 | 2007-10-11 | STEAM LEAK PAST A SAFETY RELATED O-RING "[This event occurred at] 10-11-07 at 0540 hrs in the X-342 - Feed Facility, Autoclave #1, approximately 40 minutes into the heating cycle (mode II) on a refeed cylinder. An operator encountered an audible steam leak past the Viton 'O' ring at the 12 o'clock position. The steam was secured and autoclave shell opened. Inspection of the Viton 'O' ring resulted in the discovery of a separation of the splice joint. A pressure decay was performed to determine if the O- ring would have performed its 'Q' function. The test failed resulting in a 24 hour event." The licensee has contacted the Regional NRC inspector for this facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-10-11
43714 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-10-11 14:41 | 2007-10-11 15:11 | 2007-10-11 | UNAUTHORIZED UNESCORTED ACCESS GRANTED TO FACILITY A contract employee was granted unescorted access to the plant protected area based on erroneous drug testing results. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-10-11
43713 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2007-10-11 13:00 | 2007-10-11 13:19 | 2007-10-31 | UNUSUAL EVENT DECLARED DUE TO POTENTIAL TAMPERING Immediate corrective actions taken upon discovery. Resident inspectors, State & Local authorities have been notified. Call HQ Operations Officer for further details. * * * UPDATE ON 10/12/07 AT 1706 EDT FROM DON PEARCE TO MACKINNON * * * "Security and FBI personnel have completed an extensive investigation of the system indications observed. The results of their investigation indicates there was no evidence to support that intentional tampering or vandalism had occurred. In addition station personnel have performed extensive walkdowns of safety systems and identified no abnormalities. The Unusual Event (HU4) is terminated." R3DO (Patty Pelke), NRR EO (M J Ross-Lee) , IRD Manager (Brian McDermott), FEMA (Mike Laforty) and DHS SWO (M. Inszer) notified. * * RETRACTION FROM J. GROFF TO J. KNOKE AT 1516 EDT ON 10/31/07 * * "Further investigation into this event has determined that it was caused by poor workmanship by pipe insulators when using a drill to remove mirror insulation retaining rivets. The potential for tampering was ruled out based on interviews, and evidence that was reconstructed. Therefore, since it has been determined that the event was not caused by tampering/vandalism or malicious mischief, this report is retracted. The licensee notified the NRC Resident lnspector. Notified R3DO (Madera) , NRR EO ( MJ Ross-Lee). Emailed IRD (McDermott) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | SAFEGUARDS REPORTS |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 73.71(b)(1) |  |  | 1 | 2007-10-14
43712 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2007-10-11 01:00 | 2007-10-11 07:48 | 2007-10-11 | TONE ALERT SYSTEM OOS FOR PLANNED MAINTENANCE "The Tone Alert Radio System for the James A. Fitzpatrick (JAF) Nuclear Power Plant was taken out of service for planned maintenance. This constitutes a partial loss of the public Prompt Notification System (Loss of Communication) and thus is reportable under 10CFR50.72(b)(3)(xiii). The county alert sirens, which also function as part of the public Prompt Notification System, are operable, compensatory measures are in place to notify the affected county residents." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 10/11/07 AT 1552 EDT FROM TIM PAGE TO JOHN MACKINNON * * * "At 0748 on 10/11/07, the James A. Fitzpatrick (JAF) Nuclear Power Plant reported that the Tone Alert Radio System had been taken out of service for planned maintenance. JAF reported this as a partial loss of the public Prompt Notification System (Loss of Communication) under 10CFR50.72(b)(3)(xiii). "Subsequent review of information received from the National Weather Service (NWS) which maintains the system, and review of information contained in NUREG-1022, has determined that the period of time the Tone Alert Radio System was out of service is not reportable under 10CFR50.72(b)(3)(xiii). "The following updated information is provided: "The Tone Alert Radio System was out of service for planned maintenance from 10/10/07 at 2350 hours to 10/11/07 at 0013 hours (total elapsed time of 23 minutes). "Compensatory measures were in place during this time period to notify the affected county residents." R1DO (William Cook) notified. NRC Resident Inspector, State and Local Officials were notified of this event retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-11
43711 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-10-10 22:45 | 2007-10-11 05:20 | 2008-01-30 | UNIT 2 HPCI PUMP SEAL FAILURE "On 10/10/2007 a 2245, the Unit 2 High Pressure Coolant Injection (HPCI) Pump developed a leak of approximately 5 gpm due to a suspected pump seal failure. "HPCI was in service for a scheduled surveillance test per plant procedure OPT-09.2, HPCI System Operability Test. "When the leak was identified, operators secured HPCI. The leak was isolated by securing the pump, closing the pump suction isolation valves, isolating the keep fill supply valves. Operators declared the Unit 2 HPCI System inoperable when the keep fill system was isolated. "No automatic system isolation or actuation set points were reached. "Safety significance is minimal due to the operability and availability of redundant systems. If a Loss of Coolant Accident (LOCA) were to occur the Reactor Core Isolation Cooling (RCIC) System would automatically inject and if necessary the Automatic Depressurization System (ADS) would depressurize the reactor pressure vessel allowing low pressure Emergency Core Cooling Systems (ECCS) to inject. All low pressure ECCS are operable. "Plant risk has been evaluated and remains 'Green'. "The Unit 2 HPCI system has been removed from service. The pump suction isolation valves have been closed. Injection piping keep fill connections have been isolated. These actions were taken to stop the leakage of system water out of the failed pump seal. "Actions have been taken to protect redundant safety systems, including the RCIC System and ADS. "In accordance with Technical Specification 3.5.1 Required Actions: RCIC has been verified to be operable, and HPCI must be restored to operable status within 14 days. "HPCI pump seal replacement is being planned in accordance with the site's Work Management process. This event has been entered into the sites Corrective Action Program and an investigation into the cause of the seal failure will be performed." The licensee notified the NRC Resident Inspector. * * * RETRACTION RECEIVED FROM LEE GRZEK TO JOE O'HARA AT 1045 EST ON 1/30/08 * * * "On October 11, 2007, at 0520 hours, the control room Supervisor made a notification (Event Number 43711) to the NRC Operations Center in accordance with. 10 CFR 50.72(b)(3)(v)(D) (i.e., any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident). The notification was made as a result of the High Pressure Coolant Injection (HPCI) system being declared inoperable due to indications of a main pump seal leak. Specifically, water was discovered leaking an approximate five gallons per minute from the main pump turbine side seal during performance of OPT-09.2, 'HPCI System Operability Test.' "Basis for Retraction "Unit 2 HPCI was declared inoperable when the main pump seal leak was first identified. Upon further detailed engineering evaluation, it has been determined that the HPCI system was not rendered inoperable as a result of the condition identified on October 10, 2007, and was able to fulfill its safety functions in the degraded condition. "The HPCI pump uses seal purge water piping in combination with mechanical seals to limit shaft leakage. The investigation found debris blocking the seal purge piping, which led to the seal faces overheating and subsequent failure. Water intrusion into the oil system was determined to be the limiting impact of the seal failure. The limiting event for HPCI was determined to be 4.1 hours of operation during a loss of Feedwater event with HPCI only, due to the short runtimes followed by long idle times which maximize water intrusion. The evaluation concluded that the HPCI pump would be able to operate for 4.1 hours, as required for the limiting event, and would be available for 8 hours. Thus, Unit 2 HPCI was degraded but able to meet all required safety functions. "On this basis, the HPCI system was capable of performing its safety functions to mitigate the consequences of an accident and the issue is not reportable under 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident was notified of this retraction." Notified R2DO(Bonner) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-10-11
43710 | -1 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2007-10-11 01:00 | 2007-10-11 04:25 | 2007-10-11 | TONE ALERT RADIO SYSTEM OUT OF SERVICE FOR MAINTENANCE "The tone alert radio system for Nine Mile point was taken out of service for planned maintenance. Per Site Emergency Planning procedures this constitutes a partial loss of the Public Prompt Notification System (Loss of Communication) and thus is reportable under 10 CFR 50.72 (3)(b)(xiii). "The tone alert radio system is installed in Oswego County residences and businesses who can not hear the siren system when activated. The tone alert radio system notifies Oswego County resident of emergency situations. The tone alert radio system is maintained and operated by the National Weather Service (NWS). "NWS estimates that the system will be out of service for approximately 6 hours. The county alert sirens, which also function as part of the public prompt Notification System, are operable." The licensee notified the State and local governments. The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 10/11/07 AT 1510 EDT FROM BRIAN FINCH TO JOHN MACKINNON * * * "The Oswego County Emergency Management Office was notified on 10/11/07 at approximately 1150 by the National Weather Service, NWS (Binghamton, NY) that the Tone Alert System is in service and fully functional. The NWS informed Oswego County that the time the Tone Alert System was out of service from 10/10/07 at 2350 until 10/11/07 at 0013 for a total of 23 minutes. The 23 minutes is less than the one hour criteria for a 10CFR50.72 notification. As such, the initial notification is retracted." R1DO (W. Cook) notified. The NRC Resident Inspector was notified of this retraction by the licensee. State and Local Officials have also been notified of this retraction by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-11
43709 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2007-10-10 21:00 | 2007-10-10 20:20 | 2007-10-10 | PLANNED SHUTDOWN DUE TO WATER MAIN BREAK The licensee initiated a planned shutdown of the fuel fabrication processes, following notification from the City of Columbia (SC) of a water main break offsite from the facility. The City of Columbia will shut off the water supply from the facility at 2100 EDT to conduct repairs on the water main. This water outage is anticipated to last a few hours. The licensee can remain in this condition indefinitely. The licensee has verified that fire fighting and cooling water tanks are at capacity. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2007-10-10
43708 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-10-09 17:00 | 2007-10-10 16:16 | 2007-10-10 | SAFETY SYSTEM VALVE DID NOT OPERATE AS EXPECTED "At 1700 CDT, on 10-09-07 the Plant Shift Superintendent (PSS) was notified that the C-333 Unit 4 Cell 3 freezer/sublimer computer indicated that the 'B' valve failed to unknown status. Investigation by an operator determined that the 'B' valve would not operate electrically and was in the open position. The freezer/sublimer automatically transitioned to the Hot Standby Mode (FS4) and the electrically failed 'B' valve was closed manually by an operator. The freezer/sublimer was being operated in mode FS1, the freeze mode, at the time of the failure. TSR 2.4.3.1 requires the high-high weight trip system and its associated 'B' valve to be operable in mode FS1. It was determined that the system would not have been able to perform its intended safety function with the 'B' valve disabled. This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATR-07-2675; PGDP Event Report No. PAD-2007-16" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-10-10
43707 | 0 | ECS MID-ATLANTIC |  |  |  |  | 2007-10-08 16:30 | 2007-10-10 14:22 | 2007-11-14 | TROXLER MOISTURE DENSITY GAUGE DAMAGED A Troxler moisture density gauge was damaged by construction equipment in Midlothian, VA (NW corner of Midlothian Turnpike and Route 288). The plastic shell was damaged, but there was no damage to the rod or housing. The licensee conducted a leak test and is awaiting results. No abnormal radiation levels were detected on the outside of the housing. The licensee is in possession of the gauge and is planning to ship the gauge back to the manufacturer for repair. Troxler Model 3430 S/N: 26757 Sources: 40 milliCurie Am/Be & 8 milliCurie Cs-137 Source S/N: 47-22173 & 75-8778 (licensee uncertain which S/N is paired with each source) * * * UPDATE ON 11/14/07 AT 2:40 PM FROM JOHN LONGEST TO KARL DIEDERICH * * * The source has been returned to Troxler. The leak test certificate indicates that the source is leaking. However, the leakage is within regulatory limits, and the source may remain in use. "On October 10, 2007, John D. Longest the Radiation Safety Officer (RSO) for the Richmond office of ECS Mid-Atlantic, LLC (ECS) responded to a call where one of our on-site technicians reported a damaged portable nuclear density gauge. The gauge in question was a Troxler 3430 (SN # 26757) and had been properly signed out that morning by ECS Technician [DELETED], an authorized gauge user. The call was received at approximately 1645 HRS and incident occurred at approximately 1630 HRS. The project site is located at the northwest corner of the intersection of Midlothian Turnpike (Route 60) and Route 288 in Chesterfield County, Virginia. Based off of GPS locations for previous tests conducted at the site of the incident, location of the incident is approximately (Longitude: 77° 41'22.963"W - Latitude: 37°30'49.867"N). "Upon arrival, at approximately 1715 HRS, it was observed that an area surrounding the damaged gauge had already been cordoned off with caution tape, in a 15 foot radius. Weather was noted to be 80°F, clear skies, calm wind. The gauge had clearly been damaged and the rod was extended downward. The equipment operator (R.G. Griffith employee [DELETED]) was moved after the incident to another part of the site to fill out an 'Employee/ Witness Statement Form' and was with the R.G. Griffith Safety Officer [DELETED]. ECS Technician [DELETED] was approximately 50 feet north of the gauge filling out an "Employee/ Witness Statement Form" for R.G. Griffith. Copies of the two "Employee/ Witness Statement Form" papers are attached. It was requested that [DELETED] and [DELETED] be interviewed, after their paperwork had been completed and prior to leaving the site for this investigation. "Utilizing a 'Troxalert' Radiation Monitor, calibrated July 18, 2007 readings were immediately taken at the following distances: "50 feet - 0 mR/hr 25 feet - 0 mR/hr 10 feet - 0 mR/hr 5 feet - 0 mR/hr 1 foot - 1.5 mR/hr 0 feet - 2.5 - 10 mR/hr (high value against gauge at source end) "At this point it was accessed that the source rod and housing were intact. Source rod was in the downward 'test' position could be retracted though shutter block and locking mechanism would not engage on its own. The source rod was manually secured so that source was housed while placing gauge into its transport box. Prior to closing transport box source rod, was secured so that source remained within housing during transport. Later the shutter block was able to be closed. Gauge was properly locked and secured in transport vehicle. Gauge was returned to the office of ECS in Richmond, VA, to its designated storage room. "On October 9, 2007, at approximately 1500 HRS, a call was made to the toll-free number posted on the NRC website (1-800-368-5642). The call was transferred to 'public affairs' when a request to report the incident was made. After being transferred to 'public affairs,' information regarding the gauge serial number, type and pertinent details regarding the incident were provided. A second call reporting the incident was made at 1422 HRS on October 10, 2007 (Event # 43707). "After securing the gauge in a privately owned vehicle, it was noted by [DELETED] of R.G. Griffith that the equipment operator had left the site and was headed home and couldn't provide any additional statement at that time. Based on the verbal and written statement collected by ECS Technician [DELETED] as well as a written statement provided by R.G. Griffith equipment operator [DELETED], the following occurred during the incident. "Technician had been on-site, in the general vicinity of incident location for majority of working day observing and testing compaction of soils per ASTM Specification D-2922. As required by the site, [the technician] was wearing proper safety equipment including OSHA compliant boots, hard hat, safety goggles and fluorescent orange vest. While not in operation, the gauge was properly secured in vehicle. Compaction of fill was being accomplished utilizing an 815 roller/ dozer, generally running in a north-to-south direction across a fill area, approximately 150 foot by 250 foot. "[The technician] noted that several passes had been made in an area and decided to begin testing. [He] removed scrape plate, hammer, drill pin and extracting tool from his vehicle, to prepare an area for testing, gauge remained secured in his vehicle during this preparation. After returning preparation materials to his vehicle, the gauge was taken to previously prepared test location. At this time it was noted that a Volvo truck had unloaded another pile of fill to be spread and compacted. [The technician] began testing, took about three steps back from his gauge crouched down so he could see on the display panel when test was done, at this time he was facing away from the compaction equipment. "In preparation to spread newly placed fill, the 815 roller turned into a east-west direction, unaware of [the technician's] location. The operator noted that after turning [the technician] was out of his visibility in a 'blind spot'. "After a few moments [the technician] looked back at the 815 roller, as he had heard the reverse warning (beeping) on the equipment. When he realized that the operator wasn't slowing down, he began jumping, waiving and shouting in an attempt to alert the driver. As the roller continued towards him, [The technician] tried to extract the gauge. He was unable to move it quickly because the source rod was lowered. [The technician] leapt out of the path of the 815 roller to avoid personal harm unable to prevent the gauge from being run over. "After the operator saw [the technician], he stopped and was shown what had just happened. [The technician] insisted that they begin roping the area off. [The technician] stated that he was asked, but declined, to remove the gauge from the work area so compaction could continue. Operator continued making passes elsewhere, before returning his equipment to its storage location at the front end of the site. "The gauge has been leak tested and results have been attached. Documentation of gauge disposal through Troxler Electronic Laboratories. Inc. have been attached as well. Prior to shipment to manufacturer for disposal, readings were taken 3 feet (1 meter) outside of transport box and were recorded at 0.6 mR/hr." R1DO (Holody) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-10-10
43706 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2007-10-10 13:12 | 2007-10-10 14:09 | 2007-10-10 | PRESSURIZER PORV OPENED MOMENTARILY WITH RCS DISCHARGE OF APPROXIMATELY 10 GALLONS "On 10/10/2007 at 1312, Crystal River Unit 3 was performing maintenance on its Pressurizer Pilot Operated Relief Valve (PORV). The I&C technicians were replacing a circuit board card in the circuitry for the PORV. The PORV had been selected to close during the replacement of the card. When the PORV was selected to its auto position, the PORV opened and was immediately closed by the reactor operator. It was estimated that the PORV was opened for 2 second with a total flow of 10 gallons. This rate is in excess of the 25 gpm as found in the EAL. The event was quickly terminated with the closing of the PORV and PORV block valve. The plant remains stable with the PORV and PORV block valve closed. CR3 briefly met the conditions of an Unusual Event, however declaration was not required." The licensee is still trouble-shooting the cause of the event. The reactor is stable at full power and the technical specification action statement requirement for an inoperable PORV valve (TS 3.4.10) have been satisfied. The licensee reported this event for information based on the guidance of NUREG 1022 concerning reporting an event that was rapidly terminated that may have met the criteria of an emergency based on an after the fact review. The licensee notified the State and local authorities and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY | OTHER UNSPEC REQMNT | OFFSITE NOTIFICATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  |  |  | 50.72(b)(2)(xi) |  | 0 | 2007-10-10
43705 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-10-10 | 2007-10-10 05:35 | 2007-10-12 | LOSS OF ERDADS AND ERDS LINK "The Emergency Response and Data Acquisition System (ERDADS) was out of service at 0000 EST on 10/10/2007. This resulted in a loss of the ERDS link of plant data to the NRC. This is an 8-hour reportable event pursuant to 10CFR50.72(b)(3)(xiii) Major Loss of Assessment Capability. The cause of the loss appears to be a computer malfunction, there is no evidence of tampering. Follow-up notification to the NRC will be given once Unit 4 ERDS is returned to service." As of 0515 ERDADS was available in the licensee control room, but the ERDS link was not available with the NRC. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM NIELSEN TO HUFFMAN AT 1341 EDT ON 10/12/07 * * * "Repairs are complete and the Unit 4 ERDADS system was tested Sat. at 1216 EDT on 10/12/07. The ERDS link of plant data to the NRC has been restored on Unit 4." The licensee notified the NRC Resident Inspector. R2DO (Desai) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-10
43704 | 0 | PENNSYLVANIA STATE UNIVERSITY |  |  |  | 1000 KW TRIGA MARK III | 2007-10-09 16:00 | 2007-10-09 16:45 | 2007-10-10 | POSSIBLE LEAK AT PENN STATE RESEARCH REACTOR Pennsylvania State University Operations personnel noticed increased makeup at the Breazeale (Triga) reactor, an open pool reactor. At 1600, the leak rate was measured at approximately ten gallons per hour. The Pennsylvania Department of Environmental Health was notified of the probable leak to the environment (possibly to the ground around the containment pool). The licensee has not reached any required reporting criteria. Water activity: Gross Alpha: less than minimum detectable Gross Beta: approx. 3.8 picoCuries/liter Chromium Gamma: approx. 103 picoCuries/liter * * * UPDATE FROM MARVIN MENDONCA VIA E-MAIL TO JOE O'HARA AT 0606 ON 10/10/07 * * * Mark A. Trump, Associate Director of Operations, Breazeale Nuclear Reactor Radiation Science and Engineering Center Pennsylvania State University, University Park, PA 16801 provided the following information to Marvin Mendonca via e-mail at 0536 on 10/10/07. "At approximately 1600 hrs on 10/9/07 review of water inventory data on the reactor pool indicates a probable leak of approximately 10 gallons per hour from the approximately 71,000 gallon pool. A walk down of reactor systems does not show any signs of leakage into any interfacing systems leading to a probable conclusion that the leak is through the concrete pool wall into the biological shielding (earthen wall). This leakage amount is well within normal makeup system capacity and is at the low threshold of our ability to determine the leakage due to variables such as evaporation rates. "The reactor is in a safe condition, all reactor pool water chemistry is normal but notification is being done to the PA Department of Environmental Protection (as required). "Notification of the NRC operational department is also being made concurrently. Notification number 43704." Notified R1DO(Cook), NRR(Mendonca), NRR(Adams), FSME(Flanders), and NRR(Cunningham). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | NPR | [5 empty] | 0 | 2007-10-09
43703 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-10-09 09:15 | 2007-10-09 09:41 | 2007-10-09 | ELEVATED ONSITE TRITIUM LEVELS "Thirty new ground water monitoring wells were recently installed at Catawba Nuclear Station in support of the Nuclear Energy Institute (NEI) ground water initiative. The initial sampling of one of these wells displayed a level of tritium that triggered the communication protocol of the NEI initiative on ground water protection. The tritium concentration for this well was 42,335 picocuries per liter (pCi/l). The threshold for initiating the communication protocol is 20,000 pCi/l. This well is inside the owner controlled area. Adjacent wells surrounding this well do not have similar tritium levels. The station is continuing to investigate the source of tritium identified in this well. Samples from the remaining wells are far below the communication protocol threshold. There is no public risk associated with this well sample. There is no indication that tritium has migrated off the Catawba site in the ground water at the communication threshold. Also this well is not a drinking water source and therefore, there is no potential dose to plant workers or the public." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-09
43702 | 0 | ST. VINCENT HOSPITAL |  |  |  |  | 2007-10-08 | 2007-10-08 16:13 | 2007-10-08 | POTENTIAL PERSONNEL OVEREXPOSURE A representative of Landauer (the optically stimulated dosimeter provider) reported to the hospital that a person on the hospital staff received a 113,165 millirem deep dose whole body reading for the reporting period of 8/1/07 - 8/31/07. The shallow dose reading was 107,506 millirem. The Radiation Safety Officer (RSO) contacted the individual with the high dose reading. The individual said that he had no ill health effects so he believed the reading was not correct. The individual said that he normally wears his dosimeter attached to a lanyard that he wears around his neck. He did remember one day when a therapist brought him his dosimeter from a linear accelerator room. The individual did not recall leaving his dosimeter in the room. The RSO talked to a representative of Landauer about distinguishing between a potential dose from an accelerator and other doses the individual may have received from performing his duties but this could not be definitively done. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2007-10-08
43701 | 0 | AREVA NP INC. |  |  |  |  | 2007-08-13 | 2007-10-08 15:30 | 2007-10-08 | PART 21 REPORT - AREVA MINIMUM CRITICAL POWER RATIO The licensee provided the following information via facsimile: "The defect is in the calculation of steady-state core Minimum Critical Power Ratio (MCPR) by the core monitoring system when the SPCB critical power correlation is used for ATRIUM-10 fuel. Specifically, the defect is in the additive constants, a parameter used by the SPCB critical power calculation and based on test data." AREVA notified the affected plants. Affected Plants: Browns Ferry, Units 2 & 3 Columbia Grand Gulf LaSalle, Units 1 & 2 River Bend Susquehanna, Units 1 & 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-10-08
43700 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2007-10-04 | 2007-10-08 09:53 | 2007-12-18 | AGREEMENT STATE REPORT - MOLYBDENUM 99 CONCENTRATION TOO HIGH ON ELUTION ON MOLYBDENUM 99/TECHNETIUM- 99M GENERATOR The State provided the following information via email: "Event Cause: MOLYBDENUM 99 CONCENTRATION TOO HIGH ON ELUTION ON MOLYBDENUM 99/TECHNETIUM- 99M GENERATOR "Event Date: 10/04/2007 Report Date: 10/05/2007 "Licensee/Reporting Party Information: "Name: PHARMACY SERVICES OF THE QUAD CITIES, License Number: 0207-1-82-NP, DAVENPORT, IA 52807 "IDPH received a call from the Pharmacy Services of Quad Cities RSO on Friday, October 5, 2007, concerning a Bristol-Myers Squibb (BMS) Mo99/Tc99M generator that they had received on Wednesday, October 3, 2007. The licensee first eluted the generator on Thursday, October 4, 2007, and discovered an elevated Mo99 concentration in the elution. Subsequent elutions also had elevated Mo99 concentrations. The licensee contacted the manufacturer (BMS) and was asked to ship the generator back to the manufacturer. The licensee contacted IDPH concerning the shipping container. An Information Notice that was issued in 1997 talks to this issue, and IDPH told the licensee to hold the generator 10 1/2 lives or a special salvage container would be needed to ship the generator back to BMS." The State reported that elutions greater than .15 micro Curies per milli Curie Tc-99m are unacceptable and exceed establish limits. See Information Notice No. 84-85: 'Molybdenum Breakthrough From Technetium-99m Generators' Also a state representative said that the lot number of this generator was "M275711D," the size was 15 curies, the calibration date is 10/2 and the expiration date is 10/6. "As of Monday October 8, 2007, the generator is being held at the pharmacy. "Corrective Actions: Action Number: 1 MANUFACTURER WILL NOTIFY CUSTOMERS OF DEFECT "Keywords: ELEVATED MO99 CONCENTRATION FROM GENERATOR ELUTION "Source of Radiation: Source Number: 1 Form of Radioactive: ELEVATED MO99 CONCENTRATION "Radionuclide or Voltage (kVp/MeV): MO-99 "Source Use: RADIOPHARMACEUTICAL "Manufacturer: BRISTOL-MEYERS SQUIB "Device/Associated Equipment: Device Number: 1 "Device Name: RADIOPHARMACEUTICAL GENERATOR "Manufacturer: BRISTOL-MEYERS SQUIB "Problem with Equipment: ELEVATED MO99 "Reporting Requirements: 30.50(b)(2)(ii) - The 24 hour report of an event where required equipment is disabled or fails to function as designed when the equipment is required to be available and operable when it is disabled or fails to function. "Iowa Event # IA070004" * * * UPDATE FROM IDPH (FARRINGTON) TO CROUCH VIA EMAIL AT 0938 EST ON 12/18/07 * * * "The manufacturer, Bristol-Meyers Squibb Medical Imaging Inc., reported back to the Iowa licensee number: IA-207-1-82-NP that it was indeterminate as to the cause of the problem. The State of Iowa considers this event closed." Notified R3DO (Duncan) and FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2007-10-11
43699 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-10-07 01:14 | 2007-10-07 05:56 | 2007-10-07 | PRIMARY CONTAINMENT LEAK RATE EXCEEDED "At 0114 EDT on 10/7/07, Fermi 2 feed water line check valves, B2100-F010B and B2100-F076B, failed their local leak rate tests. The leakage rate of the inboard check valve (B2100-F010B) was 297.3 SCFH and the leakage rate of the outboard check valve (B2100-F076B) was indeterminate due to leakage exceeding the capability of the leak rate monitor. Thus, the minimum path leakage through penetration X-9B is 297.3 SCFH. This leak rate exceeds the Primary Containment allowable leakage rate (1.0 La) of 296.3 SCFH per Tech. Spec. 5.5.12. The NRC Resident Inspector has been notified of this event." The licensee is reporting a degraded safety function associated with the primary containment barrier. The licensee intends to repair the leaking valve and retest it prior to any mode change. There is no LCO associated with this condition because the licensee is in mode 5. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-10-07
43698 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-10-07 01:15 | 2007-10-07 01:55 | 2007-10-07 | LOSS OF PROMPT NOTIFICATION MESSAGE SYSTEM "Jacksonville National Weather Service does not have the capability to broadcast prompt notification messages due to phone lines or system problem at this time. Plant Hatch security notified the Operations Shift Manager at 0115 hour to notify NRC. Also, site Emergency Preparedness on call person has been contacted and security has notified the state and local agencies. Information Technology (IT) has been notified of problem." Compensatory measures performed by the local emergency response agencies will be used if needed. The licensee will notify the NRC Resident Inspector. * * * UPDATE PROVIDED BY BILL DUVALL TO JEFF ROTTON AT 0345 EDT ON 10/07/07 * * * The Jacksonville National Weather Service has restored the capability to broadcast prompt notification messages effective 0344 EDT on 10/07/07. The licensee notified the NRC Resident Inspector and the state and local emergency response agencies. Notified R2DO (Evans). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-07
43697 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2007-10-06 10:59 | 2007-10-06 15:32 | 2007-10-06 | MANUAL REACTOR TRIP DUE TO CONDENSER TUBE RUPTURE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 6, 2007, at approximately 10:59 Mountain Standard Time (MST) Palo Verde Unit 2 plant operators manually tripped the reactor from approximately 100% rated thermal power. The reactor was tripped when sodium levels in both steam generators reached trip criteria following a condenser tube rupture. Unit 2 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. "No ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. There was no loss of normal heat removal capabilities, or loss of any safety functions associated with this event. No major equipment was inoperable prior to the event that contributed to the event. " No PORVs or MSSVs lifted. Decay heat is being removed with Auxiliary Feedwater feeding the steam generators steaming to the condenser. There are no primary to secondary tube leaks in the steam generators. Emergency buses are powered by offsite power with Emergency Diesel Generators in standby. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The [NRC] Resident Inspector was informed of the Unit 2 reactor trip and this notification." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-10-06
43696 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-10-05 16:43 | 2007-10-06 11:50 | 2007-10-06 | PROCESS GAS LEAK DETECTION (PGLD) SYSTEM INOPERABLE "At 1643 CDST, on 10-05-07 the Plant Shift Superintendent (PSS) was notified that an alarm was received for the C-333 Unit 6 Cell 8 UF6 [Process Gas Leak] Detection (PGLD) System. Operators responded and found that the READY and MANUAL lights for this system were not illuminated. This PGLD System contains detectors that cover C-333 Unit 6 Cell 8 and Section 4 of the cell bypass piping. At the time of this alarm, unit 6 cell 8 and some areas of Section 4 of the cell bypass were operating above atmospheric pressure." Electricians are currently troubleshooting to determine the source of the potential short circuit that caused the problem. "[Technical Safety Requirement] (TSR) 2.4.4.1 requires that at least the minimum number of detector heads in the cell and in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 6 Cell 8 PGLD system inoperable, none of the required cell heads and only 2 of the required 3 heads in Section 4 of the cell bypass were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.C.1 was entered and a continuous smoke watch was put in place within one hour. "Engineering has determined that the system would not have been able to perform its intended safety function when this alarm came in. This event is reportable as a 24 hour event in accordance with 10 CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: "a. The equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; "b. the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand; and "c. no redundant equipment is available and operable to perform the required safety function. "The NRC Resident Inspector has been notified of this event. PGDP Assessment and Tracking Report No. ATR-07-2655; PGDP Event Report No. PAD-2007-15; Responsible Division: Operations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-10-06
43695 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-10-05 18:47 | 2007-10-05 21:15 | 2007-10-05 | SODIUM HYPOCHLORITE SPILL WHILE OFFLOADING A TANKER TRUCK "At 17:20 the Brunswick Station control room was notified of a sodium hypochlorite spill. Approximately 300 gallons of a 15% solution was released to the environment through a faulty hose fitting at a tanker truck before it could be isolated. The state is required to be notified of any hazardous chemical release greater than or equal to 100 pounds (64 gallons of a 15% sodium hypochlorite solution corresponds to 100 pounds). The North Carolina State Division of Water Quality was notified of the event at 18:47 as required by 40 CFR 355.40. The US Coast Guard (report number 850864) and Brunswick County were also notified of the event. "Minimal impact to the environment. No impact to the health and safety of the public. No impact to plant safety or operations." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-05
43694 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2007-10-05 06:17 | 2007-10-05 18:45 | 2007-10-05 | POSITIVE FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employees access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2007-10-05
43693 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-10-05 09:30 | 2007-10-05 17:58 | 2007-10-05 | POSITIVE FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to Byron, Limerick, Oyster Creek, Peach Bottom, and Three Mile Island has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector at the affected plants. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2007-10-05
43692 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-10-05 04:08 | 2007-10-05 11:30 | 2007-12-04 | LOSS OF BOTH EMERGENCY SERVICE WATER PUMPS "On October 5, 2007, at approximately 0408, while attempting to open 480 VAC breaker 1B4234A/B for preplanned maintenance, a loss of bus 1B42 occurred. The preliminary cause of the bus trip was arcing of the bucket stabs/bus bars when opening the door to breaker 1B4234A/B. The arcing was a result of the breaker bucket inadvertently pulling away from the bus. At the time of this event, the 'A' Emergency Service Water (ESW) pump was out of service for preplanned maintenance. The loss of 1B42 resulted in a loss of the 'B' ESW pump. The 'A' ESW pump was subsequently returned to service at 0458 on October 5, 2007. Note that power was conservatively lowered approximately 4% at 0512. At the time of this power reduction, the plant was not in a Technical Specification that would require a plant shutdown. "In addition to the loss of the 'B' ESW pump, the loss of 1B42 resulted in invalid Group 1-5 isolations on the 'B' side of PCIS (not including Main Steam Line Isolation Valves). "This event is reportable under 10 CFR 50.72(b)(3)(v), Any event or condition that alone at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (D) Mitigate the consequences of an accident. "The licensee notified the NRC Resident Inspector." The licensee has not yet determined if this is a mechanical failure of the breaker or a human error. However, they are looking at OE associated with this issue. * * * UPDATE AT 1324 EDT ON 10/26/07 FROM BOB MURRELL TO S. SANDIN * * * The licensee provided the following information as an update: "In addition to the ESW loss of safety function that occurred, it has been determined that from 0408 till approximately 0715 on 10/05/07, a loss of both onsite emergency AC power sources occurred. Specifically, at the time of the event, the 'A' Emergency Diesel Generator (EDG) was out of service for preplanned maintenance. When bus 1B42 was lost, this resulted in a loss of 'B' ESW. The loss of 'B' ESW resulted in the 'B' EDG being incapable of performing its safety function. Therefore, this is another example of an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident." The licensee informed the NRC Resident Inspector. Notified R3DO (Hills). * * * UPDATE AT 1619 ON 12/4/2007 FROM BOB MURRELL TO MARK ABRAMOVITZ * * * "On 10/05/07, this event was reportable under 10 CFR 50.72(b)(3)(v), Any event or condition that alone at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (D) Mitigate the consequences of an accident due to the loss of both ESW pumps. Further reviews have determined that the 'A' ESW pump was available at the time of the event and therefore, this event is not reportable for a loss of the ESW safety function. This event is still reportable for a loss of the on-site emergency AC power safety function." The licensee notified the NRC Resident Inspector. Notified the R3DO (Lara). | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-10-05
43691 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-09-24 | 2007-10-04 18:29 | 2007-10-04 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE "Keymaster's Radiation Safety Officer reported they had recently (in September 2004) received a batch of eleven Cobalt 57, foil sources, Model PHI-0106, from Isotope Products Laboratory. One of the eleven sources failed its receipt leak test. The others were tested and were not leaking. The State of Washington provided the following information via e-mail: "The contaminated foil source had Serial Number B9-774 and had an activity of 437 megabecquerels (11.8 millicuries). When wiped, the level of contamination was about 500 counts per minute above background. The source may have been leaking or could have had residual contamination; this was never determined. The source was returned to the supplier. "The work areas and personnel were surveyed and found uncontaminated. "No media attention at present. "Subsequent inspections by DOH performed 10/31/2005 and 9/21/2006 found no contamination and no additional reoccurrences of receiving contaminated sources. "Notification Reporting Criteria: WAC 246-221-250 "Isotope and Activity involved: Cobalt 57, 437 mBq (11.8 mCi). There were no overexposures. The leaking source was an Isotope Products Laboratories XRF source Model PHI-0106, S/N B7-461. The leaking source was wiped down to 416 counts, placed back into its shield. It was returned to supplier. There was minor contamination in the source storage area. The licensee has since cleaned the area. Wipe surveys performed by the licensee and DOH showed no contamination. State of Washington Event Report # WA-04-042. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2007-10-09
43690 | 0 | SCHLUMBERGER |  |  |  |  | 2007-10-04 11:10 | 2007-10-04 12:25 | 2007-10-04 | MISSING FLUID DENSITY GAUGE At about 11:10 EDT on 10/4/07 during a routine gauge inventory identified that a Thermo Measuretech (formerly Texas Nuclear) model TN-5192 fluid density gauge could not be accounted for. The gauge serial numbers are D111 and MB2856. The gauge has a 200 millicurie Cs-137 source. There is no sign of theft but the gauge has not been found at its expected storage location or any of the well sites in the area. According to records it was last used in April 2007 and last inventoried in August 2007. Schlumberger will expand the search to include all facilities in the country. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-10-04
43689 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2007-10-03 15:30 | 2007-10-03 23:38 | 2007-11-30 | POTENTIAL UNAVAILABILITY OF TWO WAY RADIO SYSTEM TO SUPPORT SAFE SHUTDOWN "In response to Self-Assessment Report SA014668 and preparation for the 2008 Triennial Fire Protection Inspection, a Fire Protection Improvement Plan implementation is in progress. Preliminary analysis of the major equipment, power supplies and cables associated with the two-way radio communication system (DCR-3341) indicates the potential for the plant two-way radio system to be adversely impacted and potentially unavailable to support post-fire safe shutdown operator actions and/or fire brigade fire fighting activities for a fire location in: - Fire Zone AX-35 (Control Room and AC Equipment Room) - Fire Zone TU-22 (Turbine Room) at the mezzanine elevation just outside Battery Room 1B - Fire Zone TU-98 (Battery Room 1B) "This review has identified discrepancies regarding the credited means of communication required for use by Operators in response to an Appendix R fire. The safe shutdown procedures E-O-06 and E-O-07, and the Manual Action Feasibility Study (Fire Protection Engineering Evaluation FPEE-003) only credit the plant two-way radio system. "However, upper tier program documents (e.g., Fire Protection Program Plan, Appendix R Design Description) do not consistently contain the same requirements. For example, the Fire Plan, Rev 7, Section 12.9 requires both the 5-channel Gai-Tronics system between key shutdown locations AND the multi-channel portable radio communications equipped with repeaters and provided for use by the plant fire brigade shall be operable at all times. The Appendix R Design Description. Rev. 5 is silent on safe shutdown communications. "It is not clear at this time whether the 5-channel Gai-Tronics should also be credited in the safe shutdown procedures. If so, then the cables supporting operation of the Gai-Tronics would need to be identified and located by fire zone to determine their availability in lieu of two-way radio communications for a fire in any of the three fire zones identified above. "Until this is verified, the Appendix R timeline for achieving sate shutdown may not be able to be met. Therefore, this is reportable under 10 CFR 50.72 (b)(3)(V)(A), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) shutdown the reactor and maintain it in a safe shutdown condition, (B) remove residual heat, (C) control the release of radioactive material, OR (D) mitigate the consequences of an accident." The licensee will notify the NRC Resident Inspector. * * * RETRACTION PROVIDED BY JACK GADZALA TO JEFF ROTTON AT 1527 EST ON 11/30/07 * * * "EN# 43689 provided notification that the Appendix R timeline for achieving safe shutdown may not be achievable due to potential loss of the credited two-way radio communication system due to fire and consequent need for face-to-face communications between the Operators. This position was adopted pending verification of the availability of the Gai-Tronics paging system. "A subsequent engineering analysis of the major equipment, power supplies and cables associated with the Fire Protection/Appendix R two-way radio communication system, the Gai-Tronics plant paging system and the dedicated Emergency Gai-Tronics System, determined that adequate communications would have been available during a fire in the subject fire zones. Operators are familiar with and skilled in the use of the Gai-Tronics system as part of their job function. Interviews with on-shift Operators confirmed that operations would use the two-way radios; and if they failed, would then use the nearest Gai-Tronics handset station and then Emergency Gai-Tronics at specific locations for an Appendix R Dedicated Shutdown scenario. Where Operator manual actions are in close proximity to the Dedicated Shutdown panel, face-to-face communications would be achievable and timely. "Consequently, the assumption of only face-to-face communications described in the Event Report would not have been necessary for all safe shutdown actions. Use of redundant communications systems (Gai-Tronics and Emergency Gai-Tronics) would have been available for fires in the subject fire zones such that the Appendix R safe shutdown time requirements would not have been significantly impacted. The loss of the two-way radio system for the identified fire zones would not have prevented the fulfillment of the safety function of systems that are needed to shut down the reactor and maintain it in a safe shutdown condition. As such, this condition is not reportable under 10CFR50.72(b)(3)(v)(A) as previously stated. "Consequently, the notification made on 10/03/2007 (EN 43689) is hereby retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (Lipa). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2007-10-03
43688 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2007-10-03 18:30 | 2007-10-03 18:43 | 2007-10-03 | OFFSITE NOTIFICATION TO SOUTH CAROLINA OSHA DUE TO NON-WORK RELATED FATALITY ONSITE "On October 3, 2007, a non-work related fatality occurred at the H. B. Robinson Steam Electric Plant, Unit No. 2. Specifically, at 1502 hours EDT, first responders were dispatched for a Progress Energy employee who suffered a medical condition that required immediate attention. Medical assistance was provided on-site by H. B. Robinson Plant first responders, and the employee was subsequently transported by ambulance to a nearby medical facility. At 1540 hours EDT, site personnel were notified that attempts to revive the employee were not successful and the employee had died. The employee was working in a non-radiologically controlled area of the plant and no radioactive material or contamination was involved. "Notification of other governmental agencies, specifically the South Carolina Occupational Safety and Health Administration (SCOSHA), was completed at 1830 hours EDT on October 3, 2007. This report is being made in accordance with 10 CFR 50.72(b)(2)(xi), which states that a report shall be made as soon as practical and in all cases within four hours of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site fatality. The resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-10-03
43687 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-10-03 14:10 | 2007-10-03 16:44 | 2007-10-03 | REACTOR TRIP ON LOSS OF FORCED FLOW TO RCS LOOP "A" "An emergency has not been declared and there has not been a release of radioactivity to the environment. "Farley Unit 2 tripped from 100% power due to a loss of forced flow in the 'A' Reactor Coolant System loop. The loss of flow resulted from de-energization of the 2A 4160V Reactor Coolant Pump Bus that provides power to the 2A Reactor Coolant Pump following the de-energization of the 2B Start Up Transformer. The loss of the 2B Start Up Transformer appears to have been the result of relay testing on Farley Unit 1. Farley Unit 1 is currently in Mode 6 for a refueling outage. "The loss of the 2B Start Up Transformer also de-energized the 2G 4160V Engineered Safeguards Feature Bus. This bus has been re-energized from the 2B Emergency Diesel Generator. "All rods fully inserted and all systems functioned as required following the trip. Decay heat removal is being provided by both Motor Driven Auxiliary Feedwater Pumps supplying flow to all three Steam Generators. Cause of event is under investigation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-10-03
43686 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-10-02 14:06 | 2007-10-03 14:35 | 2007-10-03 | RELEASE DETECTION SYSTEM (PGLD) DECLARED INOPERABLE "At 1406 CDST, on 10-02-07 the Plant Shift Superintendent (PSS) was notified that an alarm was received for the C-333, Unit 6, Cell 4, UF6 Release Detection (PGLD) System. Operators responded and found that the READY and MANUAL lights for this system were not illuminated. This PGLD System contains detectors that cover C-333, Unit 6, Cell 4, and Section 2 of the cell bypass piping. At the time of this alarm, some areas of Section 2 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 6, Cell 4, PGLD System inoperable, only 2 of the required 3 heads in Section 2 of the cell bypass were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1 .C.1 was entered and a continuous smoke watch was put in place within one hour. An investigation is ongoing and at this point a wire was found that had failed with visible insulation damage. Engineering has determined that the system would not have been able to perform its intended safety function when this alarm came in. This event is reportable as a 24 hour event in accordance with 10 CFR 76.1 20(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function." This event is similar to EN#43670 on 09/27/07. The NRC Senior Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-10-03
43685 | 0 | CARILION CLINIC |  |  |  |  | 2006-08-31 | 2007-10-03 14:21 | 2007-10-03 | MEDICAL EVENT INVOLVING HIGHER THAN PRESCRIBED DOSE On August 31, 2006 a female patient received mammosite treatment for a breast lesion using a HDR with an Ir-192 source. The treatment consisted of placing a catheter into the treatment site, inflating a balloon with between 35-75 ml saline and positioning the Ir-192 source inside the catheter into the center volume of the saline balloon. This allows for a homogenous dose to the treatment site. While in the OR (Operating Room), the catheter was inserted and saline introduced through one of the two catheter connections to inflate the balloon. The patient was taken to the HDR location where the technologist inadvertently connected the HDR to the saline vice the HDR connector. This resulted in draining the saline balloon into the HDR unit. The technologist recognized that the HDR was improperly connected, broke the connection and reconnected to the proper port. When the prescribed 416 second treatment was commenced, the HDR automatically shutdown after 223 seconds retracting the Ir-192 source to the safe position. An evaluation by the licensee concluded that the incident was not reportable since it did not meet the criteria for an underdose. During an inspection conducted 7/26/07 (Inspection Report No. 2007-001), the NRC Inspector noted that since the saline balloon had been inadvertently drained tissue in a .5 cubic centimeter volume adjacent to the source received a significantly higher dose (approximately 20 Gray) than prescribed. In a follow-up call from NRC Region I on 10/03/07, the licensee was requested to notify the NRC Operations Center of this finding. The licensee informed the prescribing physician and the patient was also notified. No adverse effects to the patient have been noted. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2007-10-09
43684 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-10-03 06:36 | 2007-10-03 13:08 | 2007-10-03 | CONTAMINATED WORKER TRANSPORTED TO OFFSITE MEDICAL FACILITY "At 0540 Eastern Daylight Time (EDT) the Unit 2 Control Room was notified of a personnel injury in the Unit 2 containment. Unit 2 is currently in a refueling outage and the individual was working in upper containment in support of the reactor vessel closure head replacement project. The individual injuries are apparently the result of being struck when a rigging clevis (not under load) dropped from an elevated position. Site emergency medical technicians responded to the scene and the individual was transported to a local medical facility [Lakeland Hospital, St. Joseph, MI] via ambulance at 0636 EDT. At the time of transport, the individual was considered to be potentially contaminated because complete surveys could not be performed while the individual was immobilized for transfer. Subsequently, after arrival at the hospital, radiation protection personnel verified the presence of low levels of contamination on outer contamination clothing and transport material. These materials are being returned to plant in accordance with DOT guidelines. "This report is being made pursuant to 10 CFR 50.72(b(3)(xii), 'Any event requiring the transport of a radioactively contaminated person to an offsite medical facility for treatment.'" The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2007-10-03
43683 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-10-02 19:08 | 2007-10-03 10:42 | 2007-10-03 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant has been placed on administrative hold. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2007-10-03
43682 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2007-09-28 | 2007-10-02 11:55 | 2007-10-02 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was received via email: "Subject: Event Report Number WA-07-084 "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "STATUS: new "Licensee: Washington State Department of Transportation Eastern Region "City and State: Spokane, Washington "License Number: WN-L035-1 "Type of License: Portable Gauge Licensee "Date of Event: 28 September 2007 "Location of Event: Spokane, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "The licensee's radiation safety officer notified Washington Department of Health (DOH) on 01 October 2007 their Troxler portable gauge, model 3430, serial number 36039 (containing maximum of 8 millicuries Cs-137 and 40 millicuries Am-241:Be) was run over on 28 September 2007 by a small roller during road repair. The gauge did not have the probe extended when struck. The gauge user immediately notified their radiation safety officer and the RSO's supervisor; radiation surveys detected no elevated radiation levels, so the licensee decided to transport the device to their storage area and inform Washington DOH the following workday, Monday 01 October 2007. It was reported that only superficial damage was done to the plastic case of the gauge. The gauge was put back in the transport case and sent back to its secured storage location. Department staff are investigating. "Washington (DOH) on-site investigation underway. "No known media attention. "Notification Reporting Criteria: "Per WAC 246-221-250 (2) (d) ~ Twenty-four (24) hour notice required for equipment failure or inability to function as designed. "Isotope and Activity involved: one Troxler model 3430, serial 36039 portable gauge, containing two radioactive sealed sources, one 8 millicuries Cs-137 maximum, & one 40 millicuries Am-241:Be maximum. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Unknown but most likely not. The unit was functioning properly on 28 September 2007. Dose rate measurements by the licensee after the gauge was rolled over detected no elevated radiation fields. "Lost, Stolen or Damaged? (mfg., model, serial number): one Troxler model 3430, serial 36039 portable gauge, containing two radioactive sealed sources, one 8 millicuries Cs-137 maximum, & one 40 millicuries Am-241:Be maximum. "Disposition/recovery: NA "Leak test? Most recent leak test was collected on 18 January 2007 (no contamination, < 0.000002 microcuries). "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) NA "Release of activity? NA "Activity and pharmaceutical compound intended: NA "Device (HDR, etc.) Mfg., Model; computer program: NA Exposure (intended/actual); consequences: NA "Was patient or responsible relative notified? NA "Was written report provided? NA "Was referring physician notified? NA "Consultant used? No." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2007-10-05
43681 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-09-28 12:00 | 2007-10-02 09:55 | 2007-10-02 | WISCONSIN AGREEMENT STATE REPORT - NDC GAUGE FOUND IN SCRAP YARD The following Agreement State report from Wisconsin was received via Facsimile: "License No.: Non-licensee "Licensee: Non-licensee "Event Location: Gorden Schneider Property "Event Type: Scrap Yard Detector "Notifications: Phone call from Sadoff yard on 9/28/07. "DHFS was contacted on 9/28/07 concerning a rejected load from Sadoff scrap yard in Fond du Lac. The yard made the initial contact and had the individual with the load talk to DHFS before leaving the yard. A hand monitor (survey) gave radiation reading of 200 microR/hr on the outside of the trailer. A metal tank was observed where the reading was noted. He was told to off load and cover it with plastic until DHFS responds. The individual with the rejected load contacted DHFS on 10/01/07 requesting what to do about the load. Evidently, the individual had made a second attempt to sell the material to Sadoff. When contacted, he reported there were CRM labels on the device. It was reported to be about a foot long, with 8 prongs and 3 fins. A label stated that it was sold under Gen. Lic. No. CL 1933-70. The label for NDC listed Duarte, CA, 91010. The individual was requested to not handle the device and to place it in a secure location. "No information on this device was in the DHFS GL database. DHFS contacted NDC and was informed that it was a Model 103 with 150 mCi of AM-241. The gauge had been sold to Sabee Co, 1718 West Eighth St, Appleton, WI on 12/12/85. The last contact that NDC had with the gauge was 11/20/95. A call was made to Sabee Co in Appleton. An individual there reported that the company was divided in 2002 and management changed in 2003. The company used to do film extrusion. The individual promised to follow up with someone who had been there for a long time and might remember more about the film extrusion process. Contact nos. were given to two former owners. DHFS plans to investigate on October 3, 2007." Media attention: None Event Report ID No.: WI070026. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-10-05
43680 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2007-10-01 22:20 | 2007-10-02 04:28 | 2007-10-03 | LOSS OF EXHAUST VENTILATION STACK FLOW AND ACCIDENT RADIATION MONITORS DUE TO PLANT DATA MULTIPLEXER FAILURE "On 10/01/2007 the failure of a plant data multiplexer (MUX) resulted in the loss of Control Room indication of all plant building exhaust ventilation stack flows and accident radiation monitors. The stack flows and accident radiation monitors are normally accessed by the plants Emergency Response Organization offsite dose calculation application but cannot be accessed at this time. Alternate means of offsite dose projections are available. The duration of the plant data MUX outage is currently unknown. Follow-up notification will be made after restoration of the plant data MUX." The cause of the failure is being investigated. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY HARDY FERRIS TO JASON KOZAL ON 10/03/07 AT 0214 EDT * * * The licensee reports that the plant data multiplexer (MUX) has been returned to service. A faulty off-gas building channel (Offgas / Radwaste Building AXM/SPING/FMIS) was the cause of the MUX failure. The off-gas channel remains out of service. The licensee notified the NRC Resident Inspector. R4DO (Nease) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-10-02
43679 | 0 | FIRSTENERGY NUCLEAR OPERATING CO. |  |  |  |  | 2007-08-02 | 2007-10-01 16:34 | 2007-10-01 | PART 21 REPORT - POPPET NUT AND STEM ASSEMBLY DEGRADATION ON MSIV "In accordance with 10 CFR 21.21(d)(3)(ii), FirstEnergy Nuclear Operating Company (FENOC) is providing the required written notification of a concern regarding the potential for vibration inducted wear on the pilot poppet nut and stem assemblies provided for use in the Beaver Valley Power Station Unit No. 2 (BVPS-2) Main Steam System Isolation Valves [MSIV] that if uncorrected could potentially create a significant safety hazard. FENOC evaluated the concern via a Prompt Operability Determination and concluded that there is reasonable assurance that currently installed valve components at BVPS-2 are operable and plans to replace the affected components during the next BVPS-2 refueling outage." Valve manufacturer of defective valve components is Weir Valves and Controls USA Inc. in Salem, MA. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-10-01
43678 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2007-10-01 13:15 | 2007-10-01 14:17 | 2007-10-30 | REPLACING THE EMERGENCY RESPONSE FACILITY COMPUTER SYSTEM "The Plant Process computer system (Emergency Response Facility Computer System) will be taken out of service for approximate 3 week period starting October 1, 2007, to implement a planned modification. The current ERFCS is being replaced and a computer outage is required for the installation of the new ERFCS. During this time period Emergency Response Data System (ERDS) and Safety Parameter Display System (SPDS) functions will not be available. However, the Qualified Safety Parameter Display System (QSPDS) will still be operable in the Control Room. This notification is being made to inform the NRC that the ERDS will be unavailable until this modification is complete. The operation of the plant systems will not be affected due to this planned action. ERDS and SPDS parameters will be monitored by control board indications. All contingency actions required by ERFCS-3, ERFCS Maintenance Outage Plant Mode 1, have been taken. Meteorological data to support the Emergency Response Organization (ERO) will be obtained from the local national weather service (if needed) as described in our Radiological Response Plan. A follow up notification, to the NRC will be given once ERDS and SPDS are returned to service. The NRC Resident Inspector has been informed." * * * UPDATE FROM KEVIN BOSTON TO J. KNOKE AT 1820 ON 10/30/07 * * * The licensee completed planned modifications and fully restored the Plant Process computer system (Emergency Response Facility Computer System). The licensee notified the NRC Resident Inspector. Notified R4DO (Powers) , T. Kardaras (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2007-10-01
43677 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-09-30 19:58 | 2007-10-01 00:57 | 2007-10-02 | UNEXPECTED AUTOMATIC START OF THE 2-1 EMERGENCY DIESEL GENERATOR (EDG) "A problem with voltage sensing circuit for 4 KV Bus G Startup power supply caused Diesel Generator 2-1 to automatically start. Loss of Startup voltage to a vital bus is an automatic start signal for the associated diesel generator. Startup power has been declared inoperable to 4 KV Bus G. All indications for Startup power to the other 2 vital busses remain normal. All systems functioned correctly in response to the sensed undervoltage condition. Unit 2 is in a 72 hour shutdown action statement per T. S. 3.8.1. An automatic start of a Diesel Generator is reportable per 10CFR50.72(B)(1)(iv)(A). The Diesel Generator has been shutdown per the annunciator response procedure and remains operable." One of the four undervoltage relay starting power fuses for EDG 2-1 was found blown. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 10/2/07 AT 1947 FROM KEN JOHNSTON TO MARK ABRAMOVITZ * * * This update is changing the reporting criteria from a valid system actuation 8-hour report to a invalid specified system actuation 60-day report. "This 60-day notification is being made in accordance with 10 CFR 50.73(a)(i), which states that in case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv)(A), other than the actuation of the Reactor Protection System when the reactor is critical, the licensee may provide a telephone notification to the NRC within 60 days after discovery of the event instead of submitting a written Licensee Event Report. "On September 30, 2007, at 19:58 PDT, EDG 2-1 automatically started, but did not load, due to a failed power supply fuse to an undervoltage sensing relay. EDG 2-1 was shutdown and placed in standby with the undervoltage sensing relay isolated from service. No actual undervoltage condition existed. EDG 2-2 and 2-3 were unaffected by this event. The affected sensing relay circuit was successfully completed. On October 1, 2007, at 18:09 PDT, TS 3.8.1 was exited. "The consequences of this event are limited to the unplanned start of EDG 2-1. The EDG started and functioned in accordance with its design. Since no actual vital bus undervoltage condition existed which required the EDG to start, and since the start occurred inadvertently as a result a single component failure, this event has been classified as an invalid actuation. The original 8-hour notification made under 50.72(b)(3)(iv)(A) is therefore retracted and replaced by this 60-day telephone notification." The licensee notified the NRC Resident Inspector. Notified the R4DO (Nease). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-10-01
43676 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2007-09-28 22:32 | 2007-09-29 02:19 | 2007-09-29 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF A STARTUP TRANSFORMER "On September 28, 2007, while reducing power for a planned refueling outage with the reactor at approximately 30 percent power in MODE 1, an unplanned actuation of the reactor protection system occurred. At 2232 a fault pressure trip signal was received on the A Startup Transformer (SUT), causing a loss of power to Aux Buses D, A & C electrical buses as well as the A-SA safety bus. The loss of A & C buses initiated the RCP underfrequency trip which tripped the Reactor and all three RCPs as designed. The A Diesel Generator automatically started and reenergized bus A-SA as designed. The auxiliary feedwater system actuated as expected due to undervoltage on the A-SA safety bus and loss of the main feedwater pumps. All control rods inserted on the reactor trip. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load reactor coolant system temperature and pressure following the reactor trip. Steam generator water levels are being maintained using auxiliary feedwater. All emergency core cooling system equipment is available. The plant electrical system is being restored at this time. The A SUT remains out of service. The cause of the loss of power from A SUT is under investigation. "This condition is being reported as an unplanned reactor protection system actuation and specified system actuation in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector was notified of this event by the licensee. The plant was in natural circulation for approximately 1 hour. The Main Steam Isolation Valves (MSIVs) were manually isolated per procedure due to loss of EHC indication. Presently the B RCP has been restored to service, MSIVs are still closed, and the motor driven auxiliary feedwater pumps are feeding the Main Steam Generators. There are not any leaking steam generator tubes. The A EDG will be secured after backfeeding of the deenergized buses have been established. | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-09-29
43675 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2007-09-28 17:00 | 2007-09-28 18:45 | 2007-09-28 | REACTOR VESSEL HEAD VENT MAY NOT BE ISOLABLE DURING A FIRE Plant engineering determined that in a postulated fire in the Control Room or Cable Spreading Room which required Control Room evacuation, that "hot shorts" may prevent the reactor vessel head vents from performing their emergency functions in accordance with the plant Emergency Operating Procedures (EOPs). Several relays in the letdown system are not isolated at the Auxiliary Shutdown Panel and have the potential for shorting during a fire. This letdown path can be aligned from the reactor vessel head vents during certain EOP scenarios. The affected reactor vessel head vent isolation transfer switches are: 3RCS*SV8095A & B and 3RCS*SV8096A & B. The site has implemented an hourly fire watch in the affected areas. The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-09-28
43674 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-09-27 23:00 | 2007-09-28 14:17 | 2007-12-12 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED IN HIGHWAY ACCIDENT The State provided the following information via email: "The Arkansas Department of Health received notification on September 27, 2007 at 11:00 p.m. a Troxler 4640B, Serial Number 1574 portable gauge was struck and damaged by a pick up truck. The gauge contains a 9 mCi, Cesium-137 source, Serial number 75-6810. "The incident occurred on Highway 412 near Springdale, Arkansas. The gauge was being used during highway construction. The authorized user was struck and killed during this incident. "The Radiation Safety Officer (RSO) was contacted and arrived at approximately 12:00 a.m. to assess the scene. The source rod along with part of the shielding was separated from the main part of the gauge. A wipe test was taken and the field survey of the wipe indicated that the source had not been ruptured. The RSO partially shielded the source by returning it to the base plate and placed the source rod back with the gauge in the transport case. The gauge was then transported to the licensee's permanent storage area. "Arkansas Department of Health personnel arrived at the licensee's facility at 9:00 a.m. on Friday, September 28, 2007. Department personnel gathered information about the incident and then conducted surveys of the gauge. It appears that the gauge shielding had been cracked and possibly compromised. The highest radiation reading was 35 Mr/hour on contact of the left end side of the gauge. "The licensee has been in contact with the manufacturer for possible disposal options." * * * UPDATE PROVIDED BY STATE (STEVE MACK) TO JEFF ROTTON AT 1032 EST ON 12/12/07 VIA EMAIL * * * The State provided the following information via email: "The Arkansas Department of Health, Radioactive Materials Program, has received documentation of the receipt and disposal on November 2, 2007 of the gauge involved in this incident by a licensed recipient [CPN of Concord, California, CA License # 1100-07]." Notified R4DO (Bywater) and FSME EO (Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2007-10-03
43673 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2007-09-28 13:10 | 2007-09-28 16:12 | 2007-09-28 | EMERGENCY SIREN ACTIVATED INADVERTENTLY DURING A THUNDERSTORM "A single siren in the Nine Mile/FitzPatrick EPZ was inadvertently activated coincident with a thunderstorm and lightning strikes in the area of the siren. Oswego Co (New York) Emergency management officials are issuing a press release regarding the storm related siren activation. Attempts to silence the siren were not effective using the systems remote activation system further indicating that lightning affected the siren. "A work crew has been dispatched to the siren to investigate and has silenced the siren. Notification is being provided to the NRC in regards to the potential for media inquiry." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-28
43672 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2007-09-28 13:00 | 2007-09-28 14:40 | 2007-09-28 | EMERGENCY SIREN ACTIVATED INADVERTENTLY DURING A THUNDERSTORM "A single siren in the Nine Mile/FitzPatrick EPZ was inadvertently activated coincident with a thunderstorm and lightning strikes in the area of the siren. Oswego Co (New York) Emergency management officials are issuing a press release regarding the storm related siren activation. Attempts to silence the siren were not effective using the systems remote activation system further indicating that lightning affected the siren. "A work crew has been dispatched to the siren to investigate and has silenced the siren. Notification is being provided to the NRC in regards to the potential for media inquiry." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-28
43671 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-09-28 11:16 | 2007-09-28 14:35 | 2007-09-28 | SMOKE FROM STEAM PLANT STARTUP REQUIRING STATE NOTIFICATION "At 0930 hours, 09/28/07, the PORTS Plant Shift Superintendent's (PSS) Office was notified of an opacity exceedance, which had occurred at the X-600 Steam Plant on 09/18/07. The PORTS PSS Office notified the Ohio Environmental Protection Agency (OEPA) of this incident, at 1116 hours, 09/28/07. This notification to another government agency is reportable to the NRC as a 4-Hour Event per the United States Enrichment Corporation (USEC) Nuclear Regulatory Event Reporting Procedure UE2-RA-RE1030, Appendix D, Section P (Miscellaneous) which states: 'USEC shall notify NRC of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site fatality or inadvertent release of radioactively contaminated materials.'" The start-up of the steam boiler was completed however, problems were encountered which created smoke after the state mandated time limit for startup smoke had expired. The licensee notified the NRC Resident Inspector and the Department of Energy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2007-09-28
43670 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-09-27 00:12 | 2007-09-27 16:02 | 2007-09-27 | TEMPORARY LOSS OF SMOKE DETECTOR FUNCTION "At 0012 CDST, on 9-27-07 the Plant Shift Superintendent (PSS) was notified that an alarm was received for the C-333 Unit 6 Cell 4 UF6 Release Detection (PGLD) System. Operators responded and found that the READY and MANUAL lights for this system were not illuminated. This PGLD System contains detectors that cover C-333 Unit 6 Cell 4 and Section 2 of the cell bypass piping. At the time of this alarm, some areas of Section 2 of the cell bypass were operating above atmospheric pressure. TSR 2.4.4.1 requires that at least the minimum number of detector heads in each defined section of the cell bypass are operable during steady state operations above atmospheric pressure. With the Unit 6 Cell 4 PGLD system inoperable, only 2 of the required 3 heads in Section 2 of the cell bypass were operable. This PGLD System was declared inoperable, TSR LCO 2.4.4.1.C.1 was entered and a continuous smoke watch was put in place within one hour. Maintenance investigated and determined that two detector heads had shorted to ground which caused this alarm. Engineering has determined that the system would not have been able to perform its intended safety function when this alarm came in. The shorted heads were replaced and the GLD System was declared operable at 0350 hours on 9-27-07 following repairs and testing. This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated o demand, and c.) no redundant equipment is available and operable to perform the required safety function." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-09-27
43669 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-09-27 10:30 | 2007-09-27 15:15 | 2007-09-28 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE WILL NOT RETRACT INTO CAMERA "At 1030 hours the licensee reported that a Sentinel model 676AE (S/N AE1017) radiography camera with a 69 Ci Co-60 source (Make 424-13; S/N 2612) failed to retract to the safe position. After several attempts to retract the source and after a close inspection of the crank device, the Agency was notified and advice sought for authorized personnel who could safely retrieve the source. At 1400 hrs., the RSO had made arrangements with the manufacturer to provide a team equipped to deal with the emergency. The licensee is authorized for fixed site radiography for the facility that he owns. Due to Increased controls, surveillance will be maintained by additional security personnel until the retrieval team is on-site, either late tonight or early tomorrow, Friday 09/28/07." Texas event report: I-8445 * * * UPDATE RECEIVED VIA E-MAIL FROM RAY JISHA TO MARK ABRAMOVITZ AT 1139 ON 9/28/07 * * * "Update, @ 0800hrs., Friday, September 28, 2007. The RSO for Matrix Metals called to report that the manufacturer's specialist arrived on the scene at ~2230hrs last night, Thursday, September 28, 2007 and the source was retracted to the save position within 20 minutes. As the source was in a shooting bay at this fabrication facility, no significant public or personnel exposures occurred. The RSO for the licensee and another authorized user remained at the facility to ensure constant surveillance as per IC requirements. Upon a more thorough inspection of the camera by the manufacturer's representative, a few mechanical issues were determined to be in need of further investigation so the device and source are being over packed today and returned to the manufacturer. A full report from the licensee will be filed" [with the state of Texas]. Notified the R4DO (Johnson) and FSME (Wastler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-10-02
43668 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-09-26 22:44 | 2007-09-27 03:48 | 2007-09-27 | AUTOMATIC REACTOR SCRAM DURING THE PERFORMANCE OF APRM SURVEILLANCE TESTING "At approximately 2244 on September 26, 2007 an unplanned reactor scram occurred. An Average Power Range Monitor (APRM) surveillance was being performed at the time. This surveillance should not have caused a full scram and the cause of the scram is under investigation. The plant responded to the scram as expected, all control rods fully inserted, and there is no need for emergency injection system operation. Critical parameters are being maintained within prescribed bands and the plant has been stabilized. A level 3 signal was received during this scram which would have caused an isolation but all affected valves were already in the closed position. "This event is being reported in accordance with 10CFR50.72(b)(2)(iv)(B) as an event that results in activation of the reactor protection system with the reactor critical." All emergency systems are available and in standby mode. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-09-27
43667 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2007-09-26 14:55 | 2007-09-26 18:04 | 2007-09-26 | TECHNICAL SUPPORT CENTER AND OPERATIONS SUPPORT CENTER VENTILATION INOPERABLE "At 1455 on September 26, 2007 investigatory surveillance testing identified that the emergency ventilation system designed to be manually initiated upon facility activation to maintain the Technical Support Center (TSC) and Operations Support Center (OSC) at positive pressure was not functioning properly. The emergency fan motor operated discharge dampers were not fully opening preventing the ability to achieve rated system flow and therefore design positive pressure. Maintenance is currently in progress to restore the degraded dampers/damper controls. Pilgrim is also investigating a temporary modification that would allow manual damper alignment to support achieving design positive pressure. Responsible Pilgrim Emergency Response Organization (ERO) personnel have been notified of this condition. The alternate technical and operations support facilities remain fully functional." The licensee notified the NRC Resident Inspector. The licensee will notify the State of Massachusetts. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-09-26
43666 | 0 | TRANSNUCLEAR |  |  |  |  | 2007-09-19 | 2007-09-26 15:59 | 2007-12-20 | PART-21 DRY CASK CANISTER DOCUMENTATION LOST "TN identified and documented in Supplier Finding Report 2007-111 that our fabricator, GE-Hitachi Nuclear Energy Americas (GHNEA), had provided inadequate fabrication records resulting in a nonconforming condition relative to the possibility of undocumented Temporary Weld Attachments (TWAs) to the confinement boundary of a loaded NUHOMS 32PTH Dry Shielded Canister (DSC) at Surry Power Station. "This condition involves a lack of documentation for use of qualified welders, approved welding procedures, approved weld filler material and compatible TWA base material, as well as a lack of the required liquid penetrant surface examination report subsequent to TWA removal. Such documentation is required per Article NB-4435 of the ASME B&PV Code Section III, which is a design feature embedded in the Technical Specifications for the NUHOMS HD license. "Based on the preliminary evaluation, it is concluded the subject DSC is capable of performing its design functions involving the structural integrity of the confinement boundary, heat removal, shielding and criticality control associated with the safe storage of spent nuclear fuel." Four DSCs were shipped (three to Surry and one to North Anna) with insufficient documentation. The documentation for one of the Surry canisters was subsequently found. Of the remaining three DSCs, one at Surry, was loaded with spent fuel. * * * UPDATE FROM TRANSNUCLEAR (NEIDER) TO HUFFMAN AT 1537 EST ON 12/20/07 * * * As of 1530 EST on 12/19/07, the licensee determined that a second Dry Shielded Canister (DSC) shipped to Surry that is loaded with spent fuel has undocumented Temporary Weld Attachments (TWAs). The original report above noted that only one DSC (serial # DOM-32PTH-001-C) with TWAs had been loaded with spent fuel at Surry. The licensee had believed that documentation for another one of the loaded DSCs had been subsequently found. Upon further review, Transnuclear has determined that Surry DSC, Serial# DOM-32PTH-003-C (loaded with spent fuel), has other undocumented TWAs that were not initially recognized. Furthermore, two additional DSCs were shipped to Surry that have undocumented TWAs. Specifically, a total of six casks have been shipped with the undocumented TWAs of which five were sent to Surry and one to North Anna. Two of the five at Surry have been loaded with spent fuel. A hold has been place on the three remaining empty DSCs at Surry and one empty DSC at North Anna. In addition, all DSCs still at the licensee's fabricators with possible undocumented TWAs have also been placed on hold. Based on this new information, the licensee is expanding the scope of its initial report. R2DO (Shaeffer) and R1DO (Henderson) notified. In addition, NMSS (Pstrak), FSME EO (Mohseni) and Part 21 coordinators (Hodge and Thorpe) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MD | OTH | PAR | 21.21 |  |  |  | 0 | 2007-09-26
43665 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-09-25 18:15 | 2007-09-26 15:01 | 2007-09-26 | AGREEMENT STATE REPORT - LOST / RECOVERED MOISTURE DENSITY GAUGE "On September 25, 2006 at approximately 6:15 P.M., a gauge user from Geo-Environmental, Inc., had returned to the office to return Troxler gauge 3440, S/N 34036 (9 mCi Cs-137, 44 mCi Am-241:Be) to it's storage location, when he noticed that the gauge was missing and immediately contacted the RSO to report the incident. After the RSO had spoken with the gauge user, the RSO received a call from the office manager that the gauge had been recovered by the Irvine Police Department on Jamboree Rd. in Irvine near the intersection of Jamboree Rd., and Richter Ave. The gauge was returned to the Geo-Environmental, Inc., office at approximately 6:45 P.M. The gauge most likely was out of the control of the licensee for approximately one hour. The gauge case was intact with a single scuff mark. The gauge was inspected by the licensee and found to be intact. The RSO then contacted RHB [DELETED] by phone to report the incident by voice mail. At approximately 9:00 A.M. on September 26, 2007, [RHB] spoke with the RSO about the incident and instructed him to have the gauge inspected and leak tested by a service provider and the RSO stated that he would take the gauge to Maurer Technical Services to be inspected and leak tested. [RHB] also instructed the RSO to provide, within 30 days, a written report, in accordance to 10 CFR 20.2201 (a)(1)(i). The RSO stated that the gauge user involved was allowed to transport the gauge in an open bed truck and with two chains and two locks and with two locks on the gauge case. He also stated that the gauge was transported with only a single lock to secure both chains." CA report number: 092607 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-10-01
43664 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-09-26 06:50 | 2007-09-26 11:37 | 2007-09-26 | OIL SHEEN IN FOREBAY AREA THAT IS NOT FROM BFN At 0650, 09/26/2007, BFN [Brown Ferry Nuclear] was notified by Site Environmental Organization that there is an oil sheen in the forebay that appears to be coming in from the river. Operations responded per site procedure RW1-007, Spill Prevention Control and Countermeasure Plan. Environmental and Fire Operations also responded to the scene. The following organizations have been notified: TVA Operations Duty Specialist, National Response Center (event #849942), Alabama Dept. of Environmental Management (Montgomery and Decatur, AL), and Corporate TVA Environmental (TVA Env. Event #1500). Site NRC Residents have been notified. The spill has been estimated to be between 50 to 100 gallons located outside the BPN Intake Structure with a sheen on the inside of the intake. The sheen has been contained to prevent entry into plant operating spaces. TVA Muscle Shoals Response Team is in route to perform cleanup. It has been verified this spill is not coming from BFN. This event is reportable to the NRC via ENS as a 4 hour report under 10CFR50.72(b)(2)(xi), as 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notifications to other government agencies has been or will be made.'" The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-26
43663 | 0 | ABB INC (CBTS) |  |  |  |  | 2007-09-25 | 2007-09-25 10:17 | 2007-09-25 | POTENTIAL FAILURE TO COMPLY WITH SPECIFICATION CONFIGURATION Two Electroswitch P/N 70034K01 L-2 Auxiliary Switch Assemblies supplied to First Energy Perry Nuclear under purchase order #45151322 were taken from a spare parts inventory and were missing a spacer bushing (P/N 650311A39) that holds the rotary contact in position. First Energy Perry Nuclear reported this under OE25399. The absence of the bushing could allow the contact to move out of position, resulting in a loss of electrical contact. The presence or absence of the spacer cannot be determined from electrical or functional tests of the switch, because the electrical contact may not be displaced from its correct operating position. The two nonconforming switch assemblies were not installed or placed in operation. Plant procedures require all switches to be opened and inspected prior to installation. ABB has taken or is taking action to quarantine and physically inspect all available on-hand inventory, notify all customers, revise dedication procedures, and review historical procurement and customer records. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21 |  |  |  | 0 | 2007-09-25
43662 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-09-25 00:05 | 2007-09-25 03:11 | 2007-09-25 | LEAKING SULFURIC ACID TANK "At 2356 CDT, 9/24/2007, the National Response Center was notified (Report Number 849830) of a leaking sulfuric acid tank located at the C-616 facility. At 0005, 9/25/2007 CDT, the Kentucky Emergency Response Team (Report Number 2007-3170) was notified of this same issue. The tank has developed a leak on the bottom and contains approximately 420 gallons of sulfuric acid which is leaking into a concrete containment dike. This containment dike can be valved to a neutralization pit. The amount of the sulfuric acid which has leaked exceeds the reportable quantity. "This event is reportable as 'USEC shall notify NRC of any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site fatality or inadvertent release of radioactively contaminated materials.' "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-07-2542: PGDP Event Report No. PAD-2007-12" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2007-09-25
43661 | -1 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-09-23 06:30 | 2007-09-24 17:18 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * NOTIFICATION TO DEQ OF POTENTIAL AIR POLLUTION LIMIT VIOLATION "At or around 6:30 am on Sunday, September 23 the main ventilator fan on the [DELETED] exhaust system in the [DELETED] Area ceased operation and the back-up ventilator was activated. It was determined that a breaker tripped on the main ventilator and power was lost. The breaker was reset and the main fan reactivated. At this time, it is not known how long the main fan was inactive. "At approximately 9:30 am the breaker on the main fan tripped again and the back-up fan was activated. The main fan was inactive for approximately 30 minutes before the breaker was reset. "The BWXT Title V Air Permit requires that if air pollution control equipment fails or malfunctions such that excess emissions occur for more than one hour, the DEQ must be notified as soon as practicable, but in no case later than four daytime business hours after the malfunction is discovered. Once Environmental Engineering was notified on Monday morning, September 24, it could not be ascertained with 100% certainty that excess emissions had occurred for more than one hour. To ensure compliance with the permit, BWXT notified DEQ within the four business hour permit limitation that an event had occurred. Should it be determined during our evaluation that an exceedance did not occur, BWXT will withdraw both the DEQ and NRC notifications. "BWXT is making this concurrent notification in accordance with 10 CFR 70 Appendix A (c)." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1429 EDT ON 09/27/07 FROM LEAH MORRELL TO S. SANDIN * * * This report is retracted based on the following: "Upon further investigation, the following was determined: "Per area operating procedures the components being [DELETED] were removed from the acid baths, and heat/agitation to the spacer component [DELETED] baths was turned-off. Following the 6:30 am fan failure it was determined that no [DELETED] activities were occurring and hence there were no excess emissions. Following the 9:30 am fan failure, the breaker was reset and the main ventilator was re-activated in approximately 30 minutes. Since the main ventilator was restarted within approximately 30 minutes, it was concluded that no excess emissions were possible for more than one hour and hence no notification was required. BWXT, therefore, has withdrawn the Title V Air Permit notification and is also withdrawing the concurrent 10 CFR 70 Appendix A (c) notification." The licensee will inform the Virginia Department of Environmental Quality and the NRC Resident Inspector. Notified R2DO(Widmann), FSME (Burgess) and Fuels OUO Gp via email. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
43660 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-09-24 16:00 | 2007-09-24 16:44 | 2007-09-25 | LOSS OF CONTROL OF SPENT FUEL SOURCE MATERIAL "Primary sources belonging to Oconee Nuclear Station were shipped with fuel assemblies to McGuire Nuclear Station. The two fuel assemblies are being stored in McGuire's spent fuel pool. The primary sources are comprised of Americium and Beryllium. The discovery was made after Oconee notified McGuire and requested an inspection of the fuel assemblies." The fuel assembly shipment from Oconee to McGuire occurred about 20 years ago. Details about the sources are not known at this time. The sources are not lost, but rather it is an accountability situation as to who has possession of the sources. McGuire confirmed it has the sources. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM D. McCORKLE TO J. KNOKE AT 1710 EDT ON 09/25/07 * * * "EN#43660 reported on September 24, 2007 stated that primary sources belonging to Oconee Nuclear Station were unknowingly shipped with fuel assemblies to McGuire Nuclear Station. The two fuel assemblies are being stored in McGuire's spent fuel pool. The discovery was made after Oconee notified McGuire and requested an inspection of the fuel assemblies. This was reported under 10 CFR 72.74, Loss of Special Nuclear Material (SNM). "After further evaluation by Site Engineering and Regulatory Compliance, it was determined that this issue was not reportable under 10 CFR 72.74 because the definition of SNM, as defined in 10 CFR 72.3, specifically excludes source materials. Therefore, no SNM was lost. "In addition, this issue is not reportable under a similar criteria, 10 CFR 73.71, Discovery of loss (or recovery) of any shipment of SNM or spent fuel, because the shipment of the fuel assemblies from Oconee to McGuire for storage was always accounted for and arrived safely. Nor do these Oconee Americium and Beryllium primary sources meet the definition of spent fuel as defined in 10 CFR 72.3." The licensee notified the NRC Resident Inspector. Notified NRR EO (M.J. Ross-Lee), R2DO (Bonser), IRD (J. Cruz), ILTAB (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | CRIT LOSS/THEFT OF SNM |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 72.74 |  |  |  | 0 | 2007-09-24
43659 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-09-22 12:45 | 2007-09-22 16:35 | 2007-09-22 | PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING DRYWELL INSPECTION "As part of a planned outage for Browns Ferry Unit 3, initial drywell leak inspections were performed after shutdown (mode 3). This inspection identified a weld defect in Residual Heat Removal (RHR) piping. The defect was in a one inch test line near manually operated valve 3-74-638B. This is classified as pressure boundary leakage and the piping is rated as ASME code class 1. The leak rate was estimated by visual observation at less than 0.25 gpm. Investigation is continuing into the cause of the weld defect. Unit 1 and 2 remain at full power and are not affected by this event. "This event is reportable within 8 hours under 10 CFR 50.72(b)(3)(ii)(A) and 10 CFR 50.73(a)(2)(ii)(A) as 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.'" The licensee plans to continue to Mode 4 (Cold Shutdown) as required by Tech Specs for pressure boundary leakage. The NRC resident inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-09-22
43658 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-09-22 03:15 | 2007-09-22 03:52 | 2007-09-22 | LOSS OF JACKSONVILLE NATIONAL WEATHER SERVICE LAND LINES "Jacksonville National Weather service has notified Plant Hatch that the capability to broadcast prompt notification messages is NOT available at this time. Plant Hatch security notified the Operations Shift Manager at 0315 hours to notify the NRC. Also, site Emergency Preparedness on call person has been contacted and he in conjunction with security has notified the state and local agencies. Information Technology (IT) has been notified of problem with 'land lines.'" Compensatory measures are in effect. There is no estimate at this time for restoration of the Jacksonville "land lines." The licensee will inform the NRC Resident Inspector. * * * UPDATE PROVIDED BY EDWEN URQUHART TO JASON KOZAL AT 0514 ON 9/22/07 * * * The licensee received notification from the Jacksonville National Weather service that the 'land lines' have been restored. Plant Hatch has regained the capability to broadcast prompt notification messages. The licensee will inform the NRC Resident Inspector. Notified R2DO (Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-09-22
43657 | 0 | MPR ASSOCIATES, INC ENGINEERS |  |  |  |  | 2007-09-21 | 2007-09-21 18:23 | 2007-09-21 | PART 21 - DEFECTIVE ANALOG ELECTRONIC CIRCUIT CARD (SBSR AVR) The SBSR AVR card is manufactured by Basler Electric Company in Highland, Illinois. Basler is a supplier of generator control equipment, including generator excitation systems and protective relays. The company maintained a 10 CFR 50, Appendix B Quality Assurance program until the mid 1990s but is presently a commercial supplier with an ISO 9001:2000 certified quality program. The basic component is an analog electronic circuit card in Basler voltage regulators used on emergency diesel generators (EDGs) in US nuclear power plants. The Basler SBSR excitation system provides closed-loop control of EDG stator voltage via an automatic voltage regulator (AVR) and an exciter. The AVR is the controller, while the exciter converts the control signal from the AVR to a field voltage that is applied to the EDG field winding. The AVR is an analog assembly. The main component of this assembly is an electronic circuit card that is referred to as the SBSR AVR card. The SBSR AVR card contains a variety of mounted components. The defect identified within this report deals specifically with the soldered electrical connections between the L1 magnetic amplifier module (magamp) and the card. While there are many Basler SBSR AVR card part numbers, all cards perform the same function and have similar components. Further, all cards utilize the same L1 magamp and all cards mount and electrically connect the L1 magamp in a similar manner. The nature of the defect is that over a period of many years, cracks can form in the solder joint connections between the L1 magamp and the circuit board. There are nine such solder connections at the L1 magamp, and all nine are susceptible to cracking. Cracks have been observed in five SBSR AVR cards that have been in service at two separate nuclear power plants. Also, another case (at one of the same two plants) exhibited symptoms similar to those exhibited by cards with cracked solder joints, but the card was not inspected for the presence of cracks nor retained. Accordingly, cracks are suspected but not confirmed in this other case. It has been observed that full circumferential cracks can form. When a full circumferential crack forms, the electrical resistance at the connection can increase significantly and electrical continuity at the connection could be lost. In four of the six cases, the observed symptom associated with the cracks is that during surveillance testing, the EDG starts and takes longer than specified to reach its rated voltage. The condition is observed to be intermittent, i.e., when the test is repeated the EDG typically starts and meets its time requirement to establish rated voltage. This intermittent nature has made troubleshooting more difficult as the symptom is typically not reproducible. This observation is consistent with the fact that a cracked solder joint may not fully and permanently lose electrical connectivity. In one of the six cases, the observed symptom was that during surveillance testing, the voltage regulator failed to properly control output voltage of the EDG. The EDG had to be shut down, and it may not have been capable of powering its design basis loads. In one of the six cases there were no symptoms or deficiencies during surveillance testing. Rather, the cracks were seen during a visual observation. For SBSR AVR cards that have been supplied by MPR, MPR has not specified maintenance requirements related to inspection or replacement. Accordingly, there are no supplier-specified actions that would ensure that degraded cards are detected or avoided. The safety hazard is that when electrical continuity is lost at L1 magamp soldered connections, the voltage regulator does not perform as intended, and the EDG could fail to deliver emergency AC power as intended. Analyses and testing by MPR in conjunction with Basler Electric confirmed that, although various symptoms can be observed, loss of electrical connectivity at some combinations of L1 magamp soldered connections could render the voltage regulator unable to control voltage. In such a case, the associated EDG would not be able to provide emergency AC power as intended. Because EDGs are important safety-related components at nuclear power plants that are relied upon for safety-related functions, the cracked solder joints could be a substantial safety hazard. MPR has provided SBSR systems, including AVR circuit cards and spare AVR cards to the following nuclear plants: Beaver Valley, Millstone, Davis-Besse, Pilgrim, Cooper Nuclear, Ginna. US Nuclear plants believed by MPR to utilize the SBSR excitation system are: ANO, Beaver Valley, Calvert Cliffs, Cooper, Crystal River, Davis-Besse, Diablo Canyon, Duane Arnold, Farley, Fermi, FitzPatrick, Ginna, Hatch, Indian Point, Kewaunee, McGuire, Millstone, North Anna, Palisades, Peach Bottom, Pilgrim, Prairie Island, Robinson, Salem, Sequoyah, and Vermont Yankee. For SBSR AVR cards that MPR has supplied, MPR will issue a maintenance bulletin to advise SBSR AVR owners that an inspection and repair program should be established. The inspection program should periodically inspect for L1 magamp solder joint cracks. The inspections should occur on a fuel cycle periodicity after 15 years of service. If cracks are found, the card should be replaced, or the joints repaired by remaking the solder connections. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-09-21
43656 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2007-09-21 15:45 | 2007-09-21 17:07 | 2007-09-21 | POTENTIAL OVEREXPOSURE OF RADIOGRAPHER HELPER The State of Oklahoma received a report from Global X-Ray Services of a high monthly exposure reading based on results from Landauer. The August badge for a radiography helper had an exposure of 5680 mR. Initial interviews with the employee determined that he had no instances where his dosimeter ever read off-scale or his rate meter ever indicated excessive exposure rates. His work record shows that he worked for 24 days in the month of August with I-192 radiographic devices. He worked with various radiographers during the month and there is no current information showing any excessive exposures for any of the radiographers. The employee is relatively new and has been averaging 200 - 300 mR per month exposure prior to the August reading. Landauer is performing analysis to determine if the dose indicates a 'Static' exposure. Both Global X-Ray and the State are developing follow-up actions at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-09-26
43655 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-08-22 12:00 | 2007-09-21 14:46 | 2007-09-21 | AGREEMENT STATE REPORT - STOLEN TRITIUM EXIT SIGN The State provided the following information via facsimile: "Reported vandalism of Tritium Exit sign located in the North Parking Structure on campus. Sign was broken open and tritium tubes removed. Police were notified. Estimated activity 12 Ci. No contamination present on wipes of area. Licensee notified all departments of the theft via a safety advisory. "As of 09/20/07 the tritium tubes have not been recovered. A 30 day reporting requirement [is being issued] because it was considered that an exposure would be highly unlikely from this incident. Since the tubes from the sign appeared to be intact when they were removed from the sign (no contamination on wipes) the radiation exposure to the individual is assumed to be zero. The licensee will be replacing all the tritium exit signs with non-radioactive exit signs by November 30, 2007." CA Report # 082207 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-09-26
43654 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-09-21 | 2007-09-21 13:06 | 2007-09-21 | AGREEMENT STATE REPORT - MISSING TROXLER GAUGE The State provided the following information via email: "Licensee called 9/21/07, 1:15 AM and reported that a Troxler gauge [model 3411, s/n 10416] is missing. It was last seen on 9/19/07 during the morning inventory in the locked storage locations along with other gauges. It was not present during the evening inventory 9/19/07. No other gauges are missing. Employees started being interviewed by the RSO on 9/20/07. The storage locks have not been tampered with. It was reported missing to the North Miami PD [report # 07-30026] and this office on 9/21/07. Florida is investigating." Isotopes were Am-241/Be (40 mCi) and Cs-137 (8 mCi). Florida Report # FL07-140. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-09-26
43653 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-09-19 15:25 | 2007-09-20 14:46 | 2007-09-20 | OFFSITE NOTIFICATION OF UNKNOWN DISCHARGE AND 24 HOUR REPORT PER APPENDIX B OF OPERATING LICENSE "[The information below concerns a] September 19, 2007 NPDES Reportable Occurrence verbiage/Notification to the Ohio Environmental Protection Agency. This notification was made on September 20, 2007. "Time of discharge is unknown. Cloudy water was discovered in 'Major Stream' diversion (also referred to as 'Red Mill Run') at approximately 1525 hours on September 19, 2007. "The amount of discharge is unknown. At the time of discovery, approximately 10 to 15 gallons of water, per minute, were observed discharging from the storm drain. On September 20, 2007, the observed discharge from the storm drain was approximately 1 to 2 gallons of water per minute. "The pH of the stream was 11.2 standard units (SU) at 1650 hours on September 19, 2007 with white powdery deposition on the stream bed. At 1000 hours on September 20, 2007, a sample taken for pH indicated 8.48 SU. "A number of small stressed fish were observed at time of discovery, along with approximately 5 to 10 small dead fish. No frogs, crayfish, or other local aquatic life forms were observed to have been negatively impacted. "Initial analysis of the sediment from the stream bed indicated the main constituents were inorganic calcium & oxygen (possible materials include but not limited to calcium oxide, calcium carbonate, calcium hydroxide). "The source of the high pH and white sediment is unknown at this time and an investigation is in progress. "The affected area [has been inspected] and recommendations for clean-up remediation [provided]. The recommendations are currently being evaluated." "This event is being reported in accordance with Appendix B to the Operating License (The Environmental Protection Plan) which requires reporting of any occurrence of an unusual or important event that indicates or could result in significant environmental impact causally related to plant operation (An example includes 'fish kills'). "This event is also being reported in accordance with 10CFR50.72(b)(2)(xi). 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an on-site facility or inadvertent release of radioactively contaminated materials'." The NRC Resident Inspector and applicable State authorities have been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-20
43652 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2007-09-19 15:04 | 2007-09-19 15:45 | 2007-09-19 | ALERT DECLARED DUE TO INADVERTENT DISCHARGE OF CO2 INTO SWITCHGEAR ROOM "At 1454 [EDT] an inadvertent discharge of CO2 occurred in the Division 3 switchgear room. The Control Building 261 foot (ground level) and below was evacuated. An ALERT emergency condition was declared at 1504 [EDT]. Emergency Response Facilities are being manned. NY State and Oswego County have been notified via the RECS line. Unit 1 was not affected. No personnel were injured. Unit 2 remains at full power. Cause is under investigation." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM SKINNER TO HUFFMAN AT 23:46 EDT ON 9/19/07 * * * The licensee terminated the ALERT at 2147 EDT on 9/19/07 base on restoration of free access in the control building and isolation of CO2 fire protection discharge systems in Unit 2. All the CO2 discharge systems were manually isolated because the licensee could not conclusively determine the cause of the fault that led to the initial inadvertent actuation. The licensee has established compensatory fire protection actions. Trouble shooting into the cause of the event continues. The licensee has notified the State and local authorities of the event termination. The NRC Resident Inspector has also been notified. Regional and HQ NRC management have been notified including R1(Dapas), NRR (Dyer), IRD (McDermott), R1DO (Krohn), and NRR EO (McGinty). Notifications to external agencies initially notified of the event were made by the HOO. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-09-19
43651 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2007-09-18 12:00 | 2007-09-18 16:29 | 2007-09-18 | SHIELD BUILDING VENTILATION SYSTEM INOPERABLE "At 1200 a condition associated with the Shield Building Ventilation Train A damper controller was identified that rendered the system inoperable. This condition was identified while Shield Building Ventilation Train B was inoperable for routine maintenance. Consequently, both trains of Shield Building Ventilation were simultaneously inoperable. Technical Specification TS 3.6.c requires a reactor shutdown within 12 hours of this condition. The routine maintenance on Shield Building Ventilation Train B was completed and retest performed at 1331. Shield Building Ventilation Train B was returned to operable and Technical Specification requirements to shutdown were exited. The plant remains in a 7 day Action Statement per TS 3.6.c with Shield Building Ventilation Train A inoperable . "This event is reportable under 10CFR50.72(b)(3)(v)(C), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.'" I&C technician was walking down a different job in the area and noticed a light illuminated on the A control board which should not have been illuminated. Additional investigation revealed an electrical condition would have prevented the modulation of the dampers thereby rendering the A train system inoperable. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2007-09-18
43650 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-08-30 | 2007-09-18 14:30 | 2007-10-19 | AGREEMENT STATE REPORT - 23 MISSING TRITIUM EXIT SIGNS Harvard University was replacing and recycling old exit signs. When workers arrived to remove the old exit signs and reprocess them, the signs could not be found. The licensee believes the exit signs may have went along with some old light bulbs that were being recycled. The licensee inspected the recycling chamber and found it free of contamination. Each sign originally contained 7.5 curies of Tritium. Decayed activity as of today is 93 curies. They initiated their investigation on August 30, 2007, and the investigation is on-going. * * * UPDATE FROM R. GALLAGHER TO P. SNYDER AT 1021 0N 10/19/07 * * * Harvard University has taken / is taking the following corrective actions: "1). Training sessions provided to Harvard University recycling program staff [identification of H3 signs and new requirements to send all such signs to the Radiation Protection Office (RPO) for processing]. "2). Revision made to EXIT Sign Fact Sheet, which focused on requirements for building managers and requires transfer of any removed radioactive signs to the RPO for reclamation. "3). Additional EXIT sign training provided to facility directors, facility managers, compliance officers, and the real estate program to heighten awareness of radioactive EXIT signs and proper recycling." The Commonwealth of Massachusetts has concluded their investigation of this matter and considers the corrective actions taken by the licensee to be acceptable. Notified R1DO (R. Bellamy) and FSME EO (G. Morell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-09-21
43649 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-09-18 08:43 | 2007-09-18 11:37 | 2007-09-18 | REFUELING WATER STORAGE TANK TEMPERATURE ABOVE OPERATING LIMITS "At 0043 on 9/18/07, during performance of Technical Specification (TS) Surveillance Requirement (SR) 3.5.4.1, the 2T-13 Refueling Water Storage Tank (RWST) was found to be at 105 degrees F. Limiting Condition for Operation (LCO) 3.5.4 A was therefore not met due to temperature being above the parametric value limit of 97 degrees F (100F technical specification value). "The cause of the elevated temperatures of 2T-13 is currently under investigation. At 0843 an orderly shutdown of Unit 2 was commenced because of the continued elevated temperature of the Refueling Water Storage Tank. Troubleshooting to identify the cause of the problem and take remedial actions continues." Unit 1 RWST temperature is 77 F. Licensee is taking action to lower Unit 2 RWST temperature. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY RICK ROBBINS TO JASON KOZAL ON 9/18/07 AT 1901 * * * "Unit 2 RWST temperature was verified at 97 degrees F at 1421 CDT. The 2T-13 RWST is operable and LCO 3.5.4.is now met. The Unit 2 power reduction was terminated at 20% reactor power. Current plans are to continue to cool down the RWST using station procedures that place the RWST on recirculation through the residual heat removal (RHR) heat exchanger with component cooling water (CCW) to cool the heat exchanger. Plans are in progress to return Unit 2 to full power on 09/18/07. "A root cause evaluation is in progress to determine the specific cause of the event; however, preliminary investigations have determined that the heaters were on with an improper setpoint. The power supply to the heaters have been turned off and temperatures are being monitored on an hourly basis while the RWST is on recirculation." The licensee notified the NRC Resident Inspector. Notified R3DO (Peterson) | 0 | 53 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-09-18
43648 | 0 | TYME ENGINEERING |  |  |  |  | 2007-09-18 08:00 | 2007-09-18 10:39 | 2007-09-18 | STOLEN TROXLER GAUGE A technician was working at a jobsite on 9/15/07, and when he completed his work about 1800, he drove to the company office in Southfield, MI. He left the Troxler gauge double locked in the back of the company pickup truck. When he reported to work on 09/18/07 at 0700 he noticed that the Troxler gauge was missing from the truck. He reported this to the RSO. The Troxler is a model 3440, s/n 36107, with Am-241/Be (40 mCi), s/n 78-998, and Cs-137 (8 mCi), s/n 77-3236. Licensee reported this to the Southfield police who issued report # 07-58570. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-09-18
43647 | 0 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2007-07-15 | 2007-09-17 17:19 | 2007-09-17 | ACTIVE SOURCE CAN BECOME DISLODGED IN HDR AFTERLOADER DEVICE The following information was received via fax: Manufacturer submitted this notification based on an event involving a High Dose Rate (HDR) Afterloader that occurred at City of Hope Hospital in Duarte, California on July 15, 2007 [See EN# 43493] "Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect- VariSource HDR Afterloader model 200 and VariSource HDR Afterloader model ID "Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: The VariSource HDR Afterloader is manufactured by: Varian-TEM Ltd., Gatwick Road, Crawley, West Sussex RH102RG, United Kingdom "Nature of the defector failure to comply and the safety hazard which is created or could be created by such defect or failure to comply: The active source can become dislodged from the internal tungsten safe if the emergency source retract hand crank is used when the active source is safely parked in the internal shield. (1) This event can only occur if the operator turns the emergency hand crank while the source is safely parked. (2) The emergency source retract hand crank is to be used only when the active source is in the out or exposed position. It is not designed, nor intended to be operated when the source is safely parked. (3) The emergency hand crank is only connected to the active source wire. It is not connected to the dummy source and its operation has no effect on the dummy source." Customer Technical Bulletin, CTB-VS-366A, "Clarification on the use of the emergency retract hand wheel to prevent accidental exposure" was issued to all users of the VariSource HDR unit on April 27, 2004. This CTB will be reissued to all domestic customers. A warning label addressing the proper use of the emergency hand crank was attached to all VariSource HDR units in 2004. A new warning label is being developed that will restate the proper use of the hand crank. Also a formal revision was made to user training to emphasize that this event is possible if the user makes an error by operating the emergency hand crank when the active source wire is safely parked in the tungsten shield. There are 186 VariSource HDR units in the United States and a list was provided to the NRC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-09-17
43646 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2007-09-17 05:59 | 2007-09-17 07:36 | 2007-09-17 | OFFSITE NOTIFICATION TO LOCAL LAW ENFORCEMENT "On 9/17/07 at 0559, an accidental discharge of a security officer's firearm occurred while conducting shift turnover and arming functions in the Station's security guard house. The officer was injured in the right leg below the knee and at this time, the injury is believed to be non-life threatening. The officer has been transported to a local hospital for treatment. No plant systems have been affected. The local NRC resident has been informed of the event. Local law enforcement [Seabrook Police and New Hampshire State Police] has also been notified and is onsite providing investigative assistance." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-17
43645 | -1 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-09-17 01:49 | 2007-09-17 03:16 | 2007-11-06 | HPCI UNABLE TO PERFORM IT'S SAFETY RELATED FUNCTION "During performance of the quarterly HPCI valve stroke test the HV-055-2F093, HPCI Vacuum Breaker Outboard PCIV, failed to close. The PCIV was declared inoperable. The valve was subsequently closed and de-energized to meet Technical Specification requirements. The valve did close from the handswitch on the subsequent attempt, investigation into the cause is in progress. The closure of this valve at 0149 on 9/17/07 prevents Unit 2 HPCI from performing it's safety related function. Unit 2 RCIC and all other Unit 2 ECCS systems remain operable." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 12:34 ON 11/6/2007 FROM MARK ARNOSKY TO MARK ABRAMOVITZ * * * "This is a retraction of the event notification made on 9/17/07 at 03:16 EDT hours. This event (43645) was initially reported as a safety system functional failure under the requirement of 10CFR50.72(b)(3)(v)(D). Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable for a planned evolution to conduct stroke time surveillance testing on the HPCl exhaust vacuum breaker primary containment isolation valves (PCIVs) and other valves. At 00:23 hours the outboard vacuum breaker PClV failed to close from the main control room hand switch. The PClV was declared inoperable and closed as required to support subsequent troubleshooting and to meet the Technical Specification (TS) 3.6.3 Primary Containment Isolation Valves action statement. TS 3.6.3 Action 'a' requires the inoperable PClV to be closed within 4 hours. This action was completed at 01:50 hours. "In addition, the HPCl system was declared inoperable following the remote manual closure of the inoperable PClV from the main control room hand switch since this made the HPCl exhaust line vacuum breaker function inoperable. The feed switch for the HPCl steam admission motor-operated-valve (MOV) was opened to prevent turbine start without exhaust line vacuum relief capability. "Troubleshooting determined that the most likely cause of the PClV failure to close was an intermittent high resistance condition on the PClV hand switch contact. The PClV failed to close on the first demand but was successfully closed on the second and third demands. The PClV hand switch contacts were cleaned and successfully tested. Unit 2 HPCl was restored to operable status at 20:25 hours. "The HPCl exhaust vacuum breaker PClVs are normally open. The automatic closure capability of though PClV was not adversely affected by the degraded hand switch contact. "The HPCl system was declared inoperable as part of a planned evolution to conduct PClV surveillance testing in accordance with an approved procedure and the plant's Technical Specifications. The HPCl system was later made unavailable for the purpose of conducting maintenance on the inoperable PCIV and completing the TS action. The failed PClV hand switch did not adversely affect the HPCl system's capability of performing its safety function. HPCl remained capable of automatic initiation until the exhaust vacuum breaker PClV and HPCl steam admission valves were closed under administrative control to support maintenance and completion of the TS action. "A condition did not exist at the time of discovery that could have prevented the fulfillment of the HPCl safety function." The licensee notified the NRC Resident Inspector. Notified the R1DO (Miller). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-09-17
43644 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-09-14 22:00 | 2007-09-15 19:26 | 2007-09-17 | AGREEMENT STATE REPORT INVOLVING POTENTIAL OVEREXPOSURES DURING INDUSTRIAL RADIOGRAPHY At approximately 2200 hrs. on 9/14/07 during radiography work at a jobsite in Vidor, TX (30 miles north of Beaumont), two radiographers noticed that their pocket dosimeters read off-scale high (range 0- 200 m R). They were using a 94 curie Co-60 camera (QSA model 943, A424-14, S/N36391B) to take radiographic shots of a 6 inch thickness steel ladle and had just changed the film in the holder which was located about 7 inches from the exposed source behind the steel ladle. It appeared that the source had not retracted into its shielded volume. A specialist in source retrieval was brought to the jobsite and the source successfully returned to its stowed position. During retrieval the specialist's pocket dosimeter also went off-scale high (range 0-5 R) at which time he switched to a higher reading dosimeter (range 0-20 R) completing the task with an indicated dose of 13 R. The State of Texas was notified of the incident at 1804 hrs. on 9/15/07 and confirmed that the licensee was sending the individuals dosimetry off for emergency reading. Further, the State contacted REAC/TS (Radiation Emergency Assistance Center/Training Site) who recommended that these individuals be immediately medically examined with followup blood chemistry tests, i.e., CBC (complete blood cell), performed the following day to document any cytogenic changes. The State will conduct an investigation to determine the cause of the overexposures. * * * UPDATE PROVIDED BY RAY JISHA TO JEFF ROTTON VIA EMAIL AT 0927 ON 09/17/07 * * * The State provided the following information via email: "The two workers 200 mR dosimeters were off scale and it appears that they were working with the source not fully retracted as a crimp in the source tube was noted approximately 1.5 feet from the camera. A ladder was used to enter the ladle from one side and the source was positioned on the opposite side with a magnetic hold on device. It has been conveyed that the hold on device fell off at some time and damaged the source tube restricting the full retraction of the source for two shots with a survey being taken on the second shot and thus the source being discovered in the exposed position. The source retrieval was difficult apparently requiring the source to be fully extended so that the source tube could be manually stripped from the drive cable. This took reportedly 12 one minute maneuvers, lead shot bags used when possible." "Blood was drawn Saturday and twice Sunday for CBC the results of which are to be faxed to REACTS. On Monday blood will be drawn with heparin/lithium for transport to REACTS for cytogenic analysis. Our inspector in the area is to conduct a recreation on the event today and more details will follow in a formal report." Texas report number I-8444 Notified R4DO (V. Campbell) and FSME EO (Morell), and IRD Manager (Blount) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-09-19
43643 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-09-13 18:00 | 2007-09-14 18:48 | 2007-09-14 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The licensee completed testing at jobsite and thought he had stowed his moisture density gauge (Troxler model 3340, SN 25752, 8 - 10 mCi Cs-137/ 40 mCi Am-241/Be). He left the jobsite in Shingle Springs, CA, and while in-transit to Elk Grove, CA (via highway 50) the technician heard a thud from outside of the vehicle but did not think anything of it. When the technician arrived at his residence he noticed the truck's tailgate was down and realized the gauge was missing. He backtracked to the jobsite and was unable to locate the gauge on the highway or at the jobsite. The technician notified the RSO, the Elk Grove Police Department and the California Highway Patrol. The State will provide more information as it becomes available. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-09-19
43642 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2007-09-14 10:50 | 2007-09-14 13:20 | 2007-09-14 | OFFSITE NOTIFICATION TO EPA REQUIRED BY NPDES PERMIT "At 0630 hours on September 14, 2007, while operating at 100% power, Pilgrim Station experienced a fish impingement on the intake structure traveling screens. Plant power was reduced to 50% and one of two seawater circulating pumps was secured. The impingement did not impact the operability of safety related cooling water systems. At 1050 hours, plant assessment determined that the impingement, involving a large school of Atlantic juvenile menhaden, is reportable to the Environmental Protection Agency (EPA) under conditions of the Pilgrim National Pollutant Discharge Elimination System (NPDES) permit. Following a substantial reduction in the numbers of fish discharged via the traveling screen outfall trough, the seawater pump was restored to service and restoration of the plant to 100% power is in progress." The licensee informed the NRC Resident Inspector and will inform both the State and EPA. | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-14
43641 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2007-09-13 23:04 | 2007-09-14 02:18 | 2007-09-14 | POTENTIAL REACTOR PRESSURE BOUNDARY LEAKAGE "During an investigation in response to a low megger reading, a small amount of water was discovered in the environmental qualification boundary of the 22B RCS Thot thermowell (TE-3-422B2). Analysis of the water on 9/13/07 at 2304 showed Cesium 137 and 134, and Magnesium 54 indicating that the source of water intrusion into the thermowell was likely reactor coolant system (RCS) fluid. We are continuing the investigation for potential causes of water intrusion other than the Reactor Coolant System. This report is being made based on the previous indication of RCS leakage into 23A, RCS Tcold thermowell (TE-3-420) [see EN #43627 from 09/10/07] and similar discovery in our preliminary investigation. "PTN Unit 3 Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.6.2.a permits no reactor coolant pressure boundary leakage in Modes 1-4. This report to the NRC is pursuant to the requirements of 10 CFR 50.72 (b)(3)(ii)(A) as a degraded condition." Turkey Point Unit 3 is presently defueled. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-09-14
43640 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2007-09-13 14:00 | 2007-09-13 17:11 | 2007-12-17 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via email: "The Minnesota Department of Health (MDH) has been notified that on September 13, 2007 at approximately 2:00 PM, a moisture-density gauge containing sealed sources of radioactive material was stolen from a pick-up truck owned by Asset Management. The truck was parked at a residence in Forest Lake, Minnesota, and the gauge was believed to have been stolen sometime during the previous night. "The MDH, which regulates the use of these types of radioactive materials in Wisconsin, is working with the Forest Lake Police Department and officials of Asset Management to recover the stolen gauge. "The moisture density gauge is used to measure the moisture content and density of soils and building materials. The gauge is a yellow box measuring approximately 30 inches in length, 14 inches in width and 17 inches in height (see attached picture). The gauge and the case weigh a total of 90 pounds. The gauge itself weighs 29 lbs. The case and the gauge are clearly marked as containing radioactive materials. . ." The gauge is a Troxler Model 3430 (S/N 33277) containing two (2) sources; 9 milliCuries Cs-137 and 44 milliCuries Am-241:Be. The State of Minnesota issued a press release with contact information for the return of the gauge. MN Report No.: MN070006. * * * UPDATE FROM MDH (JOHNS) TO CROUCH AT 1358 EST ON 12/17/07 * * * The Troxler moisture density gauge was recovered at 0600 CST this morning. An unknown person placed the gauge outside the Forest Lake, MN Police Department. The gauge appeared intact and no detectable leakage existed. The gauge was returned to the licensee. Notified R3DO (Duncan), FSME (Morell), and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2007-09-18
43639 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2005-02-01 | 2007-09-13 15:04 | 2007-09-13 | AGREEMENT STATE REPORT - DOSE DIFFERS BY GREATER THAN 50% OF PRESCRIBED The State provided the following information via email: "A teletherapy patient received a dose greater than 50% of the prescribed fractionated dose due to an improperly calculated dose delivery time. The medical physicist used a fractionated dose of 200 cGy instead of the prescribed dose of 100 cGy. This overexposure occurred during the first fraction to the patient. Before the second scheduled treatment, a different therapist questioned the long treatment time and brought the matter to the medical physicist. The physicist checked the calculations, discovered the error and cancelled the treatment for the day. The radiation oncologist anticipates no unusual acute or late effects from the delivered dose. The University of Iowa no longer is in possession of this device. It was de-sourced on November 16, 2005." The device was a sealed Co-60 teletherapy source. The therapy was targeting the bone marrow. Iowa report number: IA070003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2007-09-18
43638 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2007-05-15 | 2007-09-13 13:41 | 2007-09-13 | AGREEMENT STATE REPORT - INABILITY TO RETRACT RADIOGRAPHY CAMERA SOURCE The State provided the following information via email: "The licensee reported the inability to retract an Ir-192 radiography source (model G-60, serial #OA2910) that contained an activity of 1.45 TBq (39.12 Ci) into a SPEC exposure device (model 150, serial #456). The radiographers had attached the guide tube to a ladder within a tank at the Absolute Energy Ethanol Plant located on the Iowa/Minnesota border. Halfway through a shot, a gust of wind blew the ladder over, which crimped the guide tube such that the source could not be retracted. The radiographers located the source in the guide tube and covered it with sandbags. The crimped guide tube was then reformed using a hammer and the source was successfully retracted. A new guide tube was shipped to the jobsite and the damaged guide tube was destroyed. The two radiographers received exposures of 1.1 and 1 mSv (110 and 100 mrem) from the incident. The licensee submitted a written report to the Iowa Department of Public Health on 6/13/2007, but failed to provide the required 24-hour notification. The State of Minnesota performed an audit of the licensee on 7/12/2007 and it was determined that the incident occurred in Iowa. The root cause of the incident is the failure to properly secure the ladder per company policy. Corrective actions taken by the licensee included terminating the lead radiographer involved and providing additional instruction to all radiographers on the policy to secure ladders used as guide tube stands." Iowa report number: IA070002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2007-09-20
43637 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2007-09-12 11:30 | 2007-09-13 09:41 | 2007-09-13 | MODERATION CONTROL ITEM RELIED ON FOR SAFETY DEGRADATION "During an investigation of an unusual sinter test measurement result, it was determined that one of the Items Relied On For Safety (IROFS), as documented in the [Integrated Safety Analysis] (ISA) summary, had degraded. This report is submitted for administrative reporting pursuant to 10 CFR 70.50 Appendix A (b)(2). "The IROFS described for the moderation control of the powder additive at the Dry Conversion Process (DCP) blender operation did not function as required because of an error that occurred at the Dry Scrap Recycle (DSR) container transfer station. At no time did an Unsafe condition exist. The existing criticality safety analysis of the operation bounded the situation, was effective and was not challenged. "The container transfer station operation is shut down pending completion of an investigation and implementation of corrective actions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2007-09-13
43636 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2007-09-13 06:01 | 2007-09-13 06:48 | 2007-09-13 | NOTICE OF UNUSUAL EVENT FOR A HYDRAZINE SPILL IN THE TURBINE BUILDING "A Notification of an Unusual Event was declared at 06:01 EDT due to a chemical leak in the Turbine Building truck dock area near a roll-up door. The leak was discovered at 05:40 EDT coming from a line connecting two vertically stacked Hydrazine Metal chemical storage totes located inside a ventilated enclosure. The Hazmat Response Incident Team was formed to address the spill. Approximately 10 gallons is inside the enclosure berm. A small amount of liquid has leaked outside the enclosure berm but has been contained. Containment activities are in progress. Leak rate appears to be significantly less. Additional plant staff has been called in to support and are arriving on site at the time of this notification. The area has been roped off and plant announcements to warn personnel of this hazard have been made. (EAL-11.4, Plant Conditions Warrant Increased Awareness by Plant Staff)" The licensee notified the NRC Resident Inspector, state and local government agencies. * * * UPDATE AT 0742 ON 9/13/07 FROM CHLADIL TO ROTTON * * * The licensee terminated the Notice of Unusual Event. The termination criteria was that the spill was stopped and the licensee has established limited personnel access restrictions to the turbine building truck bay and the service building elevator. The licensee is continuing to clean the area. The licensee notified the NRC Resident Inspector and will be notifying state and local government agencies. Notified R4DO (Shannon), NRR (Ross-Lee), IRD (Blount), DHS (Haselton) and FEMA (Laforty). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-09-13
43635 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2007-09-12 06:35 | 2007-09-12 09:58 | 2007-09-12 | REACTOR SCRAM FOLLOWING INTAKE STRUCTURE TRAVELING SCREEN FOULING "As a result of high winds and a severe storm front moving through the area a Nuclear Plant Operator (NPO) found the intake canal water murky, wind speed was noted to be 40 MPH. The Traveling Screens were placed in the continuous mode of operation and increased monitoring was put in effect. At 0520 the NPO noted that 'a lot of weeds and fish were coming in through the intake' and that a full trash basket had been changed out. At approximately 0630 the NPO reported that the traveling screens were not moving and intake level was lowering due to the influx of debris. The Shift Nuclear Operator (SNO) entered the appropriate Abnormal Operating Procedure (AOP) for lowering intake level and commenced rapid power reduction. At 0635 with intake level at 240 feet the SNO inserted a manual scram and entered the appropriate AOP and Emergency Operating Procedure (EOP). "Reactor Vessel level decreased to less than 177 inches above the top of active fuel resulting in a Primary Containment Isolation System (PCIS) Group 2 isolation signal. The PCIS Group 2 isolation resulted in a valid signal to close PCIS valves in the Drywell Floor Drain System, the Drywell Equipment Drain System, the Residual Heat Removal (RHR) System, the Traversing In-Core Probe (TIP) System, the Containment Atmosphere Dilution (CAD) System, and the Reactor Water Clean-Up (RWCU) System. However, as a result of the power reduction the operators were able to maintain reactor vessel level above the actuation setpoint for the High Pressure Coolant Injection (HPCI) System and the Reactor Core Isolation Cooling (RCIC) Systems and these systems were not required to operate. "At 0640 the Scram was reset, at 0710 the Group 2 PCIS Isolation was verified, and at 0729 the Group 2 PCIS Isolation was reset. "The cause of the traveling screens stopping has been determined to be due to shear pins on the traveling water screen shearing due to excessive debris loading. "All equipment responded as expected during the downpower and subsequent manual Scram. All rods are in and the plant is stable in MODE 3, Hot Shutdown." Decay heat is being removed by dumping steam to the condenser via the turbine bypass valves. The safety buses are being powered by offsite power. The 'B' train Residual Heat Removal pump was out of service at the time of the event for planned maintenance. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM G. DORMAN TO J. KNOKE AT 1205 EDT ON 09/12/07 * * * "At 1034 with the plant shutdown and a cooldown in progress reactor vessel (RV) level lowered to less than 177 inches above TAF [Top of Active Fuel]. This resulted in a valid Reactor Protection System (RPS) Scram signal and a PCIS Group 2 Isolation Signal. AP systems responded as expected. Reactor vessel level remained above the actuation setpoint for HPCI and RCIC and they were not required to operate. RV level was restored and the Scram was reset. "At the time of the initial event and at this update the plant is in LCO action statement 3.5.1.A for the 'B' RHR Pump being out of service. The system is being restored at this time. The licensee notified the NRC Resident Inspector. The licensee also notified the state and is providing a press release to the media. Notified R1DO (Trapp). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-09-12
43634 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-09-11 15:09 | 2007-09-11 22:58 | 2007-09-12 | LOSS OF SAFETY FUNCTION - BOTH EDG'S UNAVAILABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of SSCs that are needed to mitigate the consequences of an accident. "Diesel generator #2 (DG2) was inoperable and unavailable for planned maintenance. This was day 2 of a 7 day shutdown LCO. At 1449, Diesel Generator #1 (DG1) was declared inoperable and unavailable at 1509, due to malfunction of the day fuel oil day tank high level shutoff solenoid valve. With both DGs unavailable, the required safety function was not maintained. At time 1645, DG1 was restored to an available status by repairing the diesel fuel oil day lank high level shut off solenoid. At this time DG1 is able to perform the safety function. DG1 was declared operable at 2129." While recovering the DG2 from planned maintenance, the operators were refilling the DG2 day tank and noticed the level increasing in the DG1 day tank. The operators determined that a mechanical failure of the float occurred in the DG1 solenoid valve. The valve should have remained shut to preclude overfilling the tank. The safety function of the valve occurs on a loss of power. On a loss of power, the solenoid valve fails open to allow the tank to be filled. The NRC Senior Resident Inspector has been notified. * * * UPDATE FROM E. McCUTCHEN TO J. KNOKE AT 1743 ON 09/12/07 * * * "This update is being made to correct certain technical inaccuracies in the initial Event Notification [43634] and in the additional information reflected on the NRC website. The corrected initial Event Notification is as follows. "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of SSCs that are needed to mitigate the consequences of an accident. "Diesel generator #2 (DG2) was inoperable and unavailable due to planned maintenance. This was day 2 of a 7 day shutdown LCO. While recovering DG2 from planned maintenance, operators were refilling the DG2 fuel oil (FO) day tank and noticed that level was also increasing in [Diesel generator #1] DG1 FO day tank. The operators determined that the DG1 day tank float valve and FO day tank high level shutoff solenoid valve were both shut as designed, but were leaking by. At 1449, Operators declared DG1 inoperable but available due to leak-by of the FO day tank high level shutoff solenoid valve. At 1509, DG1 was declared unavailable due to operators positioning its Maintenance Lock-Out (MLO) switch to OFF (lock out) for work on the valves. With both DGs unavailable, the required safety function was not maintained. CNS [Cooper Nuclear Station] replaced the FO day tank high level shut off solenoid valve and at 1645, restored DG1 to an available status by repositioning the MLO switch to ON. Subsequently the replacement shutoff solenoid valve was also found to leak by. CNS realigned DG FO transfer systems and declared DG1 operable at 2129." The licensee notified the NRC Resident Inspector. Notified R4DO (Shannon) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-09-12
43633 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2007-09-11 14:39 | 2007-09-11 20:33 | 2007-10-30 | AUXILIARY BUILDING SPECIAL VENTILATION AND SHIELD BUILDING VENTILATION SYSTEMS INOPERABLE "At 1439 the Control Room received a Condition Report that identified an unanalyzed condition associated with the Auxiliary Building Special Ventilation and Shield Building Ventilation Systems which resulted in declaring this equipment inoperable. The issue was recirculation flow from Auxiliary Building Special Ventilation back to the Auxiliary Building added additional area heat gain resulting in exceeding the design capacity for the area fan coil units. Technical Specification LCO was entered per TS 3.6.c requiring a reactor shutdown within 12 hours. At 1654 Engineering provided information that if the control switch for Auxiliary Building Special Ventilation Train A was maintained in the off position, the area heat load was within the capacity of area fan coil units. This was completed and both trains of Shield Building Ventilation and Auxiliary Building Special Ventilation Train B was returned to operable. Technical Specification requirements to shutdown were exited. The plant remains in a 7 day Action Statement per TS 3.6.c with Auxiliary Building Special Ventilation Train A inoperable. "This event is reportable under 10CFR50.72(b)(3)(v)(C), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.' " The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY TIM BUNKELMAN TO JASON KOZAL AT 1657 ON 10/30/07 * * * "On September 11, 2007 Kewaunee Power Station reported an unanalyzed condition associated with the Auxiliary Building Special Ventilation and Shield Building Ventilation Systems, which resulted in declaring the equipment inoperable. The issue involved recirculation flow from the Auxiliary Building Special Ventilation System back into the Auxiliary Building causing additional area heat gain resulting in exceeding the design capacity for the area fan coil units. "A subsequent engineering review concluded that required equipment in the Auxiliary Building Fan Floor area would have remained functional during a design basis accident provided service water temperature does not exceed 78.14 degrees Fahrenheit. A review of service water temperatures over the past three years did not identify any occurrences exceeding this value. Therefore, the safety function of the systems would have been met. Based on the analysis performed, Event Notification EN# 43633 is hereby retracted. "The Auxiliary Building Special Ventilation and Shield Building Ventilation Systems remain in a non-conforming condition because the maximum service water design temperature is 80 degrees Fahrenheit. Service water temperature is being administratively limited to 71 degrees Fahrenheit pending final corrective action. "The licensee has notified the Point Beach NRC Senior Resident Inspector." Notified R3DO (Madera). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2007-09-11
43632 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-09-11 15:11 | 2007-09-11 18:24 | 2007-09-12 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE RETURNED TO OWNER On 9/7/07, Component Sales Company of Houston, Texas purchased a moisture density gauge for $400.00 from [DELETED], who stated that he got the gauge at a garage sale. The Component Sales Co. representative investigated the serial number of the gauge and notified the owner of the gauge. The owner, Tolunay-Wong Engineers of Houston, Texas recovered the gauge a CPN model serial number MD80204152 with 10 millicuries of Cs-137 and 50 millicuries of Am-241/Be. The Tolunay-Wong Company representative stated that the gauge had been used the day before but did not know it was missing. The company is trying to determine if the source rod had been properly locked in place. The state believes that [DELETED] may be a minor. The State has not notified law enforcement, and is unsure whether law enforcement will be involved at all "since the gauge has been recovered." The state is investigating this matter. Texas Incident Number - I-8442 * * *UPDATE PROVIDED BY TUCKER TO KOZAL ON 9/12/07 AT 1645 * * * The State provided the following update via email: "The RSO informed the Agency on September 12, 2007, that the technician who inspected the gauge after its return confirmed that the source rod was locked in the stored position." R4DO (Shannon), FSME EO (Bubar) and ILTAB (via e-mail) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-09-14
43630 | 0 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2007-09-10 11:20 | 2007-09-11 16:03 | 2007-09-13 | MEDICAL EVENT - PATIENT RECEIVED AN UNDERDOSE OF YTTRIUM-90 On Monday 9/10/07, the licensee was administering a 66 millicurie dose of Yttrium-90 microspheres to a patient for the treatment of liver cancer through a catheter. The patient only received a dose of 47 millicuries, a 27% underdose. The licensee is investigating the cause of the misadministration, but they believe the catheter used for the administration of the isotope failed or is leaking. The licensee believes there is no permanent functional damage to the patient. The physicians have been informed by the RSO that they need to notify the patient of the underdose and report that notification to the RSO. The treatment device is from MDS Nordion and a MDS Nordion company representative was on site during the administration of the isotope. The licensee intends to use the MDS Nordion representative for technical assistance in troubleshooting this problem once background radiation levels permit a closer inspection of the catheter. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE PROVIDED BY CINDY FLANNERY (FSME) TO JASON KOZAL ON 9/13/07 AT 1352 * * * This event (EN43630) has been reviewed and determined to be a reportable medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-09-13
43629 | 0 | INDIANA STATE DEPT OF TRANSPORATION |  |  |  |  | 2007-09-10 08:30 | 2007-09-11 10:53 | 2007-09-11 | STOLEN TROXLER GAUGE On the morning of 09/10/07 the licensee [DELETED] was getting ready to calibrate a Troxler Moisture Density Gauge (Model 3440). The gauge (s/n 22678) was in the back of the company truck on the calibration block. The employee left the truck for 3-5 minutes to use the restroom and when he returned the gauge was gone. The sources in the Troxler gauge are Am-241/Be (40 mCi), and Cs-137 (8 mCi). The employee contacted his supervisor, who in turn contacted the State police (Report # 52-44047). Within 90 minutes the gauge was found in a vacant lot about a mile from the job site. The gauge was checked and found undamaged with the sources in the safe position. No one saw who might have taken the gauge from the truck. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-09-11
43628 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2007-09-10 03:00 | 2007-09-10 15:53 | 2007-09-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via email: "On Monday, September 10, 2007, the Minnesota Department of Health (MDH) was notified by American Engineering and Testing that a fire had destroyed a Troxler Model 3430 moisture density gauge. The fire occurred at a private residence, which was a farm, and spread to a pick-up truck that was parked beside the garage to that residence. The fire melted the plastic components of the gauge but did not effect the Cesium-137 source in the source rod or the Americium-241:Beryllium source that was in the lead shielding. Members of the Fire Department who responded to the fire were instructed to maintain a safe distance from the truck to avoid minimize radiation exposures. "MDH completed radiation and contamination surveys of both sources. No contamination was detected and the radiation levels were as would be expected with the shielding intact. The sources were placed in containers filled with sand to provide shielding and removed to a secure permanent storage location. The RSO and the Corporate RSO will complete leak tests and arrange for the appropriate containers for shipment to the manufacturer. "The gauge was a Troxler Model 3430, Serial Number 23279, which contained approximately 9 millicuries of Cesium-137 (Serial Number 75-5294) and 44 millicuries of Americium-241:Be (Serial Number 47-19161)." Minnesota Report number: MN07005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2007-09-13
43627 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2007-09-08 12:28 | 2007-09-10 14:51 | 2007-09-10 | REACTOR PRESSURE BOUNDARY LEAKAGE "On September 7, 2007, a small amount of water was discovered in the environmental qualification boundary of the 3B RCS Tcold thermowell (TE-3-420) during inspection of the thermowell. Subsequent mass spectroscopy analysis conducted at 1228, on September 8, 2007, indicated small levels of lithium, boron, strontium, and bromine indicating that the source of the water intrusion into the thermowell was likely reactor coolant system (RCS) fluid. "Turkey Point Unit 3 Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.6.2.a permits no reactor coolant system pressure boundary leakage. As a result of the chemical analysis and indication of fluid in the thermowell, this condition is being reported to the NRC pursuant to the requirements of 10 CFR 50.72(b)(3)(ii)(A) as a degraded condition. An investigation of the source of the water intrusion into the thermowell is ongoing. Leakage into the TE-3-420 was previously noted during the last refueling outage for Unit 3 in March 2006 and a Short Notice Outage (SNO) conducted in June 2007. Previous inspections and sampling did not indicate the presence of boron or activity levels that were consistent with RCS water. "At the time of discovery, Turkey Point Unit 3 was in Operational Mode 6 (Refueling). Turkey Point Unit 3 is presently defueled. "This is a late prompt notification. The NRC Resident inspector will be notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-09-10
43626 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-08-31 | 2007-09-10 12:46 | 2007-09-10 | AGREEMENT STATE REPORT - AM-241 SOURCES LOST DURING SHIPMENT The State provided the following information via facsimile: "Licensee received routine shipment of Am-241 button sources from supplier in China - Shenzhen CIC in Shenzhen, China on August 15, 2007. Shipment was sent via China Air from China to New York, and then transported by air to Boston. In Boston, it is then trucked via Ground Control and arrived at the licensees facility in Burlington, MA. The licensee estimates the package was sent from China sometime after July 25, 2007. "The excepted package (UN2911) was damaged when it arrived at the licensees' facility. At this time the licensee confirmed there was no contamination nor high radiation levels from the package. This package is normally not opened as it is forwarded to a customer for use in smoke detectors. On August 31, 2007, before forwarding the package, the licensee opened the package to verify its contents. The licensee discovered that 2 vials from the package were missing. "Each plastic vial contains 500 Am-241 button sources, each 0.8 microCi nominal activity, for a total of 0.4 milliCi total in each vial. "The licensee immediately notified their transport broker and their agent in China." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-09-13
43625 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-09-09 08:30 | 2007-09-09 11:02 | 2007-09-09 | PRESS RELEASE DUE TO LINN COUNTY INADVERTENT EMERGENCY SIREN ACTIVATION "A press release is being made by Linn County stating that an unknown number of Emergency Notification sirens inadvertently activated in the Cedar Rapids area. The cause for the sirens being inadvertently activated is being investigated by utility employees." These sirens are used for warning the public during severe weather, an emergency at the Duane Arnold Energy Center, or other type of community emergencies. The sirens were not activated by any of the normal control locations in Linn and Benton counties. The sirens were activated for an unknown amount of time and have been secured. Licensee has been in communication with local emergency planning organizations. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-09
43624 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-09-08 12:02 | 2007-09-08 13:29 | 2007-09-08 | PROMPT NOTIFICATION SYSTEM NOT AVAILABLE The licensee was informed by the Jacksonville, FL National Weather Service that the NOAA Prompt Notification System was not operational. Plant Hatch utilizes the NOAA system to broadcast prompt emergency notifications. Hatch will use radio and phone notifications as a backup (if needed) until the NOAA system is restored. No information was available on the cause of the NOAA system outage or when it would be returned to service. The license has notified the Georgia Emergency Management Agency, the local authorities, and will notify the NRC Resident Inspector. * * * UPDATE FROM GORLEY TO HUFFMAN AT 1817 EDT ON 9/8/07 * * * The prompt notification system was restored at 1745 EDT on 9/8/07. The license has notified the Georgia Emergency Management Agency, the local authorities, and the NRC Resident Inspector. R2DO (Shaeffer) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-09-08
43623 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-09-07 06:55 | 2007-09-07 10:17 | 2007-09-07 | PLANT EMERGENCY SIREN FALSE ACTIVATION "False siren activation near Ellsworth, Wisconsin. Sheriffs deputy turned off siren [locally at the siren]. "0655 The Sheriff called Nelson Communication. "0710 Nelson Communication called Emergency Planning Group. "0720 Emergency Planning Group called Control Room. "0750 Siren is confirmed off. "Pierce County Emergency Manager reported no media contacts were made." The licensee notified the NRC Resident Inspector, state, and local agencies. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-07
43622 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2007-09-06 23:22 | 2007-09-07 00:52 | 2007-09-13 | LEAKAGE FROM REACTOR COOLANT SYSTEM >10 GPM A relief valve (BG 8117) in the letdown system opened and released about 650 - 700 gallons of water from the reactor coolant system into the pressurizer relief tank. The rate of release from the letdown was 119 gpm. It was estimated that the pressurizer level lowered about 2-3%. The letdown system was isolated by closing the letdown orifice block isolation valve. Licensee is investigating the reason for the spurious lifting of the relief valve. Due to leakage from the reactor coolant system, the licensee entered EAL 4R. Plant is stable and operating at full power. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM THOMPSON TO ABRAMOVITZ AT 0120 EDT ON 09/07/07 * * * The licensee stated that the Unusual Event was exited at 0120 EDT. The licensee notified the NRC Resident Inspector. Notified R4DO (Pruett) and NRR EO (Evans) and IRD MOC (Cruz). * * * UPDATE AT 1635 EDT ON 09/13/07 FROM JOHN WEEKLEY TO S. SANDIN * * * The licensee is retracting this report based on the following: "This is a follow-up notification to inform the NRC that Callaway Plant is retracting an Unusual Event declaration reported on 09/07/2007 at 00:52 EDT. EAL 4R was entered and the declaration was made due to leakage from the reactor coolant system. "The basis for EAL 4R indicates that the initiating condition for an Unusual Event would include failure of a relief valve to properly close following reduction of applicable pressure and NOT simply the actuation of the relief valve as designed. "Based on troubleshooting efforts and upon review of the event, it has been determined that relief valve BG8117 functioned as designed to reduce pressure and therefore the declaration of the Unusual Event was not required. The relief valve did sense an over-pressurization and did perform its intended function. The relief valve reseated when the letdown line was isolated. Based on this, the Unusual Event declaration is retracted." The licensee informed the NRC Resident Inspector. Notified R4DO (Cain), EO (MJ Ross) and IRD (Blount). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | MO | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-09-07
43621 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-09-06 14:00 | 2007-09-06 22:29 | 2007-09-07 | AGREEMENT STATE- NORTH CAROLINA - UNAUTHORIZED REMOVAL OF PORTABLE NUCLEAR GAUGE The licensee provided the following information via email: "N.C. Radiation Protection Section was notified on 06 Sept. 2007 at 6:15 p.m. by the NC Emergency Operations EOC Warning Point of a call from the RSO for Bunnell-Lammons Engineering, Inc. (NC Radioactive Material License #011-1252-1). The RSO reported a missing employee in a white '02-'04 Chevy Silverado truck with 'BLE' logo on the doors. Secured in the truck's bed was one Model 3450 portable moisture density gauge (Serial No. 922). The gauge contained two sealed sources: (1) Cesium-137, approx.9 millicuries, and (2) Americium-241:Beryllium, approx. 44 millicuries. "The BLE employee was caught sleeping at the job site (Biltmore Town Square in Asheville, NC) at around 2:00 p.m. on 06 Sept. 2007. When the supervisor returned to the site at 4:00pm the same day to check on the employee, the employee, truck, and gauge were missing. "After RPS discussed the situation with the licensee, BLE contacted local law enforcement reporting a larceny of the truck and the radioactive material. A description of the employee and truck was given. "The Radiation Protection Section is monitoring the event and will continue to update NRC and other contacts as appropriate. "N.C. Radiation Protection has not received any media attention as of this report. No press release has been issued." * * * UPDATE ON 9/7/2007 AT 07:46 FROM LEE COX TO MARK ABRAMOVITZ * * * The State provided the following information via email: "I [Lee Cox] received a call at 07:35 from BLE RSO [DELETED] that at 07:25 this morning the employee showed up at the job site like nothing ever happened. The gauge was taken in possession by company representatives at that time in which they indicated it was still secured in the locked case with the source handle lock still in place. The RSO indicated that the gauge would be taken out of use so that a leak test of the sources could be conducted and would not be put back into operation until the results are known. The company will contact all local law enforcement of the situation and will continue to investigate this incident. Disciplinary action of the employee (most likely resulting in termination) will occur swiftly this morning." Notified the R1DO (Jackson), FSME (Zelac) and ILTAB (Sandler). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-09-11
43620 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-09-06 08:30 | 2007-09-06 19:38 | 2007-09-06 | AGREEMENT STATE REPORT - CALIFORNIA - STRONTIUM 90 SOURCE OF UNKNOWN ORIGIN FOUND The licensee provided the following information via email: "On September 6, 2007 at approximately 8:30 a.m., [REDACTED] the Brea Olinda Landfill notified RHB-Brea that a radiation alarm had been set off from a transfer truck carrying a load of waste from Taormina (CVT). The maximum reading at the surface of the truck was 0.29 mr/hr. A DOT exemption (CA-CA-07-32) was issued and the truck was allowed to return to Taormina. At approximately 1:55 p.m. an RHB inspector arrived to survey and identify the waste. The item recovered appeared to be a Sr-90 eye applicator. The dose rate was approximately 100 mr/hr at approximately 1 foot from the open source and approximately 10 mr/hr at 1 foot behind the plexiglass shield that comprised part of the handle, with a background of 13 microR/hr. The source was collected by RHB, and is in safe storage, pending an investigation as to its origin. RHB intends to work with a local manufacturer and distributor to quantify the source and determine the model and serial number. The source did not appear to be compromised. "Since a typical Sr-90 source is between 30 milliCuries and 100 milliCuries, and the criteria for an abnormal occurrence for a Sr-90 source is 81 milliCuries, we are unable to determine if this incident is an abnormal occurrence at this time. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-09-11
43619 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2007-09-06 16:05 | 2007-09-06 18:53 | 2007-09-07 | EOF DECLARED NON-OPERATIONAL "On 9/06/2007 a leak in the water supply to the Emergency Operations Facility (EOF) at Grand Gulf Nuclear Station progressed to the point that the facility is not operational. The duration of the water outage is currently unknown. Plant emergency response personnel, state, and local agencies are being informed to use the EOF backup facility." The licensee has notified State and local authorities and the NRC Resident Inspector. * * * UPDATE FROM HOLCOMBE TO HUFFMAN AT 1726 EDT ON 9/7/07 * * * The water supply to the EOF has been repaired and normal water service has been restored. The licensee declared the EOF operable at 1515 CDT on 9/7/07. R4DO (Pruett) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-09-06
43618 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-09-04 06:23 | 2007-09-06 18:06 | 2007-09-06 | AGREEMENT STATE REPORT - CALIFORNIA - THEFT OF TWO THERMO-NITON ANALYZERS The State provided the following information via email: "Two XRF Analyzers possessed under a general license by Engineering Remediation Resources Group (ERRG) were stolen from the cab of a truck parked overnight in San Francisco, California at Grove and Masonic. The serial numbers of the stolen Analyzers are 7497 and 7706. These devices contain 40 mCi of Cadmium-109 each. The police and the company from which the Analyzers were rented, Thermo-Niton in Boston, MA, have been notified. The cases for the Analyzers were found broken open about a block away from the location of the parked truck. All the equipment for the Analyzers was missing as well. The employees of ERRG, a soil gauge licensee (RML# 6739-07), have been retrained on maintaining the security of radioactive material in their possession. ERRG has agreed to offer a reward for the return of the Analyzers in a local newspaper. A 30 day reporting requirement was chosen because of the low exposure rate of Cadmium-109 and the unlikely possibility of opening the devices to get at the radioactive material. The energy of the X-Rays from Cadmium-109 are 22.1 Kev, 24.9 Kev and 88.0 Kev." CA State Report No.: 090407 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-09-11
43617 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2007-09-06 13:12 | 2007-09-06 17:34 | 2007-09-06 | LOSS OF COMMUNICATION TO HARNETT COUNTY DUE TO DAMAGED PHONE LINES "At 1312 EDT, the Harris Nuclear Plant (HNP) discovered that the Harnett County Warning Point could not be contacted while doing weekly communications drill in the Main Control Room. At 1345 Harnett County Warning Point was contacted using the Bell South phone line and Harnett County stated that the phone lines had been damaged and the Harnett County Warning Point could not receive or transmit communications from approximately 1100 to 1340 hours. HNP verified that communications are presently available for the State of North Carolina and all four counties within the 10-mile emergency planning zone. Only the Selective Signaling System to Harnett County remains inoperable and under investigation for repair. This requires an 8-hour non-emergency notification per 10CFR50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. The NRC Resident Inspector was informed." The licensee has a compensatory measure of communication via an alternate phone line to Harnett County. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-09-06
43616 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-09-05 11:15 | 2007-09-06 11:08 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * DEGRADATION OF ITEM RELIED ON FOR SAFETY "I. EVENT DESCRIPTION On August 22, 2007, in accordance with operational procedures, a pre-filter was removed from the saw enclosure ventilation in the [DELETED]. The filter was constructed with a paper core and metal housing, approximately [DELETED] high with a [DELETED] diameter. The calculated volume approached 23 liters. The weight gain measured on the filter at the time of removal was about [DELETED] grams. "Nuclear Criticality Safety (NCS) was notified because the weight gain was more than expected. Net weight difference is often used as a conservative U-235 mass until acceptable accountability measurements are completed. Preliminary ESP-2 counting showed the filter was less than the standard for containers of this size. An RWP was approved to transport the filter to drum count in order to perform NDA counting. NMC [Nuclear Materials Control] subsequently provided a U-235 value of approximately [DELETED] grams based on the greater of two counts. "II. EVALUATION OF THE EVENT It was determined that the existing NCS analysis for fuel accumulation in glove box pre-filters defined a limit of [DELETED] in a glove box pre-filter with the requirement that filters be changed out at a documented frequency determined by specific operations performed in the glove box. There was an operational requirement to check the enclosure manometer to determine if the exhaust filters need to be changed, no minimum change frequency had been specified. It is unlikely that a large fuel quantity could collect on this filter - the saw cuts only a few grams from each element, most of the cut material is zirconium, and much of the fines are collected in the coolant which is changed whenever throughput approaches [DELETED]. It is probable that the filter would clog, as indicated by the manometer check, before accumulation approached the limit. "On September 5, 2007, it was determined the requirement of the NCS analysis to implement a minimum change frequency for the saw enclosure filter had not been completed nor the ISA [Integrated Safety Analysis] been updated. Although there was no immediate safety concern and controls were in place, IROFS [Items Relied On For Safety] had not been fully implemented. The operation of the saw was suspended on 9/5/07 at 11:15 am until the procedures and ISA are revised to include the IROFS. "III. NOTIFICATION REQUIREMENTS BWXT is making this 24 hour report in accordance with 10 CFR 70.61, Appendix A, (b)(2) - Loss or degradation of IROFS that results in the failure to meet the performance requirements of 70.61. "IV. STATUS OF CORRECTIVE ACTIONS The operation has been suspended pending further investigation." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
43615 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2007-09-06 00:30 | 2007-09-06 02:00 | 2007-09-06 | OIL SPILL AT KEOWEE HYDRO STATION "Reportable oil spill (Teresstic 68, approximately 1 gallon) into the discharge of Keowee Hydro Station tailrace (Keowee River). Source of the release was the Keowee Hydro Station sump. The release is NOT continuing. Operation of units 1, 2, and 3 are unaffected. "At request of HAZMAT teams for safety during investigation and recovery of oil, commercial operation of Keowee Hydro units is restricted. Emergency operation of Keowee Hydro Units is unaffected. "HAZMAT teams have placed oil absorbent boom across Keowee Hydro tailrace (Keowee River) to contain/collect oil." The licensee contacted the Coast Guard via the National Response Center (event #847958), the State Emergency Response Committee, Oconee County Center, and Pickens County Center. The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-06
43614 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-09-05 11:17 | 2007-09-05 12:46 | 2007-10-10 | MODIFICATION TO PROCESS COMPUTER THAT IMPACT ERDS AND SPDS "The Plant Process Computer System (Emergency Response and Data Acquisition System, 'ERDADS') will be taken out of service for an approximate 4 week period (on Unit 3) to implement a planned modification. The current ERDADS is being replaced on Unit 3 and a computer outage is required for the installation of the new ERDADS. During this time period ERDS and SPDS functions will not be available for Unit 3. Unit 4 will function normally after a modification (expected duration 6 hours) to the existing computer operating system software is implemented. Also, Unit 3 Regulatory Guide 1.97 category 2D containment temperature and power system indicators for motor control centers, batteries, and inverters will not be available in the Control Room, although other instrumentation is available to monitor these parameters. "This is an 8-hour reportable event per 10 CFR 50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of plant systems will not be affected due to this planned action. ERDS and SPDS parameters will be monitored by control board indications. Compensatory actions have been developed. "Follow up notification to NRC will be given once Unit 4 ERDS and SPDS are returned to service." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY JIM SPEICHER TO JEFF ROTTON AT 1031 EDT ON 09/10/07 * * * "The Plant Process Computer System (Emergency Response and Data Acquisition System, 'ERDADS') was taken out of service on both Unit 3 and Unit 4 in order to implement a planned modification on Unit 3. The current ERDADS system is being replaced on Unit 3 during the current Unit 3 refueling outage. In order to perform this replacement, ERDS and SPDS functions had to be temporarily removed from Unit 4. "ERDADS and SPDS functions have been returned to service on Unit 4 and have been verified to operate correctly. The ERDS link for Unit 4 was satisfactorily tested on 9/7/07. "The ERDADS replacement on Unit 3 will continue with an estimated completion on September 24, 2007." The licensee notified the NRC Resident Inspector. Notified R2DO (S. Shaeffer) * * * UPDATE FROM NIELSEN TO HUFFMAN AT 1642 EDT ON 10/10/07 * * * "The Plant Process Computer System (Emergency Response and Data Acquisition System. 'ERDADS') was taken out of service in order to implement a planned modification on Unit 3. Replacement of the ERDADS system on Unit 3 is complete. The ERDS link for Unit 3 was satisfactorily tested on 10/10/07." The licensee notified the NRC Resident Inspector. Notified R2DO (Desai). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-09-05
43613 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-09-03 02:14 | 2007-09-03 05:05 | 2007-09-05 | MANUAL REACTOR SCRAM DUE TO ELECTRO-HYDRAULIC CONTROL (EHC) SYSTEM LEAK "At 0214 [CDT] on 09/03/2007 with Unit 1 at 100% power a core flow runback and manual reactor scram were initiated due to a Electro-Hydraulic Control (EHC) System leak. Units 2 and 3 were also at 100% power and were unaffected by the event. As expected reactor water level momentarily lowered below +2 inches (Reactor Low Water Level) and all appropriate PCIS [Primary Containment Isolation System] isolations, Group 2 (RHR Shutdown Cooling). Group 3 (RWCU), Group 6 (Ventilation), and Group 8 (TIP) were received along with the auto start of CREVs [Control Room Emergency Ventilation] and 3 SBGT trains. "This event is reportable as a 4-hour and 8-hour non-emergency notification along with a 60-day written report in accordance with 10 CFR 50.72(b)(2)(iv)(B), 10 CFR 50 72(b)(3)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(A) as 'any event or condition that results in valid actuation of RPS or PCIS.' "All control rods fully inserted, the electrical grid is stable, the EDGs and ESF systems remain available, and decay heat is being removed via the Turbine Bypass Valves and reactor water level is being controlled by the Reactor Feedwater System. The licensee notified the NRC Resident Inspector. "Investigation into the cause of the leak is ongoing." * * * UPDATE FROM DON SMITH TO HUFFMAN AT 1357 EDT ON 9/05/07 * * * "The Unit 2 Refuel Zone Inboard Exhaust Damper, 2-FCO-64-10, failed to indicate closed in the Control Room at Panel 2-9-25 in response to the Group 6 isolation signal received during the Unit 1 Reactor SCRAM on 09/03/2007 at 0214 CDT as required by the plant design. The damper was physically verified to be open. The Unit 2 Refuel Zone Outboard Exhaust Damper, 2-FCO-64-09 automatically isolated as designed in response to the Group 6 isolation signal fulfilling its Safety Function, was verified closed and was later tagged closed as required by Technical Specifications. Investigation into the cause of the failure of the 2-FCO-64-10 is ongoing." The licensee notified the NRC Resident Inspector. R2DO ( Ernstes) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-09-03
43612 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-09-01 16:58 | 2007-09-01 20:22 | 2007-09-01 | OFFSITE NOTIFICATION RELATED TO FATALITY "The purpose of this report is to notify the NRC of a fatality involving a contract worker at the South Texas Project. Specifically, at 15:35 (CST), the South Texas Project Unit 1 Control Room was notified that an individual located outside of the protected area but in the owner controlled area had loss consciousness. The site emergency medical team responded and an ambulance was requested at 15:39. At 16:58 the South Texas project was notified that the individual was pronounced dead upon arrival at Matagorda General Hospital. The South Texas Project will be notifying OSHA of the fatality. A press release is not planned at this time, but is under consideration." The resident NRC inspector has been notified | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-09-01
43611 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2007-08-31 07:03 | 2007-08-31 11:05 | 2007-08-31 | LOSS OF EMERGENCY RESPONSE CAPABILITY - TSC SUPPORT CENTER (TSC) DUE TO PLANNED ELECTRICAL MAINTENANCE "This report is being made pursuant to 10CFR50.72(b)(3)(xiii), 8-hour Non-Emergency Report due to the loss of emergency assessment capability. The normal AC power supply and backup diesel generator were taken out of service for planned load center cleaning maintenance activities and the Technical Support Center (TSC) was declared non functional at 0703 Central Daylight Time on 8/31/2007. The maintenance activities are expected to last approximately 16 hours. Affected Emergency Response Organization members have been, instructed to report to designated backup facilities, per procedure EIP-ZZ-00240, in the event of an emergency. "Though this does not affect state or local response capabilities, the SEMA Senior Radiological Emergency Program Planner and local personnel have been notified of this planned maintenance outage as a courtesy. "The licensee has notified the NRC Resident Inspector." * * * UPDATE ON 08/31/07 AT 1730 EDT BY STEVE KOCHERT TO MACKINNON * * * "The normal AC power supply and backup diesel generator were restored to service and the TSC was declared functional at 1627 CDT on 8/31/2007. Affected Emergency Response Organization members have been instructed to resume normal use of the TSC in the event of a emergency. "The licensee has notified the NRC Resident Inspector." R4DO (Troy Pruett) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-31
43610 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2007-08-30 15:13 | 2007-08-30 17:16 | 2007-08-30 | AUTOMATIC REACTOR SCRAM ON TURBINE STOP VALVE CLOSURE Event Description: "Reactor scram (4 hr notification) automatic scram "Primary containment isolation of Groups 2,3,4, and 5 due to RPV Level < low level setpoint (<127") due to reactor scram. (8 hr notification). Actions Taken (reference applicable Technical Specifications): "Implemented OT 3100 (Reactor Scram Procedure) EOP-1 (RPV Control). Placed the plant in a stable condition and implemented OP 0109, Plant Restoration. " The NRC Resident Inspector was notified of this event by the licensee. Reactor was initially at approximately 63% power due to cooling tower damage which occurred more than a week ago. License was performing a surveillance test of the # 2 turbine stop valve. The valve was shut per the surveillance test procedure but they were unable to open the valve. Personnel were in the heater bay and mechanical assistance was applied to open the valve. The valve opened quickly at which point the licensee received a turbine stop valve closure signal which generated an automatic reactor scram. All rods fully inserted into the core. Reactor vessel water level decreased below 127 inches, due to the reactor scram, which caused primary containment isolation of groups 2,3,4 and 5. Reactor vessel water began to increase because Reactor feedwater pumps "A" & "B" were still operating. Reactor feedwater pump "B" was secured. When reactor vessel water increased to 173 inches, high level alarm, reactor feedwater pump "A" automatically tripped. Highest reactor vessel water level increased to was approximately 179 inches. No SRV's opened. All Emergency Core Cooling Systems, EDGs are fully operable if needed and the electrical grid is stable. Reactor vessel water level is being maintained using a reactor feedwater pump. Only other anomaly was that for some unknown reason automatic pressure control went to mechanical pressure control during the transient. Licensee is investigating the event. | 0 | 0 | 0 | 62 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-08-30
43609 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-08-13 | 2007-08-30 11:22 | 2007-08-30 | AGREEMENT STATE REPORT - LOST GAS CHROMATOGRAPH The licensee provided the following information via facsimile: "A portable gas chromatograph with a 15 mCi source of Ni-63 was lost during Hurricane Katrina when the levees broke. This is a General License device. LDEQ was not notified of this loss until August 13, 2007." LA Event Report - LA070025 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-09-04
43608 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2007-08-30 | 2007-08-30 11:08 | 2007-08-30 | POTENTIAL FITNESS FOR DUTY SAMPLE COLLECTION ERROR The licensee is conservatively making this report although no specific FFD impacts are indicated. A non-licensed employee responsible for FFD sample collection did not meet station reliability expectations and his access to the site has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2007-08-30
43607 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-08-30 08:58 | 2007-08-30 09:18 | 2007-08-31 | PLANNED ELECTRICAL MAINTENANCE REMOVES TSC HVAC FROM SERVICE "Planned preventive maintenance activities are being performed today (August 30, 2007) on the Hatch Nuclear Plant's Normal Supply Breaker (1C) to the Diesel Generator Building Motor Control Center (MCC) (MPL # 1R24-S026). This MCC feeds the Technical Support Center (TSC) 480V AC distribution panel (MPL# 1R25-S102) which supplies power to the TSC HVAC. The work activities affecting the TSC are planned to be performed and completed expeditiously within one work shift (<12 hours). During this work activity the TSC HVAC system will be removed from service. If an emergency condition occurs that requires activation of the Technical Support Center, during the time these work activities are being performed, it will take no more than four hours to return the equipment back to functional status, dependent on the stage of the work activity at the time the emergency occurs. Plans are to utilize the TSC for any declared emergency during the time these work activities are being performed as long as radiological conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the evolution." The licensee will notify the NRC Resident Inspector. * * * UPDATE PROVIDED BY FRANK GORLEY TO JEFF ROTTON AT 0923 EDT ON 08/31/07 * * * The planned maintenance was completed successfully and the TSC HVAC system was returned to service at 1748 EDT on 08/30/07. The licensee notified the NRC Resident Inspector. Notified the R2DO (Shaeffer) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-30
43606 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-08-29 | 2007-08-29 13:42 | 2007-09-04 | AGREEMENT STATE REPORT - HIGHER THAN PRESCRIBED DOSE "On 08/29/07 at 10:55 a.m., the agency received a call from [the] RSO for the licensee, reporting a High Dose Remote Afterloader (HDR) misadministration that occurred on 08/22/07. The RSO reports that today, 08/29/07, it was discovered that a patient received one HDR treatment on 08/22/07, with 2500 cGy being delivered instead of the planned dose of 500 cGy per fraction for 5 fractions. The RSO reports that the unit was a Varian VariSource loaded with Ir-192. The RSO will include model & serial numbers for the unit & source in his 15-day report to the agency. "The misadministration was discovered today after an independent physicist's review of the treatment plan. "The RSO stated the patient denies any symptoms and was being seen by the Radiation Oncologist. He stated the patient's family and referring physician were also notified." Texas Incident No.: I-8439 Texas Event Report No.: TX-07-43606 * * * UPDATED INFORMATION ON 08/31/07 VIA EMAIL FROM LATISCHA HANSON TO MACKINNON * * * Telephone call placed to (deleted), Ph.D., L.M.P., RSO for the licensee for updated information from 08/29/07 after the patient was seen by the Radiation Oncologist: "Deleted reports that the patient was seen by the Radiation Oncologist & is being observed in a 'wait & watch' following. (Deleted) reported that the patient's Pulmonologist has taken over & (deleted) stated the Pulmonologist said 'We may have gotten lucky & even cured the guy.' "The patient is still reported as doing well, with no adverse side effects being reported, as stated by (deleted). "(Deleted) stated a CT was performed prior to the planned second treatment on 08/29/07, with no adverse effects viewed on the CT scan. " ***ADDITIONAL NOTE TO ORIGINAL REPORTED INFORMATION*** "Deleted reported on 08/29/07 that this HDR misadministration occurred as a result of the incorrect isodose line being chosen & entered into the treatment planning system. (Deleted) reported that the treatment planning system then normalized the calculations to this incorrect isodose line & the resulting treatment dose was what was delivered on the first treatment day. (Deleted) stated the Oncologist signed & approved this treatment plan & that (deleted) himself, did a second calculation check on the treatment plan. The calculation error was caught by an independent physicist PRIOR to the planned second treatment. "Incident Investigations will continue to update this incident as current information is received. "Incident Investigation personnel plan to conduct an onsite investigation upon receipt and review of the required 15-day report from the licensee." FSME EO (Sandra Wastler) & R4DO (R. Nease) notified. * * *UPDATE ON 09/04/07 FROM LATISCHA HANSON VIA EMAIL TO MACKINNON * * * "On 08/29/07 at 10:55 a.m., the agency received a call from (delete), L.M.P., RSO for the licensee, reporting a High Dose Remote Afterloader (HDR) misadministration that occurred on 08/22/07. The RSO reports that today, 08/29/07, it was discovered that a patient received one HDR treatment on 08/22/07, with 2500 cGy being delivered instead of the planned dose of 500 cGy per fraction for 5 fractions. The RSO reports that the unit was a Varian VariSource loaded with Ir-192. The RSO will include model & serial numbers for the unit & source in his 15-day report to the agency. "The misadministration was discovered today after an independent physicist's review of the treatment plan. "The RSO stated the patient denies any symptoms & was being seen by the Radiation Oncologist. He stated the patient's family & referring physician were also notified." R4DO (Pruett) & FSME (Jack Davis) notified. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-09-04
43605 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-08-28 13:54 | 2007-08-28 15:17 | 2007-08-28 | AUTOMATIC REACTOR TRIP AFTER DIGITAL FEEDWATER SYSTEM FAILURE "At 13:54 on 8/28/07, DC Cook Unit 1 experienced an automatic reactor trip due to low steam generator water level coincident with low feedwater flow on #11 steam generator. The cause was a malfunction of the Main Feedwater Pump Digital Control System, which remains under investigation. This requires a 4-hour report under 10CFR50.72(b)(2)(iv)(B). "Both Motor-Driven Auxiliary Feedwater Pumps automatically started due to the reactor trip. The Turbine-Driven Auxiliary Feedwater Pump (TDAFP) started automatically due to low-low water levels in at least two steam generators, which is expected for a reactor trip from 100% power. The automatic actuation of the reactor protection system and the TDAFP start require an 8-hour report under 10CFR50.72(b)(3)(iv)(A). "All systems functioned as expected after the trip, and no major components were out of service at the time of the trip. This is a non-complicated trip. "The NRC resident has been notified." The reactor tripped at 15% steam generator level and then level went off scale low as expected. All control rods fully inserted. No primary or secondary safeties or relief valves lifted with the exception of a feed heater relief valve. The plant is feeding steam generators with the motor driven auxiliary feed water pumps and dumping decay heat to the main condenser. The plant is in the normal shutdown electrical lineup. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-08-28
43604 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2007-08-27 22:05 | 2007-08-27 22:41 | 2007-10-23 | SAFEGUARDS REPORT The licensee discovered a potential failure, degradation or vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for details. * * * RETRACTION RECEIVED FROM DENNIS BEMIS TO JOE O'HARA AT 1554 ON 10/23/07 * * * This event has been retracted because the licensee determined that there was no potential failure, degradation or vulnerability in a safeguard system. The licensee notified the NRC Resident Inspector. Contact the HOO for further details. Notified R1DO(Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-08-27
43603 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-08-27 16:45 | 2007-08-27 20:45 | 2007-08-27 | GRATING INSIDE CONTAINMENT FOUND UNSECURED "At 1645 hours on 8/27/07 it was determined that a section of grating in the containment pool swell region was not properly restrained. During a postulated large break Loss of Coolant Accident, the grating could become dislodged and subsequently impact the ECCS suction strainer located in the suppression pool below the grating. An engineering review determined that the force of the impact could be larger than the impingement forces that had been previously evaluated. The forces were postulated to impact one of two concentric suction strainers. The resulting damage could cause either Residual Heat Removal B and C loops or High Pressure Core Spray (not both) to be inoperable. This condition was determined to meet the reporting requirements for 10 CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in: (B) The nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' Since one of the strainers was for High Pressure Core Spray, a single train safety system, this event was also determined to meet the reporting criteria for 10 CFR 50.72(b)(3)(v)(D), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of systems needed to (D) mitigate the consequences of an accident.' "Technical Specification 3.5.1, ECCS - Operating, was entered and Required Actions taken within the specified completion time. The grating was subsequently restored to design configuration and the Technical Specification LCO was exited." "Time of restoring grating to design was 1838 8/27/07, exited Tech Spec 3.5.1. Location of grating is in the Containment Building on the 599' elevation near the lower air lock. The section is a 3 X 7 foot piece of grating that is located on the level just above the suppression pool. We still are investigating when the grating hold down plates were removed, potentially removed during our recent recirc motor replacement in July 07. The grating hold down plates were discovered by an Operations Roving Operator during his tour on rounds." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | UNANALYZED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2007-08-27
43602 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-08-27 | 2007-08-27 20:26 | 2007-10-26 | ONE CHANNEL OF LOW MAIN STEAM LINE PRESSURE SIGNAL MISTAKENLY REMOVED FROM SERVICE FOR 33 MINUTES "On 8/27/07 at approximately 12:05, during performance of STP 3.3.6.1-02 step 7.7.2 the jumper was installed on contacts 1 and 2 of relay A71B-K4A PCIS TRIP CHANNEL A1 A MAIN STEAM LINE LO PRESSURE. The jumper should have been installed on contacts 1 and 2 of relay A71B-K4C PCIS TRIP CHANNEL A2 C MAIN STEAM LINE LO PRESSURE. "The incorrectly installed jumper on contacts 1-2 of relay A71B-K4A resulted in the channel A1 not being able to trip on a low main steam line pressure signal of 850 psig (PS1014) thus making the function of PS1014 inoperable. At the same time PS1016 was being tested for channel A2 thus making the function for pressure switch PS1016 inoperable. Per Technical specification 3.3.6.1 'Primary Containment Isolation Instrumentation' function 1b 'Main Steam Line pressure - Low' with both PS1014 and PS1016 inoperable, the tripping capability for channel A for Main steam Line Pressure - Low would be lost. This would be a automatic function with isolation capability not maintained per TS 3.3.6.1 condition B. Required action B.1 requires isolation capability to be restored in 1 hour. The I&C techs entered the AOT time for PS1016 at 11:32 AM and exited the AOT at 12:05 PM. Therefore, the isolation capability was lost for 33 minutes of the 1 hour. "There was no violation of Technical Specification 3.3.6.1 function 1b. "This event is reportable under 10 CFR 50.72(b)(3)(v), 'Any event or condition that alone at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (D) Mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 09:10 ON 10/26/2007 FROM ROBERT MURRELL TO MARK ABRAMOVITZ * * * "An UFSAR review has determined that the Main Steam Line Low Pressure isolation is intended to mitigate a transient event. Specifically, the isolation is a safety feature intended to mitigate the consequences of an EHC Pressure Regulator Failure - Open. This transient is not a Design Basis Accident (DBA). Therefore this event resulted in a loss of a Safety Feature, not a loss of a Safety Function. This event is not reportable under 10CFR50.72(b)(3)(v)(D) because the event did not result in a condition that would have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident." Notified the R3DO (Hills). The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-08-27
43601 | 0 | MICRON TECHNOLOGY INC. |  |  |  |  | 2007-08-27 | 2007-08-27 16:12 | 2007-09-24 | LOST STATIC ELIMINATORS On 7/27/07 when completing an inventory, Micron Technology, discovered that nine (9) static eliminators were missing. The company did a thorough search of areas in and around where these instruments were expected to be installed and looked in their warehouse where removed equipment is typically taken when removed from use but the eliminators were not found. The company is continuing its search. All of the eliminators had Po-210 sources with an activity of about 10 millicuries when purchased. One source was purchased in August of 2003. Four sources were purchased in June of 2005 and four sources were purchased in August of 2005. The company plans on implementing a number of measures to ensure that eliminators are not lost in the future: 1. A cradle to grave tracking system will be implemented along with; 2. implementation of additional training and; 3. procedures for a more structured process from start to finish. * * * UPDATE ON 08/31/07 AT 1201 EDT FROM KEVIN LUNDHAGEN TO MACKINNON * * * 4 of the 9 missing static eliminators have been found and they have been confirmed by their serial numbers. The 4 static eliminators were found inside a purge box. They are being shipped back, today 08/31/07, to the license holder, NRD, which is located in Grand Island, New York. Linda Gersey of NRC Region IV asked Micron Technology to update this event with the above information. Micron Technology is still looking for the other 5 missing static eliminators. FSME EO (S. Wastler) and R4DO (R. Nease) notified. E-mailed to ILTAB. * * * UPDATE ON 09/24/07 AT 1126 EDT FROM KEVIN LUNDHAGEN TO JOE O'HARA * * * The 5 remaining static eliminators have been found. The 4 static eliminators were found inside a purge box. They are being shipped back to the license holder, NRD, which is located in Grand Island, New York. The fifth static eliminator was shipped back to the manufacturer in 2004. FSME EO(M. Burgess) and R4DO(C. Johnson) notified. E-mailed to ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-08-27
43600 | 0 | LOGAN GENERATING PLANT |  |  |  |  | 2007-08-27 | 2007-08-27 15:19 | 2007-08-27 | LOST TRITIUM EXIT SIGN On August 15, 2007 Logan Generating Station personnel noted that a tritium exit sign was missing from its installed location. They did an extensive search of the premises from that time until August 27, 2007 when they concluded that the sign was lost. The search involved looking in the coal crushing area as well as the feeder and conveyor sites. An email was sent to plant employees asking if they knew the whereabouts of the sign. They completed walking searches of the remainder of the Coal Storage Building as well as a search through their trash cans and dumpsters without finding the sign. The sign was last seen present in its expected location during an inventory of tritium exit signs conducted on July 10, 2007. The activity of the sign was originally 15 to 20 curies in the 1993 to 1994 time frame in which it was purchased. The plant will conduct additional training on exit signs during its regular annual training period as well as continuing their monthly and quarterly inspections of installed nuclear devices. The lost sign was additionally reported to the New Jersey Environmental Radiological Group. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-08-27
43599 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-08-27 06:00 | 2007-08-27 06:48 | 2007-08-28 | SHIPMENT FAILED TO ARRIVE ON TIME A shipment failed to arrive on time. The NRC Resident Inspector will be notified. Contact HOO for further details. * * * UPDATE FROM J.R. TRAUTVETTER TO J. MACKINNON AT 0730 ON 08/27/07 * * * Shipment arrived on site at 0720 EDT. R1DO (J. Dwyer), FSME (C. Flannery), IRD (T. Blount ) and ILTAB (L. English) notified. NRC Resident Inspector was notified by the licensee. * * * RETRACTION FROM B. LITKETT TO P. SNYDER AT 2005 ON 08/28/07 * * * While the shipment did not arrive on time, it was enroute to the station in the custody of the driver the entire time in question. Therefore the shipment was never lost and this event is retracted. The licensee notified the NRC Resident Inspector. Notified R1DO (Burritt), FSME (McConnell), IRD (McDermott), and ILTAB (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 74.11(a) |  |  |  | 0 | 2007-08-27
43598 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-08-26 08:35 | 2007-08-26 10:28 | 2007-08-26 | SAFEGUARDS REPORT - POTENTIAL VULNERABILITY TO A SAFEGUARD SYSTEM "Safeguards system degradation related to the monitoring and detection of a PA boundary. Compensatory actions taken. Contact the Headquarters Operations Officer for details." The licensee will notify the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-08-26
43597 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-08-25 10:58 | 2007-08-25 15:14 | 2007-08-25 | AUTOSTART OF ALL EMERGENCY DIESEL GENERATORS DUE TO A GRID DISTURBANCE "A switchyard grid disturbance caused undervoltage relays to start both unit's Emergency Diesel Generators (EDGs). 1A, 1B, 2A, and 2B [EDGs] started which met ESF actuation [conditions]. The [EDGs] did not supply the emergency [buses] due to voltage returning to normal immediately. The grid fault was isolated and the [EDGs] were secured." The EDGs are now available to respond if needed. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-08-25
43596 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2007-08-25 08:25 | 2007-08-25 09:55 | 2007-08-27 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE A representative from the State of Kansas contacted the NRC Operations Center to report a stuck radiography source. The source is stuck at Chanute Manufacturing Shop, 1700 South Washington Street, Chanute, Kansas. The company has a radiography shop and was performing a radiography shot of a drum when the guide tube stand fell approximately 2 feet and kinked the guide tube while retracting the source. The camera is an Amersham Model 880 with less than 100 Curies of Ir-192. The licensee reports the source is "stuck good". A 1 Mr/hr boundary has been established, and the area is secured. The state is unsure how far the source is from its fully retracted storage location. The licensee is attempting to locate a recovery team, and the State of Kansas is requesting assistance in locating a recovery team. At 1110 EDT, the State of Kansas called back to report that the licensee has made arrangements with QSA Global of Boston, MA to come to the site today and recover the source. * * * UPDATE ON 08/27/07 AT 1034 EDT FROM DAVID WHITFILL TO MACKINNON * * * QSA arrived on 08/25/07 and completed recovery operations at 2017 CDT on 08/25/07. Highest dose received by a QSA person during recovery operations was 50 millirems as measured by an ion chamber detector. R4DO (R. Nease) and FSME (C. Flannery) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2007-08-29
43595 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-08-25 07:30 | 2007-08-25 07:41 | 2007-08-25 | ERDS SYSTEM AND PORTIONS OF PLANT COMPUTER OUT OF SERVICE FOR PLANNED MAINTENANCE OUTAGE The licensee will perform a planned power outage on Unit 1 which will take the ERDS system, 25% of the control room annunciators, and portions of the plant computer out of service. Some points on the plant computer will not be able to be monitored during the outage. However, the licensee has compensatory measures in place to monitor those parameters on the control boards. The outage is scheduled from 0730 CDT until 1800 CDT. The licensee will enter Technical Specification LCO 3.1.3.1 and 3.1.3.2. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1905 EDT ON 8/25/07 FROM ROGER SHALLEY TO S. SANDIN * * * The licensee restored ERDS to service at 1805 CDT on 8/25/07 and will inform the NRC Resident Inspector. Notified R4DO (Jeff Clark). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-25
43594 | 0 | PALISADES | 1 |  |  | [1] CE | 2007-08-24 19:57 | 2007-08-25 01:27 | 2007-08-26 | PARTIAL LOSS OF PROCESS COMPUTER PARAMETERS TO ERDS "A portion of the Palisades Plant Process Computer (PPC) including a significant number or Emergency Response Data System (ERDS) trended input became inoperable due to a host computer failure. The cause of the host computer failure is unknown. "Necessary redundant control room parameters exist and are functioning. Palisades is currently in no associated Technical Specification LCOs. "Repair of the host computer will be prudently pursued. NRC notification of repair completion will occur." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2005 ON 8/26/07 FROM MULFORD TO SNYDER * * * The licensee restored the host computer at 1757 on 8/26/07 so it is now providing accurate data. The licensee notified the NRC Resident Inspector. Notified R3DO (Lara). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-25
43593 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2007-08-24 09:47 | 2007-08-24 15:25 | 2007-08-24 | REACTOR TRIP BREAKER UNDERVOLTAGE TRIP FAILURE DURING SURVEILLANCE TESTING "During routine surveillance testing on Unit 1 'B' Train Solid State Protection System, per FNP-1-STP-33.2B, the 'B' Train Rx Trip Breaker Failed to trip when a trip signal was sent from one of the manual function test push buttons. Indicated voltage did go to zero, but the Reactor Trip Breaker did not open. Per the testing sequence, the shunt trip for this breaker was being blocked at this time. A timeout was taken to determine the best course of action. Following discussions with Shift Manager, Duty manager, Emergency Director, and Electrical Maintenance supervision, it was decided to determine if the breaker would trip via the shunt trip mechanism. The surveillance testing was continued, and the 'B' Reactor Trip Breaker opened when the test signal was again inserted with the shunt trip unblocked. The 'B' Reactor Trip Breaker was replaced with a new breaker, and was subsequently tested sat per applicable sections of the surveillance test procedure. "***This event did not result an any offsite radiation release, and did not pose a threat to the general public.***" The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW | [5 empty] | 0 | 2007-08-24
43592 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-08-24 11:30 | 2007-08-24 13:41 | 2007-08-24 | FIRE BARRIER SEPARATION CRITERIA NOT MET FOR AFWP ROOMS "On August. 24, 2007, Prairie Island staff completed a past operability evaluation of a condition involving a missing fire barrier, such that the required degree of separation for redundant safe shutdown trains was lacking. The floor trench which transverses the auxiliary feedwater pump (AFWP) rooms has a 12 inch thick concrete barrier at the interface of Fire Areas 31 and 32 (Unit 1 and Unit 2 AFWP rooms). That barrier is required by NRC commitment to prevent the flow of flammable liquid (i.e., oil) and fire suppression water from transferring fire from one AFWP room to the other. That barrier contains penetrations which shall be controlled like any other fire barrier penetration. "One of those penetrations is a 4 inch pipe sleeve. When stuffed with fire-retardant wool and capped with provided threaded caps, it is a qualified seal. However, for approximately ten years, the 4 inch sleeve has contained a 3 inch hose. During most of this 10 year period there were hourly fire watches in these two fire areas, which were an acceptable compensatory measure. However; for a period between Sept. 19, 2005 and April 9, 2006 there were no hourly fire watches in place. Prairie Island staff concluded the required degree of separation was lacking with no compensatory measures, thus the as-found condition is reportable per 10 CFR 50.72(b)(3)(ii) as an unanalyzed condition that significantly degraded plant safety." This condition was discovered and corrected on 8/10/07. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-08-24
43591 | 0 | GENERAL ELECTRIC CO. |  |  |  | SPENT FUEL STORAGE FACILITY | 2007-08-23 18:50 | 2007-08-23 22:20 | 2007-08-23 | UNUSUAL EVENT DECLARED DUE TO SEVERE WEATHER IN THE AREA Per the site emergency plan, MOI's 202 and 233, at 1850 local time, the licensee declared an Unusual Event due to severe weather including tornado warnings. The licensee sheltered personnel onsite. No damage was sustained at the site. There was no radiological release. No offsite assistance was requested. At 1930 local time the licensee terminated the Unusual Event due to expiration of the tornado warnings. The licensee notified state authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | UNUSUAL EVENT | 3 | IL | FUE | [5 empty] | 0 | 2007-08-23
43590 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-08-23 15:30 | 2007-08-23 20:14 | 2007-08-23 | MANUAL REACTOR TRIP BECAUSE OF LOWERING CONDENSER VACUUM "At 1530 hours on 8/23/07, Braidwood Station Unit 2 was manually tripped due to lowering condenser vacuum. The lowering condenser vacuum resulted from the trip of two circulating water pumps. The cause of the two circulating water pump tripping is under investigation. All control rods inserted and there were no complications during the trip and all systems functions as required. Following the unit trip, the Auxiliary Feedwater System actuated as expected to maintain steam generator level. At the time of the unit trip, the Braidwood Station area was experiencing severe thunderstorms. "Additionally, at 1604 hours, 19 of 70 emergency sirens for the Braidwood Station were declared inoperable due to a loss of power from storms in the area. As of 1704 hours, 19 sirens (greater than 25%) remain inoperable. This event is considered a major loss of offsite response capability and applies to both Braidwood Station Unit 1 and Unit 2. "These events are is being reported under: (1) 10 CFR 50.72(b)(2)(iv)(B) as an event that results in the actuation of the reactor protection system (RPS) when the reactor is critical, (2) 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the PWR auxiliary feedwater system. (3) 10 CFR 50.72(b)(3)(xiii) as a major loss of offsite response capability." All safety buses remained powered by offsite power throughout this event. Emergency diesel generators are available if needed. No steam generator PORV's lifted as a result of the trip. Decay heat is being discharged to the condenser via the steam dumps. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  | Power Operation | Power Operation |  | Power Operation | Hot Standby |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  | 0 | 2007-08-23
43589 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-08-23 13:00 | 2007-08-23 15:54 | 2007-08-23 | OFFSITE NOTIFICATION INVOLVING A 70 GALLON DIESEL SPILL WITHIN 1 MILE OF THE SITE BOUNDARY "On August 23, 2007, at 1300 EDT, the Susquehanna Control Room was notified of a diesel fuel oil spill from a ruptured saddle tank on a tanker truck. The truck was located within 1 mile of the site boundary, on company property, NOT within the plant protected area. Approximately 70 gallons of diesel fuel oil was spilled in the immediate vicinity of the parked truck and did not get into any waterway. The remainder of the fuel oil was pumped from the ruptured tank into a 55 gallon drum. The event did not meet thresholds for reporting to the state of Pennsylvania. However, the contractor (Rizzo Associates) performing the work made a courtesy call to the Department of Environmental Protection with subsequent notifications made to the Susquehanna control room. This 4 hour notification is made per 10CFR50.72(b)(2)(xi) for 'Any event or situation related to the health and safety of the public or onsite personnel, or protection of the environment for which a news release is planned or notification to other government agencies has been or will be made.' The clean-up plan was discussed with the DEP and is currently in progress. This incident had no impact to SSHS or its operating units." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-08-23
43588 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2007-08-22 18:12 | 2007-08-23 15:42 | 2007-08-23 | FITNESS-FOR-DUTY REPORT INVOLVING A CONTRACT EMPLOYEE SUPERVISOR A contract employee supervisor was determined unfit for duty based on site policy regarding alcohol use during a for cause fitness-for-duty test. The employee's unescorted access to the plant has been placed on administrative hold. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2007-08-23
43587 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2007-08-23 13:54 | 2007-08-23 15:20 | 2007-08-23 | RECEIPT INSPECTION SURVEYS INDICATE RAD LEVELS GREATER THAN EXPECTED "A package removed from the transport flatbed had a gamma dose rate of 224 [millirem per hour] on contact which exceeded the 10 CFR 71.47 limit, and is therefore reportable per 10 CFR 20.1906(d)(2). "No issue with personnel exposure or a dose to public since the highest dose rate was found on the bottom of the package which was secured to the flatbed. No other limits were exceeded." The licensee notified the NRC Resident Inspector. | 12 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2007-08-23
43586 | 0 | TESTAMERICA ST. LOUIS |  |  |  |  | 2007-08-20 | 2007-08-23 12:27 | 2007-08-23 | POTENTIAL VIOLATION OF LICENSE INVOLVING AN INADVERTENT DISPOSAL OF RADIOACTIVE MATERIAL On Monday 8/20/07, a package containing a small quantity of natural uranium, was inadvertently discarded and taken to the Bridgeton Landfill. The material was shipped as an Excepted Package - Limited Quantity from General Engineering Laboratory which is located in South Carolina to TestAmerica. The package was received, opened and set aside. On Monday, workers inadvertently disposed of the package as trash. The total activity of the material was .265 microcuries (natural uranium with a specific activity of 34 picocuries/gm). The licensee does not believe that a search of the landfill would locate the material due to the shredding and mulching process and the extremely small quantity involved. An accident investigation is in progress which will identify appropriate corrective actions. The licensee will notify the State of Missouri Department of Natural Resources. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2007-08-23
43585 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2007-08-21 14:40 | 2007-08-21 17:23 | 2007-08-21 | OFFSITE NOTIFICATIONS OF AN OIL SPILL "On 8/21/2007, at approximately 13:30 a St. Lucie County employee spilled approximately one half gallon of unused motor oil into the intake canal while maintaining a mangrove watering pump in the owner controlled area. The county notified FPL Land Utilization Dept which responded to mitigate the spill. Land Utilization determined the spill was reportable at 14:12 and notified the Shift Manager. "Per the plant's Oil and Hazardous Material Response Procedure several outside governmental agencies were notified of this event between 14:40 and 15:20 EDT. The following agencies were notified: National Response Center, Department of Environmental Protection, Florida's State Emergency Response Commission, and the Coast Guard Marine Safety Office. This non-emergency notification is being made pursuant to 10CFR50.72(b)(2)(xi) due to the notification of outside governmental agencies in response to this environmental event." Notified DOE (Anthony), EPA (Snowden), USDA (David Timmons), HHS (Jamie), and FEMA (Irwin). National Response Center Report: #846356 The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-08-21
43584 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2007-08-21 14:15 | 2007-08-21 16:58 | 2007-08-21 | REACTOR SCRAMMED DUE TO REACTOR WATER LEVEL 3 RPS ACTUATION "The 'A' Reactor Feed Pump controller failed downscale causing reactor water level to lower. Feed pump was manually tripped as reactor water level passed through 20 inches (Narrow Range) in an attempt to stabilize level. "Reactor scrammed on Level 3 (11.4") as designed. Mode switch placed in Shutdown. Lowest level observed was -25". All control rods fully inserted. No ECCS initiations were received and all systems responded as designed. "Level 3 is also a Group 3 Shutdown Cooling Isolation setpoint. No valves isolated due to them being in their SOI [system operating instructions] position 'closed' prior to the event." The IC Tech group was working on the Feedwater Pump Controller at the time of the trip and could have possibly caused this situation. However, this has yet to be determined. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-08-21
43583 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2007-08-21 10:30 | 2007-08-21 15:49 | 2007-08-21 | FITNESS FOR DUTY - UNLICENSED SUPERVISOR FAILED RANDOM DRUG TEST An unlicensed supervisor had a confirmed positive random fitness-for-duty test. Unescorted access has been terminated unfavorably, as well as the PADS being updated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2007-08-21
43582 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2007-08-20 21:03 | 2007-08-20 22:06 | 2007-08-21 | INOPERABLE HOUSE SERVICE TRANSFORMERS "This report is made in compliance with Tech spec 2.7, 4 hour NRC notification of inoperable house service transformers. The 161 Kv electrical supply to both house service transformers T1A-3 and T1A-4 was lost at 21:03 EDT. Fast transfer to 22 Kv was successful. AOP-31, 161 Kv Grid Malfunctions, abnormal operating procedure was entered. Technical Specification 2.7 (2) c, 72 hour LCO was entered. "Background: The site was in a tornado warning between 20:30 and 21:00 EDT. Wind speeds were observed in excess of 60 mph by the site weather tower. One of the two switchyard breakers 3451-5 on the 345 Kv system opened at 20:50 EDT. The 345 Kv output breaker 3451-4 remained closed." The EDG are in standby and ready for service if required. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 08/21/07 AT 0400 EDT FROM K. BOSTON TO MACKINNON * * * The 161Kv electrical supply has been returned to service and Tech Spec 2.7(2)c has been exited at 0029 EDT on 08/21/07. Breaker 3451-5 remains open. System walk downs have to be completed before breaker 3451-5 can be closed. R4DO (J. Clark) notified. The NRC Resident Inspector is presently in the control room. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2007-08-20
43581 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-08-20 10:53 | 2007-08-20 14:35 | 2007-08-20 | ELECTRICAL BREAKER B4305 UNABLE TO FUNCTION "During panel walk downs in the Main Control Room, an Operator discovered no light indication for V-AC-4, B RHR ROOM AIR COOLING UNIT. Operator was dispatched to Breaker B4305 and 'B' RHR room to determine cause of loss of indicating light. The Operator determined that breaker B4305 (V-AC-4, 'B' RHR ROOM AIR COOLING UNIT 480V SUPPLY) was unable to function. Division II RHR pumps, Division II CS pump, and associated low pressure injection systems were declared inoperable. Tech Spec Actions 3.5.1.A, 3.5.1.B, and 3.5.1.M were entered resulting in entry into LCO 3.0.3 at 1053 on August 20, 2007. At 1151 on August 20, 2007 power reduction was commenced using normal shutdown procedures. "Site Electricians determined that a line fuse had blown. The fan motor was meggared and all three line fuses were replaced. At 1230 on August 20, 2007, V-AC-4 was tested and returned to service. Division II RHR pumps, Division II CS pump and associated low pressure injection systems were declared operable. LCO 3.0.3 and T.S. Actions 3.5.1.A, 3.5.1.B, and 3.5.1.M were exited. Power reduction was terminated at 98%." At the completion of the call the power level had returned to 100%. The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-08-20
43580 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2007-08-19 17:00 | 2007-08-19 22:19 | 2007-08-19 | PLANT SHUTDOWN DUE TO UNISOLABLE REACTOR COOLANT SYSTEM LEAKAGE "On 08/18/2007 at 16:03 EDT a Planned Manual Reactor Trip was initiated on Unit 2 based on increased unidentified RCS leakage. The RCS leakage had increased over a two day period and surpassed the hard limit of 0.28 gpm established by a plant Operational Decision Making (ODM) plan. The downpower was initiated on 08/18/07 at 10:35 EDT from 100% power and proceeded in a controlled manner to 25% power. The Feedwater Control System was maintained in the automatic mode. Station Power was transferred by procedure from the Auxiliary to the Startup Transformers. The reactor was manually tripped at 16:03 EDT. Following the reactor trip, EOP-1, Standard Post Trip Actions, and EOP-2, Reactor Trip Recovery procedures were completed without contingencies and the unit was stabilized in Mode 3. Decay heat was removed by the Steam Bypass Control System (SBCS) to the condenser. The Steam Generators were fed by the MFW System and levels remained above Auxiliary Feedwater Actuation (AFAS) setpoint. There were no significant equipment failures identified post trip. The plant was cooled down and entered Mode 5 on 8/19/07 at 15:09 EDT. "On 8/19/07 at 17:00 EDT while in Mode 5, a Containment walkdown confirmed the 2B1 RCP Seal injection line to be the only active RCS leakage source. The leak is unisolable from the RCS and is located at or adjacent to a socket weld on the 3/4" Class 1 Schedule 160 seal injection line. Removal of obstructions and insulation must occur before the specific details of the leak can be identified. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(3)(ii)(A). Additional investigation is being perform to determine the detailed configuration of the leak and the root cause." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-08-19
43579 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2007-08-18 19:55 | 2007-08-19 02:23 | 2007-09-14 | EMERGENCY DIESEL GENERATOR WORK PLATFORMS NOT PROPERLY RESTRAINED "On August 18, 2007, at about 1955 PDT, both of SONGS Unit 3 Emergency Diesel Generators (EDG) were found in a condition that was not seismically analyzed. At about 2015 PDT on August 18, 2007, both of SONGS Unit 2 EDGs were found to be in the same unanalyzed condition. The condition involved EDG maintenance work platforms that had not been properly restrained, and, in the position found, could potentially render the EDGs inoperable during a seismic event. "SCE is reporting this occurrence as a potential loss of safety function in accordance with 10CFR50.72(b)(3)(v). "SCE took immediate actions to properly restrain the EDG work platforms, and an evaluation will be conducted to determine the cause of this event. At the time of this occurrence, Unit 2 was operating at about 99% power and Unit 3 was operating at about 100% power. SCE has notified the NRC Senior Resident Inspector about this occurrence and will provide them with a copy of this report." * * * UPDATE AT 1853 EDT ON 09/14/07 FROM SUSAN GARDNER TO S. SANDIN * * * The licensee is retracting this report based on the following: "On August 18, 2007, SCE reported that Emergency Diesel Generator (EDG) work platforms on both Units 2 and 3 had not been properly restrained. This resulted in a condition unanalyzed for seismic events. Consequently, both trains of EDGs on both Units 2 and 3 were declared inoperable. "SCE evaluated configuration of the platforms for vulnerabilities to a design bases event. SCE concluded that the DGs were operable as-found. "Consequently, SCE is retracting the phone report to the NRC (Event Log No. 43579)." The licensee will inform the NRC Resident Inspector. Notified R4DO (Jones). | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2007-08-19
43578 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-08-18 02:10 | 2007-08-18 20:18 | 2007-08-18 | FEED FACILITY AUTOCLAVE O-RING FAILURE "08-18-07 at 0210 in the X-342 , Feed Facility, Autoclave #1, 10 minutes into the heating cycle (mode II) experienced an air leak past the Viton O-ring. The steam was secured and autoclave shell opened 30 minutes later. Inspection of the Viton O-ring resulted in the discovery of a 3/8" separation of splice joint. A pressure decay was performed to determine if the O-ring would have performed its 'Q' function. The test failed resulting in a 24 hr. event." This was reported under 10CFR76.120(c)(2)(i). The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2007-08-18
43577 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-08-17 21:58 | 2007-08-18 00:02 | 2007-08-18 | OFFSITE PUBLIC ALERTING SIRENS INOPERABLE FOR A SHORT TIME DUE TO A LIGHTNING STRIKE "On the evening of 8/17/07 several light(n)ing strikes were noted in the Vogtle Electric Generating Plant area during a rain storm. Information Technology (IT) personnel were dispatched to check for proper operations of IT equipment and found the primary transmitter for the offsite public alerting sirens to be damaged and out of service. IT personnel swapped the offsite public alerting sirens over to a secondary transmitter and verified that they were operable and returned them to service @ 22:01 hrs on 8/17/07. The primary transmitter will be repaired next week. This is reportable under 10CFR50.72(b)(3)(xiii). (8 hour notification)" The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-18
43576 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-08-17 15:00 | 2007-08-17 18:20 | 2007-08-17 | AGREEMENT STATE REPORT - LOST BRACHYTHERAPY SOURCES "At approximately 9:00 AM the Agency was informed by [DELETED] Walter Boswell Memorial Hospital that on 8/14/2007 at approximately 4:30 PM, two seeds of Iodine 125 were discovered missing in the operating room number 10. Originally, 9 seeds were taken to surgery by a nuclear medicine technician to be sterilized. Only 7 seeds were returned from surgery. A search was initiated and the results were negative. Each seed contained 0.34 millicuries of Iodine 125. The Agency dispatched a team to attempt to locate the missing sources. The seeds have not been located. "The Agency and the Hospital continue to look for the sources. "The U.S. NRC and FBI are being notified of this event. "First Notice: 07-011" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-08-22
43575 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2007-08-17 10:53 | 2007-08-17 15:21 | 2007-08-17 | OFFSITE NOTIFICATION PERFORMED DUE TO EXTERNAL ENVIRONMENTAL EVENT "On Friday August 17, 2007 at 10:30 CDT, the Fort Calhoun Nuclear Station Control Room was notified of a 'diesel fuel' type smell and oil sheen on the Missouri River. Further investigation found the source of the oil was from an outside source upstream of Fort Calhoun Station, which is approximately 20 miles north of Omaha, NE. Per station procedures, the Omaha Public Power District (OPPD) Corporate Environmental Affairs was notified of the oil sheen observations. "On Friday, August 17 at 1053 CDT, OPPD Corporate Environmental Affairs contacted the Nebraska Department of Environmental Quality (NDEQ) of the oil sheen observations. Two contacts were made to Release Response Unit and the Compliance Inspectors Office. OPPD Corporate informed the NDEQ that an oil sheen was observed coming down the river past Fort Calhoun Station. The oil sheen smelled of diesel fuel or similar odor. The oil sheen was not coming from Fort Calhoun Station." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-08-17
43574 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2007-08-17 08:00 | 2007-08-17 11:00 | 2007-08-17 | OFFSITE NOTIFICATION TO THE UNITED STATES DEPARTMENT OF TRANSPORTATION "Pursuant to 10 CFR 50.72(b)(2)(xi), Energy Northwest hereby informs the Nuclear Regulatory Commission (NRC) of an intent to report a undeclared shipment of hazardous material to the Department of Transportation (DOT). "Energy Northwest recently discovered that two EntryScan Explosive Detectors, each containing a 10 mCi (millicurie) Nickel-63 source, were transferred to PPL Susquehanna, LLC without designating the shipment as Radioactive Material, Excepted Package, Instruments or Articles, 7, UN2911 and received in Berwick, PA on April 17, 2007. Energy Northwest has confirmed that the devices are under the control of an entity licensed to possess such material. "There were no consequences associated with this incident and the potential for radioactive exposure of any individual as a result of this shipment was negligible." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-08-17
43573 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2007-08-17 09:55 | 2007-08-17 10:35 | 2007-08-17 | WEATHER ALERT SYSTEM WAS INOPERABLE "Received notification from VY E-Plan of an outage of the Ames Hill NOAA transmitter. "Made notifications per AP 0156. E-Plan Duty Officer investigating the cause. "Ames Hill NOAA transmitter restored at 1037. No sirens were affected during the transmitter outage. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-17
43572 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-08-16 13:32 | 2007-08-16 17:26 | 2007-08-16 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2007-08-16
43571 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-08-15 | 2007-08-16 13:01 | 2007-08-16 | AGREEMENT STATE REPORT - Sr-90 SOURCE FOUND "On August 1, 2007, Wisconsin Radiation Protection was notified a general licensed Sr-90 gauging device had been found. The device is a model 3F11, Strontium-90 source, Barber-Coleman Model 015202 source holder. The label indicates a source activity of 100 millicuries in July 1989. The device was found amid manufacturing equipment that had been purchased at an auction in 1999 when a company in Nevada had gone out of business. The equipment had been transported to Wisconsin and stored in an off-site warehouse. The equipment was never used and was in the process of being sorted prior to being sent for salvage. The device was found during this process. The company did not know the device bad been shipped to their location. "The company has contacted a broker to dispose of the device. Wisconsin Radiation Protection is in contact with the broker." Wisconsin Event Report ID: WI070018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-08-21
43570 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2007-08-15 | 2007-08-15 18:06 | 2007-08-30 | AGREEMENT STATE REPORT - INADVERTENT SHIPMENT OF RADIOACTIVE MATERIAL The State provided the following information via email: "DRH received notification on 8-15-07 from the Washington Dept. of Health, about the possibility of two (2) Industrial Dynamic Models FT-12 (Device Serial # 101942/Source # 318) and FT-50 (Device Serial No. 116158/Source # 3109) each containing 100 millicuries of Americium 241, being [inadvertently] delivered to a company in Mississippi. Washington DOH asked MS DRH to assist. DRH sent inspectors to the Canton, Mississippi location and verified that the sources were in both devices. DRH called Washington DOH and reported that the devices were indeed at that location. "DRH called contractor QSA Global for assistance with disposal. QSA will deal directly with company that shipped devices to Mississippi. "DRH confirmed both sources were in [the] devices with survey measurements of 0.7 Mr/hr at [the] surface." Mississippi report number - MS 07003 * * * UPDATE FROM STATE OF MISSISSIPPI (SMITH) TO HUFFMAN AT 1735 EDT ON 8/30/07 * * * The State provided the following information via email: "The Americium sources (2 sources/100 millicuries each) in the Industrial Dynamic Filtec gauges were picked up for disposal by licensed contractor on 8-30-07. DRH will also notify State of Washington DOH about disposal of sources." R4DO (Nease) and FSME (McConnell) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2007-08-30
43569 | 0 | POTTSTOWN MEMORIAL MEDICAL CENTER |  |  |  |  | 2007-08-06 | 2007-08-15 15:26 | 2007-08-15 | MISPLACED I-125 SEED SHIPPED TO MEDICAL CENTER Pottstown Memorial Medical Center asked Core Oncology Mills to ship seventy six (76) I-125 seeds (0.345 mCi each), and one of those 76 would be used for calibration. Core Oncology Mills shipped seventy seven (77) thinking that Pottstown Memorial Medical Center requested 76 seeds plus one for calibration. On 07/17/07, the shipment arrived from Core Oncology Mills which contained 76 seeds plus one seed in a separate package in a different location from the 76 seeds. Pottstown Memorial Medical Center looked for 76 seeds, which they counted, and believed this was all the seeds in the shipping package. When Pottstown Memorial Medical Center realized there were 77 seeds in the shipment, they looked for the missing seed, and reported it could not be found. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-08-15
43568 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-08-15 08:38 | 2007-08-15 13:25 | 2007-08-15 | NOTIFICATION TO STATE DUE TO CONTAMINATED MATERIAL DISCOVERED IN FREE RELEASE SCRAP MATERIAL "At 0838 CDT on 08/15/2007, the State of Alabama Radiological Control Inspector [Deleted] was provided a voluntary notification that a small container of contaminated pipe compound was found in a local scrap metal recycling facility during an initial screening of a shipment of Browns Ferry Nuclear Plant (BFNP) scrap material. "At 1630 on 08/14/2007, TVA received notification from Tennessee Valley Recyclers that a shipment of scrap metal from BFNP alarmed their truck monitor during the initial screening. The item was identified as a small metal can (4 oz.) containing pipe threading compound. The item was quarantined. Follow-up survey confirmed no additional contaminated material in the shipment. "TVA retrieved the quarantined item. Follow-up radiation surveys of the container at BFNP confirmed that the material did not exceed any reporting requirement thresholds. All free release of material from the low level radwaste facility has been suspended pending the results of the investigation of the event. "As a result of this voluntary notification to the State, this event is reportable as a 4-hour Non-Emergency Notification in accordance with 10CFR50.72(b)(2)(xi) as 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a notification to other government agencies has been made." BFNP survey indicated 6000 cpm of Co-60. The licensee notified the NRC Resident Inspector. | 100 | 90 | 100 | 100 | 90 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-08-15
43567 | 0 | ENGINEERING CONSULTANT SERVICES |  |  |  |  | 2007-08-14 17:10 | 2007-08-14 17:17 | 2007-08-14 | TROXLER MOISTURE DENSITY GAUGE DAMAGED ON CONSTRUCTION SITE At 1710 EDT on 08/14/07, a Troxler moisture density gauge, model 3430, serial number 36254, was in use at a construction worksite on VA Route 460. A large piece of construction equipment was backing up and while the gauge technician attempted to get the vehicle driver's attention, the vehicle ran over the Troxler gauge. The 8 millicurie Cs-137 source was extended and after the damage could only be retracted to within 4 inches of the gauge case. The technician kept the extended source in the ground and controlled access to the area. The gauge technician called the NRC Operations Center for assistance. R1DO (Paul Krohn) and FSME EO (Holonich) were notified and briefed by the licensee technician on what assistance was required. During the conference call the RSO was notified and the company was dispatching personnel to the scene to assist. * * * UPDATE PROVIDED BY CURTIS HOWELL TO JEFF ROTTON AT 1953 EDT ON 08/14/07 * * * The licensee was able to retract the source and close the shutter door. No significant personnel exposure was received. The area has been opened for unrestricted access. Notified R1DO (Krohn) and FSME EO (Holonich). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2007-08-14
43566 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC |  |  |  |  | 2007-08-14 | 2007-08-14 14:40 | 2007-08-14 | ROSEMEOUNT 1154 PRESSURE TRANSMITTER CALIBRATION PROBLEM The supplier provided the following information via facsimile: Pursuant to 10 CFR Part 21, section 21.21(b) Rosemount Nuclear Instruments, Inc. [RNII] is writing to inform NRC that a total of ten (10) Model 1154 and 1154 Series H output range code 4 pressure transmitters whose model code includes special option suffix N0026 or N0079 may not calibrate at all of the published values [9 shipped to 2 utility sites in the United States]. "During evaluation of two returned Model 1154 output range code 4 pressure transmitters with special option suffix N0026, the cause of the customer-reported calibration problem was isolated to the amplifier circuit card assembly (CCA). Upon replacement of the amplifier CCAs the two affected transmitters calibrated and functioned normally. "During root cause analysis it was observed that a single resistor (R316) on each affected amplifier CCA had an incorrect resistance value. The R316 resistor enables a standard upper range limit (URL) of a transmitter with output range code four to be increased from 150 inches water to 210 inches water in combination with a minimum span of 75 inches water. This R316 resistor allows the transmitter to achieve performance specifications, calibration ranges, and spans as indicated by the special option drawing. "To meet site specific application requirements transmitters may be field recalibrated to different upper and lower range values and/or spans. Model 1154 and 1154 Series H transmitters with special option suffix N0026 or N0079 and amplifier CCAs whose R316 resistors were not replaced during the sub-assembly process, will have incorrect resistance values and may not calibrate to all upper and lower range values and/or spans published for the applicable special option. However, if an affected transmitter has been successfully calibrated, having the incorrect resistance value will not adversely affect transmitter performance during normal operation or accident conditions. "The manufacturing records for the two returned Model 1154 transmitters (with amplifier CCAs with part number 01154-0001-0006) were carefully reviewed. The sub-assembly traveler lacked the required material traceability information, indicating that the R316 resistors were not replaced. In an abundance of caution RNII carefully reviewed all sub assembly travelers for part number 01154-000l-0006. No other discrepancies were found. "The corrective action which has been taken; the name of the individual or organization responsible for that action; and the length of time taken to complete that action: "(a) RNII verified all transmitters in production and finished goods with applicable special options utilizing 01154-0001-0006 amplifier CCA's contained the correct board and resistor. No discrepancies were found. (Complete: 7/24/2007) "(b) RNII evaluated all 01154 CCA's in production to ensure they contained the correct resistor. No discrepancies were found. (Complete: 7/20/07) "(c) RNII examined all manufacturing paperwork for 01154-0001-0006 amplifier CCAs built and shipped prior to 7/24/2007. No additional discrepancies were found. (Complete: 7/25/2007) "(d) An internal corrective action request was initiated. All corrective actions will be completed by 8/15/07. "The end user is advised to determine the impact of this potential non-conformance on its plant operations and safety and take action as deemed necessary. RNII can supply replacement 01154-0001-0006 amplifier CCAs which can be installed per section five of the product manual or the transmitter can be returned to RNII for rework. If it is determined that return of affected transmitter(s) is required, RNII should be contacted to facilitate the return process." Plants affected: Saint Lucie (6 received) , and Waterford 3 (3 received). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2007-08-14
43565 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-08-14 12:51 | 2007-08-14 13:22 | 2007-08-14 | TECHNICAL SUPPORT CENTER UNAVAILABLE FOR EMERGENCY USE "Fermi 2 removed the Technical Support Center (TSC) heating ventilation and air conditioning system from operation to facilitate preventive maintenance activities on August 14, 2007. During this work, the facility will not be available for emergency use. Fermi is making this notification in accordance with 10 CFR 50.72(b)(3)(xiii). In the event TSC activation is necessary, the EOF will be utilized. Activation and use of the EOF as a backup for the TSC is included in Fermi's Radiological Emergency Response Preparedness Plan, and drills have been held performing both the TSC and EOF functions from the EOF. Fermi will notify the NRC upon completion of this work, which is scheduled for Wednesday August 15, 2007." The licensee will notify the NRC Resident Inspector. * * * UPDATE PROVIDED BY JEFF GROFF TO JEFF ROTTON AT 2342 EDT ON 08/14/07 * * * "Preventive Maintenance activities on the TSC HVAC system have been complete. The TSC is now available for use." The licensee notified the NRC Resident Inspector. Notified R3DO (J. Cameron) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-14
43564 | -1 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-08-13 15:22 | 2007-08-13 20:37 | 2007-08-15 | POTENTIAL HOT SHORT ISSUE WITH CONTAINMENT SPRAY SUMP SUCTION VALVES " A condition is being reported as a conservative measure regarding a situation involving potential fire induced circuit failures on associated circuits. Plant Vogtle is considered to be in compliance with its current fire protection licensing basis, Branch Technical Position CMEB 9.5.1 as endorsed by UFSAR Appendix 9B, however, this condition is being reported as the generic industry issues associated with multiple spurious circuit failures have not been resolved to date. "A potential hot short issue exists involving Containment Spray Sump Suction valves 1(2)HV-9002A, 1(2)HV- 9003A, 1(2)HV-9002B, and 1(2)HV-9003B. If a fire were to occur in a location where the control circuit cables for those valves run in the same electrical raceway, a credible condition exists where either flowpath could spuriously open which would cause the Refueling Water Storage Tank (RWST) to drain down to the containment sumps. "The fire zones where associated cables are located were placed under a compensatory hourly fire watch until compensatory measures were established. As an interim corrective action, operator manual actions have been specified and incorporated into plant procedures to deenergize and verify closed one valve in the series flowpath upon determination that a credible fire exists. These manual actions are in accordance with RIS 2006-10 for plants which are licensed to operate after January 1, 1979. Southern Nuclear will determine long term corrective actions for this condition. "The effects of a fire sufficient to cause a spurious operation of multiple valves is not expected to be immediate and thus will allow sufficient time to perform the manual actions." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY G. SAXON TO J. KOZAL ON 8/15/07 AT 1522 * * * "An eight hour report (EN#43564) per 10CFR50.72(b)(3)(ii)(B) was conservatively reported based on a fire-induced hot short issue (multiple-spurious) which could result in the spurious opening of Containment Spray Sump Suction valves 1(2)HV-9002A, 1(2)HV-9003A, 1(2)HV-9002B, and 1(2)HV-9003B. HV-9002 and HV-9003 are two valves in series between the containment emergency sump and the containment spray pumps. If a fire were to occur in a location where the control circuit cables for those valves run in the same electrical raceway, it is postulated a condition may exist where either flowpath could spuriously open which would cause the Refueling Water Storage Tank (RWST) to drain down to the containment sumps. "The VEGP design basis defines a spurious control signal action/inaction as being caused by a single hot short, open circuit, or short-to-ground for a single component. Since all three conditions are postulated, the assumption that all adverse conditions will happen to the subject component(s) yields a conservative evaluation. Where a hi/low pressure interlace (fire-induced LOCA) is involved, an unlimited number of spurious control signal actions/inactions are postulated. Calculations have been reviewed to ensure these design criteria have been met. "At this time, there is no definitive new guidance (Generic Letter, etc.) by the NRC on how licensees are to handle analysis of multiple spurious shorts. The status and history of misunderstanding and confusion relative to the regulatory and design requirements is well documented in NRC EGM 98-002 Rev. 2 and EGM 07- 004. The NRC staff and the industry are currently working to resolve questions raised by the industry about the adequacy of the existing staff guidance concerning fire-induced circuit failures and the consistency of staff interpretations of both the guidance and the underlying regulatory requirements. "In summary, VEGP is in conformance with the current design basis. However, as defense-in-depth, actions have been taken that include implementation of hourly fire watches in the affected zones until procedural guidance for performance of manual actions were added to the Annunciator Response Procedures for the Fire Alarm Computer. The manual actions consist of opening the breakers for one of the emergency sump-to containment spray pumps suction isolation valves and then verifying the valves are closed. "Based on the above discussion, SNC is retracting EN#43564." The licensee will notify the NRC Resident Inspector. Notified R2DO (Ogle). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-08-13
43563 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-08-13 14:20 | 2007-08-13 19:49 | 2007-10-03 | INOPERABLE RADIATION MONITORS DUE TO SETPOINT CALCULATION ERRORS "On August 13, 2007 at 14:20 [EDT], the Susquehanna Control Room was notified that during review of calculations for the Secondary Containment Radiation Monitor Setpoints errors were identified in Tech Spec Allowable Values and TRM Trip Setpoints that rendered them non-conservative. The affected instruments are Refuel Floor Wall, Refuel Floor High, and Railroad Access radiation monitors. The condition affects both Susquehanna Units. The radiation monitors are required to be operable for conditions noted in footnotes (a), (b), and (c) in Tech Spec tables 3.3.6.2-1 and 3.3.7.1-1 (i.e. operations with a potential for draining the reactor vessel, during CORE ALTERATIONS and during movement of irradiated fuel assemblies in the secondary containment, and movement of irradiated fuel assemblies within or above the Railroad Access Shaft). The function of these instruments is to initiate systems that limit fission product release during and following certain postulated accidents and to minimize the consequences of radioactive material in the control room environment. "The radiation monitoring instruments were declared inoperable. All movement of irradiate fuel assemblies was halted (dry fuel storage activities were in progress at the time of notification). Based on this action, these monitors are no longer within the specified Applicability, and are therefore not currently required to be operable. The event has been determined to be reportable within 8 hours under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM G. ROBINSON TO J. KNOKE AT 1222 EDT ON 10/03/07 * * * "On August 13, 2007 PPL Susquehanna reported that during a review of calculations for the Secondary Containment Radiation Monitor Setpoints, errors were identified in Tech Spec Allowable Values and TRM Trip Setpoints that rendered them non-conservative. The affected monitors were declared inoperable and the required LCO & TRO Actions entered. A subsequent engineering review determined that the values used to establish the Tech Spec Allowable Values and TRM Trip Setpoints were based on a Realistic Source Term, not a Design Basis Source Term. These values were sufficiently conservative to compensate for the errors in the calculations and the dose release limits from a Design Basis Accident would not have been challenged. It was concluded that the existing Tech Spec values and setpoints remained valid and the monitors were operable in their original condition. Based on this conclusion Event Notification EN# 43563 is being retracted." The licensee notified the NRC Resident Inspector. R1DO ( Powell) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-08-13
43562 | -1 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-08-13 09:00 | 2007-08-13 17:04 | 2007-08-30 | INADEQUATE FIRE PROTECTION ON SAFETY CHILLED WATER SYSTEM ELECTRICAL CABLES "At 0900 on July 30 2007, an Engineer noted during the review of a revision to the Comanche Peak Fire Safe Shutdown Analysis that a cable associated with the control circuitry for Train B of the Safety Chilled Water System may not be adequately protected from a potential fire. By design, electrical control cables for Trains A and B of the Safety Chilled Water System are located in the same fire zone. The original design specified that the Train B electrical control cables in this zone were to be protected with fire barrier material (thermolag). However, in this case the fire barrier material was found to be missing from the Train B electrical control cables. Upon discovery of this condition, a fire impairment was implemented for the affected fire zone. "Engineering performed an evaluation of this condition and at 0900 on August 13, 2007 concluded that if a fire occurred in the affected fire zone, the required degree of separation for redundant safe shutdown trains was inadequate (i.e. both A and B trains were affected) and this would adversely affect the control circuitry and potentially prevent the Unit 1 Safety Chilled Water System from performing its intended safety function. The Unit 1 Safety Chilled Water Systems safety function at Comanche Peak is to remove heat dissipated from engineering safety features equipment and to maintain ambient temperatures in rooms containing safety related equipment below maximum design temperatures. "This condition is similar to an example given in NUREG 1022, Rev. 2, Section 3.2.4 for an unanalyzed condition that significantly affects plant safety (fire barrier missing such that the required degree of separation for redundant safe shutdown trains is lacking). Therefore, this condition is reportable per 10CFR50.72(b)(3)(ii)(B), 'The nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.'" The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 08/30/07 AT 1249 EDT FROM RAUL MATINEZ TO MACKINNON * * * "CPNPP is retracting Event Notification 43562 based on the following: "Further review of this issue by Engineering has determined that the required degree of separation for redundant safe shutdown trains was adequate and the Unit 1 Safety Chilled Water System was capable of performing its intended safety function. Therefore, this condition is not reportable per 10CFR50.72(b)(3)(ii)(B), 'The nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "CPNPP has informed the NRC Resident Inspector." R4DO (R. Nease) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-08-13
43561 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2007-08-13 10:00 | 2007-08-13 14:31 | 2007-08-14 | EMERGENCY OPERATIONS FACILITY VENTILATION INOPERABLE "This event is being reported under 10CFR50.72(b)(3)(xiii) for a major loss of offsite emergency response capability. "At 2325 Central Daylight Time (CDT) on 8/12/2007, Callaway Plant received a trouble alarm for the Emergency Operations Facility (EOF). Investigation revealed the EOF had lost one phase of incoming rural electric power which is believed to have been caused by a severe thunderstorm in the area. At 0001 CDT on 8/13/2007, the EOF diesel generator was started and aligned to provide power to all building loads. An EOF functionality evaluation was performed for a loss on normal power with the EOF being supplied from the diesel generator and pre-existing degraded air conditioning cooling capacity. The evaluation concluded that the EOF was fully functional. "At approximately 1000 CDT on 8/13/2007, maintenance personnel reported to the Control Room that the emergency ventilation system in the EOF was not functional based on the pressurization fans rotating in reverse. Three phase electrical loads at the EOF are incorrectly polarized apparently due to improper terminations at the diesel generator. If an emergency condition occurs during the time repairs are being made, the EOF will be utilized as long as radiological conditions allow. Procedure EIP-ZZ-C0010, EMERGENCY OPERATIONS FACILITY OPERATIONS, section 4.4, directs EOF management to evaluate the need to relocate operations to the Backup Emergency Operations Facility, as required. Affected emergency responders have been notified of facility conditions and a courtesy notification has been made to the State Operations Branch Chief." The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY KEITH DUNCAN TO JEFF ROTTON AT 1248 ON 08/14/07 * * * "The EOF (Emergency Offsite Facility) rural electric power was restored to the building at 1730 (CDT) on 8/13/2007. At 0059 (CDT) 8/14/2007 the EOF diesel work was completed, restored and retested satisfactorily. Building temperatures were verified to be at 85 deg F and lowering, this is within the 55-95 deg F range for functionality. The EOF is considered restored to a fully Functional Status. The licensee notified the NRC Resident Inspector. Notified R4DO (Gaddy) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-13
43560 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-08-11 17:51 | 2007-08-11 21:25 | 2007-08-11 | AUTOMATIC SCRAM DUE TO NEUTRON MONITORING TRIP SIGNAL "On 08/11/2007 at 1751 CDT, Browns Ferry Unit 1 received an Automatic SCRAM due to a Neutron Monitoring (APRM) Trip Signal . Preliminary investigation indicates the trip signal was caused by a Recirculation System Flow Transmitter sensing line becoming separated giving an indicated low flow signal to the neutron monitoring system. With the indicated low flow and high (100%) power, the neutron monitoring system initiated an APRM Simulated Thermal Power Flow Biased Reactor Scram. All control rods inserted and all systems responded as required to the automatic SCRAM signal. No Emergency Core Cooling System (ECCS) initiations occurred as a result of the SCRAM. Reactor water level lowered below Level 3 (+2") (lowest indicated level reached -33") as a result of the SCRAM and was recovered to the normal level band by the Reactor Feed Pumps (RFPs). The expected Primary Containment Isolation System (PCIS) Groups 2, 3, 6, and 8 isolations were received due to Reactor Water Level lowering below Level 3 (+2") (lowest indicated level reached -33") with all systems isolating as required. Reactor pressure is being controlled using Main Steam Bypass Valves. Reactor Level is being maintained in band using Reactor Feed Pumps. Plant to remain in Mode 3 and initiate repairs to the failed sensing line. Investigation into the event is proceeding. "This event is reportable under 10CFR50.72(b)(2)(iv)(B), any event or condition that results in a valid actuation of the Reactor Protection System; 10CFR50.72(b)(3)(iv)(A), any event that results in an actuation of the specified systems. This event also requires a 60 day written report in accordance with 10CFR50.73(a)(2)(iv)(A). "The NRC Senior Resident Inspector has been informed of this event." The sensing line had a flow limiter on it and the line was isolated locally. Amount of leakage not known at this time. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-08-11
43559 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-08-01 | 2007-08-10 12:12 | 2007-08-10 | AGREEMENT STATE REPORT - MASSACHUSETTS - RECEIPT OF LEAKING SOURCES The State provided the following information via facsimile: "Thermo NITON Analyzers LLC reported that it had received 10 (ten) sealed sources from Isotopes Products Laboratories (IPL) that were contaminated or leaking sources. Five (5) of the sealed sources exceeded leak test reporting limits of 0.005 microcuries (185 Bq) removable activity and five (5) sources were contaminated, but with less than 0.005 microcuries (185 Bq) removable activity. "The ten (10) sealed sources were each identified as IPL Model XFB-3, each containing 40 millicuries of Cd-109. Each sealed source was individually wipe tested by Thermo NITON Analyzers LLC and each wipe test was analyzed by a licensed consultant. "Thermo NITON Analyzers LLC shipped back the affected sealed sources to IPL via Federal Express Priority Overnight shipment on 8/1/07. Thermo NITON Analyzers LLC stated that IPL is in licensed possession of the sources in Burbank, CA where they are being evaluated by their quality group. "The area where the source leak tests were acquired was surveyed thoroughly by Thermo NITON Analyzers LLC and no contamination was found. "Thermo NITON Analyzers LLC reports that the following five (5) sources exceeded the reporting limit of 0.005 microcuries by the amount indicated. 1. Serial Number NR9014 was 1.02 times the state limit of 0.005 microcuries. 2. Serial Number NR9012 was 1.08 times the state limit of 0.005 microcuries. 3. Serial Number NR9019 was 1.00 times the state limit of 0.005 microcuries. 4. Serial Number NR9020 was 2.46 times the state limit of 0.005 microcuries. 5. Serial Number NR9011 was 2.88 times the state limit of 0.005 microcuries. "Thermo NITON Analyzers LLC reports that the following five (5) sources were contaminated but did not exceed the reporting limit of 0.005 microcuries. The percent of the limit is reported below. 1. Serial Number NR9016 was 44% of the state limit of 0.005 microcuries. 2. Serial Number NR9013 was 18% of the state limit of 0.005 microcuries. 3. Serial Number NR9015 was 34% of the state limit of 0.005 microcuries. 4. Serial Number NR9018 was 42% of the state limit of 0.005 microcuries. 5. Serial Number NR9017 was 26% of the state limit of 0.005 microcuries". | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-08-15
43558 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2007-08-07 16:00 | 2007-08-09 10:41 | 2007-08-09 | PART 21 - TWO COMMERICAL GRADE RELAYS CONTAINED DEFICIENCIES " Event: On August 7, 2007, Duke Energy (Duke) completed a reportability determination which concluded that two relays contained deficiencies and were reportable under Part 21. The relays were Commercial Grade Items dedicated by Duke. Following dedication, a bench test performed on August 26, 2004 revealed that relay contacts were not set up properly at the factory. Eight other relays from the same purchase order were acceptable. The relays were Magnecraft Struthers-Dunn part number 219ABAP-115/125D. The Part 21 evaluation in 2004 was terminated based on incorrect guidance in the applicable Duke administrative directive. The directive error was identified March 29, 2007 and a review of prior Part 21 reportability determinations was initiated. The original 2004 problem report on these relays was reopened, leading to this Part 21 report being made at this time. "Initial Safety Significance: None. The defective relays were never installed. The intended applications could not have resulted in a significant safety hazard. However, the Duke administrative directive on Part 21 evaluations states that all potential applications where the component might be installed as a substitute must be considered. Duke has concluded that installation in some unspecified application 'could have resulted in a significant safety hazard' and therefore the issue is being reported. "Corrective Action(s): In 2004: There were eight (8) additional relays from the same purchase order. These were retested and found acceptable. The two identified defective relays were returned to the manufacturer. The manufacturer concluded that the relay contacts were improperly assembled. They consider this an isolated case. In 2007: The Duke administrative directive on Part 21 evaluations was corrected. Previous Part 21 determinations were reviewed, leading to this report." NRC Resident Inspector was notified of this Part 21 notification by the licensee. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2007-08-09
43557 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-08-06 | 2007-08-08 17:36 | 2007-08-08 | NORTH CAROLINA AGREEMENT STATE - NUCLEAR MEDICINE TECHNOLOGIST SELF ADMINISTERED SPARE RADIONUCLIDES The State provided the following information via facsimile: "Incident description as reported to NCRP [North Carolina Radiation Protection]: Nuclear Medicine Technologist (NMT) working in the Lenoir, NC office of the Licensee performed a diagnostic cardiac imaging exam on himself. He administered himself with 39.4mCi Tc-99m Myoview for a stress test and followed it up with 11.6 mCi Tc-99m Myoview for the rest test. Both administrations occurred on 8/6/07 and were done without the Licensee's or an Authorized User's knowledge or consent; using a dose intended for a patient that did not show-up for their scheduled diagnostic cardiac imaging exam. The NMT 'read' the resulting diagnostic images and observed a cardiac problem, then apparently called the Licensee's office in Hickory to get a second opinion. The Nuc Med Supervisor (Located in the Hickory Office) was made aware of the administration at approximately 1530 on 8/6/07, and the RSO was notified at approximately 1800 on 8/7/07. "The Licensee reported that the Lenoir office is attended by a single NMT assisted by a Nurse. The rest of the Lenoir office is a non-nuclear cardiology practice although there is an Authorized User (an MD) at that location. At the time of the administration the Authorized User was attending non-nuclear study patients and was not aware of the activities being performed by the NMT on himself. The NMT performed the stress part of this diagnostic administration with Nursing assistance. The licensee reported that the Nurse felt that the NMT was doing something wrong but assisted the treadmill portion of the stress test for safety reasons. Sometime during this span of time the Authorized User at the Lenoir office went to the Hickory office to attend patients and was at that office when the NMT called and reported what he had done. "NCRPS actions: (1) requested a complete written report with statements from all individuals involved from the Licensee, which will be evaluated; (2) report to NRC Op Center in case this turns out to be immediately reportable; (3) consider follow-up inspection/incident investigation; (4) possible escalated enforcement actions to be determined." NC Incident # 07-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-08-13
43556 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2007-08-08 15:25 | 2007-08-08 16:09 | 2007-08-08 | ALERT DECLARED TO DUE POTENTIAL HAZARDOUS ATMOSPHERE IN A EMERGENCY DIESEL GENERATOR ROOM While the licensee was conducting maintenance activities in the E3 Emergency Diesel Generator (EDG) room, a CO2 fire extinguisher was observed to be leaking. Personnel were evacuated from the room due to a potential hazard from CO2 buildup in the room. The licensee was initially unable to determine the concentration of Oxygen or CO2 in the EDG room but made a decision to declare an Alert at 1536 EDT in accordance with EAL H.A.7, "Life Threatening Atmosphere Potential." The licensee does not consider the condition a threat to plant operation. State and local authorities have been notified. The licensee has also notified the NRC Resident Inspector. The licensee anticipates that a press release will be issued. * * * UPDATE FROM LICENSEE (JANKAUSKAS) TO HUFFMAN AT 1707 EDT ON 8/08/07 * * * The licensee terminated the Alert at 1653 EDT base on Oxygen concentrations in the E3 EDG room above 20% and confirmation that Oxygen levels in the other 3 EDG bays (4 total) also confirmed above 20%. State and local authorities have been notified. The licensee will notify the NRC Resident Inspector. R1DO (Summers), IRD (Cruz), and NRR EO (Ruland) notified. The following offsite agencies were notified of the Alert termination: DHS (Akers); FEMA (Bisco); DOE (Turner); and USDA (Leadbetter). | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-08-08
43555 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-06-09 05:11 | 2007-08-08 13:06 | 2007-08-08 | INVALID ACTUATION OF THE 'C' EMERGENCY DIESEL GENERATOR "This 60-day notification is being made in accordance with 10 CFR 50.73(a)(1), which states that in case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv), other than the actuation of the Reactor Protection System when the reactor is critical, the licensee may provide a telephone notification to the NRC within 60 days after discovery of the event instead of submitting a written LER. "On 6/9/07 at approximately 0511 hours, the 'C' Emergency Diesel Generator (EDG) and associated 'C' Emergency Service Water pump unexpectedly started while performing procedure TP-024-147, Diesel Generator 'C' Restoration after being out of service for scheduled overhaul and corrective maintenance activities. The EDG inadvertently started in response to an invalid emergency start signal that occurred when the incorrect states ink (SL-8) was opened in panel 0C521C. The cause of this event was due to a human performance error. The EDG was subsequently shutdown following the inadvertent start. Post- maintenance testing of the 'C' EDG was successfully completed. "The consequences of this event are limited to the unplanned start of the 'C' EDG. The EDG started and functioned in accordance with its design. Since no actual plant condition existed which required the EDG to start, and since the start occurred inadvertently as a result of human error, this event has been classified as an invalid actuation. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-08-08
43554 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-08-01 | 2007-08-08 09:55 | 2007-08-08 | RADIOGRAPHIC CAMERA SOURCE CONNECTOR ASSEMBLY MALFUNCTION The following information was provided by the State via facsimile: "On 8/1/07, one of Integrity Inspection Solutions crews was setting up for radiographic operations at a temporary job site. While connecting the crankout to the exposure device, the source connector assembly broke. Due to this happening before the first exposure on the job, there was no source disconnect. Another crankout was available and the job was completed. The crankout manufacturer could not be determined. The crankout will be sent to an authorized agent for repair. The crankout was used with a SPEC 150 camera." LA Event Report ID No.: LA070023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-08-13
43553 | 0 | NASA GODDARD SPACE FLIGHT CENTER |  |  |  |  | 2007-08-03 16:20 | 2007-08-08 09:49 | 2007-08-08 | MISSING SOURCE DURING INVENTORY Licensee conducted radioactive source inventory on 08/03/07 at 1620 and discovered one Am-241 sealed source containing 50 microcuries was not in its assigned storage location. It's normal storage location is in a storage locker inside of a square enclosure built of shielding bricks. On 08/07/07 the source was located in the storage locker behind its normal storage location. Facility procedures will be modified to prevent reoccurrence. * * * UPDATE PROVIDED BY DAN SIMPSON TO JEFF ROTTON AT 1649 EDT ON 08/08/07 * * * The following information was provided by the licensee via fax: (i) Description of source: Americium-241 source (AM-241-587), 50 microcuries on October 1, 1995, manufactured by Isotope Products Laboratories, model number: PHR-241-50U, A2 capsule. "(ii) A description of the circumstances under which the loss or theft occurred: On August 3,2007 (Friday), the Radiation Protection Office (RPO) staff conducted a quarterly radiation source inventory in Building 2, room W102A's storage locker. During the inventory, radioactive source Am-241-587, a 50 microcurie source, was not readily visible in the locker. The RPO staff noted that the source sign out sheet had not been filled out showing that the source had been moved out of the room. The RPO staff contacted the Authorized User and told him that they were not able to locate the source in the locker and told him that he needs to check with anyone that may have been using the source to see if they know of its whereabouts. The RPO staff notified the RSO (who was out of the office) by email at 4:17 p.m. that the source had not been located during the inventory. "On August 6, 2007 (Monday), the RSO, upon reading the email sent by the RPO staff, reviewed the requirements of 10 CFR 20.2201 and misinterpreted the value listed in Appendix C and followed the notification requirements listed in 10 CFR 20.2201(ii), which allowed for 30 day notification. The RSO went to room W102A and reviewed the status of the locker. It was noted that all the sources were now being maintained on the bottom of the locker behind lead bricks. On April 17, the last time the inventory was completed by the RPO, the sources were stored on different shelves to help segregate the authorized user's sources from each other. After looking inside the locker and throughout room W102A and W102 the source was not sighted. "On the morning of August 7, the RSO instructed the RPO staff to go back and search the locker and remove all of the leads bricks surrounding the sources to ensure that the source in question was not there. At around 8:30 am, upon removing all of the bricks it was found that radioactive source Am-241-587 had gotten pushed up against the back of the locker behind the lead bricks. This apparently had taken place when the sources had been moved to the bottom shelf behind the lead bricks by the researchers. "On the morning of August 8, the RSO, while writing the report for this event, noticed that he misread the Appendix C value for Americium-241 and an immediate notification to the NRC based on 10 CFR 2201(a)(i) was required. The RSO then made an immediate notification to the NRC Operations Center at 9:49 a.m. "(iii) A statement of disposition, or probable disposition, of the licensed material involved; Radioactive source Am-241-587 had been in the locker throughout this whole process and never was missing, but had been improperly stored by the authorized users when they reconfigured the way the sources are stored in the radiation locker. "(iv) Exposures of individuals to radiation, circumstances under which the exposures occurred, and the possible total effective dose equivalent to persons in unrestricted areas; Room W102A is a restricted area and since the source had been in a shielded configuration throughout this whole event, no individuals received any exposure in unrestricted areas. "(v) Actions that have been taken, or will be taken, to recover the material; The source was found inside the authorized locker behind bricks that had been set up by the researchers. "(vi) Procedures or measures that have been, or will be, adopted to ensure against a recurrence of the loss or theft of licensed material: - A Radiation Safety Officer Notice will be sent to all users of radioactive sources to inform them of this event and explain the importance of notifying the RPO of any changes to the way in which radioactive sources are being stored in their areas. -Modifications will be made to the current Standard Operating Procedures (SOP) used by the RPO staff for performing quarterly source inventories, which will expand the Notifications section to ensure that staff members get in direct contact with the RSO when a source on the inventory is not located. - Appropriate staff will be trained on all modification to the procedures." Notified R1DO (Summers) and FSME EO (McConnell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-08-08
43552 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-08-07 15:06 | 2007-08-07 16:20 | 2007-08-07 | REACTOR SCRAM ON LOW REACTOR WATER LEVEL FOLLOWING PARTIAL LOSS OF CONDENSATE FEEDWATER FLOW "Unit 2 RPS actuation / unplanned scram occurred at 1506 eastern time on low reactor water level scram initiation. The unit experienced a partial loss of condensate feedwater due to the trip of 2D 4160 volt station service bus [non-safety related]. The 2C 4160 volt bus remained in service supplying power to one condensate pump and one condensate booster pump. Investigation of the 2D 4kv bus trip is in progress. Also received a Group II isolation signal due to low reactor water level." The reactor is currently stable with water level at 37 inches. Normal feedwater has been used to makeup water level and decay heat is being discharged to the condenser via turbine bypass valves. All rods fully inserted. No SRVs lifted during the transient. The lowest water level reached was -5 inches. The Unit remained in a normal electrical lineup. There were no significant LCOs in effect at the time of the scram. There was no impact on Unit 1. The licensee notes that I&C activities had been in progress on the 2D 4kv bus about the time that it tripped however there is currently no specific connection between these activities and the bus trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-08-07
43551 | 0 | U.S. ARMY |  |  |  |  | 2007-08-06 23:00 | 2007-08-07 11:14 | 2007-08-07 | FIRE IN RADIOACTIVE WASTE STORAGE FACILITY "6 Aug 2007 there was a small fire at ANAD's [Anniston, AL Army Depot] radioactive storage warehouse building 86. During a security patrol they noticed smoke coming out of building 86 and sent out emergency notifications to Safety, Fire Department and later to HazMat. After the Fire Department arrived they sent out notification to contact the Radiation Safety Office (RSO) and to respond. Fire personnel forced the personnel door open and accessed the fire situation from the exterior of the building. The box pallet was smoldering approximately 10 feet from their door. Fire personnel remained at the door entrance and fought the fire from that location. At no time was any of the fire personnel put in jeopardy to be overly exposed to the radioactive waste which was being stored in the warehouse. The fire was extinguished with the very least amount of water, which reduced the spread of contamination to the unaffected part of the warehouse. The fire chief was in contact with the RSO during this operation until his arrival at approximately 7:40. The damage was two wooden box pallets which contained several tritium sources awaiting waste disposal. At this time [the licensee] is not sure exactly how many sources was involved, [estimate the number to around 100 sources] containing on average 10 Ci of tritium each were involved. Many did burst due to the heat thereby releasing the tritium it contained. Surveys to the fire personnel equipment showed no contamination. Personnel were given a bioassay the following day to insure no uptake of tritium gas. Because a small amount of water was used to extinguish the fire, the spread of tritium contamination to the sealed floor area is minimum. The initial survey levels found are in the 8,000-28,000 dpm range to the floor involving an area of 10'X10'. "Cause of the fire was the result of some decon media (hydrogen peroxide) which had been sealed in a zip lock bag along with some paper towels. The hydrogen peroxide breaks down to pure oxygen and was sealed within a zip lock bag. Apparently there must have been a small amount of some oily residue also within the bag as part of the clean up process. As the oxygen content within the zip lock bag increased and interacted with the oil residue the bag begin to smolder causing the fire to start. * * * UPDATE PROVIDED BY JEFFREY HAVENNER TO JEFF ROTTON AT 1644 EDT ON 08/07/07 * * * "The local RSO performed an inventory of the contents of Bldg 86 this afternoon. He has calculated the total release of tritium to be 788 Ci [from 92 devices]. Notified R3DO (Riemer), R1DO (Summers) and FSME EO (McConnell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2007-08-07
43550 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-08-06 13:10 | 2007-08-06 15:21 | 2007-08-06 | REACTOR TRIP DUE TO SPURIOUS INTERLOCK SIGNAL TO FEEDWATER REGULATING VALVES "This 4-hour notification is being made to report that Salem Unit 2 has experienced an automatic reactor trip. The trip was initiated by a low steam generator level on 22 SG (14 percent narrow range). The low steam generator level was apparently caused due to the feedwater regulating valve closing as a result of a spurious 'Feedwater interlock' signal. Post trip the following occurred: 21, 22, & 23 auxiliary feedwater pumps auto started after the trip due to valid steam generator low levels (14 percent) as expected on a unit trip. 23 Auxiliary feedwater pump [turbine driven] was tripped in accordance with the emergency operating procedure and will be returned to an operable condition following recovery of steam generator levels. "Salem Unit 2 is currently in mode 3. Reactor coolant system pressure at 2235 psig and temperature is 547 degrees F with decay heat removal via the main steam dump system. Unit 2 has no active shutdown Tech Spec Action statements in effect. " There was no major secondary equipment tagged for maintenance prior to the event." On the reactor trip, all control rods fully inserted. No primary or secondary relief valves or safety valves lifted. The electric plant is in a normal shutdown lineup. This event had no effect on Unit 1. The licensee notified the NRC Resident Inspector. The licensee will notify the Lower Alloways Creek township, the State of NJ Bureau of Nuclear Engineering, and the State of Delaware. The licensee also plans on issuing a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-08-06
43549 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-08-04 10:25 | 2007-08-05 09:33 | 2007-08-14 | X-342 FACILITY CONTAINMENT SHUTDOWN "On Saturday August 4th 2007 at 1025 hours, Autoclave # 1 in the X-342 Facility experienced a Containment Shutdown due to the actuation of both 'A' and 'B' EXTREME PRESSURE AUTOCLAVE alarms. The autoclave was in (applicable) TSR MODE II 'Heating' for 55 minutes when these actuations occurred. After reviewing the other autoclave operating parameters and the results of the as-found pressure loop values, it is evident that there was no release of UF6 inside this autoclave. Operations and Engineering Personnel are continuing their investigation into the circumstances surrounding this event in an attempt to identify the cause of the alarm actuations. With no evidence to suggest these alarms were caused by an invalid signal, the Plant Shift Superintendent's (PSS) Office is reporting this event as a valid actuation of a 'Q' Safety System. "The autoclave was placed in MODE VII 'Shutdown' and declared inoperable by the Plant Shift Superintendent (PSS). No release of radioactive material occurred as a result of the incident. This event is being reported in accordance with UE2-RA-RE1030 Appendix D. J. 2. Safety Equipment Actuations." The licensee notified the Department of Energy and the NRC Resident Inspector. * * * RETRACTION PROVIDED BY RON CRABTREE TO JEFF ROTTON AT 1232 EDT ON 08/14/07 * * * " Following a comprehensive review of the circumstances surrounding this incident by the PORTS Nuclear Regulatory Affairs (NRA) Group, a recommendation was made to the PSS Office that this event be retracted. This recommendation was based upon the determination that the 'Q' Safety function of the 'A' and 'B' EXTREME PRESSURE AUTOCLAVE alarms is to actuate when the internal autoclave shell pressure rises above the operating steam pressure (thereby indicating a UF6 release within the autoclave and placing the autoclave in containment. Since there was no UF6 release and the autoclave internal pressure was only due to steam, there was no valid signal to the 'Q' Autoclave Shell High Pressure Containment Shutdown System. Per the reporting criteria stated in PORTS SAR section 6.9, Table 1, criteria J.2, this is not a reportable event due to the 'Q' system actuation being caused by an invalid signal. Based upon the information provided, the PORTS PSS Office is retracting this event." The licensee notified the NRC Resident Inspector. The licensee will be notifying the Department of Energy. Notified R2DO (Ogle) and FSME EO ( Flannery). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2007-08-05
43548 | 0 | US ARMY |  |  |  |  | 2007-07-30 | 2007-08-03 16:32 | 2007-08-03 | TWO MISSING M114 A1 ELBOW TELESCOPES "Location : Anniston AD [Army Depot], Anniston, AL "Date reported to the licensee: 2 Aug 2007 by the Anniston AD RSO "Licensed material involved: M114A1 elbow telescopes 2 each. NSN 1240-00-150-8889. Each elbow telescope contains 5.6 curies of tritium ( gaseous form). "Historical information: On 30 June, two M102 howitzers left the maintenance repair facility at Anniston Army Depot from bldg. 418. Each howitzer contains a carrying case that contains the M114A1, M140 alignment device and M137 pantel telescope. The M102 howitzers and associated cases were transported to a contractor operated paint facility located on post in bldg 143. The howitzers were to be painted. When work was completed by the contractor, the howitzers and associated carrying cases (containing the tritium fire control devices) were moved to the Defense Logistics Agency (DLA) shipping area on or about July 23rd. During the week of July 23rd, DLA personnel inspected the howitzers and associated components prior to them being shipped. It was at this time that DLA discovered that the M114A1 elbow telescopes were missing from each of the respective cases. The other tritium devices in the carrying case (M140 and M137) were still present. The licensee RSO contacted Army CID on 3 August for assistance in investigating the loss of the devices. Army CID from Ft. McPherson, GA office will begin their investigation on Monday August 6th 2007. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-08-03
43547 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2007-08-03 | 2007-08-03 13:25 | 2007-08-03 | COLORADO AGREEMENT STATE REPORT - LOST CUSTOM SOURCE The State provided the following information via facsimile: "This is the initial notification for an incident that was reported to this Department [State of Colorado] on this date. A research licensee reported the loss of a custom source containing approximately 120 microcuries of Am-241. The source, a stainless steel tube approximately 6 inches long and 1 inch in diameter, was manufactured by NRD with model number A001, and was used as an air stream ionization device contained in aerosol and gas-phase measurement instruments. The Am-241 is plated on a foil within the tube. The licensee reported the last known use was in March 2006. However, the licensee moved to a new location in December 2006, and the RSO stated that it is possible the source was lost at that time. The licensee reported that all efforts to locate the source have failed including a search of their former use location. No other details are available at this time." COLORADO Incident #: I07-12 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2007-08-08
43546 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-08-03 08:55 | 2007-08-03 10:18 | 2007-08-03 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) OUT OF SERVICE "Loss of [SPDS] for greater than 8 hours [is expected] because of a failed plant computer system. Troubleshooting to resolve computer issues is in progress." The licensee entered established contingency procedures to compensate. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY JAY LEBERSTIEN TO JEFF ROTTON AT 1407 ON 08/03/07 * * * "At 1205 hours, the Unit 2 SPDS was returned to operable." The licensee notified the NRC Resident Inspector. Notified R2DO (Moorman) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-03
43545 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-08-02 | 2007-08-02 12:40 | 2007-12-03 | TEN TRITIUM EXIT SIGNS STOLEN FROM CONSTRUCTION SITE The following information was received via fax: "Hotel under construction in Ft. Lauderdale, FL. Ten exit signs containing tritium were stolen. Owner contacting police and is searching for items. No further action will be taken on this incident." The exit signs are general licensed material, model number SLXTURW10, manufactured by Forever Light, Inc. Each sign contains 7.09 Curies tritium. The signs were installed Saturday, 7/28, and noticed missing yesterday, 8/1. Florida Incident No.: FL07-116 *** UPDATE FROM STEVE FURNACE TO HOWIE CROUCH AT 1047 ON 12/03/07 *** During clean up of the construction site storage area, all ten exit signs were found and are in the possession of the building contractor. Notified FSME EO (Morrell), R1DO (Rogge) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-08-07
43544 | 0 | WESTINGHOUSE NUCLEAR SERVICES |  |  |  |  | 2007-08-02 | 2007-08-02 13:24 | 2007-08-02 | POTENTIAL DEFECT INVOLVING FAILURE OF WESTINGHOUSE DB-25 CIRCUIT BREAKER "The following information is provided pursuant to the requirements to 10 CFR 21 to report the potential for the existence of a SUBSTANTIAL SAFETY HAZARD. This issue concerns the failure of a Westinghouse DB-25 circuit breaker to close after a new closing solenoid moving core relay release arm was installed at site. Westinghouse supplied closing solenoid moving core release arms that do not meet the material hardness requirement for safety-related applications at Constellation Nuclear, Robert E Ginna Generating Station. "Background: The closing solenoid moving core relay release arm for DB-25 circuit breakers is manufactured for and commercially dedicated by Westinghouse for Class 1E applications. After plant personnel installed a new closing solenoid moving core relay release arm on a DB-25 safety-related breaker and placed the breaker in service it failed to close on demand. The investigation of this breaker showed that the closing solenoid moving core relay release arm had interfered with the body of the control relay. While investigating this issue, it was determined that the closing solenoid moving core relay release arm material was from a single batch that did not meet the required material hardness specification. Westinghouse shipped twenty- five closing solenoid moving core relay release arm kits to a single plant from the batch that did not meet the material hardness requirement. "Evaluation: It is Westinghouse's understanding that the direct cause of the failure is that the closing solenoid moving core relay release arm material was too weak and bent after several closures of the breaker. This changed the mechanical and electrical timing of the circuit breaker, preventing it from closing again. "Safety Impact: Two of twenty five closing solenoid moving core relay release arms were actually installed on breakers at the plant [Ginna]. Only one breaker was actually placed into service. Had the defective closing solenoid moving core release arms been installed in redundant safety related breakers, this condition could have resulted in a common mode failure and the plant could have been in a condition outside the design basis. If the breaker was closed, the breaker would open but would then be unable to close again. "Corrective Action: Upon discovery of the DB-25 circuit breaker failing to close [at Ginna], plant personnel took corrective actions to remove the defective closing solenoid moving core relay release arms from service. Westinghouse removed the remaining defective closing solenoid moving core relay release arms from stock. "Plant Applicability: This notification is applicable to Robert E. Ginna Generating Station. Westinghouse has confirmed only one batch of closing solenoid moving core relay release arms was not manufactured to the correct hardness specification. No other plant received closing solenoid moving core relay release arms made from the batch that did not meet the correct material hardness specification from Westinghouse. "Communications: Robert E. Ginna Generating Station is aware of the issue. Westinghouse will be issuing a Nuclear Safety Advisory Letter (NSAL) documenting this issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-08-02
43543 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-08-01 12:00 | 2007-08-01 17:26 | 2007-08-01 | 77 OUT OF 108 PROMPT NOTIFICATION SYSTEM SIRENS FAILED THEIR MONTHLY TEST "On August 1, 2007, at 1200 Eastern Daylight time the prompt notification system (PNS) monthly test was performed and 77 of the 108 PNS sirens were not responsive to the test. This is considered to be a major loss of offsite response capability. Testing is being performed to ensure operability of the PNS sirens, trouble shooting has not identified the current problem with the system. 34 of the 77 sirens have been successfully tested and testing of the remaining sirens is being conducted." State, Local and the NRC Resident Inspector have been notified of this by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-08-01
43542 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2007-07-31 12:00 | 2007-08-01 11:30 | 2007-09-14 | 24 HOUR REPORT OF A PROCESS NOT INCLUDED IN THE INTEGRATED SAFETY ANALYSIS "During a review of the Fuel Manufacturing Operation (FMO) Integrated Safety Analysis (ISA) it was discovered that controls associated with the container transfer station in the Dry Scrap Recycle (DSR) area had not been included in the updated ISA Summary. Although process controls exist, they were not declared or documented in the ISA as IROFS (Items Relied on For Safety). This report is submitted for administrative reporting pursuant to 10CFR70.50 Appendix A(b)(1). At no time did an unsafe condition exist. The existing criticality safety analysis of the operation bounded the situation, was effective, and was not challenged. "All affected equipment is shut down pending revision of the ISA to document IROFS for this process. "While this did not result in an unsafe condition, this event is being reported pursuant with the reporting requirements of 10CFR70.50 Appendix A within 24 hours of discovery." The licensee has notified Region 2 (Gibson) ,State, and local authorities. * * * UPDATE AT 1433 EDT ON 09/14/07 FROM SCOTT MURRAY TO S. SANDIN * * * The licensee provided the following information as a supplemental report: "A detailed review of authorized process equipment and controls was performed to ensure each has been evaluated in an ISA and the required IROFS have been identified. This review identified ten other processes with a valid criticality safety analysis that were not specifically documented as a part of an ISA evaluation and the required IROFS had not been identified. The ISA reviews for these have been completed and the required IROFS documented. A total of twelve new IROFS have been identified." The licensee will inform the NRC Region 2 Office and the Headquarters Project Manager. Notified R2DO (Musser) and FSME (Wastler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | DEV FROM ISA | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(5) |  |  |  | 0 | 2007-08-01
43541 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-08-01 02:05 | 2007-08-01 02:55 | 2007-08-01 | UNUSUAL EVENT DECLARED DUE TO FIRE IN PROTECTED AREA GREATER THAN 10 MINUTES "An Unusual Event was declared based on a fire lasting > 10 minutes within the Protected Area. Fire was on a Pole Mounted Transformer located on the 230 KV Supplemental Power System in the North East corner of the Protected Area. Helper Cooling Tower Fans were lost and sequenced back on. Unit 1 maintained 100% Rated Thermal Power. Unit 2 reduced power to 91.2% due to increasing Circulating Water Temperatures per procedure. Fire was extinguished at 0213 using dry chemical fire extinguishers." Fire was initially spotted at 0152 EDT. It is believed that a snake may have caused the transformer to arc and that the arcing caused the wood transformer pole to catch on fire. Other than the brief loss of helper cooling to the circ water, there was no other impact on the facility. No offsite assistance from the fire department was called or needed. The licensee terminated the Unusual Event at 0250 EDT. The licensee notified local and State Authorities and the NRC Resident Inspector. | 100 | 91 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-08-01
43540 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-07-31 | 2007-07-31 16:07 | 2007-07-31 | AGREEMENT STATE REPORT - STOLEN RADIOACTIVE MATERIAL "On July 31, 2007, the licensee notified DHFS of the theft of a control device for a Masterminder 2 x-ray crawler. It has been stored in a locked storage trailer at a temporary jobsite located a few miles north of Rome, WI. The lock had been cut, and other equipment had been stolen. The device contains a Cs-137 source with an approximate activity of 126.5 mCi. Local law enforcement and the Federal Bureau of Investigation have been notified, and are investigating. State and local emergency management have been notified, and a DHFS emergency responder has been dispatched to the site. "The company was doing radiography on a natural gas pipeline. WeldSonix has provided a picture of the device. "DHFS is planning on issuing a press release." The state indicated that the device was 25 years old, and the activity level should be reduced by one half-life. "Event Report ID No.: WI 07-0014" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-08-03
43539 | -1 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-07-16 12:00 | 2007-07-31 15:40 | 2007-08-27 | AGREEMENT STATE REPORT FROM WISCONSIN - LOSS OF TWO PALLADIUM-103 SEEDS RSO telephoned DHFS July 31, 2007. "The RSO notified DHFS by telephone of the possible loss of two Pd-103 implant seeds. The two seeds were unaccounted for following a July 16, 2007 prostate seed implant procedure. "During the procedure, the Physicist was making the strands using the BARD QuickLink system. About half way through the case he made a relatively long link. When the authorized User tried to load this link it was easily traveling through the implant needle so he retracted it and emptied the entire strand on the OR table backwards through the needle. A new link was made and properly implanted into the patient. Because they needed to use nearly all the ordered seeds for the procedure, the Physicist attempted to take apart the problem link using a pair of tweezers. This required some force to separate the links and seeds. While doing this at least two of the links separated and 'flew' off the table. The past experience with seeds falling in the operating room was that they were relatively easy to find immediately post procedure with the survey meter, so they completed the implant. The on-going inventory indicated there would be 5 leftover seeds. Multiple surveys of the operating room resulted in the recovery of 3 seeds. Surveys of all bed linens were conducted, no additional seeds were located." The patient will be returning to the facility for routine post implant CT imaging. The implant seed count will be repeated at that time. Event Report ID No.: WI070015 * * * RETRACTION ON 08/27/07 AT 1005 EDT FROM LEOLA DEKOCK VIA EMAIL TO MACKINNON * * * "DHFA has received additional information from the licensee. The patient returned to the facility for routine post implant imaging. The implant seed count was repeated at that time. The seed count performed at the time of the implant indicated 115 seeds had been implanted. The additional imaging has identified the presence of 117 seeds." R3DO (J. Lara) & FSME (C. Flannery) notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-08-03
43538 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-07-31 09:30 | 2007-07-31 13:39 | 2007-07-31 | OFFSITE NOTIFICATION DUE TO SMALL HYDRAULIC FLUID SPILL IN INTAKE BAY "OIL SHEEN IN THE PLANT FOREBAY "At 0930 plant personnel reported an oil sheen in the plant Forebay at the Intake Structure. The source was hydraulic oil from a small boat used to harvest and remove Milfoil [ biological plant; marine life] from the Forebay. Actions were initiated in accordance with plant procedure RWI-007, Spill Prevention Control and Countermeasures Plan. The volume of the spill was approximately one (1) gallon. The spill was stopped, contained, and clean-up efforts are in progress. "At 1100 the National Response Center was notified of the hydraulic oil spill along with other Alabama State and local agencies. "This event is reportable as a 4-hour non-emergency notification in accordance with 10 CFR 50.72(b)(2)(xi) as an event or condition related to protection of the environment for which notification to other government agencies was made. "The licensee has notified the NRC Senior Resident Inspector." Specifically, the licensee notified the Alabama Department of the Environmental Management, Alabama Emergency Management Agency, and Limestone County Emergency Management Agency. | 95 | 100 | 100 | 95 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-07-31
43537 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-07-31 00:51 | 2007-07-31 05:16 | 2007-07-31 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On 7/31/07 at 0051, the High Pressure Coolant Injection (HPCI) system was declared inoperable. The HPCI valve quarterly IST was in progress and the BJ-HV-8278 HPCI to Feedwater injection valve failed to respond to an open signal during stroke timing. "Loss of the HPCI system is reportable under 10CFR50.72 (b)(3)(v) as loss of a single train safety system required to mitigate the consequences of an accident. No additional Emergency Core Cooling Systems are inoperable. The D Safety Auxiliary Cooling System (SACS) pump is inoperable for motor replacement." The licensee is in a 14 day Hot Shutdown LCO. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-07-31
43536 | 0 | US EPA |  |  |  |  | 2007-07-30 16:25 | 2007-07-30 16:25 | 2007-07-30 | MISSING/LOST NICKEL-63 15 MILLICURIE SOURCE The Radiation Safety Officer (RSO) for The United States Environmental Protection Agency located in Cincinnati, OH reported they are missing a 15 millicurie Ni-63 source. The source was last seen December 01, 2006 when its 6 month leak test was performed. After the source was leak tested, the source was placed back in an unlocked drawer, where it has been kept since December 2001. The source was located below the HP Model # 5890 Series II Gas Chromatograph in which is it was used. The RSO said that they have been looking for the missing source since early June and they have been unable to find the source. The RSO said that anybody working for the US EPA in their building can enter the room in which the source was stored. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-07-30
43535 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2007-07-17 10:00 | 2007-07-30 14:30 | 2007-07-30 | AGREEMENT STATE REPORT - SIX LOST PALLADIUM - 103 SEEDS The following information was received via e-mail: "This is notification of an event in Washington State as reported to the WA Department of Health, Office of Radiation Protection. "STATUS: Update/Closed "Licensee: Swedish Medical Center "City and State: Seattle, Washington "License Number: WN-M008-1 "Type of License: Broad, Medical "Date and time of Event: July 17, 2007, about 10 am. "Location of Event: First Hill Campus, Operating Room, Seattle WA. "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "The licensee reported that beginning at 7:30 am on July 17, 2007; they administered 96 of 102 Palladium-103, prostate cancer therapy seeds. The 6 remaining seeds were counted and placed in a glass storage vial. The vial was labeled and put into a leaded storage container and then placed in the procedure room source storage area. "At 10 am, it was noted that only a single storage vial was present where two were expected since two cases had been completed by that time. The rooms, waste containers and other items and adjacent areas were searched and surveyed. A survey of the biohazard storage room was also conducted with no readings above background detected at any of the locations. Others involved with the implants searched and were also unable to find the seeds. "At 2:30 pm the RSO was notified. Another search and survey with a Ludlum Model 2221 scaler/rate meter using a model 44-3 probe was conducted at that time. An on site search through the trash compactor of approximately ¼ of the total waste in the compactor was also unsuccessful at finding them. The staff reviewed the implant records and determined that 6 seeds were still missing. At 8:50 pm, the RSO stopped the search and declared the seeds lost. At approximately 9:20 pm, the RSO transmitted an electronic notification to Washington DOH regarding the 6 missing prostate seeds. "On July 18, 2007, at 8:30 am, the RSO learned the majority of the linens from the previous day's procedure were still on the loading dock. The RSO had the linen carts segregated and conducted a search and survey. The RSO completed this search and did not find the seeds in the linens. The off site laundry facility was contacted. The laundry facility manager indicated that no containers were found and they would be on the lookout for such a container. "After reviewing the timeline and interviewing staff regarding the events, the RSO has determined the cause of the event was inattention to detail and human error on the part of the staff responsible for seed count and reconciliation. "An analysis of the seed count and reconciliation process indicates that keeping the unused seeds in the procedure room until all cases for the day have been completed may have contributed to this event. The RSO has immediately required that at the completion of each individual procedure the unused seeds are removed from the procedure room and an independent count of the seeds conducted. This is to be performed before the next case occurs to allow immediate survey of the procedure room in the event the seed count cannot be reconciled. The RSO also has stipulated that trained staff must be present for all procedures while seeds are in use. "The RSO has scheduled training for July 26, 2007 to review this event with all operating room staff involved with this procedure. The RSO will also review the procedural changes that have occurred as a consequence of this event. Immediately contacting the RSO will also be emphasized to other users of radioactive material at their periodic radiation safety training and to new users during their orientation. "The department considered the licensee to have made every reasonable effort to locate the seeds. Therefore the department did not conduct an on-site investigation. "Notification Reporting Criteria: WAC 246-221-240 Reports of Stolen, Lost, or Missing Radiation Sources . "Isotope and Activity involved: Palladium-103 seeds (six), 1.08 mCi/seed average. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): No "Lost, Stolen or Damaged? (mfg., model, serial number): LOST: Six Palladium-103 therapy seeds (no SN's), TheraSeed model 200 , manufactured by TheraGenics, 1.08 mCi/seed average, total of 6.48 mCi. "Disposition/recovery: Irretrievably lost, no recovery expected. "Leak test? N/A "Vehicle: N/A. "Release of activity? Other than the loss of the 6 seeds, none. "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: N/A "Exposure (intended/actual): consequences: None expected. "Was patient or responsible relative notified? No. "Was written report provided to patient? No. "Was referring physician notified? Yes, on July 18, 2007. "Consultant used? No. Washington Report: WA-07-068 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2007-08-05
43534 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-07-28 16:57 | 2007-07-28 19:24 | 2007-07-28 | OFFSITE NOTIFICATION TO FIRE DEPARTMENT "At 1605 hours on 7/28/07, an offsite breaker in the Beaver Valley Power Station Switchyard developed a failed 'B' phase which resulted in a fire and a subsequent 'B' phase insulator failure. Station fire brigade personnel were dispatched. Offsite assistance was requested at 1657 hours. The fire was extinguished at 1747 hours. The offsite fire department left the site at 1806 hours. "The circuit containing the failed breaker is associated with a local steel manufacturer and is not a feeder to Beaver Valley Power Station. This is a 4 hour reportable event per 10CFR50.72(b)(2)(xi), Notification to Offsite Governmental Agencies. The operation of BVPS Unit 1 plant systems are not affected by this event. At BVPS Unit 2, the non safety related station air compressors tripped during this event. A backup air compressor was manually started. These compressors were reset and restarted locally without impacting the operation of Beaver Valley Unit 2. "No EAL criteria was met for this event." The licensee intends to issue a press release. The NRC Resident Inspector has been notified | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-07-28
43533 | 0 | THYSSENKRUPP WAUPACA |  |  |  |  | 2007-07-25 20:00 | 2007-07-28 11:32 | 2007-08-02 | DAMAGED LEVEL GAUGE The licensee (a foundry) reported damage to a level gauge (Texas Nuclear/Thermal Fischer Scientific containing a 100 millicurie source) due to a loss of area cooling. The cooling was lost when a unrelated fire damaged a water cooling pump in another part of the facility and radiant heat from the foundry process apparently caused damage to lead shielding around the gauge. The damage was discovered when the gauge started reading erratically. Investigation into the erratic level reading revealed a high radiation level in the vicinity of the gauge. The area in the vicinity of the gauge was cordoned off and assistance from the gauge manufacturer was requested. Shielding on one of the gauges was found to be partially melted and was assumed to have occurred when cooling in the area was lost. No contamination or damage to the source took place and no overexposure occurred. The damaged gauge and another gauge in the area were both removed and packaged for shipment back to the manufacturer for repair. * * * UPDATE AT 1347 EDT ON 8/2/07 FROM GARY GREUBEL TO S. SANDIN * * * Two gauges, S/N B3224 and B3223, approximately 8 feet apart were involved in the above incident. Each gauge contained a 100 mCi Cs-137 source. Both gauges have been packaged and are awaiting shipment to the manufacturer. Notified R3DO (Orth) and FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | IN | MAT | [5 empty] | 0 | 2007-07-28
43532 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2007-07-27 14:15 | 2007-07-27 17:02 | 2007-07-27 | AGREEMENT STATE REPORT - FAILURE OF SOURCE TO RETRACT The State provided the following information via email: "ODH Bureau of Radiation Protection received a phone call from Varian Medical Systems at approximately 3:15 PM EDT regarding a situation which had occurred at a customer's location (St. Elizabeth Hospital in Youngstown, Ohio). The incident occurred at approximately 2:15 PM EDT. A Varian technician was performing maintenance on a Gamma Med Model 12i HDR unit, with the source extended into a shielded safe. During the maintenance action the technician disconnected a nylon tube that was part of the source wire travel path. This action caused the retract mechanism in the unit to energize, retracting the source wire from the safe, exposing approximately 8 inches of the source wire and the source end. The source is approximately 9.5 Curies of Iridium-192. "Varian personnel believe that the disconnection of the nylon tube reduced the tension on the source wire, causing the park switch to no longer sense the presence of the wire, and energizing the retraction mechanism, which then pulled the source from the safe. The technician realized that something was not right when he heard the drive mechanism energize, and exited the treatment room immediately. Varian estimates the exposure to the technician as approximately 15 mrem, based on the activity of the source and time required to exit the room. The technician was not wearing his dosimetry at the time the incident occurred. "Varian is sending an additional engineer to the customer location to assist with source recovery, with an estimated arrival time between 7:00 PM and 8:00 PM EDT. Varian has set-up a mock scenario at their office with the same model unit in the same configuration as what is present at the customer site. They have performed run throughs of source recovery, and have determined that the most effective method of retrieval will be to grasp the source wire with 18" forceps and then guide the source wire back into the shielded safe. They expect the evolution to take 5 - 8 seconds with an estimated whole body exposure of 25 mrem or less." Ohio report # 2007-046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2007-08-01
43531 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2007-07-26 16:30 | 2007-07-27 16:27 | 2007-07-27 | FIRE IN THE PELLETING AREA "On 7/26/07, an attempt to extinguish a small grease fire with water was observed by a Westinghouse engineer. This is a violation of IROFS-PELFIRE-902 (also identified as IROFS-BWR-107), which restricts the use of water for fire suppression in pellet/rod areas. The fire observed was located beneath the Line 4 polypak lift. The fire was estimated to be approximately three feet by three feet in area and approximately 2 inches in height. Three polypaks with an unknown quantity of material were observed on the lift at the time the fire occurred. "The fire was believed to have been started by weld sparks originating from overhead work being performed by construction workers. The water used to extinguish the fire was delivered to the fire in hardhats and welding masks that the construction personnel had at their immediate disposal from a nearby hand-wash basin. The total quantity of water involved was estimated to be a maximum of one gallon. "Notification is being made based on the potential for 'Any natural phenomenon or other external event, including fires internal and external to the facility, that has affected or may have affected the intended safety function or availability or reliability of one or more items relied on for safety', reference Appendix A, Section (b)(4) to Part 70 of 10CFR70. "Safety Basis: At no time was the integrity of nearby special nuclear material (SNM) containers challenged. No SNM was involved with the fire. None of the water involved in putting out the fire came into contact with SNM. Even if fissile material had been present during the fire, and that water had contacted and mixed with the fissile material, the quantity of water was limited to approximately one gallon. The minimum quantity of water necessary to challenge the normal case conditions involving homogenous SNM is 3.8 gallons. It should also be pointed out that the quantity of water was limited by the ability of the construction personnel to apply the water using their improvised method and further limited by the source of the water. (The intention of PELFIRE 902 is to prevent the large, uncontrolled addition of water as with firefighters wielding fire hoses attached to an effectively infinite source.) "Summary of Activity: All construction work has been halted pending a stand-down meeting with personnel. The event was documented in the plant Corrective Action Process (CAPs #07-208-C007). "Conclusions: Problem was self identified by Westinghouse Operations personnel. The fire was put out immediately and there was no challenge to the integrity of nearby special nuclear material containers. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. A causal analysis will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | NAT PHENOM AFFECTING SAFETY | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(4) |  |  |  | 0 | 2007-07-27
43530 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2007-07-26 09:00 | 2007-07-27 15:26 | 2007-07-27 | AGREEMENT STATE REPORT - MALFUNCTION OF RADIOGRAPHY CAMERA SAFETY EQUIPMENT The State provided the following information via facsimile: A licensee technician was performing an exposure with a INC Model IR-100 (Source: Ir-192 source strength: 41 Ci) on a test coupon in the company shooting room. When the technician attempted to retract the source the safety latch popped up to indicate that the source was in the shielded position. The technician approached the camera with a survey meter. The technician, thinking the source was retracted, turned the key to lock the camera. When the technician surveyed the front of the camera, the survey meter went off scale. The technician realized there was a malfunction exited the area and contacted the Assistant RSO (ARSO). The ARSO and the technician determined that the source was still in front of the safety latch and not shielded. The licensee called the manufacturer for guidance. The licensee freed the source, and after several attempts was able to engage the safety latch and lock the source in the stowed position. The camera has been taken out of service and is being shipped to the manufacturer for repair. Both the technician and the ARSO received between 2-3 mR during the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2007-08-01
43529 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2007-07-27 12:00 | 2007-07-27 13:13 | 2007-07-27 | OFFSITE NOTIFICATION DUE TO HYDRAZINE SPILL "At 1200 EDT, the following off-site agencies were notified of 0.68 gallons of 35 weight-percent Hydrazine spillage into a concrete berm: National Response Center, State Emergency Response Commission, and Florida Department of Environmental Protection. The amount of Hydrazine spilled was greater than the reportable quantity of 0.34 gallons of 35 weight-percent hydrazine. As stated above, the leak was fully contained in its designated containment area and none reached the environment. The leak has been identified and stopped, area has been cleaned. Notification is due to 10CFR50.72 (b)(2)(xi), due to notification of off-site agencies." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-07-27
43528 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-07-26 10:30 | 2007-07-27 09:42 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * UNANAYLZED CONDITION - UNFAVORABLE GEOMETRY CONTAINER "On 7/26/07 at approximately 10:30 AM, an unusual condition occurred in the outside alley west of [DELETED]. During movement of a portable Raschig ring vessel from the Recovery [DELETED] to the Central Storage [DELETED], the vessel tipped over, spilling its contents. The vessel contained uranium-[DELETED] waste solution at less than [DELETED] gram U-235 per liter. "In order to transfer the portable Raschig ring vessel outside of a radiologically controlled area, the vessel was covered by two 55-gallon plastic bags in order to contain contamination within the vessel as it was being transferred outside the radiologically controlled area. The vessel overturned creating an unfavorable geometry container via the outer 55 gallon plastic bag that collected solution from the spill separately from the Raschig rings. "The solution from the portable Raschig ring vessel was sampled and found to have a concentration of [DELETED] grams U235 per liter. The solution that collected in the outer bag was held at a [DELETED] height approximately [DELETED]. The inner bag also contained some solution, but it also contained Raschig rings, and therefore was not of immediate concern. Although the configuration of the tipped over vessel created an unfavorable geometry, due to the low concentration of the solution and the [DELETED] height, there was little risk of a criticality accident. The vessel was outside the process area when it tipped over, so there was no opportunity that additional uranium-[DELETED] solution could have been collected in the bags or the vessel. "Previous safety analyses considered the issue of whether a spilled vessel could preferentially separate high concentration solution from the Raschig rings in a Raschig Ring vessel, leaving solution in the vessel without the poisoning effect of the rings and concluded that event was not credible. In this event, however, the spilled solution was preferentially separated from the Raschig rings though the concentration remained low. Based on these facts, this condition that was not fully analyzed in the Integrated Safety Analysis (ISA). "The immediate corrective action was to suspend operations associated with the vessel, isolate the spilled material, and clean up the spill. Corrective actions to prevent recurrence are being developed. Since this event was not fully analyzed in the ISA, transfer of bagged Raschig ring vessels containing uranium-[DELETED] solutions shall not occur until appropriate evaluations are performed. "The operators involved in the event were Fitness For Duty tested. BWXT is making this 24 hour report in accordance with 10 CFR 70.61, Appendix A, (b)(1). "The NRC Resident Inspector has been notified." * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-05-11
43527 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-07-26 | 2007-07-27 09:05 | 2007-07-27 | PART 21 NOTIFICATION - FAILURE OF ENERSYS (EXIDE) BATTERY In March 2005, battery cell internal resistance for an EDG battery bank revealed five cells with abnormal resistance. "There was one cell for which no reading could be obtained and was replaced immediately. A second cell had a reading that was nearly four times the average of the associated string and was subsequently replaced as a proactive measure during the EDG maintenance outage. Three (3) other cells were noted with higher than average readings that are not considered to be operability concerns. In total, five (5) cells out of a total of 240 were found with higher than expected internal resistance values." The failed battery was destructively tested revealing significant corrosion within the battery. The unit-2 batteries have been replaced. The unit-1 batteries will be replaced in the fall 2007 outage. Manufacturer: Enersys (Exide) Model: 3CA-5 Serial Number: beginning with 05 The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 21.21 |  |  |  | 0 | 2007-07-27
43526 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-07-26 17:06 | 2007-07-26 21:11 | 2007-07-26 | ACCIDENT MITIGATION REPORT - UNIT 2 HPCI ISOLATED DUE TO SMALL BORE STEAM LEAK "At 1706 hours on 07/26/07, a through wall leak was identified on the U2 High Pressure Coolant Injection (HPCI) Inlet Drain Pot drain piping. This piping is ASME Code class 2 piping and as required by the Technical Requirements Manual the piping was isolated which resulted in isolation of the U2 HPCI System. U2 HPCI was declared inoperable. This event is reportable under 10CFR50.72(b)(3)(v)(D). Piping repair preparations are in progress." During the performance of operator rounds, the licensee noticed a puddle of fluid on the deck and wet lagging overhead. Upon removal of the lagging, the licensee noticed a small steam leak in a 1" small bore line. The licensee is currently in a 14 day LCO under technical specification 3.5.1 F(1) and F(2). The licensee is currently developing a work package to repair or replace the line. The licensee notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-07-26
43525 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-07-26 09:02 | 2007-07-26 16:32 | 2007-07-26 | UNANALYZED CONDITION - FLOOD DOORS CLOSED CAUSING A POTENTIAL LOSS OF BOTH VITAL SWITCHGEAR "At 09:02 on 07/28/07, an outplant operator identified that DOOR-18, which is a normally open fire door, had closed due to a failed fusible link. With this door closed, the pathway for a potential flood due to a high energy line break (HELB) is blocked therefore closing off a drain path for the water. This represented an unanalyzed condition where both divisions of essential switchgear could be impacted. As a result, both divisions of essential switchgear were declared inoperable and Technical Specification LCO 3.0.3 was entered. At 09:55 on 07/26/07, the closed fire door was restored to the open state. Both divisions of switchgear were declared Operable and LCO 3.0.3 was exited. No system actuations occurred as a part of this event." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-07-26
43524 | 0 | US ARMY |  |  |  |  | 2007-07-24 | 2007-07-26 16:12 | 2007-07-26 | FAILED SOURCE SHIELD LOCK ON MOISTURE DENSITY GAUGE "The Tester, Density and Moisture (Soil and Asphalt) Nuclear Method Campbell Pacific Model MC-1 (CCE), NSN 6635-01-030-6896, Serial Number M17112090, is assigned to the 980th Angering Battalion at Austin, TX. The MC-1 Tester had on manufacture (in 1977) 10 mCi of Cesium 137 and 50 mCi of Americium 241/Be. The sources are solid, sealed, and double encapsulated. The MC-1 Tester is licensed through an Army NRC license 21-01222-05, issued to the US Army TACOM Life Cycle Management Command (LCMC), located in Warren, MI. "The tester was used in Iraq in 2005 and was shipped back to the unit location in Texas in 2006. It is unknown, if the tester had any mechanical difficulties in Iraq . The tester had received servicing through CPN International, Inc. on June 19, 2003. [Servicing included replacing] standard wear items such as gaskets and the handle. Also, the electronic assembly was bench tested with the two detectors, and the body of the tester is cleaned with the guidetube and rod assembly cleaned/lubed. The tester was also calibrated and leak tested "The tester hasn't been used since its use in Iraq . The tester has been in storage with the only interaction being physical inventories, radiation surveys of the storage and leak tests of the radioactive sources. "On 24 July 2007, the undersigned received an e-mail (after-hours) indicating that the referenced tester was inoperative with an inoperative handle lock, that wouldn't engage. The e-mail asking for disposition of the tester. Confirmation of the information was made with two Army personnel doing internal radiation audits of Army radiation programs, who were visiting the unit. The Army personnel were told on their visit, that there was some difficulty with the locking mechanism. They were told, that the tester was hard to unlock and that they (the unit) didn't lock the handle for this reason. "The tester is inside its transport case, locked inside of a lead lined box, inside of a locked connex container, which is locked inside a gate at the unit location. The tester sources to include rod remain inside the tester housing and no other apparent tester deficiencies outside the lock mechanism has been observed. The shutter is in place and closed. The tester will not lock in the various positions (i.e. safe, 6 inch, 8 inch and 12 inch). When the lock button is pushed in, it springs out. The lock could not be locked with the key. There are no known personnel exposures. The tester sources were last leak tested on July 2, 2007, which showed no leakage. "The only personnel having access to the keys and the tester is the Local RSO. This ensures that the tester is not used. The transport case containing the tester is also now locked. "It is planned to transport the tester back to the manufacturer for disposition. The tester has been coded as H for unserviceable. Instructions were provided to the unit today to perform a wipe test of the shipping container, prepare the tester for shipment, and to ship it to the manufacturer. "Also, a reminder e-mail was sent to the unit and to various Army Commands of the requirement to report tester safety defects immediately to TACOM LCMC Warren, MI. This e-mail was sent again today (July 27, 2007) as it was sent out on July 5, 2007." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-07-26
43523 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-07-26 08:50 | 2007-07-26 11:47 | 2007-07-26 | OFFSITE NOTIFICATION The licensee made offsite notifications to law enforcement agencies in regards to a security event at the site. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 1 | 2007-07-26
43522 | 0 | LOUDOUN HOSPITAL |  |  |  |  | 2007-07-24 15:30 | 2007-07-25 16:02 | 2007-07-25 | LOST I-125 SEED The licensee was performing a prostate seed case requiring 12 loose I-125 seeds with an activity of .34 mCi each. The seeds were assayed in the licensee hot lab and transported to the operating room for the procedure. After completion of the procedure only 11 seeds were accounted for. The RSO was notified. The seed was verified to not be in the patient. The licensee completed search for the material throughout the operating room and hot lab with no success. The licensee contacted the NRC Region 1 representative. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-07-31
43521 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-07-23 | 2007-07-25 14:17 | 2007-07-25 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA STUCK CONTROL ASSEMBLY The State provided the following information via facsimile: "During a routine maintenance inspection it was noted that the control assembly [of the radiography camera] would not project or retract the drive cable. After an investigation, it was found that 2 of 4 'small gear housing' screws were interfering with the gear teeth of the large gear. "The two screws that interfere with the operation of the large gear only interfere when they are loose in the housing. Since the outside of the small housing is where the handle for the controls is kept, the screws inevitably come loose over time and use. Since the screws are applied in the housing there is no way to tighten the small housing screws with out disassembling the control arm assembly. "A small design change is needed on these 4 small housing screws to prevent a source from stuck out in the shielded position." Equipment involved: SPEC 150, (no serial number provided), Source: Ir-192 (no source strength provided), Control assembly: SPEC 'Red-Red' conduit control. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-07-30
43519 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2007-07-25 04:30 | 2007-07-25 06:52 | 2007-07-25 | SOURCE STUCK OUTSIDE OF RADIOGRAPHY CAMERA Team Industrial was performing radiography at the Sinclair Refinery in Tulsa, Oklahoma approximately 25 feet above the ground. During the exposure, the camera fell approximately 3-4 feet onto scaffolding. The fall damaged the ball joint connecting the source to the retraction wire i.e. the source will not retract. The RSO has contacted their corporate office and is contracting with a source retrieval company. The area has been secured and cordoned off. Inability to enter this area does not affect continued refinery operation. The radiography technician received a dose of 40 mR during this incident. Source: 27 Ci Ir-192 Camera: Amersham 880D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-07-30
43518 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-07-24 16:45 | 2007-07-24 22:05 | 2007-07-24 | HIGH PRESSURE COOLANT INJECTION INOPERABLE DUE TO FAILED POWER SUPPLY "At 1645 on 7/24/07 during the transfer to the Normal Power Supply of the 3A 250 RMQV Board upon completion of scheduled maintenance. Unit 3 High Pressure Coolant Injection system received a 120 VAC Power Failure and was declared inoperable. 120VAC HPCI power is supplied by the Unit 3 ECCS Div 2 Analog Trip Unit Inverter. The Inverter lost power during the 250vdc board transfer and was not able to be restored to service. "Investigation is still continuing on the failure of the Div 2 ECCS Inverter. "This event is reportable as an 8-hour Non-Emergency Notification in accordance with 10 CFR 50.72 (b)(3)(v)(B) as; 'Any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to: Remove Residual Heat' ; and 10 CFR 50.72 (b)(3)(v)(D), 'any event or condition that at the time of discovery could have prevented the fulfillment of the Safety Function of structures or systems that are needed to; mitigate the consequences of an accident.' "This event also requires a 60 day written report in accordance with 10 CFR 50.73 (a)(2)(v)(B) and 10 CFR 50.73 (a)(2)(v)(D). "NRC EVENT # 43518 was reported to Mr. Kozal and the NRC Resident (C. Stancil) was notified at 1925 CDST on 07/24/07." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-07-24
43517 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-07-24 09:02 | 2007-07-24 19:51 | 2007-07-24 | PLANT EMPLOYEE TESTED POSITIVE FOR ALCOHOL DURING A RANDOM FITNESS-FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been revoked. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector was notified of this event notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.73 |  |  |  | 0 | 2007-07-24
43516 | 0 | LESTER COX MEDICAL CENTER |  |  |  |  | 2007-07-24 10:00 | 2007-07-24 14:15 | 2007-07-24 | MEDICAL EVENT - ADMINISTERED DOSE LESS THAN PRESCRIBED DOSE The treatment consisted of 3 fractionated high dose rate (HDR) brachytherapy procedures. The dose was prescribed by the physician at 5 millimeters from the surface of the cylinder, however, the dose was calculated at the surface of the cylinder. The HDR brachytherapy was administered at 5 millimeters as prescribed. Due to the discrepancy between the prescribed and calculated dose an under dose of the patient of over 4 Grays (Gy) resulted. The prescription was for an administration of 15 Gy. Only 10.3 Gy was administered. The physician is planning to add one more fraction to complete the intended treatment of 15 Gy. The patient will be informed of this misadministration. The licensee indicated that they will verify the prescription and the film prior to administration to insure consistency between the two. Additionally, when the dose distribution is plotted, the licensee will overlay the cylinder over the dose distribution to visually verify the dose. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-07-30
43515 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-07-24 02:56 | 2007-07-24 10:40 | 2007-07-30 | TECHNICAL SUPPORT CENTER VENTILATION INOPERABLE "During performance of the Technical Support Center (TSC) Ventilation System Operability Test, an outside air damper failed to close causing a failure of the TSC Ventilation System to attain the required 0.125 inches water column positive pressure. If an emergency condition occurs during the time the repairs are being made, plans are to utilize the TSC as long as radiological conditions allow. Procedure F3-6 ACTIVATION AND OPERATION OF THE TSC, section 7.6, directs TSC management to relocate TSC activities to a radiological safe area if necessary." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 07/30/07 AT 1449 EDT FROM MARK LOOSBROCK TO MACKINNON * * * Technical Support Center (TSC) Ventilation System is now operable. R3DO (Steve Orth) notified. The NRC Resident Inspector was notified of this event update by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-07-24
43514 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2007-07-21 05:00 | 2007-07-24 09:57 | 2007-07-24 | AGREEMENT STATE REPORT INVOLVING EQUIPMENT DAMAGE DUE TO A VEHICLE ACCIDENT The following information was provided via email: "At approximately 5:00 AM on Saturday morning the Division's Radiological Duty Officer (RDO) was notified by the Illinois Emergency Management Agency Communications Center that a nuclear gauge was involved in a vehicular accident at the 3rd Street on-ramp at I-70 (E) in East St. Louis, Illinois. The RDO then contacted the responsible licensee, Fred Weber, Inc., and talked to [DELETED], the licensee's Radiation Safety Officer, who was at the scene. "The RSO reported that the portable gauge had been struck at high speed by a car which had crossed into the marked and barricaded construction zone on the entrance ramp to the interstate. As a result the gauge had been destroyed into many parts. One of those parts, the source rod containing Cs-137 in a special form capsule had become separated from the gauge and its shielded housing. Using a hand held Geiger counter, [the RSO] performed wipe tests on the gauge base containing the Am-241 source and the Cs-137 source rod and found no removable gross contamination. [The RSO] had also contacted the manufacturer, Troxler for assistance and instruction in resolving the scene. "After discussion with the Agency's RDO, [the RSO] was able to place the source rod in its original shielding and secure the rod into the shielding with tape. He then placed the base of the gauge and the source rod, with the shielding, in its Type 'A' transport case and filled any voids with sand to provide additional shielding and stabilization. Radiation readings taken by [the RSO] from the side of the case exhibited normal levels. "The RDO then contacted the St. Clair County Emergency Services [DELETED]. [DELETED] of the Hazardous Materials unit were enroute to the scene at the time of that call. When they arrived, they performed confirmatory radiation surveys with their radiation instrumentation and noted no contamination on the roadway. Radiation levels of the transport case were also determined to be at normal levels. Surveys of [the RSO] noted no contamination. [The RSO] transported the gauge back to their storage site in Maryland Heights, MO. Arrangements were made for [the RSO] to contact the gauge manufacturer for further instructions with regards to returning the device for repair/disposal. "[The RSO] confirmed he would send the required written report as well as notify the U.S. Nuclear Regulatory Commission as the firm is also an NRC licensee. Pending receipt of that report and successful disposition of the damaged gauge, this item remains open. This event was reported to the U.S. NRC Operations Center on July 24 and assigned event number 43514. "Corrective Actions: Action Number: 1 Corrective Action: EQUIPMENT RETURNED TO MANUFACTURER FOR REPAIR OR DISPOSAL "Keywords: DEVICE INVOLVED IN ACCIDENT "Source of Radiation: Source Number: 1 Form of Radioactive - SEALED SOURCE Source Use: PORTABLE GAUGE Manufacturer: AMERSHAM Model Number: Serial Number:77-5535 Radionuclide or Voltage (kVp/MeV): CS-137 Activity: 0.008 Ci or 0.296 GBq Problem with Source: NONE Source Number: 2 Form of Radioactive SEALED SOURCE Source Use: PORTABLE GAUGE Manufacturer: AMERSHAM Model Number: Serial Number: 78-2987 Radionuclide or Voltage (kVp/MeV): AM-BE Activity: 0.040 Ci or 1.48 GBq Problem with Source: NONE "Device/Associated Equipment: Device Number: 1 Device Name: PORTABLE GAUGE Manufacturer: TROXLER Model Number: 3440 Serial Number: 38181 Problem with Equipment: SHIELDING COMPROMISED "Reporting Requirements: Reporting Requirement: 32 IAC 340.1220(c)(2) - The Licensee shall notify the Division within 24 hours in the event equipment is disabled or fails to function as designated. Mode Reported: Telephone" The licensee whose principal business location is in Maryland Heights, MO is also licensed and maintains storage locations in Illinois due to the volume of work performed in that state. Illinois Report ID: IL070041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-07-27
43513 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2007-07-20 08:00 | 2007-07-23 15:36 | 2007-07-23 | AGREEMENT STATE - STUCK RADIOGRAPHY CAMERA SOURCE "On the morning of July 20, [DELETED], RSO for McNDT, called. He was taking some radiographs while inside a water tower in Darien, IL and the magnetic cable stand used to hold the film cartridge fell over onto the cable and crushed the guide tube. He reported that he could not retract the source to the shielded position in the camera. The source is a 34 Ci Ir-192 source; the camera is a QSA 660B. The scene was secured and under constant oversight by the RSO. [DELETED] reported that there have been no overexposures or any injuries. [DELETED] estimated that some 6 inches of guide tube used to position the radiography source had been crushed/deformed by equipment that had been used to position the radiography source 8 feet high up against the wall of the tank. The guide tube was then stretched straight along the floor of the water tower which is approximately 50 feet in diameter. The damaged section of the tube was approximately 30 inches from the end of the 14 foot length of guide tube. A 'hot zone' barrier required by regulations was established around the water tower before the radiography job was begun. Dose rates around that zone were less than 60 milliR/hr. The water tower is near the intersection of Plainfield and Cass Avenues in Darien behind a retail shopping area. As the area is a construction area, there is fencing surrounding the work site so control of the scene has been relatively easy to maintain. "Upon arrival at the scene, the investigators added bags of lead shot to the area where the source was determined to be. The drive cables and crank were then physically secured with the camera and a strong force was applied to the cranking mechanism. This resulted in the successful return of the cable with the Ir-192 source back into the radiography camera. Afterwards, the guide tube was surveyed and found to be free of contamination. The camera ports were likewise monitored with negative removable contamination present. The device (AEA QSA, Inc. model 660B w/ S/N B2020) has been secured and tagged as out of service until it can be returned to the manufacturer for source exchange and recertification. Surface dose rates on the radiography camera were at the expected 5 to 10 milliR/hr. Total exposures to personnel as measured by pocket dosimeters were very low (70 milliR to the RSO, 60 milliR to [DELETED] and 55 milliR to [DELETED]). [DELETED] was advised of our expectations for return of the potentially damaged source cable and the need to send in his own dosimetry in for immediate analysis to confirm the measured exposure prior to our staffs' arrival." Illinois Item Number: IL070040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-07-26
43512 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2007-07-23 07:00 | 2007-07-23 10:58 | 2007-07-23 | MARYLAND AGREEMENT STATE REPORT - STOLEN TROXLER At 1000 EDT on 07/23/07, the licensee notified the State of Maryland of a Troxler moisture density gauge that was stolen from a trailer at a temporary job site located at 11540 Berry Road, Waldorf, MD. The gauge is a Model 3430, serial # 22355, with an 8 millicurie Cs-137 source and a 40 millicurie Am-241:Be source. While the gauge was in storage, the source rod was locked, the gauge case was locked, and the gauge was stored in a locked trailer on the temporary job site. The local police have been notified and are investigating. The State of Maryland will issue a press release on 07/24/07 if the gauge is not recovered. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2007-07-26
43511 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-07-23 09:32 | 2007-07-23 10:00 | 2007-07-23 | TECHNICAL SUPPORT CENTER (TSC) OUTAGE FOR PLANNED MAINTENANCE "Planned preventive maintenance activities are being performed today (July 23, 2007) on the Hatch Nuclear Plant's Alternate Supply Breaker (5C) to the Diesel Generator Building Motor Control Center (MCC) (MPL # 1R24-S026). This MCC feeds the Technical Support Center (TSC) 480V AC distribution panel (MPL# 1R25-S102) which supplies power to the TSC HVAC. The work activities affecting the TSC are planned to be performed and completed expeditiously within one work shift (less than or equal to 6 hours). During this work activity the TSC HVAC system will be removed from service. "If an emergency condition occurs that requires activation of the Technical Support Center during the time these work activities are being performed, it will take no more than three hours to return the equipment back to functional status, dependent on the stage of the work activity at the time the emergency occurs. Plans are to utilize the TSC for any declared emergency during the time these work activities are being performed, as long as radiological conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev 1 since this work activity affects an emergency response facility for the duration of the evolution." The licensee informed the NRC Resident Inspector. * * * UPDATE ON 07/23/07 AT 1952 FROM T. SPRING TO MACKINNON * * * "Update: On 07/23/07 at 1935 EDT, the HVAC System for the TSC was returned to functional status following the replacement of the alternate supply breaker to MCC 1R24S026. 1R24S026 was energized restoring power to the TSC HVAC System." R2DO (M. Lesser) notified. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-07-23
43510 | 0 | MATTINGLY TESTING SERVICES |  |  |  |  | 2007-07-20 17:00 | 2007-07-20 21:00 | 2007-07-20 | RADIOGRAPHY CAMERA SOURCE STUCK IN GUIDE TUBE A manager from the licensee's company called to inform the NRC of a problem involving a radiography camera with a source stuck in the guide tube. The radiography camera, an INC IR-100 with a 97 curie Iridium-192 source, was being used at the Cenex Refinery in Laurel, MT. The camera was perched at an elevated location on an I-beam when the collimator fell and put a sharp bend in the guide tube. The radiographer attempted to retract the source but was unable to get it past the bend. The radiographer left the camera and unretracted source in its work location to minimize his exposure to the source after ensuring that it was well secured. The radiographer established a 2 millirem boundary around the camera location and then attempted to call the RSO. The radiographer also called a company manager who responded to the site and subsequently contacted the NRC. Currently there is no health and safety concern because the area is cordoned off and the location of the camera is in a part of the refinery that is being expanded (new construction) so there is no concern about refinery worker exposure. The RSO is not at his home and cannot be reached by cell because of the spotty cell coverage in many parts of Montana. The licensee plans to maintain 24 hour around the clock coverage of the boundary and camera until expertise can be brought to the site to recover the source or place it in a condition where it can be removed from its current location without excessive exposure. There are currently 5 employees from the company onsite to maintain this coverage. The licensee will continue to attempt to contact the RSO but the worst case condition may require coverage to be extended until normal working hours on Monday morning (7/23) when the RSO comes back to town. The licensee is also trying to contact the RSO of a competitive radiography company in the area that could lend assistance. The licensee's representative plans to brief the NRC in approximately 12 hours on the status of their efforts to secure the source. * * * UPDATE FROM LICENSEE (FICEK) TO HUFFMAN AT 2300 EDT ON 7/20/07 * * * The licensee was able to fabricate a tool using a 15 foot section of conduit with a vice grip taped to the end. Using this tool, they were able to push the collimator up level with the camera and straighten the bend in the guide tube. The radiographer was then able to crank the source back into the camera. The source is now in its safe shielded position and has been secured in the company truck and the licensee is preparing to leave the site. The licensee did not know what level of exposure the radiographer received during this event but did not believe it was excessive. R4DO (Gody), R4 (Wert), and NMSS EO (Brach) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | MT | MAT | [5 empty] | 0 | 2007-07-20
43509 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2007-07-19 12:00 | 2007-07-20 17:28 | 2007-07-20 | AGREEMENT STATE REPORT FROM THE STATE OF NEBRASKA On 07/20/07 at 1445 CDT the Radiation Safety Officer for Becton-Dickinson Infusion Therapy System, Inc Pool Irradiator located in Broken Bow reported a component failure at the Pool Irradiator. The irradiator was operating on 07/19/07 when one of the totes carrying medical supplies to be sterilized became jammed in the irradiator. The alarm sounded as expected. The source of the Pool Irradiator went back to its shielded position, lowered back into the pool. The Control Panel for the pool irradiator did not indicate, light did not come on, that the source had gone back into the pool. The licensee went to the penthouse, above the irradiator pool, and found that there was no extra cable in the penthouse which indicated the source had gone to its safe position, entered the pool. Radiation readings taken in the penthouse also indicated that the source was in the pool. The licensee tried to unlock the door to enter the maze to unjam the tote but they were unable to unlock the door because the control panel indicated that the source had not gone to its safe position. The licensee then called MDS Nordion, manufacturer of the irradiator and owner of the irradiator fuel, and informed them of the problem. MDS Nordion informed them how to over ride the access system. After three tries they successfully over rode the access system, required 3 people at 3 different locations at the same time to over ride the system. After opening the access door 2 people with 2 separate radiation survey meters entered the maze. Normal background radiation levels were detected. It was found that the control switch indicating that the source was in its safe position was not in its correct position, down. The switch was replaced. As of 07/20/07 the Pool Irradiator is operating. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2007-07-25
43508 | 0 | OCEANEERING INTERNATIONAL |  |  |  |  | 2007-05-22 | 2007-07-20 17:28 | 2007-07-20 | POSSIBLE OVEREXPOSURE EVENT DURING RADIOGRAPHY IN GULF OF MEXICO Oceaneering International received a report from Landauer that two of their radiographers had May badge exposures of 5467 millirem and 5549 millirem (deep dose) respectively. The radiographers had been working on a pipe laying barge about 40 miles off the coast of Louisiana during the month of May when these potential overexposures occurred. Oceaneering International immediately stopped work of one of the radiographers. The other radiographer had already stopped working due to a personal injury. Interviews with the radiographers indicated that both individuals had removed their shirts during work on a hot day with their exposure badges still attached to the shirts The shirts could have been placed in a location that was near the radiography work and picked up the exposure. Both radiographers had self-reading dosimetry that was read and logged daily. The total May exposures logged on the self-reading dosimeters were 126 millirem and 147 millirem respectively. Oceaneering International is licensed under an Agreement State license from the State of Louisiana. This event has already been reported to the State of Louisiana and is under investigation by the State (See Agreement State Report EN#43481). However, after the RSO for Oceaneering International had discussions with NRC Region IV (Leonardi) about this event, the RSO decided to report the event to the Operations Center since the event occurred offshore and is under NRC jurisdiction at the time it occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2007-07-20
43507 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-07-19 14:32 | 2007-07-19 17:08 | 2007-09-04 | AGREEMENT STATE REPORT FROM THE STATE OF TEXAS EVENT: Radioactive Material (RAM) found - sealed License Number: "Unlicensed" "The agency received a call at 2:15 p.m. today (7/19/07) from DSHS Food & Drug Inspector, (DELETED) inquiring about four radiation devices found with 1994 inspection stickers on each of them. She said there appears to be some concern as of what company owns them and the facility they are located at. She gave me three names of possible companies, or owners: "I Q Distributors "Diversified Materials Services "Diversified Medical Services Inc. "The facility is located at: 2400 Central Parkway, Suite LP in Houston, Texas 77092. She is currently on location. "Agency Action Taken: Region 6 RAM Inspector to go to the facility as soon as possible to conduct incident investigation & identify sources." Texas Incident Number: I-8428 * * * RETRACTION FROM L. HANSON TO P. SNYDER AT 1657 ON 9/4/07 * * * The NRC received the following information from the Agreement State of Texas via facsimile: "On 08/23/07, the Agency received a telephone call from the individual who received the gauges from Kellogg Brown & Root, Inc. (KBR) & was given the following information: "The individual stated that on 03/03/06, he purchased a portion of the building at 2400 Central Parkway, Ste. L, Houston, Texas. The purchaser reported to the Agency that he was not aware that the portion of the building he just bought, Suite L, contained the alloy analyzers found by DSHS inspectors until he was recently contacted by the agency. He stated he thought he bought lab equipment only & was unaware that the building purchase included the alloy analyzers. The other suite, Suite P, is not owned by him & overseen by the initial individual contacted at the site by the agency's inspectors. He is not sure why this individual did not make the suite distinction with the inspectors nor contact him to let him know the building was being inspected. "He contacted the agency's general licensing acknowledgement (GLA) division & was given the following information: These devices with Fe-55 and Cd-109 sources and no longer issued a GLA so anyone can possess these devices if transferred by manufacturer/distributor. A transfer is allowed if the devices are transferred in their physical location, which occurred when he bought the building. "Additionally, the agency received documentation from the manufacturer that they removed the RAM sources from the two empty analyzers & shipped the analyzers back to KBR in 1997. The two analyzers which had very low-strength RAM sources were transferred in accordance with the above stated allowance. "The purchaser asked if the agency could give him information on how he could dispose of the analyzers. The agency responded by forwarding information to the purchaser for possible contacts who could assist him with disposal. "BASED ON THE ABOVE INFORMATION, THE AGENCY IS REQUESTING A RETRACTION OF THIS INCIDENT, SINCE IT IS NOW DEEMED NON-REPORTABLE." Notified R4DO (T. Pruett) and FSME (J. Davis). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-07-24
43506 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-07-18 15:50 | 2007-07-19 14:16 | 2007-07-24 | AGREEMENT STATE REPORT FROM THE STATE OF TEXAS "On 07/18/07 at 3:50 pm, the agency received a telephone call from (deleted), the Chief Tech for the licensee, reporting the misadministration of patient involving Thallous Chloride. The nuclear medicine tech reported that a patient was injected twice with a total of 4mCi of Thallous Chloride. "The licensee reported that the patient was informed the same day of the misadministration. "Licensee was informed that the 30-day report is due 08/17/07." Agency Action Taken: The licensee will submit the required written report within 30-days as per 25 Texas Administrative Code (TAC) 289.202(xx). Texas Incident number: I-8427 * * * UPDATE PROVIDED BY CINDY FLANNERY TO JEFF ROTTON AT 0741 ON 07/24/07 * * * This event (EN43506) has been reviewed and determined to NOT be a reportable medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-07-25
43505 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2007-07-18 15:15 | 2007-07-19 10:28 | 2007-07-19 | POSITIVE RANDOM FITNESS FOR DUTY TEST A licensed operator had a confirmed positive random fitness-for-duty test. The test sample was taken on 07/15/07 and the Medical Review Officer confirmed a positive test at 1515 EDT on 07/18/07. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 26.73 |  |  |  | 0 | 2007-07-19
43504 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2007-07-18 11:00 | 2007-07-19 09:39 | 2007-07-19 | AGREEMENT STATE REPORT - DEFECTIVE RADIOGRAPHY CAMERA The licensee provided the following information via email: "Licensee notified [Ohio] Bureau of Radiation Protection (BRP) at approximately 11:00 AM on 7/18/07. Licensee reported that an Ir-192 radiography source in the guide tube of a radiography camera could not be fully retracted. Source is housed in an Amersham Model 660B camera (Serial number: B1558). Source activity is 86 curies. Source was being used at a temporary job site in East Palestine, Ohio. Radiography crew was from licensee's Pennsylvania office. Source was being used in a building away from customer's main production facilities, in a make-shift chamber behind 3 foot concrete block walls. Area has been secured by licensee personnel, roped off, with boundaries established to ensure no exposure to non-radiological workers or members of the public. Licensee stated that no over exposure licensee personnel are expected as a result of this occurrence. QSA Global has been contacted by licensee to assist with source retrieval. Information current as of 11:45 AM, 7/18/07. "UPDATE: Ohio BRP Duty Officer received call from QSA Global requesting waiver of 3-day notification for reciprocity work to enter Ohio and retrieve stuck source. Permission was granted. QSA Global rep stated that they would not be on-site until Thursday, 7/19. Information current as of 5:00 PM, 7/18/07. "UPDATE: BRP Duty Officer contacted Licensee rep at temporary job site to discuss security of the camera and source. Licensee stated that boundaries are being maintained at the site and that the licensee would have a two-man crew (radiographer and assistant) on site throughout the night until QSA Global arrived to effect repairs. Information current as of 5:30 PM, 7/18/07. "UPDATE: BRP Duty Officer spoke with licensee personnel Thursday morning, 7/19/07. Licensee had crews in attendance at the site throughout the night to maintain security of temporary job site. Licensee stated that the radiography camera had been maintenenced and resourced approximately two weeks ago. After discussions with the manufacturer the licensee suspects that a spring clip at the connecting nut may have dislodged, causing the nut to become misaligned and preventing the source from retracting. QSA Global is expected on site at approximately 1:30 PM on today (7/19/07). Information current as of 9:25 AM, 7/19/07." Equipment is being returned to manufacturer for repair or disposal. Ohio Notice: OH070004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2007-07-24
43503 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-07-18 12:20 | 2007-07-18 18:43 | 2007-08-30 | UNANALYZED CONDITION - VENT SPACE LESS THAN DESIGN BASIS "During an inspection of the Unit 2 Reactor Building Steam Chase as a result of a similar situation being previously discovered on Unit 1, a storage gangbox was noted to be resting on one of the two hinged blowoff panels in the floor of the Steam Chase (elevation 130') and the hinged blowoff panels were determined to be restrained which would prevent their opening. The blowoff panels are designed to open to provide pressure and temperature relief between the torus room and 130 ft elevation of the reactor building for high energy steam line breaks. The 'as found' configuration of the blowoff panels hinder their capability to open, which constitutes a non-conforming and unanalyzed condition in that the vent area between the torus room and main steam chase in the reactor building is less than the area assumed in the analysis for a HPCI steam line break. "As such, for a HPCl steam line break in the torus room, the short term pressure across the torus room ceiling would likely be greater than 2.3 psid, which is the maximum differential pressure stated in Chapter 15A of the Unit 2 FSAR. There is no known analyzed limit for the differential pressure between the torus room and the 130 ft elevation of the reactor building. The actual differential pressure given the 'as found' condition is not known at this time. "Corrective actions have been taken to restore the assumed vent area between the torus room and the reactor building 130ft elevation. The gang box has been removed and both blow off panels no longer have restricted movement. The remaining 3' x 3' floor plug has also been removed, completely restoring the assumed vent area into compliance. Based on this information there is reasonable assurance that an adequate vent path currently exists such that the plant is no longer considered to be in a condition that significantly degrades plant safety. "However, since the actual differential pressure given the 'as found' condition is not known at this time, the 'as found' condition as previously discussed is assumed to be an unanalyzed condition that represents a condition that significantly degraded plant safety; however, additional information is needed in order to more conclusively determine this. If more conclusive information is provided that indicates otherwise an update notification will follow." This was also reported under 10CFR50.72(b)(3)(v)(D). The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM GORLEY TO HUFFMAN AT 1435 EDT ON 8/30/07 * * * "A review of the 'as found' configuration of the plant was performed to determine if this configuration would still be bounded by the calculations that support the HELB analysis in the Unit 2 FSAR. The 'as found' configuration consisted of having one torus plug in place rather than open and the two hinged torus ceiling blow-off panels bolted shut instead of being free to open. This engineering review concluded that if the torus ceiling blow-off panels do not open and with only one torus plug open, the torus pressures will not exceed the current FSAR pressures. Additionally, the torus pressures were found to be acceptable as a result of the modeling of friction in the HPCI pipe break mass and energy releases. "This being the case, for a HPCI steam line break in the torus room, the short term pressure across the torus room ceiling would be 1.93 psid for the 'as found' condition which is less than the maximum differential pressure of 2.27 psid as stated in Chapter 15A of the Unit 2 FSAR. "It should be noted that corrective actions were taken upon discovery and that the assumed vent area between the torus room and the reactor building 130 ft elevation was restored shortly following discovery. The gang box was removed, the restraint on the blow-off panels removed and both blow-off panels were confirmed to have full range of motion to open if the conditions were present that would warrant that movement. "Based on this review of the design calculations while taking the 'as found' conditions into consideration, the conclusion reached is that the nonconforming 'as found' conditions did not represent a condition that significantly degraded plant safety. For this reason this condition that was initially reported under 10CFR50.72(b)(3)(ii)(B) is being retracted." The licensee will notify the NRC Resident Inspector. R2DO(Shaeffer) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2007-07-18
43502 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2007-07-18 15:49 | 2007-07-18 18:07 | 2007-07-19 | SPILL OF ETHYLENE GLYCOL REPORTED TO STATE "Notified New Jersey D.E.P. [Department of Environmental Protection] of a spill of ethylene glycol in the Site Emergency Building at Oyster Creek. The spill was reported to NJDEP in accordance with N.J.A.E. 7:1.E, 7:26. The spill was contained and cleaned." The spill occurred during work on the Site Emergency Building air conditioning system. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 07/19/07 AT 1303 EDT FROM STEVE FULLER TO MACKINNON * * * "At 11:55 on 7/19/07, New Jersey Dept. of Environmental Protection (NJDEP) was informed that: The spill of ethylene glycol, reported to them on 07/18/07, was subsequently determined to be a substance other than ethylene glycol; it was not a hazardous substance; and it was not discharged to the environment. "Therefore, no report was required and the NJDEP notification (on 07/18/07) was retracted. "For the above reasons, the 4 hour non emergency ENS notification , made under EN # 43502, is hereby retracted." NRC R1DO (Jim Krafty) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-07-18
43501 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2007-07-18 17:06 | 2007-07-18 17:42 | 2007-07-18 | UNAUTHORIZED PERSON ENTERED THE PROTECTED AREA. An actual entry of an unauthorized person into a protected area. Immediate compensatory measures taken upon discovery. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-07-18
43500 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-07-17 15:59 | 2007-07-17 19:10 | 2007-07-17 | FIRE INSIDE OF OWNER CONTROL AREA "A small fire was discovered in an office building outside the protected area. The fire was extinguished using a hand held water fire extinguisher. The office building was evacuated as a precaution. One individual received a minor burn and was tended to by an onsite EMT. Local fire department responded to assist in smoke removal. EAL classification did not apply since the fire was outside the protected area. Fire was reported to be a trash can fire with fire damage being limited to the trash can, adjacent wall, and ceiling tile. Courtesy notifications to state and local government agencies have been made." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-07-17
43499 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2007-07-17 08:00 | 2007-07-17 15:21 | 2007-08-30 | UNANALYZED CONDITION - VENT SPACE LESS THAN DESIGN BASIS "During a review of the temporary repair of the steam line drain bypass line in the Unit 1 Reactor Building Steam Chase, two storage gangboxes were noted to be on the grated opening in the floor of the Steam Chase (elevation 129 ft). These grated openings are designed to be open to provide pressure and temperature relief between the steam chase and the torus room for high energy steam line breaks. "Appendix N to the Unit 1 FSAR credits the openings for venting the steam chase to the torus room through the openings for a main steam line break, and for venting the torus room to the steam chase for a HPCI steam line break in the torus room. The most limiting event is the HPCI steam line break in the torus room and the vent path associated with that event. Original assumptions used in the calculation for the vent opening did not adequately account for the grating itself and for louvers installed in a previous plant modification. As a result the vent area was further reduced. "Upon further review of the above condition, it has been determined that a non-conforming and unanalyzed condition exists In that the vent area between the torus room and main steam chase in the reactor building is less than the area assumed in the analysis, even without gangboxes covering a portion of the grating. "As such, for a HPCI steam line break in the torus room, the short term pressure between the torus room and the corner rooms (diagonals) is greater than 2 psid, which is the stated limit in Appendix N of the Unit 1 FSAR. The corner rooms contain ECCS components in the RHR and core spray systems. Based on engineering judgment there is reasonable assurance that the present nonconforming condition does not prevent safety systems and structures from fulfilling their safety function. This is based on the following information: "Structural Steel floor elevation platforms do not appear to have been credited in the structural design capability of the walls. These platforms should act to help maintain the wall intact with increased pressure. The increased pressure transient is a very short term transient, approximately 2-3 seconds in duration, after which the pressure will return to within 2 psid. It is expected that the wall would withstand this transient without degrading the performance of the low pressure ECCS systems or other structures and components. Lastly, the probability of occurrence of a steam leak leading to an instantaneous line break is very small. There is currently no report of steam leaks from the HPCI line, and although a probability evaluation has not been performed, it is likely that the probability of occurrence of such a break is very small. Thus, there is no known immediate threat that would prevent safety systems from performing their safety function. More detailed review is continuing at this point. "Short term corrective action will be required to increase the open 'vent' area between the torus room and the reactor building 130 ft elevation and restore at least the assumed vent path from the torus room. This can be accomplished by removing the gangboxes over the vent area in the steam chase and/or completing a floor plug evaluation of vent area needed between the torus room and the reactor building 130 ft elevation which will restore compliance with the 2 psid criteria. Analysis is currently underway to assess the pressure and temperature effects on the safety related structures and equipment by these short term actions. "Regarding reportability, based on engineering judgment as previously discussed, the unanalyzed condition does not represent a condition that significantly degraded plant safety; however, additional information is needed in order to more conclusively determine this. For this reason this condition is being conservatively reported under 10CFR50.72(b)(3)(ii)(B) until such time as more conclusive information is provided to make the final determination." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM GORLEY TO HUFFMAN AT 1435 EDT ON 8/30/07 * * * "Upon further review of the above 'as found' conditions, it has been determined that there are existing conservatisms in the current analysis which bound the flow restriction caused by the gang boxes on the grating. The evaluation concluded that the gang boxes found on the grated opening in the floor of the steam chase would not increase the pressures in the Unit 1 reactor building as a result of HELB conditions. Thus the pressure between the torus room and the corner rooms (diagonals) which is limited to 2 psid as stated limit in Appendix N of the Unit 1 FSAR is not affected. In addition, an additional open floor plug (the 3 ft by 3 ft floor plugs between Elevation 130 and the torus room below found to be covered by a hinged metal plate) is acceptable since it causes less differential pressure across reactor building compartments during the HELB's evaluated. "The results of this additional review confirmed the original engineering judgment that there was reasonable assurance that the as found nonconforming condition did not prevent safety systems and structures from fulfilling their safety function. Short term corrective actions were completed upon discovery of he 'as found' condition to further increase the open 'vent' area between the torus room and the reactor building 130 ft elevation and restore at least the assumed vent path from the torus room. This was accomplished by removing the gang boxes over the vent area in the steam chase. "Based on this review of the design calculations white taking the 'as found' conditions into consideration, the conclusion reached is that the nonconforming 'as found' conditions did not represent a condition that significantly degraded plant safety. For this reason this condition that was initially reported under 10CFR50.72(b)(3)(ii)(B) is being retracted." The licensee will notify the NRC Resident Inspector. R2DO (Shaeffer) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-07-17
43498 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2007-06-27 08:28 | 2007-07-17 15:17 | 2007-07-17 | FAILED RELAY STARTS ONE TRAIN OF THE DECAY HEAT RIVER WATER SYSTEM "This event is being reported via a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. In this case, the telephone report is not considered an LER. This report is being made under 10CFR 50.73 (a)(2)(iv)(A). "During Engineered Safeguards Actuation System (ESAS) logic testing on June 27, 2007, an invalid actuation of the 'A' train of the Decay Heat River Water System (DR) occurred. The DR is comprised of the 'A' and 'B' trains, and serves as the reactor's ultimate heat sink. The ESAS has three independent input channels, which cause actuation in a two out of three logic. During ESAS logic testing, the channel under test is placed in the tripped state. Actuation relays in the other two channels should remain energized by the outputs from the other two channels not under test. The invalid actuation of the 'A' DR train during testing on June 27, 2007, was due to a failed ESAS relay in one of the other two channels not being tested. During this invalid actuation, the 'A' DR train was fully actuated. The operation of this normally standby system did not have any adverse impact on plant operation, nor any negative impact on the DR. "The failed relay that caused the invalid actuation during ESAS logic testing did not impact the OPERABILITY of the ESAS, since the relay was failed in the actuated state. The failed relay was replaced on June 29, 2007." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-07-17
43497 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-07-17 09:00 | 2007-07-17 14:26 | 2007-07-27 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The State provided the following information via email: "At approximately 9:00 AM July 17, 2007, the Agency was informed that the Licensee had a gauge in a pickup truck traveling north from 67 Avenue and Lower Buckeye to I-10 noticed at the I-10 ramp the gauge was missing. He began the trip at approximately 7:00 AM. The Gauge case was secured in the truck as required. He did not put the gauge in the case however. The gauge is a Troxler Model 3430, Serial Number 39005 and contains 8 mCi of Cesium-137 and 40 mCi Am:Be-241. The Company plans a press release and will offer a reward for the gauge. "Phoenix PD is investigating. "The Agency continues to investigate this event. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." Arizona report number: 07-010 * * * UPDATE PROVIDED BY AUBREY V. GODWIN TO JASON KOZAL ON 07/27/07 AT 1306 EDT * * * "The gauge has been recovered. It was found by a street sweeper. It was not opened and no radiation exposures appear to have occurred. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." Notified the R4DO (Smith), FSME (Thorp), ILTAB (via e-mail) , Mexico (e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-07-20
43496 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2007-07-11 | 2007-07-17 11:49 | 2007-07-17 | AGREEMENT STATE REPORT - MOISTURE GAUGE SOURCE DISCONNECTED FROM CABLE The State provided the following information via facsimile: "This is the initial notification for an incident that occurred on 7/11/07. A broad-scope licensee reported the loss and recovery of a 50 mCi, Am:Be source from a CPN Model 503DR soil moisture gauge. The gauge was being used as part of an irrigation/moisture study in an agricultural field located about 10 miles south of Sterling, CO. The licensee reported that the source/detector assembly became disconnected from the cable during use, and fell to the bottom of a test hole. The gauge users notified their RSO, and he was able to respond to the scene, retrieve the source, and place it back into the shielded position within the gauge using a remote handling tool. There were no radiation exposures to the gauge users or members of the public, and the RSO estimated his exposure to be less than 20 millirem. The licensee has contacted the manufacturer and is investigating the cause of the problem." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2007-07-20
43495 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2007-07-17 05:22 | 2007-07-17 06:30 | 2007-07-17 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL (RVWL) "An automatic reactor scram occurred at 0522 on 07/17/07 due to a low reactor water level, following a trip of the 'C' Reactor Feed Pump. Reactor water level lowered to the low-low level setpoint and a reactor isolation occurred. Reactor level has been returned to the normal band and a reactor cooldown has been initiated using isolation condensers." The cause of the "C" RFP trip is attributed to an electrical fault as sensed on ground sensing and differential sensing instrumentation. No flames or smoke was observed, however, operators reported an acrid smell of insulation. Following the automatic scram on low reactor water level [138" above top of active fuel (TAF)], level continued to decrease to the low-low setpoint of 86" TAF resulting in a reactor isolation signal. The reactor isolation signal initiates closure of the Main Steam Isolation Valves (MSIVs), trip of the Recirc Pumps and actuation of the Isolation Condensers. Current reactor pressure is 520 psig with a cooldown rate of 82F/hr. The licensee plans to issue a press release and will take the Unit to cold shutdown for repairs. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1000 EDT ON 07/17/07 FROM STEVE FULLER TO S. SANDIN * * * The following information reported under 10CFR50.72(b)(3)(iv)(A) was provided as an update: "The following systems actuated upon receipt of a lo-lo reactor water level signal, subsequent to the reactor scram, reported under EN #43495, which occurred at 0522 on 07/17/07: MSIVs - Isolation Isolation Condensers - Initiation Standby Gas Treatment - Initiation Recirc Pumps - Trip Containment Valves - Isolation Core Spray - Start, but no injection Containment Spray - Manual initiation only, following use of EMRVs to control Rx pressure, causing elevated Torus water temperature." The licensee informed the NRC Resident Inspector. Notified R1DO (Krafty). * * * UPDATE AT 1122 EDT ON 7/17/07 FROM STEVE FULLER TO S. SANDIN * * * The following information reported under 10CFR50.72(b)(2)(xi) was provided as an update: "Notified the New Jersey D.E.P. of an unplanned plant shutdown which occurred at 0522 07/17/07. There was no environmental impact from the plant shutdown. "This notification is required to be made within 12 hours of an unplanned plant shutdown." The licensee informed the NRC Resident Inspector. Notified R1DO (Krafty). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) |  | 0 | 2007-07-17
43494 | -1 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2007-07-16 20:00 | 2007-07-16 20:47 | 2007-07-20 | SAFEGUARDS REPORT INVOLVING FAILURE TO MAINTAIN ADEQUATE CONTROL OF SECURITY EQUIPMENT Safeguards system degradation related to failure to maintain positive control of security equipment. Immediate compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. * * * RETRACTION ON 07/20/07 AT 1656 EDT FROM ALAN DAY TO MACKINNON * * * Upon investigation it was determined that the licensee always had positive control of their security equipment. The NRC Resident Inspector has been informed of this retraction. Contact the Headquarters Operations Officer for additional details. R2DO (Mark Lesser) notified. E-mailed to 73.71 Group | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-07-16
43493 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-07-15 22:00 | 2007-07-16 20:38 | 2007-07-16 | AGREEMENT STATE REPORT - UNPLANNED EXPOSURE DURING CALIBRATION TEST The State provided the following information via facsimile: A doctor was performing a monthly calibration test and position verification test. During the test, an error message was received using a dummy source. The doctor entered the room with a survey meter which showed no elevated radiation reading. The emergency handwheel was used to retract the dummy wire. After about 12 turns, the room radiation alarms initiated and the doctor left the room. Troubleshooting disclosed that the source had become exposed and the doctor received approximately 75 Mr exposure. Source: Ir-192, 5.2 Curies Varian Medical Systems model Varisource HDR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-07-19
43492 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-07-17 07:00 | 2007-07-16 18:09 | 2007-07-19 | TECHNICAL SUPPORT CENTER INOPERABLE DUE TO PLANNED RELOCATION "On 07/17/07 at 0700 hours CDT the Monticello Nuclear Generating Plant's (MNGP) Technical Support Center (TSC) will begin relocation to a new facility. The relocation activities include implementation of compensatory measures to maintain the TSC functions during the transition. The compensatory measures include having the Emergency Director report to the Control Room and co-locating the remaining TSC staff at the EOF should an event declared requiring Emergency Response Organization (ERO) activation. The ERO has previously successfully demonstrated the ability to implement these compensatory measures. The relocation and testing of equipment in the new TSC are scheduled to be complete[d] on or before 07/23/07. "The site Emergency Response Organization has been notified of the relocation and instructed on the planned compensatory measures to be implemented during the move. MNGP will notify the NRC upon completion of the relocation and declaration of TSC operability in the new location. This event is considered reportable per 10 CFR 50.72 (b)(3)(xiii). The licensee has notified the NRC Resident Inspector." * * * UPDATE ON 07/19/07 AT 1546 EDT FROM GERALD HOLTHAUS TO MACKINNON * * * "On 07/19/07 at 1400 hours CDT the Monticello Nuclear Generating Plant's Technical Support Center (TSC) was declared operable after its relocation to a new facility. Relocation and testing activities have been completed and the Emergency Response Organization has been notified of the cessation of compensatory measures. NRC R3DO (Eric Duncan) notified. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-07-16
43491 | 0 | FLORIDA BUREAU OF RAD CONTROL |  |  |  |  | 2007-07-11 | 2007-07-13 15:53 | 2007-07-13 | AGREEMENT STATE - INADVERTANT DOSE TO PATIENT GALLBLADDER The State provided the following information via facsimile: "On July 11 a SIR-Spheres procedure was performed to treat a carcinoma on the liver. After review of the CT images on July 12, the physicist believes that 20% of the dose went to the gallbladder (which sits on top of the liver). The doctor and patient were notified on July 12. Licensee will follow up with patient in future visits to determine if there is any gallbladder damage. This office was notified on July 13. Licensee will submit a written report. Florida is investigating." Typically, a sphere contains 2270 MBq of Y-90. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | HOS | [5 empty] | 0 | 2007-07-19
43490 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-07-13 08:00 | 2007-07-13 16:33 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * UNATTENDED VACUUM CLEANER IROFS "On July 13, 2007 at approximately 8:00 a.m., in the Recovery Area Specialty Fuels Facility (SFF), a concern regarding an unattended Raschig ring vacuum cleaner with no top and hose attached was brought to the attention of the SFF foreman. The vacuum cleaner was in the Conversion Area which is part of the Container Control Area (CCA). The vacuum cleaner is used to collect spills and for general cleaning purposes. The vacuum cleaner was filled with Raschig rings to the level of the side mounted hose connection in accordance with procedure. Removal of the top created a free space of approximately [DELETED] in diameter by [DELETED] deep above the hose connection that contained no Raschig rings. With the hose connected and in an upright position, a volume of approximately [DELETED] was created, in violation of the NCS Posting. Solution could have collected in the vacuum cleaner, filling the Raschig ring portion of the vacuum cleaner and the free space above the rings before spilling onto the floor. The foreman immediately removed the hose from the vacuum cleaner and subsequently notified Safety Management. The top was placed back on the vacuum cleaner. "Evaluation of the Event "Although the configuration of the unattended vacuum cleaner (no top with hose attached) created a potential unfavorable geometry in the CCA, there was no immediate safety concern. Uranium [DELETED] materials were not being processed in the area at the time and have not been processed in the area for approximately 2 years. Although there is a sprinkler system overhead, there are no other lines containing uranium [DELETED] solutions in the immediate area. The vacuum cleaner drum was sampled and found to contain [DELETED] of liquid with a concentration of less than [DELETED] grams 235U per liter. Considering that the vacuum cleaner was partially full, an additional [DELETED] liters of solution would have been necessary to fill the vacuum cleaner above the Raschig rings, which is a significant accumulation that would likely have been identified by area personnel. The liquid in the drum would also have served to dilute any solution added to the vacuum cleaner. The combined effect of these as found conditions was such that a criticality was highly unlikely. "This event is bounded by existing scenarios in our ISA. The scenario deals with an [DELETED] Recovery Container Entry Requirements. Specifically, the scenario addresses [DELETED liters that is filled with uranium [DELETED] solution. The scenario credits the following controls as IROFS [Item Relied On For Safety]. "1. [DELETED]. "2. [DELETED]. "The first IROFS was degraded for this event to occur. The second IROFS was not compromised. As a result double contingency was lost." The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
43489 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-07-06 04:10 | 2007-07-13 13:59 | 2007-07-13 | VEHICLE ACCIDENT DURING TRANSPORT OF RADIOPHARMACEUTICAL SOURCES "On Friday, July 6, 2007, at approximately 4:10 am, an accident involving a vehicle transporting radiopharmaceuticals occurred on Route 3 North near Exit 32 in Chelmsford, Massachusetts. The Radiation Control Program (RCP) was informed about the accident via the State Police at approximately 5:15 am. The first responder from the RCP arrived at the scene of the accident at about 6:15 am. "A vehicle carrying patient radiopharmaceutical doses had rolled over on Route 3 North beyond Exit 32, emptying 18 Type A transport containers onto the highway and over an embankment. A brook tributary to a lake is at the bottom of the embankment where the accident occurred. Six of the containers had dropped into brook. The rest were strewn about the highway and the embankment. "The containers were carrying radiopharmaceuticals in the form of Tc-99m bulk and patient doses, F-18 in the form of FDG for PET imaging, and I-131 for patient therapy. The Tc-99m was transported in an internally shielded Type A nylon covered container and the I-131 and F-18 were transported in Type A shielded ammo boxes. "In all, 17 of the 18 containers were recovered. None of the containers recovered had any external contamination. One ammo box had a torn off lid, but the tungsten syringe shield containing a dose of F-18 was not breached. The 18th ammo box container with 2 F-18 doses totaling 271.21 mCi was not recovered. However, the F-18 had decayed approximately 7 half-lives by 4:00 pm, so there was no radiological consequence. Since this box had fallen onto the bottom of the brook and, due to the fact that no other container was breached, it was concluded that the two tungsten syringe shields would not have been breached. "There was no release of radioactive material in this event. There was not breach of any internal container housing the radioactive material. "This event is considered closed. There were no radiological consequences to members of the public and emergency workers." Attempts to recover the last container included using divers and metal detectors. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-07-18
43488 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-07-12 16:30 | 2007-07-12 19:14 | 2007-07-12 | UNALLOWABLE MANUAL ACTIONS CREDITED FOR FIRE SAFE SHUTDOWN "During performance of NFPA-805, Transition Project Task SUP-1, 'Manual Action Compliance,' it was determined manual operator actions are being credited in IX/12-A Lower 4KV Room and XII/14-A Upper 4KV Room to achieve and maintain hot safe shutdown. The manual actions are to provide temporary ventilation capability to the 4KV rooms to assume continued operability of vital switchgear. The switchgear provides power to equipment needed to achieve and maintain hot shutdown. These manual actions were specified in an Appendix R Section III.G.1/G.2 fire area; however, they do not meet the criteria for allowable manual actions specified in RIS 2006-10, 'Regulatory Expectations with Appendix R paragraph III.G.2 Operator Manual Actions.' No system actuations occurred as part of this event. "The discovery of these manual actions is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii)(B) and has been entered into the site's corrective action program The alternate compensatory measure for these areas is to perform the specified manual actions. An extent of condition review will be initiated that will encompass the remainder of the safe shutdown areas. The results of the extent of condition will be documented in the site's corrective action program with compensatory measures being established as appropriate. "The 60 day licensee event report, submitted to the Commission in accordance with 10 CFR 50.73(a)(2)(ii), will provide the results of the manual action compliance review and follow-up corrective actions. This is based on preliminary data and further investigation is ongoing." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-07-12
43487 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-07-12 10:15 | 2007-07-12 18:35 | 2007-07-12 | FIRE INSPECTION ANALYSIS OF PRESSURIZER PORVS AND BLOCK VALVES "During a review of abnormal operating procedure (AOP) 10A, Safe Shutdown-Local Control, by the NRC triennial fire inspection team, it was identified that fire damage to the reactor coolant system (RCS) power-operated relief valve (PORV) and block valve circuits as a result of a fire in the cable spreading room could also result in simultaneous damage to a block valve circuit and spurious actuation of a PORV. While the actions included in abnormal operating procedure (AOP)-10A provide reasonable assurance that positive control of RCS Inventory is maintained, these steps do not ensure that simultaneous failure of the block valve circuit and spurious operation of a PORV will not result in RCS depressurization. Therefore, a postulated fire may potentially remove the ability to fully implement the Safe Shutdown Strategy. Compensatory measures in the form of twice-per-shift fire rounds in the cable spreading room have been implemented." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-07-12
43486 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-07-11 17:04 | 2007-07-12 17:31 | 2007-07-12 | RAIN CAUSES OVERFLOW OF RWST WATER BASIN "The following voluntary report is being made as a result of the Industry Ground Water Protection Initiative NEI-07-07. During a heavy rain downfall on 7/11/2007, the U1 Refueling Water Storage Tank (RWST) water basin overflowed. This overflow was slightly contaminated due to prior contamination of insulation which surrounds the RWST. The rainfall is believed to [have leached] the contamination from the insulation to the basin. In accordance with NEI-07-07 guidance, a voluntary communication has been made to the appropriate State/Local officials. Thus the purpose of this notification is to inform NRC of this voluntary notification to State/Local agency. The release was less than regulatory (ODCM or 10 CFR 20 Appendix B) limits. " The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2007-07-12
43485 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2007-07-12 | 2007-07-12 15:25 | 2007-07-12 | STOLEN MOISTURE DENSITY GAUGE At 9am on 7/12/07 the licensee noticed that their Troxler, Model 3440, S/N 20970, moisture density gauge was stolen. The gauge had been secured in a truck with a lock and chain inside a locked case at 3pm on 7/11/07. The licensee noticed that the lock on the case had been cut and the gauge was gone. The licensee reported the incident to the Lexington Police Department as case identification number 07131235. The gauge has a 0.04 curie Americium-241 source and a 0.008 curie Cesium-137 source. The sources were last leak checked in April of 2007. The state is following up on this issue. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2007-07-17
43484 | 0 | ST LUKES REGIONAL MEDICAL CENTER |  |  |  |  | 2007-07-12 | 2007-07-12 14:40 | 2007-07-12 | MISSING Ir-192 SOURCE A 6 Curie source was being shipped by Federal Express from the Twin Falls branch of St Luke's Regional Medical Center to Alpha-Omega in Louisiana. A cardboard box arrived in Louisiana containing what appeared to be aircraft parts. See also Event Notification #43480 * * * UPDATE ON 7/12/07 AT 1525 FROM JEFFERSON FAIRBANKS TO MARK ABRAMOVITZ * * * The source was found at Alpha-Omega in Louisiana. It had been at their location and misreported as lost. Notified the R4DO (Gaddy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-07-12
43483 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-07-11 19:26 | 2007-07-12 11:50 | 2007-07-12 | SAFEGUARDS SYSTEM DEGRADATION Safeguards system degradation due to computer malfunction. Compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-07-12
43482 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-06-25 | 2007-07-12 07:53 | 2007-07-12 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA The licensee provided the following information via facsimile: "Agreement State Agency: Louisiana Department of Environmental Quality "Event Report ID No.: LA070020 License No.: LA-5694-L0IA "Licensee: Ohmstede "Event date and Time: June 25, 2007 "Event Location: Sulphur, LA Event type: Equipment Notifications: LA DEQ "Event description: Ohmstede sent an Amersham 660B camera serial number B1072 to QSA Global for a source exchange. Before a new source was put into the camera, QSA Global discovered that the camera had a cracked S tube. The camera has been removed from operation and is in storage." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-07-17
43481 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-05-31 | 2007-07-12 07:12 | 2007-07-12 | AGREEMENT STATE REPORT - POTENTIAL PERSONNEL OVEREXPOSURE The State provided the following information via facsimile: "Agreement State Agency: Louisiana Department of Environmental Quality "Event Report ID No.: LA070019 "License No.: LA-7396-L01 "Licensee: Oceaneering International, Inc "Event date and Time: May 2007 "Event Location: Houma, LA "Event type: Overexposure "Notifications: LA DEQ "Event description: Oceaneering received a notification from Landauer that one of Oceaneering's employees was over exposed for the month of May 2007. The dose that was reported for this employee was 5467 mrem (deep), 5677 (eye), and 5892 (shallow). This incident will be investigated and DEQ will forward new information once it is received. Transport vehicle description: N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-07-17
43480 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-07-11 | 2007-07-11 15:59 | 2007-07-16 | AGREEMENT STATE REPORT - MISSING IR-192 SOURCE The licensee provided the following information via facsimile: "A facility in Twin Falls, Idaho was shipping a 6 Ci Ir-192 HDR source back to Alpha & Omega Services for disposal. The carrier was FedEx. When the package arrived at Alpha & Omega and was opened, it contained a helicopter part and not a source. Will update when information is available." Event Report ID No: LA070018 See also Event Notification #43484 * * * UPDATE AT 1054 EDT ON 7/16/07 FROM RICHARD PENROD TO S. SANDIN * * * The following information was received via fax: "This source was never lost. The facility did not follow their SOPS and log in the shipment from FEDEX. The source was in the facility the entire time." Notified R4DO (Pick) and FSME (Wastler). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-07-16
43479 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2007-07-10 19:54 | 2007-07-10 22:55 | 2007-07-10 | MAIN TURBINE TRIP CAUSING A REACTOR SCRAM "During a planned power reduction to support thermal backwash of the main condenser, an automatic reactor scram resulted from a main turbine trip. The cause for the turbine trip is currently under investigation. Following the reactor scram, the expected reactor level shrink resulted in valid group 2, Reactor Building Ventilation, and group 6, Reactor Water Cleanup System isolations. All safety systems and equipment functioned as designed. A schedule for plant restart has not yet been determined." All control rods fully inserted and no safety relief valves lifted from the scram. Minimum level after the scram was -10 inches. Decay heat is being removed using the main turbine bypass valves to the main condenser and maintaining level using normal reactor feed water. The plant is using the normal shut down electrical lineup and slowly cooling down (currently at 820 psi). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-07-10
43478 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2007-05-10 | 2007-07-10 13:40 | 2008-03-27 | MEDICAL AFTERLOADER-APPLICATOR PLACED IN INCORRECT LOCATION "On 10 May 2007 it was discovered that a patient who was being treated for recurrent endometrial cancer (Paravaginal Tumor) had received a dose which differed from the prescribed dose for the fraction by greater than 50%. The intended dose to the patient was 500 cGy to the tumor. However, the actual dose administered was 12 Gy to an unintended site (the dose delivered was approx. 54 mm from the tip of the catheter instead of 5 mm from the tip). It was noted in the misadministration report that there were no critical structures that were exposed above any threshold tolerance. Due to a physics catheter measurement error, which was entered into the treatment plan, the catheter did not go in as deeply as intended but stopped short of the target. On audit of the procedure, and remeasurement of the catheter, the chief physicist identified the error in measurement and filed a report with the RI RCA. Corrective actions in addition to re-measurement and subsequent adjustment of treatment plan included adjustment in the dose per remaining fractions to provide the correct dose to the target." Rhode Island Report: RI-07-001 Actual initial dose was approximately 10% of expected. Source Ir-192, 8.05 Curies A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM FLANNERY TO O'HARA VIA E-MAIL AT 0949 ON 7/11/07 * * * "This event (EN43478) has been reviewed and determined to be a reportable medical event." * * * UPDATE FROM FERRUOLO TO SNYDER VIA FACSIMILIE AT 1452 ON 3/27/08 * * * The following information was received from the State via facsimilie: "Based on preliminary information obtained per voice and e-mail: underdosing on initial fraction of treatment was due to improper measurement of the catheter. Adjustments were made in subsequent fractions. Written documentation of the incident stated that no critical structures were exposed above the threshold tolerances." Notified R1DO (Bellamy) and FSME (McConnell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2007-07-13
43477 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-07-07 | 2007-07-09 15:38 | 2007-07-18 | AGREEMENT STATE REPORT - MISSING MOISTURE DENSITY GAUGE The licensee provided the following information via email: "On July 9, 2007, Corporate RSO for Professional Service Industries, called to report a moisture density gauge missing during quarterly inventory. The RSO reported that Troxler model 3430 S/N 30189 was missing when inventory was conducted on 07/07/07. The gauge contains two radioactive sources; an 8 mCi Cs-137 source S/N 750-2295, and a 40 mCi Am-241 source S/N 47-27166. The sources were leak tested on 03/14/07. The last known use of the device was on 06/09/07. The employee assigned the moisture density gauge returned the truck and keys to the office and did not return to work. It was assumed the gauge had been placed back into storage. It is possible the employee stole the gauge. The RSO reported that a list of about 20 pawnbrokers in the area were contacted and informed that there was a $500.00 reward offered for the return of the gauge. The RSO reported that the employee was wanted in California for back child support. Company representatives searched his former residence, but didn't find evidence of the gauge there. I [State] told the RSO that we would place a notice to the State Pawnbrokers Association. I [State] also suggested that, if they will accept it, he [RSO] should file a theft report with Dallas Police Department. The RSO asked that we notify the Pawnbrokers' Association of the reward offer and that it is a 'no questions asked' offer." Texas Incident # I-8424 * * * UPDATE ON 7/18/2007 AT 1618 FROM LATISCHE HANSON TO MARK ABRAMOVITZ * * * The State provided the following information via email: The licensee has checked e-bay and local pawn shops and failed to find the gauge. On the advice from LLEA, a certified letter was sent on 7/11/2007 to the ex-employee who last had the gauge. When ten days expire, the licensee will re-contact LLEA and submit a theft report. Notified the R4DO (Pick), FSME (Brach), ILTAB (e-mail) and Mexico (e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-07-12
43476 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2002-07-31 | 2007-07-09 14:07 | 2007-07-09 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR GAUGE The licensee provided the following information via facsimile: "During the routine license inspection on 5/15/07, the inspector learned that one of the licensee's nuclear gauges (Humboldt, SM 486) was run over by a water truck at a jobsite in Menifee, Riverside on 7/31/02. The licensee did not report the incident to the Department [California Department of Public Health]. An incident report was generated by the licensee, dated 7/31/02, and filed. According to the incident report, the gauge was immediately inspected for damage by the ARSO. The sources and shielding were found to be undamaged and completely intact. The casing and electronic parts were badly damaged. The gauge was transported to their office for further evaluation and a leak test was performed. The results of the leak test were received August 12, 2002, and the gauge was not leaking. "The nuclear gauge still has not been repaired, and is not being used by the licensee, although the leak test is being done on the required frequency. As part of the routine inspection, a Notice of Violation was issued on 5/30/07 for failure to report/notify the Department, within 24 hours of the incident and failure to submit a written report within 30 days after the incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-07-12
43475 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2007-07-07 11:03 | 2007-07-07 11:51 | 2007-07-11 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM (SPDS) DUE TO PLANNED MODIFICATION "At 11:03 hours EST, on July 7, 2007, the Plant Information Computer System (PICS) was removed from service to perform a planned modification to install and test a Standard Digital I&C System Platform (DICSP) infrastructure and to update the network configuration of PICS. The expected duration of PICS inoperability is approximately 24 to 36 hours. PICS provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Plant Process Computer System (PPCS), Emergency Response Computer Logger (ERCO-1), Meteorological Data link system and the Inadequate Core Cooling Monitor (ICCM). The loss of PICS requires alternate methods, as described in plant procedures, to be used for the above described functions. Therefore, appropriate assessment of plant conditions, notifications and communications can still be made, if required, during the time that PICS is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii) which is any event that results in a major loss of emergency assessment capability, offsite response capability or offsite communications capability. As previously stated, alternate means remain available to assess plant conditions, make notifications and accomplish required communications, as necessary. An additional notification will be provided when PICS operability is restored. "The NRC Resident Inspector has been notified." * * * UPDATE FROM RICHARD SWEENEY TO JOE O'HARA AT 1653 ON 7/8/07 * * * "Engineering change (EC) of PICS continues. Testing of the installed modifications is now in progress. As stated above, alternate means remain available to assess plant conditions, make notifications, and accomplish required communications, as necessary. Testing of the EC and EC turnover is expected to be completed on 07/09/2007. The plant computers, including SPDS, are presently running providing plant data thus are available but not operable." The licensee notified the NRC Resident Inspector. Notified R2DO(Henson) * * * UPDATE FROM RICKY RAWLS TO JOHN KNOKE AT 2043 ON 7/10/07 * * * "Crystal River Unit 3 initially reported removal of its Plant computer systems from service for planned modification on 07/07/07 at 11:51 and made the required notification in accordance with 10 CFR 50.72(b)(3)(xiii). The Engineering change associated with the Safety Parameter Display System (SPDS) and the Plant Information Computer System (PICS) has been completed and the systems are currently running providing data. Modification testing has been completed and the systems are considered operable. The compensatory measures put in place to assure appropriate assessment of plant conditions, notifications and communications have been terminated." Licensee also stated that the ERDS system is now operable. The licensee notified the NRC Resident Inspector. Notified R2DO (Hopper) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-07-07
43474 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2007-07-05 10:01 | 2007-07-05 13:51 | 2007-07-05 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTIVATION OF PUTNAM COUNTY SIREN SYSTEM "This is a voluntary report for information only applicable to reporting under 10 CFR 50.72(b)(2)(xi) for notification to other government agencies. At approximately 1001 hours ET the new siren system in Putnam County was actuated inadvertently during testing. At approximately 1005 hours, Putnam County notified Entergy that the sirens had sounded. At approximately 1006 hours, a siren cancel signal was initiated. There has not been an event related to the health and safety of the public or onsite personnel, or protection of the environment. The current siren system which is used for meeting offsite emergency notification requirements did not sound and remains operational. The Counties (Westchester, Rockland, Orange, Putnam) were notified. The New York State Emergency Management Office (SEMO) was notified. Local television, radio and print media were also notified. The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  |  | 50.72(b)(2)(xi) |  |  | 0 | 2007-07-05
43473 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2007-07-04 02:14 | 2007-07-04 02:42 | 2007-07-04 | UNUSUAL EVENT DECLARED DUE TO A LOSS OF CONTROL ROOM ANNUNCIATORS "Failure of main control board annunciator panels A, B, C, and D occurred at 0158 hours. At that time the control room had just commenced a load reduction to repair the turbine control valve #3. The load reduction was terminated at the time of the annunciator panel failure. Reactor power is 98.5%. "Unusual Event EAL is 7.3.1 "RCS Pressure is 2235 psig "RCS Temperature is 573 degrees" The plant is currently stable and holding power. The Plant Process Computer remains operable monitoring at power parameters. The licensee has commenced an investigation to determine the cause of failure related to the power supply for the affected annunciator panels. The licensee informed both State and local agencies and the NRC Resident Inspector. * * * UPDATE PROVIDED BY SHIFT MANAGER (GARNISH) TO JEFF ROTTON AT 1553 ON 07/04/07 * * * The licensee exited the Unusual Event at 1542 EDT on 07/04/07. All repairs have been completed, successful post maintenance test is complete, and all annunciator panels have been restored to operable condition. A blown fuse was discovered on the AA panel flasher card. The flasher cards for the AA panel and the A panel have been replaced. Two separate annunciator cards in the D panel have also been replaced. The licensee informed both State and local agencies and the NRC Resident Inspector. Notified R1DO (Rogge), NRREO (Lubinski), IRD (Cruz), R1 RA (Collins), NRR ET (Dyer), DHS (Frost), and FEMA (Dwight). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-07-04
43472 | 0 | EMERSON PROCESSING MANAGEMENT |  |  |  |  | 2007-06-27 | 2007-07-03 17:58 | 2007-07-03 | PART 21 NOTIFICATION - FISHER TYPE 67C SERIES REGULATOR SCREW FRACTURE The manufacturer provided the following information via facsimile: This is a summary of a communication that was sent to inform all Fisher customers of record. "Fisher Controls has determined that a faulty batch of screws (Fisher Part Number T13526T0012) was used in the applicable constructions listed below. In some cases, a fracture occurred in the threaded shank, while in other cases the screw head fractured. Multiple screw fractures were also found on the same regulator. The screw fractures were found in four different product orders. "The function of the screw depends on the type of construction: * On all models, the screw retains the diaphragm between the body and the spring case (six screws per regulator). * On the Types 67C and 67CR, the screws retain the bottom plate (four screws per regulator) * On the Types 67CF and 67CFR, the screws retain the drip well (four screws per regulator). "If the screw is compromised, the ability of the regulator to retain pressure or function correctly may be impaired. Any abnormal function of an instrument supply regulator might, in turn, cause unexpected behavior of the instrument itself due to supply pressure changes. These changes could result in a range of performance problems, up to a loss of process control. "Fisher has stopped shipment of these products and is currently purging their inventory. "This notice applies only to the subject equipment supplied by Fisher Controls International LLC that meets all of the following criteria: * Can be any of the following constructions: Fisher Types 67C, 67CR, 67CF and 67CFR Instrument Supply Regulators or Type R130 Series Manifold Regulators. * Must be manufactured in China between March 1 and June 15, 2007, with date of manufacture 3-07, 4-07, 5-07 or 6-07 stamped on the product. "Action Required: * No action is required for plants that do not have the subject equipment. * Do not install any of the equipment specifically identified in this notice. * If your plant has any of the equipment specifically identified by this notice or experienced problems regarding expected performance from these regulators, contact your local Fisher Representative Sales Office regarding appropriate corrective action. "10CFR21 Implications: * The recipient of this notice is requested to review the information contained in this notice to determine its applicability to his/her facility. * If no equipment meeting the applicability requirements listed above have been provided by Fisher Controls International LLC, then no further action is required. * If equipment meeting the applicability requirements listed above have been supplied and used in a safety-related application, Fisher Controls requests that the recipient of this notice review it and take appropriate action in accordance with 10CFR21." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21 |  |  |  | 0 | 2007-07-03
43471 | 0 | UNIVERSITY OF MISSOURI, COLUMBIA |  |  |  |  | 2007-07-03 14:00 | 2007-07-03 17:26 | 2007-07-05 | SURFACE CONTAMINATION EXCEEDING LIMITS ON PACKAGE At 1400 CDT on 07/03/07, the University of Missouri, Columbia campus received a scheduled delivery of a radioactive material shipment containing 11 millicuries of I-131. During the receipt inspection, radioactive contamination was discovered on one spot on the top corner of the ammo can lid used for transport. Using two different measuring techniques, the contamination was between 470-700 dpm/sq cm. A second swipe survey of the same spot had no contamination. A radiation survey conducted of the container showed a 30 mRem/hr hot spot in the same area where the contamination was removed. The ammo can has been bagged and will be stored in the secure hot lab in the veterinary facility until the carrier can return to pickup the transport can on 07/05/07 or 07/06/07. The Mid America Isotopes company located in Ashland, MO delivered the package to the facility. The carrier was notified at 1600 CDT of the contamination. This shipment was one of several that were prepared and delivered today, but it is not known if there was any contamination of the other packages or the vehicle. * * * UPDATE AT 12:30 ON 7/5/2007 FROM MARY ALDRICH TO MARK ABRAMOVITZ * * * "The inner container was intact, not leaking, and was used as intended." Notified the R3DO (Lanksbury) and FSME (Moore). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2007-07-03
43470 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2007-04-02 | 2007-07-03 14:29 | 2007-07-03 | NEBRASKA AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The State provided the following information via email: "The licensee purchased the facility in December of 2006 from Hartland Warehouse. Upon receiving the State of Nebraska's annual inventory of Generally Licensed Devices in April of 2007, they did an inventory and found the following sign missing: Isolite Exit Sign model 2040-01-02 containing 10 curies of H-3 in January of 1992 and serial #1135. "The current licensee believes that the missing sign was located on the second floor of the office at one time. A door that led to a landing on the second floor and stair steps that led down to the first floor at sometime previously were torn down and the door blocked off. The licensee believes that the sign was removed and disposed of in the landfill." Nebraska Event Number: NE070003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2007-07-06
43469 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-06-29 | 2007-07-03 09:29 | 2007-07-03 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION "Christus St. Francis Cabrini hospital called and reported an over exposure on a treatment using an HDR [High Dose Rate system]. The HDR system delivered a dose 40% more than what the treatment plan called for to the patient. The overexposure for the treatment was reported as 1400 cGy. This is all of the information we have at this time. An investigation has started for this incident." LA report number - LA070017 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-07-09
43468 | 0 | US ARMY |  |  |  |  | 2007-06-26 | 2007-07-02 17:03 | 2007-07-03 | DAMAGED CAMPBELL PACIFIC MOISTURE DENSITY GAUGE On June 26, 2007, the 62nd Engineering Unit, located in Ft. Hood, Texas and recently returned from deployment, sent an email to the US Army TACOM LCMC, located in Warren , MI regarding a damaged Campbell Pacific (CPN) MC-1 moisture density gauge, serial number: M7112095. The device contains a 10 millicurie Cs-137 source and a 50 millicurie Am-241:Be source (1977 activity strength). The email requested guidance on the failure of the device handled assembly to lock in 'safe' or any other position. The lead trap door is disconnected from pushrod and fails to allow source rod to extend. The unit is on recuperative leave and the US Army will follow up with the unit personnel later this week. The US Army will continue to investigate to determine the status of the device, where and when it was damaged, and the status of the sources and the device's storage location. * * * UPDATE PROVIDED BY KAREN MCGUIRE TO JEFF ROTTON AT 1329 ON 07/03/07 * * * "The tester was used in Iraq and was shipped back to the unit in Texas in Dec 06. In Iraq, the tester had some difficulty with the lead trap door not easily sliding out of the way, when the rod was pushed down, but it did function. The rod locking mechanism worked in Iraq. "On 18 Jun, the Local Radiation Safety Officer (LRSO) with the 62nd Engr Bn was notified verbally of a display problem involving the tester. A trained operator made the notification. On 26 June, the LRSO and Alternate LRSO both trained operators then decided to check out the tester. They cranked down on the display screw and the tester display functioned. They then decided to check the tester out further and discovered that the handle wouldn't lock in the safe and other positions. They compared this to another tester and then determined that the tester had a problem needing maintenance. The LRSO then sent an e-mail on 26 June asking for maintenance or turn-in instructions. "The maintenance check (which includes ensuring proper function of the tester, the rod moving freely through the ranges and cleaning the tester of any dust and dirt) at the unit was the first, since its arrival from IRAQ. The unit planned to use the tester, but after discovering the problem with it, they then used another tester. The testers at the unit have maintenance done every six months depending on the use of the equipment. "The rod with the source is inside of the tester housing. The tester is stored like normal in its transport case. The shutter is in place and closed. The lead trap door is in place. The lead trap door just doesn't slide out of the way when the source rod is lowered, thus it is preventing the source from being exposed or from coming out of the tester. The rod when operated will move through different positions, but will not lock at those positions (i.e. safe, 6 inch, 8 inch and 12 inch). This is due to a pin engaging defect. The rod will fully retract. If the tester probe is locked, then the rod will not move through the positions. There are no known personnel exposures. "The tester is in a double locked room and the tester is in a locked DOT 7A container inside of a locked greenlee box. The only personnel having access to the keys and the testers are the LRSO and Alternate LRSO. This ensures that the tester is not used." Licensee is awaiting the results of a radiation survey of the storage area to be performed today (the last one performed was in April) and results from a leak test, which was performed on 27 June 07. The radiation survey was requested as a result of the tester failure and the leak test was performed, because it is the annual leak test period for the testers. The leak test was sent to our Army lab in Redstone, AL. Licensee has placed a call to expedite the analysis of the leak test and to check if they have received it. It is planned to transport the tester back to the manufacturer for disposition. Notified R3DO ( R. Lanksbury) and FSME EO (M. Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-07-02
43467 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2007-07-02 | 2007-07-02 16:51 | 2007-07-02 | SAFEGUARDS REPORT - LOSS OF CONTROL OF SAFEGUARDS INFORMATION Safeguards information was lost and uncontrolled for a period of time and then recovered. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-07-02
43466 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-07-02 16:00 | 2007-07-02 16:25 | 2007-07-02 | LOSS OF CONTROL OF SAFEGUARDS INFORMATION AT CONTRACT COMPANY Safeguards information uncontrolled for a period of time. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-07-02
43465 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2007-07-02 16:00 | 2007-07-02 16:24 | 2007-07-02 | SAFEGUARDS REPORT - LOSS OF CONTROL OF SAFEGUARDS INFORMATION Safeguards information was lost and uncontrolled for a period of time and then recovered. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-07-02
43464 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-06-29 | 2007-07-02 11:49 | 2007-07-05 | ARIZONA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The State provided the following information via email: "At approximately 4:00 PM June 29, 2007, the Agency [Arizona Radiation Regulatory Agency] was informed that the Licensee had a pickup truck stolen with a Troxler Model 3440 gauge, SN 35574. The theft occurred at approximately 2:40 PM when someone jumped into the truck, which was running while the employee loaded tools. The truck is a white 2006 Chevrolet. The Troxler gauge was locked in a 16 gauge steel tool box with a hardened and anti-theft designed lock and hasp. The steel box is bolted to the frame of the truck. The gauge contains 8 mCi of Cesium-137 and 40 mCi Am:Be-241. "Phoenix PD is investigating and has issued report number 2007-71277015 "The Agency continues to investigate this event. "The states of CA, NV, CO, UT, and NM, FBI, and Mexico are being notified of this event." Arizona Event Number: 07-009 * * * UPDATE FROM AUBREY GODWIN TO JOE O'HARA VIA E-MAIL AT 1230 ON 7/5/07 * * * "As of 4:00 PM July 3, 2007, the vehicle and device have been recovered. There is evidence the device was removed from the shipping container and the source possibly exposed. The Agency continues to investigate this event and the possible exposure of individuals. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." "Supplemental Notice: 07-009S." Notified R4DO(Powers), FSME(Moore), Mexico (via e-mail) and ILTAB (via e-mail) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-07-05
43463 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-07-02 07:15 | 2007-07-02 08:35 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * ENTRY OF AN UNAUTHORIZED PERSON INTO THE PROTECTED AREA "Actual entry of an unauthorized person into the protected area. The licensee notified the NRC resident inspector. Contact the Headquarters Operations Officer for additional details." * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2008-05-11
43462 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-06-29 17:52 | 2007-06-29 20:45 | 2007-06-29 | REACTOR TRIP AND SPURIOUS SAFETY INJECTION "At 1752 hours EDT Unit 2 received a 'B' train safety injection (SI). This spurious SI on 'B' train caused a trip of the main feedwater pumps and a turbine trip. The Unit 2 reactor tripped due to the turbine trip. The single train SI resulted in ECCS flow to the RCS. Both trains of SI were manually initiated per station procedures. The 'B' train of SI could not be reset and this resulted in RCS inventory increasing and lifting of the pressurizer PORV's. The pressurizer relief tank rupture disc ruptured and released water to the containment sump. SI flow to the core has been secured. Normal charging has been returned to service. This event is reportable per 10CFR50.72(b)(2)(iv)(A) for ECCS flow to the RCS. 10CFR50.72(b)(2)(iv)(B) for RCS Actuation (Rx/Turbine Trip). 10 CFR50.72(b)(3)(iv)(A) for AFW pump start, containment phase 'A' isolation, ECCS pumps actuation, and EDG starts. The AFW pump auto started during the event and operated as expected. Cause of the 'B' train SI is unknown at this time." All rods fully inserted. All systems functioned as required with the exception of the 'B' train SI which spuriously actuated and then could not be reset. All equipment started as expected from the SI actuation. AFW is still supplying cooling water to the steam generators at this time and decay heat is being discharged via steam dumps to the condenser. The licensee does not yet know how much water was discharged to the containment sump. The reactor is currently stable at no-load temperature and pressure with the level in the pressurizer a little high but tracking down to normal. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2007-06-29
43461 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-06-29 | 2007-06-29 14:23 | 2007-06-29 | AGREEMENT STATE - MASSACHUSETTS - DEUTERIUM CONTAMINATED WITH TRITIUM RECEIVED BY NON-LICENSED BUSINESS The agreement state provided the following information via facsimile: "The Agency was informed by a non-licensed business, Cambridge Isotopes Laboratory of 50 Frontage Road, North Andover, MA, that a shipment of deuterium water received from a foreign vendor, Ontario Power Generation, was contaminated with Hydrogen-3. Upon a customer complaint, the business hired a consultant to analyze an aliquot from the original batch shipment and the aliquot has been determined to contain 20 millicuries per liter of tritium. The business has also notified their employees, the vendor from which the shipment originated, and three of the company's customers in the United States that received finished, and contaminated , product from the company. Bioassay procedures are being implemented and surveys are commencing to determine if personnel became contaminated or if the facility became contaminated." This report has been assigned MA DPH / RCP docket # 06-7156. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-07-04
43460 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-06-29 11:00 | 2007-06-29 13:38 | 2007-07-05 | AGREEMENT STATE REPORT - CONTAMINATED AREA The agreement state provided the following information via facsimile: "During response to a fire, an on-site response personnel monitored area dose rates of 4 mrem/hour beta dose at waist level in an area about 20 meters east of building. On 06/29/07 Agency representatives and licensee confirmed area dose rates. Area was on pavement inside a fenced area. Caution tape was used to isolate the area. The licensee does not have regularly scheduled work hour on Friday, so the contract RSO said he will respond on Monday. This event does not appear to be related to the fire on-site [EN# 43447] because there is visible metallic contamination in the proximity of scrape-like tracks in the pavement. Suspected contaminate is DU." Discovery date and time was 06/27/07 at 02:00 EDT. * * * UPDATE AT 1008 EDT ON 7/5/07 FROM BRUCE PACKARD TO S. SANDIN VIA FAX * * * The following information was provided as an update: "On 7/2/07 contract RSO performed survey of the area. Licensee sealed the most active area with roof coating (thin non-fibrous roofing cement). Dose rates were reported to drop by a factor of 2. When the coat cures the licensee will add another coat. "Rough calculation confirmed this spill is greater than 5 X 105 CMR 296 B values. "Because Starmet was required to provide multiple agency access to this area as part of CERCLA cleanup, it is unlikely that the cause of the event or the responsible party will be identified." Notified R1DO (Rogge) and FSME (Moore). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-07-04
43459 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-05-30 | 2007-06-29 12:28 | 2007-06-29 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE The licensee provided the following information via facsimile: "Oceaneering reported an over exposure to one of the industrial radiographers. The RSO received a notification from Landauer of an over exposure to the licensee's employee. This employee received a dosage on his May 2007 badge of 5549 mrem (deep) and a year to date dosage of 5788 mrem. The RSO is going to discuss this issue with the employee and send the LDEQ additional information. Once the additional information is received, it will be forwarded to the NRC. "Louisiana Event Number - LA070016" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-07-04
43458 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-06-29 00:14 | 2007-06-29 00:20 | 2007-06-29 | RADIATION MONITORING INFORMATION TO ERDS AND SPDS WILL BE UNAVAILABLE DURING PLANNED UPGRADE TO THE SYSTEM. "The computer servers which supply radiation monitoring information to the ERDS (Emergency Response Data System) and SPDS (Safety Parameter Display System) systems will be taken out of service to implement a planned upgrade. The servers are being replaced with upgraded models and are expected to be out of service for approximately 4 to 8 hours. The ability of radiation monitors to alarm in the control room will be unavailable while the servers are being replaced. The in plant radiation monitoring skids will be unaffected, as will any automatic actions generated by the monitors. The safety related radiation monitor displays in the control room will also remain available. As a compensatory measure while both servers are unavailable, a dedicated radiation protection technician will monitor the in plant radiation monitor skids to update the control room if anomalous indications are observed. In addition, operations will record the safety related radiation monitor readings every 2 hours. "This is an 8 hour reportable event per 10CFR50.72(b)(3)(xiii), Major Loss of Assessment Capability. The operations of BVPS Unit 2 plant systems is not affected by this planned action. BVPS Unit 1 is not affected by this planned action. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1736 EDT ON 6/29/07 FROM G. STOROLIS TO W. HUFFMAN * * * The Radiation Monitor System Servers have been upgraded and returned to service and the Radiation Monitoring Information to the Emergency Response Data System (ERDS) and Safety Parameter Display System (SPDS) is now available and returned to service. The licensee will notify the NRC Resident Inspector. R1DO (Powell) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-29
43457 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2007-06-28 17:17 | 2007-06-28 21:53 | 2007-06-28 | REACTOR TRIP DUE TO CONDENSATE PUMP TRIP "Reactor trip at 1717 hrs PDT due to [condensate pump] COND-P-2B trip. Reactor power was at 70% with [condensate pump] COND-P-2A secured. Reactor vessel level reached -50 inches and was restored with High Pressure Core Spray and Reactor Core Isolation Cooling. Main Steam Isolation Valves closed as expected due to the reaching -50 inches. All systems operated as expected. Further investigation into COND-P-2B trip is underway. Plant is stable in mode three, heat removal is being maintained by RHR-P-2B and Safety Relief Valves." All rods fully inserted on the automatic reactor scram. All safety systems were available at the time of the trip. The trip was considered uncomplicated. The reactor pressure is currently being maintained between 500 to 600 psi and water level between 60 to 80 inches. The licensee was at 70% power at the time of the trip due to maintenance of condensate pump P-2A. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-06-28
43456 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2007-06-27 13:50 | 2007-06-28 12:18 | 2007-06-28 | MEDICAL TREATMENT WITH CONTAMINATION "On June 27, 2007 a Honeywell employee sustained multiple contusions and abrasions to his head, face, and body as a result from a fall from the permanently installed man-lift device. The incident occurred at 1350 at the Honeywell Specialty Materials facility (Feeds Material Building) in Metropolis, IL. The employee was transported to the local medical facility with measurable levels of natural uranium contamination of 5,000 dpm/100 cm² on his clothing and skin. "Honeywell Health Physics personnel accompanied the injured employee to the hospital where they provided contamination control recommendations to the attending medical staff. No contamination was detected on hospital facilities, equipment or staff following the treatment of the injured employee. "Following decontamination of the injured employee survey results were less than 1,000 dpm/100 cm². "All contaminated materials from the injured employee's decontamination and treatment were collected and returned to the Honeywell Specialty Materials site." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(3) |  |  |  | 0 | 2007-06-28
43455 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-06-28 09:55 | 2007-06-28 10:56 | 2007-06-28 | LOSS OF GREATER THAN 25% OF THE EPZ SIRENS FOR GREATER THAN 1 HOUR "This eight hour notification is being made per 10 CFR 50.72(b)(3)(xiii) to report a loss of >25% of the EPZ sirens for greater than one hour. 44 of 165 offsite sirens are not functioning due to loss of power/equipment problems because of a recent storm. Efforts are in progress to restore the affected sirens. "At 1000 6/28/07 less than 25% of sirens are unavailable." The licensee notified the NRC Resident Inspector, the State of Pennsylvania, and local governments. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-28
43454 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-06-27 15:55 | 2007-06-27 18:44 | 2007-06-29 | TECHNICAL SUPPORT CENTER HABITABILITY ISSUE "At 15:55 ET on 6/27/07 - notified by the Vogtle Emergency Preparedness that the limit switch full closed indication on the Technical Support Center (TSC) HVAC Outside Air Damper not being functional [which] impacted habitability of the TSC. This is due to the full closed limit switch providing a signal to inflate the sealing boot on the associated damper. This is reportable under 10CFR 50.72(b)(3)(xiii). (8 hour notification) "At 6:53 ET on 6/27/07 - TSC HVAC was placed in service in the filtration mode with the damper limit switch manually adjusted to provide full closed indication. The TSC HVAC is fully functional and supporting TSC habitability at this time. "TSC HVAC will remain in service in the filtration mode until the repair plan for the damper is implemented." The licensee notified the Region 2 Duty Officer (Ayres). * * * UPDATE AT 1037 0N 6/29/07 FROM C. WILLIAMS TO P. SNYDER * * * "A plan has been created to repair the limit switch on the TSC HVAC Outside Air Damper. This will require securing the TSC HVAC for a period of time, thus rendering the TSC non functional. A plan has been written to cover required actions to be taken in the event of a plant event, in accordance with 10CFR50.54(q). Estimated outage time is four hours, it may be shorter depending on actions required to adjust limit switch to return full functionality to the TSC HVAC. You will receive a follow-up call when full TSC functionality has been restored." The licensee notified the NRC Resident Inspector. Notified R2DO (Ayers). * * * UPDATE AT 1249 EDT 0N 6/29/07 FROM C. WILLIAMS TO W. HUFFMAN * * * "The TSC HVAC outside air damper limit switch has been repaired and the TSC has been returned to functional status. The TSC HVAC was non-functional from 11:24 to 12:17 EDT." The licensee notified the NRC Resident Inspector. R2DO (Ayres) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-27
43453 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2007-06-27 10:15 | 2007-06-27 15:20 | 2007-06-28 | LOSS OF COMMUNICATIONS CAPABILITY AT EOF "At approximately 1015 On June 27, 2007, with the James A. Fitzpatrick (JAF) Nuclear Power Plant operating at 100% reactor power, a loss of phone service occurred in the Emergency Operations Facility (EOF) and Joint information Center (JIC). "Discussions with the Oswego County 911 Center (only county within the 10 mile EPZ) determined that phone service in the service area was lost at approximately 1015 hours on June 27,2007. Most telephone and data capability at the EOF and JIC are out of service at this time. Cellular arid satellite phone backups are available at the EOF and JIC. The primary and backup means to notify federal, state and local agencies from JAF are unaffected and have been tested and are operational. The Emergency Response Organization (ERO) notification system is unaffected and has been confirmed to be operational. Sirens and tone alert systems are unaffected. "This loss of phone service is considered to be a major loss of offsite communications capability and is therefore reportable as an eight (8) hour telephone notification under 10 CFR 50.72(b)(3)(xiii). "Repairs are in progress. "The NRC resident inspector has been briefed and the New York State PSC will be notified." See related Event #43451. * * * UPDATE AT 1242 EDT ON 6/28/07 FROM PAGE TO HUFFMAN * * * "Phone service has been repaired, tested and restored to the EOF and JIC. The NRC Resident and New York State PSC have been informed. R1DO (Powell) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-27
43452 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-05-03 00:58 | 2007-06-27 15:17 | 2007-06-27 | INVALID SYSTEM ACTUATION "This event is being reported in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A). This condition meets the criteria of 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that results in manual or automatic actuation for any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B). The specific requirements apply here to 'General containment isolation signals affecting containment isolation valves in more than one system.' "During the performance of surveillance instruction 'Low Pressure Coolant Injection (LPCI) 'B' and 'C' Initiation and Loss of EH12 Response Time Test,' the following valves auto closed during the test activities: - 1G61-F0075 (Containment Equipment Drain Inboard Isolation), - 1G61-F0165 (Containment Floor Drain Inboard Isolation), - 1P11-F0090 (Containment Pools Drain Inboard Isolation), and - 1P50-F140 (Containment Vessel Chilled Water Inboard Return MOV Isolation) "The signals are considered to be invalid as the signals were a result of test activities and not actual plant conditions. The valve logic to close the valves was momentarily satisfied due to the sequence of electrical power restoration during the test; however, the test did not address the valve movement and the valve actuations could not be considered to be preplanned. The system actuations were considered to be partial, and the valves functioned successfully as designed. "The event was captured within the corrective action program under condition report (CR) 07-19866. "The resident inspector was notified of this event notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-06-27
43451 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2007-06-27 10:15 | 2007-06-27 14:33 | 2007-06-27 | LOSS OF COMMUNICATIONS CAPABILITY AT EOF "At approximately 1015, Nine Mile Point Emergency Planning noted the loss of phone service in the Emergency Operations Facility (EOF) and Joint News Center (JNC) during a routine surveillance. Nine Mile Point emergency planning staff were subsequently notified at 1030. [During] discussions with the Oswego County 911 center (sole 10 mile EPZ county), it was determined that phone service in the Windstream phone company that services that area was lost at approximately 1015 hours. Most telephone and data capability at the EOF and Joint Information Center (JIC) is out of service at this time. Cellular and satellite phone backups are available. The primary and backup means to notify the local and state agencies from Nine Mile Point and JA Fitzpatrick is unaffected and has been tested as operable. The Emergency Response Organization (ERO) notification system is unaffected and has been confirmed as operable. Sirens and tone alerts are unaffected. "Local phone service provider is investigating cause which is currently unknown." The licensee notified the NRC Resident Inspector. See related Event #43453. * * * UPDATE FROM MINNICK TO HUFFMAN AT 2034 EDT ON 6/27/07 * * * "Repairs to the emergency phone systems have been completed and all systems tested satisfactory as of 2012 on June 27, 2007." The licensee notified the NRC Resident Inspector. R1DO (Powell) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-27
43450 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2007-05-01 23:39 | 2007-06-27 12:56 | 2007-06-27 | INVALID SYSTEM ACTUATION "This telephone notification to report an invalid actuation is provided in accordance with 10 CFR 50.73(a)(1), which states, 'In the case of an invalid actuation reported under Sec. 50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' The specific reporting requirement in 10 CFR 50.73(a)(2)(iv)(A), states, 'Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).' For this report, the affected system was the emergency AC electrical power systems as listed in 10 CFR 50.73(a)(2)(iv)(B)(8). Specifically, the Train A emergency diesel generator (EDG) automatically started due to an invalid system actuation. "On May 1, 2007, at approximately 2339 hours (EDT), with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in MODE 5 with reactor coolant system temperature at approximately 84 degrees F, during activities associated with surveillance testing as part of Refueling Outage 24, the Train A EDG automatically started from the standby condition. The Train A EDG did not automatically connect to the associated emergency bus (E-1), because no E-1 bus undervoltage (UV) signal was present. The automatic start was caused by the inadvertent grounding of a test connection lead that was being used to monitor the Train A EDG during testing. The grounding of the test lead resulted in a drop in voltage on the starting circuitry that caused the actuation of the 4A diesel start relay. The Train A EDG successfully started and achieved the required speed and voltage. As previously stated, the EDG did not load because no UV signal was present on the associated E-1 bus. No failures or abnormalities were noted. "The Train B EDG remained operable during this event and the Train A EDG was able to provide power to E-1 emergency bus, if necessary. "The invalid EDG start event was entered into the corrective action program for HBRSEP, Unit No. 2. The investigation of this event has been completed. The results of the investigation determined that the EDG start was caused by improper isolation of a safety significant power source from the field installed equipment. The Plant Nuclear Safety Committee has reviewed the investigation associated with this reportable event and concurred with the investigation. Corrective actions for this event are in progress and are being tracked via the corrective action program." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-06-27
43449 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-06-27 09:21 | 2007-06-27 11:34 | 2007-06-28 | REACTOR TRIP DUE TO OFF-SITE POWER FLUCTUATION "Switchyard line 2001 tripped and re-energized during a thunderstorm. This caused main generator output breaker, ACB 3-4, to trip open. At this time '1D' reactor coolant pump (RCP) tripped and caused a reactor trip. Cause for the '1D' RCP trip is under investigation. "The heat sink is being provided by Aux Feedwater and the use of Steam Dumps. Electrical power is being provided by offsite power." All rods inserted. There were no complications during the trip and all systems functioned as required. Offsite power remained available throughout the transient. The electrical transient had no impact on Unit 2. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2217 EDT ON 6/28/07 FROM B. SHEAR TO W. HUFFMAN * * * "This is a revision to a previously transmitted ENS call on 6/27/07 EN# 43449. "Braidwood Unit 1 Reactor automatically tripped on a loss of '1D' RCP greater than P-8 setpoint. The cause of the RCP trip was an electrical disturbance during a thunderstorm. "The reactor trip automatically caused a main turbine and generator trip. Auxiliary feedwater system automatically started on the low-2 S/G water level that is expected from a full power reactor trip. Auxiliary feedwater and main steam dumps are providing a heat sink. "A switchyard line also tripped during this electrical transient causing multiple switchyard breakers to open. Electrical power is being provided by offsite power. "All control rods fully inserted. There were no complications during the trip and all systems functioned as required. Offsite power remained available throughout the transient. The electrical disturbance had no impact on Unit 2. "The licensee notified the NRC resident inspector." R3DO (Louden) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-06-27
43448 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2007-06-26 13:05 | 2007-06-27 09:29 | 2007-06-27 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "The SC Department of Health and Environmental Control (DHEC) was notified on Tuesday, June 26, 2007, at 1315 hrs, that a Humboldt Model EZ 5001, s/n 4965, containing 10 mCi of Cs-137 and 40 mCi of Am-241:Be, had been damaged at 1305 hrs on June 26 2007. The RSO stated that the gauge had been damaged by a bulldozer. [The SC DEHC] Duty Officer responded to the scene and arrived at 1510 hrs. The area around the gauge had been properly roped off and the source rod was locked in its shielded position. The gauge handle and rod had been snapped off at the top of the gauge and the top of the gauge was cracked open at the rod end. The gauge was secured in the transport container and the inspector advised the RSO to return the gauge to the permanent storage location, secure it from further use, and to contact the gauge manufacturer for further instruction regarding disposal. "The RSO was advised by [the SC DEHC] to submit a written report detailing this event to the Department within 30 days. The event is open and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system. "Location: Calvary Baptist Church, 3810 Grandview Drive, Spartanburg, SC" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-07-02
43447 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-06-26 20:00 | 2007-06-27 09:05 | 2007-07-12 | AGREEMENT STATE REPORT - SMALL FIRE AT LICENSEE'S FACILITY "On Wednesday, June 26, 2007, at approximately 8:00 PM EST a fire was reported at the Starmet NMI facility in Concord, Massachusetts [2229 Main Street]. Starmet NMI possesses two materials licenses with Massachusetts, License No. SM-0179 and License No. SU-1453. The fire occurred in the foundry area within the facility, formerly used for the manufacture of depleted uranium munitions. The fire appeared to be contained to a small area within the building, in the vicinity of a 55-gal drum, a 5-gal bucket and a small pile of metal shavings. "Radiological surveys performed once the fire was extinguished resulted in no elevated readings from any of these containers or the material. The investigation is ongoing and more information will be provided as it is obtained." * * * UPDATE FROM ROBERT GALLAGHAR TO SNYDER AT 1416 ON 7/12/07 * * * "The Concord Fire Department has determined the cause of the fire to have been the auto-ignition of metal filings and therefore non-suspicious in nature. The official fire investigation has been closed. No off-site radiological consequences resulted from this fire. Notified FSME (Holonich), R1DO (Lorson) via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-07-02
43446 | 0 | WATTS CONSTRUCTORS, LLC |  |  |  |  | 2007-06-26 13:00 | 2007-06-26 20:45 | 2007-06-26 | NUCLEAR MOISTURE DENSITY GAUGE STOLEN FROM CONSTRUCTION SITE At approximately 1300 HST on 6/2607, the licensee discovered that their Nuclear Moisture Density Gauge, a CPN Model MC-3 Serial Number M3409007585, had been stolen from a storage shed at the construction site. The outer storage shed lock and the lock on the gauge's storage container were cut. In addition to the gauge some propane equipment was also taken. The Honolulu PD is on-site conducting an investigation. The construction site is located on Ford Island (federal property portion) in Pearl Harbor near Building 184. The project is for NOAA with contract administration provided by Department of the Navy. The last known use of this particular gauge by the licensee was on 6/8/07. The licensee is evaluating whether to offer a reward for the return of the stolen gauge. The licensee's RSO was informed of the theft by staff at the construction site. Notified the State of Hawaii Rad Health. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-06-26
43445 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2007-06-25 | 2007-06-26 19:12 | 2007-06-26 | OREGON AGREEMENT STATE REPORT - UNDERDOSE DUE TO EQUIPMENT MALFUNCTION "On June 25, 2007, during a patient treatment, the computer operating the Varian VariSource High Dose Rate After loader reported an error 18, Wire drift detected. This indicated that the source wire positioning system was out-of-specification and the HDR was terminating treatment. Treatment was immediately discontinued and the patient removed from the room. The positioning QA was performed and the system found to be within typical operating limits. The treatment was resumed, but the same error recurred. Treatment was discontinued with only a partial treatment delivered. No errors in positioning or site occurred. The physician and patient were notified immediately after the treatment was terminated. "Varian Service was notified of the occurrence and a field engineer was dispatched to clean the system the following day. The source and dummy wire transport systems were cleaned and tested. The medical physicists performed several QA tests concerning positioning and source output, and certified the HDR After loader system as ready for patient treatment. "Dosimetry reconstruction of the delivered dose indicates that 17.8% of the prescribed dose was delivered. Physician will reconstruct new treatment plan. Treatment Details: The patient was receiving HDR treatment #2 to a Miami vaginal cylinder with tandem. This apparatus is connected to the HDR After loader (with radioactive wire) with 7 separate connecting tubes, one for each treatment channel. During connection, bloody fluid was noted on one of the connectors, cleaned, and the tube connected. The treatment was initiated, but after that tube was treated, the device's computer indicated the wire positioning was not reproducible (error code 18 - Wire drift detected) and the treatment was paused. The QA positioning test was run and within acceptable limits. The treatment was continued, but the device again indicated positioning errors. The treatment was discontinued without being fully completed. "Protective caps covering the tubes were removed in surgery instead of waiting until the patient arrived in the department, a typical procedure that had not caused an incident in the past. In the future, it is prudent to leave them connected until the patient is ready to be connected to the treatment device. Two lessons learned from this experience: For HDR cases using a tandem, the tandem channel should be treated first, since the prescribed dose is more influenced by tandem dose than by ovoids or vaginal cylinder. The protective caps on the applicator should be left on as long as possible to reduce or preclude any fluid in the closed system. "Device: Varian VariSource High Dose Rate After loader, S/N#: 600379, SS&D #: CA-0661-D-103-S, Source: Alpha - Omega Model #: VS 2000, SS&D #: CA-1080-S-102-S, S/N #: 02-01-0588-001-041907-10089-97, Activity: 10.089 Ci on 4/19/07" * * * UPDATE AT 0844 EDT ON 6/26/07 FROM FSME (FLANNERY) TO JASON KOZAL VIA EMAIL * * * "This event (EN43443) has been reviewed and determined to be a reportable medical event." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2007-07-02
43444 | 0 | SOIL & MATERIALS ENGINEERING, INC. |  |  |  |  | 2007-06-25 15:00 | 2007-06-25 18:00 | 2007-06-25 | TROXLER MOISURE DENSITY GAUGE SOURCE FOUND MISSING AFTER FIELD USE A Troxler Moisture Density Gauge, Model 3430 S/N 22053, was evaluated in the shop after use at a temporary jobsite two hours earlier today in Royal Oak, MI. At the time the Authorized User (AU) attributed the inconsistent G-M readings to survey instrument error. However, further evaluation in the shop noted that the Cs-137 source (8 mCi) connected to the extendable source rod was missing. The licensee is enroute to the temporary jobsite in an effort to locate and recover the missing source. * * * UPDATE AT 2000 EDT ON 6/25/07 FROM FRANK HENDERSON TO S. SANDIN * * * The licensee located and recovered the missing source. The source, shielded in a portable container of sand, is enroute to their facility in Plymouth, MI where the licensee will contact Troxler Labs for assistance. Established conference call between R3 (Shear, Gattone) and the licensee (Henderson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | SAFETY EQUIPMENT FAILURE | [8 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) | 30.50(b)(2) |  |  | 0 | 2007-06-25
43443 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-06-19 | 2007-06-25 16:45 | 2007-06-26 | AGREEMENT STATE REPORT INVOLVING HIGHER THAN PRESCRIBED DOSE DELIVERED The following notification was received from the State of NY Bureau of Environmental Radiation Protection via fax: "AS Agency -New York State Department of Health "Event Report - ID # NYS DOH 07-002 "Licensee Name and License Number - Withheld as per NYS Law "Event Date - June 19, 2007 "Event Type - Medical Event "Event Description: "A medical event involving yttriurn-90 Zevalin (Ibritumomab Tiuxetan) for treatment of non-Hodgkin's lymphoma was reported to NYS DOH by telephone on June 22, 2007. The authorized physician user (AU) approved a dosage of 29 mCi for treatment on June 19, 2007, however a dose of 36.7 mCi was administered. "This Zevalin patient (A) was scheduled to receive treatment at the hospital on June 19, 2007. The radiopharmacy prepared the dose but observed that the assay from the supplier was approximately 10 mCi higher than their assay. They reviewed their data including their most recent calibration of the dose calibrator with a NIST traceable syringe standard. They decided to use their NIST traceable calibration factor and associated assay. The dose was dispensed and the patient was treated. "Another Zevalin patient (B) was scheduled for treatment on June 20, 2007. In preparing patient B's dose the radiopharmacy observed the same condition as with patient A's assay. At this point they realized they had a problem and patient B's dose was not dispensed. An investigation began. "The radiopharmacy identified the error. They used an AEA Technology QSA Inc. model SIM.SY2 (Sealed Source Registry No. MA-1059-S-360-S) to calibrate their Capintec CRC-15R dose calibrator as well as the hospital's dose calibrator. This source is specifically designed to calibrate Capintec CRC-15R units for yttrium 90 assays. The calibration source label has an assay of 20mCi (740 MBq) of strontium 90/ytrrium 90 and a calibration date of Nov. 14, 2004. However, the source certificate lists the yttrium 90 'Equivalent Activity' as 30.68 mCi (1135 MBq), which is the value that should have been used for the calibration. Apparently the certificate was not available (misplaced?) on June 8 &10 for the calibration. The radiopharmacy used the decay-corrected value from the label rather than a decay-corrected value of the certificate's 'Equivalent Activity'. Since the same calibration error was performed on the hospital's dose calibrator, the hospital's assay matched up with that of the radiopharmacy and with the intended dosage. "The patient's daughter and the referring physician were notified on the day after discovery. The treating physician is assessing situation and the possible effects to the patient. "Intended dose - 29 mCi "Delivered dose - 37.6 mCi "Date of treatment - 6/20/07 "Date of error discovered - 6/20/07 "Isotope/drug - yttrium-90/Zevalin "Reported/notification dates: "Patient/patient rep. - 6/20/07 "Referring MD - 6/20/07 "NYS DOH - 6/22/07 "Cause: Dose calibrator calibration error "Effect - patient's condition and effects are being assessed "Investigation - RCA required "Initial Written report due 6/29/07" * * * UPDATE AT 1107 EDT ON 6/26/07 FROM FSME (FLANNERY) TO JASON KOZAL VIA EMAIL * * * "This event (EN43443) has been reviewed and determined to be a reportable medical event." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2007-06-29
43442 | 0 | WYETH RESEARCH LABORATORY |  |  |  |  | 2007-06-11 | 2007-06-25 13:09 | 2007-06-29 | ANALYTICAL INSTRUMENT SHIPPED OFF SITE WITH RADIOACTIVE SOURCES INSTALLED During a scheduled radioactive source leak test and inventory activity on 18 June 2007, the licensee discovered two Ni-63 sources missing. It was determined that the sources had been shipped off site with the analytical instrument they were installed in on 06/11/07 for an upgrade to a part of the instrument not related to the radioactive sources. The device is a Berger supercritical fluid extraction device and the sealed source device is an Accenture G-2390A, source serial numbers U0891 and U0892. Each source activity level is 14 millicuries. The instrument is scheduled to be returned to the licensee after the upgrade is complete on 06/28/07. The licensee plans to remove the sources from the instrument since their lab has never used that portion of the instrument in the operation of their laboratory. * * * UPDATE FROM WICKLINE TO HUFFMAN AT 1408 EDT ON 6/29/07 * * * The licensee provided the following information via email: The Berger Supercritical Fluid Chromatography instrument with the generally licensed Ni-63 source was returned to Wyeth on 6/29/07. The source was intact. Doses to personnel from the source are not expected because Ni-63 is a weak beta emitter. R1DO (Powell) and FSME EO (Flannery) notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-06-25
43441 | 0 | BLAZOSKY ASSOCIATES, INC |  |  |  |  | 2007-06-25 09:40 | 2007-06-25 10:02 | 2007-06-25 | DAMAGED TROXLER MOISTURE DENSITY GAUGE The Radiation Safety Officer (RSO) of Blazosky Associates, Inc. called to report a damaged Troxler gauge. The damage occurred at the ERPA site on 06/25/07 as a pickup truck backed over the gauge. At the time the gauge was retracted and not actively in-use. The employee at the site called the RSO. The employee visually examined the gauge and saw that the sources were intact and the shutter still closed. No leakage was found. The RSO will conduct a leak test and radiation check and return the instrument to Troxler. The gauge is a Troxler Model 3440, Serial Number 29883. Sources were 8 mCi of Cs-137 and 40 mCi of Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-06-25
43440 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2007-06-21 20:00 | 2007-06-22 03:34 | 2007-06-22 | "SPDS (SAFETY PARAMETER DISPLAY SYSTEM) INOPERABLE DUE TO PLANT COMPUTER INOPERABILITY "The Wolf Creek Nuclear Plant Information System (NPIS; Plant Computer) was conservatively declared inoperable at 2000 (CDT) on 06/21/2007 due to questions concerning accuracy of some of the computer point outputs. Initial troubleshooting and investigation identified that some computer points may be reading 0.1% to 0.2% lower than actual process parameter. Investigation is ongoing to determine the scope and cause for this condition and to correct the problem. Compensatory measures for loss of NPIS are being implemented in accordance with procedure OFN RJ-023, NPIS Malfunctions. The plant is stable with power being maintained at or below 100% based on Nuclear Instruments." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-22
43439 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2007-06-21 16:30 | 2007-06-21 17:29 | 2007-06-21 | ITEM RELIED ON FOR SAFETY NOT RELIABLE UNDER ALL SCENARIOS. "During a review of the Integrated Safety Analysis for an additive addition step, it was determined that one of the Items Relied on for Safety (IROFS), as documented in the ISA Summary was not reliable. This report is submitted for administrative reporting pursuant to 10CFR70.50 Appendix A (a)(5). At no time did an unsafe condition exist. The existing criticality safety analysis of the operation bounded the situation, was effective and was not challenged. "The IROFS described for the additive sequence did not prevent incorrect type of additive from being added under all scenarios. "All affected equipment is in the process of being shut down pending revision of the ISA IROFS for this additive addition process. Units will remain shutdown pending final investigation and implementation of additional preventive actions. "Independent controls on moderation remained intact. The as found condition was previously analyzed and demonstrated to be safe. At no time did an unsafe condition exist." Licensee will notify NRC Region 2, North Carolina Radiation Protection Agency, and the New Hanover County Emergency Management Agency. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | PROTECTIVE ACTION PREVENTED | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(a) |  |  |  | 0 | 2007-06-21
43438 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2007-06-21 01:42 | 2007-06-21 16:26 | 2007-06-21 | FIRE DUE TO SEQUENCING PROBLEM "At approximately 0142 hours on 6/21/2007, during Solid Waste Uranium Recovery (SWUR) operations, a sequencing problem caused a cardboard box containing combustible waste with about [Deleted] U-235 to be fed on top of a closed feed hopper door. As the equipment cycled the incinerator fire door, the box, which was on top of the feed hopper door ignited. The box was inside the feed hopper containment shroud when it ignited. The integrity of the containment shroud remained intact during the fire. However, some smoke did escape into the room. "Operational personnel put out the fire (a single box of 3.5 cubic feet) using a hand held fire extinguisher. "The plant emergency response team (PERT) was activated via plant paging system at 0145 and the Richland Fire Department was called. The Richland Fire Department arrived at 0155. With appropriate PPE (SCBA), two PERT and two Richland Fire Fighters entered the facility and confirmed that the fire had been previously extinguished. "The SWUR process is currently shut down and will remain down pending investigation and completion of appropriate corrective actions. "The fire was limited to a single 3.5 cubic foot box containing [Deleted] U-235. All facility HEPA filters remained undamaged during the event." There was no release of radioactive materials. All areas surveyed after the fire was extinguished were free of radioactive contamination. The individuals that put out the fire and the individuals that subsequently entered the area to confirm that the fire had been extinguished were evaluated for internal contamination with negative results. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 70.50(b)(4) |  |  |  | 0 | 2007-06-21
43437 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-05-05 12:00 | 2007-06-21 14:07 | 2007-06-21 | SPECIAL NUCLEAR MATERIAL DISPOSAL RECORDS INCOMPLETE DURING ACCOUNTABILITY AUDIT "In accordance with the requirements of 10 CFR 2.390, Public inspections, exemptions, requests for withholding, Section (d)(1), Exelon Generation Company, LLC (EGC) requests that the following information is subject to disclosure only in accordance with the provisions of 10 CFR 9.19, in that the information concerns the material control and accountability program. "This is a non-emergency Event Notification made in accordance with 10 CFR 20.2201 (a)(1)(ii) to inform the NRC of lost or missing licensed material. "In preparations for an upcoming Special Nuclear Material (SNM) Control and Accountability (MC&A) audit, Dresden Nuclear Power Station (DNPS) has determined that for items containing less than 1 gram of special nuclear material, records of all shipments are not retrievable and may not have been maintained. 10 CFR 70.51 states that disposal records shall be forwarded to the NRC prior to license termination, which indicates that the licensee should retain records until license termination. It has been determined that prior to 1988, DNPS did not maintain records of non-fuel SNM less than 1gram to the required level and that after 1988, the records retention requirements only required retention of the SNM shipment documentation for 3 years after transfer of the material. These situations resulted in records discrepancy in the shipment of non-fuel SNM less than 1gm. A search of storage locations was performed and the detectors were not located on-site. "This lack of records is not an indication of theft or diversion of the Special Nuclear Material. "As the shipment records cannot be located, there is a lack of records documenting the current location of the detectors; however, based on available records and station practices, it is believed that these detectors were shipped in accordance with procedures and applicable regulations as radioactive waste to a licensed low level radioactive waste disposal facility (i.e. Barnwell) or to other licensed facilities (i.e. another nuclear station, item vendor). DNPS is working with Barnwell and other non-fuel SNM shipment locations such as potential returns to the fabricator and inter-company shipments to attempt to find records of shipments. "Current records searches have resulted in 67 detectors that are documented to have been received on-site but for which there is no shipment or disposal record. The detector type with the highest quantity of SNM is an LPRM, which has approximately 0.001 gram per detector string. Conservatively assuming all 67 items are LPRMs strings, the total quantity of SNM that has been documented to have been received on-site but for which there is no shipment or disposal record is 0.1206 gram of special nuclear material. "This notification satisfies the 30-day notification requirement of 10 CFR 20.2201 (a)(1)(ii). A subsequent written report will be made in accordance with 10 CFR 20.2201(b)." The licensee notified the NRC Resident Inspector. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 20.2201(a)(1)(ii) |  |  |  | 1 | 2007-06-21
43436 | -1 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-06-21 03:15 | 2007-06-21 04:05 | 2007-08-01 | HPCI INOPERABLE DUE TO QUARTERLY VALVE STROKE TEST FAILURE "During performance of the quarterly HPCI valve stroke test the HV-55-2F006, HPCI pump discharge isolation valve to Core Spray failed to open within the maximum allowed time. The HV-55-2F006 valve is a motor operated valve and the maximum allowed opening time is 17.25 seconds. The valve was given an open signal via the hand switch as required by the test but did not initially respond. Several minutes later the valve went full open. HPCI was declared inoperable at 0315 on 6/21/2007. Cause for valve stroke time failure is not known at this time." As a result, the licensee is in a 14 day shutdown LCO. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM ARNOSKY TO HUFFMAN AT 0807 EDT ON 8/01/07 * * * This is a retraction of the event notification made on 6/21/07 at 04:05 hours EDT. This event (#43436) was initially reported as a condition that at the time of discovery could have prevented the fulfillment of the High Pressure Coolant Injection (HPCI) system safety function under the requirement of 10CFR50.72(b)(3)(v)(D). The Unit 2 HPCI system was declared inoperable due to failure of the HPCI pump discharge isolation valve to Core Spray to open within the maximum allowed time during surveillance testing. The valve was required to open within 17.25 seconds but opened several minutes after the open signal was initiated. The open contactor was replaced and the valve was successfully tested. The affected valve was declared operable on 6/22/07 at 04:07 hours. The HPCI system was restored to operable on 6/23/07 at 04:07 hours following completion of maintenance and testing activities. An evaluation determined that HPCI was capable of injecting sufficient flow to complete its safety function through the unaffected operable injection flow path to the feedwater header. The achievable flow rate would have exceeded the leakage from a one-inch liquid line break. Also, HPCI operation remained capable of being terminated by operator action during an ATWS event. Therefore, HPCI remained capable of fulfilling its safety function while the injection flow path to Core Spray was unavailable. A condition did not exist at the time of discovery that could have prevented the fulfillment of the HPCI safety function. The licensee notified the NRC Resident Inspector. R1DO (White) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-06-21
43435 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2007-06-20 22:50 | 2007-06-21 03:24 | 2007-06-21 | FAILED INSTRUMENT AIR HEADER LEADS TO MANUAL REACTOR TRIP At 2250 on 6/20/07, "Instrument Air header pressure failed at a brazed joint. The loss of Instrument Air pressure caused the Steam Generator (S/G) Feedwater Regulating Valves to stop controlling and S/G level, E-088, to rise uncontrolled. Control Room Operators tripped the reactor manually. Main Feedwater Pumps were manually tripped to stop excess feedwater to the S/Gs. Loss of Instrument Air failed the normal cooling to Containment. Containment Emergency Cooling units were manually started to provide containment cooling. The standard post trip actions were carried out with all safety functions satisfied." The site is proceeding with post trip recovery. The Instrument Air leak was isolated at 2321 PDT. All control rods fully inserted on the manual trip. RCPs are in operation transferring decay heat to the S/Gs. Emergency feedwater is feeding the S/Gs with steam being discharged to the condenser via the steam dumps. Atmospheric relief valves were used to discharge steam to the atmosphere initially for approximately 20 minutes following the trip. There are no primary to secondary tube leaks. Containment isolation failed closed as expected following the loss of instrument air pressure to the containment. Normal offsite power is available and the emergency diesel generators are available if needed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-06-21
43434 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2007-06-18 16:00 | 2007-06-20 18:54 | 2007-06-20 | OREGON AGREEMENT STATE REPORT - POTENTIAL UNDERDOSE TREATMENT TO LIVER "Written order was requested for a therapy dose of 2.45 GBq (66.2 milliCuries) of Y-90 TheraSphere for treatment to the patient's liver. 1.74 GBq (47 milliCuries) was received from MDS Nordion and used for treatment. Calculation error may have contributed to under treatment with approximately 80 Gray delivered to the liver with an intended dose of 100-110 Gray. Concern to not exceed lung dose of 15 Gray achieved with treatment dose at low end of optimal range. Physician notified and will consult with patient to decide whether to conduct additional treatment." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2007-06-26
43433 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2007-06-20 13:55 | 2007-06-20 16:35 | 2007-06-20 | MAJOR LOSS OF EMERGENCY ASSESSMENT CAPABILITY - 13 OF 44 EMERGENCY SIRENS OUT OF SERVICE "On June 20, 2007, a disturbance on the transmission system was experienced causing a loss of 13 of 44 emergency sirens (approximately 30 percent) for Clinton Power Station. At 1355 hours (CDT), since power was not restored to these sirens within one hour, this event was determined to be a major loss of emergency assessment capability. At 1512 hours, only 6 sirens (14 percent) remain out of service. At this time, an estimated return to service has not been provided for the remaining sirens." "DeWitt County, Illinois Emergency Management Agency, and the NRC Resident have been informed of this information. " | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-20
43432 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-05-16 | 2007-06-19 14:37 | 2007-06-19 | LOUISIANA AGREEMENT STATE REPORT - MEDICAL EVENT DUE TO DISPENSING ERROR The State provided the following information via facsimile: "Description of Event - A customer called the [Cardinal Health] pharmacy on Wednesday, May 16, 2007 to report that the late injection of Tc-99m sestamibi, a heart imaging agent, showed no heart uptake on the film. Instead there was only soft tissue uptake. The activity dispensed and injected matched the prescription. The next day the patient was brought back to the department and the image indicated that the dose injected was Tc-99m medronate, a bone imaging agent. "Investigation and Root Causes - A large dose of Tc-99m sestamibi was ordered at 0600 calibrated for 1400. A biliary dose was also ordered at the same time. These were the only two doses drawn at that time. After notification by the hospital, an investigation revealed that the activity and volume remaining in the sestamibi vial plus the volume and activity dispensed matched the total volume and activity of the prepared kit (after correction for decay). The concentration for the sestamibi kit is normally 30% greater than for a bone imaging kit. Since the volume was correct, no flags were detected during dispensing. It is not Cardinal Health policy to test used syringes due to blood borne pathogen hazards. No other clients that were dispensed doses from the same vial reported errors in imaging. From this analysis, Cardinal Health can find no errors on its part to account for the imaging error. "Actions Taken to Prevent a Recurrence - Cardinal Health has protocols in place to prevent dispensing errors of the type described above. Since the error cannot be attributed to Cardinal Health, corrective action is unnecessary. LA event Report ID No.: LA070015 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-06-25
43431 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-06-13 11:00 | 2007-06-19 14:41 | 2007-06-19 | AGREEMENT STATE REPORT FROM MASSACHUSETTS - CONTAMINATION DUE TO IODINE-131 This Agreement State report from the Commonwealth of Massachusetts was received via facsimile: "Cat moved (kicked) during I-131 injection resulting in a couple of drops on veterinarian gloved hands, exam table, and floor. Contaminated Area subsequently mopped which seemed to spread more than clean the area. Contaminated area covered with plastic and access was restricted for more than 24 hours. Inside the room, the highest measurements on the floor, with a Ludlum 44-88 GM, was 12 Mr/hr on one spot, and 2-5 Mr/hr in all other floor areas - all measurements are at 1 cm. There was no personal contaminations and one small spot on a technicians sweatshirt sleeve which measured 15 mR/hr at 1 cm. With the 44-88 GM. All thyroid measurements indicate no internal intake of I-131. " Event type Description: Contaminated Area restricted for more than 24 hours. Cause of Description: Cat moved (kicked) during I-131 injection resulting in a couple of drops on veterinarian gloved hands, exam table, and floor. Contributing Factor: Contaminated Area subsequently mopped which seemed to spread more than clean the area. Docket No.: 06-7113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-06-22
43430 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2007-06-19 06:35 | 2007-06-19 11:09 | 2007-06-19 | TECH SPEC REQUIRED SHUTDOWN DUE TO INSTRUMENT LINE STEAM LEAK "During performance of a plant shut down personnel entered the Drywell to investigate a steam leak. At 0635 hours, personnel identified steam leaking from a flexible hose instrument line (approximately 1" diameter) that is welded to an elbow tap on the C Main Steam line and concluded that the leak constitutes pressure boundary leakage. This required entry into TS 3.4.5, Condition C. This requires that the unit be in Mode 3 in 12 hours and Mode 4 in 36 hours, which is a TS required shutdown. "The station has determined that this event is reportable under the provisions of: 10 CFR 50.72 (b)(2)(i) for the plant shutdown required by Technical Specifications, as a 4-hour notification; 10 CFR 50.72 (b)(3)(ii)(A) as an event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, as an 8-hour notification. "The NRC resident inspector has been notified." The leaking line goes to a steam line flow instrument. The leak indication was first noticed yesterday and the licensee decided to shutdown to investigate before the leak was verified by the drywell entry. | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2007-06-19
43429 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2007-06-18 08:00 | 2007-06-18 14:31 | 2007-07-11 | DIGITAL CONTROL SYSTEM FAILED FOR UNKNOWN REASON "At approximately 0800, lost all FMB control room monitors associated with Digital Control System (DCS). Several valves in UF6 process failed in unexpected position. No release and no exposures. System immediately put in a safe configuration. Root cause has begun and system will be kept in safe configuration for now (not restarted) until cause determined and corrected. This is a Courtesy Notification." The NRC Resident Inspector and the NRC Regional Project Manager (Pelchat) were informed of this information call by the licensee. * * * UPDATE FROM PARSCALE TO HUFFMAN AT 1146 EDT ON 7/11/07 * * * "The cause has been determined to be attributable to a UPS failure. This UPS failure resulted in a re-initialization of system configuration which, upon power restoration, caused process valves to move to the system's default configuration for the subsequent re-start mode. This default configuration was not correct for the state the system was in at the time of the re-initialization. The programming logic for valve alignment in the event of a re-initialization has since been corrected. There was no release and no exposure, and the system was immediately put in a safe configuration. The root cause is continuing. This is an update to the Courtesy Notification made on 6/18/07." Notified R2DO (Hopper), FSME (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | IL | FUE | [5 empty] | 0 | 2007-06-18
43428 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-04-16 22:23 | 2007-06-18 12:50 | 2007-06-18 | INVALID ESF ACTUATION DURING REFUELING OUTAGE "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report an invalid Engineered Safeguards Feature (ESF) actuation of the Auxiliary Feedwater(AFW) system reportable under 10 CFR 50.73(a)(2)(iv)(A). "On April 16, 2007, at 2223 with Unit 1 in Mode 3, starting up from refueling outage 18, the 11 Steam Generator Feed Pump (SGFP) trip AFW Pump Auto Armed light extinguished unexpectedly and the Steam Generator (SG) sample valves 11 through 14-SS94 and SG Blowdown valves 11 through 14-GB4 closed. At the time, the 11 and 12 SGFPs were already tripped and the 11 and 12 Auxiliary Feedwater pumps were in service. No control room manipulations were in progress. A signal was generated to start the already in service AFW pumps. "The invalid signal to start the AFW pumps was determined to be from a faulty SGFP alternate trip relay. The defective relay was replaced and the isolation signal was reset and retested satisfactorily. "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an invalid ESF actuation and invalid system actuation. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-06-18
43427 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-02-18 12:00 | 2007-06-18 12:17 | 2007-06-18 | AN AGREEMENT STATE REPORT FROM THE STATE OF FLORIDA - DAMAGED TROXLER GAUGE This event was called in by the State of Florida Bureau of Radiation Control: "Troxler Gauge damaged on site February 22, 2007. Company RSO notified this office on June 18, 2007. Back loader drove over gauge and damaged it. Gauge leak tested by Atlantic Drilling and found to be satisfactory." Incident Location: Fort Lauderdale, Davie Blvd between 31st and 32 streets. Isotope(s)/Activities: Cs-137 (10 mCi) and Am-241/Be (40 mCi) State of Florida Incident Number: FL07-100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-06-21
43426 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-06-13 23:00 | 2007-06-15 11:19 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * INFORMATION REPORT REGARDING DEGRADATION OF MONITORING AND DETECTION OF BOUNDARY Degradation of monitoring and detection related to owner controlled area boundary. Contact the Headquarters Operations Officer for details. The licensee will inform the NRC Resident Inspector. * * * UPDATE ON 06/18/07 AT 1347 ET PER LARRY ANTHONY (SECURITY OPERATION MANAGER) TO MACKINNON * * * Per follow-up this is not a reportable NRC report. It is an officer performance adhering to procedure. The NRC Resident Inspector will be notified of this update by the licensee. R2DO (Scott Shaeffer) and FSME (Greg Morell) * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | VA | FUE | [5 empty] | 0 | 2008-05-11
43425 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2007-06-15 06:50 | 2007-06-15 10:52 | 2007-06-15 | SAFEGUARDS REPORT INVOLVING FAILURE TO MAINTAIN ADEQUATE CONTROL OF SECURITY EQUIPMENT Safeguards system degradation related to failure to maintain positive control of security equipment. Immediate compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC Resident Inspector. * * * UPDATE AT 1241 EDT ON 06/15/07 FROM G. L. PLUMLEE III TO JOE O'HARA * * * The licensee is retracting this report after further review concluded that the incident is logable and not reportable. Contact the Headquarters Operations Officer for additional details. The licensee will inform the NRC Resident Inspector. Notified R4DO(Hay) and 73.71 Group via e-mail. | 0 | 96 | 100 |  | 96 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-06-15
43424 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2007-06-14 18:19 | 2007-06-14 20:21 | 2007-06-15 | TECH SPEC. REQUIRED SHUTDOWN DUE TO 72 HOUR COMPLETION TIME NOT MET "At 1819 hours, an orderly shutdown on Unit 1 commenced as the result of Technical Specification Action Condition (TSAC) 3.7.5.B.1 completion time of 72 hours not being met for the 1P-29 turbine-driven auxiliary feedwater pump. The pump was declared inoperable on June 12, 2007, at 0131 hours as a result of high pump bearing temperatures. Repairs and testing performed to date have not satisfactorily resolved the problem. "This non-emergency notification is being made in accordance with 10CFR50.72(b)(2)(i). The PBNP resident inspector has been notified." The licensee plans to conduct an extended duration test of the 1P-29 AFW pump. This test is scheduled to commence shortly and will last approximately 4 to 6 hours. The licensee will have two different hold points in the test to take pump bearing temperature data. The licensee has one emergency diesel generator (EDG) out of service (OOS), but an alternate EDG is aligned to ensure all four vital buses have vital power in the event of an loss of offsite power. No other safety related systems are OOS at this time. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RICK ROBBINS TO JOE O'HARA AT 2006 ON 06/15/07 * * * "This is an update to EN#43424: Regarding Unit 1 turbine driven auxiliary feedwater pump inoperability and Technical Specification required shutdown. "PBNP Unit 1 entered MODE 3 on 6/15/07 at 0407. "PBNP Unit 1 entered MODE 4 on 6/15/07 at 1712. "Technical Specification Action Condition 3.7.5.D.1 required Unit 1 to be in MODE 3 by 0731 and MODE 4 by 1931 on 6/15/07. All Technical Specification Required Actions for the AFW pump OOS have been met within the required times." The licensee informed the NRC Resident Inspector. Notified R3DO(Stone). | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-06-14
43423 | 0 | DOW CHEMICAL |  |  |  |  | 2007-06-14 | 2007-06-14 16:20 | 2007-06-14 | FIXED GAUGE FOUND WITH SHUTTER OPEN WHILE IN STORAGE The licensee was evaluating a fixed gauge in storage for possibly returning it to service when they discovered that the gauge's shutter was stuck open. Temporary lead shielding was installed and the licensee is in the process of contacting the manufacturer in order to have the device repaired and/or the source removed. The device is an Ohmart SHRM L-200, S/N 3269, containing 35 milliCuries of Cs-137. It was removed from service and has been in storage since 1994. The gauge was positioned face down such that radiation surveys did not detect that the shutter was open. The licensee does not believe that any personnel received any significant exposure since the storage area is ground level (no basement) and has limited access (locked). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-06-14
43422 | -1 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2007-06-14 10:30 | 2007-06-14 14:54 | 2007-06-28 | AGREEMENT STATE REPORT - POTENTIAL PERSONNEL OVEREXPOSURE The licensee's RSO received a phone call from Landauer at 1030 this morning to report a badge which had a deep dose reading of 6437 milliRem, an eye dose reading of 6437 milliRem, and a shallow dose reading of 6400 milliRem. The badge was assigned to the Chief of Surgery for the licensee for the month of January 2006. The RSO is investigating the cause for the fifteen month delay (January 2006 till June 2007) in processing the badge. Landauer told the RSO that this was a "dynamic" exposure to the badge meaning that the badge was moving during the time period of exposure. Iowa Item Number IA-070001. * * * RETRACTION PROVIDED BY RANDY DAHLIN TO KOZAL ON 6/28/07 AT 0847 * * * Upon further investigation of it was determined that the exposure is solely due to fluoroscopic procedures. Radiation generated from fluoroscopic equipment is not regulated by the NRC. Due to this fact the event should not have been reported to the NRC and is retracted. The State of Iowa will continue to investigate this matter with its licensee. Notified R3DO (Louden) and FSME EO (Flannery). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2007-06-19
43421 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-06-14 08:10 | 2007-06-14 14:20 | 2007-06-14 | UNABLE TO PERFORM SAFE SHUTDOWN AS A RESULT OF APPENDIX R FIRE AFFECTING HPCI "During verification of plant procedures associated with achieving safe shutdown during and after an Appendix R fire, it was determined that there was no readily available success path to secure HPCI when required. The scenario in question involves a fire-induced spurious HPCI initiation that must be terminated within 10 minutes to prevent flooding main steam lines and disabling both available methods of hot shutdown. For this event, RCIC is one defined method of temperature and pressure control to achieve hot shutdown. The other defined method requires ADS valves to lower pressure to allow CS to provide makeup water. As written, the procedure steps provided to Operations personnel would not have been sufficient to isolate steam to the HPCI turbine. All other methods to secure HPCI that would have been reasonably available required operation of components that could have been affected by the same fire that caused the spurious initiation of HPCI. "The procedures have been changed to provide Operations personnel adequate and effective instructions to isolate HPCI when required after a spurious initiation during an Appendix R fire. "This is being reported under 10 CFR 50.72(b)(3)(v)(A) as a condition that could have prevented the plant from achieving safe shutdown. "The Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2007-06-14
43420 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-06-13 08:00 | 2007-06-13 11:48 | 2007-06-13 | NOTIFICATIONS MADE FOR DETECTION OF TRITIUM IN ONSITE WATER SAMPLES "On May 8, 2007, measurable levels of tritium were identified in two manholes (i.e., MW-5 and MW-6) that route cable to a nearby meteorological tower. The manholes are located within the boundaries of the site owner controlled area. The manholes are also in close proximity to the Storm Drain Stabilization Pond (SDSP). The SDSP is an area of approximately 64 acres consisting of a non-lined perimeter dike of approximately 12 to 15 feet in height. The site storm drain system collects in the storm drain collector basin and is then pumped to the SDSP. The storm drain collector basin receives overflow from the Turbine Building air-wash system, which contains very small amounts of tritium. By plant design, the tritiated water of the SDSP is then pumped into the intake canal during monitored, controlled releases, compliant with all permits and regulations. "As a result of ongoing investigations to determine the source and potential migration path of the tritium, an increased environmental sampling program was initiated. On June 13, 2007, tritium levels in excess of Nuclear Energy Institute (NEI) voluntary reporting criteria were confirmed to be present in new onsite shallow groundwater wells. "Immediate corrective actions taken were to perform additional sampling of areas surrounding the stabilization pond and [to reconfigure] the Turbine Building air-wash system. The reconfiguration of the turbine building airwash system will be done to eliminate the designed pathway of water to the storm drain collection basin and to the storm drain stabilization pond. "Additional corrective actions include installation of additional monitoring wells at various locations to determine groundwater flow and checking for the presence of tritium. "There is no indication that tritium has migrated into drinking water sources and all offsite monitoring has resulted in non-detectable levels of tritium. It is believed that the likely source of the tritiated water is seepage from the SDSP. The following agencies will be updated on the status of the onsite tritium samples and informed of the pending press release: State Officials, City of Southport, Brunswick County, NEI, INPO, and ANI." The Licensee notified the NRC Resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-06-13
43419 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2007-06-12 16:45 | 2007-06-12 17:33 | 2007-08-08 | SECURITY SUSPENDED SAFEGUARDS REQUIREMENTS DUE TO SUDDEN SEVERE WEATHER Security suspended safeguards requirements due to sudden severe weather. Compensatory actions were taken. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM NIELSEN TO HUFFMAN AT 1318 EDT ON 8/8/07 * * * The licensee is updating this event to indicate that it is not reportable under 10 CFR 73.71 Appendix G. Rather, it is reportable under a requirement in the licensee's Physical Security Plan. Specifically: "Upon further review, it has been determined that the suspension of security measures for imminent, severe, or hazardous weather conditions needed to protect site security personnel is allowed by the FPL Physical Security Plan (PSP) Section 19.2. The notification requirement is contained in PSP Section 19.3 which requires a one-hour report to the NRC Operations Center, therefore, a follow-up written report is not required." The licensee notified the NRC Resident Inspector. R2DO (Musser) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW | [5 empty] | 1 | 2007-06-12
43418 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2007-06-11 | 2007-06-11 21:59 | 2007-06-11 | NOTIFICATION OF UNUSUAL EVENT DECLARED BECAUSE OF POTENTIAL AIRCRAFT THREAT The site declared an Unusual Event in response to an aircraft on a path to fly over the facility. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident inspector. | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | KS | POW |  | 50.72(a) (1) (i) |  |  |  | 1 | 2007-06-11
43417 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2007-06-11 08:05 | 2007-06-11 16:57 | 2007-06-11 | ALABAMA AGREEMENT STATE REPORT - A GEORGIA LICENSED MOISTURE DENSITY WAS DAMAGED IN ALABAMA This event was received via facsimile from the State of Alabama "SUBJECT: Alabama Incident 07-25 - Damage to Instrotek Model 3500 Moisture Density Gauge. "On the morning of June 11, 2007 at approximately 8:05 am CDT, the Alabama Office of Radiation Control received a phone call from a representative of the Georgia Department of Natural Resources advising the Agency that a moisture density gauge containing radioactive material had been run over by a dozer at a temporary job site in Phenix City, Alabama. The gauge was an Instrotek model 3500, serial number 583 containing 10 millicuries of Cs -137 and 40 millicuries of Am-241:Be. The licensee, Building and Earth Sciences of Columbus, Georgia notified the Georgia Department of Natural Resources at the time the incident occurred. Upon notification, the writer called the licensee's technician at the site to check the status of the incident. According to the licensee, the sources were in the shielded position and the area was restricted. The licensee's Radiation Safety Officer arrived at the scene and surveyed the area, the dozer and the gauge. Radiation levels around the gauge were found to be within the normal range. The gauge was placed in the transport container and returned to the licensee's facility and a leak test was performed. Leak test results are pending. Building and Earth Sciences is authorized to possess and use radioactive material under their Georgia Radioactive Material License No. GA. 1136-1. "This is all the information that this Agency has at this time and is current as of 3:00 pm CDT, June 11, 2007." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2007-06-14
43416 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2007-06-10 20:03 | 2007-06-11 01:17 | 2007-07-06 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE DUE TO FAILED INVERTER "At 2003 on 6/10/07, the division 3 Nuclear System Protection System (NSPS) inverter power supply failed for unknown reasons. As a result of this failure, the High Pressure Core Spray (HPCS) system has been declared inoperable. This is a failure of a single train safety system and is reportable under 10 CFR 50.72(b)(3)(v)(D). Troubleshooting has been initiated to determine the cause of this failure." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 07/6/07 AT 1639 EDT FROM TOM CHALMERS TO MARK ABRAMOVITZ * * * "This event is being retracted. An evaluation was performed and it was determined that no loss of safety function occurred following the failure of the Division 3 NSPS Inverter. The investigation determined that a circuit board failed on the inverter causing a blown fuse. The inverter was found in the reverse transfer position and AC power was automatically transferred to its alternate source, supplying its Division 3 loads. The High Pressure Core Spray system remained fully capable of performing its safety function to start and inject under both LOOP and LOCA conditions." The licensee will notify the NRC Resident Inspector. Notified the R3DO (Lanksbury). | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-06-11
43415 | 0 | B. JONES & SONS PAVING |  |  |  |  | 2007-06-10 | 2007-06-10 14:00 | 2007-06-12 | STOLEN NITON METAL ANALYZER The licensee possessed a Niton Metal Analyzer (believed to be a Model XRF but not certain). The analyzer is used for scrap metal alloy analysis. The analyzer was inadvertently left in the company truck which was being used for personal business. The truck was broken into while parked at a hotel in Humble, Texas (Country Heart Inn and Suites) and the Niton Analyzer was stolen. The licensee did not know the source in the analyzer. Based on information found on the internet it is believed to be a 40millicurie Cadmium-109 source. The licensee plans to file a police report. R4DO (Shannon) will ensure that the State of Texas is notified. * * * UPDATE FROM DARREL WIEDEMAN TO JOE O'HARA AT 1308 ON 6/12/07 * * * Mr. Wiedeman reports that the metal analyzer has been found abandoned in an empty field near Humble, Texas. The individuals who found the device notified the owner via the contact information on the device. The owner's representative is on the way from Indiana to Texas to take custody of the analyzer. Additionally, the device has a 30 millicurie Am-241source, not Cadmium -109, as previously reported. Mr. Wiedeman notified Randy Erickson (R4 State Liaison) and State of Texas. Notified R3DO(Phillips), R4DO(Hay), FSME(Morell), ILTAB(via email), and Mexico(via fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-06-10
43414 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-06-09 11:00 | 2007-06-09 15:53 | 2007-06-15 | AUTOMATIC REACTOR SCRAM DUE TURBINE TRIP AS A RESULT OF HIGH MOISTURE SEPARATOR REHEATER TANK LEVEL "On 06/09/2007 at 1100 CDT, Browns Ferry Unit 1 received an automatic SCRAM due to a Turbine Trip Signal caused by a Moisture Separator Drain Tank Level High. All control rods inserted and all systems responded as required to the automatic SCRAM signal. Two Main Steam Relief Valves (MSRVs) momentarily lifted in response to the pressure transient. No Emergency Core Cooling System (ECCS) initiations occurred as a result of the SCRAM. Reactor water level lowered below Level 3 (+2") as a result of the SCRAM and was recovered to the normal level band by the reactor feed pumps (RFPs). The expected Primary Containment Isolation System (PCIS) Groups 2, 3, 6, and 8 isolations were received due to reactor water level lowering below Level 3 (+2") with all systems isolating as required. Additionally, the expected initiation of the RPT breakers from the turbine trip was received which resulted in the trip of both reactor recirculation pumps. Reactor pressure is being controlled using Main Steam Bypass Valves. Reactor Level is being maintained in band using RFPs. Cooldown is in progress to Mode 4. Investigation into the event is proceeding. "The NRC Senior Resident Inspector has been informed of this event. "This event is reportable under 10CFR50.72(b)(2)(iv)(B) 'any event or condition that results in a valid actuation of the Reactor Protection System'; 10 CFR50.72(b)(3)(iv)(A), ' Any event that results in an actuation of the specified systems'. This event also requires a 60 day written report in accordance with 10CFR50.73(a)(2)(iv)(A)." * * * UPDATE FROM BOLAND TO HUFFMAN AT 1850 EDT ON 6/9/07 * * * Follow-up review of the reported reactor scram revealed that the Group 8 isolation did not function as required. Specifically, the licensee provided the update below concerning the function of one of the reactor's five Traversing Incore Probes (TIP) that had been used the previous day for flux mapping and were in the drywell (not fully retracted) to permit decay when the scram occurred. "The Group 8 isolation signal received during Unit 1 Rx SCRAM on 06/09/2007 @ 1100 did not automatically go to completion as designed. The 'D' TIP failed to automatically withdraw as required. When the TIP was manually withdrawn, the TIP Ball valve closed as required. The local resident was notified. A work order and PER was written to correct the deficiency." The other four TIPs did retract and the corresponding ball valves shut as expected. R2DO (Fredrickson) notified. * * * UPDATE FROM TIM GOLDEN TO JOE O'HARA AT 1804 ON 6/15/07 * * * "Review of available data indicates that no Main Steam safety relief valves (MSRVs) opened in response to the Unit 1 reactor scram on 06-09-2007. There were no indications of an open MSRV on any discharge tailpipe thermocouple or acoustic monitor. Initial indications of the discharge tailpipe thermocouples for MSRVs 1-PCV-1-5, 1-PCV-1-30, and 1-PCV-1-31 did indicate slight increases in temperature (5 to 18 degrees F) as reactor pressure decreased, which resulted in the initial assumption of two SRVs opening. However, this behavior is a classical indication of slight main seat leakage. This equipment condition is under review via an open PER. The multiple reactor pressure instrumentation responses were reviewed. The peak reactor pressure was indicated at approximately 1093 psig which is 42 psi below the lowest nominal MSRV setpoint. Based upon the observed peak reactor pressure and no indication of an MSRV opening, it would appear that the MSRVs performed as required to during the reactor pressure transient event. The licensee will notify the NRC Resident Inspector. Notified R2DO(Shaeffer). | 0 | 0 | 0 | 79 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-06-09
43413 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2007-06-08 09:10 | 2007-06-08 10:49 | 2007-06-08 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE. "During the performance of quarterly HPCI valve testing in accordance with OP4120 one of the two injection valves, HPCI-19, did not stroke open as required. Prior to testing the HPCI system was in normal standby line up. HPCI-19 was stroke tested during the outage on 6-1-07 and operated normally. HPCI-19 was also tested and verified to open during the ECCS test on 6-1-07." HPCI was declared inoperable per Technical Specification 3.5.E.2 (14 day Limiting Condition of Operation). All other ECCS systems and the EDGs are fully operable and the electrical grid is stable. The licensee has initiated repair efforts. The NRC Resident Inspector was notified of this event by the licensee. | 81 | 0 | 0 | 81 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-06-08
43412 | 0 | CARBOLINE COMPANY |  |  |  |  | 2007-06-07 | 2007-06-07 11:11 | 2007-06-07 | PART 21 REPORT INVOLVING CARBOLINE COATINGS The following information was received via fax: "Subject: 10CFR Part 21, Notification of Potential Safety Related Noncompliance Deviation "Notification By: Carboline Company "Phone: (314) 644-1000 x2456, Fax: (314) 644-4617 "Based on information supplied to Carboline Company (US) through Carboline Korea, Ltd. (Carboline's Korean affiliate), it is our understanding that Korea Power Engineering Company (KOPEC) has stated that the only Carboline material approved for use on KOPEC projects, is the Carboline Korea, Ltd. Material manufactured in Korea. Carboline Company's protective coatings manufactured in the US have not been tested or approved for KOPEC project work. We have not tested the Carboline US material to the KOPEC curve; the KOPEC curve is a 360°F and the pressure is either 57 or 60 PSIG. This curve is more stringent than the standard curves used by US utilities. "We have been made aware that, in some cases, material ordered from Carboline US and shipped as ordered, has in fact been utilized on units/equipment for KOPEC projects. "Carboline (US) supplied Carboline US products as ordered. We are in most cases unaware of the end customer. The Carboline products supplied were manufactured in accordance with our 10CFR50 Appendix B QA program and we accept 10CFR Part 21 for all US orders of nuclear grade material. "Note: Carboline Korea is not an approved sub-contractor/vendor under the Carboline US program and we have not supplied any Carboline Korea Ltd. Manufactured product to any US nuclear customer. "From this point forward, Carboline material manufactured in the US will not be supplied for KOPEC project work. "The following information is provided as required by 10 CFR 21.21(d) (4): "(i) Name and address of individual informing the commission. Dwayne Meyer, Director of Technical Resources and Marikay Speckert, QA Manager Carboline Company 350 Flanley Industrial Ct. Brentwood, MO 63144 "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains the defect. "Protective Coatings ordered and supplied from Carboline Company (US); the only approved Carboline products for KOPEC work are those manufactured by Carboline Korea. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply with or contains the defect. "We do not know which Carboline (US) nuclear customers may have used US material when Carboline Korean manufactured material was required. We are notifying all NUPIC members and Carboline non-utility, nuclear customers that have purchased from Carboline Company (US) over the last 5 years. "(iv) Nature of the defect or failure to comply and the safety hazard which is created by such a defect or failure to comply. "Because we do not know who is using the material for KOPEC projects or the details of the material use; we do not have the capability to perform the evaluations to determine if a defect exists or the potential effect of such defect. "We have not tested the Carboline US material to the KOPEC curve; the KOPEC curve is a 360°F and the pressure is either 57 or 60 PSIG. This curve is more stringent than the standard curves used by US utilities. "The Carboline Korea Ltd. Products are manufactured in our Korean plant for nuclear service. The Korean products have been tested and certified to meet KOPEC's specific performance and qualification standards. Carboline Company's (US) nuclear grade products are manufactured and qualified for nuclear service according to the standards set forth in the US. The formulations, raw material suppliers and the production processes are similar however they are not exactly the same and we do not know the significance of these differences. "(v) The date on which the information of such defect or failure to comply was obtained. "May 23, 2007, KOPEC informed us through our Carboline Korea affiliate, that we (Carboline US) needed to inform one of our customers that their undelivered component needed to be redone with Carboline Korean manufactured material. "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part. "We do not know which Carboline (US) nuclear customers may have used US material when Carboline Korean manufactured material was required. We are notifying all NUPIC members and Carboline non-utility, nuclear customers that have purchased from Carboline Company (US) over the last 5 years. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "1) We have informed our Sales Force and Customer Service personnel of the need to recognize/identify orders that are for use on international projects. We then contact the customer and clarify products required and facilitate getting material from Carboline Korea if needed. This was handled by Dwayne Meyer, our Director of Technical Resources, and has been in place for approximately two weeks. "2) Our Korean made nuclear products will undergo a name change in the near future. This will help us clearly identify them on project specifications. This will assure that the products used on KOPEC projects use the same raw materials and the same processes at the same manufacturing plant location. This is being addressed by Doug Moore, our Director of International Business Development directly with our Carboline Korea management and this will be in place by July 1, 2007 at the latest. In the interim, we require that the coating requirement specification be supplied so that we can clearly identify the proper coating for the project. "3) We are looking at having some Carboline Korea manufactured material stocked in Carboline (US) warehouse in our Lake Charles LA facility. Our QA department is working with our International Group. We are still looking into this; in the interim we are facilitating the orders for Carboline Korea material. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "We submitted the above plan (vii) to KOPEC and, through our affiliate; we understand that it is acceptable. "In summary, Carboline has taken appropriate corrective action, notified the NRC, and shall notify all customers promptly. "If you have any questions or need additional information concerning this notification, do not hesitate to contact Dwayne Meyer, Director of Technical Resources at (314) 644-1000 extension 2550, or Marikay Speckert, QA Manager at (314) 644-1000 extension 2456." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MO | OTH | PAR | 21.21 |  |  |  | 0 | 2007-06-07
43411 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-05-08 | 2007-06-06 12:36 | 2007-06-07 | AGREEMENT STATE REPORT INVOLVING EQUIPMENT FAILURE OF RADIOGRAPHY CAMERA The following report was received from the Louisiana Department of Environmental Quality (LA DEQ) via fax: "[A] field inspection was performed on a field crew for METCO. [While] performing the inspection a misconnect test was performed. The crank outs had a serial number of MST 225 manufactured by AEA Technologies and the camera was an Amersham 880 Sigma with serial number S1712. This misconnect test failed. The crank outs were removed [from] operation and taken back to the shop. The problem was located on the crank out and was repaired. A misconnect test was then performed with the same camera and an additional camera and it passed the test. METCO stated that they will pay closer attention to damage and wear and tear on equipment." LA Event Report ID No.: LA070014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-06-11
43410 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2007-06-06 13:10 | 2007-06-06 18:10 | 2007-06-06 | CONTAINMENT ISOLATION VALVES FOUND MISALIGNED "On 6/06/07 at 13:10 EDT while performing a surveillance to verify the position of administratively locked valves for Containment and Shield Building Integrity, two manual Containment Isolation valves were found Locked Open, versus the required Locked Closed position. The valves were restored to the Locked Closed position at 13:30 EDT of the same day. "The subject valves, V18794 and V18796, provide Service Air (a non-safety class system) to the Containment during Mode 5 and 6 conditions through Containment Penetration #8. The subject valves are required to be returned to Locked Closed prior to entering Mode 4 in accordance with the Plant Technical Specifications 3.6.1.1 for Containment Integrity and plant procedures. The valves are to be verified in the Locked Closed position once every 31 days per Administrative Procedure 1-0010123 Appendix E, which was last performed on 5/09/07. Unit 1 exited Mode 5 and entered Mode 4 on 5/20/07 following a refueling outage and is currently in Mode 1 at 100% power. It is assumed the valves have been incorrectly positioned since entering Mode 4. "The Service Air System is intact and pressurized at approximately 110 psig. There is no open path from Containment to the outside atmosphere. "This event is being reported pursuant to 10CFR50.72(b)(3)(ii)(A), based on principal safety barriers being seriously degraded." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-06-06
43409 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2007-06-06 13:17 | 2007-06-06 14:32 | 2007-06-07 | PUBLIC NOTIFICATION SYSTEM INOPERABLE "Notified at 1220 by Emergency Plan personnel that a tone test initiated by the National Weather Service from Albany, NY, failed to activate tone alert radios via the Ames Hill NOAA transmitter. Notified at 1317 that the WTSA Studio to transmitter link also failed to activate the tone alert radios. The tone alert radio system was working when a severe thunderstorm was issued at 1205 on 6-5-07." The licensee has sent a technician to repair the transmitter. The licensee notified the NRC Resident Inspector and will notify the states of Vermont, Massachusetts, and New Hampshire. * * * UPDATE PROVIDED BY ANDREW WISNIEWSKI TO JEFF ROTTON AT 0931 ON 06/07/07 * * * Repairs were completed to the tone alert radio system last night and testing was completed this morning. At 0821 the tone alert radio system was declared to be operable. The licensee notified the NRC Resident Inspector and the states of Vermont, Massachusetts, and New Hampshire. Notified R1DO (Barkley) | 4 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-06
43408 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2007-06-06 07:45 | 2007-06-06 09:32 | 2007-06-06 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN INITIATED ON UNIT 3 "At 0746, on 6/6/2007, a Unit 3 shutdown was initiated in accordance with station procedures. Unit 3 entered Technical Specification (TS) 3.0.3 at 0745 on 6/6/2007. "TS 3.0.3 was entered when the Analog Rod Position Indicator (ARPI) for control rod F-4 was declared inoperable. Control rod F-4 is located in control bank C. The ARPI for control rod M6, which is also in control bank C, has been previously declared inoperable. With two ARPIs in control bank C inoperable, TS Limiting Condition for Operation 3.1.3.2, Action a, cannot be met thus necessitating entry into TS 3.0.3. ARPI repairs will be performed as required." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM E. NEVILLE TO P. SNYDER AT 1400 ON 6/6/07 * * * Turkey Point Unit 3 entered Mode 3 at 1152 on 6/6/07 after manually tripping from approximately 25% power. At 1152 Turkey Point exited TS 3.0.3 since the condition for which it was entered no longer applied. The site borated to compensate for the control rods for which position indication was lost. All control rods fully inserted on the trip. The plant is currently steaming to atmospheric relief valves. No primary to secondary tube leaks exist. The licensee will notify the NRC Resident Inspector. Notified R2DO (Fredrickson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-06-06
43407 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2007-06-05 15:17 | 2007-06-05 20:03 | 2007-06-05 | MANUAL REACTOR TRIP AFTER FEEDWATER VALVE FAILURE "On 06/05/07 at 1512 hours CDT, operators observed that the Unit 1 main feedwater regulating valve (1 FD-476B) was going full open to full shut and entered abnormal operating procedure (AOP) 2B for a feedwater system malfunction. An immediate inspection of the valve determined that the valve positioner arm was disconnected, with the positioner arm locknut found on the floor adjacent to the valve. Operators manually tripped the Unit 1 reactor at 1517 hours CDT in response to the loss of 'B' train main feedwater control. During the trip, the auxiliary feedwater system actuated due to low level in the 'B' steam generator and an actuation of the ATWS mitigating system (AMSAC). "Plant systems and equipment functioned properly following the manual trip with the following exceptions: A switchyard bus section 2 lockout occurred, resulting in loss of 345 Kv Line 121; 1FD-2603 bleeder trip valve (1 HX-22A moisture reheater drain) stuck open; and 1 P-129A turbine bearing oil lift pump did not automatically start, but was successfully started manually. "Troubleshooting and additional investigations are continuing. The affected equipment has been quarantined. Unit 1 is in MODE 3 and is stable. Unit 2 was unaffected by the Unit 1 manual trip." All control rods fully inserted on the trip. No safety or relief valves lifted from the trip. Reactor pressure and temperature are being maintained with main feedwater and steaming to the main condenser. Emergency Diesel Generator GO-1 (two EDGs per train) and one Service Water Pump are out of service for replacement. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-06-05
43406 | 0 | MEADWESTVACO VIRGINIA CORP. |  |  |  |  | 2007-06-05 14:58 | 2007-06-05 15:50 | 2007-06-05 | THREE LOST TRITIUM EXIT SIGNS The licensee reported that after a thorough search of their facility in Covington, VA they cannot account for three (3) tritium exit signs. The licensee had decided to return all of their tritium exit signs to the manufacturer, SRB Technologies. They were able to return 136 of their 139 signs. The activity of two of the signs was originally 20 Curies each on October 1990 for one sign and July of 1992 for the other sign. Because of decay the activity of the signs now is estimated to be 7.8 Curies and 8.6 Curies respectively. The activity of the third sign is estimated to be in the same range. The licensee is not sure when the signs were lost but two were installed above an old door in the facility that was replaced with a new door in a remodel some time ago so they may have ended up in a land fill. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-06-05
43405 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-06-04 20:08 | 2007-06-04 21:54 | 2007-06-04 | FIRE SAFE SHUTDOWN CAPABILITY IMPACTED BY A BREAKER COORDINATION ISSUE "An engineering analysis has identified existing breaker coordination issues and their effect on plant fire protection and resulting safe shutdown capability. Cables associated with certain breakers do not have qualified fire barriers in place to prevent an upstream breaker from tripping. The affected cables are in fire areas that credit the affected train as the assured post fire safe shutdown train. The failure mode of concern is that a fire in the area where the cable is located could cause a short circuit between the cable connectors." The fault current calculated for these cases is high enough to trip the upstream breaker(s) and it cannot be assured that the downstream load breaker(s) will act to clear the fault first. "[This] event was initially discovered on 5/17/07. Mitigative actions were taken at that time, in the form of establishing fire watches for the affected fire areas. Reportability implications were discovered as a result of additional discussions that took place on 6/4/07." "The following cables and power sources are impacted by this notification: "CABLE NO. FIRE AREA AFFECTED PANEL 1CA581 Unit 1 Auxiliary Feedwater Pump Turbine Control Panel Room 1EDF 2CA581 Unit 2 Auxiliary Feedwater Pump Turbine Control Panel Room 2EDF 1IRE761 Unit 1 577 elevation Electrical Penetration Room 1EPD 2IRE761 Unit 2 577 elevation Electrical Penetration Room 2EPD "Panels 1EDF and 2EDF are 125 VDC Vital Instrumentation and Control Auctioneered Distribution Centers. Loads fed from these distribution centers include Train 'B' circuits associated with the following: 4 KV Essential Switchgear Control Power, Diesel Generator Load Sequencer Control Power, and Auxiliary Feedwater System Control Power. "Panels 1EPD and 2EPD are 125VDC Vital Instrumentation and Control Panel boards. These panel boards supply a variety of Train 'B' safety related control power loads." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-06-04
43404 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-06-04 16:00 | 2007-06-04 17:28 | 2007-06-06 | UNANALYZED CONDITION DUE TO IDENTIFIED NON COMPLIANT FIRE PROTECTION MANUAL OPERATOR ACTIONS "During performance of NFPA-805 Transition Project Task SUP-1, 'Manual Action Compliance,' it was determined there were 5 non-compliant manual operator actions that were being performed to achieve and maintain hot safe shutdown in Fire Area 29, Admin Building Electrical & Piping Room 1. These manual actions were being performed in an Appendix R Section III.G.1/G.2 fire area, however, they do not meet the criteria for allowable manual actions specified in RIS 2006-10, 'Regulatory Expectations with Appendix R Paragraph III.G.2 Operator Manual Actions.' "The discovery of these non-compliant manual actions is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii). The alternate compensatory measure for Fire Area 29 is to perform the manual action. An extent of condition review has been initiated that will encompass the remainder of the safe shutdown areas in both Prairie Island Nuclear Generating Plant (PINGP) units. The results of the extent of condition will be documented in the site's corrective action program with compensatory measures being established as appropriate. The 60-day licensee event report, submitted to the Commission in accordance with 10 CFR 50.73(a)(2)(ii), will provide the results of the manual action compliance review and follow-up corrective actions." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM W. BODIN TO P. SNYDER AT 1643 ON 6/5/07 * * * "During performance of NFPA-805 Transition Project Task SUP-1, 'Manual Action Compliance,' it was determined that non compliant manual operator actions are credited to achieve and maintain hot safe shutdown for a fire. The following actions were identified during the extent of condition reviews conducted subsequent to EN 43404 report. Numbers of Non-compliant Actions and Fire Areas Affected: "2 actions for Fire Area 2, Ventilation Fan Room, Unit 1; "2 actions for Fire Area 10, Train A Event Monitoring Equipment Room; "6 actions for Fire Area 20, Unit 1 4.16 KV Safeguards Switchgear (Bus 16); "2 actions for Fire Area 22, 480V Safeguards Switchgear (Bus 121); "1 action for Fire Area 23, Unit 2, 4.16 KV Normal Switchgear (Bus 23, 24); "2 actions for Fire Area 30, Administration Building Electrical & Piping Room #2; "1 action for Fire Area 33, Battery Room 11; "1 action for Fire Area 34, Battery Room 12; "6 actions for Fire Area 37, Unit 1 480V Normal Switchgear Room; "4 actions for Fire Area 41A, Screenhouse (DDCWP Rooms); "6 actions for Fire Area 41B, Screenhouse Basement; "10 actions for Fire Area 58 and 73, [Auxiliary] Building Ground Floor Unit 1 & 2; "2 actions for Fire Area 59, [Auxiliary] Building Mezzanine Level Unit 1; "1 action for Fire Area 80, 480V Safeguard Switchgear Room (Bus 112); and "4 actions for Fire Area 81, 4.16 KV Safeguard Switchgear Room (Bus 15). "These manual actions are credited for safe shutdown in an Appendix R Section III.G.1/G.2 fire area; however, they do not meet the criteria for allowable manual actions specified in RIS 2006-10, 'Regulatory Expectations with Appendix R Paragraph III.G-2 Operator Manual Actions.' "The discovery or these non-compliant manual actions is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii). The manual actions have been determined to be feasible and will be treated as alternate compensatory measures for Fire Areas 2, 10, 20, 22, 23, 30, 33, 34, 37, 41A, 41B, 58, 59, 73, 80, and 81. An extent of condition review is continuing that will encompass the remainder of the safe shutdown areas in both Prairie Island Nuclear Generating Plant (PINGP) Units." The licensee notified the NRC Resident Inspector. Notified R3DO (M. Phillips). * * * UPDATE AT 16:28 ON 6/6/2007 FROM W. BODIN TO M. ABRAMOVITZ * * * "During performance of NFPA-805 Transition Project Task SUP-1, 'Manual Action Compliance,' it was determined that noncompliant manual operator actions are credited to achieve and maintain hot safe shutdown for a fire. The following actions were identified during the extent of condition reviews conducted subsequent to EN 43404 report. # Non-Compliant Actions 1 action for Fire Area 4, Fuel Handling Area 12 actions for Fire Area 31, 'A' Train Hot SD panel, AFW & Air Compressors 11 actions for Fire Area 32, 'B' Train Hot SD panel, AFW & Air Compressors 2 actions far Fire Area 38, Unit 2 480V Normal Switchgear Room 1 action for Fire Area 39, Radwaste Building 2 actions for Fire Area 46, Cooling Tower Equipment House 4 actions for Fire Area 69, Turbine Building Ground & Mezzanine Floors Unit 1 3 actions for Fire Area 70, Turbine Building Ground & Mezzanine Floors Unit 2 2 actions for Fire Area 71, Containment Unit 2 2 actions for Fire Area 72, Containment Annulus Unit 2 5 actions for Fire Area 74, Aux Building Mezzanine Level Unit 2 "These manual actions are credited for safe shutdown in an Appendix R Section III.G.1/G.2 fire area, however, they do not meet the criteria for allowable manual actions specified in RIS 2006-10, 'Regulatory Expectations with Appendix R Paragraph III.G.2 Operator Manual Actions.' "The discovery of these non-compliant manual actions is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii). The manual actions have been determined to be feasible and will be treated as alternate compensatory measures for Fire Areas 4, 31, 32, 38, 39, 46, 69, 70, 71, 72, and 74. This concludes the extent of condition review of the safe shutdown areas in both Prairie Island Nuclear Generating Plant (PINGP) units." The licensee notified the NRC Resident Inspector. Notified the R3DO (Phillips). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-06-04
43403 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2007-06-04 06:55 | 2007-06-04 10:10 | 2007-06-04 | PARTIAL LOSS OF THE PUBLIC PROMPT NOTIFICATION SYSTEM "The following event is reportable per 10CFR50.72 (b)(3)(xiii) due to partial loss of the Public Prompt Notification System. "On 6/4/07 at 06:55 the Tone Alert Radio System went out of service This was communicated by the Oswego County Emergency Operations Center at 08:30. The loss of the Tone Alert Radio System is a result of a loss of Verizon phone service in the Binghamton, NY area where the Tone Alert Radio System is controlled from. The cause of Verizon phone service being out of service is unknown. Preliminary information estimates several hours until restoration complete. The county alert sirens, which also function as part of the Public Prompt Notification System are operable." The licensee notified State/local agencies and the NRC Resident Inspector. * * * UPDATE FROM J. DRISCOLL TO P. SNYDER AT 1922 ON 6/4/07 * * * "On 6/4/07 at 06:55, the Tone Alert Radio System was lost due to a loss of Verizon phone service in the Binghamton, NY area, which controls the Tone Alert Radio System. At 10:10, this event was reported by ENS communication in accordance with 10CFR50.72 (b)(3)(xiii) for a partial loss of the Public Prompt Notification System. "On 6/4/07 at 14:05, the Oswego County EOC notified Nine Mile Point that the Tone Alert System was returned to service." The licensee notified the NRC Resident Inspector. Notified R1DO (Barkley). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-04
43402 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2007-06-04 06:55 | 2007-06-04 09:58 | 2007-06-04 | LOSS OF TONE ALERT SYSTEM "At 0830 on June 4, 2007, with the James A. Fitzpatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified JAF that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 0655. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The National Weather Service is currently working to determine the cause of the failure and time frame for system restoration. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing Local Law Enforcement Personnel for 'Route Alerting' of the affected areas of the EPZ. Oswego County Emergency Management has verified that the Oswego County Sheriff's Department is on standby for Route Alerting. "The event has been entered into the corrective action program and the resident inspector has been briefed and the state PSC will also be notified." * * * UPDATE AT 14:57 ON 6/4/2007 FROM GENE DORMAN TO MARK ABRAMOVITZ * * * "Notified the NYS PSC at approximately 10:30 EDT [regarding original event notification]. "The failure of the Tone Alert Radios was determined to be a loss of telephone interconnection service between Binghamton and Syracuse. The Tone Alert Radios were restored to service at 14:05." The licensee notified the NRC Resident Inspector and the NY PSC. Notified the R1DO (Barkley). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-06-04
43401 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2007-05-31 10:00 | 2007-06-01 14:59 | 2007-06-01 | AGREEMENT STATE REPORT - DAMAGED TROXLER This event took place in the Southmoor Subdivision, Phase 2, Eagle Mountain, UT. "This event involved Troxler, model 3440, serial number 28420, containing 8 [millicuries] of Cs-137 and 40 mCi of Am-241:Be. The technician was testing sidewalk compaction ahead of the cement crew and was trying to keep ahead of the concrete truck. To do so, the technician would put the gauge in the back of his truck and drive about 200 feet along to the next test site. The gauge was not put in the transportation box nor was it secured. The technician drove off the asphalted road onto a 'roughed in' dirt road. When the truck hit the bump, the Troxler gauge slid or bounced out of the truck and hit the asphalt. The technician realized very quickly that the gauge was no longer in the truck and could see it approximately 200 feet behind the vehicle. Initially, the source rod remained in the safe shielded position, but the technician tried to lift the gauge by the handle and the source rod totally detached from the remaining portion of the gauge. "The Am-241:Be source was not damaged and remained in place." UT Event Report ID No.: UT-07-006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2007-06-06
43400 | 0 | WASHINGTON UNIVERSITY |  |  |  |  | 2007-05-29 10:15 | 2007-06-01 15:56 | 2007-06-14 | CANCER TREATMENT OF RADIOACTIVE IODINE RESULTS IN A DOSE TO FETUS A patient was seen by the prescribing physician on May 22, 2007 about a cancer treatment with Iodine 131. The hospital conducted a pregnancy test on the patient. The result was negative. The individual was advised not to get pregnant prior to the treatment. On May 29, 2007, the treatment was conducted at Barnes Jewish Hospital Radiation Oncology. The prescribed dose was for 125 millicuries of I-131. 125.5 millicuries of I-131 was the actual administered dose. On May 30, 2007 the patient called the hospital to report that she conducted a home pregnancy test with positive results. The patient was asked to come in to the hospital on May 30, 2007 for another test. The hospital radiation safety officer received the results of the test on May 31, 2007. The results were positive. The staff at the hospital calculated a dose to the adult uterus as an approximation for the dose received by the fetus. The dose was estimated to be 25 to 34 rem. The risk to the fetus is still being determined by the hospital. The possible effects on the fetus will be discussed with the patient at a future date. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3047(a) |  |  |  | 0 | 2007-06-14
43399 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2007-05-17 | 2007-06-01 13:25 | 2007-06-01 | AGREEMENT STATE REPORT - NITON DEVICE SHUTTER MALFUNCTION "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "The licensee's radiation contact individual notified Washington Department of Health (DOH) on 18 May 2007 that their Niton XLp 818 device's [used for metal composition identification] shutter mechanism malfunctioned. It contains a 30-millicurie americium-241 sealed source. "On the morning of May 17, 2007 when the licensee attempted to start their analyzer, it failed to start properly. They called the manufacturer who was unable rectify the problem over the phone. They performed a shutter test using a Ludlum Model 19 survey meter; the reading was approximately 90 microR per hour which was greater than expected. As instructed by the manufacturer's service representative, the analyzer was packaged, properly labeled and shipped back to the manufacturer's location in Rhode Island via Federal Express. The manufacturer will repair the malfunction and perform shutter and device leak tests. "DOH verified with the manufacturer's technical contact that the proper packaging included lead shielding adequate to completely shield the source and shutter, even if the shutter was stuck full open. "No DOH on-site investigation. No known media attention. "Notification Reporting Criteria: "Per WAC 246-233-020 General License - Certain measuring, gauging or controlling devices. "Isotope and Activity involved: one 30-millicurie americium-241 sealed source. "Overexposures? Unknown but most likely not. The unit was functioning properly on 16 May 2007, but first thing in the morning on 17 May 2007 the unit would not start up properly. It was then the malfunction was discovered. No workers were exposed. The RCI (radiation contact individual) and one supervisor were the only people to handle this instrument after it had failed. "Lost, Stolen or Damaged? (mfg., model, serial number): No loss or stolen. No obvious damage. It did not appear that it was dropped or anything happened to it between shut down on 16 May 2007 and start up on 17 May 2007. "Leak test? Shutter tests have been performed and documented every six months. Most recent leak test was 13 December 2005 (no contamination, < 0.000002 microcuries)." WA report number : WA-07-048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2007-06-06
43398 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-05-31 | 2007-06-01 10:15 | 2007-06-07 | AGREEMENT STATE REPORT OF A MEDICAL EVENT INVOLVING AN UNDERDOSE The following information was received via email from the State of Wisconsin: "Event Report ID No.: WI070011 "License No.: 079-1281-01 "Licensee: Aurora St. Luke's Medical Center "Event Location: Aurora St. Luke's Medical Center, Milwaukee, WI "Event Type: Medical Event "Notifications: RSO called DHFS 5/31/2007 "Event description: On the morning of 5/31/2007 a Y-90 TheraSphere procedure was attempted. 1.05 GBq (28.3 mCi) was prescribed by the authorized user's written directive to deliver 123 Gy to the patient tumor. The activity in the dose vial was in agreement with this written directive. The TheraSphere Delivery Device (TDD) was appropriately set up by the radiopharmacist and the RSO, following the check list provided by the TheraSphere manufacturer, MDS Nordion. The interventional radiologist prepared the patient under fluoroscopy and positioned the catheter to fit his desired treatment site. This was completed at 9:30 a.m. At 9:40 the TDD was attached to the catheter. The TheraSphere injection was then started by the authorized user. The RSO was monitoring the radiation exposure in the room and did not see the normally-expected rise in exposure rate as the TheraSpheres enter the catheter and then the patient. After a few moments (after the injection of about half the balloon-inflator/syringe) the injection was stopped to evaluate what had happened. The authorized user and RSO then noticed that the blue stopcock was in the wrong position, directing the TheraSpheres into the waste vial and not into the patient. "A radiation survey revealed that most of the radioactivity was now in the waste vial, very little (if any) in the patient, and some possibly remaining in the dose vial. It was decided to complete the normal four flushes of the dose vial into the patient, and to estimate the administered dose based on the activity in the waste vial. "After the procedure the activity in the waste vial was measured in the dose calibrator in nuclear medicine. 25.9 mCi Y-90 was measured at 10:40 a.m. This constitutes approximately 94% of the activity that was originally in the dose vial (accounting for decay). "The RSO estimates the dose delivered to the target volume in the patient liver is 6% of the intended dose, or 7 Gy. "At 11:00 a.m. the RSO measured the exposure rate at the surface of the patient to be 0.00 Mr/hr with a GM survey meter and 0.0 Mr/hr with an ionization survey meter. Therefore, very little of the activity was injected into the patient. The waste vial is now being held for decay-in-storage. All personnel in the procedure, the TDD, and the room were surveyed and found to be free of contamination. "The patient will be scheduled for re-treatment in the next few weeks. "The licensee is evaluating the checklist provided by the manufacturer. DHFS will review the licensee's 15-day report and evaluate the licensee's proposed corrective actions. "Media attention: None" * * * UPDATE AT 1128 EDT ON 6/1/07 FROM FSME (FLANNERY) TO J. ROTTON * * * This event (EN43398) has been reviewed and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-06-06
43397 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2007-05-31 16:40 | 2007-05-31 23:22 | 2007-05-31 | ONE HOUR REPORT NOTIFICATION: COMBUSTIBLE MATERIAL EXCEEDING ITEM RELIED ON FOR SAFETY (IROFS) LIMITS FOUND "BACKGROUND: "AREVA NP Richland routinely stores unmoderated uranium oxide powder ( < 1.0 wt.% moisture and < 1.0 wt.% moisture equivalent of approved additives) in metal 45-gallon drums with neutron absorbing inserts in warehouse #6. Metal 5-gallon pails containing no more than 18 kg of powder placed 4 per 25 inch X 25 inch metal pallet are also allowed to be stored in this warehouse in the same locations authorized to store 45-gallon drums. The option to storage of 5-gallon buckets in warehouse 6 is only occasionally used. "EVENT DESCRIPTION: "On May 31, 2007 at approximately 1640 PDT, a member of the AREVA safety staff completed a calculation to determine the volume of combustible material present in wooden pallets being used to store empty 45-gallon drum in the aisle between storage locations in warehouse 6. The presence of 27 wooden pallets had been observed during a previous walkthrough of the SNM storage warehouse. The volume of combustible material present in these pallets was about 56 [cubic feet]. The definition of failure of the administrative IROFS that restricts the amount of combustible material in this area is 54 [cubic feet]. "Currently the only SNM storage containers present in warehouse 6 are 45-gallon drums with neutron absorbing inserts. When these 45-gallon drums are stored in this area accidental nuclear criticality remains 'highly unlikely' even when the IROFS limiting the presence of combustible material fails. "However, if the restriction on the amount of combustible material fails and uranium oxide powder is stored in 5-gallon containers in this warehouse only a single IROFS would be present and accidental criticality does not remain highly unlikely. "SAFETY SIGNIFICANCE OF EVENT: "The safety significance of this condition is low because an accidental nuclear criticality for the as-found condition (only 45-gallon drums are currently being used to store uranium oxide powder) is still highly unlikely. Note: The condition being reported is only a potential but authorized plant condition. Furthermore, the municipal fire department works closely with the AREVA emergency response organization (ERO) when they respond to plant abnormal events and emergencies. The NCS organization is an integral part of the ERO and participates in the decision making during such events if NCS concerns exist. "There have been no known fires in this warehouse during its existence of over 20 years. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "Criticality could potentially occur during firefighting if the SNM in storage looses geometry control coincident with moderation. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "The process parameters controlled in the various storage warehouses include geometry, mass, moderation and neutron absorbers depending upon the storage configuration. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Plant-wide fire controls are established to ensure that large fires that would require the intervention by the municipal fire department are highly unlikely. This assures that the potential NCS concerns relative to fire-fighting with water are compliant with regulatory requirements. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "After discovery of the deficiency, the combustible material was removed from the warehouse. The material is currently compliant with the above listed requirements." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2007-05-31
43396 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2007-05-31 02:10 | 2007-05-31 10:43 | 2007-05-31 | LOSS OF EMERGENCY PLAN SIRENS DUE TO 69KV DISTRIBUTION SYSTEM FAULT "At 02:10 am CDT Wolf Creek's surrounding area experienced a power loss when a fault occurred in the 69KV distribution system. Power was lost in the cities of Burlington, New Strawn and the surrounding area. Wolf Creek's emergency plan sirens are powered from substations fed from the 69 KV distribution system. Associated with this power loss, Wolf Creek initially lost power to seven [of 11 total] Emergency Sirens. Four of the sirens had power restored in approximately 5 minutes, the remaining three Emergency Sirens remained without power for greater than 2 hours. Power was restored to the area surrounding Wolf Creek at approximately 04:30 am CDT. The Coffey County Sheriff's office was kept informed of siren status in the event that they would need to make local notifications. Wolf Creek remained connected to the electrical grid through all three 345 KV lines during the loss of the 69 KV system. "Coffey County, Kansas Department of Health and Environment, Kansas Department of Emergency Management and the Federal Emergency Management Agency Region 7 have been notified of the loss of sirens. "The Wolf Creek Communications Group has physically verified that all sirens have been returned to service." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-05-31
43395 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-05-29 08:35 | 2007-05-29 11:22 | 2007-05-29 | MANUAL REACTOR SCRAM DUE TO LOSS OF FEED PUMPS AFTER ELECTRICAL TRANSIENT "On 5/28/07 with Hope Creek in Operating Condition 1 at 100% Reactor power, an electrical transient and loss of 'A' and 'B' reactor feed pumps resulted in lowering reactor water level. Operators inserted a manual reactor scram at 0835 in response to the lowering reactor water level. Reactor water level lowered to (-) 38 inches subsequent to the manual scram, resulting in initiation of High Pressure Coolant Injection (HPCl) and injection to the reactor vessel. The Reactor Core Isolation Cooling (RCIC) system also initiated but tripped. Investigation of the cause of the electrical transient, loss of the 'A' and 'B' RFP's, and trip of the RCIC system are currently in progress. "Initial review of the event indicates that all other systems operated as expected. Current plant conditions as of 1100 are: Hope Creek is in mode 3 at 715 psig with heat removal to the main condenser via the Main Turbine Bypass valves. All control nods fully inserted on the scram. "This report also documents a 4 hour report under 10CFR50.72(b)(2)(iv)(A) for valid ECCS initiation and injection to the reactor vessel (RAL 11.3.1)." The reactor is stable with the water level currently at 17 inches and feedwater being supplied by the 'C' feed pump. No Safeties lifted during the transient. All systems functioned as required except for the trip of the RCIC. The licensee was not in any major technical specification LCO at the time of the trip. The licensee notified the NRC Resident Inspector. The licensee will also notify the States of NJ and Delaware, and Lower Alloways Creek Township. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-05-29
43394 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2007-05-29 08:08 | 2007-05-29 10:09 | 2007-06-13 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) REMOVED FROM SERVICE FOR COMPUTER UPGRADE "On 05/29/2007 at 08:08 am CDT, the Wolf Creek Nuclear Plant Information System (NPIS) was removed from service for a planned computer system upgrade. The system upgrade will result in the SPDS and Emergency Response Data System (ERDS) being inoperable for approximately three weeks. "Wolf Creek Nuclear Operating Corporation is making this ENS notification pursuant to the criteria of 10 CFR 50.72(b)(3)(xiii). There is no other loss of emergency assessment capability concurrent with the removal of the NPIS from service. Plant personnel entered the appropriate Off-Normal procedure and will obtain local readings for the equipment that is normally monitored by SPDS and NPIS during the plant computer upgrade. "The Senior NRC Resident has been briefed on this evolution and the planned return to service of the system." * * * UPDATE FROM LANE TO SNYDER AT 1802 EDT ON 6/11/07 * * * "On 06/09/07 at 18:46 CDT, the Wolf Creek Nuclear Plant Information System (NPIS) was returned to service following the computer upgrade. This restored the Safety Parameter Display System (SPDS) to OPERABLE and made the Emergency Response Data System (ERDS) available for use. The ERDS system will not be considered OPERABLE until testing has been performed with the NRC to confirm proper data transmissions. "Some data points and processes are still being tested prior to being returned to service." The licensee notified the NRC Resident Inspector. Notified R4DO (M. Hay). * * * UPDATE FROM JIM KURAS TO JOE O'HARA AT 1633 EDT ON 6/13/07 * * * "On 6/13/07 at 14:57 CDT (ERDS) testing with the NRC completed satisfactory to confirm proper data transmission." The licensee notified the NRC Resident Inspector. Notified R4DO(Hay). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-05-29
43393 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-05-28 22:50 | 2007-05-29 05:01 | 2007-05-29 | EMERGENCY DIESEL GENERATOR ACTUATION DUE TO MOMENTARY UNDERVOLTAGE CONDITION "Unit 1 was making preparations to parallel to the grid on 5/28/07. All busses had been transferred to the Startup power supply (230 KV System). Operations then started a large 12KV motor, Circulating Water pump 1-2. Starting this large motor caused a momentary dip in startup voltage. This voltage dip was sufficient to pick up the undervoltage relay on vital bus G, causing a start of that bus's Emergency Diesel Generator (EDG). The bus remained supplied by the startup power supply, the EDG did not load. This valid start of EDG 1-2 is being reported per 10CFR50.72(b)(3)(iv)(A). "The EDG was subsequently shut down and returned to it's normal standby condition." There is nothing unusual or not understood about this event and all systems functioned as required. The licensee notified the NRC Resident Inspector. | 8 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-05-29
43392 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-05-28 01:00 | 2007-05-28 08:48 | 2007-06-29 | HPCI PUMP INOPERABLE DUE TO DIFFERENTIAL PRESSURE SETTING NOT WITHIN SPECIFICATION "On 5/28/07 at 0100 CDT, Browns Ferry Unit 1 was performing 1-SR-3.5.1.7 (Comp) HPCI Comprehensive pump test when it was determined that HPCI pump set differential pressure was not within specifications and therefore would not support a declaration of operability for HPCI. "The event is reportable under 10CFR 50.72(b)(3)(v)(B) - 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat' and 10CFR 50.72(b)(3)(v)(D) - 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident'. "This event also requires a 60 day written report in accordance with 10CFR 50.72(b)(3)(v)(B) and 10CFR50.73(a)(2)(v)(D). "Initial investigation reveals a potential problem with the test equipment." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM M. RASMUSSEN TO W. HUFFMAN AT 1810 EDT ON 6/29/07 * * * "This report is being retracted. Engineering has re-evaluated the test results and determined that HPCI System pump met its design basis requirements during testing activities. As such, the circumstance discussed in this event report did not result in any condition that could have prevented the fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident. Therefore, this event is not reportable under 10CFR50.72(b)(3)(v)(B) or 10CFR50.72(b)(3)(v)(D). The licensee notified the NRC Resident Inspector. R2DO (Ayres) notified. | 9 | 0 | 0 | 9 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-05-28
43391 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-05-27 11:17 | 2007-05-27 18:08 | 2007-05-31 | MANUAL REACTOR TRIP IN MODE 3 DURING CONTROL ROD TESTING "On May 27, 2007, at 11:17 PDT, with Diablo Canyon Power Plant (DCPP) Unit 1 in Mode 3 (Hot Standby) during day 28 of refueling outage 14, operators manually actuated the reactor protection system. All rods fully inserted. "Operators were performing Surveillance Test Procedure (STP) R-1 C 'Digital Rod Position Indictor Functional Test'. While control bank C was being re-inserted, at 42 steps withdrawn, rod N-13 indicated position changed to 24 steps withdrawn. In response to this 18 step deviation, and in accordance with STP R-1C, operators opened the reactor trip breakers. "At the time of the event, the reactor coolant system remained at normal operating temperature and pressure, and all other shutdown and control rod banks remained fully inserted. "This event is being reported as an 8-hour non-emergency event in accordance with 10 CFR 50.72(b)(3)(iv)(A) for a valid actuation of the reactor protection system." Unit-1 is maintaining temperature with atmospheric steam dumps and aux feed water. Electrical power is from 500 KV backfeed (normal electrical shutdown lineup). Control rod N-13 was being tested along with seven other control rods. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/27/07 AT 2301 EDT BY JOY SKAGGS TO MACKINNON * * * "(STP) R-1C 'Digital Position Indicator Functional Test' was re-performed on control bank C to obtain additional information. "At 1706 hours, while control bank C was being re-inserted, at 138 steps withdrawn, rod N-13 indication dropped to 126 steps withdrawn. Rod motion was stopped to gather data. All other shutdown and control banks remained fully inserted. "At 1725 hours, operators manually actuated a reactor trip to fully insert all control bank C rods. All rods fully inserted. "(STP) R-1C 'Digital Rod Position Indicator Functional Test' was re-performed on control bank C for further evaluation. At 1838 hours, while control bank C was being re-inserted, at 168 steps withdrawn, rod N-13 indication dropped to 150 steps withdrawn. Rod motion was stopped to gather data. All other shutdown and control banks remained fully inserted. "At 1840 hours, operators manually actuated a reactor trip to fully insert all control bank C rods. All rods fully inserted. "At the time of the event, the reactor coolant system remained at normal operating temperature and pressure, and all other shutdown and control rod banks remained fully inserted." R4DO (C. Johnson) notified. The licensee will notify the NRC Resident Inspector. * * * UPDATE PROVIDED BY LARRY PARKER TO JEFF ROTTON AT 0951 EDT ON 05/31/07 * * * "On May 27, 2007, in response to the initial occurrence of Rod N-13 slipping at 11:17 PDT, PG&E contacted the vendor and researched operating experience to develop a troubleshooting plan. Management approved a plan based on the vendor recommendations, which consisted of exercising all rods successfully five cycles. It was acknowledged that additional slipping events could occur requiring mitigation by opening the reactor trip breakers. Upon implementation of this plan, two similar events occurred and are described in the update above [provided on 05/27 at 2301 EDT]. Following these events, Rod N-13 was successfully cycled five times without any deviation. Reactor startup was then allowed to proceed and there have been no further rod position deviation events." The licensee notified the NRC Resident Inspector. Notified R4DO (C. Cain) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-05-27
43390 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2007-05-24 15:40 | 2007-05-25 13:01 | 2007-05-25 | AGREEMENT STATE REPORT - Pd-103 SOURCE BROKEN OPEN The State provided the following information via facsimile: "Called to report an incident at Holy Cross Hospital. At 1540 hours, on 5/24/07, in room 11 of the operating room of the hospital, the Licensee ruptured a 3.2 mCi Palladium-103 seed while conducting a patient implant therapy. Preliminary licensee evaluation indicates that the Mick Applicator jammed and failed to advance. Efforts to free the device may have led to the seed fracture. The patient therapy was halted after 60 of the 83 seeds (given in the written directive) were successfully implanted. The Oncologist has indicated that the 60 seeds implanted were adequate for successful therapy and no additional seeds would be administered. Licensee followed radiation spill procedures and radiation surveys conducted by licensee RSO showed radioactive material contamination on the Mick Applicator and surrounding absorbent chucks. Contaminated materials have been controlled and stored in nuclear the medicine department. Smears of adjacent OR surfaces and floor were negative for contamination. The OR was released at about 1900 hours that day. The licensee has notified the manufacturer of the incident. Licensee will send initial written report by CBD 5/29/07 with follow-up detailed report within 30 days." Maryland Radioactive Material License: MD-31-001-03 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2007-05-31
43389 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-05-24 16:30 | 2007-05-25 09:41 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * 24-HOUR REPORT INVOLVING AN ITEM RELIED ON FOR SAFETY (IROFS) "BWXT operates a multiple-component acid cleaning operation for SNM [DELETED] components. One of the potential accident scenarios specifically evaluated in the Integrated Safety Analysis (ISA) is for the multiple components to be dislodged from the fixture and fall into the acid solution. If the components were to remain in the acid for a sufficient time, the acid could dissolve the [DELETED] releasing the SNM into unfavorable geometry acid tank. Dissolving through the [DELETED] and dissolving sufficient quantities of SNM to result in a potential safety issue would take about an hour. "To protect against this accident scenario, the fixture is designed to handle the components while maintaining the required spacing (IROFS). In addition, there is an engineered feature consisting of a timer and automatic acid dump valve (IROFS). This system will dump the entire acid bath from the tank well before the [DELETED] material is breached. "On May 24 2007, at approximately 4:30 p.m., an operator was placing a fixture holding 9 components on a 10 position fixture into the acid solution tank. The fixture hung up on the tank. The resulting impact caused 7 of the components dislodge from the fixture and fall into the tank. The fixture maintaining the spacing between components is an IROFS. The operator immediately initiated a manual dump of the acid solution and opened the water valve to rinse any residual acid off the components in the tank. The second IROFS, automated timer that activates the dump valve, was not challenged since the operator manually dumped the tank. "BWXT is making this 24 hour report in accordance with 10CFR70.61, Appendix A, (b)(2). "The component acid bath operation has been suspended and the failed fixture was tagged and taken out of service. The components which fell into the tank were inspected and found to have no loss of [DELETED] integrity. "The operator involved in the incident was FFD tested. "The NRC Resident Inspector has been notified and an investigation team has been established to perform a thorough review of the incident." * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
43388 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2007-05-23 12:00 | 2007-05-24 17:14 | 2007-05-24 | AGREEMENT STATE REPORT FROM MINNESOTA - MISSING IODINE-125 SEED The following event was received via e-mail "On April 23, 2007, 101 I-125 seeds (10 strands, each strand containing 10 seeds, and one calibrated seed) were received by the Nuclear Medicine Hot Lab and transported from the Nuclear Medicine Hot Lab to Rad Oncology for assay on April 24, 2007. All seeds were accounted for. One strand was dismantled and all 10 seeds were assayed and stored in a lead pig. The area was surveyed at the end of the assay process, and the seeds were maintained under lock until the next morning when they were retrieved for the procedure. "The following morning the strands were taken to the Operating Room for the procedure. The 10 loose seeds used in the assay were loaded in a Mick Cartridge (a device used for surgery) and transported to the OR. "After the procedure all seeds implanted, seeds in strands and the cartridge (as a whole and not counting the seeds loaded in it) were accounted for. All strands were stored in a lead pig, and the cartridge was stored in a second pig. The package containing both pigs was transported to Rad Oncology and was kept under lock at all times. "On May 23, 2007, a re-count of the seeds was completed before sending them to the manufacturer. The calibrated seed and the seeds from the strands were accounted for. The cartridge contained 9 out of the 10 seeds it was supposed to be holding. The seed activity at the time it was missed (5/23/07) was 0.361 mCi. "The area where the cartridge was loaded and unloaded was surveyed as well as the two units that were used to sterilize the seeds. Surveys of some of the areas where the package was transported are still in progress." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2007-05-29
43387 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-04-01 02:49 | 2007-05-24 12:54 | 2007-05-24 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION DUE TO A FAILED RELAY COIL "This 60-day telephone notification is being made under reporting requirements specified by 10CFR50.73 (a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 0249 on April 1, 2007, with the Duane Arnold Energy Center (DAEC) operating at 100% power, an invalid Group 3 isolation on the 'B' side of PCIS occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation, and Purge, Containment Nitrogen Compressor Suction and Discharge; Recirculation Pump Seals, and Post Accident Sample System. "This event was caused by a failed (open) relay coil in a Potter Brumfield model KH4690 24VDC relay in the 'B' Fuel Pool Exhaust Radiation Monitor logic. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-05-24
43386 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2007-05-22 17:00 | 2007-05-24 12:45 | 2007-06-14 | LOST/STOLEN TROXLER MOISTURE DENSITY GAUGE Rogers Group Company conducted a test at mile marker 63 on Edward T. Breathitt Parkway. After the test was completed they placed the Troxler 4640-B Moisture Density gauge [S/N 1772], 9 millicuries of Cs-137 [Sealed Source Model No. A-102112], in the back of the bed of truck, did not store it or tie it down, and they drove 3.5 miles South on Edward T. Breathitt Parkway at which time they turned around and drove back to mile marker 63. When they arrived back at mile marker 63 they discovered that the gauge was missing, believe that the gauge had fallen out of the truck while it was being driven. They retraced their route that they had taken and asked several working crews if they had seen the missing gauge. The gauge was not found and the licensee believes that a motorist had stopped and picked up the gauge. The licensee notified the State Police of the missing gauge. Reference Number: KY070002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE RECEIVED FROM BRIAN PARSLEY TO JOE O'HARA AT 1519 ON 6/14/07 * * * The Troxler Gauge has been found and returned to the licensee. Apparently, the gauge was recovered on 5/22/07 by a former employee of the Rogers Company, in the same general area where it was lost. The former employee took the gauge to his home in Vansans, Indiana. The individual reported the recovered gauge to the Vansans Police Department who contacted the Kentucky State Police. Both law enforcement agencies were able to confirm the identity of the gauge, and the gauge has been placed in the custody of the licensee. Notified R1DO(Doerflein), R3DO(Phillips), and FSME(Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2007-05-29
43385 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-05-24 08:15 | 2007-05-24 12:26 | 2007-05-24 | OFFSITE NOTIFICATION MADE TO ANOTHER GOVERNMENT AGENCY "A required 24-hour notification was made by Paducah Regulatory Affairs to EPA Region IV in Atlanta, GA at 0815, 5-24-2007. The notification was made concerning a PCB spill of greater than the agreed upon action level of 10 pounds of PCBs confined within a building. "The approximate 3 gallon PCB oil spill was from an electrical capacitor located inside the C-333 Process Building. The oil spilled onto a concrete floor and was contained to the immediate area. The area was flagged and posted as a PCB spill area and clean up is in progress. "This event is reportable as a 4 hour event as required by the NRC NUREG 1022, a specific report made to a government agency. PGDP Assessment and Tracking Report No. ATR-07-1362; PGDP Event Report No. PAD-2007-06; Worksheet No. 43385." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2007-05-24
43384 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2007-05-24 11:00 | 2007-05-24 12:23 | 2007-05-24 | EMERGENCY OPERATIONS FACILITY OUT OF SERVICE FOR PLANNED MAINTENANCE "EOF resources OOS due to planned maintenance of electrical supply transfer switch. No power available to EOF." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 13:39 ON 5/24/07 FROM BRUCE SHICK TO MARK ABRAMOVITZ * * * Power was restored to the EOF at 13:30 on 5/24/07. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-05-24
43383 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-05-23 | 2007-05-24 10:08 | 2007-10-11 | AGREEMENT STATE REPORT INVOLVING TWO STOLEN TROXLER MOISTURE DENSITY GAUGES Greenhorne and O'Mara Consulting Engineers Report: "Licensee called BRC at 8:20am on 5/24/07 to report (2) Troxler gauges stolen from their temporary work site in Nokomis, FL [corner of SR 681 and US 41]. Both gauges were last seen 5/23/07 around 6 pm and were discovered missing early morning 5/24/07. Gauges were locked and secured inside a steel container (conex box) at the temporary job site. Sarasota County Sheriffs department was notified and is investigating. A police report is expected shortly. One of the Troxler gauges belongs to another licensee at the work site: Hubbard Construction company (see incident # FL-07-084). Both licensees were made aware that the BRC recommends that they offer a reward for information leading to the recovery of the gauges and that they advertise in the newspaper, and/or inform the local TV News regarding the reward offer. NRC and HSER were notified. Investigation will continue." Both gauges are Troxler Model 3411B (S/N's 20029 and 6127), each containing two (2) sources, i.e., 8 millicuries Cs-137 and 40 millicuries Am-241:Be. At the time the State of FL was notified, the Sarasota Sheriff's Department was enroute to the scene. Florida report: #FL-07-083 and FL-07-084. Florida License Numbers: Hubbard: 1100-1, Greenhorne and O'Mara: 2143-1 * * * UPDATE ON 10/11/07 FROM STEVE FURNACE TO RYAN ALEXANDER * * * On 10/11/07, the State notified the HQ Operations Officer that both Troxler gauges were found in the woods near Naples, FL (Sarasota Co.) with the handle locks intact on 10/01/07. The Florida Bureau of Radiation Control verified no abnormal radiation coming from or contamination on the gauges. The State contacted the licensees and returned the gauges to the licensees. Notified FSME EO (Flanders), R1DO (Cook), and ILTAB (e-mailed) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-05-29
43382 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-05-24 02:32 | 2007-05-24 05:11 | 2007-05-25 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "This 4-hour notification is being made to report that Salem Unit 2 automatically tripped on low steam generator water level. The automatic trip was preceded by lowering steam generator feed pump suction pressure, followed by the trip of both steam generator feed pumps on low suction pressure. The cause of the low suction pressure was due to a condensate system breach that occurred in the Condensate Polisher building. The condensate polishing system has been isolated and condensate pressure has stabilized. "Salem Unit 2 is currently in mode 3 with reactor coolant system temperature at 547 degrees with pressure at 2235 psig. Auxiliary feedwater pumps 21, 22, and 23 started automatically, as expected, due to the low steam generator level. Decay heat removal is via the steam dumps to the main condenser. All equipment functioned as designed. There were no personnel injuries. "A 15 minute notification was made to the State of New Jersey due to hydrazine laden water exiting the Condensate Polisher building and entering the storm drainage system." All control rods fully inserted following the reactor trip. Emergency Diesel Generator are available, if needed. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 17:18 ON 5/25/2007 FROM ERIC POWELL TO MARK ABRAMOVITZ * * * "In addition to hydrazine that was contained in the condenser water that exited the Condensate Polisher Building, supplemental samples determined that the water also contained tritium at approximately 50,000 picoCuries per liter. The state of New Jersey was updated with this information." Notified the R1DO (Trapp). The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-05-24
43381 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-05-24 02:11 | 2007-05-24 04:42 | 2007-05-24 | MANUAL REACTOR SCRAM DUE TO ELECTRO-HYDRAULIC CONTROL (EHC) SYSTEM LEAK "On 05/24/2007 at 0211 CDT Browns Ferry Unit 1 initiated a Manual reactor SCRAM due to an Electro-Hydraulic Control (EHC) System pressure lowering and reservoir level lowering due to an EHC system leak. The leak was from #6 Main Turbine Combined Intermediate Valve (CIV). All Systems responded as required to the manual SCRAM signal. No Emergency Core Cooling System (ECCS) initiations occurred as a result of the manual SCRAM signal. Reactor water level was maintained in the normal band during the SCRAM. There were no Primary Containment Isolation signals received during the SCRAM. The EHC leak was stopped due to reservoir level depletion and EHC pumps being secured. There were no indications of main steam relief valves (MSRVs) opening. Reactor pressure is being controlled using Main Steam Line Drains. Reactor Level is being maintained in band using Control Rod Drive pumps. Repair of the EHC leak is in progress." The Scram was characterized as uncomplicated. All rods fully inserted. The only significant equipment out of service at the time was RCIC. When the leak was initially discovered, it was about 60 drops per minute. When repairs were attempted, the piping separated and approximately 600 gallons of EHC fluid was discharged out the break onto the turbine building floor. Cleanup of the EHC fluid is in progress and environmental monitoring is in place to assure no offsite release of the spill. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-05-24
43380 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-05-22 05:15 | 2007-05-22 12:07 | 2007-05-22 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE "At 0830 on 5-22-07, the radiation safety officer notified [California Radiological Health Branch] that a vehicle (Chevy Silverado with an attached camper shell) was stolen with a nuclear gauge locked in the camper shell (Troxler, model 3440, #18250 with 8 mCi Cs-137 & 40 mCi Am-241:Be). The gauge was locked inside a transport case, the transport case was chained, blocked, & braced in the camper shell. The gauge user does not remember if the door to the camper shell was locked. The gauge user had not secured and locked the club to the steering wheel and he does not think the handle of the gauge was locked. The driver discovered the theft around 0515 this morning when he returned to his vehicle after being in a donut shop for approximately 10 minutes. The donut shop is located in Bellflower on the corner of Alondra and Eucalyptus. The Lakewood Police Department were notified and they took the report of the theft. The RSO was asked to notify [California Radiological Health Branch] immediately if the gauge was recovered. The licensee will be cited for failing to properly secure the gauge. Corrective actions: The licensee will counsel the gauge user, will provide refresher training to all gauge users on the required security of the gauge while in transit, and will perform unannounced inspections of each gauge user's vehicle to ensure they are following the company's established policies and procedures regarding the security of gauges while in transit." Lakewood Police Report #: 607-14202-1337-093 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-05-25
43379 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-05-21 12:31 | 2007-05-21 19:17 | 2007-05-21 | POTENTIAL DIVISION 1 EDG DAMAGE DUE TO LOSS OF SERVICE WATER COOLING DURING CONTROL ROOM FIRE "During a review of an Operating Experience issue (LO-GLO-2006-0090 CA5), a condition was found which is not consistent with the assumptions of the River Bend post-fire safe shutdown analysis. 10CFR50 Appendix R states that for alternate shutdown capability (i.e shutdown from outside the main control room) support systems (service water cooling) for critical post-fire safe shutdown components must remain free from fire damage. Generic Letter 86-10, 'Implementation of Fire Protection Requirements' state that the following assumptions are required for evaluation of a control room fire: 1) fire induced spurious operation of safe shutdown components has occurred; 2) offsite power is lost and; 3) loss of automatic starting of the onsite AC generators as well as the automatic function of valves and pumps whose circuits could be affected by a control room fire. "In addition to loss of automatic start of the emergency diesel generators, the post-fire safe shutdown analysis must also evaluate the consequences if the diesel generators do start concurrent with fire induced multiple spurious actuations. Since control circuits for motor operated valves for the standby service water system are routed in the control room, fire induced shorts could place these valves in a position that would prevent service water from cooling the Division 1 emergency diesel generator. In the time required for Operations personnel to evacuate the control room and re-establish control of the standby service water system at the Division 1 Remote Shutdown panel, thermal damage to the diesel generators could render the Division 1 generator incapable from performing its post-fire function. "The RBS [River Bend Station] post-fire safe shutdown analysis is based on the assumption that the diesel generator high temperature trip function would remain functional based on the fact that the trip logic is located outside of the main control room and therefore would remain free from fire damage. The investigation performed during the OE review uncovered the fact that at RBS when the emergency diesel generator is started in the emergency mode the non-safety trips (such as high temperature) are by-passed. The loss of off-site power starts the diesel generator in the emergency mode; therefore the high temperature trip is by-passed. With the non-safety trips by-passed, the diesel generator will continue to run even without sufficient cooling. "This condition involves compliance with 10CFR50, Appendix R. Plant equipment remains capable of performing the remaining design functions. The scope of this analysis deficiency is limited to the Main Control room fire scenario, with multiple concurrent failures. The Control Room is continuously manned. The affected cables in the MCR under-floor area are protected by automatic fire detection and automatic suppression systems, which would rapidly detect and smother a fire. Introduction of ignition sources, such as work involving welding or grinding is strictly controlled by station procedures. Furthermore Standing Order #193 Revision 3 limits hot work in the main control room during Modes 1,2 and 3." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-05-21
43378 | 0 | WASHINGTON HOSPITAL CENTER |  |  |  |  | 2007-03-23 | 2007-05-21 15:08 | 2007-08-09 | PART 21 DEFECT - BRACHYTHERAPY SEEDS UNABLE TO RETURN TO TRANSFER DEVICE AFTER TREATMENT "Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: "Facility: Washington Hospital Center; "Activity: IVRT using a Beta Cath System. "Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: "Best Vascular, Inc. (formerly known as Novoste Corporation). "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply: "The patient is treated with beta radiation using the Beta Cath device. For the treatment, the sources are monitored and confirmed in the correct treatment position by fluoroscopy. At the completion of treatment, sometimes the seeds are unable to return to the transfer device. Therefore, the beta-rail catheter with all the seeds in it is taken out immediately and placed in the bail out box. The box is then transported back to the storage area. Patient and the area are surveyed to ensure that they are free from all radiation sources. The patient receives the full dose as prescribed. No additional or unnecessary dose is delivered to the patient. There were no medical events. The hospital's Radiation Safety Officer and Best Vascular (Novoste) are notified when this incident occurs. A faulty device is returned to the manufacturer and not used on patients. An incident report is filed for each incident. The device with the catheter is shipped back to Best Vascular for disposal and a new replacement source is requested. The incident is deemed as equipment malfunction. It is an inherent problem with the device itself. "The date on which the information of such defect or failure to comply was obtained: "2007: 1/18/07, 2/12/07, 3/7/07 and 3/23/07 "2006: 9/7/06, 11/6/06 "2005: 2/18/05, 4/8/05, 4/14/05, 8/3/05, 10/6/05 "In the case of a basic component which contains a defect or fails to comply, the number and location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: "The device consists of a hydraulic system and it fails while retracting the sources after the treatment is complete. It happens for both 60 mm and 40 mm devices that we currently use. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action: "Corrective Action: The licensee always followed the manufacturer's emergency procedure. "Organization: Washington Hospital Center "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: "Recommend the vendor to perform an extensive QC test before shipping the device to the customer. It may reduce the number of occurrences." * * * UPDATE FROM MOHAPATRA TO HUFFMAN AT 13:29 EDT ON 8/9/07 * * * The licensee was performing another IVRT (Intravascular Radiation Treatment) today (8/9/07 at 10:35 EDT) when the Brachytherapy device failed to retract. The device was using a 60 mm catheter with 24 Strontium-90 seeds. As noted above, the licensee uses a Beta Cath System that were originally supplied by Novoste Corp and are now serviced under Best Vascular, Inc. The catheter with the seeds were immediately removed and placed in a "bail-out" box. The device with the catheter and seeds will be returned to the manufacturer. There was no exposure issue or medical event as a result of this malfunction. This report is being made to document continued problem with this device as noted in the previous report. The licensee plans to contact the NRC Regional Inspector (Gabriel) about this event. The R1DO ( Summers) and FSME (Zelac) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | DC | OTH | PAR | 21.21 |  |  |  | 0 | 2007-05-21
43377 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-05-17 | 2007-05-21 14:40 | 2007-05-22 | AGREEMENT STATE REPORT - MEDICAL EVENT "RSO contacted this office [Florida Bureau of Radiation Control] at 1335 hours 21-May-2007 to report a medical event. Patient has metastatic cancer and no thyroid. Doctor prescribed a whole body scan. Technologist gave patient a therapy dosage for the cancer, instead of the scan. Doctor and patient notified of misadministration. This incident referred to the radioactive materials office for investigation. No further action will be taken on this incident." The therapy dosage administered was 26.8 mCuries of I-131 in liquid form. Florida Incident number: FL07-081 * * * UPDATE BY E-MAIL AT 1547 EDT ON 5/22/2007 FROM C. FLANNERY TO JEFF ROTTON * * * "This event has been reviewed and determined to be a reportable medical event." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-05-25
43376 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2007-05-19 11:27 | 2007-05-19 16:15 | 2007-05-19 | REACTOR SCRAM DUE TO TURBINE TRIP ON LOSS OF CONDENSER VACUUM "Grand Gulf scrammed at 11:27 on 5/19/07 due to Turbine trip caused by loss of vacuum (believed to be from condenser neck seal). All safety systems responded as required. All control rods inserted. No ECCS systems were required to initiate. Reactor vessel level 3 was reached and both divisions of isolation logic initiated. All associated valves already closed (normal lineup). "Present condition is Mode 3 and reactor pressure is 250 psig. Cooldown is in progress." No relief valves lifted as a result of the scram. Decay heat was initially removed via bypass valves to condenser. The plant then shifted to decay heat removal via drains and SRV's. Suppression pool temperature is 80 degrees and available if required. Offsite power is available and all emergency systems are available if needed. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-05-19
43375 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-05-19 02:12 | 2007-05-19 05:26 | 2007-05-19 | MANUAL REACTOR TRIP DUE TO CONTROL ROD HCU VALVE BONNET LEAK INTO REACTOR BUILDING "On the evening of 5/10/2007, Cooper began a scheduled down power to accomplish required preventive and corrective maintenance, including replacement of directional control valves on three control rod drive (CRD) hydraulic control units (HCU). HCU 26-27 was hydraulically isolated for maintenance. The plant was in a single recirculation loop configuration to perform corrective maintenance on 'A' Recirculation Motor Generator. A single reactor feed pump was in operation for corrective maintenance to the 'A' Reactor Feed Pump lube oil system. "At approximately 0025 CDT on 5/19/2007 reports from the field indicated that a small water leak had developed from the body to bonnet seal of CRD-V-122 for HCU 26-27. The manual isolation valves for the HCU were already closed to isolate the maintenance area. However, due to seat leakage past one or both of the manual isolation valves, the leakage continued and degraded to the point that a visible plume of steam was issuing from the valve. Further, high airborne activity level developed in the vicinity of the HCU bank in the Reactor Building. As a precaution, the Control Room supervisor (CRS) evacuated the Reactor Building at 0125 CDT. "At 0200 CDT, the CRS entered the station reactor scram procedure and performed the preparation steps of transferring electrical loads to the startup transformer. At 0212 CDT, the reactor was manually scrammed. All rods inserted normally. A Group 2 containment isolation signal was received on low reactor water level at 3". During the recovery, the remaining reactor feed pump was manually tripped at 50" in accordance with station procedures due to high RPV level conditions. " 'B' RFP was restarted when conditions permitted and is being used to control RPV level. RPV pressure is being controlled by the bypass valves rejecting heat to the main condenser. "This report is being submitted pursuant to 50.72 (2)(iv) for a critical scram and specified system actuation for the Group 2 containment isolation. "Currently, the leak into the Reactor Building has stopped. Radiological conditions are being assessed and a repair and recovery plan developed. "The Senior Resident Inspector has been informed." The scram was characterized as uncomplicated and all systems functioned as required. No personnel contaminations or off-site releases occurred due to the HCU valve leak. | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-05-19
43374 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-05-18 17:45 | 2007-05-18 19:37 | 2007-05-18 | INOPERABLE HPCI PUMP "While investigating an oil leak on the HPCI oil piping, the reservoir level was determined to be higher than expected. Further investigation led to the discovery of water in the HPCI oil system. The quantity of water in the oil was sufficient to impede normal HPCI operation. Therefore, HPCI was declared inoperable." The licensee noticed an oil leak while conducting routine plant rounds. When the operator investigated the oil leak further, he noticed the oil level in the reservoir was higher than expected. The licensee is investigating the source of the water but they believe the seal leak-off line may be clogged. The licensee plans to drain down, flush the system, refill and run the pump for operability determination by the afternoon of 5/19/07. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-05-18
43373 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-05-18 18:03 | 2007-05-18 19:03 | 2007-06-15 | TWO IRRADIATED FUEL PELLETS UNACCOUNTED FOR IN UNIT 3 SPENT FUEL POOL "This is a non-emergency Event Notification made in accordance with 10 CFR 20.2201(a)(1)(ii) to inform the NRC of lost or missing licensed material. "As part of a self-assessment of the Material Control and Accountability (MCA) program at Dresden Nuclear Power Station (DNPS), EGC reviewed a 1977 vendor fuel reconstitution report for a failed fuel assembly. This report indicated the encapsulation of two fuel pellets from a previous fuel inspection. After considerable investigation to locate these pellets, at 1803 hours on May 18, 2007, EGC determined that the specific location of two irradiated fuel pellets from a previously failed fuel bundle in the DNPS Unit 3 spent fuel pool (SFP) was unknown (i.e., unaccounted). As the location of the two pellets cannot be positively identified at this time, this is being reported as lost or missing licensed material. This determination is based on an initial review of inventory and fuel reconstitution records and an on-going inspection of the Unit 3 and 2 spent fuel pools. "The two pellets came from a broken fuel rod found during a Unit 3 fuel reconstitution effort in 1973 after its first cycle of operation. The two pellets were recovered, and placed in a stainless steel bucket. Subsequently, both pellets were encapsulated in an aluminum container in November 1976. A special nuclear material inventory performed in April 1977 indicated the presence of the pellets in the aluminum container in the Unit 3 SFP. No other records since that inventory have been identified indicating the location of the fuel pellets. "EGC has contacted more than 25 current and former employees who were working in the fuel handling, reactor engineering and SNM Control areas during the 1970's and 1980's in an effort to determine the likely location of the fuel pellets. "EGC has inspected all readily accessible areas of the Unit 3 SFP. Open containers in the SFP, empty fuel storage cells and SPF cells containing objects that can be easily moved (i.e., blade guides, dummy fuel assemblies) have been searched and were determined to not contain the fuel pellets. Search of remaining areas of the Unit 3 SFP is in progress. Although it is unlikely that the two pellets were transferred to the Unit 2 SFP, EGC is also inspecting the Unit 2 SFP and has completed a search of all open containers and empty fuel storage cells. Inspection of both pools is scheduled to be completed by June 1, 2007. "In parallel with the physical inspections, EGC has also performed an extensive review of site documentation in an effort to determine the location of the fuel pellets. This search has included SNM piece counts, inventories and move sheets, NRC Form 741 and 742's, radiological material shipping records, fuel pool re-rack and cleanup campaign records, reactor engineering logs, fuel handler logs, and shipping records of possible vendors that might have received a shipment of radiological material. The documentation search has not revealed the location of the fuel pellets. "Based on the nature of the fuel rod encapsulation and radiation monitoring, a high degree of confidence exists that the pellets are in a restricted area of the plant or otherwise under the control of a facility licensed by the NRC such that the public health and safety has not been adversely affected. In addition, there is no evidence of theft or diversion. This notification satisfies the 30-day notification requirement of 10 CFR 20.2201(a)(1)(ii). A subsequent written report will be made in accordance with 10 CFR 20.2201(b)." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1441 EDT ON 06/15/07 FROM WILLIAM HIGGINS TO S. SANDIN * * * The following information was provided as an update including identification of additional applicable reporting criteria: "This is an update of a non-emergency Event Notification that was previously made on May 18, 2007 in accordance with 10 CFR 20.2201. "This is a non-emergency Event Notification made in accordance with 10 CFR 74.11, 'Reports of loss or theft or attempted theft or unauthorized production of special nuclear material,' paragraphs (a) and (b) to inform the NRC of lost special nuclear material (SNM). "As part of a self-assessment of the Material Control and Accountability (MCA) program at Dresden Nuclear Power Station (DNPS), Exelon Generation Company, LLC (EGC) determined that the specific location of two irradiated fuel pellets from a previously failed fuel bundle in the DNPS Unit 3 spent fuel pool (SFP) was unknown (i.e., unaccounted). This determination was based on an initial review of inventory and fuel reconstitution records. "EGC has completed an extensive search for the pellets including the interview of current and former employees, inspection of the Units 2 and 3 SFP, and performed an extensive review of site documentation. The search has not revealed the current location or final disposition of the fuel pellets. "Based on the nature of the fuel pellets and radiation monitoring, a high degree of confidence exists that the pellets are in a restricted area of the plant or otherwise under the control of a licensed facility such that the public health and safety has not been adversely affected. In addition, there is no evidence of theft or diversion. "This notification satisfies the one-hour notification requirement of 10 CFR 74.11, paragraphs (a) and (b). A subsequent written report will be made in accordance with 10 CFR 20.2201(b). "The licensee has informed the NRC Resident Inspector of this issue." Notified R3DO (Ann Marie Stone) and ILTAB (via email). THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 98 | 98 | 0 | 98 | 98 | 0 | -1 | -1 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X | LOST/STOLEN SNM |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 20.2201(a)(1)(ii) | 74.11(a) |  |  | 1 | 2007-05-18
43372 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2007-05-18 | 2007-05-18 16:05 | 2007-05-18 | AGREEMENT STATE REPORT - LOST & RECOVERED TROXLER GAUGE An employee of Applied Geotechnical Engineering Consultants was using a Troxler moisture density gauge at a jobsite. He left the gauge on the tailgate of his truck and then drove away. The gauge fell off and was picked up by a member of the public, who in turn called the licensee. The licensee picked up the gauge. The state did not have detailed information concerning the Troxler gauge, however, they did say the sources were in the locked position. Typically the Troxler gauge has sources of Am-241/Be (40 mCi) and Cs-137 (8 mCi). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2007-05-23
43371 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-05-17 | 2007-05-18 15:08 | 2007-05-18 | AGREEMENT STATE REPORT - SUSPECTED RADIATION BADGE OVEREXPOSURE "The RSO called to notify the Agency that for the April '07 dosimeter report, a reading of 5,131 mrem was assigned to the dosimeter worn by a radiography trainee. This individual is no longer employed by the licensee. "According to existing radiation reports, the trainee was not actively involved in performing industrial radiography for the said time period. He also claims to have stored his badge in a trailer for at least five days of the month opening a question to deliberate tampering. Radiography with Ir-192 was being performed in the general area but the trainee alleges that his participation was limited to a barricade watch. Other personnel with Conam support this recollection. [The Texas Department of Health Incident Investigation Program] will submit a completed report when the licensee and the Agency complete the investigation." Event Report ID: 07-43371 Texas Incident No: I-8414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-05-23
43370 | 0 | VARFLEX CORPORATION |  |  |  |  | 2007-05-18 | 2007-05-18 11:07 | 2007-05-18 | ELECTRICAL INSULATING SLEEVING HAS NOT BEEN SUBMITTED FOR UL FLAMMABILITY COMPLIANCE The licensee provided the following information via facsimile: "Since 1999, our customer, Transco Products Inc., Chicago IL, has purchased items of electrical insulating sleeving (natural Varglas Silicone Resin 500 Sleeving Class H-A-1) in various sizes from us with the requirements that they be UL recognized for 200 degrees C, 600 volt service and that they comply with ULs VW-1 flammability requirements to be accomplished by a Certificate of Conformance attesting to those points. "Although this sleeving's UL recognition for 200 degrees C, 600 volt service is covered under UL File E63450, and is not recognized for complying with the type VW-1 flammability classification under File E63450, the material was certified to Transco's purchase orders. "Transco's customer is Exelon Corporation, Chicago, IL. "However, although the above product has not been submitted to, nor has it been recognized by, UL for compliance to its VW-1 flammability requirements, Varflex tests, done in complete accordance with ULs VW-1 Test procedures, indicate the product does qualify for UL recognition and, therefore, does not create a substantial safety hazard. "UL recognition will be pursued." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2007-05-18
43369 | -1 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2007-05-17 12:30 | 2007-05-17 20:23 | 2007-06-26 | DEGRADED CONDITION - DEGRADATION OF PRINCIPAL SAFETY BARRIER "Under 10CFR50.72 (b)(3)(ii)(A), the following event has been determined to be reportable. This section concerns the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. This criteria was determined to apply to material problems that cause abnormal degradation of or stress upon a principal safety barrier (in this case, Reactor Coolant System). "On 5/17/07, a Nine Mile Point Unit 1 shutdown was in progress for forced outage inspection and repairs of the Turbine Lube Oil system. Prior to the shutdown, a discrepancy was being experienced between Reactor level readings from channel 11 and 12 Reactor Level columns. A step change increase of 2 inches of Reactor level had occurred on May 6th, 2007 on Reactor Level column 12. This change was coincident with an increase of 18 [degrees] F of the reference leg and 2 [degrees] F decrease of the variable leg. The level difference was then 5 inches with a Technical Specification limit of 6 inches based on current Drywell temperature. The condition was documented in the Corrective Action Program, compensatory actions were taken, and an Integrated Response Team was formed to investigate and determine the cause. Calculations by engineering determined a leak of 4 drops per minute could explain the observed indications. "During the initial drywell entry a visual examination was performed on the reference leg instrumentation line associated with Reactor Level Column 12. The piping was visually examined for any evidence of leakage. The exam was performed from the bottom of the condensing pot piping to the drywell shell penetration. The examination revealed a wet area at the bottom of a 1.0 inch 90 degree pipe elbow at an associated socket weld. The weld had one drop approximately 1.0 inch from the toe of the welds on the bottom of the pipe. The drop was wiped away with a leather gloved hand, which did show evidence of leakage. After waiting approx. 15 minutes, no additional leakage was observed. Reactor pressure had been lowered to approximately 400 psig at the time of the inspection due to the Reactor shutdown in progress. The piping, welds and Reactor level column above were closely examined and no other wetness or evidence of leakage was found. Also an exam was performed below pipe weld 012 (surrounding areas) and again no evidence of leakage could be found. No staining or other discoloration could be seen. The observations were documented in the Corrective Action Program." The licensee also provided the following information: Location of the Leak: 12 Yarway Reactor Level Reference Leg Leak Rate: 1 drop per minute T.S. Limits: 5 gallons per minute Sudden or Long-term Development: Sudden Leak Start Date: 5-06-2007 Time: 08:10 a.m. EDT Coolant Activity: 2.02 E-3 microcuries/ml Secondary: N/A List of Safety Related Equipment Not Operational: None The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1705 EDT ON 06/26/07 FROM BRIAN FINCH TO J. ROTTON * * * The licensee is retracting this report based on the following: "Following plant shutdown the piping segment from the 12 Yarway Reactor Water Level Reference Leg initially believed to be leaking was removed from the station for examination and testing. The piping segment was subjected to a 1600 psig nitrogen pressure test for approximately one half hour with no indications of leakage. Additional nondestructive examinations were performed which also did not show evidence of through-wall indications. Based on the exploratory nondestructive examination and leak testing completed in the field and on the removed piping segment, it was determined that there was no actual leakage in the drywell associated with the 12 Yarway Reactor Water Level Reference Leg piping. Further leak testing identified a 5 to 6 drop-per-minute leak from the drain valves associated with the 12 Yarway Reactor Water Level Reference Leg. Based on engineering analysis, this amount of leakage through the drain valve assemblies accounted for the level instrumentation differences noted between channel 11 and 12 Reactor Water Level columns. "Following maintenance and repair activities, in-situ leak checks were performed on the reference leg piping in the drywell and the associated instrument rooms outside the drywell during plant startup on 5/22/2007 at approximately 900 psi with no leakage identified. "Due to the leakage being identified in the valve assemblies for the level instrumentation and not in the piping inside the drywell, this issue does not represent a reportable condition under 10CFR50.72 and therefore is being retracted." The drain valve has been repaired. The licensee informed the NRC Resident Inspector. Notified R1DO(Powell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-05-17
43368 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-05-17 13:40 | 2007-05-17 14:07 | 2007-05-17 | OFFSITE NOTIFICATION DUE TO FAILED EMISSIONS TEST "I am calling you to provide a notification of a potentially failed air emission test on an auxiliary boiler. There is absolutely no evidence to suggest that any emissions from our boilers caused any harm to human health, welfare, or the environment. The emissions are not continuing and there is no assistance required or requested. The statute requires I provide this notification to assert an affirmative defense or a rescission as appropriate. The New Jersey Department of Environmental Protection Hotline was called to report this, Case number 07-0517-134537, operator 27. "During the start-up tuning and testing of our new auxiliary boilers, it appears that a malfunction of equipment during testing resulted in inconclusive test results for NOx loading for our #1 Boiler. For the testing runs, the measured volumetric stack flows were significantly higher than the stoichiometrically calculated stack flows based on fuel flow measurements. "While we are still investigating this discrepancy, we preliminarily believe that it was the result of either equipment malfunction, performance of necessary equipment maintenance and equipment start-up and shutdown." The licensee has notified the State (DEP) and will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-05-17
43367 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2007-05-16 16:55 | 2007-05-16 20:08 | 2007-05-17 | LOSS OF 26 EMERGENCY SIRENS DUE TO SEVERE WEATHER "Due to severe weather storms in the area surrounding Indian Point Energy Center, 26 of the 156 emergency sirens have been out of service as of 1655 hours on 5/16/07 due to either loss of local AC power (24 sirens) or communications problem (2 sirens). 15 of the 26 sirens are in Rockland County; the remaining 11 sirens are in Westchester County. Sirens in Orange and Putnam counties were unaffected. Rockland and Westchester Counties have been notified and route alerting is available as an alternate means of public notification. Additionally, a high speed telephone notification system is available for public notification by the counties. Contact of the local utilities has been initiated to request power restoration to the areas associated with the 24 effected sirens; the communication problems with the remaining 2 sirens are under investigation." The licensee notified the NRC Resident Inspector, New York State Public Service Commission, and Rockland, Westchester, Putnam and Orange counties. * * * UPDATE PROVIDED BY JOHN WELLS TO JEFF ROTTON AT 0318 EDT ON 05/17/07 * * * "Update on status of report on siren status. As of this time only 12 sirens remain out of service and this is below the 16 siren reportability requirement. Breakdown of siren outages is as follows: Rockland County - 2 sirens with power issues only, and Westchester county - 10 sirens out of service of which 6 are due to power and 4 due to communications issues." The licensee will be notifying the NRC Resident Inspector, New York State Public Service Commission, and Rockland, Westchester, Putnam and Orange counties. R1DO (Perry) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-05-16
43366 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-03-19 02:20 | 2007-05-16 14:30 | 2007-05-16 | INVALID SPECIFIED SYSTEM ACTUATIONS DURING TESTING "This 60-day ENS report is being made per 10CFR 50.73(a)(2)(iv)(A) and 10CFR 50.73(a)(1) to report invalid automatic actuations of systems listed in paragraph (a)(2)(iv)(B), namely core spray (CS) and residual heat removal (RHR). "Unit 2 commenced refueling outage activities on Saturday March 10, 2007. Relay replacements for the 4 kv safeguard bus LOCA auxiliary control time delay relays were planned for all four buses due to a relay failure on Unit 1 that was identified during the prior refueling outage testing. "On Monday March 19, 2007, at 02:20 hours, during emergency diesel generator (EDG) surveillance testing a Unit 2 Division 3 LOCA signal was inadvertently initiated during the planned replacement of the D23 bus LOCA auxiliary control relay (162-117). The relay was being replaced at a pre-determined step in the test. The relay was in an energized state when removed. When the new relay was installed an unplanned actuation of LOCA load shedding and sequential loading occurred. The relay was subsequently replaced and tested successfully. "D23 EDG had been secured just prior to the event. The following loads were tripped and automatically restored: 2C CS pump and D234 load center breaker. The C emergency service water (ESW) pump tripped and did not restart since the EDG was not running. The 2C RHR pump continued to run. The 2A CS loop received a partial actuation in that the Division 3 signal was initiated but the Division 1 signal was not initiated. The 2C CS pump was operating in full flow test mode; therefore, it tripped and re-started as designed and 2A CS pump did not start which was expected. The 2A CS loop automatic valve alignment is initiated by the Division 1 signal; therefore, no automatic 2A CS loop valve alignment occurred. "On Wednesday March 21, 2007 at 14:08 hours during EDG surveillance testing a Unit 2 Division 2 LOCA signal was initiated during the test which started the D22 EDG and tripped the D224 load center breaker as expected. However, the load center breaker did not re-close which was not expected and other expected actions did not occur. At 14:41 hours, 33 minutes later, the remaining LOCA actions occurred when 2B RHR pump, 2B CS pump, and 2B reactor enclosure recirculation system (RERS) fan automatically started, and D224 load center breaker automatically closed due to a late actuation of the D22 bus LOCA auxiliary control relay (162-116). At 15:48 an additional unexpected relay actuation caused the 2B CS pump and D224 load center breaker to trip. The relay had been replaced earlier in the day and the ongoing testing was intended to satisfy the post maintenance test (PMT). However, the relay did not actuate at the point in the test designated as the PMT; the relay actuated unexpectedly 33 minutes later. "The cause of the first event was a less than adequate technical review of a test revision that added a step to replace the bus LOCA auxiliary control relay. The affected tests have been revised to replace the relay at a point in the test when it is de-energized. The cause of the second event was an equipment failure due to an intermittent connection between the relay pin connector and the relay base. The affected relay and base have been replaced and tested successfully. "All of the systems that received start signals functioned successfully. The only equipment malfunction was associated with the degraded relay. The RHR and CS starts were partial actuations. The D22 EDG train start was an expected actuation. The C ESW train was tripped but was not automatically started. "This event is reportable per 10CFR50.73(a)(2)(iv)(A) since 2B RHR pump, 2B CS pump, and 2C CS pump automatically actuated on an invalid signal. "Component data: Equipment name: D22 Bus LOCA Aux Control Time Delay Relay Equipment number: 162-116 Manufacturer: A348 Amerace Corp Model number: ETR14D3A002 Serial number: 83330224" The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-05-16
43365 | -1 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-05-16 00:50 | 2007-05-16 04:10 | 2007-05-16 | POTENTIAL SABOTAGE TO UNIT 1 COMPONENT The site noticed an act of potential sabotage to a Unit 1 component out of service for maintenance. The Unit is currently shut down. Compensatory actions were taken. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. * * * RETRACTION FORWARDED BY JOHN HUBBLE TO JOE O'HARA AT 1218 ON 5/16/07 * * * Upon further investigation, the licensee has retracted this event. Contact the HOO for additional details. The licensee will notify the NRC Resident Inspector. Notified R4DO (Bywater), R4IAT (Howell), ILTAB (Danis), IRD (Leach), NRR EO (Ross-Lee) and 73.71 Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-05-16
43364 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2007-05-15 11:16 | 2007-05-15 14:46 | 2007-05-15 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP DUE TO DIFFERENTIAL GENERATOR PROTECTION "At 11:16 am Eastern Daylight Time, a reactor trip occurred at the H. B. Robinson Steam Electric Plant, Unit No. 2. The unit was at approximately 82% reactor power and power level was being increased after restart from a refueling outage that had ended on May 13, 2007. The reactor protection system actuation was identified as a turbine trip signal that caused the reactor trip. The turbine trip signal appears to have been caused by the generator differential protection circuitry. The reactor is currently stable in MODE 3. All control rods indicated fully inserted following the reactor trip. The Auxiliary Feedwater (AFW) System actuated as expected in response to plant conditions, except the 'A' motor-driven AFW pump did not start. The plant operators manually started the 'A' motor-driven AFW pump. The cause of the 'A' AFW pump failure and the cause of the reactor trip are being investigated. The primary system and steam generator power operated relief valves and safety valves did not actuate during this event. "The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable at this time. Decay heat is currently being removed by use of the normal feedwater system and the condenser steam dumps. The 'B' Main Feedwater Pump also tripped during this event. The 'A' Main Feedwater Pump continued to operate and is being used to supply main feedwater to the steam generators." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-05-15
43363 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-05-15 00:58 | 2007-05-15 01:53 | 2007-05-17 | REACTOR SCRAM DURING TESTING "An automatic reactor scram occurred due to lowering reactor water level. Digital feedwater tuning activities were in progress at the time of the scram. All systems functioned as designed. The reactor water level has been restored to normal level band. The plant is stable in Hot Shutdown. There were no ECCS injections." At the time of the scram, the feedwater pump was in manual control for feedwater tuning. When water level started going down quickly, the operator was not able to restore sufficient feedwater flow before the level 3 (water level low) actuation. All control rods fully inserted on the scram. No valves repositioned and no safety or relief valves lifted after the scram. Reactor water level is being maintained with the motor feed pump and decay heat is being removed to the main condenser. The plant is in the normal shutdown electrical lineup. Reactor pressure is 509 psi and stable. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM FREDERICK SMITH TO FANGIE JONES ON 05/17/07 AT 1301 * * * "This call is to clarify information provided in notification Event Number 43363 made by the Perry Nuclear Power Plant on May 15, 2007. The second paragraph, fourth sentence of the notification states: 'No valves repositioned and no safety or relief valves lifted after the scram.' The intent of the portion of the sentence 'No valves repositioned' was supposed to be in reference to the reporting requirement in 10 CFR 50.72(b)(3)(iv) to report any event or condition that results in valid actuation of general containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs). "The event on May 15, 2007, did not meet the 'containment isolation valves in more than one system / MSIVs criterion', however, subsequent review of the event identified that Residual Heat Removal 'B' Heat Exchanger Second Vent to Suppression Pool Containment Isolation Valve 1E12-F073B, closed, as designed, in response to the reactor coolant level 3 (water level low) condition that was present during the event. No additional reporting criteria have been identified and this update has been provided to clarify the earlier statement. "The NRC Resident Inspector has been notified." Notified R3 RDO, (Ring), and NRR EO, (Ross Lee). | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-05-15
43362 | -1 | SENTARA CAREPLEX HOSPITAL |  |  |  |  | 2007-04-17 12:00 | 2007-05-14 08:48 | 2007-05-18 | PATIENTS THYROID CONTAINING 200 MICROCURIES OF IODINE-131 INADVERTENTLY SHIPPED FROM HOSPITAL On March 30, 2007 a patient was given 5 millicuries of Iodine-131 to his thyroid. On April 2, 2007 the patients thyroid was removed and processed by the Lab. The thyroid was kept by the Sentara CarePlex Hospital located in Hampton, VA for 2 weeks in case there were pathology questions. On either April 16 or 17, 2007 the thyroid was sent to Stericycle Autoclave Facility located in Baltimore, MD. Stericycle Autoclave Facility, received the thyroid on April 17, 2007 and discovered that the thyroid was still radioactive. Sentara CarePlex was informed of this and they contacted one of their contractor RSOs. The RSO picked up the thyroid and has stored it for future disposition. The thyroid was calculated to have 200 microcuries of Iodine-131 as of April 17, 2007. * * * RETRACTION FROM SANDY WOLFF TO JOE O'HARA AT 1601 ON 5/18/07 * * * Sandy Wolff, a Radiation Safety Officer for Sentara, spoke to Sandy Gabriel, NRC Region I and was told that this is not a reportable event. Since the administration of the radionuclide was not intended to remove the patients thyroid gland, Ms. Wolff was told that the licensee is not expected to keep track of the removed organ. Notified R1DO (Perry) and Cynthia Flannery (FSME). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-05-14
43361 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2007-05-13 15:20 | 2007-05-13 18:26 | 2007-05-13 | TRANSPORT OF POTENTIALLY CONTAMINATED PERSON TO OFFSITE MEDICAL FACILITY At 1451 EDT, a contractor employee working in the turbine building in a potentially contaminated area, reported having chest pains and difficulty breathing. At 1520 EDT, the individual was transported to Oconee Memorial Hospital, Seneca, SC. Radiation Protection had not yet determined if individual was contaminated. Enroute to the hospital, Radiation Protection determined individual was not contaminated. This determination was made prior to arrival to the hospital. After treatment at the hospital, the individual was released. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2007-05-13
43360 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-05-12 10:25 | 2007-05-12 18:09 | 2007-05-12 | EMERGENCY DIESEL GENERATORS START DUE TO LOSS OF OFF SITE START UP POWER "On May 12, 2007, at 10:25 am PST, offsite startup power was lost to Diablo Canyon Units 1 and 2. This is the 8-hour non-emergency event notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) for a valid actuation of five emergency diesel generators (EDGs) due to the loss of startup power. "Unit 1 is in a refueling outage in No Mode, with all fuel offloaded to the spent fuel pool (SFP). Auxiliary power is cleared for maintenance and offsite power was being provided by startup power. EDG 1-3 was also cleared for maintenance. On the loss of startup power, EDGs 1-1 and 1-2 auto-started and powered their loads. Since SFP cooling is not automatically loaded on the EDGs, Operators re-started a SFP Cooling pump. This re-established decay heat removal via component cooling water (CCW) (two of three pumps remained operable) and auxiliary saltwater pump 1-2. SFP temperature remained at approximately 105 degrees F. "Unit 2 remained in Mode 1 at 100 percent power with auxiliary power supplying Unit 2 equipment. The loss of startup power caused all three EDGs to auto-start but they did not load. "At approximately 11:30am PDT, startup power was restored to the site via the Mesa substation. Operators completed restoration of startup power to plant equipment by approximately 14:30 PDT. "The cause of the loss of startup power was reported as a failed Morro Bay - Diablo transmission line." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-05-12
43359 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2007-05-11 16:00 | 2007-05-12 12:07 | 2007-05-12 | BULLETIN 91-01 LOSS OF DOUBLE CONTINGENCY "During the quarterly shutdown and clean-out of a rotary press used for pressing UO2-Gd203 powder in FMO, it was observed that approximately half of the schedule 80, one-inch diameter Chlorinated Poly Vinyl Chloride (CPVC) tubes placed in the lower shaft casing of the press did not extend the full length of the cavity as required by the nuclear safety analysis. These tubes are credited as a fixed neutron poison inside the casing and must extend the entire length of the cavity in order for the unit to be demonstrated safe geometry for [LEU] enriched UO2 under optimal moderation conditions. The independent control on mass remained intact, thus no unsafe condition existed. The as-found condition was analyzed and demonstrated to be safe. "The unit was in a shutdown condition and contained no Uranium at the time of the discovery. "While this did not result in an unsafe condition, this event is being reported pursuant to NRC Bulletin 91-01 within 24 hours of discovery. "NUMBER AND TYPES OF CONTROLS NECESSARY UNDER NORMAL OPERATING CONDITIONS The basis of criticality safety relies on geometry and mass as independent criticality safety controls. "NUMBER AND TYPES OF CONTROLS WHICH FUNCTIONED PROPERLY UNDER UPSET CONDITIONS Mass control remained intact, thus no unsafe condition existed. "NUMBER AND TYPES OF CONTROLS NECESSARY TO RESTORE A SAFE SITUATION Control on geometry demonstrated by current analysis. No uranium present at time of discovery. "SAFETY SIGNIFICANCE OF EVENTS Low Safety Significance - independent control on mass remained intact - additional failure modes required before a criticality accident could occur. The as-found condition was analyzed and demonstrated to be safe. "SAFETY EQUIPMENT STATUS Unit was shutdown for maintenance and will remain Shutdown until CPVC tube error corrected. "STATUS OF CORRECTIVE ACTIONS Unit will remain shutdown pending final investigation results and implementation of additional preventive actions." The licensee will be notifying the North Carolina Radiation Protection Agency and the New Hanover County Emergency Management Agency. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2007-05-12
43358 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2007-03-15 01:02 | 2007-05-11 18:36 | 2007-05-12 | INVALID ECCS AND SYSTEM ACTUATIONS "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1), to report an invalid actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). "On March 15, 2007, with Unit 2 in a refueling outage, the reactor vessel was filled to a solid condition and being depressurized following the completion of the vessel hydrostatic test. At 0102 CDST, with pressure indicating approximately 43 psig, the 2B Residual Heat Removal (RHR) pump was started in the shutdown cooling mode. With the vessel solid, the resultant pressure transient caused invalid reactor vessel low-level trip signals and Division 2 and 3 ECCS actuations. "The 2C RHR pump auto-started and injected into the vessel. The 2A Diesel Generator (DG) started, and 2B RHR Injection valve (2E12-F042B) auto-opened. The Division 3 ECCS actuation did not result in any equipment starts because the High Pressure Core Spray pump and the 2B DG were properly removed from service at the time of the event. The operators verified that the reactor vessel low-level trips and ECCS actuations were invalid, and shut down the 2C RHR pump and the 2A DG. The 2B RHR Injection Valve was also closed. "The cause was determined to be a knowledge deficiency compounded by less than adequate procedural guidance regarding starting shutdown cooling while the reactor vessel is in a solid condition. Corrective actions included reviewing the event with licensed operators, revising the appropriate operating procedures, and developing just-in-time training for future use. "The event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an invalid ECCS actuation and invalid system actuation." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-05-11
43357 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2007-05-11 14:05 | 2007-05-11 15:00 | 2007-05-11 | SAFEGUARDS REPORT Attempted introduction of contraband material into the Protected Area (PA). Immediate compensatory measures taken upon discovery. Contact the Headquarters Operations Officer for additional details. The licensee informed local authorities and will inform the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-05-11
43356 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2007-04-27 | 2007-05-11 10:55 | 2007-05-14 | AGREEMENT STATE REPORT MEDICAL EVENT - PATIENT UNDERDOSE A patient was to receive 150 mCi of I-131 for thyroid cancer on April 27, 2007. The dose was two capsules in a single vial (tube). The intended dose activity was reported to be correct. The patient was presented with the vial containing the dosage. The patient took the dosage. The vial and lead container were placed in storage. On May 9, 2007 a nuclear medical technician discovered a capsule in the vial. The patient had received one-half of the intended dose. The technician reported the discovery to the RSO who reported the incident to the Oklahoma Radiation Management Section supervisor (May 9, 2007 at 5:26 p.m.) by e-mail. Radiation Management Section investigators interviewed St. Anthony Hospital nuclear medicine technicians on May 10, 2007. The patient will be notified. The RSO will submit a written report within 15 days of the initial report. The unused capsule will decay-in-storage. State of Oklahoma Medical Event reportable under 10CFR35.3045(a)(1)(i) Event Cause Failure to verify that the entire dose was administered A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE BY E-MAIL AT 07:01 ON 5/14/2007 FROM C. FLANNERY TO M. ABRAMOVITZ * * * "This event has been reviewed and determined to be a reportable medical event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-05-15
43355 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2007-05-10 15:30 | 2007-05-10 20:16 | 2007-05-10 | OFFSITE NOTIFICATION DUE TO ELEVATED TRITIUM LEVELS "On May 7, 2007, a horizontal concrete wall crack at approximately 990 ft 6 inch elevation in a radiologically controlled room located inside the protected area, was observed to have water drops forming on the surface. Samples were collected in enough quantity to perform radiological and chemical analysis. The analysis indicated tritium concentration of 110,000 pCi/L. The limits for tritium in the FCS Off-Site Dose Calculation Manual is 20,000 pCi/L. Based on this analysis a conservative decision to notify the state and local agencies was made on 5/10/2007 at 15:30 CDT per the NEI Ground Water Protection Program. These off-site notifications will be made on 5/11/2007. Further investigation is on-going." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-05-10
43354 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-03-12 20:27 | 2007-05-10 15:22 | 2007-05-10 | INVALID TUBINE DRIVEN AUXILIARY FEEDWATER PUMP STARTS "This report describes three invalid actuations of the Unit 2 Turbine Driven Auxiliary Feedwater (TDAFW) pump that occurred on March 12,2007. This report is being made in accordance with 10CFR50.73(a)(1), which states, in part, 'In the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' "On March 12, 2007 at 2027, while performing operator rounds, Operations personnel heard a venting noise coming from the vicinity of the Main Steam Line 2-04 to Auxiliary Feedwater Pump Turbine Steam Supply Valve. One of the Operators put his hand close to the exhaust pilot valve, restricting the venting air flow, which increased the sensing pressure on one of the valve's ports. The valve swapped, exhausting the diaphragm. This caused the TDAFW steam supply valve to fail open and the TDAFW pump started and reached full flow. Operations responded to the event by manually running back the Main Turbine load to 1100 Mew to ensure Reactor Power remained less than 100%. The TDAFW pump was secured and the steam supply valve hand switch was placed in AUTO. "At 2056, an I&C technician was leak checking the valve actuator and tubing joints. The I&C technician got within close proximity of the Main Steam Line 2-04 to Auxiliary Feedwater Pump Turbine Steam Supply Valve and restricted the venting air flow, which increased the sensing pressure on one of the exhaust pilot valve's ports. The pilot valve swapped, exhausting the diaphragm. The TDAFW Steam Supply Valve failed open again and the TDAFW pump started a second time and reached full flow. "At 2100, Shift Operations placed the steam supply valve in pullout and declared the TDAFW inoperable. To prevent further inadvertent starts, Operations decided to close the upstream isolation valve. While in the process of closing the isolation valve, the Operator heard air venting from the vicinity of the Main Steam Line 2-04 to Auxiliary Feedwater Pump Turbine Steam Supply Valve. The Operator put his hand under the exhaust pilot valve such that the air flow was restricted, which increased the sensing pressure on one of the valve's ports. The pilot valve swapped, exhausting the diaphragm. The TDAFW steam supply valve failed open again and the TDAFW pump started a third time. Since the upstream isolation valve was partially closed, the TDAFW pump only reached a partial flow of 235 gpm. Shift Operations initiated a clearance to prevent further inadvertent TDAFW pump starts and a work order was initiated to determine the failure mechanism. On March 13, 2007 at 2223, Shift Operations declared the TDAFW pump operable. "The specific train and system that actuated was the third AFW train on Unit 2. During each of the three TDAFW pump starts, the system started and functioned correctly. During the first two pump starts, the train actuation was complete. As described above, on the third start the train actuation was partial due to less than full flow being developed. "The second and third TDAFW pump starts took place during trouble shooting and clearance isolation activities, respectively, which occurred prior to the cause being identified. The three AFW invalid actuations occurred due to incorrect setup of the exhaust pilot valve for the Main Steam Line 2-04 to Auxiliary Feedwater Pump Turbine Steam Supply Valve. "The NRC Resident Inspector will be notified of this report." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-05-10
43353 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-05-09 16:23 | 2007-05-09 19:33 | 2007-05-17 | UNANALYZED CONDITION DUE TO IDENTIFIED NON COMPLIANT FIRE PROTECTION MANUAL OPERATOR ACTIONS "During performance of NFPA-805 Transition Project Task SUP-1, 'Manual Action Compliance,' it was determined there were 11 non-compliant manual operator actions that were being performed to achieve and maintain hot safe shutdown in Fire Area A06 (1B32 area). These manual actions were being performed in an Appendix R Section III.G.1/G.2 fire area, however, they do not meet the criteria for allowable manual actions specified in RIS 2006-10, 'Regulatory Expectations with Appendix R Paragraph III.G.2 Operator Manual Actions.' "The discovery of these non-compliant manual actions is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii). Appropriate compensatory measures have been established for Fire Area A06 via initiation of hourly fire rounds. An extent of condition review has been initiated that will encompass the remainder of the safe shutdown areas in both Point Beach Nuclear Plant (PBNP) units. The results of the extent of condition will be documented in the site's corrective action program with compensatory measures being established as appropriate. The 60-day licensee event report, submitted to the Commission in accordance with 10 CFR 50.73(a)(2)ii), will provide the results of the manual action compliance review and follow-up corrective actions. "The PBNP Resident Inspector has been notified of this event." * * * UPDATE 1735 EDT ON 05/15/07 FROM ERIC SCHULTZ TO S. SANDIN * * * "This is an update to EN 43353 submitted at 19:33 EDT on 05/09/07: "During performance of NFPA-805 Transition Project Task SUP-1, 'Manual Action Compliance,' it was determined that non-compliant manual operator actions are credited to achieve and maintain hot safe shutdown for a fire. The following actions were identified during the extent of condition reviews conducted subsequent to EN 43353 report. # Non-Compliant Actions 1 - Fire Area A03, 1P-2C CVCS Charging Pump Cubicle 1 - Fire Area A04, 1P-2B CVCS Charging Pump Cubicle 1 - Fire Area A05, 1P-2A CVCS Charging Pump Cubicle 6 - Fire Area A07, Chemical Drain, Laundry Tank and Reactor Coolant Pump Seal Filter Room 5 - Fire Area A08, HVAC Equipment Room & Pipeway No. 1 Valve Gallery Area "These manual actions are credited for safe shutdown in an Appendix R Section III.G.1/G.2 fire area, however, they do not meet the criteria for allowable manual actions specified in RIS 2006-10, 'Regulatory Expectations with Appendix R Paragraph III.G.2 Operator Manual Actions.' "The discovery of these non-compliant manual actions is being reported as an unanalyzed condition as defined by 10 CFR 50.72(b)(3)(ii). Appropriate compensatory measures have been established for Fire Areas A03, A04, A05, A07 and A08 via initiation of hourly fire rounds. An extent of condition review is continuing that will encompass the remainder of the safe shutdown areas in both Point Beach Nuclear Plant (PBNP) units. "The PBNP Resident Inspector has been notified of this event." Notified R3DO (Mark Ring). * * UPDATE BY HALL TO KOZAL ON 5/16/07 AT 1737 * * * "This is an update to EN 43353 submitted at 19:33 EDT on 05/09/07: "During performance of NFPA-805 Transition Project Task SUP-I, 'Manual Action Compliance,' it was determined that the following non-compliant manual operator actions are credited to achieve and maintain not safe shutdown for a fire. These actions were identified during the extent of condition reviews for the above referenced report [The following non-compliant actions were identified:] "5 [actions for] Fire Area A01, Primary Auxiliary Building El. 44'& 66' (Except FX237) 5 [actions for] Fire Area A01-G, Unit 1 Façade 5 [actions for] Fire Area A01-H, Unit 2 Façade 3 [actions for] Fire Area A10, Radioactive Gas Treatment Area 3 [actions for] Fire Area A11, Pipeway No. 4 Valve Gallery 1 [actions for] Fire Area Al 2, 2P2C CVCS Charging Pump Room 1 [actions for] Fire Area A13, 2P2B CVCS Charging Pump Room 1 [actions for] Fire Area A14, 2P2A CVCS Charging Pump Room 12 [actions for] Fire Area A15, 2B32 Motor Control Center Area 21 [actions for] Fire Area A23N, North Side of Auxiliary Feedwater Pump Room 19 (actions for] Fire Area A23S, South Side of Auxiliary Feedwater Pump Room 8 [actions for] Fire Area A25, D06 Battery Room 9 [actions for] Fire Area A26, D05 Battery Room 7 [actions for] Fire Area A27, G01, Diesel Generator Room 7 [actions for] Fire Area A28, G02 Diesel Generator Room 1 [actions for] Fire Area A29, Air Compressor Room 1 [actions for] Fire Area A61, P206A & P207A Fuel Oil Pump Room 7 [actions for] Fire Area A71, Diesel Generator Building, Train B Areas" The licensee notified the NRC Resident Inspector. Notified R3DO (Ring). * * * UPDATE BY RODE TO MCLEAN/KOZAL ON 5/17/07 AT 1815 * * * "During performance of NFPA-805 Transition Project Task SUP-1, 'Manual Action Compliance,' it was determined that the following non-compliant manual operator actions are credited to achieve and maintain hot safe shutdown for a fire. These actions were identified during the extent of condition reviews for the above referenced report. [The following non-compliant actions were identified:] 28 Fire Area A01- A, Primary Auxiliary Building, EL. 8' & Below 18 Fire Area A02, Containment Spray / Safety Injection Pump Room 11 Fire Area A01-CN, Primary Auxiliary Building, EL 26' South Wing 10 Fire Area A01-CS, Primary Auxiliary Building, EL 26' South Wing 9 Fire Area A16, D106 Battery Room 9 Fire Area A17, D04 Electrical Equipment Room 9 Fire Area A18, DO3 Electrical Equipment Room 8 Fire Area A19, D105 Battery Room 16 Fire Area A01-E,Turbine Building & South Service Building 1 Fire Area A01-F, Yard Area 1 Fire Area A54, D305 Swing Battery & D301 Charger Rooms 5 Fire Area A36, Unit 1 Containment Area 5 Fire Area A46, Unit 2 Containment Area 7 Fire Area A68, Train B East Duct Bank & Manholes 2 Fire Area A70, Train A West Duct Bank & Manholes" The licensee notified the NRC Resident Inspector. Notified R3DO (Ring) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-05-09
43352 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-05-04 | 2007-05-08 15:40 | 2007-05-16 | AGREEMENT STATE REPORT - LOUISIANA - WORKER OVEREXPOSURE The State provided the following information via facsimile: "[A licensee representative] with Nondestructive and Visual inspection notified the Louisiana Department of Environmental Quality on May 4, 2007 of an overexposure. The indicated exposure from the badge reading is 5123 mrem. Additional information will be forwarded once it is received." Louisiana Event Report ID No.: LA070011 * * * UPDATE FROM LOUISIANA (VIA E-MAIL) TO HUFFMAN AT 11:39 EDT ON 5/16/07 * * * Upon further investigation, it has been determined that there were two separate incidents where employees of Nondestructive & Visual Inspections, LLC may have exceeded the annual dose limit of 5 rem. The first incident was the original basis for the above initial notification. "The worker involved] is an industrial radiographer, certified by the State of Louisiana. [The worker] . . .was employed by NVI, LLC from April 30, 2005 until March 29, 2007, at which time he was terminated for violating company policies. [The worker] did not turn in his March 2007 TLD badge. "In February 2007, [the worker's] lifetime dose equivalent, while employed at NVI, LLC was 5117 millirems. His year to date dose equivalent for 2007 at this time was 132 millirems. His year to date dose equivalent for 2006 was 2535 millirems. This dose includes a calculated dose for the month of December 2006 for a badge that according to [the worker] was lost. On May 1, 2007, NVI, LLC received an exposure notification from Landauer for [the worker's] December 2006 TLD badge of 3156 millirems. This put his year to date dose equivalent for 2006 at 5691 millirems, which exceeds the annual dose limit for radiographers. The lost badge was apparently found and returned to Landauer by mistake. There is no way to determine what dose the badge had been exposed to during the four months that it was unaccounted for. "[NVI, LLC] has tried on numerous occasions to reach [the worker] by phone to discuss this matter with him. [NVI, LLC] has been unsuccessful in attempts [to reach him] so far. "The second incident involves another [worker]. [The worker] is an industrial radiographer trainee, certified by the State of Louisiana.. . . .[The worker] has been employed by NVI, LLC, since April 1, 2005. "On May 4, 2007, [NVI, LLC ] received an exposure notification from Landauer. [The worker's] dose for the month of March 2007 was 5363 millirems. His year to date dose equivalent for 2007 is 5514 millirems. [NVI, LLC] notified [the worker] immediately and informed him that he could not perform radiography. [NVI, LLC] met with [the worker] the same day and discussed the overexposure. [The worker] stated that there was no way possible that he could have receive such a dose. He stated that at no time did he ever go offscale or have any type of incident or accident while performing his duties during the month of March 2007. . . .[The worker] is still employed by NVI, LLC and has been reassigned to perform other NDT methods that do not include radiography." R4DO (Bywater) and FSME (Morell) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-05-11
43351 | 0 | PALISADES | 1 |  |  | [1] CE | 2007-05-08 13:22 | 2007-05-08 15:23 | 2007-05-08 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "On May 8, 2007 at 1322 hours, the reactor automatically tripped from approximately 100% power due to low level in the 'B' Steam Generator. The low level condition resulted from spurious closure of the 'B' feedwater regulating valve. The feedwater regulating valve closure appears related to an instrument and control troubleshooting work activity that was in progress at the time of the event. Investigation into the cause is continuing. "In additions an automatic actuation of the auxiliary feedwater system occurred, as designed, to restore steam generator levels. All systems functioned as designed. Decay heat is being removed via steaming through the turbine bypass valve to the main condenser." All control rods fully inserted. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-05-08
43350 | -1 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-05-08 09:59 | 2007-05-08 10:09 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * ALERT DECLARED DUE TO A FIRE IN THE SUPER COMPACTOR FACILITY WITH A POSSIBLE RADIOACTIVE RELEASE BWXT declared an alert condition onsite at 0959 EDT due to a fire at their super compactor facility where dry active waste is compacted with a possible uncontrolled release. The fire was extinguished in about 20 minutes. BWXT initially requested offsite fire assistance but called it off after extinguishing the fire. The licensee notified state and local authorities and the NRC Resident Inspector. * * * UPDATE AT 11:30 ON 5/8/07 TO SNYDER * * * BWXT terminated the alert condition at 1130 EDT. The licensee notified state and local authorities and the NRC Resident Inspector. * * * RETRACTION PROVIDED BY LEAH MORRELL TO JEFF ROTTON AT 0836 ON 06/01/07 * * * "On Tuesday, May 8, 2007 at 0957, BWX Technologies, Inc. declared an Alert per the BWXT Emergency Plan and internal emergency procedures. BWXT contacted the NRC Operations Center to report that an Alert had been declared due to a radioactive waste drum fire that occurred in the supercompactor building and the fact that there was a possibility that 'restricted area airborne concentrations may have been in excess of 10 CFR 20 Appendix B, Table 1' as defined in the BWXT Emergency Plan and internal emergency procedures. Analysis of samples taken during the emergency indicated no detectable activity. Surveys of the potentially impacted areas and personnel responding to the event found no unusual elevations. Also, data for the routine fixed air sampling and stack programs did not show any elevated samples indicative of an increase in contamination in the area or a release of materials during the event. Therefore, the Alert criteria of airborne concentrations in excess of 10 CFR 20 Appendix B, Table 1 were not met. BWXT is requesting that the Alert declaration that was made on May 8, 2007 be retracted. The BWXT NRC Resident [Inspector] has been notified of the retraction. "State and Local Agencies Notified: Campbell County Emergency Services, Amherst County Emergency Operations Center, Commonwealth of Virginia (Department of Emergency Services)" Notified R2DO ( Widmann), and FSME EO (Flannery). * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | VA | FUE |  | 70.32(i) |  |  |  | 0 | 2008-05-11
43349 | 0 | VALLEY QUARRIES, INC |  |  |  |  | 2007-05-06 22:00 | 2007-05-07 10:55 | 2007-05-07 | STOLEN TROXLER GAUGE On the morning of 5/7/07 the licensee noticed that a Troxler Moisture Density Gauge (Model 3430) was missing. The gauge was in the company truck the evening of 5/6/07. An employee of the company took the company truck home (Fayetteville, PA 17222) and sometime during the evening (after 22:00) a company cell phone and the gauge was taken from the truck. The sources in the Troxler gauge are Am-241/Be (40 mCi), and Cs-137 (8 mCi). The licensee filed a report with the PA State Police, (Incident # H03-1661925). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-05-07
43348 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-05-06 20:31 | 2007-05-06 21:23 | 2007-06-26 | UNAUTHORIZED ACCESS TO THE PROTECTED AREA. IMMEDIATE COMPENSATORY ACTION TAKEN UPON DISCOVERY. The NRC Resident Inspector will be notified of this event by the licensee. Call the Headquarters Operation Officer for further details. * * * RETRACTION PROVIDED BY BILL MASON TO JEFF ROTTON AT 1547 EDT ON 06/26/07 * * * Investigation revealed that the individual granted access should not have been characterized as unauthorized. Licensee therefore retracts EN #43348. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO (Ayres). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Hot Shutdown | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-05-06
43347 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2007-05-05 12:10 | 2007-05-05 15:00 | 2007-05-05 | OFFSITE NOTIFICATION MADE TO THE STATE OF NEBRASKA DUE TO A SMALL OIL SPILL Nebraska Department of Environmental Quality was notified of an oil spill while backwashing a screen in the intake structure. Approximately 2 gallons of oil was spilled. Most of the oil spill was contained and wiped up using oil drip pads. There was no evidence that oil had been released into the Missouri River. The NRC Resident Inspector was notified of this offsite notification by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-05-05
43346 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-05-04 23:05 | 2007-05-05 02:13 | 2007-05-05 | MANUAL REACTOR SCRAM ON LOSS OF FEEDWATER The condensate prefilters isolated earlier in the day and the bypass valve automatically opened. The computer controlling these valves was in the process of being replaced when the bypass valve shut. "Unit experienced a loss of feedwater due to condensate pre-filter valves going closed. The reactor was manually scrammed and HPCI was used to restore reactor water level. MSIVs closed and the U2 and U2/3 EDGs auto started on low level." All rods fully inserted on the manual scram. Minimum level was approximately -54 inches. Decay heat is being removed using the isolation condenser and level is being maintained with Control Rod Drive leak by. No safety or relief valves lifted during this event. The plant is in the normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2007-05-05
43345 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-05-04 12:56 | 2007-05-04 16:01 | 2007-05-04 | MANUAL REACTOR SCRAM DUE TO LOSS OF COOLING TO NUMBER 2 MAIN TRANSFORMER "At approximately 1256 CDT on May 4, 2007, a manual reactor scram was initiated following the loss of cooling to the no. 2 main transformer. Reactor power at the time of the scram was approximately 70 percent (initially 100% power). Following the scram, reactor water level briefly decreased below Level 3, resulting in the automatic closure of containment isolation valves in the suppression pool cooling system. This isolation was confirmed to have occurred as designed. Reactor pressure and water level control were promptly established. All control rods inserted, and no emergency injection system operation was required. "This event is being reported in accordance with 10CFR50.72(b)(2)(iv)(B) as a condition resulting in a manual actuation of the reactor protection system." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-05-04
43344 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2007-04-04 16:47 | 2007-05-04 14:21 | 2007-05-04 | 30-DAY REPORT INVOLVING A LOSS OF ACCOUNTABILITY OF LESS THAN 1 GRAM SNM "This is a non-emergency Event Notification made in accordance with 10 CFR 20.2201(a)(1)(ii) to inform the NRC of a loss of accountability of a very small amount (e.g., particle size) of special nuclear material (SNM). As part of preparations for an NRC inspection of Columbia's SNM Control and Accounting Program (April 16-19, 2007), documentation concerning the recovery of two pieces of a broken fuel rod was obtained. The documentation revealed existence of potential fuel particles estimated to be less than 1 gram in aggregate located in the spent fuel pool. The location of these particles cannot be positively identified at this time and is therefore being reported as missing SNM under 10 CFR 20.2201(a)(1)(ii). "The particles were created during a 1990 refueling outage while inspecting a leaking fuel bundle. To identify the leaking rod, the bundle was disassembled and rod-by-rod electronic sorting performed. Ultrasonic examination identified the leaking rod; however, during the inspection the rod bent and snapped while being guided through a fuel inspection funnel. A procedure was approved and successfully executed to recover the broken rod sections. Following the recovery, an inspection was performed with an underwater camera to determine if any fuel pellets had been released as part of the evolution. No fuel pellets were identified; however, a small dark particle of material surrounded by smaller black particles was observed in a stainless steel bucket which had been positioned under the broken fuel rod pieces. It is believed that the bucket containing the particles was suspended off the west wall of the spent fuel pool, north of the work table. The location of the particles within the bucket cannot be positively identified at this time. "The contents of the bucket have been described by the individuals involved in the broken rod recovery as a small particle of material roughly the size of a fingernail clipping surrounded by a few black particles the size of ground pepper. An underwater survey indicated a radiation level of greater than 400 R on contact for the material. The total amount is believed to be considerably less than 10 percent of a single pellet's worth of material, or less than 1 gram. "Energy Northwest is continuing to investigate this event. Based on the information gathered to date, the nature of the particles, and the existence of radiation monitoring, a high degree of confidence exist that the particles are located in the bottom of the spent fuel pool or in an otherwise radiologically controlled location such that the health and safety of the public would not be adversely affected. In addition, there is no evidence of theft or diversion. "This notification satisfies the 30-day notification requirement of 10 CFR 20.2201(a)(1)(ii). A subsequent written report will be made in accordance with 10 CFR 20.2201(b). "The NRC Resident and SNM Control and Accounting Inspectors have been informed of this issue." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-05-04
43343 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2007-05-04 08:53 | 2007-05-04 12:40 | 2007-05-04 | FITNESS-FOR-DUTY REPORT INVOLVING A NON-LICENSED SUPERVISOR A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2007-05-04
43342 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-05-04 06:00 | 2007-05-04 11:40 | 2007-05-04 | AGREEMENT STATE REPORT FROM TEXAS - STOLEN HUMBOLDT MOISTURE DENSITY GAUGE. The following information was provided via e-mail: "On Friday, May 4, 2007, around 10:20 a.m., the Agency received notification by Alliance Laboratories, Inc., that a 2002 metallic gray Dodge Ram 1500 pickup truck that was carrying a moisture/density gauge, Humboldt Scientific Inc, Model 5001, SN#4455, with two sources 11 mCi of Cs-137, SN 1654CM, and a 44 mCi Am-241, SN NJ04752, was stolen sometime between 0600-0800 hrs. from an apartment complex in Houston, Texas. Houston Police Department has been notified and the case number is 06-4781007B. The Agency also notified the [Headquarters] Operations Officer at the NRC, at 1040 hours, and the event number is 43342." Texas Incident Number: I-8409. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-05-09
43341 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-05-04 01:37 | 2007-05-04 03:36 | 2007-05-04 | 73.71 SAFEGUARDS REPORT Discovered vulnerability in a safeguards system that could have allowed access to a controlled area if the degradation had continued. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE AT 1642 EDT ON 5/4/07 FROM JEFF BAARTMAN TO S. SANDIN * * * After further review and an investigation, the licensee concluded that this event was not reportable. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. Notified R3DO (Lipa), ILTAB (Hahn), 73.71 Group (Email) and IRD (Cruz). | 50 | 100 | 0 | 50 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-05-04
43340 | 0 | MATTINGLY TESTING SERVICES |  |  |  |  | 2007-05-01 12:10 | 2007-05-02 11:18 | 2007-05-03 | RADIOGRAPHY CAMERA SOURCE TUBE DAMAGED Approximately 1210 on 05/01/07, the RSO was contacted by one of his radiographers at Cenex in Laurel, MT that he couldn't get the source back into the radiography camera. The area was roped off pending the arrival of the RSO to take corrective action. The camera is an INC Model IR100 with 76 curies of Ir-192. The licensee did not know the serial number. At 1245 the RSO arrived at the site and noticed a sharp angled cut on the source tube. The RSO shielded the source with lead and lead shot and replaced the source tube then retracted the source back into the camera. The RSO believes the damage to the source tube was caused by the radiographer. The RSO received 16 mrem exposure and the radiographer received 6 mrem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-05-03
43339 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-05-02 14:55 | 2007-05-03 08:27 | 2007-05-03 | POSSIBLE RADIATION EXPOSURE BEYOND OCCUPATIONAL LIMITS "Radiographer received possible over exposure at job site. Radiographer had film badge and pocket dosimeter, but did not survey prior to changing film in preparation for next exposure. Discovered source was exposed when he attempted to crank out source. Radiographer contacted RSO on 2 May 2007 at 1455 hours. RSO contacted this office on 3 May 2007 at 0800. State contacted NRC on 3 May 2007 at 0827 hours. Film badge sent for emergency processing, pocket dosimeter was off scale. The State will investigate this afternoon's incident." Source: 48.3 Ci Ir-192 Estimated dose received: 9 Rem Location of incident: Sanford, FL Time duration of incident: less than 2 minutes Areas of greatest exposure estimated to be the forearm and hand Incident Number: FL07-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-05-08
43338 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2007-05-03 01:46 | 2007-05-03 03:09 | 2007-05-03 | OFFSITE NOTIFICATION - RELEASE TO ENVIRONMENT "Notified New Jersey Department of Environmental Protection of a release of sodium hypochlorite to the environment. The amount of sodium hypochlorite released was small (11.5 lbs) and well below the Federal (100 lbs) and state reportability limits for quantity." Leak was from a hose on the chlorination system that supports the Service Water system. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-05-03
43337 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2007-01-16 | 2007-05-02 14:00 | 2007-11-02 | AGREEMENT STATE REPORT - DOSE TO PATIENT On March 9, 2007, a consultant for the Aroostook Medical Center (TAMC) notified the TAMC Nuclear Medicine Department a medical event may have taken place on January 16, 2007. The licensee investigated the report and found that a 4 millicurie dose of I-131 was given to a patient on the date in question as a whole body scan. However, the licensee determined that the ordering physician actually wanted an I-131 uptake and scan of 150 microCuries of I-131. Upon further investigation, the licensee determined that the scheduling person (who does not have a background in Nuclear Medicine) ordered the I-131 whole body scan. The licensee initiated a report of medical event and contacted the patient's physician. The licensee calculated the whole body effective dose equivalent and the dose to the thyroid from the excess dose of I-131. The dose to the patients thyroid gland was calculated to be approximately 14000 rem and the whole body effective dose equivalent was calculated to be approximately 6.4 rem. The licensee determined that if the proper amount of I-131 had been administered, the doses would have been 525 rem and 0.24 rem respectively. A doctor at the licensee's facility determined that the dose given to the patient on March 16, 2007 will not have any effects on the patient. "To prevent further events as this one, the Hospital and Radiation Safety Officer has decided that any further requests for I-131 procedures will be verified directly with the referring physician." There are now policies in effect to prevent this situation from happening again. The state of Maine entered this report into NMED as number ME070016. * * * UPDATE AT 07:07 ON 5/3/2007 FROM CINDY FLANNERY TO MARK ABRAMOVITZ * * * "This event (EN43337) has been reviewed and determined to be a reportable medical event." * * * UPDATE PROVIDED AT 1622 EDT ON 11/02/07 VIA FAX FROM STATE OF MAINE (SEELEY) TO JEFF ROTTON * * * "Nature and Probable Consequences: The licensee reported that a patient undergoing treatment for malignant melanoma and presenting an asymmetric thyroid, received a Tc-99m scan and ultrasound was subsequently scheduled for a whole body scan utilizing I-131 to further diagnose the problem. The scan was ordered and the CNMT questioned the whole body scan and asked the physicians office to clarify what they wanted: an uptake or a whole body scan. The oncologist's secretary confirmed a whole body scan. On January 16, 2007 the patient received 0.1458 MBq (3.94 mCi) of I-131. "On March 6, 2007 during a follow-up visit with an endocrinologist it was recognized that the wrong scan was performed. Upon investigation by the licensee and the licensee's consultant it was discovered that a medical event had indeed occurred. The administration (0.1458 MBq (3.94 mCi) vs the intended dosage of 5.55 MBq (150 microCuries)) of [I-131] resulted in a thyroid dose of 51.22 Gy (5,122 rad) and a whole body dose of 15.37 Sv (153.66 Rem) using NUREG-CR-6345 methodology. (if ICRP#30 or FGR #11 methodology used, results are 70 Gy (7000 Rad) for a thyroid dose and 21.25 Sv (212.5 Rem) dose to the whole body. "The patient and referring physician were notified of the error. No negative health effects from this administration are expected. On March 28, 2007, the licensee sent a letter to the State confirming that a medical event had occurred. "Cause(s): This medical event was caused by human error. The licensee failed to verify the prescribed dosage for a specific patient directly with the referring physician and a written directive was not filled out. "Actions Taken to Prevent Recurrence: "Licensee - Corrective actions taken by the licensee included revising procedures to improve communication with referring physicians to include the CNMT speaking directly with the referring physician or Authorized User to confirm test to be done. Also, written directives will be done for all administrations of I-131 in quantities greater than 30 microCuries. "State Agency - The State Radiation Control Program (RCP) performed an on site investigation on May 24, 2007 and requested corrective action by the licensee. The RCP issued a Notice of Violation on November 1, 2007 and awaits the licensee's response. The RCP did initially review and accept the licensee's proposed corrective actions during the on-site investigation. "This event is closed for the purpose of this report." Notified R1DO (Dentel) and FSME EO (Morell). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2007-05-05
43336 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-02-02 13:39 | 2007-05-02 09:39 | 2007-05-02 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The State provided the following information via facsimile: "Patient was scheduled for administration of 30 millicuries of 90Y [Yttrium-90] microspheres. The delivery catheter developed a leak during the administration. Leakage was mostly contained within the Plexiglas box containing the vial of microspheres. There was very minimal contamination outside of the box. "Licensee performed bremsstrahlung measurements of the patient and the Plexiglas box. Based on differences, the administered dose was determined to be only 66% of the prescribed dose. "Licensee noted that this was the first of a two part administration of the microspheres and the dose at the next treatment will be adjusted to compensate for the 'missing' activity. "The device manufacturer (Sirtex) traced the leaky units to one operator who had deviated from the normal assembly procedure. Sirtex destroyed the remainder of that lot number and replaced them with a new, tested lot." NC Event Report ID number: NC-07-02 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM C. FLANNERY TO P. SNYDER AT 1436 ON 5/02/07 * * * The NRC's medical events review committee has determined that this report is a medical event. Notified R1DO (Holody) and FSME (Morell) via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-05-05
43335 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2007-05-01 17:00 | 2007-05-01 17:51 | 2007-05-01 | OFFSITE NOTIFICATION OF A SPILL OF ACIDIC WATER The licensee made an offsite notification to the Maryland Department of the Environment based on the release of approximately 705 gallons of very acidic demineralized water (Ph of 1) to a storm drain. The drain is connected to a system that leads to the Chesapeake Bay. The acidic water is coming from a non-isolable leak from the 11 Waste Neutralizing Tank. The leakage is onto a gravel base below the tank which is about 5 feet from the storm drain. The leak rate is at a rate of about 1 GPM. The licensee has set up a system to divert some of the leakage from the storm drain and capture it in waste barrels but some of the water is still being spilled onto the ground. The long term remediation of this problem is to neutralize the tank with a caustic solution and then discharge the tank. The licensee has also notified Calvert County and the NRC Resident Inspector. * * * UPDATE FROM MORGAN TO HUFFMAN AT 1940 EDT ON 5/1/07 * * * The licensee also made a report of this spill to the National Response Center (EPA). R1DO (Holody) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-05-01
43334 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-05-01 10:00 | 2007-05-01 13:37 | 2007-05-01 | AGREEMENT STATE- MASSACHUSETTS - EXCESSIVE CONTACT RADIATION LEVEL ON SHIPPING PACKAGE The State provided the following information via facsimile: "Licensee received Type A package containing 100 millicuries of Na-22 from Los Alamos National Lab. External Radiation measurement of the package on contact was 360 mrem/hr. The TI on the package was listed as 7 (the licensee measured a TI of 8.5). "Package was shipped on April 30, 2007 and flown to Boston Logan Airport by Fed Ex, after which it was trucked by Fed Ex to the licensee site at 331 Treble Cove road in Billerica, MA. "The licensee has informed Fed Ex of the external radiation measurements." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-05-04
43333 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2007-03-03 08:14 | 2007-05-01 13:17 | 2007-05-01 | INVALID ECCS ACTUATION DURING REFUELING OUTAGE "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1), to report an invalid actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). "On March 3, 2007, Unit 2 was in a refueling outage. Reactor penetration nozzles were being flushed to remove crud deposits. At 0814 CST, Low Reactor Vessel Level 1, Level 2, and Level 3 alarms were received in the Main Control Room, and the Division 1 Emergency Core Cooling System (ECCS) initiated. The Low Pressure Core Spray (LPCS) pump started on the ECCS initiation signal and injected into the Unit 2 reactor vessel. In addition, the '0' Diesel Generator auto-started, and the Low Pressure Coolant Injection valve (2E12-F042A) auto-opened. "Operators verified that reactor vessel and reactor cavity water levels were normal, and then stopped the ECCS injection into the vessel by placing the LPCS pump control switch in pull-to-lock. ECCS is not required to be operable in Mode 5 with the spent fuel pool storage gates removed and water level greater than or equal to 22 feet above the Reactor Pressure Vessel (RPV) flange. "Investigation determined that the low reactor vessel water level signal occurred when the flushing wand was inserted into instrument nozzle N14A, which is the reference leg tap for the reactor vessel level instruments. The transient in differential pressure sensed by the level instruments resulted in the invalid actuation. "Corrective actions included a revision to the model work order for this task to clearly identify the nozzles that shall and shall not be flushed during this evolution. "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an invalid ECCS actuation and invalid system actuation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-05-01
43332 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2007-04-12 06:20 | 2007-05-01 11:23 | 2007-05-01 | PRIMARY CONTAINMENT ISOLATION DUE TO LOSS OF RPS POWER SUPPLY "On April 12. 2007 at approximately 0620, with the James A Fitzpatrick Nuclear Power plant (JAF) operating at 100% reactor power, an equipment malfunction occurred, resulting in the tripping of one of the two 'B' Reactor Protection System (RPS) motor generator Electrical Protection Assembly (EPA) breakers. This caused a corresponding loss of power to the 'B' RPS bus, a half scram and primary containment isolation valve closures. Appropriate actions were taken in accordance with Abnormal Operating Procedure (AOP)-60, 'Loss of RPS Bus 'B' Power'. All equipment operated as designed as a result of the loss of power to the 'B' RPS bus. "At 0629, the 'B' RPS bus was placed on the alternate power supply. At approximately 0658 the RPS half scram was reset and at approximately 0702 Primary Containment Isolation System (PCIS) isolation signal was reset. Restoration of the various isolated systems commenced shortly thereafter. The reactor remained at 100% power throughout the event and Technical Specifications (TS) Limiting Condition for Operation (LCO) Actions were entered for the affected equipment as required. "The above event meets the reporting criteria of 10 CFR 50 73(a)(2)(iv)(a) since the loss of RPS bus resulted in primary containment isolation signals affecting containment isolation valves in more than one system. The following systems or components isolated as a result of the loss of 'B' RPS bus: Reactor Water Cleanup, Reactor Building Ventilation, 'B' Containment Atmosphere Dilution, Torus Vent and Purge, Drywall Equipment and Floor Drain Sumps, 'B' Drywall Containment Atmospheric Monitors, Recirculation System Sample Line Main Steam Line Drains, Residual Heat Removal drain valve to Radwaste, Standby Gas Treatment (auto initiated). "Since the signal was invalid (the result of loss of power vs. an actual containment isolation condition), this event meets the criteria in 10 CFR 50.73 (a)(1) for being reported as a 60 day telephone notification in lieu of a written LER. "The loss of the 'B' RPS bus was caused by the tripping of one of the two in-series 'B' RPS motor generator EPA breakers. An apparent cause evaluation of the failure is in progress (Condition Report CR-JAF-2007-01422). At this time the failure is attributed to the failure of a subcomponent (capacitor) on the EPA breaker logic card. The logic card was replaced, restoring the 'B' RPS motor generator to service. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-05-01
43331 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-04-30 20:17 | 2007-05-01 00:39 | 2007-06-11 | HPCI DECLARED INOPERABLE DUE TO PRIMARY CONTAINMENT NITROGEN LEAK "At 1007 on the morning of 04/30/2007, operations personnel identified an adverse trend in Primary Containment Nitrogen makeup frequency. The subsequent investigation determined that Primary Containment Nitrogen was leaking backwards thru V22-0017 HPCI Turbine Exhaust Line Stop-Check Valve and V22-0016 HPCI Exhaust Check Valve, via the HPCI exhaust vacuum breakers and the environment of the HPCI room via the turbine seals. "The degradation of V22-0016 and V22-0017 constitute a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. (50.72(b)(3)(v)(D)). "At 2017 on the evening of 04/30/2007, V22-0017 HPCI Turbine Exhaust Line Stop-Check Valve and V22-0016 HPCI Exhaust Check Valve were declared inoperable due to Primary Containment Nitrogen leakage as described above. "At 2032 on the evening of 04/30/2007, V22-0017 HPCI Turbine Steam Exhaust Line Isolation was shut to isolate Primary Containment Nitrogen leakage. "With V22-0017 shut, HPCI is INOPERABLE and Unavailable." The licensee is in a 14 day LCO under section 3.6.1.3 for Primary Containment Isolation Valves (PCIV). However, they are in a 72 hour LCO for having "A" core spray and HPCI inoperable, concurrently. The licensee expects to have "A" core spray restored during dayshift on 5/1/07. Additionally, the licensee is in a 7 day LCO for EDG OOS. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY E. VANN TO J. KOZAL ON 5/01/07 AT 1048 * * * The licensee provided a correction to the TS LCO statement referenced in the initial report. The 14 day LCO is not under section 3.6.1.3 for Primary Containment Isolation Valves (PCIV). The correct LCO statement is 3.5.1 for ECCS Operating. The licensee will notify the NRC Resident Inspector. R3DO (Lipa) notified. * * * RETRACTION PROVIDED BY ROBERT MURRELL TO P. SNYDER ON 6/11/07 AT 1511 * * * "The purpose of this notification is to retract a previous report made on 5/01/07 at 0039 (ET) (EN 43331). Notification of this issue to the NRC on 5/01/07 was initially made due to the High Pressure Coolant Injection (HPCI) system being declared inoperable due to a primary containment nitrogen leak. "Specifically, at the time, operations personnel identified an adverse trend in Primary Containment Nitrogen makeup frequency. The subsequent investigation determined that Primary Containment Nitrogen was leaking backwards thru V22-0017, HPCI Turbine Exhaust Line Stop-Check Valve, and V22-0016, HPCI Exhaust Check Valve, via the HPCI exhaust vacuum breakers and the environment of the HPCI room via the turbine seals. "Since the initial report, Engineering has determined that the HPCI system was capable of performing its safety function. "This conclusion is based on the fact that V22-0016 and V22-0017 open during HPCI operation and the closing function is no longer included in the 10CFR50 Appendix J Testing Program since the line does not constitute a potential primary containment atmospheric pathway during and following a Design Basis Accident (DBA). MO2290A and MO2290B (HPCI Turbine Steam Exhaust Vacuum Breaker motor operated valves), which are Appendix J Program valves, communicate with both the HPCI exhaust line and the torus air space and will isolate during a Design Basis Accident (DBA). Therefore, the HPCI injection was still operational and the HPCI exhaust line will not communicate directly with the containment atmosphere and will not provide a containment atmospheric pathway during and following a Design Basis Accident. "All safety design functions of V22-0016 and V22-0017 were met. Additionally, as-left valve closure testing on both V22-0016 and V22-017 were successful and both valves were fully operable. "This event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report per 10 CFR 50.73." The licensee notified the NRC Resident Inspector. Notified R3DO (A.M. Stone). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-05-01
43330 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-04-30 07:00 | 2007-04-30 18:39 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * FAILURE OF A SAFETY RELATED ACID DUMP VALVE TO PASS A WEEKLY TEST "BWXT operates a component acid cleaning operation for [DELETED] components. One of the potential accident scenarios specifically evaluated in the Integrated Safety Analysis (ISA) is allowing the component to remain in the acid for sufficient time to dissolve the component and SNM into an unfavorable geometry acid solution. Dissolving through the [DELETED] and dissolving sufficient quantities of SNM to result in a potential safety issue would take hours." "To protect against this accident scenario, there are strict procedural controls (Items Relied On For Safety - IROFS) on the duration of time the component is in the acid. In addition, there is an engineered feature consisting of a timer and automatic acid tank dump valve (IROFS). This system will dump the entire acid bath from the tank well before the [DELETED] material is breached in the event the operator does not remove the component." "On April 30, 2007, at approximately 7:00 a.m., during a weekly functional test of the acid tank dump valve, the valve failed to open. This weekly test is listed in the ISA as a management measure to assure the continued availability and reliability of the dump valve system (IROFS). The last successful scheduled test of the valve was on April 24, 2007. The last successful use of the valve to dump the tank occurred on April 27, 2007. Therefore, the ability of the dump valve system (IROFS) to perform its intended safety function is questionable from April 27, 2007 to April 30, 2007. [DELETED] components were processed during the period when the functionality of the dump valve is in question. However, all [DELETED] operations were performed in accordance with operating procedures and there was no over [DELETED]. "BWXT is making this 24 hour report in accordance with 10 CFR 70 Appendix A, (b)(2). "There is currently no [DELETED] components being processed in the acid tanks." The licensee notified the NRC Resident Inspector. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
43329 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-04-30 15:02 | 2007-04-30 16:49 | 2007-04-30 | REACTOR TRIP DUE TO GRASS INTRUSION INTO CIRCULATING WATER INTAKE STRUCTURE "A manual trip of Salem Unit 1 was initiated due to a loss of the circulators from heavy grassing at the circulating water intake structure. All rods fully inserted on the trip and all systems responded as designed, with decay heat being removed via the atmospheric relief valves and subsequently the steam dump system. All Auxiliary Feedwater pumps auto started as expected on low steam generator levels from the trip. Salem Unit 1 had entered the abnormal operating procedure for circulating water due to two (2) circulators being out of service; one circulator previously emergency tripped due to excessive traveling water screen [differential pressure] and a second circulator emergency tripped soon thereafter. The procedure provides guidance to trip the plant if less than three (3) circulators are in service and power is above ten (10) percent. Two (2) of the remaining four (4) in-service circulators emergency tripped due to excessive traveling water screen differential pressure. At this point the manual reactor trip was initiated. The crew entered emergency operating procedures and stabilized the plant at no load conditions. "No personnel injuries have occurred as a result of the trip. Salem Unit 2 was not affected and is operating at 100% power. "Salem Unit 1 is currently in Mode 3. Reactor Coolant System temperature is 547° F with pressure at 2235 psig. "All ECCS and ESF Systems are available. Actions are being taken to return circulators to service." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-04-30
43328 | 0 | ACUREN - USA |  |  |  |  | 2007-04-30 14:00 | 2007-04-30 15:49 | 2007-04-30 | RADIOGRAPHY CAMERA MISSING IN TRANSIT The licensee's RSO reports that a Sentinel Model 880 delta radiography camera containing a 31 curie Iridium-192 source is missing in transit. The camera was shipped with two other radiography cameras from Anchorage Alaska on April 24, 2007. The cameras were being sent to QSA Global in Baton Rouge, Louisiana for source replacement. Two of the cameras arrived at QSA Global as scheduled on April 26, 2007. However, the third camera has not yet arrived as of the time of this report. The shipper is Federal Express. Each camera was assigned a separate FedEx tracking number but all three cameras were shipped at the same time. The RSO is attempting to track the package but has not yet received priority attention. The FedEx tracking system still shows the package in transit at Oakland CA. The RSO was not notified of the missing shipment by QSA Global until approximately 1400 CDT on 4/30/07. * * * UPDATE FROM GRAY TO HUFFMAN AT 1814 EDT ON 4/30/07 * * * The licensee reports that after a high priority trace by FedEx, the package was confirmed to still be in Oakland CA. FedEx stated that the camera will be sent onto Baton Rouge tonight. The licensee no longer considers the shipment missing. R4DO (O'Keefe), FSME (Morell), IRD(Cruz), and ILTAB (Sandler) notified. Applicable Federal Agencies have also been made. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-04-30
43327 | 0 | PLASTECH |  |  |  |  | 2007-04-24 | 2007-04-30 11:43 | 2007-04-30 | LOST STATIC ELIMINATOR Plastech contacted the NRC Operations Center to inform us that they performed an inventory on 4/24/07 and identified that an Amstat Industries, Inc. static eliminator S/N A2DF555, Model - P2021-8101 was missing and presumed lost. The static eliminator has not been seen since November of 2006. The person providing the report said that the initial activity of the static eliminator was 10 milli Curies but did not know what isotope was used in the device. Typically Amstat Industries static eliminators use Polonium-210. The company recognized the loss during an inventory required to renew their lease. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-04-30
43326 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-04-30 09:00 | 2007-04-30 09:45 | 2007-04-30 | LOSS OF EMERGENCY RESPONSE FACILITY - TSC VENTILATION SYSTEM UNAVAILABLE DUE TO MAINTENANCE "Planned preventive maintenance activities are being performed today (April 30, 2007) on the Hatch Nuclear Plant's Technical Support Center (TSC). These work activities are planned to be performed and completed expeditiously within one work shift (< 12 hours). These maintenance activities include the performance of preventive maintenance on the TSC filter train, air handling unit, condensing unit and fan unit for the TSC filler train. During a portion of the time these activities are being performed, this equipment will not be available for operation. As such, the TSC HVAC will be rendered non-functional during the performance of portions of the work activity. "If an emergency condition occurs that requires activation of the Technical Support Center, during the time these work activities are being performed, it will take no more than two hours to return the equipment back to functional status, dependent on the stage of the work activity at the time an emergency occurs. Plans are to utilize the TSC for any declared emergency during the time these work activities are being performed as long as radiological conditions allow. Procedure 73EP-EIP-063-0. Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the primary TSC. "This event is reportable per I0CFR50.72 (b) (3) (xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility for the duration of the evolution." The licensee notified the NRC Resident Inspector. The licensee will make a courtesy notification to the State and local officials. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-04-30
43325 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-04-20 16:00 | 2007-04-30 08:04 | 2007-04-30 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION "North Carolina Radioactive Materials Branch was notified by the radiation safety officer from UNC Hospitals of a possible misadministration involving the administration of MDS Nordion Yttrium 90 microspheres. The licensee initially contacted us immediately on the next business day following the patient administration, but was not certain at the time if the event was a misadministration because calculations and measurements had to be made to determine the percentage of the prescribed dose delivered. The licensee has determined that the patient only received approximately 72% of the prescribed dose (22.6 millicuries), which qualifies the event as a misadministration under current North Carolina Regulations. "The misadministration occurred because of a leak in the administration set during delivery of the dose. The licensee has been asked to determine if the leak was because of an apparent manufacturing defect with the administration set, or the result of an assembly error by the licensee. The licensee will report the cause of the event in the Misadministration Report that must be submitted within 15 days of the event. No harm is expected to the patient because of this event. The patient's physician and authorized user will determine if an additional administration is necessary to account for the dose not delivered initially." North Carolina Report Number: NC-07-02 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-05-03
43324 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2007-04-29 15:26 | 2007-04-29 17:48 | 2007-06-19 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO BOTH EMERGENCY DIESELS DECLARED INOPERABLE "At 1453, [the licensee] declared D/G [Emergency Diesel Generator] - A inoperable due to outside air temperature exceeding 78.2 degrees Fahrenheit and entered Technical Specification 3.7.b.2 [which has a] 7-day LCO. At 1526, outside air temperature increased to greater than 81.4 degrees Fahrenheit and D/G - B was declared inoperable. With both D/Gs declared inoperable, Technical Specification 3.0.c , Standard Shutdown Sequence was entered. No other safety related components are inoperable at this time. Plant shutdown was initiated at 1624 on 4/29/07." Based on recent findings by the licensee, the EDGs may not be capable of generating the minimum electrical power output needed to support a safety bus when outside air temperature exceeds certain limits (Operability Determination 151 dated April 26, 2007) The licensee is in the process of making ventilation modifications that will correct this condition. The licensee expects that the temperatures will drop below the EDG inoperability limits before the plant actually shuts down. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 06/19/07 AT 1515 ET FROM JACK BADZALA TO MACKINNON * * * "EN 43324 provided notification of initiation of a unit shutdown due to both emergency diesel generators (EDGs) being declared inoperable due to outside air temperature exceeding allowable limits. Unit shutdown had been initiated per Technical Specification (TS) 3.0.c, Standard Shutdown Sequence, due to TS 3.7 not being met. "A subsequent engineering evaluation allowed for increasing the allowable limit for outside ambient air temperature at which the EDGs are operable. The highest outside ambient air temperature recorded on 04/29/2007 (83.5 F) did not exceed the new allowable limit. Therefore, based on the new evaluation, both EDGs remained operable. TS 3.7 remained met and no TS shutdown was required. Consequently, this condition did not meet any reportability criteria in 10 CFR 50.72. "As a result, the notification made on 4/29/07 (EN 43324) is hereby retracted." NRC R3DO (Patrick Louden) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 89 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-04-29
43323 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2007-04-27 15:44 | 2007-04-27 17:54 | 2007-04-27 | INADVERTENT SIREN ACTUATION "This is a voluntary report under 10 CFR 50.72(b)(2)(xi). Approximately 1544 EST, the new siren system in Westchester County actuated inadvertently during testing. A press release has been issued. There has not been an event related to the health and safety of the public or onsite personnel, or protection of the environment." The New York Public Utility Commission has been notified. The licensee will notify the NRC Resident Inspector. | 100 | 1 | 0 | 100 | 1 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Startup |  | Power Operation | Startup |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-04-27
43322 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2007-04-26 19:30 | 2007-04-26 23:05 | 2007-04-26 | DEGRADED CONDITION DURING WELD DEPOSIT OVERLAY REPAIR "On April 26, 2007, at approximately 1930 it was reported that the N2K recirculation system inlet nozzle had slight water seepage. The seepage developed during welding operations being performed to install a full structural weld overlay over the nozzle and stopped almost immediately during the welding. The weld overlay was being installed as a conservative measure following UT inspections that had been performed earlier during the outage. This event is being reported in accordance with 10 CFR 50.72(b)(3)(ii)A. The plant is in stable condition." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-04-26
43321 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-04-24 | 2007-04-26 18:19 | 2007-04-26 | AGREEMENT STATE REPORT - NORTH CAROLINA - MISADMINISTRATION OF IODINE-131 The State provided the following information via facsimile: The State of North Carolina was notified on 4/26/07 of a misadministration of diagnostic Iodine-131. The event involved a "misdrawn and mislabeled dose from Shertech Pharmacy in Ashville NC (NC licensee 011-1203-1). The written directive [from the hospital] was for 30 microcuries for a diagnostic thyroid scan but 33.9 millicuries was delivered labeled as 33.9 microcuries. Nuclear Medical Technologist at Memorial Mission missed the error because they read the numbers (33.9) but not the units (millicuries vs. microcuries). Dose was administered on 4/24/07 and the error was found on 4/26/07. Patient and physician notified. Licensee is following up with Shertech." No information is available on any potential medical impact of the misadministration on the patient. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-05-02
43320 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-04-25 16:33 | 2007-04-25 17:13 | 2007-04-25 | FIRE AND EXPLOSION NEAR H2 STORAGE SHED "NOUE declared due to minor fire/explosion in area of the H2 storage shed. EAL 4.6.U.1.2. Fire has been put out 17:01 4/25/07." The fire was extinguished by the onsite fire brigade. There were no injuries. Offsite fire department assistance was requested however, the fire was extinguished prior to their arrival and the fire department did not enter the protected area. The licensee notified the NRC Resident Inspector. At 17:24 the decision was made that the NRC would remain in the normal mode of operation. * * * UPDATE AT 1754 ON 4/25/2007 FROM WESLEY HILL TO JOHN MacKINNON * * * The Unusual Event was terminated at 17:36 because the fire was out. Only minor damage was reported to the H2 storage shed. The licensee notified the NRC Resident Inspector. Notified DHS (John Frost), FEMA (Dwight Fuller), R2DO (Payne), NRR EO (Case), and IRD (Cruz). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-04-25
43319 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-04-25 | 2007-04-25 13:07 | 2007-04-25 | ONE I-125 PROSTATE SEED REPORTED MISSING The State provided the following information via email: "On 3/27/07, licensee reports being unable to locate a single Bard STM 1251 prostate seed containing 0.35 millicuries of Iodine-125 (60-day half-life) soon after a 130-seed (120 stranded seeds and 10 single seeds) medical procedure. This single titanium cylindrical capsule measures 0.8 mm (~0.03 inch) in diameter and 4.5 mm (~0.18 inch) in length (see Sealed Source Registry No. IL-1074-S-101-S). The last known location of the seed was in an operating room within the licensee's facility in Springfield, MA. "The licensee conducted an extensive search of its facilities as described in its written report dated April 9, 2007. The licensee assumes the seed is lost at this point in time. "In order to prevent recurrence, the licensee implemented updated seed counting and inventory control procedure changes and assignment responsibilities. "Cause description: Inconsistent use of seed well container. All 10 single seeds were placed in one well instead of placing one seed in each of ten wells within container. "Corrective action: Updated seed counting, inventory control procedure changes, and assignment responsibilities." Massachusetts Event Docket Number: 04-6969 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-04-30
43318 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2007-04-25 11:01 | 2007-04-25 11:36 | 2007-04-25 | LOSS OF OFFSITE POWER WHILE DEFUELED While the offsite grid operator was performing electrical switching in the switchyard, Millstone 3 experienced a complete loss of offsite power. The "A" emergency diesel generator started and supplied power to the protected vital train electrical buses. Power to Spent Fuel Pool Cooling, Service Water, and Component Cooling Water was restored. Spent Fuel Pool level was not affected. No radiation was released from the plant. Offsite power was restored to the site at approximately 11:50. The NRC did not escalate response mode for this event. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1430 ON 4/25/2007 FROM AL ELMS TO MARK ABRAMOVITZ * * * The Unusual Event was terminated at 14:27. The electrical lineup has been restored to the shutdown electrical lineup. The licensee notified the NRC Resident Inspector. Notified FEMA (Dwight Fuller), DHS SWO (John Frost), NRR EO (M.J. Ross-Lee), R1DO (Trapp), R2DO (Payne), R3DO (Passehl), R4DO (Smith), and IRD (Cruz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Refueling; FMode3: Refueling | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-04-25
43317 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-04-24 22:48 | 2007-04-25 01:33 | 2007-04-25 | MANUAL TRIP DUE TO LOSS OF CIRCULATORS "A manual trip of Salem Unit 1 was initiated due to a loss of circulators from heavy grassing at the circulating water intake. All rods fully inserted on the trip and all systems responded as designed with decay heat being removed via the steam dump system. All Auxiliary Feedwater pumps automatically started as expected on low steam generator levels from the trip. "The unit had previously entered the abnormal operating procedure for circulating water due to two circulators being out of service; one had previously emergency tripped due to high traveling water screen differential pressure and a second had been out of service for condenser waterbox cleaning. Alarms were received indicating rapid rising differential pressure on the remaining four in-service circulators' traveling water screens. "In accordance with the abnormal procedure, the Control Room Supervisor directed the tripping of the circulators and the reactor. There were no complications encountered as a result of the trip and all equipment operated as expected. The operating crew stabilized the plant at no load conditions. Salem Unit 1 is currently in Mode 3 with RCS at normal operating temperature and pressure. Actions are being taken to return the circulators to service." Unit 2 was not affected at this time and is operating at 100% power. The licensee notified the NRC Resident Inspector and the local township Licensee will be issuing a press release. *** UPDATE FROM LICENSEE(MEEKINS) TO KNOKE AT 0853 EDT ON 04/25/07 *** The power level was at 40% when the manual trip occurred and not 100% as previously reported. Notified R1DO (Trapp) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-04-25
43316 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-04-24 | 2007-04-24 17:11 | 2007-04-24 | MOISTURE DENSITY GAUGE STOLEN The State provided the following information via email: "On Tuesday, April 24, 2007, the State of Wisconsin, Department of Health and Family Services, Radiation Protection Section was notified that a CPN Model MCM-2 roofing gauge, containing 50 mCi of Am-241 had been reported stolen near Crete, Illinois. The Department was notified because the gauge is under ownership of a State of Wisconsin company. The gauge appears to have been in the State of Illinois under the control of a company employee that resides in Illinois and is performing work at a client's location in Illinois. The owner did not file for reciprocity with the State of Illinois. "Upon further investigation by the Department, the Department learned that the owner of the gauge does not have a proper Wisconsin Radioactive Material License. The owner received the gauge in a transfer of ownership when the past owner (a Wisconsin Radioactive Material License, #133-1249-01, Roofing Consultants LTD) sold the company to the current owner. The name of the company did not change when the ownership changed occurred, so the company is still operating under the name of Roofing Consultants LTD. The State of Wisconsin is currently investigating this transfer of ownership. "The State of Illinois has been contacted concerning this incident and is in contact with the Will County Sheriff Department. The State of Illinois and the State of Wisconsin will continue to investigate this incident." Wisconsin Event Number: 07-009 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-04-27
43315 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-04-24 02:10 | 2007-04-24 04:04 | 2007-04-24 | AUTOMATIC REACTOR SCRAM WITH ECCS INJECTION ON LOWERING REACTOR VESSEL WATER LEVEL "Limerick Unit 2 automatically shutdown on low reactor water level (+12.5 inches) at 0210 on 4/24/07. The cause is under investigation at this time. "All control rods inserted as required. HPCI and RCIC initiated, injected and restored reactor water level. Lowest reactor water level noted was -73 inches. "Primary containment isolation signals on +12.5 inches and -38 inches occurred. All isolations completed as required." "The plant is currently in hot shutdown maintaining normal reactor level with feedwater in service." Approximately 16000 gallons was injected in 4 minutes. There was no indication of RCS leakage. The licensee is investigating whether a feedwater runback had occurred. No SRVs lifted with the highest pressure observed at 1050 psi. The main condenser remains in service for decay heat removal. All EDGs are available, if needed. The licensee informed the NRC Resident Inspector and will inform both the State and Local authorities. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2007-04-24
43314 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2007-04-23 15:00 | 2007-04-23 16:24 | 2007-04-23 | NEBRASKA AGREEMENT STATE REPORT - THREE MISSING SELF LUMINOUS SIGNS CONTAINING TRITIUM The licensee provided the following information via e-mail "The licensee received six model 880-12-6-20 self-luminous signs from Safety Light Corporation in May of 1994. The report from Safety Light did not list serial numbers. The licensee's facility was remodeled in 2005. They have done a number of searches for the missing signs and have not been able to locate them. The licensee does not know where they are. They assume that the signs were misplaced during the remodel. This Department does not have the model numbers as they were not a part of the report from Safety Light in 1994. The licensee previously had not done a complete inventory to record the serial numbers." Event Cause: Inattention to Detail Corrective Action: No Corrective Action Taken Each of the three missing Safety Light Corporation signs initially contained 11.5 cuires/425.5 GBq of Tritium Event Date: 07/01/2005 Reporting Requirement: 20.2201(a)(1)(i) - Report of theft or loss of licensed material > 1000 x App C value Reference Number: 04-20-07 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2007-04-26
43313 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-04-23 10:24 | 2007-04-23 11:25 | 2007-04-23 | AUTOMATIC REACTOR TRIP DUE TO GENERATOR GROUND RELAY ACTUATION "Vogtle Unit 2 tripped from 53% power due to a turbine trip /P9 reactor trip RPS actuation during power ascension following completion of refueling outage 2R12. Initial investigation indicates that a generator neutral ground relay actuated causing an automatic main generator turbine trip. No visual damage is apparent on any plant equipment. "All systems responded as expected. Both motor driven auxiliary feedwater pumps and the turbine driven started on lo-lo steam generator level and AMSAC. "The NRC Resident Inspector was notified." All control rods fully inserted upon RPS actuation, the atmospheric relief valves lifted momentarily and reseated as expected, and no safety valves lifted. After the trip, steam generator level was being maintained with auxiliary feed pumps and steam was being dumped to the condenser. The plant was placed in the normal shutdown electrical lineup. | 0 | 0 | 0 | 0 | 53 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-04-23
43312 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-04-22 03:20 | 2007-04-22 13:53 | 2007-04-22 | UF6 RELEASE DETECTION SYSTEM INOPERABLE "At 0320 CDST, on 4-22-07 the Plant Shift Superintendent (PSS) was notified that the control power for C-337A #1 Autoclave had been lost due to a blown control power fuse. Investigation of a problem with the Autoclave 1 West CV-510 valve close indicating light not functioning properly was in progress at the time the fuse blew. Maintenance personnel were performing non-intrusive checks of the valve's limit switch and had activated the limit switch operating plunger when the fuse blew. No maintenance work package was used for these checks. The power supply for the local autoclave area audible and visible alarms for the UF6 Release Detection System are fed from the #1 Autoclave control power. Due to this loss of control power, the UF6 Release Detection System was rendered inoperable. At the time of the incident, the C-337A facility was operating in an operational mode in which the UF6 Release Detection System was required to be operable, TSR 2.2.4.1 Mode 5. The C-337A Operations Monitoring Room where UF6 Release Detection System alarms would have been received was unoccupied at the time of the fuse failure due to C-337A personnel in the autoclave area assisting with the CV-510 light investigation. The system was declared inoperable and Limiting Conditions of Operation (LCO) required action, TSR 2.2.4.1 A.1, was put in place until power could be restored. Subsequent troubleshooting revealed the CV-510 limit switch was broken and has shorted the control circuit to ground when activated causing the fuse to blow. Power was restored and the UF6 Release Detection System was declared operable at 0539 on 4-22-07 following repairs and PMT. "The event is reportable as a 24 hour event as required by 10 CFR 76.120(c)(2)(i); An event in which equipment is disabled or fails to function as designed when the equipment is required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-04-22
43311 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-04-20 03:45 | 2007-04-20 09:58 | 2007-04-20 | AGREEMENT STATE REPORT INVOLVING THEFT OF RADIOPHARMACEUTICALS FROM DELIVERY VEHICLE At 0345 hours on 4/20/07 a Cardinal Health, Inc. delivery vehicle (Ranger Pickup) parked at the Presbyterian Hospital located at 200 Hawthorne Lane in Charlotte, NC was broken into and had six (6) Type-7A ammo cans stolen. The ammo cans contained forty-nine (49) unit doses of Tc-99m (total activity 1.669 Curies) used for diagnostic work. The Charlotte-Mecklenburg Police Department was notified of the theft. NC plans on issuing a press release regarding this incident. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-04-25
43310 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-04-18 13:30 | 2007-04-19 09:16 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * UNFAVORABLE GEOMETRY CONTAINER BELOW LIMIT IN URANIUM RECOVERY GENERAL PURPOSE AREA "I. Event Description "On Wednesday April 18, 2007, at approximately 1330, Uranium Processing and Research Reactors (UPRR) personnel notified Nuclear Criticality Safety that a procedural deviation had occurred during the transfer of solution from favorable geometry columns to an unfavorable waste container. The event occurred in the General Purpose Area of the Uranium Recovery Facility where used organic solution from the solvent extraction system is purified for re-use or disposal. The General Purpose Area is physically segregated from the Dissolution and Solvent Extraction Processing Areas of Uranium Recovery, is not part of the Container Controlled Area, and consequently carefully controlled use of unfavorable geometry containers is part of the approved process. "Dual, independent sampling of the organic solution's uranium concentration is performed according to procedure to verify Nuclear Criticality Safety limits are met prior to bringing the solution into the General Purpose Area. The solution is then processed in favorable geometry columns to remove uranium in accordance with procedural requirements. After processing, the solution can be returned to the extraction process by performing dual sampling and subsequent transfer to a borosilicate glass Raschig ring filled (critically safe, neutron poisoned) container. If however, the material is to be disposed of, then an additional dual sampling by Nuclear Materials Control personnel is required prior to transfer to an unpoisoned, unfavorable geometry waste container through an inline monitor. "In this event, approximately 60 liters of solution required processing. The operator performed the initial dual, independent sampling of the solution for entry to the process. The results of sampling [DELETED], well below the operating limit of [DELETED]. The operator then processed the solution according to procedure to remove the majority of the uranium. He then obtained two samples of the remaining low concentration solution and verified acceptability of the solution for transfer. These results were [DELETED], respectively. At this point the operator transferred the solution to an unfavorable geometry waste container without the required NMC samples or inline monitor. "II. Evaluation of the Event "10 CFR 70 Appendix A states that the NRC must be notified of an event within 24 hours followed by a 30-day written report if the following condition is met: "(b) Twenty-four hour reports. Events to be reported to the NRC Operations Center within 24 hours of discovery, supplemented with the information in 10 CFR 70.50(c)(1) as it becomes available, followed by a written report within 30 days; "(2) Loss or degradation of items relied on for safety that results in failure to meet the performance requirement of §70.61. "An evaluation has determined that this event resulted in loss or degradation of items relied on for safety (IROFS's) resulting in failure to meet the performance requirement of §70.61 in that the risk of a credible high-consequence event (i.e., a criticality accident) was no longer limited such that its likelihood was highly unlikely. However, multiple other IROFS's as noted above (dual input sampling, uranium removal processing, and dual sampling prior to transfer) were in place and functioning to prevent a criticality accident. "The documented ISA scenarios were reviewed. The evaluated scenario for this operation identified multiple IROFS to prevent transfer of an unsafe mass of uranium to an unfavorable geometry waste drum. "1. First and foremost, the concentration limit of [DELETED] grams [DELETED]/liter verified by two independent samples ensures the mass of material in the process is limited. "2. Second, dual independent sampling is performed by two different organizational groups to ensure an acceptable mass prior to transfer from the column system to unfavorable geometry. "3. Third, the solution is transferred through an active in-line monitoring system that terminates the transfer (i.e., shuts off the flow) if an unacceptable concentration is detected. "Of these controls, the first was executed properly in this event. Part, but not all, of the second control set was also executed. The third control was not used. "Criticality safety calculations supporting the ISA demonstrate that even if the solution was at the upper limit for entry to the area, no Uranium was removed during processing, and the material was transferred to unfavorable geometry without verification, that a criticality could still not occur. "III. Notification Requirements "The event is reportable under 10 CFR 70 Appendix A (b) (2) Loss or degradation of items relied on for safety that results in failure to meet the performance requirement of §70.61. "IV. Status of Corrective Actions: "The solution has been returned to the favorable geometry columns using the approved procedures, and the concentration was confirmed by sampling to be less than [DELETED] grams [DELETED]/liter. Operations in the Uranium Recovery Facility General Purpose Area, where this process is performed, have been suspended. An investigation of the event is underway." A facility representative notified the NRC Resident Inspector. * * * UPDATE AT 1107 ON 4/20/07 FROM L. MORELL TO P. SNYDER * * * "BWXT's investigation of this issue is ongoing. Based on our investigation and associated time lines, BWXT believes that notification may also have been required under 10CFR70, Appendix A:(a)(5). This determination was made at approximately 10:30 am on April 20, 2007. "This reporting criteria states: "Loss of controls such that only one item relied on for safety, as documented in the ISA Summary, remains available and reliable to prevent a nuclear criticality accident, and has been in this state for greater than 8 hours. "Therefore, BWXT is providing this update to the notification report and a corrected page 1 of the original Event Notification that includes identification of 10CFR70, Appendix A: (a)(5). The facts of the issue as described in the initial report remain as stated." The coversheet of the original event notification has been revised to include the additional notification requirement as a result of this report. The facility will notify the NRC Resident Inspector. Notified R2DO (Munday), FSME EO (Morell) and Fuels OUO Group (via e-mail). * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | ONLY ONE SAFETY ITEM AVAILABLE | [8 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) | PART 70 APP A (a)(5) |  |  | 0 | 2008-05-11
43309 | 0 | SMITH MEDICAL ASD INC |  |  |  |  | 2007-02-26 | 2007-04-18 15:18 | 2007-04-18 | LOST OR STOLEN STATIC ELIMINATOR Po - 210 SOURCE On February 26, 2007 a 5 millicurie Polonium 210 source static eliminator button was identified as lost or stolen from a silicone extruder frame. The device was last used on February 23, 2007. The lost button was 1 of 3 buttons on the extruder. The device model number is P2042, serial number A2FD631. The static eliminator is leased from Amstat Industries, 3012 North Lake Terrace, Glenview, IL 60026. A department-wide search and an interview with all employees was conducted without success. It is believed that the button may have been swept up during floor cleaning and ultimately disposed of in a land fill. The search for the missing button will continue and corrective actions have been put in place to prevent reoccurrence. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-04-18
43308 | 0 | COMMUNITY HOSPITAL INDIANAPOLIS |  |  |  |  | 2007-04-18 13:30 | 2007-04-18 14:20 | 2007-05-15 | MEDICAL EVENT - PATIENT RECEIVED DOSE LESS THAN PRESCRIBED The following information is taken from a facsimile sent by Community Hospital Indianapolis: A patient undergoing Yttrium-90 theraSphere treatment of the liver received an under dose. The original estimated intended dose was 301 Gray (Gy). The authorized user confirmed the setup during performance of the pre-administrative checklist. The under dose occurred due a mis-positioned stopcock that resulted in part of the intended source material being directed to a waste vial rather than the patient catheter. When the mis-directed (source) liquid was noted in the waste vial tubing, the authorized user re-checked the delivery system and corrected the stopcock orientation. Based on a delivered source activity of 3.28 GigaBecquerel (GBq), the estimated dose received by the patient is 130 Gy. The patient has been notified of the under dose. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE AT 1200 EDT ON 05/15/07 FROM ANDREA BROWNE TO OPS CENTER VIA COMMERCIAL MAIL * * * The following information was received as an update to this report via letter dated April 30, 2007 addressed to the Operations Center: "After an investigation by the region III office, Community Hospitals, Indianapolis, Materials License Number 13-06009-01 is expanding the written follow-up to the verbal report of a medical event made 4/18/07, given Notification Number 43308 and the written report filed 4/18/07. "Per 35.3045 "(i) Licensee's Name: Community Hospitals of Indiana, Inc. (#13-06009-01) "(ii) Name of Prescribing physician: [DELETED] (Authorized User) "(iii) Brief Description of Event: Partial dose routed to waste vial because of incorrect stopcock orientation. The prescribed treatment site was the right liver lobe; the prescribed treatment site dose was 120 Gy. Because of the partial routing of the dose to the waste vial the dose delivered to the right liver lobe was 54.4 Gy. "(iv) Why event occurred: Authorized user confirmed setup was correct when queried during the pre-administration checklist. However, stopcock was turned so that dose was directed to waste vial rather than into the patient delivery catheter. The interventional radiologist noted liquid in the waste vial tubing and directed the authorized user to stop; The authorized user re-checked the delivery system and corrected the stopcock orientation. The remainder of the dose was delivered to the patient. "(v) Effect, if any, on the individual who received the administration: It is believed by the radiation oncologist and the interventional radiologist that there will be no effect on the patient. This treatment is one of several planned for this patient. Justification for this conclusion is that the original estimated tumor dose was 301 Gy based on the written directive of 120 Gy to the right lobe of the liver. Based on a delivered activity of 3.28 GBq, considering the tumor hypervascularity and volume, the estimated tumor dose is 130 Gy as a result of the 54.4 Gy delivered to the right liver lobe. This is within the dose range that the FDA has accepted for tumor dose in cases of liver metastases. "(vi) Actions planned to prevent recurrence: A second individual (the interventional radiologist, radiologic technologist, nurse, or similarly trained individual) will be required to check the delivery setup portion in addition to the individual actually delivering the dose. This second check will be built in to the checklist. "(vii) Certification that the licensee notified the individual (or the individual's responsible relative or guardian), and if not, why not: The interventional radiologist has notified the patient of the event. The referring physician was also notified of the event. "This revised report will also be sent to the Operations Center." Notified R3DO (Bruce Burgess) and FSME (Greg Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-04-19
43307 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-03-12 | 2007-04-18 13:05 | 2007-04-18 | AGREEMENT STATE REPORT - IRRADIATOR WATER CONDUCTIVITY GREATER THAN LIMIT "On March 13, 2007, the Agency was notified by the licensee that their source pool conductivity had exceeded 100 microsiemens per centimeter (uS/cm). The facility had completed a source replacement the week of February 21, 2007 and had regenerated their ion exchange resin on March 9, 2007. On March 11, 2007, the water conductivity was found to be 269.1 uS/cm. The licensee conducted an investigation and found that the system used to control the regeneration of their ion exchange resins, had failed to operate properly due to a power outage. The purification resins were replaced and the conductivity was reported to be 69.34 uS/cm on March 30, 2007 and 1 uS/cm on April 4, 2007. The licensee has upgraded the control system and is measuring conductivity twice a day to prevent a reoccurrence." Texas report number - I - 8402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-04-23
43306 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2007-04-16 11:45 | 2007-04-17 12:28 | 2007-04-17 | AGREEMENT STATE REPORT - CONTAMINATED SHIPMENT EXCEEDING DOT REGULATIONS The licensee provided the following information via facsimile: "The Radiation Safety Officer at Energy Solutions waste processing facility [Duratek Radwaste Processing, Oak Ridge ,TN] called the State to report an incoming shipment [open bed trailer] containing 12 boxes [of Dry Active Waste - 323 millicuries] from Dairyland Power Cooperative in Genoa, Wisconsin was surveyed for receipt and found to have greater than 200 Mr/hr on one box. The dose rate exceeded the DOT regulations referenced in 49 CFR 173.441. NRC regions 1 and 3 were notified on 4/16/07." In further discussions with Dairyland Power Cooperative it was stated that when the shipment left La Cross power plant facility the survey of the boxes was within DOT shipping regulations. During transport the Dry Active Waste most likely settled to the bottom of the box which accounted for the elevated radiation levels. Dairyland Power Cooperative stated the state of TN would be contacting the state of WI about this incident. TN Report ID Number: TN-07-074 *** UPDATE FROM STATE OF TN (SHULTS) TO KNOKE AT 1600 EDT ON 04/17/07 *** Spoke to state of TN and they indicated they were not contacting the state of WI since Dairyland Power Cooperative was a NRC licensee. Notified FSME (Morell) and R1DO (Miller) and R3DO (Kozak). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2007-04-20
43305 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-04-16 19:15 | 2007-04-17 11:36 | 2007-04-17 | LARGE WATER LEAK ON HIGH PRESSURE FIRE WATER SYSTEM "At 1915, on 04/16/07, the Plant Shift Superintendent was notified of a large water leak on High Pressure Fire Water system. This system provides water for fire suppression to the plants process buildings. An alarm was received indicating a drop in the level of High Pressure Fire Water (HPFW) elevated tank. The buildings were contacted to look for a large water leak and the leak was quickly located inside the C-337 process building. The exact system leaking was not apparent as the leak was under the building concrete floor. To stop the leak the HPFW pumps supporting the system were shutdown and the sectional valves outside the building were closed. This action made the HPFW system for all process buildings inoperable. LCO actions 2.4.4.8 and 2.4.4.6 were entered. The leak was determined to be on C-337 system C-12 and this system and the two adjacent systems were isolated and all other previously isolated valves were reopened. The HPFW pumps were restarted and the HPFW elevated tank was refilled to the TSR required level. These actions restored HPFW operability to the other areas in the plant at 2101 hours. TSR required hourly fire patrols were initiated for the affected area in C-337. The leak is located on an underground eight inch header under the alarm and actuation controls for system C-12 inside the building. "This is being reported as an event in which equipment is disabled or fail to function as designed when the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and no redundant equipment is available." The licensee stated that this leak caused substantial damage to the concrete pad on the floor of the building. No structural damage is believe to have occurred but the concrete pad with have to be completely removed, the piping repaired, and eroded earth backfilled. A new concrete pad will then likely need to be poured. Nearly half a million gallons of water may have been lost through the break before it was isolated. The licensee has checked the site outfalls and no contamination was detected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-04-17
43304 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2007-04-13 | 2007-04-16 14:49 | 2007-04-16 | AGREEMENT STATE REPORT - LOST CONTROL OF 2 MILLICURIES OF IR-192 The licensee provided the following information via facsimile: "This is initial notification that the Department is investigating an incident involving licensed radioactive material that was discovered at a [Grand Junction, CO] landfill on 4/13/07. Apparently, a licensee using radioactive materials for subsurface well tracing activities lost control of 4-10 bottles of resin bead waste containing Ir-192. Radiation readings taken on the waste containers indicated about 2 millirem per hour at one meter. The company believed to be responsible for the waste, Protechnics, responded to the scene and removed the material to their facility for decay. So far, there is no indication that any members of the public were exposed to radiation in excess of established limits. An investigation is in progress." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2007-04-19
43303 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-04-15 09:30 | 2007-04-15 23:30 | 2007-04-16 | SAFETY SYSTEM ACTUATION - AUTOCLAVE HIGH CONDENSATE LEVEL ALARM RECEIVED DURING HEATUP "At 0930 hours, Autoclave (AC) # 2 in the X-344 Facility experienced a Steam Shutdown due to high condensate level alarms (A) and (B) actuating. The AC was in applicable TSR Mode II 'Heating' for 45 minutes when the actuation occurred. This is considered a valid actuation of a 'Q' Safety System. The autoclave was placed in MODE IV 'Shutdown' and declared inoperable by the Plant Shift Superintended (PSS). An investigation is underway to determine the cause of the actuation. No release of radioactive material occurred as a result of the incident. This event is being reported in accordance with UE2-RA-RE1030 Appendix D. J. 2. Safety Equipment Actuation." The NRC was notified of this by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-04-16
43302 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-03-15 | 2007-04-13 18:15 | 2007-04-13 | AGREEMENT STATE REPORT - THREE LOST TRITIUM EXIT SIGNS "The RSO called [1625 CDT on 4/13/07] to report that during their quarterly inventory check, the facility discovered that (3) tritium exit signs were lost: Mfg: BetaLux Model 171-20-R-U-WH-D-RD, Serial Numbers: 255-381; 255-319; 255-399, Activity Source: 20 Ci each. "Root Cause: The RSO [and] Incident Review board believe the exits signs were inadvertently knocked down [and] thrown away, so that the person responsible would not be found out [and] held accountable. TI runs a 24 hour-7day operation, so the RSO explains it is very difficult to find the culprit(s). "Committee corrective action: Current [and] replacement signs will be attached with a secondary tether so that if the signs are knocked down, they will not fall down, but dangle until refastening is performed. "Texas Incident Number: I-8403." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-04-18
43301 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2007-03-07 | 2007-04-13 15:56 | 2007-04-16 | AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via facsimile: "A brachytherapy misadministration involving a 31year old female patient with a history of vaginal cancer was reported to NYS DOH BERP on 3/9/07. "The patient was successfully treated to 5590 cGy to the target volume using external beam (IMRT) therapy and she was to receive 2500-3000 cGy via interstitial brachytherapy with both Cesium-137 and lridium-192 (seeds in ribbons) sources. "The medical physicist developed a treatment plan as directed by the authorized user/ radiation oncologist using a commercial treatment planning software application. Eleven ribbons with 8 seeds each and an activity of 1.855 mgRaEq per Ir-192 [3.19 mCi] seed were ordered from Best Industries. Hospital owned Cs-137 sources were selected for use. The medical physicist verified source strength of all sources. The oncologist reviewed and approved the plan. He prescribed a total dose of 2500 cGy to be delivered to the 50 cGy-isodose line for a total treatment time of 50 hours. "At 2:30 PM on 3/6/07 the sources were placed into the patient. A Syed template was used to place the ribbons and the Cs-137 sources were loaded into a tandem applicator. "On 3/7/07, late in the morning, the medical physicist performed a manual check of the treatment plan calculations and identified a significant discrepancy - the hand calculations indicated a significantly higher dose rate than what was generated from the treatment planning software. An investigation ensued, which included consultation with the TPS vendor's application specialist. After several hours of investigation it was determined that the original treatment plan was in error, and at 5:30 PM on 3/7/07, after 27 of the intended 50 hour treatment time, the radiation oncologist decided to remove the sources [from the patient]. "Instead of the intended 2500cGy, the patient received an estimated dose of 4590 cGy and the anterior rectal dose was approximately 7300 cGy. "The licensee provided a written report as required, and DOH staff performed an on-site investigation on 3/21/2007. "Cause and contributing factors: "1. The primary error was the use of an inappropriate Dose Rate Factor in the TPS. The value used corresponded to the DRF for Air Kerma however the source strength entered was in MgRaEq. The physicist should have changed the units of source strength or entered the correct DRF. "2. Changing the units of activity in the TPS does not generate a prompt for a new Dose Rate Constant. "3. During the physics review it was determined that acceptance testing of this treatment planning software did not include Iridium-192. The acceptance testing covered Cesium -137 and Iodine -125 seeds which where the only materials being used at the time. If this testing had been performed the physicist would have been more likely to recognize that the treatment planning system does not automatically select the correct dose rate factor when the source strength units are changed. "4. There was no check of the preplan before the seeds arrived although there was sufficient time (sources ordered 2/27/07). The plan was approved on 3/6/07. "5. Neither the physicist nor the radiation oncologist had prepared a treatment with Ir-192 in six years and the physicist had not used this particular TPS for Ir-192 implants. It would have been prudent to have an additional review or outside review in order to verify there were no oversights or errors. "6. The double check was not done until after the day after sources had been implanted. Again while the physicist was observing the minimum requirements of Part 16 it would have been prudent to perform a check of the calculations either prior to the implant or immediately thereafter. "Corrective action: The policy and procedures have been changed to require a check of calculations for any single fraction brachytherapy treatment to be performed and approved prior to initiation of treatment. "Patient condition and follow-up: The radiation oncologist disclosed that the patient is at risk for radiation cystitis, rectal proctitis and more importantly, fistula formation between the rectum and the vagina. The patient will be monitored closely over the next year by both her gynecologic oncologist and the radiation oncologist. The patient is currently being treated with broad spectrum antibiotics along with daily treatments in a hyperbaric oxygen chamber." NY Event No: NYS-DOH 07-001 * * * UPDATE ON 4/16/2007 AT 1112 FROM FLANNERY (NRC/FSME) VIA E-MAIL TO HUFFMAN * * * This event has been reviewed and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2007-04-17
43300 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-04-12 10:00 | 2007-04-12 16:41 | 2007-04-12 | FITNESS FOR DUTY - POSITIVE RANDOM TEST A non-licensed employee supervisor had a confirmed positive test for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been denied. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.73 |  |  |  | 0 | 2007-04-12
43299 | 0 | US DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2007-02-14 11:10 | 2007-04-11 20:03 | 2007-04-25 | TRANSPORTATION PACKAGE SURFACE EXCEEDING SURFACE CONTAMINATION LIMITS "Pursuant to 10 CFR 20.1906, a receipt wipe test of a package of radioactive material indicated that removable radioactive contamination of the package surface exceeded the limits in 10 CFR 71.87(i). The package was received at the VA Medical Center, 6010 Amarillo Boulevard West, Amarillo, TX, at about 1110 on February 14, 2007. This VA Medical Center is a site of use listed on Master Material License Permit No. 30-01747-02 held by the New Mexico VA Health Care System, 1501 San Pedro SE, Albuquerque, New Mexico 87108. A wipe test sample of the exterior of the package was measured as containing 107,000 dpm shortly after package receipt. "The package was received from Panhandle Nuclear Pharmacy, 6700 West 9th Street, Amarillo, TX 79106. The package contained 11 millicuries of Tc-99m for use by the nuclear medicine department. "The commercial radiopharmacy, which was the final delivery carrier, was promptly notified. However, the staff of the nuclear medicine department did not notify the Radiation Safety Officer (RSO). The RSO discovered today [04/11/07] that the package contamination had exceeded an amount requiring notification of the NRC. "The VA National Health Physics Program will follow up on this event and will also notify the NRC project manager for our master material license." * * * UPDATE FROM LEIDHOLDT TO HUFFMAN AT 1915 EDT ON 4/25/07 * * * The licensee provided the following information via email: "As a followup review to this event, the facility Radiation Safety Officer has discovered that receipt wipe tests of the outer surfaces of two other packages of radioactive material indicated removable radioactive contamination exceeding the limits in 10 CFR 71.87(i). A wipe test of a package received on June 12, 2006, was assayed as 33,200 dpm and a wipe test of a package received on January 10, 2007, was assayed as containing 28,600 dpm. "The packages were received from Cardinal Health, 27 Medical Drive, Suite A, Amarillo TX 79106 [information redacted]. The packages both contained Tc-99m for use by the nuclear medicine department. "In both cases, the commercial radiopharmacy, which was the final delivery carrier, was promptly notified. The small amounts of removable contamination, less than two percent of a microcurie on either wipe sample, make it unlikely that any harm was caused in either case. "The VA National Health Physics Program will follow up on this incident. We will also notify the NRC project manager for our master material license." This is a supplement to the original report in that, similar to the initial report, the Amarillo facility staff did not notify the RSO and the required NRC notifications were not made at the time of occurrence. R3DO(Passehl), R4DO(Smith), and NMSS EO (Pierson) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | TX | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2007-04-11
43298 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-04-11 14:05 | 2007-04-11 15:20 | 2007-04-11 | UNAUTHORIZED ESCORTED VISITOR ENTRY Actual entry of an unauthorized person (escorted visitor) into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2007-04-11
43297 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-04-10 | 2007-04-11 15:02 | 2007-04-11 | AGREEMENT STATE REPORT - MALFUNCTIONING GAUGE SHUTTER The State provided the following information via facsimile: The licensee uses a Themo Electron Model SR-U2 device, no serial number provided, to measure thickness. The device contains a Sr-90 50 millicurie source. On 04/10/07, the licensee left a phone message that the gauge shutter stuck closed [Different gauge than reported in EN #43296]. A contractor has been called to fix the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-04-16
43296 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-03-27 | 2007-04-11 14:23 | 2007-04-11 | AGREEMENT STATE REPORT - MALFUNCTIONING SHUTTER The State provided the following information via facsimile: The licensee uses a Themo Electron Model SR-U2 device, serial number 1179BC, to measure thickness. The device contains a Sr-90 50 millicurie source. On 03/27/07 the gauge shutter stuck open. The unit was secured by restricting access to the one door that leads to the area where the gauge is located. The gauge vendor has been called. On 03/30/07, a contractor, RSI, came in to repair the broken spring on the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-04-16
43295 | 0 | VICTOR RIVERA ASSOCIATES |  |  |  |  | 2007-04-10 08:14 | 2007-04-10 12:14 | 2007-04-10 | DAMAGED CPN MOISTURE DENSITY GAUGE Soil compaction equipment ran over a CPN moisture density gauge. The sources were fully contained. A portable radiac verified no abnormal radiation and wipe test swipes will be read later to verify the sources are not leaking. The gauge will be shipped back to CPN International for repair and/or disposition. Gauge Model: MC-1 Serial Number: M15096422 Sources: Cs-137 10 milliCuries Am-241 50 milliCuries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PR | OTH | GEN |  |  |  |  | 0 | 2007-04-10
43294 | 0 | FAIRBANKS MORSE ENGINE |  |  |  |  | 2007-04-09 | 2007-04-09 20:30 | 2007-04-09 | PART 21 NOTIFICATION - DIESEL CAM ROLLER BUSHING FAILURES "The [fuel pump] cam roller bushing part number 16100527 (and part number 16600336 for the kit containing cam roller bushings) for the Fairbanks Morse Engine Opposed Piston engine Emergency Diesel Generator shipped prior to August 2001 may be made from an incorrect material that is too soft for the application. "The subject emergency diesel generator would not have been able to achieve its maximum load rating and therefore not have been able to perform its intended function." The potentially affected plants are: Alabama Power/Farley Arkansas Power Amergen /GPU/TMI Constellation/BG&E Detroit Edison/Fermi Dominion/Millstone Vepco Georgia Power/Hatch Vermont Yankee Exelon/PECO - Limerick/Peach Bottom FPL/NMC/IES/Duane Arnold NMC Prairie Island/Northern States Progress Energy (CP&L) SCANA/South Carolina Electric and Gas Electronuclear (Electrobras) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2007-04-09
43293 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-03-05 15:00 | 2007-04-09 17:39 | 2007-04-09 | AGREEMENT STATE REPORT - POSSIBLE RELEASE OF TRITIUM GAS The licensee provided the following information via email: "Sometime between 03-05-2007 and 03-09-2007, 12 Tritium Exit signs containing approximately 6.2 Ci of Tritium each were released from Stanford University to the Newby Island Landfill in Milpitas, CA. The exit signs were reported to have been crushed on a hard surface with a possible release of the Tritium gas contained in the glass beads in the exit signs, and then covered with 60 tons of dirt. The Tritium exit signs are manufactured by the Isolite Safety Light Corporation in Bloomberg, PA. Licensee RSO will contact the Isolite Safety Light Corporation for more information concerning the Tritium exit signs and determine if the Tritium therein was released as a gas, or if any remains after crushing the glass beads that may be water soluble. The General Manager of the Newby Island Landfill was contacted by licensee RSO." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-04-12
43292 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2007-04-09 07:30 | 2007-04-09 15:17 | 2007-04-10 | SEISMIC MONITORING SYSTEM OUT OF SERVICE "On April 9, 2007, at approximately 0730 hours, the keyswitch for the Seismic Monitoring System was discovered in the off position, rendering the Seismic Monitoring System unavailable. The system has apparently been in this configuration since March 29, 2007, when deficiencies were found during routine calibration checks. The ability to declare an Unusual Event per Emergency Action Level 8.A.1 would not be significantly hampered by this event, because this declaration would be based on either personnel feeling an earthquake, or detection via the Seismic Monitoring System. However, the unavailability of the Seismic Monitoring System could potentially hamper the operators in determining the magnitude of an earthquake in order to determine if it reached Operating Basis Earthquake levels or Safe Shutdown Earthquake levels. Therefore, this could potentially hamper the declaration of an Alert or Site Area Emergency, respectively, per Emergency Action Levels 8.A.2 or 8.A.3. Therefore, this event is being considered reportable per 10 CFR 50.72(b)(3)(xiii), as it results in a loss of emergency assessment capability. Compensatory measures are being established to obtain an off-site source of this information in a timeframe that can support timely declaration of an emergency." The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 04/10/07 AT 0936 EDT FROM THOMAS PHILLIPS TO MACKINNON * * * "At time 0639 on 4/10/2007 the Seismic Monitoring System Instrumentation was reset. The Seismic Monitoring System is now FUNCTIONAL. "With the SMA-3 Key Switch in the OPERATE position and the system RESET, the Seismic signal processing system and output devices are functioning to provide a STA SEISMIC INSTR ON alarm and to indicate if an OBE or SSE threshold has been exceeded. Therefore, the emergency assessment capability to declare an ALERT for EAL 8.A.2 or a Site Area Emergency for EAL 8.A.3 is restored. The Seismic Monitoring System remains INOPERABLE pending completion of DB-MI-04222, Seismic Instrumentation Calibration." R3DO (S. Burgess) notified. NRC Resident Inspector will be notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-04-09
43291 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2007-04-08 22:32 | 2007-04-09 04:26 | 2007-04-09 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "Energy Northwest is reporting initiation of a planned shutdown of Columbia Generating Station Pursuant to 10 CFR 50.72(b)(i), 'The initiation of any nuclear plant shutdown required by the plant's technical specifications.' This plant shutdown is undertaken prior to 1032 PDT on 4/9/07 which is the expiration of the completion time of Technical Specification Limiting Condition for Operation 3.8.7 Required Action C. This plant shutdown is undertaken due to complications from recovery of the failure of a backup power supply to power converter E-IN-2A/2B reported in event notification # 43290." The NRC Resident Inspector was notified of this event by the licensee. | 85 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-04-09
43290 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2007-04-07 13:44 | 2007-04-07 17:26 | 2007-04-07 | FIRE IN THE REACTOR PROTECTION SYSTEM DIVISION 2 EQUIPMENT ROOM "On April 7, 2007 at 1330 Pacific Daylight Time (PDT) Columbia Generating Station (CGS) experienced an electrical fire in the Reactor Protection System (RPS) Division 2 equipment room. Currently, reactor level is stable and being controlled with the feedwater system. Reactor pressure is stable and being controlled with the turbine bypass valves in automatic. All safety systems are functional and there were no ECCS system actuations. At this time the plant is stable and the source of the fire was an electrical transformer which feeds the alternate electrical power supply to a Division 2 inverter isolation logic." Plant operation was not impacted and the plant continues to operate at about 95% power. The first responder on-site extinguished the fire with a hand held fire extinguisher at about 1339 local time. The licensee has informed the NRC Resident Inspector. * * * UPDATE AT 1758 EDT ON 4/7/07 FROM F. SCHILL TO P. SNYDER * * * The Emergency Action Level (EAL) entry condition for the Alert was a 'report by plant personnel of visible damage to equipment contained in a safe shutdown building' EAL 9.2.A.1. The equipment damaged was the backup power supply to the inverter. CGS has a fire watch established in the area to watch for reflash. * * * UPDATE AT 2024 EDT ON 4/7/07 FROM F. SCHILL TO P. SNYDER * * * The Alert condition was terminated at 1721 PDT based on the fact that no reflash was seen by the fire watch, the extent of the equipment damage is understood and the area is now cool. Notified: R4DO (Cain), NRR EO (Haney), IRD Mgr. (Blount), R4 (Gwynn), DHS (Akers), FEMA (Sweetser), USDA (Jimenez), HHS (Dalziel), EPA (Natl. Resp. Cntr. - Crews). | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 4 | WA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-04-07
43289 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-04-06 16:00 | 2007-04-06 19:01 | 2007-04-06 | OFFSITE NOTIFICATION - SPILL OF MOLYBDATES FROM CCW. "This is a non-emergent event. "At 1600 EDT, Unit 5 (conventional Co-Generation plant) reported to Florida state agencies a spill of their Closed Cooling Water due to a failure of a system valve. The magnitude of the spill was approximately 2500 gal of cooling water which contained Molybdates. The water was contained in the site's normal drain system. "Agencies notified: Florida State Warning Point Florida Department of Environmental Protection - District Florida Department oh Environmental Protection - District Citing Office "The actual event occurred at 0822. Turkey Point Control Room was informed of the notification at 1610." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-04-06
43288 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-04-04 | 2007-04-06 12:27 | 2007-04-06 | IMPROPER APPLICATOR LENGTH LEADS TO WRONG DOSE "St. Vincent Hospital, (Green Bay, Wisconsin) notified [the state of Wisconsin] of a medical event by telephone, on April 5, 2007. The medical event occurred on April 4, 2007 and involved an HDR unit. Initial information indicated an incorrect length of catheter was used during the treatment. A [state] inspector was dispatched to the facility on April 6, 2007. "On April 4, 2007, a patient was scheduled for a single-fraction interstitial treatment using a Varian Vari-Source HDR unit containing 6.24 Curies of Iridium-192. The patient was to receive 900 centigray to the vagina. An incorrect applicator length (100 cm) was input into the treatment plan. The actual applicator length was 120 centimeters. The source is believed not to have entered the patient's body during treatment. The authorized user and the patient were notified, and the patient will return for retreatment on April 12. The licensee is performing their own investigation into the event, including a reenactment of the event." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-04-09
43287 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2007-04-06 | 2007-04-06 16:58 | 2007-04-06 | CERTAIN MODEL 1152 PRESSURE TRANSMITTERS MAY LEAK ABOVE 2000 PSI PROCESS PRESSURE Model 1152 pressure transmitters shipped to facilities between June 12, 2006 and December 20, 2006 may exhibit leakage from a threaded connection interface between the flange and the vent/drain valve seat if subjected to a process pressure greater than 2000 psi. Consequently, performance to published hydrostatic test specifications, or sealing at the maximum working pressures above 2000 psi cannot be assured. The following potentially affected utilities were identified: Ameren UE, Alabama Power Co., Detroit Edison Co., Dominion, Entergy, Exelon Generation Co., First Energy Corp., FPL Duane Arnold LLC, Georgia Power Co., Nuclear Management Co., Omaha Public Power District, Pacific Gas and Electric, Pennsylvania Power and Light Co., Progress Energy Florida Inc., South Carolina Electric and Gas, and Tennessee Valley Authority. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2007-04-06
43286 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2007-01-11 12:11 | 2007-04-06 14:50 | 2007-04-06 | INITIATION OF INVALID PRIMARY CONTAINMENT ISOLATION SIGNALS "This is not an L.E.R. The report is being made to the NRC under 10 CFR 50.73(a)(2)(iv)(A), and the 60 day telephone notification option under 10 CFR 50.73(a)(1). The event included invalid 'general containment isolation signals affecting containment isolation valves in more than one system' as discussed in 10 CFR 50.73(a)(2)(iv)(B). "(a) 'The specific train(s) and systems that were actuated.' "On January 11, 2007 at 12:11 hours, Unit 2 received invalid Primary Containment Isolation signals to both Group 5 (RHR Shutdown Cooling System Isolation valves) and Group 10 (Reactor Core Isolation System Isolation valves) during instrumentation surveillance testing. While performing testing of the Division I Group 5 and Group 10 isolation functions of the RHR ambient temperature instrumentation, Technicians omitted a procedural step, resulting in the invalid signal actuations. "(b) 'Whether each train actuation was complete or partial.' "The event resulted in closure of the RCIC steam supply header outboard containment isolation valve. The Division 1 RHR Shutdown Cooling System isolation valves were already closed at the time of the isolation signal. "(c) 'Whether or not the system started and functioned as designed,' "The Primary Containment Isolation instrumentation logic and associated valve closure function (for RCIC) actuated as designed. The reporting of this event exceeds the 60 day notification requirement as a result of initially not fully understanding the impact of the invalid signal actuation. This condition has been entered into the Corrective Action Program." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2007-04-06
43285 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2007-04-06 11:11 | 2007-04-06 11:59 | 2007-04-06 | MAIN GENERATOR TRANSFORMER EXPLOSION - NO IMPACT ON PLANT SAFETY RELATED SYSTEMS At 1143 on 4/6/07 the licensee declared an Unusual Event due to a main transformer explosion in the protected area. The event was declared in accordance with EAL 8.2.2. Unit 3 automatically tripped due to a load reject at the main generator. The Unit is currently stable at normal operating temperature and pressure. Decay heat is being removed via the steam dumps to the main condenser. All emergency diesel generators are available if needed but safety buses are currently supplied with offsite power. At the transformer site the deluge system actuated and the fire brigade responded. The fire was out at the time of the report The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1232 ON 4/6/07 FROM LAUGHLIN TO HUFFMAN * * * The offsite local fire department was called by the licensee but their support was not needed and they were released. * * * UPDATE AT 1259 ON 4/6/07 FROM LAUGHLIN TO HUFFMAN * * * The licensee exited Unusual Event at 1247 based on the fact that the fire was confirmed to be extinguished, there was no damage to safety equipment and the plant was in a safe and stable condition. * * * UPDATE AT 1440 ON 4/6/07 FROM PRUSSMAN TO KNOKE * * * "On April 6 at 1143 hours, an unusual event was declared based on Emergency Action Level 8.2.2, an explosion in the 'B' phase of the 31 main transformer. This is a one hour reportable event to the NRC made at 1159 hours. This is an update of EN 43285. The NUE was terminated at 1247 hours. "The State and County were also notified of the unusual event. A press release was made. Although no one was injured as a result of this event, a four hour report is being made since this is related to on-site personnel safety. The main generator tripped and this resulted in a consequential reactor trip. The Reactor Protection System shut down the reactor at 1109 hours, a four hour report. The plant operated as designed and the Auxiliary Feedwater System actuated, an eight hour report. The fire was reported to the Control Room at 1111 hours. The fire was put out in less than 15 minutes. "The event is currently under investigation." The header information in this event was revised as a result of this update to indicate 'Offsite Notification.' | 0 | 0 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) |  | 0 | 2007-04-06
43284 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2007-04-05 12:00 | 2007-04-06 11:20 | 2007-04-06 | ILLINOIS AGREEMENT STATE REPORT Pinnacle Food Group located in St. Elmo, IL reported that between March 13 through 20, 2007 they were performing general maintenance for the up coming canning season. After the cleanup they discovered that a Industrial Dynamics Model FT50 fixed gauge containing 100 millicuries of Am-241 used for fill level measurements was taken as scrap metal to either Grossman Iron & Steel or PSE Metals which are both located in St. Louis, MO. These scrap metal yards were both notified on 04/05/07 by Pinnacle Food Group that their scrap yard may have the missing gauge in their yard. Pinnacle Food Group has hired a consultant and he arrived at the scrap yards on 04/06/07 and he is looking for the missing gauge. So far no contamination has been detected in either scrap yard. IL. Incident # IL-070020. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-04-11
43283 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-04-04 15:14 | 2007-04-05 08:36 | 2007-04-06 | UNAUTHORIZED ACCESS GRANTED. IMMEDIATE COMPENSATORY MEASURES TAKEN UPON DISCOVERY. Contact HOO for further details. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-04-06
43282 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2007-04-05 | 2007-04-05 21:22 | 2007-04-06 | POTENTIALLY CONTAMINATED PERSON WITH A BACK INJURY TRANSPORTED TO LAKE EAST HOSPITAL "At 2005, an injury occurred to a worker when the individual fell and injured his back. At 2122, the worker was attended by local Emergency Medical Personnel who transported the individual to our local Hospital. Due to his back injury his back will not be able to be completely monitored until arrival to the hospital. The individual is being classified as potentially contaminated. Radiation [Protection] personnel are accompanying the victim on the ambulance and to the local hospital emergency room to aid in radiological assessment. "Due to our procedures we will be making notifications to the State Of Ohio and the local county Emergency Management Agencies of the incident. Due to the offsite notifications a 4 hour non-emergency call is required." The individual was a contractor onsite for outage support. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2249 ON 4/5/07 FROM A. RABENOLD TO SNYDER * * * "The contractor individual was found in the Containment Drywell 630 foot elevation. He fell off of scaffolding approximately 4-5 feet to the grating. When the medical personnel arrived at the scene they found him unconscious. He regained [consciousness] when medical personnel arrived at the scene. "At 2218 [the licensee received a] report from Radiation Protection personnel that the individual was not contaminated." Notified R3DO (L. Kozak). * * * Update on 04/06/07 at 1130 EDT from M. Nemcek to MacKinnon * * * The injured person was found not to have contamination on him but it was reported to Perry Nuclear Power plant that fixed contamination was found on his Protective Clothing (PC), Safety Belt and Tool Belt. Fixed contamination on the PC direct contact reading was between 100 to 150 cpm. Fixed direct on contact contamination on the Safety Belt & the Toll Belt was between 100 to 500 cpm. No contamination found in the ambulance or in the Hospital. NRC Resident Inspector was left a message of this information by the licensee. NRC R3DO (L. Kozak) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0 | 2007-04-05
43281 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2007-04-05 10:23 | 2007-04-05 15:23 | 2007-04-05 | OFFSITE NOTIFICATION - ALERT DECLARED DUE TO REPORT OF A FIRE IN THE CONTROL BUILDING "At 1023 on April 5, 2007, an ALERT was declared because of a control room alarm and local report of a fire at transformer XPN08A. There was a possibility of affecting safety related equipment. Investigation at the scene did not reveal evidence of an active fire. Smoke and a red glow in the back of the transformer was observed. The transformer has been isolated from the bus and power supply. "There was no evidence of equipment damage other than to the affected transformer. Areas adjacent to the transformer room were checked for fire, with no evidence of fire. The ALERT was closed out at approximately 1115. "The NRC Resident Inspector was informed. State, local and other government agencies were informed of the event declaration. A press release was issued. "NOTE: initial notification of the ALERT was made to the NRC (HOO) at 1040 CDT. (See EN43279)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-04-05
43280 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-04-05 09:08 | 2007-04-05 14:01 | 2007-04-05 | AUTOMATIC REACTOR TRIP CAUSED BY SPURIOUS SAFETY INJECTION DURING TESTING "At 09:08 am on 4/5/2007, during surveillance testing of Unit 2 Train A safeguards logic at power, a spurious Train A safety Injection (SI) actuation occurred resulting in reactor protection system (RPS) actuation. Train A SI was in "Test" at the time and should not have caused the RPS trip. The operating crew manually actuated Train B SI as required by emergency operating procedures. All automatic actions for a reactor trip and safety Injection occurred as required. Reactor Coolant System (RCS) pressure decreased below the shutoff head of the high head Emergency Core Cooling System (ECCS) pumps during the transient, resulting in momentary ECCS discharge to the RCS. SI has been terminated per emergency operating procedures. "Prairie Island Unit 2 has been stabilized in mode 3, at about 2235 psig and 547 degrees average RCS temperature. Decay heat Is currently being removed by auxiliary feedwater and secondary steam dump to the main condenser. The cause of the actuation signal is under investigation. All control rods fully inserted. No primary power operated relief valves or safety valves lifted. No steam generator safeties lifted. Safeguards buses are powered by offsite power. The Unit 2 Emergency Diesel Generators (EDG) started but did not load. "Unit 1 Control Rod Drive Mechanism cooling isolated as designed in response to the actuation and has since been restored. Otherwise, Unit 1 was unaffected and remains in mode 1 at 100% power." The licensee notified the NRC Resident Inspector. The licensee will also be notifying the State, local and other Government agencies and will be issuing a press release. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2007-04-05
43279 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2007-04-05 10:23 | 2007-04-05 11:38 | 2007-04-05 | ALERT DECLARED DUE TO A FIRE IN THE CONTROL BULDING At 1023 Central Daylight Time the licensee declared an Alert due to a transformer fire in the non-safety related PN08 transformer phase 'A.' There were no visible flames seen by onsite licensee personnel but an area of the transformer was glowing with a smokey haze in the area. The fire brigade responded. The plant was already in a shut down condition entered on 4/1/07 for a refueling outage. Decay heat was being removed using Residual Heat Removal the train 'B.' The licensee declared the alert based on a potential impact to the operating Residual Heat Removal train. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1215 ON 4/5/07 FROM LICENSEE COMMUNICATOR TO SNYDER * * * The licensee exited the Alert condition at 1215 Eastern Daylight Time based on their assessment that no impact to operating safety related RHR equipment occurred and any impact would have been conservative in that flow to the core would not have been interrupted. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | ALERT | 4 | MO | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-04-05
43278 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2007-04-05 07:30 | 2007-04-05 07:59 | 2007-04-05 | SECURITY DEGRADATION Uncompensated degradation in a security system that could allow unauthorized access to the protected area. Immediate compensatory measure taken upon discovery. Call the Headquarter Operations Officer for further details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-04-05
43277 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2007-04-02 13:30 | 2007-04-04 19:43 | 2007-05-07 | AGREEMENT STATE REPORT - FIXED LEVEL GAUGE SOURCE FAILURE TO RETRACT The following information was reported to the NRC via facsimile: The Utah Division of Radiation Control was initially notified by telephone on April 3, 2007 at about 10:20 am MST by the licensee's consultant that a source of a fixed level gauge at the Hunter Power Plant near Castle Dale, Utah failed to retract into the safe shielded position. The gauge is a Texas Nuclear Model 5197, Serial Number 1305 level gauge containing 100 millicuries of Cs-137. The licensee contacted their service consultant who discovered that the handle on the gauge was bent. The consultant indicated that it appeared that someone had attempted to turn the handle on the gauge without pulling the button. This act had apparently bent the handle. When the licensee had attempted to close the device properly, the bent handle did not allow the drive cable to align properly with the source to retract it. This incident is being tracked by the State as Utah Report ID No. UT-07-0002. * * * UPDATE AT 1320 EDT ON 5/7/07 FROM GWYN GALLOWAY TO S. SANDIN * * * The State of Utah representative called to correct the incident date from March to April. Notified R4DO (O'Keefe) and FSME (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2007-04-09
43276 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-02-25 03:58 | 2007-04-04 14:01 | 2007-04-04 | INVALID SECONDARY CONTAINMENT ISOLATION "The following information is provided as a 60 day telephone notification to NRC under 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of the 10CFR50.73(a)(2)(iv)(B) [general containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves]. NUREG1022 Revision 2 identifies the information that needs to be reported as discussed below. "(a) The specific train(s) and system(s) that were actuated. "This report is being made under 10CFR50.73(a)(2)(iv)(a). On February 25, 2007 at 3:58 AM EST Units 1 and 2 received an invalid full Secondary Containment Isolation. The following initiations and isolations were observed: All Fission Product Monitor Valves isolated, both Units' SBGT trains initiated and the reactor building ventilation supply and exhaust fans tripped and isolated, and the refueling floor ventilation supply and exhaust fans tripped and isolated. Operations personnel verified that all Secondary Containment isolations and initiations occurred as expected. "The isolation was caused by a blown fuse. During investigation into the Secondary Containment isolation, fuse 1D11A-F14A in panel 1H11-P606 was found to be blown. After replacing this fuse, the isolation signal cleared and all related systems were returned to normal operation. Fuse 1D11A-F14A supplies the trip auxiliary units 1C51A-Z2A and 1C51A-Z2C. Loss of power to these units de-energizes several relays which are also deenergized as a result of a Refueling Floor Vent High Radiation signal which would actuate the same isolation logic and cause an SBGT initiation. "(b) Whether each train actuation was complete or partial. "The four Standby Gas Treatment (SBGT) fans auto started and both Unit One and Unit Two reactor building and refueling floor normal ventilation systems automatically shutdown and isolated. The SBGT initiation and the ventilation system shutdown were both complete actuations. "(c) Whether or not the system started and functioned successfully. "The above system functioned successfully." The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-04-04
43275 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-04-03 | 2007-04-04 12:02 | 2007-04-04 | AGREEMENT STATE REPORT - STOLEN PALLADIUM SEEDS The State of Louisiana received a report from a licensee representative that 101 Palladium 103 seeds, with a total activity of 132 millicuries, were stolen. The seeds were stolen from a truck at 2235 Highway 178 in Sunset, LA. The seeds had been accepted by the licensee from the shipper and were going to transported to the hospital by the licensee representative. The licensee notified the Louisiana State Police and local law enforcement and is following up on the incident. * * * UPDATE ON 4/4/07 AT 1630 EDT FROM PATE TO SNYDER * * * The following information was received via e-mail from the State of Louisiana: At the time of the theft the truck was parked at the residence of the licensee's Radiation Safety Officer (RSO). The RSO contacted the St. Landry Parish Sheriff and the Louisiana State Police. The seeds were in the vehicle on the rear seat inside a red, padlocked, metal tool chest labeled as radioactive material. The approximate dimensions of the tool chest are 1.5 to 2 feet long and 8 to 10 inches wide. The seeds were contained in seven plastic sleeves that were attached to the inside of one stainless steel container that was inside another stainless steel container. Louisiana Department of Environmental Quality has dispatched three inspectors out to search the area where the sources were stolen with instrumentation. "If the Palladium sources were piled together outside of their shielded containers, this would result in a radiation exposure roughly 16.6 [millirem/hour] at one foot. "[The RSO] has stated that the facility will be notifying the public by television and newspapers." Notified R4DO (C. Cain) and FSME EO (D. Rathbun). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-04-09
43274 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2007-04-01 | 2007-04-03 18:05 | 2007-04-03 | SEVERAL CHECK SOURCES STOLEN FROM A UTILITY TRAILER The following information was received via e-mail from the State of New Mexico: "[NM Radiation Protection Control Bureau] received notification at approximately 2:30 p.m. that seven (7) sets of button check sources licensed to the NM Radiation Control Bureau were being stored in a NM Department of Health utility trailer that was stolen in Albuquerque, NM over the weekend. These sources are used as check sources for survey meters (also stolen) during training sessions for emergency response personnel at facilities along the WIPP routes in NM. This incident is being investigated by NM State Police and the Albuquerque Police Department. Personnel from the Department of Homeland Security, the NM Department of Health, and the WIPP Emergency Response Program of the NM Radiation Control Bureau are also involved in the investigation and will provide a press release. The following sources were reported missing: 7-10 nanoCurie Pu-239 7-10 nanoCurie Sr-90 (exempt) 7-1 microCurie Cs-137 (exempt) "More details will be provided as they become available." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2007-04-06
43273 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-04-03 16:00 | 2007-04-03 18:49 | 2007-04-03 | TROXLER GAUGE DAMAGED DURING FIRE At approximately 1600 hours, a propane tank at a construction site located at 15136 Rutan Lane in Charlotte, NC exploded. The resulting fire fully engulfed a pickup truck containing a Troxler moisture density gauge. NC Radiation Protection was informed at 1703 hours by NC Emergency Management of the incident and has dispatched an Inspector to the scene to assist Hazmat. The initial radiation readings provided by Hazmat show preliminary readings of .3 mr/hr (not sure whether this is contact or near the gauge). * * * UPDATE PROVIDED BY LEE COX TO JEFF ROTTON AT 2205 ON 04/03/07 * * * The North Carolina Radiation Protection Inspector is onsite at the scene of the explosion. The truck was damaged beyond repair and the Inspector was able to locate both gauge sources with survey instruments. The Troxler gauge is a model 3440 with a 40 millicurie Am-241:Be source and a 8 millicurie Cs-137 source. Both sources were located in the bed of the truck. The Am-241 source was outside the gauge housing and the Cs-137 source was still attached to the source handle/rod. Neither source was breached. The Inspector was able to use various retrieval instruments to pickup both sources and place them into a temporary transportation package created on the scene and use available material for shielding and packaging to secure the sources. The temporary transportation package was secured in the bed of a truck with a cab over the truck bed. Radiation readings in the cab of the truck and on the sides of the truck bed were background. Radiation readings at a distance of 1 meter from the package was < 2 mR/hr. The radiation reading on contact was 15 mR/hr. The truck with the damaged Troxler gauge was escorted by the NC Radiation Protection Inspector to the South Carolina licensee's site located at 3575 Center Circle, Fort Mill, SC 29715, South Carolina License # -777. The gauge manufacturer, Troxler, was contacted and will be sending a DOT approved transportation container so that the licensee can return the damaged gauge to the manufacturer. NRC Region 1 (Kinneman) and the State of South Carolina were notified by the North Carolina Radiation Protection Office. Notified R1DO (Gray) and FSME EO (Rathbun) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-04-06
43272 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2007-04-03 04:16 | 2007-04-03 05:07 | 2007-04-03 | MANUAL REACTOR TRIP WHILE PERFORMING BOILER FEED PUMP MAINTENANCE "The Indian Point Unit 3 reactor was manually tripped at 04:16 on 4/3/2007 due to low steam generator levels that occurred while the 31 MBFP [main boiler feed pump] speed control was being isolated for maintenance. Indian Point Unit 3 is currently in mode 3 with all automatic actions for a manual reactor trip occurring as required. Unit 2 was unaffected and remains in mode 1 at 100% power." The reactor was manually tripped when steam generator levels reduced to 18% in all four steam generators. All rods inserted on the trip. No safety or relief valves lifted due to the trip. The motor driven aux feedwater pumps automatically started on low steam generator level and are being used to maintain steam generator level. Atmospheric steam dumps are maintaining reactor temperature. The Unit 3 electrical lineup is the normal shutdown electrical lineup. The licensee has notified the state Public Service Commission. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-04-03
43271 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-04-02 11:25 | 2007-04-02 12:48 | 2007-04-02 | MANUAL REACTOR SCRAM DUE TO LOWERING REACTOR VESSEL WATER LEVEL "This report is being made under 50.72(b)(2)(iv)(B) for inserting a manual scram due to lowering reactor pressure vessel level. The lowering level resulted from a loss of non-essential 4160 VAC bus 1A2 and subsequent loss of 'B' Reactor Feed Pump. "In addition this report is being made under 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any systems listed in paragraph (b)(3)(iv)(B) of this section due to PCIS groups 2, 3, and 4 being received when reactor water level dropped below 170". All isolations went to completion. The reactor water level drop is normal following a scram from full power due to void collapse in the reactor vessel. "After the initial scram, vessel level rose to 211" causing the 'A' Reactor Feed Pump to trip. Before a Reactor Feed Pump could be restarted and adequate feed flow established, another scram signal and isolation occurred when vessel level dropped below 170". Control rods were already fully inserted and isolation valves in the isolated condition when this occurred. Reactor water level was restored to normal and the PCIS group isolations were reset. "The current plan is to remain in Hot Standby (Mode 3) and determine the cause of the loss of 1A2 non-essential 4160 VAC bus." The licensee informed the NRC Resident Inspector. * * * UPDATE PROVIDED BY MIKE DAVIS TO JEFF ROTTON AT 1621 EDT ON 04/02/07 * * * "This update is being added to clarify that the second scram on 170 " vessel level described in the original report also constituted a 50.72 (b)(3)(iv)(A) reportable event." The licensee notified the NRC Resident Inspector. Notified R3DO (Kozak) | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-04-02
43270 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-03-30 | 2007-04-02 12:30 | 2007-04-02 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE "On March 30, 2007, in Dallas, TX, during a torrential rainstorm, the driver of a truck carrying radioactive material slammed into the guardrail of a bridge. The driver, who is the Radiation Safety Office for the company, was thrown from the truck and hospitalized. The moisture density gauge (Troxler Model 3450, S/N 544) transport case was thrown from the truck and fell [approximately] 40 feet to a service road where the transport case broke apart and the gauge ended up on the side of the road. The next morning the Dallas Fire and Rescue Department (DFD) was alerted that a nuclear gauge had been transported in the truck and was unaccounted for. Once the gauge was sighted and radiation symbols identified, DFD closed the service road and called in an environmental firm for assistance. Four hours later the Agency was notified by DFD via the Agency's answering service. DFD personnel suited up and retrieved the gauge. The gauge was found to be undamaged except for a broken display. The two sources in the gauge (40mCi, AmBe-241, S/N47-28488 and 8mCi, Cs-137, S/N750-7116) were still retracted into the body of the device and appeared undamaged. The instrument was removed to a secure location and the licensee is making arrangements for the manufacturer to retrieve and repair the unit. The investigation is on-going." TX Incident No.: I-8400 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-04-05
43269 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2007-04-01 10:45 | 2007-04-01 12:55 | 2007-04-01 | TECH SPEC REQUIRED SHUTDOWN DUE TO EDG INOPERABILITY "During post-maintenance operability testing, Diesel Generator 4 exhibited unstable power output while synchronized to the grid. This testing was being performed at the conclusion of a planned Diesel Generator 4 maintenance outage. Preventive maintenance activities included in this scheduled outage included replacement of various relays in the Diesel Generator control logic and replacement of the engine governor. "Brunswick Nuclear Plant Unit 1 is commencing a unit shutdown as required by Technical Specification 3.8.1 Condition H due to the inoperability of Diesel Generator 4 lasting longer than seven (7) days. TS 3.8.1 Required Action H.1 requires Unit 1 to be in MODE 3 by 1615 on 4/1/2007 and in MODE 4 by 1615 on 4/2/2007. This event is reportable per 10CFR50.72(b)(2)(i). "Power reduction was commenced at 1045 in accordance with station procedures for unit shutdown. Power level has been reduced from 100% to 53%. Unit 1 shutdown will continue until the unit is in MODE 4 or until the engine is declared operable following appropriate repairs and testing. "Unit 2 is in MODE 4, Cold Shutdown. The inoperable Diesel Generator 4 is not needed to meet the requirements of Unit 2 Technical Specification 3.8.2. "The inoperability of Diesel Generator 4 is of minimal safety significance for Unit 1. Unit 1 has two operable off-site circuits and three (3) Diesel Generators are operable. The remaining three (3) operable Diesel Generators and off-site circuits are adequate to supply electrical power to the on-site Class 1 E Distribution System. This maintains the safety function of the AC sources. Unit 1 is being shutdown to place the unit in MODE 4 where the inoperable Diesel Generator 4 is not required. Unit 2 is currently in MODE 4 and does not require Diesel Generator 4 to be operable. As such, this event is of zero safety significance for Unit 2. "During post-maintenance operability testing, Diesel Generator 4 exhibited unstable power output while synchronized to the grid. Station engineering and a vendor representative continue to evaluate the engine/generator performance. Repair plans will be developed and implemented as appropriate following completion of the engineering evaluation." The inoperability of Diesel Generator 4 will prevent Unit 2 from changing mode for returning the plant to service. The licensee notified the NRC Resident Inspector. | 53 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-04-01
43268 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2007-03-30 10:30 | 2007-03-30 16:24 | 2007-03-30 | SAFETY EQUIPMENT FAILURE - PROCESS GAS LEAK DETECTION SYSTEM "At 1030, on 3-30-07 the Plant Shift Superintendent was notified of the failure of the C-333A Process Gas Leak Detection (PGLD) detector head YE-613-21. Detector head YE-613-21 is located in the piping trench between the autoclaves. The trench detector heads are scheduled to be replaced at a six month interval. Operators were performing an "as-found" test on the head prior to scheduled replacement. The detector head did not alarm as required when smoke was applied during the test. The Process Gas Leak Detection system is required to be operable according to TSR 2.2.4.1. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(l). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function." The YE-613-21 detector head was replaced approximately 6 months ago and was last known to be functional approximately one month ago after some wiring tests were conducted in the area of the detector head. The permittee is conducting failure cause analysis to determine failure mode and possibly identify when failure occurred. The NRC Senior Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-07-0819; PGDP Event Report No. PAD-2007-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2007-03-30
43267 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2007-03-30 07:40 | 2007-03-30 14:40 | 2007-03-30 | CRITICALITY WARNING SYSTEM ALARM ACTUATION DUE TO POWER FLUCTUATION "At approximately 0740 on 3/30/2007, a segment of the inside Criticality Warning System (CWS) covering the Fuel Manufacturing Operation (FMO) failed due to an apparent voltage fluctuation in the power supply to the system. The fluctuation resulted in activation of the CWS evacuation alarm. "All personnel promptly evacuated the facility and the emergency organization assembled in accordance with normal procedures. A total of 5 out of 6 FMO CWS Data Acquisition Modules (DAMS) were affected by apparent power supply fluctuation. Two additional DAMS, which are independent, continued to provide coverage of the Dry Conversion Process (DCP) process areas. "The Emergency Director determined that the processes should stay shut down and all personnel not engaged in troubleshooting or recovery actions remain out of the area while investigations and additional testing was conducted. Follow-up tests replaced select hardware, and installed additional power supply monitoring equipment to aid diagnostics. All DAMS have been successfully reset and the inside FMO CWS system returned to normal operation. "Current plans are to resume normal operations beginning with the 1500 (evening) shift. "The event is being reported within 24-hours pursuant to 10CFR70.50(b)(2) as a safety equipment failure." The licensee will also be providing a courtesy notification to the North Carolina Department of Radiological Protection and the New Hanover County Emergency Management organization. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2007-03-30
43266 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2007-01-12 | 2007-03-30 10:30 | 2007-03-30 | PART 21 - ROSEMOUNT PRESSURE TRANSMITTER MAY NOT BE SEISMICALLY QUALIFIED "During routine operations on the RNII production floor, it was observed that an incorrect torque wrench was being used at mechanical assembly to tighten the Sensor Module Lock Nut. The incorrect tool was calibrated to a value of 12.5 ft-lb, resulting in undertorquing of the lock nut. The incorrect torque wrench was removed from service and replaced with a tool calibrated to the correct torque value of 35 ft-lb. RNII reworked all affected transmitters that had not yet shipped to the correct torque value. "Assembly with the incorrect tool could result in certain pressure transmitters having a degraded environmental seal between the sensor module and the electronics housing during or after a seismic event." The five affected models have been delivered to the Byron and Comanche Peak nuclear stations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2007-03-30
43265 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2006-05-31 | 2007-03-29 12:48 | 2007-03-30 | MEDICAL EVENT - PATIENT RECEIVED DOSE GREATER THAN PRESCRIBED "The possible medical event occurred at a broad-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. "The permittee is VA Eastern Colorado Health Care System, Denver, Colorado. The possible medical event occurred on May 31, 2006. The possible medical event was discovered on March 28, 2007. "The basis for the possible medical event is under 10 CFR 35.3045(a)(1)(i) and involved administration of a dose different from the dose prescribed in the written directive. "Specifically, the written directive for a patient therapy procedure listed the dose to be 15 millicuries Iodine 131 when in fact 30 millicuries was given to the patient. Since the clinical intent was for the patient to receive 30 millicuries, the possible medical event will not have any adverse impact on the patient. "The permittee has implemented corrective actions to prevent a recurrence of the circumstances that resulted in the possible medical event. "The Department of Veterans Affairs will evaluate the circumstances related to the possible medical event and submit a written report to NRC, Region III, within 15 days." * * * UPDATE ON 3/30/2007 AT 0720 FROM FLANNERY (NRC/FSME) VIA E-MAIL TO ABRAMOVITZ * * * This event has been reviewed and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | AR | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-03-30
43264 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2007-03-29 09:00 | 2007-03-29 12:08 | 2007-03-29 | OFFSITE NOTIFICATION TO LOCAL LAW ENFORCEMENT Licensee requested offsite assistance from local police department. Contact Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-03-29
43263 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2006-05-03 12:00 | 2007-03-29 11:37 | 2007-03-30 | AGREEMENT STATE REPORT FROM OKALAHOMA - HIGHER DOSE THAN PRESCRIBED This event took place between 05/03/06 and 03/27/07 and involved ten patients during this time period being treated for prostate cancer using Iodine-125. Kay County Hospital LLC (formally known as Via Cristi Hospital) had changed from ordering I-125 doses in Air-Kerma to millicuries. During the time period from 05/03/06 to 03/27/07 they used the incorrect dose count. This caused each of the ten patients to receive a dose 27 percent higher than the written directive. This did not pose any harm to the patients. The error was discovered on 03/28/07 by a newly hired Medical Physicist. The licensee is in the process of notifying the affected patients. The licensee will also being working with the software vendor to develop better training and procedures for the performance of dose calculations to prevent reoccurrence. * * * UPDATE ON 3/30/2007 AT 0720 FROM FLANNERY (NRC/FSME) VIA E-MAIL TO ABRAMOVITZ * * * This event has been reviewed and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-03-30
43262 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-03-28 13:41 | 2007-03-28 17:39 | 2007-05-24 | HPCI INOPERABLE DUE TO SURVEILLANCE TEST FAILURE "During the running of the HPCI operability, STP 3.5.1-05, the discharge relief, PSV 2302, lifted and failed to reseat. The relief valve discharges to the Torus Area floor and was captured in the floor drain sump system. The STP was aborted and the HPCI system was declared inoperable. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 05/24/07 AT 1302 EDT BY ROBERT MURRELL TAKEN BY MACKINNON * * * "The purpose of this notification is to retract a previous report made on 3/28/07 at 1739 (ET) (EN 43262). Notification of this issue to the NRC on 3/28/07 was initially made as a result of declaring HPCI inoperable during the running of the HPCI operability, Surveillance Test Procedure (STP) 3.5.1-05. HPCI was declared inoperable when the discharge relief, PSV 2302, lifted and failed to reseat. The relief valve discharges to the Torus Area floor and was capture in the floor drain sump system. The STP was aborted and HPCI system was declared inoperable. "Since the initial report, Engineering had determined that the HPCI system was capable of performing its safety function. "Engineering concluded that the stuck open HPCI discharge pressure relief valve would not have prevented HPCI from fulfilling its design function of providing adequate high pressure makeup to the reactor vessel. Existing operating procedure guidance would have ensured that HPCI injection would not have been terminated in the event it was needed under accident conditions, even with PSV2302 stuck open. Operating procedure guidance and Reactor Building floor drain sump pump capacity are adequate to prevent a flooding concern. "This event is not considered a Safety System Functional Failure and is not reportable to the NRC as a Licensee Event Report (LER) per 10 CFR 50.73." The NRC Resident Inspector was notified of this retraction by the licensee. R3DO (Richard Skokowski) notified. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-03-28
43261 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2007-03-27 | 2007-03-28 16:44 | 2007-03-28 | AGREEMENT STATE - GEORGIA - DAMAGED DENSITY GAUGE The State provided the following information via email: "Nova personnel had placed the portable density gauge on the tailgate of the truck and drove off prior to secure the gauge to the truck bed. The Radiation Safety Officer (RSO) of Nova was notified of the incident and responded to the scene. The RSO stated the gauge case had broken apart and the circuit board on the gauge had been damaged. He had surveyed the source rod and source and based on the measurements determined the source rod to be intact and the source not leaking. The fire department and the County had the area secured until it was determined the gauge could be packed up and removed from the road. The RSO stated he would send the gauge to Regis [a gauge repair firm] for either disposal or repair. " Georgia Report GA-2007-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2007-04-02
43260 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-03-28 10:00 | 2007-03-28 11:44 | 2007-03-28 | AGREEMENT STATE REPORT - INCORRECT DOSE TO PATIENT DURING I-131 BEXXAR THERAPY "Mis-administration while performing l-131 therapy. Procedure is called a [Bexxar] Therapy. 74 mCi was prescribed, but the patient received only 5 to 10 mCi. T connector to catheter was not properly fitted tight enough causing connector to come loose from tubing. Some 1-131 spilled on floor. Incident happened on 28-March-2007 at 10:00 am this office notified at 11:10 am. This incident is referred to Radioactive Materials for investigation." The patient and the prescribing physician are aware of the dosing error. The licensee plans to conduct another procedure 3/30/07. The state will follow up with the licensee on this incident. This incident is being tracked as Florida incident number FL07-054. * * * UPDATE FROM FLANNERY (NRC/FSME) VIA E-MAIL TO HUFFMAN AT 1530 EDT ON 3/28/07 * * * This event has been reviewed and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-03-31
43259 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2007-03-27 20:50 | 2007-03-28 01:51 | 2007-03-28 | LOW STEAM GENERATOR WATER LEVEL INITIATED AUXILIARY FEEDWATER SIGNAL AND A REACTOR TRIP SIGNAL "This 8-hour notification is being made to report that an Auxiliary Feedwater (AFW) system actuation signal was generated and a Reactor Protective Signal (RPS) generated with the reactor subcritical. "On March 27, 2007 at approximately 2050, Salem Unit 1 was in Mode 3 following a planned manual reactor trip to begin a scheduled refueling outage. Operators had established initial Reactor Coolant System cooldown using the steam dumps for heat removal and the 11, 12, and 13 AFW pumps for steam generator make-up. All three pumps had been previously placed in-service in accordance with plant procedures. As plant cooldown proceeded, narrow range levels in 11, 12, and 13 Steam Generators reached the low steam generator setpoint trip, resulting in a valid ESF actuation (i.e., start signal to the AFW pumps); however all AFW pumps were already in-service. "The actuation signal also generated a reactor trip signal to be initiated by the reactor protection system; however, the plant was already in a shutdown condition with the reactor trip breakers open. "The lowest level during this transient occurred in 13 Steam Generator and was 11.3% narrow range level. Steam generator water level was restored to a normal value and the RCS cooldown recommenced. There were no equipment failures that contributed to this event. "The NRC Resident has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-03-28
43258 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-03-19 | 2007-03-27 17:52 | 2007-04-02 | AGREEMENT STATE - CALIFORNIA - MEDICAL MISADMINISTRATION The State provided the following information via facsimile: "On March 16, 2007, the licensee initiated a 'Mammosite' treatment of a patient, with a total prescribed dose of 3400 cGy (3400 rad) to be delivered in 10 fractions of 340 cGy (340 rad) each, over the course of 5 days, using a Nucletron, Model 105.999 HDRA with 4.1 Ci Ir-192 (as of the first day of treatment). The first five fractions were delivered uneventfully. During the last five fractions, the radiation therapy technologist accidentally imported the wrong treatment plan, resulting in an underdose to the treatment area. The dwell position of the source was actually fully outside of the patient, so the tumor received effectively no dose. The licensee is calculating the skin and whole body dose to the patient, but currently estimates it will not have an adverse affect upon the patient. The patient and referring physician have been notified, and re-treatment has been scheduled to begin tomorrow. This event was discovered upon review of the patient's chart when the patient returned for a follow-up exam. The licensee will provide a written report of the event within 15 days." CA Report #032707 * * * UPDATED 1346 EDT ON 4/2/07 FROM CYNTHIA FLANNERY (FSME) * * * "This event has been reviewed by FSME and found to be a medical event." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-03-30
43257 | -1 | BEST MEDICAL INTERNATIONAL, INC |  |  |  |  | 2007-03-26 11:00 | 2007-03-26 13:26 | 2007-03-28 | PERSONNEL OVEREXPOSURE ASSEMBLING PALLADIUM SEEDS On 3/26/07, the licensee's RSO received dosimetry reading (from Landauer) on employees working at his facility indicating that a worker had a deep dose exposure of 9683 mrem and an extremity dose of 9200 mrem. This exposure occurred sometime over the previous two months - the measured dose period was from 1/01/07 to 3/01/07. The individual with the potential overexposure works in the fabrication of Palladium - 103 seeds, a soft gamma emitter, used for brachytherapy treatment. The cause of the overexposure is currently unknown. The dosimetry of coworkers does not indicate overexposures. A survey of the work area shows no contamination and no previously unidentified possible sources of exposure. The worker is a female, approximately 30 years old, and does not exhibit any medical symptoms. No information on pregnancy status was available. Interviews with the individual are in progress. * * * RETRACTION ON 03/28/07 AT 1130 EDT VIA E-MAIL FROM KRISHNAN SUTHANTHIRAN TO MACKINNON * * * "We retract the statement. The initial statement was based on information from a dosimeter company without further investigation. Upon further investigation we believe this reading to be in error. Individuals normally receive between 25-30mR per month. Given the fact the isotope they work with is exclusively Pd-103 and the work is inside shielded boxes it's unlikely for them to get such exposure. Our belief at this time is that this reading is in error. We believe the individual's exposure was not higher than they received in previous months. Further, given this is Pd-103, a state (not NRC) regulated isotope, we have and will continue to report findings to the state." NRC R1DO (Anthony Dimitriadis) & FSME (Greg Morell) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2007-03-26
43256 | -1 | LANCASTER GENERAL HOSPITAL |  |  |  |  | 2007-03-23 13:00 | 2007-03-23 19:30 | 2007-03-28 | POTENTIAL OVEREXPOSURE INVOLVING BRACHYTHERAPY SOURCE At 1300 hours on 3/23/07, a male patient received I-125 seed implants for treatment of prostate cancer. The RSO received a call at approximately 1730 hours from the Radiation Oncologist Physicist who had identified that the wrong units were input into the dose planning computer. This resulted in a potential overexposure. A CAT scan is scheduled for Monday, 3/26/07, to verify source placement and more accurately calculate the overexposure. At this time, the preliminary information provided indicates a prescribed dose of 145 Gray with an estimated dose delivery of 155 Gray. The licensee does not believe that there will be any adverse effects to the patient. Following the more accurate calculation the licensee will review whether this notification meets the reporting criteria. The licensee has notified the prescribing physician of the error. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE ON 3/28/07 AT 1417 FROM MONTAGENESE TO SNYDER * * * This event is retracted by the licensee. Since the time of the original notification the licensee has established, by dosimetry readings, that the exposure was below the reporting criteria. Notified R1DO (Dimitriadis) and FSME EO (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-03-29
43255 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-03-22 08:30 | 2007-03-23 08:22 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * POSSIBLE UNANALYZED CONDITION OF MASS-MODERATOR CONTROLLED GLOVEBOX "At approximately 8:30 am on March 22, 2007, NCS [Nuclear Criticality Safety] was questioned by an NRC inspector regarding control methods for the RTRT [Research Test Reactor & Targets], HEU [High Enriched Uranium] and LEU [Low Enriched Uranium] compact press glovebox lines regarding hydraulic fluid entry into the glovebox. The glove box is a mass-moderator controlled box. Mass and moderator upset conditions were considered during the ISA [Integrated Safety Analysis] and are documented in the SAR. However, no moderator upset condition (reflecting hydraulic leak into the press box) is documented in the SAR. Moderator upset (reflecting hydraulic leak into the box) is considered in the NCS analysis supporting the SAR analysis and operation. Moderator upset was specifically evaluated, and results documented in the NCS analysis. The evaluation demonstrated the glovebox remained subcritical and below license limits even if fully flooded with hydraulic fluid. "At the time of discovery, the glovebox line was not in operation and there was no evidence of a hydraulic leak. Soon after notification, RTRT Operations removed the glove boxes from service and the press glovebox operations were subsequently locked out from use. "At this time BWXT believes this may be an unanalyzed condition in the ISA and is therefore reporting this event under 10 CFR 70, Appendix A (b)(1). BWXT continues to research the ISA documentation to determine the extent of the evaluation during the ISA. If more information is found BWXT may withdraw this notification. "BWXT has notified the NRC Resident Inspector." * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-05-11
43254 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-03-03 | 2007-03-22 12:00 | 2007-03-22 | AGREEMENT STATE - LOUISIANA - TROXLER GAUGE MALFUNCTION The State provided the following information via facsimile: "On March 5, 2007 there was a malfunction with a Troxler gauge. After performing a moisture/density test, the technician squeezed the release handle, pulled up the rod, and walked away from the test location. While walking towards the truck, an assistant told the technician that he had dropped something. When the technician looked, [he] realized that the object that had fallen was the bottom piece on the Troxler gauge rod. The technician told the assistant to stay away from the broken piece. The technician then carefully picked up the piece with a shovel from the truck and placed it on the tailgate. A brief observation of the broken rod was taken by the technician to assure that the [source] pellet was still in place and not dropped on the ground. He then noticed that the weld on the rod was the main cause of the problem. At this time the technician immediately staked out the area and called his equipment manager - a repair technician [redacted] with Gamma-Tron, and his Supervisor [redacted]. He then shoveled the broken rod into the containment box were the gauge was located. It was locked and secured as he transported it to the company equipment container were it was placed and double locked for safety. A sign was placed at the container to keep other employees from disturbing the gauge. All of the previously mentioned personnel were contacted and made aware of the situation. On March 6, 2007, [the technician] from Gamma-Tron placed the source back into the safe position. [The technician from Gamma-Tron] assured the facility that the radioactivity was controlled. [The technician] then took the gauge to QSA Global so the unit could be disposed of properly." LA report number LA070008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-03-27
43253 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-03-21 18:45 | 2007-03-21 20:05 | 2007-03-21 | OFFSITE NOTIFICATIONS MADE TO STATE , LOCAL AND COUNTY AGENCIES "The Prairie Island Nuclear Plant has a turbine building sump that collects water from the secondary side of the plant and this water contains trace levels of tritium. When we normally discharge the water from the sump, it is either sent to the river or to a permitted area on plant property. Earlier today, the discharge was lined up to the permitted area on plant property. The end of the line was frozen, causing approximately 100 - 150 gallons of the water to be diverted to a non-permitted area inside the plant property. "This notification is being made due to the notification of offsite agencies (state , local and county)." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-03-21
43252 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-03-05 | 2007-03-20 10:57 | 2007-03-20 | AGREEMENT STATE - MEDICAL EVENT RELATED TO DOSE LESS THAN 20% PRESCRIBED "Upon quality review a misadministration was discovered by hospital staff on March 3, 2007; the actual medical procedure was performed on January 23, 2007. It is estimated that patient was administered a dose less than 20% of the intended dose. State was notified on 19 March 2007. This incident is referred to [the State's] radioactive materials [office] for investigation." The misadministration involved a Gamma Knife. A quality review by the licensee confirmed that a treatment dose was prescribed as - 40% of maximum dose equivalent equals 11Gy; but was calculated as - 50% of maximum dose equals 11Gy. This discrepancy resulted in the administration of a dose that was 20% less than intended. State Report FL07-046 * * * Update on 03/20/07 at 1408 EDT via e-mail from FSME (C. Flannery) to MacKinnon * * * This event has been reviewed and determined to be a medical event. Immediate release to the public is authorized. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-03-21
43251 | 0 | UNDERWOOD ENGINEERING |  |  |  |  | 2007-03-19 17:00 | 2007-03-20 07:41 | 2007-03-20 | STOLEN TROXLER MOISTURE DENSITY GAUGE Licensee's truck was parked at worksite from 0930 until 1700 EDT on 03/19/07 with the gauge triple locked in the bed of the truck the entire day. When the licensee's employee was leaving the worksite at the end of the workday, it was noticed that the gauge was missing. The worksite is located Audenreid High School, 3301 Tasker Street, Philadelphia, PA. The Philadelphia Police Department was notified (Report # 07-17-011252). The gauge is a Troxler, Model 3430, Serial Number 030500 with a Cs-137 8 millicurie source, and an Am-241:Be 40 millicurie source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-03-20
43250 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-03-19 19:55 | 2007-03-19 22:59 | 2007-03-19 | OFFSITE NOTIFICATION DUE TO POTENTIAL MEDIA INTEREST RELATED TO A SECURITY THREAT A non-credible security threat resulted in contact with local law enforcement. Because of the potential for media interest, the licensee also contacted State and Local agencies and the Prairie Island Native American Community. The licensee has not yet determined if a media or press release will be issued. Contact the Headquarters Operations officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 1 | 2007-03-19
43249 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2007-03-19 18:16 | 2007-03-19 21:16 | 2007-03-19 | OFFSITE NOTIFICATION MADE TO NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION "Notified the New Jersey State, Department of Environmental Protection that Oyster Creek generating station was not in compliance with the NJPDES permit due to equipment malfunction. "The malfunction was an electrical bus fault which resulted in a trip of both operating dilution pumps. "Alternate power is now being supplied to the dilution pumps. The pumps have been restarted. "There has been no observed impact on the environment.." NRC Resident Inspector was notified of this event by the licensee. | 82 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-03-19
43248 | 0 | KAMPNER IRON AND STEEL |  |  |  |  | 2007-03-16 | 2007-03-19 12:31 | 2007-03-19 | ORPHAN SOURCE FOUND IN STATE OF PENNSYLVANIA DURING SCRAP METAL RECYCLING A truck carrying a load of scrap metal set off a rad alarm at a metal recycling facility. The truck returned to its origin (Kampner Iron and Steel) where the source of the radioactivity was found to be a TN Technologies gauge Model 5191 (Serial number B927) containing a 200 millicurie source of Cs-137. TN Technologies was contacted and it was determined that the gauge was purchase under a general license by Rapco Inc of Tennessee in 1977. It is believed that the gauge was used for process measurements of fluidized coal flow. A health physics contractor for Kampner Iron and Steel (Applied Health Physics) and a representative for the State of Pennsylvania were present when the gauge was recovered. Field testing indicated that the source was intact and no contamination present. The gauge was place in a drum and locked in a secured location at Kampner Iron and Steel and posted per regulations. Based on radiation measurements, the health physics contractor does not believe that the source resulted in any personnel exposures. Kampner Steel has been in contact with TN Technologies on options for retrieval of the gauge. Investigation into the status of Rapco Inc and how the gauge wound up as scrap are also in progress. The NRC Region 1 Office (Lodhi) has been notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2007-03-19
43247 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-03-18 19:40 | 2007-03-18 22:07 | 2007-03-18 | MANUAL REACTOR SCRAM DUE TO COOLANT CHEMISTRY CONCERNS "This report Is being made under 50.72(b)(2)(iv)(B) for inserting a manual reactor scram due to high levels of reactor coolant chlorides, sulfates, and conductivity. These elevated chemistry parameters may be due to a possible resin intrusion following the placement of a Condensate Demineralizer in service. "In addition, this report is being made under 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any systems listed in paragraph (b)(3)(iv)(B) of this section' due to PCIS groups 2, 3, and 4 being received when reactor water level dropped below 170 inches. All isolations went to completion. The reactor water level drop is normal following a scram from 28% power due to void collapse in the reactor vessel. Reactor water level was restored to normal and the PCIS group isolations were reset. "The current plan is to cooldown the plant and enter Mode 4." The scram was characterized as uncomplicated. All rods fully inserted. No safety relief valves lifted. Reactor water low level was approximately 165 inches and was restored with normal reactor feedwater. Decay heat is currently being removed via steam line drains. There were no electrical alignment or grid issues as a result of the transient. No significant Technical Specification LCOs were in effect at the time of the scram. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-03-18
43246 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-03-17 23:46 | 2007-03-18 04:41 | 2007-03-18 | RPS TRIP SIGNAL AND CONTAINMENT ISOLATIONS RECEIVED DURING MAINTENANCE "With the plant in refueling outage with all rods in and in Mode 5, a RPS trip and a containment isolation was received at 2347, 03/17/07. This event occurred when Div #2 Bus 16 Bus Pot Drawer was opened during isolation of 1AR Transformer Metering under C/O-17605. The opening of this Pot Drawer caused Div #2 4KV Bus 16, Div #2 480V LC-104 and Div #2 480V MCC-141, 142, 143, and 144 to open. 'B' RPS tripped causing full RPS trip due to SRM shorting removed. The loss of power caused RBV [Reactor Building Ventilation] and Spent Fuel Pool Radiation Monitors to trip and cause containment isolation to occur. Investigation into C/O-17605, restoration of power, resetting of RPS and containment isolation in progress." The containment valves that received an isolation signal were: Primary Containment Atmosphere Control, Post Accident H2/O2 Control system, Post Accident Sampling system, O2 analyzing and SCTMT isolation (H&V). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-03-18
43245 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2007-03-17 16:58 | 2007-03-17 21:11 | 2007-03-17 | GROUP ISOLATIONS FOLLOWING MANUAL REACTOR SCRAM "On March 17 2007, at approximately 1658 EDT, Group 2 (Reactor Building Ventilation Isolation) and Group 6 (RWCU Isolation) automatic containment isolation signals were received due to low reactor water level following the insertion of a manual scram signal. The manual scram signal was inserted following the reaching of internal administrative limits on changes in unidentified drywell leakage. The receipt of these isolation signals is not unusual following the insertion of a scram signal. "The reactor was manually shutdown due to reaching internal administrative limits on changes in unidentified drywell leakage. Prior to the manual shutdown, the leakage had not reached the applicable Technical Specification limits. Drywell leakage as of 1800 EDT was 1.3 GPM identified and 2.59 GPM unidentified with the unit in Hot Shutdown Mode. "All safety systems responded as expected. The plant is in a stable condition. Investigation is continuing." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-03-17
43244 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-03-16 21:00 | 2007-03-17 13:20 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * MATERIAL CONTROL AND ACCOUNTING PROCESS MONITORING ALARM RESOLUTION "In accordance with 10CFR74.57(f)(2), a report to NRC is required for the following event. On March 16, 2007 the Alarm Threshold Limit was exceeded for [DELETED] Extraction (Column Based) System. This was officially reported to the Measurement Control Unit Manager on March 16, 2007 at approximately 21:00. The time in which the potential alarm situation was initially reported to Measurement Control personnel was approximately 12:00 on March 16, 2007. A re-analysis of the process material cleared the alarm at approximately 13:00 on March 17, 2007. The initial test difference exceeded the Alarm Threshold Limit. The final difference after re-analysis was below the Alarm Threshold Limit. "Per E41-116 and the Fundamental Nuclear Material Control Plan (FNMCP), an Alarm Investigation Team was established since a process monitoring test exceeded its Alarm Threshold Limit." The licensee secured the process while investigating the alarm condition but subsequently restarted once the alarm was verified cleared. The licensee notified the NRC Resident Inspector and the NRC Project Manager. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 74.57 |  |  |  | 0 | 2008-05-11
43243 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2007-03-16 22:09 | 2007-03-17 02:13 | 2007-03-17 | AUTOMATIC REACTOR TRIP CAUSED BY SAFETY INJECTION SIGNAL At 2209 on 3/16/07, the plant tripped on a Safety Injection (SI) signal initiated because of low main steam line pressure in the 'A' main steam loop. The licensee is currently conducting a post trip review but believes that the low main steam line pressure in 'A' loop was caused by a spurious isolation of the 'B' Main Steam Line Isolation Valve (MSIV). The isolation in the 'B' main steam loop lead to high main steam flow and low main steam line pressure in the 'A' main steam loop. The 'A' MSIV then also auto-closed on the SI signal. The plant is currently stable in Mode 3 at about 2235 psig pressure and 547 degrees average Reactor Coolant System (RCS) temperature. All control rods fully inserted on the trip. Decay heat is currently being removed by auxiliary feedwater feeding the steam generators and steaming out the plant atmospheric steam valves. Since plant pressure did not decrease below 1500 psig, SI did not actually inject into the RCS. The licensee secured SI. No primary PORV's or safety valves lifted. No main steam safeties lifted according to plant closure indicators. There are no primary to secondary steam generator tube leaks. All electrical safeguards buses are powered by offsite power. The Emergency Diesel Generators (EDG) started but did not load and were shut down. The EDGs are operable and available if needed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-03-17
43242 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-03-15 15:32 | 2007-03-15 17:27 | 2007-03-15 | HPCI DECLARED INOPERABLE DURING STARTUP TESTING "While performing the HPCI Pump Operability Test (34SV-E41-005-2), HPCI failed to start. Upon starting the HPCI Turbine, the turbine control valve failed to open. It was observed that alarm 'Oil Filler Differential Pressure High' was received (setpoint 11 psid). Local indication indicated that the differential pressure was 12 psid. Operators locally at the turbine did not observe any movement of the turbine shaft. The HPCI system was returned to standby and an investigation by Engineering and I & C has been initiated. [The licensee] suspects a problem with the EGR (Electronic Governor Module)." The licensee will remain at the current power level and mode until the HPCI is repaired. The licensee notified the NRC Resident Inspector. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-03-15
43241 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-03-14 17:30 | 2007-03-15 13:45 | 2007-03-16 | AGREEMENT STATE REPORT ON DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "At approximately 8:30 AM, March 15, 2007, the Agency was informed that a Density Moisture Gauge had been run over by a large steel compacting roller which crushed the gauge. This had occurred at approximately 5:30 PM on March 14, 2007. It appeared that when it occurred, the operating rod was in the safe position and the source was shielded. During the attempt to retrieve the gauge, the source fell out of the shielded position and the internal sources fell out of the capsule. These were retrieved from the site and placed along with the crushed gauge into the transport container and returned to the office of the licensee. Wipe tests were taken and no spreadable contamination was noted. "The Agency is currently inspecting the licensee and will continue follow-up evaluations as necessary. " State Report # 07-05 * * * UPDATE FROM THE STATE OF ARIZONA (VIA FAX) TO HUFFMAN AT 14:04 EDT ON 3/16/07 * * * "The Agency performed an inspection of the broken gauge and source at the licensee's office on the morning of March 15, 2007. The broken gauge and source were removed from the Troxler transport case and the broken Cs-137 source and AmBe/241 source were examined and wipe tested. The sources and broken gauge were returned to the transport case, stored in the gauge storage room with additional shielding material placed around it and locked up awaiting shipping and transport containers from Troxler. A field survey of the site where the gauge was run over was conducted again and no radioactive material was detected. Initial wipe test data from the two sources indicates no spreadable radioactive contamination. Discussion with the licensee indicates that exposure to the gauge technician during source retrieval was minimized." R4DO (Shannon) and FSME EO (Giitter) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-03-20
43240 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2007-03-14 14:35 | 2007-03-14 22:22 | 2007-05-04 | TWO OUT OF THREE AUXILIARY FEEDWATER PUMPS OUT OF SERVICE "A pinhole leak was discovered on B train Essential Service Water (ESW) system piping while preparing the pipe surface for non-destructive examination. Control room personnel were notified of the leak at 1435. B ESW was immediately declared inoperable. At the time of control room notification, surveillance testing on the Turbine Driven Auxiliary Feedwater Pump (TDAFP) was in progress. This surveillance testing made the TDAFP inoperable and non-functional. The surveillance activities were terminated and the TDAFP was returned to operable status at 1438. "B ESW is the safety related water source for B train of auxiliary feedwater (AFW). For the three minute period between notification of the pinhole leak until the TDAFP was restored to operable status, there were two auxiliary feed pumps inoperable. This met the conditions for entry into T/S LCO Action 3.7.5.D which requires a plant shut down to Hot Standby within 6 hours. This action was exited when the TDAFP surveillance testing was terminated. Additionally, with 2 of 3 auxiliary feedwater pumps non-functional for 3 minutes, there was a condition which could have prevented fulfillment of a safety function for those 3 minutes." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1555 EDT ON 5/4/07 FROM KEITH DUNCAN TO S. SANDIN * * * The licensee provided the following information as the basis for retracting this report: "On March 14, 2007, (Event Number 43240) Callaway Plant reported a condition that, at the time, was believed to be a condition which could have prevented fulfillment of a safety function. At that time the 'A' motor driven auxiliary feedwater pump (MDAPP) was operable, the turbine driven auxiliary feedwater pump was not functional because of a surveillance test in progress. The 'B' MDAFP was presumed to be non-functional because of a pinhole leak in the 'B' train essential service water (ESW) system piping. 'B' ESW is the safety related water source for the 'B' MDAFP. "Subsequent inspection, non-destructive examination, analysis and evaluation of the 'B' train ESW piping determined that the structural integrity of the pipe was retained. 'B' ESW pump was able to provide the required flow to the train. 'B' train ESW was functional with the pinhole leak. With the 'B' ESW train functional, the 'B' train of auxiliary feedwater had its emergency water source. The auxiliary feedwater system would have been able to fulfill its safety function. This event is not reportable per 10CFR50.72(b)(3)(v)." The licensee will inform the NRC Resident Inspector. Notified R4DO (O'Keefe). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-03-14
43239 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-03-14 23:00 | 2007-03-14 22:06 | 2007-03-15 | OUTAGE OF SPDS AND ERDS "At 2300 hours, on 03/14/2007, the Unit 2 SPDS and ERDS system will be removed from service to support restoration activities from a planned maintenance outage on the power supply. The duration of work is expected to be approximately 20 hours. (Scheduled for completion at 1900 hours on 03/15/2007). During this time, Control Room indications and alternate methods will be available. "Since the Unit 2 SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM HUFFORD TO HUFFMAN AT 2336 EDT ON 3/15/07 * * * The SPDS and ERDS systems were returned to service at approximately 2230 EDT on 3/15/07. The licensee notified the NRC Resident Inspector. The R1DO (Hott) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-03-14
43238 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2007-03-14 14:55 | 2007-03-14 20:36 | 2007-04-13 | HPCI DECLARED INOPERABLE "During performance of a Unit 2 High Pressure Coolant Injection System (HPCI) Pump, Valve, Flow and Unit Cooler Functional and In-service Test, the High Pressure Coolant Injection System (HPCI) was declared inoperable. The inoperability is due to failure of AO-2-23-042 "HPCI Steam Line Drain Inboard Isolation to Main Condenser" to open. The AO-2-23-042 is normally open and its passive safety function is to remove any steam condensation from the HPCI pump turbine steam supply line. HPCI is a single train safety system rendered inoperable by this condition." The licensee notified the NRC Resident Inspector. * * * RETRACTION RECEIVED FROM DAVID FOSS TO JOE O'HARA AT 1431 ON 4/13/07 * * * "The purpose of this notification is to retract a previous report made on 3/14/07 at 2036 hours (EN# 43238). Notification of this issue to the NRC on 3/14/07 was initially made as a result of the discovery of a failure of AO-2-23-042 'HPCI Steam Line Drain Inboard Isolation to Main Condenser' to open. This condition was discovered during performance of a routine Unit 2 High Pressure Coolant Injection System (HPCI) Pump, Valve, Flow and Unit Cooler Functional and In-Service Test. Failure of this valve to open results in water condensing in the HPCI steam supply line. HPCI had already been considered inoperable since approximately 0934 hours on 3/14/07 as a result of the performance of the test. Repairs were made to the AO-2-23-042 valve and HPCI was returned to an operable status by 2205 hours (IR 603918). "Since the initial report, it has been determined that this condition is not reportable. HPCI was declared inoperable as a result of the performance of the surveillance test and therefore, the HPCI system inoperability was considered a planned evolution. In accordance with NUREG-1022, reporting of planned inoperabilities are not required to be reported unless a condition is discovered that could have prevented the system from performing its function. Water entering the HPCI steam supply piping only occurred as a result of the performance of the surveillance test and could not have caused HPCI to be inoperable during non-test conditions. The AO-2-23-042 is normally open when HPCI is required to be operable and its passive open safety function is to remove any steam condensation from the HPCI pump turbine steam supply line. The active safety function of the valve is to close on design basis events involving the initiation of HPCI. The passive open safety function is not required when the HPCI system is inoperable for testing. The active safety function was unaffected by this condition. "The NRC resident has been informed of the retraction." Notified the R1DO(Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-03-14
43237 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2007-03-12 15:00 | 2007-03-14 19:34 | 2007-03-14 | AGREEMENT STATE REPORT - LOST/STOLEN EXIT SIGNS The State provided the following information via email: "On 3/14/07 the Strongsville Ohio Police Department was notified that ten (10) tritium exit signs were missing and presumed stolen from a storage area at a local shopping center construction site. The apparent theft occurred between 3 PM on 3/12/07 and 1 PM on 3/13/07. The contractor reporting the incident stated that the signs could have been taken by anyone that had access to the construction site, because many different contractors were using the same storage area. The ten signs were all packaged in one box. The signs are manufactured by SRB Technologies as the Betalux-E Life Safety Sign, Model 171. They are distributed by Cooper Lighting under the name Sure Lites, TRX1 series. The signs are rated for a 20-year life cycle." Ohio event # - OH70003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2007-03-19
43236 | 0 | MC SQUARED, INC. |  |  |  |  | 2007-03-07 | 2007-03-14 16:15 | 2007-03-14 | LOST TROXLER MOISTURE DENSITY GAUGE This event was entered per the request of NRC Region 1 On the morning of 3/7/07 the reporting company noticed that a Troxler Moisture Density Gauge (Model 3411B, Serial Number 13563) was missing. The gauge was used Friday 3/2/07 at a jobsite at 35050 Halls Road, Clewiston, Florida and placed in a storage trailer. The jobsite was on a Seminole Indian Reservation. The trailer had not been broken into. The Seminole Reservation authorities are investigating. The licensee will submit a written report. This report was originally reported to the state of Florida, see event # 43219 reported on 3/7/07, since the reporting company was a Florida Licensee (License Number 3424-1). The reporting company also called the NRC on 3/7/07 at 15:18 regarding this same event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | FL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-03-14
43235 | 0 | FAIRBANKS MORSE |  |  |  |  | 2007-03-13 12:00 | 2007-03-14 11:41 | 2007-03-14 | 10 CFR 21 NOTIFICATON - IDENTIFICATION OF DEFECT WOODWARD GOVERNOR PIVOT PIN DEFECT This Part 21 was received via facsimile Pursuant to 10 CFR 21.21 (d)(3)(ii), Fairbanks Morse Engine is submitting a written notification on the identification of a defect that is considered to be a substantial safety hazard. (II) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect. Facility: Duane Arnold Energy Center Basic component which fails to comply or contains a defect: Woodward governor actuator model EGB13P, part number 16403190, Woodward part number 9903-561 for Fairbanks Morse Engine Emergency Diesel Generator (EDG). (iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. Fairbanks Morse Engine 701 White Avenue Beloit, WI 53511 (IV) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. Nature of defect: Per Woodward service bulletin 01393 dated January 2007, a pivot pin within the governor actuator was manufactured from incorrect material. The subsequent case hardening of the pivot pin made from incorrect material resulted in through hardening, making the pivot pin more brittle. Safety hazard which could be created by such defect: Per Woodward service bulletin 01393, a potential for pivot pin fracture exists which would result in the governor actuator going to the minimum fuel setting. The EDG would not be capable of carrying load under this condition. The inability of an EDG to carry a load during a design basis event would be considered a loss of safety function. (v) The date on which the information of such defect or failure to comply was obtained. Fairbanks Morse Engine received Woodward service bulletin 01393 on 1/11/07. Duane Arnold Energy Center was notified of this situation via e-mail dated 1/12/07. (vi) In the case of a basic component which contains a defect or fails to comply, the number and location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part. The list of potentially affected governor actuators identified in Woodward service bulletin 01393 contains only 3 units (serial numbers 14693610, 14687576 and 14699005) that were purchased by Fairbanks Morse Engine on purchase order 1079037-I. All 3 units were sold to Duane Arnold Energy Center and had not been assembled to the EDGs. (vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. The 3 units were repaired at Woodward on 1/18/07 by replacing the though hardened pivot pin with one that was from a lot that was verified via destructive analysis to be hardened to the properly case depth. All future lots of pivot pins will have case depth measurements taken to ensure proper case depth. (viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, Is being, or will be given to purchasers or licensees. The need for repair of the 3 units was communicated to Duane Arnold Energy Center on 1/12/07. The repaired governor actuators were returned to Duane Arnold Energy Center on 1/26/07. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2007-03-14
43234 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2007-03-13 14:30 | 2007-03-13 20:15 | 2007-03-13 | POTENTIAL HAZARD AFFECTING CRITICALITY CONTROLS DISCOVERED "BACKGROUND: "AREVA NP Richland routinely uses propane powered forklifts to move SNM in and between process buildings and warehouses. These forklifts have been routinely left inside these warehouses when not being used. During re-evaluations of facility hazards, AREVA safety staff questioned the acceptability of such practices in the context of 10CFR 70.61. "EVENT DESCRIPTION: "On March 13, 2007 at approximately 14:30 PDST, a member of the AREVA safety staff briefed site management on the conclusion of the safety staff that the practice of leaving propane powered forklifts unattended inside SNM storage warehouses for extended periods of time did not meet the performance requirements of 10 CFR 70.61 in that under certain postulated circumstances, a propane deflagration could occur and initiate a large fire. During some postulated fire-fighting scenarios, it was determined that accidental nuclear criticality was not 'highly unlikely'. "SAFETY SIGNIFICANCE OF EVENT: "The safety significance of this condition is low because an accidental nuclear criticality is still considered unlikely. The municipal fire department works closely with the AREVA emergency response organization when they respond to plant abnormal events and emergencies. The NCS organization is an integral part of the ERO and participates in the decision making during such events if NCS concerns exist. "There have been no propane fires on site during the time of the deficient analysis. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "Criticality could potentially occur during firefighting if the SNM in storage looses geometry control coincident with moderation. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "The process parameters controlled in the various storage warehouses include geometry, mass, moderation and neutron absorbers depending upon the storage configuration. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Plant-wide fire controls are established to ensure that large fires that would require the intervention by the municipal fire department are highly unlikely. This assures that the potential NCS concerns relative to fire-fighting with water are compliant with regulatory requirements. However, in certain areas of the plant the scenario of a propane deflagration and the potential subsequent large fire and response by the municipal fire department could not be shown to be highly unlikely during this unlikely condition. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "After discovery of the deficiency, a prohibition of allowing propane powered vehicles to remain unattended for significant amounts of time in warehouses is being established. Additionally, a restriction against using water for fire-fighting in the areas of concern, without approval of a Criticality Safety Engineer is being established. These administrative actions will ensure that accidental nuclear criticality due to a propane-induced fire scenario remains highly unlikely." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2007-03-13
43233 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-03-13 15:27 | 2007-03-13 16:47 | 2007-03-13 | MANUAL REACTOR TRIP DUE TO "A" MAIN FEEDWATER PUMP "At 1527 EST on 3/13/07 a manual reactor trip was actuated on Unit 2 due to 'A' MFPT (main feedwater pump turbine) malfunction. All systems responded as expected following the manual trip. The plant is currently stable in Mode 3 (Hot Standby) at 547 (degrees) F. No primary system or steam generator safety valves opened due to this trip. AFW (auxiliary feedwater pumps) system started and operated as designed." All emergency core cooling systems, emergency diesel generators are fully operable if needed and the electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-03-13
43232 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-09-22 22:00 | 2007-03-13 15:44 | 2007-03-13 | REPORTED UNDER NRC BULLETIN 91-01 24 HOUR NOTIFICATION "On September 22, 2006, during a heavy rain storm, the water level in the C-310 position #4 scale pit reached 3 5/8 inches (3.625 inches). The scale pit liquid sensor alarm system did not function as credited, in violation of NCSA 310-004. The water was found by operators by visual inspection. NCSA 310-004 credits the liquid sensor alarm to provide notification of water in the pit in excess of 2.5 inches. At the time of the event, the water level was measured to be less than 3 5/8 inches (3.625 inches) deep. However, subsequent measurements accounting for slope in the scale pit floor show that the water could actually have been as deep as 4 3/8 inches (4.375 inches). The two process conditions relied upon for double contingency are mass and geometry. "The first leg of double contingency is based on preventing a release of fissile material containing greater than a safe mass of uranium from getting into the scale pits. This is controlled through reliance on the integrity of the UF6 cylinder, liquid UF6 piping, pigtail, and liquid UF6 handling equipment. Since a UF6 release containing greater than a safe mass has not occurred, the mass parameter has been maintained Therefore, this leg of double contingency is maintained. "The second leg of double contingency relies on the scale pit liquid sensor alarm system to provide notification of water in the pit in excess of 2.5 inches. Requiring the liquid sensor to alarm at 2.5 inches allows ample time to react and prevent the accumulation of more than 3.68 inches water. Although the alarm system did not function, operators performed a surveillance of the scale pits and identified water in the #4 scale pit in excess of 2.5 inches. NCSE 032 shows that the 'subcritical' slab height of UO2F2 solution in the C-310 scale pit is 4.1 inches at (deleted) wt% U235. The NCSE determined that an unsafe geometry slab height (is., greater than 4.1 inches) cannot form if the initial water height is less than 3.6 inches. The as-found water height corrected for the scale pit slope was determined to be as deep as 4 3/8 inches (4.375 inches). Therefore, the parameter limit specified in NCSE 032 was exceeded and double contingency was not maintained. "The NRC Senior Resident Inspector has been notified of this event. PGDP Problem Report No. ATRC-06-3103; PGDP Event Report No. PAD-2007-01: NRC Worksheet No. SAFETY SIGNIFICANCE OF EVENTS: Although the scale pit liquid sensor alarm system failed to alarm when water in the pit exceeded 2.5 inches, an insufficient amount of water was available to achieve a criticality. The assay of the product withdrawal system at the time of the event was less than (deleted) wt%. Additional KENO and bucking calculations were included in design analysis calculation to illustrate the margin of conservatism. Those calculations show that the scale pit would have remained below the PGDP USL even for UO2F2 slab heights up to 7.75 inches at (deleted) wt%. In addition, a UF6 release containing greater than a safe mass did not occur. POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for criticality to be possible, a large UF6 release containing greater than a critical mass of uranium would have to form in the scale pit, and the pit would have to contain a sufficient amount of water. CONTROLLED PARAMETERS: The two process conditions relied upon for double contingency are mass and geometry. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: Product withdrawal assay at the time of the event was less than (deleted) wt% U235. However, no UF6 release occurred. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: All C-310 scale pit sensor alarming systems have been repaired and verified to work properly and put back in service. The NRC Resident Inspector was notified of this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2007-03-13
43231 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-03-13 07:30 | 2007-03-13 15:14 | 2007-03-13 | LOW MAIN CONDENSER VACUUM ISOLATION SIGNAL RECEIVED DURING PLANT SHUTDOWN "It was discovered that a valid Low Main Condenser Vacuum group 1A Nuclear Steam Supply Shutoff System (NS4) isolation for the Main Steam Isolation Valves (MSIV's) had been received while breaking main condenser vacuum while in Mode 4 for planned refueling outage 2R09. The isolation actuation was received as main condenser vacuum lowered below the isolation setpoint during the planned evolution of breaking of main condenser [vacuum]. All valves for this isolation signal had previously been closed by approved plant procedures while in Mode 3. The valid isolation signal was caused by not having the isolation signal bypassed as allowed by approved plant procedures." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-03-13
43230 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-12-31 12:00 | 2007-03-12 15:17 | 2007-03-12 | AGREEMENT STATE REPORT -TWO OVEREXPOSURES This Agreement State report was received from the State of Louisiana via facsimile. "Bayou Inspection Services reported an overexposure [of] two employees. (Deleted) received an annual dose of 5055 mR. (Deleted) received an annual dose of 5330 mR. Radiation Safety Officer stated he talked to both employees and told them they must do a better job of protecting themselves from exposure to radiation." Event Report ID No.: LA070004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-03-18
43229 | -1 | SIBLEY MEMORIAL HOSPITAL |  |  |  |  | 2007-03-12 12:00 | 2007-03-12 13:57 | 2007-03-13 | INCORRECT RADIONUCLIDE ADMINISTERED TO PATIENT The licensee was performing a gall bladder study that required a dose of 5 millicuries of Tc-99 to be administered. A participant in the study was given the wrong radionuclide Gallium Citrate (Ga-67), accelerator produced, in error. Both syringes containing the doses were located in the same case, which was delivered to Sibley Hospital by Mallinckrodt. The licensee informed the patient of the error and that there is minimal risk of adverse effects to the patients health. The actual dose versus the prescribed dose is still under investigation. Additional corrective actions will be determined at a later date. * * * UPDATE 0900 EDT ON 3/13/07 FROM JORDIE KECK TO S. SANDIN * * * The licensee is retracting this report after conducting a review that concluded no reporting criteria was met. Notified R1DO (Hott) and FSME (Morell). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-03-18
43228 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-03-10 00:30 | 2007-03-10 00:14 | 2007-03-10 | PLANNED MAINTENANCE FOR UNIT 2 SPDS AND ERDS SYSTEM "At 0030 hours, on 03/10/2007, the Unit 2 SPDS and ERDS system will be removed from service for planned maintenance outage on the power supply. The duration of work is expected to be approximately 12 hours. (Scheduled for completion at 1230 hours on 03/10/2007). During this time, control room hardwire indications will be available. "Since the Unit 2 SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii). The licensee has redundant indication in the control room and will notify the Operations Center when the planned maintenance work is complete. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 03/10/07 AT 2019 EST FROM RICH KLINEFELTER TO MACKINNON * * * "This is a followup courtesy notification to EN # 43228. The Unit 2 SPDS and ERDS systems, as noted (above), have been restored to normal as of 19:50 on 03/10/2007." NRC Resident Inspector was notified of this update by the licensee. NRC R1DO (Neil Perry) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-03-10
43227 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2007-03-09 10:43 | 2007-03-09 15:02 | 2007-03-12 | MANUAL REACTOR TRIP AT REDUCED POWER DUE TO INADEQUATE FEEDWATER CONTROL "At approximately 0803 Central Standard Time (CST) on 3/9/2007, Callaway Plant received indications of a condenser tube leak. At approximately 0826 CST, a power reduction from 100 percent to less than 5 percent was initiated in accordance with the Secondary Water Chemistry Program. At 1043 CST, with the reactor at approximately 30 percent power, a manual reactor trip was initiated due to inadequate feedwater control to the C steam generator. There was indication of feedwater flow to and increasing level in the C steam generator with both the main feedwater reg valve and its bypass valve closed. Cause of the inadequate feedwater control is under investigation. "All safety systems functioned as designed with the exception of the digital rod position indication for control rod K10 which failed during the trip due to an existing problem. Control rod K10 is believed to be fully inserted, but is being treated as indeterminate at this time. Main feedwater isolation and motor-driven auxiliary feedwater actuations occurred as expected. Both trains of the emergency diesel generators and the offsite power supplies are available. " Callaway plant is currently stable in Mode 3 at normal reactor coolant system parameters. "This notification is being made in accordance with 10CFR50.72(b)(2)(iv)(B) for manual reactor trip (RPS actuation), 10CFR50.72(b)(2)(xi) for offsite notification and 10CFR50.72(b)(3)(iv)(A) Specified System Actuation. "The licensee informed the resident inspector of the event and will be making State notifications. A press release is expected." * * * UPDATE ON 03/12/07 AT 2116 EDT FROM S. GANZ TO MACKINNON * * * "Repairs were made to the Digital Rod Position Indication (DRPI) for control rod K10. The cause was determined to be a bent pin on a cable connector. When DRPI was restored, control rod K10 was verified to be fully inserted. Post maintenance testing was completed satisfactorily. "The cause of the inadequate feedwater control for the C steam generator was a failure of the positioner for the C main feedwater reg valve. The positioner was replaced and tested satisfactory. "The plant is currently in Mode 2 (Startup) "The resident inspector was informed of the update." R4DO (Mike Shannon) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2007-03-09
43226 | -1 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-03-09 14:23 | 2007-03-09 14:48 | 2007-05-12 | UNUSUAL EVENT DECLARED DUE TO RCS LEAKAGE GREATER THAN TECH SPEC LIMIT "A Notification of Unusual Event has occurred on Unit 2 due to Reactor Coolant System (RCS) unidentified leakage greater than 10 gallons per minute." The licensee notified NRC Resident Inspector. Notified USDA (Brzostels). * * * UPDATE AT 1754 ON 3/9/06 FROM T. PETRAK TO P. SNYDER * * * "No actual RCS leakage occurred and the RCS always remained intact. The additional water injection occurred and the RCS always remained intact. The additional water injection into the Reactor Coolant System was required to makeup for gases that came out of solution and accumulated in the reactor vessel head and were being vented from the RCS during a planned drain down." The licensee terminated the Unusual Event at 1751 on 3/9/07. The licensee notified the NRC Resident Inspector, state, and local government agencies. The licensee will remain in Mode 5 for their planned outage. Notified R2DO (G. Hopper), NRR EO (M. Case), IRD (T. Blount), NRR (J. Dyer), DHS (McKentry), FEMA (Biscoe), DOE (Wyatt), EPA (Burgess), HHS (Dalviel), USDA (Giles). * * * UPDATE AT 1531 EDT ON 5/11/07 FROM ROBERT DORMAN TO GERRY WAIG * * * This report is retracted based on the following: "On 3/9/07, an NOUE was declared while Unit 2 was in Mode 5, draining the RCS to support Rx Vessel disassembly, due to what was then diagnosed as an RCS Unidentified Leak greater than 10 gpm. Subsequent review of the event revealed that no leak existed and the mismatch between charging and letdown, which was the basis of the leak determination, was caused by a nitrogen bubble being vented from the Rx Vessel Head and the additional charging volume was displacing the nitrogen volume as it was being vented. As a result, Vogtle Unit 2 is retracting the NOUE classification that was made on 3/9/07." The licensee informed the NRC Resident Inspector. Notified R2DO (Ernstes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-03-09
43225 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-03-09 13:45 | 2007-03-09 14:32 | 2007-03-09 | SECONDARY CONTAINMENT BYPASS LEAKAGE RATE EXCEEDED "Appendix J Local Leak Rate Testing has determined that Tech Spec Acceptance Criteria for Secondary Containment Bypass Leakage has been exceeded. During the performance of SE-259-044 the combined SCBL limit of 9scfh was exceeded. Test results were within Administrative and Acceptance Criteria for the 10CFR50 Appendix J limits of 0.6La. The leakage limit is 9scfh. The identified degraded condition is reportable as a condition of the nuclear power plant, including its principle safety barriers being seriously degraded per 10CFR50.72(b)(3)(ii)." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-03-09
43224 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-03-09 00:30 | 2007-03-09 06:23 | 2007-03-09 | MAIN STEAM LINE FLOW INSTRUMENT LINE PRESSURE BOUNDARY LEAKAGE "With Unit 2 in Mode 4 for a planned refueling outage, a one-inch socket weld elbow on an instrument line off the 'D' main steam line was identified as leaking water. Leakage was quantified as less than 20 drops per minute (with the main steam lines full of water). "This elbow is on a steam line flow instrument (just below its condensing chamber) and is located in the Unit 2 drywell (primary containment). "This item constitutes a primary coolant boundary leak discovered while shutdown." A pressure test is planned to be performed after the repair of the instrument line elbow is completed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-03-09
43223 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2007-03-08 14:50 | 2007-03-08 16:15 | 2007-03-09 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO A DEGRADED SEAL IN THE "A" REACTOR RECIRCULATION PUMP "Reactor Recirculation Pump 'A' removed from service due to a degraded seal. TS 3.4.1 entered to meet requirement for single loop operation at 1050. When the pump was secured, the 3D monicore system failed preventing verification of thermal limits. TS 3.4.1 action D entered at 1450 required to be in mode 3 (Hot Shutdown) within 12 hours." The NRC Resident Inspector was notified of this event by the licensee. Reactor Recirculation Pump 'A' seal is degraded, no increase in leakage. Licensee is in contact with General Electric in trying to restore the 3D monicore system. All Emergency Core Cooling Systems and the Emergency Diesel Generators (all 3 divisions) are fully operable if needed and the electrical grid is stable. Nine Mile Point Unit 1 is in coastdown for a scheduled refueling outage. Nine Mile Point Unit 2 should be in Mode 3 (Hot Shutdown) by 0100 hours on 03/09/07. * * * UPDATE AT 1241 EST ON 03/09/07 FROM CHRIS SKINNER TO MACKINNON * * * "On March 8, 2007 at 1709, surveillance for thermal limit verification was completed satisfactorily and TS 3.4.1 was exited. The reactor was no longer required to be shutdown per Technical Specifications; however, the plant shutdown continued for performance of maintenance activities." R1DO (Neil Perry) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-03-08
43222 | 0 | TMI-2 ISFSI |  |  |  | ISFSI | 2007-03-08 11:55 | 2007-03-08 14:20 | 2007-03-08 | DEGRADATION OF PROTECTED AREA BOUNDARY Degradation of Protected Area Boundary. Immediate compensatory actions taken upon discovery. Call Headquarters Operation Officer for further details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | ID | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2007-03-08
43221 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2007-03-07 20:50 | 2007-03-08 01:07 | 2007-03-08 | HPCI DECLARED INOPERABLE FOLLOWING SURVEILLANCE TESTING "While Performing HPCI ATTS Panel, 1H11-P927, Functional Test & Calibration Surveillance (57SV-SUV-013-1S) For Ambient Torus Temperature High, The HPCI System Isolated. The Functional Test & Calibration Was Complete. The Isolation Was Reset. Following Return Of The Test Switch To Normal, HPCI Isolation Trip Logic 'A' Initiated & Closed 1E41-F002. HPCI Isolation Valve F002/F003 Alarm Annunciated When The Isolation Valve Started Closing & The HPCI Turbine Trip Solenoid Energized. I&C Investigating Time Delay Relay For Possible Cause." HPCI has been declared inoperable placing Unit 1 in TS LCO A/S 3.5.1.c - 14 days to restore. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-03-08
43220 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2007-03-07 | 2007-03-07 18:35 | 2007-02-27 | AGREEMENT STATE REPORT- MEDICAL EVENT - UNDERDOSE TO PATIENT During a series of fractional medical treatments given to the patient on 2/13/07 through 2/20/07, a dose of 24000 centigray was administered to the dose area of the patient instead of the 31092 centigray prescribed dose. The isotope used was Iridium-192. The source strength was unknown at the time of the report. "The HDR misadministration was the result of a failure to correct for the proper length of the type of connector used in the procedure. The error resulted in a dose more than 20% below the prescribed dose. The error in the procedure was identified during the review process following the conclusion of the last dose fraction." The length of the connector differed from the correct length by 1.4 centimeters. The prescribing physician said that the patient will likely have a skin reaction to the treatment that will heal with time. "The [Colorado Health] Department's inspector is scheduled to conduct an inspection at the Penrose Hospital on Monday, March 12, 2007. He was briefed with the known details of the misadministration at this date and will look further into this matter." The state expects to provide additional information at a later date. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2007-03-09
43219 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-03-07 | 2007-03-07 15:18 | 2007-03-07 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The State provided the following information via facsimile: The gauge was used at a jobsite at 35050 Halls Road, Clewiston, Florida on a Seminole Indian Reservation. After being used on the jobsite, the gauge was placed in a storage trailer. The gauge is a Model 3411B Troxler soil moisture density gauge, serial number 13563. The gauge contained a 8 millicurie Cs-137 source and a 40 millicurie Am-241:Be source. "Device was used Friday 03/02/07 and placed in a storage trailer. It was noticed missing when the trailer was opened 03/07/07 [in the morning]. The trailer had not been broken into. The Seminole Reservation authorities are investigating. Licensee will submit a written report. [State of] Florida will investigate within the limits of its authority. FL Incident Number: FL07-039 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-03-12
43218 | 0 | TYCO ELECTRONICS |  |  |  |  | 2007-03-05 | 2007-03-07 09:30 | 2007-03-07 | POTENTIAL DEFECT IN E7000 RELAYS "Notification of limited E7000 relay recall (CII-010). "During our normal assembly processing of nuclear E7000 relays, Tyco Electronics experienced an issue with a component. A spring in the base assembly broke during the calibration process. An analysis of the spring revealed non-conforming heat treatment causing the spring to become brittle. Further investigation revealed that this condition was limited to one specific lot of springs." The cause of the defect was determined to be stress corrosion cracking (SCC). Testing of other springs in this lot did not identify additional defective springs. Tyco's inspection process has been changed to better detect SCC. The defective springs have been purged from inventory and customers notified. Plant affected by this recall are: Braidwood Farley Fitzpatrick Indian Point 3 Limerick Millstone North Anna Oyster Creek Peach Bottom Perry Prairie Island San Onofre Susquehana Vogtle Watts Bar Other agencies/organizations: Delphi Controls Engine Systems Inc Entergy Oswego Warehousing Ergy Tech GE Nuclear Energy Progress Energy Carolinas Trentec Inc - Curtiss-Wright Flow Control Group | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2007-03-07
43217 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-03-07 03:05 | 2007-03-07 06:11 | 2007-03-07 | EMERGENCY DIESEL GENERATOR AUTOSTART ON LOSS OF "B" RESERVE STATION SERVICE TRANSFORMER "The Unit-2 H Emergency Diesel Generator (EDG) automatically started on a Degraded Voltage/Under Voltage (DV/UV) signal due to the loss of the 'B' Reserve Station Service Transformer (RSST). The Unit-2 H Emergency Diesel Generator is supplying the Unit-2 H 4160 Volt Bus. Both Unit 1 and Unit 2 were stabilized using the appropriate abnormal procedures. "During the event, the Unit 2 'B' Main Feed Water Pump motor, 2-FW-P-1B1, was noted to be running with the other motor, 2-FW-P-1B2, not running. The Unit 2 'B' Main Feed Water Pump was subsequently placed in Pull-to-Lock. Investigation continues as to the cause of the loss of the 'B' Reserve Station Service Transformer and the start of the Unit 2 'B' Main Feed Water Pump motor. The licensee notified the NRC Resident Inspector. | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-03-07
43216 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-03-05 13:08 | 2007-03-06 10:10 | 2007-03-06 | UNAUTHORIZED ENTRY INTO PROTECTED AREA Actual entry of an unauthorized person into the protected area. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-03-06
43215 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2007-03-05 14:00 | 2007-03-05 16:42 | 2007-03-05 | AGREEMENT STATE REPORT - STOLEN CPN MOISTURE DENSITY GAUGE "On the afternoon of March 5, 2007 at approximately 2:00 pm, the Radiation Safety Officer for Quality Assurance Testing Laboratories, Inc. of Montgomery, Alabama notified the State that a CPN model MC-3 moisture density gauge was stolen from its storage location in Montgomery, Alabama. Quality Assurance Testing Laboratories, Inc. is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 819. The gauge was last seen Thursday, March 1, 2007 when it was placed in storage. The gauge was discovered missing at 10:00 am on the morning of March 5, 2007. The Montgomery Police Department was notified and responded. The stolen gauge was identified as a CPN model MC-3, serial number M300705778, with 10 millicuries of Cs-137 and 50 millicuries of Am-241-Be. The RSO indicated that the gauge was stored in a locked shed that had no windows. The door is equipped with a regular door lock and a deadbolt. There was no sign of forced entry and only the one gauge was stolen. Other gauges containing radioactive material were in the building but not affected. The RSO indicated that the transport case was not locked and the source shutter was not locked. According to the RSO, no other equipment was stolen. The licensee is canvassing the pawn shops within the city providing them pictures for their information." Alabama Event 07-14. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2007-03-08
43214 | -1 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2006-11-01 | 2007-03-05 15:38 | 2007-03-14 | AGREEMENT STATE - PERSONNEL UNDEREXPOSURE The State was notified by the licensee's RSO that a patient had an underexposure by 24%. The State will provide updates as licensee information is received. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION PROVIDED BY K. SIEBERT TO KOZAL ON 3/14/07 AT 1333 EDT * * * After review of the event by the licensee and the State, the material involved in this event (Palladium -103) is accelerator produced and is not regulated by the NRC. Therefore, this event is not reportable and is retracted. Notified R4DO (Shannon) and FSME (G. Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2007-03-11
43213 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2007-02-20 08:30 | 2007-03-05 13:27 | 2007-03-05 | AGREEMENT STATE REPORT - ABANDONED INDUSTRIAL GAUGE FOUND IN SCRAP YARD The following was provided by the State via facsimile: "On the morning of 03/02/07 NCRPS became aware of a potential unknown radioactive source discovered [on 2/20/07] by a scrap yard [State Line Scrap Metal]. NCRPS dispatched a health physicist in an effort to gain reliable information. The health physicist was at the scrap yard by early afternoon and had collected technical information to be used in fully analyzing the unknown source. The source is potentially an abandoned industrial gauge (licensed radioactive material) and NCRPS is following protocol to determine a responsible party. The source was packaged in a 55 gallon drum and isolated in a safe and controlled manner (exposure rates less than 2 mR/hr) prior to site departure on 03/02/07. "NCRPS is continuing event evaluation and determining necessary follow-up actions." The State has not determined the source or the strength of the source at this time. NC report ID number: NC-07-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2007-03-08
43212 | 0 | SCHLUMBERGER - P.T.C. |  |  |  |  | 2007-03-01 | 2007-03-05 11:45 | 2007-03-05 | PULSE NEUTRON GENERATOR TRITIUM SOURCE MISSING The licensee reported that a shipment of a pulse neutron generator (PNG), ID #1146-01, containing a 1.5 curie tritium sealed source (s/n 5066) was determined to be lost by the freight forwarder (Yellow Freight) and reported missing in transit to the licensee's NJ facility on 3/1/07. The PNG originated in Indonesia, arrived at Dallas - Fort Worth Airport, and cleared Customs on 2/9/07. The PNG package was picked up by Yellow Freight and was to be shipped to NJ through Nashville TN. It appears that there are some discrepancies with the Yellow Freight tracking number and that the package never arrived at Nashville. A search for the package is still in progress. The licensee intends to notify NRC Region 1 inspector (Jackson). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-03-05
43211 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2006-07-01 | 2007-03-05 08:00 | 2007-03-05 | AGREEMENT STATE - MISSING AMERICIUM-241 SOURCE The following information was provided by the State of Maryland via facsimile: Diageo is a State of Maryland general licensee for a 100 millicurie Am-241 radioactive material gauge used to measure the fill height of beverages bottled at the facility. Diageo provided a report in writing to the State on 1/8/07 that the source was missing. "The source and its source holder were discovered missing from an Industrial Dynamics Company (IDC) Model FT-50 device by the company around June 2006. Diageo and IDC conducted an extensive search of the facility and did not locate the source. The State conducted an investigation of the incident on 2/16/07 and no root cause of the loss/theft could be identified. Visual search and surveys were conducted in facility inventory areas. Interviews with IDC confirmed that only IDC or other qualified specific licensees are allowed to remove the source holder from the unit. IDC states that they did not remove the source from the device. Diageo states that their personnel did not remove the source. Potential waste stream routes from the facility are being investigated. Diageo states that they cannot identify any mechanism whereby the source could have gotten into the company waste stream. Diageo failed to report the incident to local law enforcement." During the State investigation the following issues were identified: "failure to maintain inventory records; failure to conduct leak tests; failure to perform operational test at required frequencies; and non-operational source indicators lights. Maryland has reported the case to local FBI." The State has notified Region 1 (White and Janda) about this event. The State Report number is MD070004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2007-03-08
43210 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-03-02 23:32 | 2007-03-03 05:16 | 2007-03-03 | REACTOR SCRAM SIGNAL DUE TO HIGH DISCHARGE VOLUME LEVEL The licensee was performing testing that inserts a reactor scram manually to verify that the backup scram valves port air. Moments after the scram was reset a second scram came in from a scram discharge volume high level. The second scram was not called out in the test, nor were there steps to bypass the scram discharge volume scram signal prior to resetting the manual scram. All rods were already fully inserted and, consequently, there was no rod motion as a result of the scram. The licensee states the unexpected scram signal was a result of an error in the test procedure. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2007-03-03
43209 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2007-03-02 19:12 | 2007-03-02 22:33 | 2007-03-02 | UNIT 3 HPCI INOPERABLE DUE TO PINHOLE LEAK ON THE STEAM SIDE "At 1912 hours on 03/02/07, a through wall leak was identified on the U3 High Pressure Coolant Injection (HPCI) Inlet Drain Pot drain piping. This piping is ASME Code class 2 piping and as required by the Technical Requirements Manual the piping was isolated which resulted in isolation of the U3 HPCI System. U3 HPCI was declared inoperable. This event is reportable under 10CFR50.72(b)(3)(v)(D). Piping repair preparations are in progress." The leak was discovered by a licensed operator on rounds. The Technical Specification is a 14 day LCO. The licensee notified the NRC Resident Inspector. | 0 | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-03-02
43208 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-03-02 10:30 | 2007-03-02 18:17 | 2007-03-02 | AGREEMENT STATE REPORT - DAMAGED CPN GAUGE The following was provided by the State via facsimile: "A moisture density gauge was being used at a construction site in Glendale, CA (near the Water Department and the Los Angeles River). (CPN, model MC3, serial number M36097108). The gauge user had placed the gauge into a box (plastic milk carton) which was then going to be passed down into a trench where it would be used. There was a delay and the box with the gauge inside were placed on the edge of the property waiting to be used. According to [the licensee], the gauge user went to the bathroom, but the other workers were aware of the location of the gauge. At the same time a front loader truck was moving several large pieces of metal. The pieces vibrated off and dropped onto and crushed the gauge. "[The licensee] said the sources appeared to be intact, however the plastic gauge housing was destroyed and the lead shielding leaves that normally surround and shield the end of the source rod (where the Cs-137 source would normally reside in a shielded position) were not in position anymore and were therefore not shielding the Cs-137 source now. [A] Los Angeles County Radiation Management Health Physicist, responded to the site to do an evaluation and to survey the source. The sources were intact and undamaged. There was no contamination. The dose rate at 1 foot was 20 milliRoentgen per hour (mR/hr). The end of the source rod was shielded and the remains of the gauge were placed into the transportation case. The gauge was transported by the RSO to Maurer Technical Services (the CPN manufacturer representative) [Deleted] so it can be shipped back to the manufacturer for disposal. The highest dose to any individual from this event was probably less than 5 millirem total. Corrective actions: The RSO will give refresher training to all gauge users to review their existing policies and procedures - gauge users are to have control over the gauge at all times." CA report number: 030207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-03-07
43207 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2007-03-02 10:14 | 2007-03-02 17:03 | 2007-03-16 | FITNESS FOR DUTY - LICENSED EMPLOYEE A licensed employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been revoked. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY S.GARDNER TO KOZAL ON 3/16/07 1728 EDT * * * The licensee provided a retraction regarding the above positive alcohol fitness-for-duty test. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. R4DO (Shannon) notified. | 0 | 99 | 98 | 0 | 99 | 98 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2007-03-02
43206 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-03-02 11:00 | 2007-03-02 14:27 | 2007-03-02 | AGREEMENT STATE REPORT - TROXLER GAUGE FOUND IN SCRAP HEAP The following was provided by the State via facsimile: "Event Location: Miller Compressing, Milwaukee, WI "Event Type: Found Radioactive Material-Portable Moisture Density Gauge "Notifications: Miller Compressing called [the] Department of Health and Family Services (DHFS) "Event description: A Troxler moisture density gauge was found at Miller Compressing on 2/22/07. It was in a load of scrap and was separated by the staff at Miller Compressing. "Additional Information: Miller Compressing is scrap metal recycler in Milwaukee. "The DHFS staff in Wisconsin has been in contact with the state of Illinois Emergency Management Agency and Troxler Electronic Labs to try and identify an owner or former licensee. The gauge was initially distributed to an Illinois licensee in 1977. The portable gauge is a Troxler Model 3411. The plate on the device indicates the device serial number is 4942. The back plate identifies the nuclides as 8.9 mCi of Cs-137 on 9/5/77 ([serial number] CC-1968) and 40 mCi of Am241:Be on 9/14/77 ([serial number] CAA-1031). The serial no. does not match any gauges currently reported as lost or stolen. "The shipping container is damaged. The gauge is intact. Miller Compressing is storing the gauge in a locked location on site. DHFS staff will follow up with a site visit." WI report number: W070005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-03-07
43205 | 0 | NJ DEPT OF ENVIRONMENTAL PROTECTION |  |  |  |  | 2007-03-01 | 2007-03-02 10:54 | 2007-03-02 | ORPHAN GENERAL LICENSE SOURCE DISCOVERED AT SCRAP METAL DEALER A scrap metal dealer, Sims Hugo Neu, discovered a radioactive source during metal sorting activities at their facility. The source is identified as a Krypton-85 Ohmart Gauge; S/N 2862 B X; Source Holder ID BAL; SO# NJ 940602681B. The activity of the source was 65 milliCuries on 10/94. The owner of the source is currently unknown. The source was received at the dealer from a "feeder facility" and so the origin of scrap is not easily traced. The scrap dealer notified the NJ Department of Environmental Protection. New Jersey has been in contact with NRC Region 1 (D. White and D. Janda) and is attempting to track the owner via the serial number. The source has been isolated and secured. Sims Hugo Neu is located at 1 Linden Avenue, Jersey City, NJ. New Jersey is reporting this for information only. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | GEN |  |  |  |  | 0 | 2007-03-02
43204 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-03-01 08:15 | 2007-03-01 16:14 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * POTENTIAL DEGRADATION OF SAFETY SYSTEMS "During the investigation of a suspected operational upset an accumulation of fissile material exceeding the controlled limit was found in an enclosure. The material was placed in a safe geometry container after inspection of the system. Samples were obtained expeditiously to determine the actual mass of the material. This particular operation has been suspended until corrective actions are in place. This is a failure of an Item Relied on for Safety (IROFS) if the mass is determined to be in excess of the limit. "[The event is of] very minimal safety significance. No actual safety consequences [occurred] due to the always safe mass of fissile material for the as-found conditions. Two additional IROFS were available and reliable to perform their safety function. "There were no actual safety consequences to the workers, the public, or the environment. The quantity of fissile material was below the always safe mass for the conditions. Also, the fissile material was contained in an enclosure used for normal operations." The licensee notified the NRC Resident Inspector. * * * UPDATED AT 1242 EST ON 3/2/07 FROM NICHOLAS W. BROWN TO J. KOZAL * * * The licensee is retracting this event based on the following: "On 3/1/2007, NFS made a 24-hour report to the operations center based on 10CFR70, Appendix A, Paragraph (a)(2). 10CFR70, Appendix A, Paragraph (a)(2) requires a 24-hour report for loss or degradation of items relied on for safety (IROFS) that results in failure to meet the performance requirement of Sec. 70.61. The report was made because an accumulation of fissile material potentially exceeding the allowed mass was discovered in an enclosure. "Samples of the material were obtained and analyzed. The results demonstrated that the mass limit was not exceeded; therefore, the documented safety basis including the Item Relied On For Safety (IROFS) in question remained intact. Based on this information it is requested that this event report be retracted." The licensee notified the NRC Resident Inspector. Notified R2DO (Seymour), FSME EO (Wastler), and Fuels OUO group. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
43203 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2007-03-01 08:00 | 2007-03-01 11:22 | 2007-03-01 | AGREEMENT STATE REPORT - STOLEN HUMBOLDT MOISTURE DENSITY GAUGE The following information was provided via facsimile: "The SC Department of Health and Environmental Control was notified on Thursday, March 1, 2007, at 1015 hrs, that a Humboldt Model EZ 5001, s/n 4751, containing 11 mCi of Cs-137 and 44 mCi of Am-241:Be, had been stolen from the rear of a company truck, located at Extended Stay America, Spartanburg, SC. [The State of SC] contacted [the] RSO, at 1030 hrs and was advised that [the] authorized user, had reported at 0800 hrs that the gauge had been stolen from the vehicle. [The RSO] stated that the tailgate was locked to prevent access to the steel lock box that the gauge storage container was secured in and the lockbox is bolted to the truck bed. The tailgate had been damaged to gain access to the lockbox and a blowtorch had been used to cut the lock of the steel box. [The RSO] stated that local law enforcement had been notified and a police report had been completed. [The RSO] stated that he would e-mail an incident report, police report, and images of the security measures used to secure gauges in company vehicles within the next two business days. "[The RSO] was advised by the State of SC to submit a written report detailing this event to the Department within 30 days. [The RSO] was advised that if the gauge was recovered, to contact the Department immediately. The event is open and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system." The licensee is located in Marietta, GA and has a reciprocity license in SC. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2007-03-06
43202 | 0 | ZION | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-02-28 13:05 | 2007-02-28 14:16 | 2007-02-28 | EXTREMELY SMALL AMOUNT OF SNM UNACCOUNTED FOR "This is a non-emergency event notification in accordance with 10 CFR 20.2201(a)(1)(ii) to report an accountability discrepancy of licensed material. "In the process of reviewing records, it was identified that all disposition records for reactor incore detectors could not be found. The reactor incore detectors contain very small quantities of U-235 and were used to monitor reactor power at Zion Station from 1972 to 1988. "The unaccounted for material was classified as missing on February 28, 2007 due to lack of records documenting the current location of the detectors; however, based on available records and discussions with former Zion Nuclear Material Custodians, it is believed that these detectors were shipped as radioactive waste to the Barnwell Low-Level Radioactive Waste Disposal Facility located in South Carolina. A search of storage locations at Zion was performed, but the detectors have not been located. "Historical records indicate that it was common practice for Zion Station to dispose of detectors in this manner. There is no evidence of theft or diversion of these detectors. The incomplete records involve 43 incore detectors received onsite prior to 1988. The detectors contain an extremely small amount of Special Nuclear Material and pose no significant safety concern. Depending on design, each incore detector contained between 0.0025 grams to 0.0004 grams of Uranium 235 resulting in an aggregate quantity of approximately 0.102 grams of Uranium 235. The activity of this quantity is approximately 0.22 microcuries. This quantity is greater than the reportability threshold of 10 times the quantity specified in Appendix C to 10 CFR 20 which is 0.01 microcuries. "A subsequent written report will be made in accordance with 10 CFR 20.2201(b)." The licensee will notify the NRC Resident Inspector and the State. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | Decommissioned | Decommissioned |  | Decommissioned | Decommissioned |  | NON EMERGENCY | 3 | IL | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-02-28
43201 | -1 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-02-14 | 2007-02-28 12:07 | 2007-03-13 | AGREEMENT STATE REPORT - DISPENSING ERROR FOR THALLIUM -201 DOSE The following information was provided by the state via facsimile: "Description of Event: On February 14, 2007, a customer called to report that the Thallium-201 Chloride dose they ordered was only 2.9 mCi instead of the 4.0 mCi requested. Thallium-201 Chloride is an imaging agent used for myocardial perfusion imaging or parathyroid and tumor imaging. Another TI-201 dose was sent to the customer to account for the incorrect activity. "An investigation revealed that the pharmacist who dispensed the dose had selected the incorrect setting on the dose calibrator when assaying the dose at the pharmacy. The dose calibrator was set on Tc-99m instead of TI-201, resulting in an incorrect assay. "Root Causes: The root cause of this event was an error by the pharmacist while assaying the dose. By not double-checking that the dose calibrator was on the correct setting, an incorrect assay was recorded. "Actions Taken to Prevent a Recurrence: In an effort to prevent a recurrence of this event, the pharmacist will be sure to check that the correct isotope settings are in place on the dose calibrator for the dose being assayed. Additionally, checking the volume on the dose label will help reinforce that the pharmacist has checked which dose is being assayed and if the isotope setting is correct." LA Event Report ID No.: LA070003 * * * UPDATE AT 0915 EDT ON 3/13/07 FROM RICHARD PENROD TO S. SANDIN * * * The State of Louisiana is retracting this report following a review which concluded that their reporting criteria was not met. Notified R4DO (Shannon) and FSME (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-03-05
43200 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2007-02-02 | 2007-02-28 11:49 | 2007-02-28 | AGREEMENT STATE REPORT - CONTAMINATION FROM LEAKING SEALED SOURCE The following information was provided by the state via facsimile: On 02/05/07, the licensee notified the Louisiana Department of Environmental Quality that one of its Electron Caption Detectors (ECD) had a removable activity above 0.005 microcuries as a result off a recent "wipe test". The ECD is a Agilent Technologies, Inc. model number: 19233-69570, serial number YA353 with an estimated activity of 15 millicuries of Ni-63. Leak test results from a test performed on 01/26/07 were 0.024 microcuries. The wipe test results were reported to the licensee on 02/02/07. On 02/07/07 an onsite inspection was performed by licensee corporate personnel. On 02/07/07 the ECD was returned to the manufacturer's location in Wilmington, DE for disposal. LA Event Report ID No.: LA070002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2007-03-05
43199 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2007-02-28 06:35 | 2007-02-28 10:01 | 2007-02-28 | MANUAL REACTOR TRIP FOLLOWING MALFUNCTION OF PRESSURE TRANSMITTER "At approximately 0633 AM on February 28, 2007, control room operators manually initiated a reactor trip after observing decreasing steam generator levels as a result of low feed water flow. Control room alarms indicated low main feed water pump suction pressure which was subsequently, attributed to a malfunction of the main feed water pump low suction pressure cutback pressure transmitter (PT-408B) on the common main feed pump water supply header. The malfunction of the main feed pump water low suction cutback pressure transmitter resulted in a cutback of both main feed water pumps reducing main feed water flow to the steam generators and causing decreasing steam generator levels. "All control rods fully inserted and all safety systems responded as expected. The auxiliary feedwater system actuated as expected from low steam generator levels which occurs as a result of a full power reactor trip. The emergency diesel generators (EDGs) did not start as offsite power remained available. The plant was stabilized in hot shutdown with the [Auxiliary Feedwater System] providing decay heat removal via the main condenser. The main feed water pumps are shutoff and secured. "The event is under investigation and a post trip review is being conducted. A courtesy call to stakeholders will be made." All EDGs remain available in standby. No steam generator Power Operated Relief Valves or Main Steam Safety Valves lifted. The licensee notified state and will notify local authorities. The licensee plans to issue a press release. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-02-28
43198 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2007-02-28 01:20 | 2007-02-28 05:53 | 2007-02-28 | UNIT 2 REACTOR MANUALLY SCRAMMED DUE TO DECREASING CONDENSER VACUUM "At 0120 hours on February 28, 2007 the Unit 2 Reactor was manually scrammed due to decreasing condenser vacuum. All control rods fully inserted during the scram. Reactor water level decreased to approximately -10", which resulted in automatic Group II and III isolations as expected. All systems responded properly to the event. Unit 2 remains in Mode 3, maintaining reactor pressure, with reactor water level in the normal level band. The cause of this event is still under investigation. "Unit 1 was unaffected by the event and remains at 97% power. "This report is being made in accordance with 10CFR50.72 (b)(2)(iv)(B) and 10CFR50.72 (b)(3)(iv)(A)." The Main Condenser remains in service removing decay heat via the bypass valves. All ECCS equipment is available, if needed. The licensee will inform the State and has informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-02-28
43197 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2007-02-27 22:26 | 2007-02-28 05:40 | 2009-06-04 | HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABILITY "On February 27, 2007, at approximately 2200 hours, testing of the Unit 2 High Pressure Coolant Injection (HPCI) system was in progress in accordance with 0PT-09.2, HPCI System Operability Test following system maintenance. Soon after the HPCI turbine was started a high level alarm condition in the HPCI barometric condenser was experienced. Evidence suggests the most probable cause was due to failure of the 2-E41-F048, Condensate Pump Discharge Check Valve, to open. The adverse consequence of this check valve failing to open is inadequate cooling flow to the HPCI lube oil cooler. The HPCI turbine was removed from service per applicable plant procedures. "At the time of discovery, the HPCI system was inoperable for scheduled maintenance. However, this equipment failure would have prevented the HPCI system from fulfilling its safety function. Limiting Condition for Operation (LCO) per Technical Specifications (TS) 3.5.1. 'ECCS - Operating' Condition D had been previously entered on 2/25/07 at 1500, which required maintaining the Reactor Core Isolation Cooling (RCIC) system operable and restoration of HPCI operability in 14 days. All other ECCS systems are operable including RCIC. The LCO allowed outage time is due to expire on 3/11/07 at approximately 1500 hours. The licensee notified the NRC Resident Inspector. ** UPDATE FROM TURKAL TO KNOKE AT 11:33 EDT ON 04/26/07 *** "On February 28, 2007, at 0540 hours, the Control Room Supervisor made a notification (Event Number 43197) to the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(v)(D) (i.e., any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident). The notification was made as a result of an unexpected high level alarm condition for the High Pressure Coolant Injection (HPCI) system barometric condenser, which was received during the post-maintenance operability testing of the HPCI system. At the time of discovery, the HPCI system was inoperable; having been properly removed from service for planned maintenance. It was believed that check valve 2-E41-F048, which is in the discharge piping of the HPCI barometric condenser condensate pump, downstream of a connection from the HPCI lube oil cooler cooling water discharge line, did not open, as required, during the HPCI post maintenance operability run. With valve 2-E41-F048 closed, there is a potential for inadequate cooling flow for the HPCI lube oil and, as such, a potential that the HPCI system could be inoperable as a result. "Basis for Retraction Upon further review, it has been determined that the 2-E41-F048 functioned properly during the post-maintenance HPCI system operability testing. The valve was disassembled and inspected during the recent Unit 2 refueling outage and confirmed to be operating properly. As such, adequate HPCI lube oil cooling existed and HPCI could have fulfilled its intended safety function. "Physical inspection of the HPCI lube oil cooler piping, during the Unit 2 refueling outage, revealed that the lube oil cooler outlet orifice was missing. The missing orifice can result in higher than design flows through the lube oil cooler and higher backpressure at the barometric condenser condensate pump discharge. The higher backpressure can affect the ability to pump down the barometric condenser vacuum tank. Additionally, during troubleshooting activities performed prior to the refueling outage, valve 2-E41-F058, which is in the discharge piping of the HPCl barometric condenser condensate pump, upstream of the connection from the HPCI lube oil cooler cooling water discharge line, showed evidence of sticking. Either of these conditions could have caused the barometric condenser high level alarm without affecting HPCI lube oil cooling. If the barometric condenser becomes completely full, a relief valve on the tank will lift and relieve water to the HPCI room sump. The room sump pump has adequate capacity to keep up with the maximum expected flow. Operability of the HPCI system will not be affected by this condition. "The higher than design cooling water flow rate does not adversely affect the capability of the lube oil cooler to remove heat from HPCI system lube oil and, as such, does not affect HPCI operability. Additionally, physical inspection of the cooler during the refueling outage found no damage or erosion of the cooler internals, and the cooler was successfully pressure tested. "The barometric condenser condensate pump, barometric condenser vacuum pump, and barometric condenser water level instrumentation are not required to support operability of the HPCI system. "Investigation of this condition is documented in the corrective action program in Nuclear Condition Report (NCR) 223820. "On this basis, the HPCI system was capable of performing its function to mitigate the consequences of an accident and the issue is not reportable under 10 CFR 50.72(b)(3)(v)(D). "The NRC resident was notified of this retraction." Notified R2DO(Payne). *** UPDATE FROM TURKAL TO KNOKE AT 09:30 EDT ON 06/04/09 *** "On February 28, 2007, at 0540 hours, the Control Room Supervisor made a notification (EN 43197) to the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(v)(D), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident'. The notification was made as a result of an unexpected high level alarm condition for the High Pressure Coolant Injection (HPCI) system barometric condenser, which was received during the post-maintenance operability testing of the HPCI system. "Revised Basis for Retraction "On April 26, 2007, EN 43197 was retracted. The basis for the retraction stated that the 2-E41-F048 functioned properly and adequate HPCI lube oil cooling existed. It also attributed the high level in the HPCI barometric condenser to either a missing lube oil cooler outlet orifice or potential sticking of valve 2-E41-F058 versus the originally believed malfunction of the 2-E41-F048 valve. In either case, the retraction stated that if the barometric condenser becomes completely full, a relief valve (2-E41-F018) on the tank will lift and relieve water to the HPCI room sump. The room sump pump has adequate capacity to keep up with the maximum expected flow. As such, operability of the HPCI system would not be affected by either a missing lube oil cooler outlet orifice or potential sticking of valve 2 -E41-F058. "During the Unit 2 refueling outage, which began on February 28, 2009, it was discovered that the HPCI barometric condenser relief valve (2-E41-F018) had been assembled incorrectly and would not have functioned as described in the April 26, 2007 retraction of EN 43197. However, EN 43197 can be retracted without relying on proper operation of the relief valve. At the time of the event, the HPCI barometric condenser condensate pump, the HPCI barometric condenser vacuum pump, and the HPCI barometric condenser water level instrumentation were functioning properly and would have prevented condensate from reaching the HPCI turbine casing. On this basis, the HPCI system was capable of performing its function to mitigate the consequences of an accident and the issue is not reportable under 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector was notified of this revised retraction." Notified R2DO (Mark Lesser) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2009-06-04
43196 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2007-02-27 23:33 | 2007-02-28 02:04 | 2007-02-28 | REACTOR TRIP DURING THE PERFORMANCE OF A SURVEILLANCE "On 2/27/2007 at 2333 CST a Reactor Trip occurred during performance of a surveillance procedure calibrating a Nuclear Power Range instrument. The Reactor trip resulted in an automatic Turbine Trip and actuation of the Auxiliary Feedwater System. No safeguards equipment was out of service at the time of the trip. Following the trip, a steam inlet valve on a Moisture Separator associated with the main turbine failed to close which resulted in RCS temperature decreasing to 537 degF. This valve was manually isolated and RCS temperature returned to normal 547 degF. Normal heat sink to the Main Condenser was available during the event. Investigation is continuing into the exact cause of the Reactor trip. "This event is being reported under 10CFR50.72(b)(2)(iv)(B) for actuation of the Reactor Protection System and 10CFR50.72(b)(3)(iv)(A) for actuation of the Auxiliary Feedwater System." All control rods fully inserted on the reactor trip. Decay heat is being removed by Auxiliary Feedwater feeding the steam generators, steaming to the main condenser. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-02-28
43195 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-02-27 19:47 | 2007-02-27 22:15 | 2007-02-27 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO FAILED SURVEILLANCE TESTING "Both Trains of Emergency Core Cooling System (ECCS) Pump Room Exhaust Air Cleanup System (PREACS) were declared inoperable at 1620 when dampers 2-HV-AOD-228-1 and -2, Safeguards Area Exhaust Bypass Dampers, failed surveillance testing. A ramp down was initiated at 1947 as required by Technical Specification 3.0.3. "Temporary repairs to the dampers were completed at approximately 2125 and the ramp down was terminated." Temporary repair was made to the bypass damper seating surface. The licensee notified the NRC Resident Inspector. | 0 | 35 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-02-27
43194 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2007-02-26 15:14 | 2007-02-27 19:29 | 2007-02-27 | VOLUNTARY NOTIFICATION REGARDING RADIOACTIVE WASTE SHIPPING CASK CONFIGURATION "This voluntary notification is being made to inform the NRC of a condition that may be of interest to the public. "Upon arrival at the Barnwell South Carolina waste disposal facility, a shipping cask containing irradiated hardware that was shipped from Nine Mile Point Nuclear Station (NMPNS) [Unit 2] was observed to have a number of bolts that were not fully torqued [Six of 12 bolts were not fully torqued]. The subject bolts secure the cask base plate to the cask body. There was no radiological safety concern associated with the bolting condition as survey results confirmed that no radioactivity leaked from the cask. This issue has been entered into the NMPNS corrective action program and an investigation is underway to determine the cause of the as-received bolting condition." The licenses notified the NRC Resident Inspector and New York Public Service Commission. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2007-02-27
43193 | -1 | HANNIBAL CLINIC |  |  |  |  | 2007-02-27 08:30 | 2007-02-27 15:20 | 2007-03-05 | MEDICAL EVENT - TREATMENT TO WRONG PATIENT Patient "A" was suppose to receive a non-nuclear stress treatment by a technologist. Patient "B" was suppose to receive a nuclear treatment by a technologist. Patient "B" did not show up for the scheduled appointment. The technologist mistakenly gave patient "A" an injection (0.67 ml) of Tc-99m Cardolite (15 millicuries), which was suppose to go to patient "B". The attending physician notified patient "A" of this error, and deemed no corrective action to the patient was necessary. The error was determined to be that the technologist did not follow procedures, which is to verify patient name. As a corrective measure, the technologist was provided additional instruction in this matter. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. *** UPDATE FROM HASSIEN TO KNOKE AT 11:50 ON 03/05/07 *** The RSO called to retract this event stating that patient "A" did not reach the threshold of effective dose equivalent. Notified R3DO (Orth) and FSME (G. Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2007-03-05
43192 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-09-27 | 2007-02-27 14:04 | 2007-03-01 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT At 1405 EST on 02/26/07, the state received a report via the US Mail from Akron General Medical Center. On 09/27/06 a patient was receiving a 10 fraction dose for Mammo-site Breast Brachytherapy using a HDR afterloader with a total prescribed dose of 3400 RAD. A problem with the PLATO planning computer digitized the breast image using an incorrect treatment factor which doubled the fractional dose. The same total prescribed dose was delivered but in 5 vice 10 fractional doses. The patient was made aware of the error on 09/27/06. Tissue necrosis was observed due to the procedure, but it is being evaluated if any additional necrosis occurred due to the delivery of the total dose in 5 fractions vice the 10 planned fractional doses. The licensee is taking corrective action to prevent a reoccurrence of this type of error. * * * UPDATE FROM FSME (FLANNERY) TO KNOKE ON 02/28/07 * * * This event has been reviewed and determined to be a reportable medical event. * * * UPDATE FROM OHIO DEPARTMENT OF HEALTH (MARK LIGHT) TO HUFFMAN ON 03/01/07 AT 1000 EST * * * The State provided the following update to this report via facsimile: "On September 28, 2006, the licensee notified the ODH Bureau of Radiation protection that they had an event which did not meet the reporting requirement of a medical event but they were revising their HDR program to prevent a recurrence. The Bureau requested a report that was received on February 26, 2006. The patient was to receive a total dose of 3400 rad total dose through 10 fractions of 340 rad each. The patient received 5 fractions of 680 rad for a total dose of 3400 rad. Upon review of the report it was determined by consultation with NRC Region 3 that a medical event did occur because 'Prescribed Dose' for remote afterloaders includes Total Dose and Fractionated dose. The reason for the event was the Physicist entered the wrong planning film magnification into the treatment system. The patient has experienced some tissue necrosis at the treatment site, although some necrosis is expected with this therapy (MammoSite). The necrosis may have been exacerbated by the dosage scheme. The patient is being followed by her attending physician. The patient and attending physician were notified on 09/27/2006. The Bureau conducted an inspection on November 2, 2006 and identified problems with the licensee's HDR program an additional inspection will be conducted during the week of March 5, 2007." The R3DO (Lanksbury) and FSME EO (Morell) were notified. Ohio Report OH2007-11 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2007-03-01
43191 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-02-27 13:11 | 2007-02-27 13:11 | 2007-03-03 | PLANNED MAINTENANCE ON SPDS "On February 28, 2007, the Safety Parameter Display System (SPDS) will be removed from service to perform planned maintenance to the system. The maintenance will improve the overall reliability of the system. The removal of SPDS from service for Hope Creek also affects the transmission of data via the Emergency Response Data System (ERDS). Appropriate compensatory measures will be in place while SPDS is out of service. The SPDS is expected to be returned to service in approximately 2 days." The licensee notified the NRC Resident Inspector and will be notifying local officials. * * * UPDATE AT 0330 ON 03/03/07 FROM T. FOWLER TO W. GOTT * * * SPDS maintenance has been completed. The ERDS system has been returned to service, tested, and considered operational at 2100 on 03/02/07. The licensee will notify the NRC Resident Inspector. Notified R1DO (J. Rogge) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-27
43190 | 0 | CARRIER CORPORATION |  |  |  |  | 2007-02-27 | 2007-02-27 09:48 | 2007-08-23 | CHILLER COPPER SLEEVE CRACKS LEADING TO SLOW REFRIGERENT DISCHARGE Manufacturer provided the following information via facsimile: Carrier Corporation provided the following information of a potentially reportable condition regarding a Compressor and Bearing Discharge Temperature Sensor, Carrier Part #17FA999-1200-381 supplied by Carrier Corporation's Replacement Components Division to PSE&G Nuclear, LLC for use at Hope Creek Nuclear Station. "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "The operative portion of the Sensor is encased in a copper sleeve 1 1/2 inch in length and 1/4 inch in diameter which is soldered to a brass fitting, which fitting couples the Sensor to the chiller to be monitored. PSE&G notified Carrier of four (4) separate instances where a crack occurred in the Sensor's copper sleeve. This crack did not affect the Sensor's ability to function and the Sensors did not cease to function. However, the crack in the Sensor's copper sleeve did result in a leak of refrigerant from the compressor of the chiller to which the Sensor was coupled. Three (3) of these four (4) instances were noted on chillers with safety-related applications, while the fourth was noted on a chiller dedicated to a non-safety application. "PSE&G noticed the fast refrigerant leak during a routine, visual equipment inspection. As a result of this discovery, the Sensor was replaced, but a similar refrigerant leak was noticed approximately three (3) months thereafter. At approximately the same time, during pressure testing of another safety-related chiller, PSE&G noticed a similar refrigerant leak. "Safety Hazard which could be created by such a defect: While the refrigerant leak appeared to have been a slow process occurring over some period of time, had that refrigerant leak continued uncorrected, the result would have been a loss of enough refrigerant such that the chiller would be automatically shut down by a separate safety feature. Since mid- 2001 Carrier has sold the sensor to the following facilities: NRC Region 1: Limerick Generating Station, PSE&G (Hope Creek Generating Station, Salem Generating Station) NRC Region 2: Catawba Nuclear Station, McGuire Nuclear Station NRC Region 3: Braidwood Station, Perry Nuclear Power Plant NRC Region 4: San Onofre Nuclear Generating Station, Waterford 3 Steam Electric Station * * * UPDATE ON 8/23/07 AT 1424 FROM IWACHIW TO SNYDER * * * Manufacturer provided the following information via facsimile: "In response to the notice of a potential defect or failure to comply received from PSE&G, along with a report of various analysis conducted by PSE&G, Carrier convened its 'Nuclear Defect Review Board' (NDRB) to review and respond to PSE&G's notice and report. "As part of its review, Carrier's NDRB requested various additional information from PSE&G regarding the Sensor's alleged defect or failure to comply experienced by PSE&G, as well as its use and operation of the Sensor and the chillers utilizing the Sensor. The chiller use and operation data provided by FSE&O showed that the chiller was run under such an extremely light cooling capacity that Carrier has no reference test data or experience available. As a result, Carrier cannot accurately predict the effects of this low cooling capacity on the operation of the Sensor. "Carrier's NDRB also reviewed Carrier's current process of brazing the Sensor's copper sleeve, as compared to the brazing process utilized when the Sensor was first offered for sale approximately 30 years ago. Carrier's NDRB commissioned testing by a third party firm to determine if changes in the brazing process had any impact on the hardness or grain size of the Sensor's copper sleeve. This testing determined that there was no significant difference in the hardness of the Sensor's copper sleeve between a sample using the original brazing method, another sample using the current brazing method and a third sample using an alternate brazing method not previously or currently in use in connection with the Sensor. In addition, the firm indicated that it is typical that a lack of significant difference in hardness will also be an indicator of a lack of significant difference in grain size. "Carrier's third party test results showing no change in hardness or grain size, PSE&G's operation of the associated chiller at an extremely light cooling capacity and the fact that the PSE&G failures were very isolated occurrences have convinced Carrier's NDRB that the cause of the potential defect or failure to comply was other than a defect inherent in the Sensor. Rather, Carrier's NDRB believes that the potential defect or failure to comply resulted from a cause or causes external to the Sensor. "Carrier plans to work with PSE&G over the next sixty (60) days to explore these possible external causes and to take corrective actions, as may be necessary, to limit the effects of these external causes on the Sensor and/or to modify the Sensor to better operate in the presence of these external causes. "In addition to the above actions, on June 8, 2007, Carrier personnel made a visit to PSE&G to collect vibration data at the point of failure. The data collected and analyzed showed no abnormalities that would cause cracking of the sensor at the copper sleeve braze joint location. "Conclusion: "Carrier is unable, at this time, to determine the root cause of the defect. "Post Evaluation Actions "Upon completion of Carrier's evaluation, analysis and conclusions, Carrier's Nuclear Defect Review Board (NDRB) was reconvened. The NDRB determined that the supplier of the sensor would be asked to provide a modified design of the sensor to eliminate any future potential failures/defects that could result in sensor cracking and subsequent refrigerant leakage. The supplier has complied and provided a modified design of the sensor which has been approved by the NDRB. "At the present time, the modified sensor is in production. Essentially, the modification involved complete elimination of the sensor's brazed joint. This improved design consists of a probe body manufactured from a single, solid piece of brass, thus eliminating the copper sleeve portion of the probe and the braze joint, from which there could be a possible leak path thru the sensor body. Additionally, the wall thickness of the body has been increased by approximately four times its original thickness. These changes will not impact the fit or function of the sensor. In addition, prior to production for sale, the modified sensor was tested, to determine if the heavier wall would have an impact on the sensors response time. There was little if any change in the sensor's response time. The modified sensor's body is made from the same brass material as the threaded portion of the previous two piece design. The form changes slightly due to the increased wall thickness. "Any advice related to the defect or failure to comply about the facility activity, or basic component that has been, is being or will be given to purchasers or licensees. "Effective July 30, 2007, any purchase orders (PO's) or requests for quotation (RFQ's) received by Carrier for the 17FAS99-1200-381 sensors will be of the modified design described above. Carrier will notify all utilities that may have inventory of the previous design that these sensors may still be used, but only in the Bearing Temperature application, not in the Compressor Discharge Temperature application. Carriers notice will also request the utilities to segregate all previous sensor designs and clearly label them 'For Bearing Temperature Sensor Use Only. Do Not Use As Replacement for Compressor Discharge Temperature Sensor'." Notified R1DO (Dwyer), R2DO (Payne), R3DO (Lara), R4DO (Clark) and NRR (Hodge and Thorp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2007-02-27
43189 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2007-02-27 09:41 | 2007-02-27 10:36 | 2007-02-27 | FIRE INSIDE THE UNIT 3 TURBINE AREA LOAD CENTER At 0941 the licensee declared an unusual event at the site due to a fire in the protected area not extinguished in less than 15 minutes (EAL HU-6). The fire is located in the Unit 3 Turbine Area Load Center cubicle. The fire has affected Unit 3 bus duct cooling so the licensee is currently reducing power. The fire is currently out but the licensee is assessing conditions in the area. The licensee will do a thorough analysis of the affected load center to determine the extent of damage before officially exiting the unusual event. All emergency diesel generators and emergency core cooling systems are fully-operable and available if needed. The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 02/27/07 AT 1147 EST BY ADAM FRAIN TO MACKINNON * * * Unusual Event exited at 1137 EST. R1DO (Rogge), NRR EO (M.J. Ross-Lee), IRD Manager (T. Blount), FEMA (Fuller) and DHS SWO (Haselton) notified. | 0 | 60 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-02-27
43188 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-02-26 | 2007-02-26 15:31 | 2007-04-02 | AGREEMENT STATE REPORT "On 2/26/07 at about 13:30 the licensee notified the Agency that they had received 8 sources from White Sands Missile Base containing cobalt sixty (Co-60) sources. Four were estimated to have activities of 3,000 curies and four had estimated activities of 1,000 curies. Southwest opened one of the containers used to ship the sources to leak test the source. Upon opening the container, it appeared that the source was no longer contained in a source capsule. The leak test results indicated 5 million DPM. The container was resealed and no other containers were opened." Containers were opened with automation equipment, therefore no exposure to personnel occurred. TX Report TX-07-43188 * * * UDPATE ON 02/27/07 AT 0950 EST FROM ARTHUR TUCKER VIA E-MAIL TO MACKINNON * * * "On 2/26/07 at about 11:00 the licensee notified the Agency that they had received eight (8) cobalt sixty sources from White Sands Missile Range. Each of the eight sources was contained in a separate container. Four sources had estimated activities of 3,000 curies and four had estimated activities of 1,000 curies. The outside of each container was surveyed after receipt and contamination levels were found to be below their limits. SWR opened one of the containers used to ship the sources to leak test the source. The source was a Neutron Products Inc. model no. NPU-25-13000 capsule serial # T-96-5. The container was opened in SWR hot cell using manipulator arms. Upon opening the source container, it appeared that the source capsule had been breached. The leak test results indicated 5 E6 dpm of contamination. The container was sealed and no other sources were opened. The sources were removed from the hot cell. The hot cell was surveyed and found to be contaminated. The hot cell was decontaminated and returned to service. R4DO (Dale Powers) & NMSS EO (Greg Morell) notified. * * * UPDATE PROVIDED BY ART TUCKER (STATE OF TEXAS) TO JEFF ROTTON AT 1652 EDT ON 04/02/07 * * * "The State of Texas, Department of State Health Services, Radiation Control Program, is retracting event number TX-07-43188 [NRC EN #43188]. The eight sources sent to Southwest Research of San Antonio, Texas, were included in a group of sources identified at White Sands Missile Range in 1996 by the Nuclear Regulatory Commission (NRC) as failing during use. NMED item Number 960300, [and] NRC EN# 30353 documents this as well as an Executive Summary Report done by the United States Army. These sources were removed from service, and the source carrier and source itself were redesigned to operate as required. The State was not aware that the NRC had already addressed the source failures prior to sending our Event Notification [#43188] to the NRC." R4DO (Chuck Cain) & FSME EO (Larry Camper) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-03-01
43187 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-02-26 04:00 | 2007-02-26 09:41 | 2007-02-27 | TECHNICAL SUPPORT CENTER CHILLER MALFUNCTION "During the performance of rounds by a System Operator it was noticed that area temperatures in the TSC seemed higher than normal. The Control Room was notified and after investigating found that the TSC chiller was not running. An attempt was made to reset the freeze protection relay per the annunciator response procedure. The chiller would not start. Maintenance has been notified to investigate and repair the chiller. The importance of returning the chiller to service in a timely manner has been communicated to maintenance personnel and they will they will restore the chiller to operational status as soon as practical." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY THOMAS PETRAK TO JEFF ROTTON AT 1524 EST ON 02/27/07 * * * One of two TSC Chiller compressors had failed. The failed compressor has been disabled and the chiller package returned to service on 2/26/2007 @ 13:24. The capacity of one compressor is sufficient to handle the design heat load. Ventilation, filtration and pressurization of the TSC HVAC were not affected by the failed compressor. A replacement compressor and fan are expected on-site by 3/1/2007 and repairs should be complete by 3/2/2007. The licensee will notify the NRC Resident Inspector. Notified R2DO (Seymour) | 98 | 100 | 0 | 98 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-26
43186 | -1 | PALISADES | 1 |  |  | [1] CE | 2007-02-25 13:00 | 2007-02-25 17:49 | 2007-09-14 | DEGRADED ELECTRICAL CABLES TO CCW SYSTEM "On February 17, 2007, it was discovered that cables in a cable tray associated with the Component Cooling Water (CCW) system and Service Water system had sustained external damage by the heat effects from an un-insulated pipe that was in close proximity to the cable tray. "On February 25, 2007, at 1100 hrs, as a result of continued evaluation of the cables in the cable tray and the discovery of a cable with unacceptable cable damage, it was determined that all cables located within the cable tray at the effected zone (that were not already isolated or replaced) were inoperable due to the loss of qualification life and the potential for cable-to-cable interaction from degradation of the cable insulation. This condition could potentially result in spurious equipment operation, causing components to be positioned in other than their desired safety position. "Subsequently, on February 25, 2007, at 1300 hrs, it was recognized that a specific combination of two postulated cable faults could affect the CCW system resulting in a condition where there would be less than 100% of the required CCW post accident cooling capability, per Technical Specification (TS) 3.7.7.C. As a result, TS 3.0.3 was entered. At 1322 hrs, TS 3.0.3 was exited, following isolation of one of the two postulated cable faults, which restored the capability for 100% of the required CCW post accident cooling. "The condition of potentially having less than 100% of the required CCW post accident cooling is reportable per 10 CFR 50.72(b)(3)(v)(B) as a condition that could have prevented the fulfillment of the safety function of structures or systems (CCW system) that are needed to remove residual heat." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY BARB DOTSON TO JASON KOZAL ON 9/14/07 AT 1523 * * * "EN #43186 reported on February 21, 2007, that cables associated with the component cooling water system had sustained external damage by the heat effects from an uninsulated pipe in close proximity to the cable tray. This was reported as a condition that could have prevented the fulfillment of the safety function of the component cooling water system, which is needed to remove residual heat. "Subsequent evaluation of past operability concluded that these cables would not have failed as postulated, and are considered to have been operable. Therefore, the condition did not prevent fulfillment of a safety function and EN #43186 is being retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (S. Burgess). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2007-02-25
43185 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-02-24 17:56 | 2007-02-24 23:03 | 2007-02-24 | LOSS OF NORMAL ELECTRICAL LINEUP DUE TO GRID INSTABILITY FROM ADVERSE WEATHER CONDITIONS "Immediate notifications are being made for the following events: 1) Valid RPS non-critical actuation: 8 hour notification per 50.72(b)(3)(iv)(B) 2) Group 1, 2, 3, 4 and 5 isolations: 8 hour notification per 50.72(b)(3)(iv)(B) 3) Loss of decay heat removal (RHR Shutdown Cooling) isolated: 8 hour notification per 50.72(b)(3)(v)(A) 4) Auto start of 'A' Standby Diesel Generator and subsequent pick up of essential buses by both 'A' and 'B' Standby Diesel Generators: 8 hour notification per 50.72(b)(3)(iv)(A). "Just prior to the event the plant was in Mode 5 with core alterations in progress and the 'B' Standby Diesel Generator being run manually for post maintenance testing. At 1756 hours on 2/24/2007, core alterations were halted due to indications that the grid was becoming unstable. Freezing rain had been in progress all day. At 1757 hours an electrical transient occurred as some of the offsite lines coming into the switchyard were lost. The 'B' Reactor Protection System (RPS) bus was lost. A full RPS trip occurred from loss of the 'B' RPS bus and too few inputs to the 'A' RPS trip logic. The loss of 'B' RPS power resulted in Groups 1, 2, 3, 4 and 5 isolations. The Group 4 isolation caused a loss of decay heat removal capability (RHR Shutdown Cooling isolated). The 'A' Standby Diesel Generator auto started, but the 1A3 essential bus remained powered from offsite sources. The 'B' SBDG was already running. The 1A4 bus also remained powered from offsite sources. At 1820 hours, a degraded voltage trip signal was received resulting in both emergency diesel generators picking up their respective buses. "At present, the essential buses 1A3 and 1A4 are being carried by the emergency diesel generators. Only one of the six lines supplying offsite power to the site is available. Both non-essential buses are being powered from the one offsite line. The emergency buses will remain on the emergency diesel generators until additional offsite lines can be restored. RHR Shutdown Cooling was restored at 1826 hours." The licensee notified the NRC Resident Inspector, State and local officials. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | VALID SPECIF SYS ACTUATION |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2007-02-24
43184 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2007-02-24 19:20 | 2007-02-24 21:38 | 2007-02-26 | REDUCTION IN EMERGENCY PREPAREDNESS CAPABILITY "On February 24, 2007, at 1820 hours, 13 of 51 alert sirens in the Quad Cities Station Emergency Planning Zone were determined to be inoperable. This is considered a major loss of the Quad Cities offsite notification capability. The alert sirens were disabled due to a loss of power. Power was lost due to a major winter storm in the area. Repairs are in progress at the time of this notification. This report is being made due to the reduction in public notification capabilities in accordance with 10CFR50.72(b)(3)(xiii)." He licensee notified the NRC Resident Inspector, and will be notifying the State. * * * UPDATE AT 2006 ON 02/26/07 FROM JIM STORTZ TO W. GOTT * * * This is a follow up notification to report that only 4 sirens remain inoperable with no estimated time of repair due to downed poles and high voltage power lines on the ground. This is also to correct the number of alert sirens available in the Quad Cities Station Emergency Planning Zone. There are 52 sirens not 51 reported in the original report. With 48 of the 52 alert sirens operational, the station no longer meets the reporting criteria. Notified R3DO (R. Lanksbury) | 97 | 96 | 0 | 97 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-24
43183 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2005-02-22 06:00 | 2007-02-23 20:43 | 2007-03-01 | AGREEMENT STATE REPORT - MISPLACED SOURCE CAUSES POSSIBLE OVEREXPOSURE At approximately 0600 on 2/22/07 while loading a well logging source (Gulf Nuclear CSV H90 1 Curie Cs-137 source) into the pig on the truck, the crew unknowingly dropped the source in the motor pool parking lot. The source was picked up by a mechanic at approximately 0900 and he put it in the pocket of his jacket. He did not realize that it was radioactive, but thought it might be a part to something. The mechanic wore the jacket for about 4 hours. He visited several businesses including a sandwich shop. He hung the jacket in the break room where it remained for the remainder of the day and over night. On 02/23/07, the mechanic put the jacket back on. The well logging crew returned to the facility at approximately 0600 and discovered that the source was missing when they unpacked their equipment. The crew did not discover the missing source earlier because they did not need to use the source on a job site. The crew immediately started a search for the source. The mechanic produced the source when he heard that it was missing. In total the mechanic wore the jacket about 5.5 hours over the 24 hour period. This is an estimate based on an interview with the mechanic who was uncertain about the exactness of his recollection for the time he wore the jacket. The mechanic and a couple of coworkers were taken to a local hospital emergency room and examined. No abnormalities were noted. They are scheduled to return to the emergency room on 2/24/07. Oklahoma continues to investigate. There has been no media interest. The R4 PAO (V. Dricks) was also notified. * * * UPDATE ON 02/24/07 AT 1025 EST BY MIKE BRODERICK TO MACKINNON * * * Patient received two white blood cell counts, one on 02/23 and the other on 02/24, at Integris Baptist Hospital, Oklahoma City, Oklahoma, and both white blood cell counts were normal. The Doctor does not think the patient received a large dose. Patient is to report back in 1 week for follow-up testing. A blood sample of the patient will be sent to RPA located in London, England for chromosome analysis. R4DO ( Bill Jones) and NMSS EO (Joe Holonich) notified. * * * UPDATE ON 02/24/07 AT 1228 EST BY MIKE BRODERICK TO W. GOTT * * * The patient visited the hospital emergency room again on 2/24/07. The ER Physician stated there was no sign of radiation effects. Oklahoma is arranging for the exposed individual to see a radiologist and/or oncologist at the OU Health Sciences Center. Blood samples will be drawn and provided to RPA in the UK for chromosome analysis. The state investigation is continuing. R4DO ( Bill Jones) and NMSS EO (Joe Holonich) notified. * * * UPDATE ON 02/26/07 AT 1117 EST BY MIKE BRODERICK TO P. SNYDER * * * The state provided a matrix of dose rate readings taken around the source by the licensee. The state is evaluating the information. The NRC continues to interface with the state on this event. Notified R4 (C. Cain), R4DO (D. Powers) and NMSS EO (S. Wastler). * * * UPDATE ON 02/26/07 AT 1255 EST BY MIKE BRODERICK TO J. KNOKE * * * "When the mechanic removed the jacket containing the source, he initially hung it on a bollard (cement & metal post to keep vehicles away from a building) outside the logging company office. It was there all afternoon, the assistant mechanic stated that he was working in that area, so he has the possibility for exposure. The mechanic who was the main exposed person moved the jacket to the company break room at quitting time. There were staff working around the clock Thursday night, so there is a definite possibility staff were near the jacket while it was hanging there. Fortunately, the break room is small (more like a large closet) so most likely they would have gotten coffee and left. We will be interviewing staff this afternoon to try to nail this down." "The exposed individual will see a very well-qualified physician, this afternoon. DEQ staff asked him to sign medical releases authorizing release to DEQ and to NRC. A blood sample will be taken and shipped to England for chromosome analysis. "DEQ staff will be doing interviews this afternoon with facility staff who were potentially exposed to the source. DEQ staff will use this information to determine who else may warrant medical follow-up. We will also get confirmatory readings on the radiation level of the source with an ion chamber (as opposed to the GM tubes used by the company measures sent earlier). Notified R4 (C. Cain) Email only, R4DO (D. Powers) and NMSS EO (S. Wastler). * * * UPDATE ON 02/26/07 AT 1908 EST BY MIKE BRODERICK TO W GOTT * * * "The primary exposed individual ('A') has been seen by a physician from the OU Health Sciences Center who has strong radiation protection credentials. The physician's belief is that the patient will probably suffer radiation burns on his abdomen, and possibly on his fingertips. He doesn't expect any other short-term effects. No burns or other effects are visible now. There is no sign of GI tract syndrome. 'A' is going to have follow-up visits with the physician at one week and two weeks, and possibly additional visits. "A blood sample has been taken from 'A' and tomorrow it will be shipped to England for chromosome analysis. There was some delay due to international shipping requirements for biohazardous material. "DEQ and OU HSC staff worked together this afternoon to take measurements using ion chambers. The measurements showed lower readings than those calculated through inverse square law. We will prepare a detailed report tomorrow and send it. In short, the dose level with the ion chamber case in contact with the source was 3.3 rem/hour, falling off to 139 mrem/hour at one meter. A badge was exposed to the source at one inch for 3 minutes 35 seconds, and is being sent to Landauer for emergency processing, which will give us more information. "DEQ staff interviewed additional personnel at the licensee this afternoon, focusing on determining who might have been exposed to excess dose other than 'A.' Tentatively, the most at-risk individual appears to be a coworker who rode with 'A' to lunch. While they were in the cab of a pickup truck, the coworker was sitting in the passenger seat on the opposite side of 'A's' body from the source, and across a sandwich shop booth from 'A' during lunch. After lunch, 'A' and the coworker worked together on a logging truck with the coat (and source) hanging a couple of yards away. They spent most of their time under the truck, which would have provided considerable shielding. Tentatively we think it is conceivable the coworker broke the limit for dose to the public, but doubt there was medically significant exposure. We will do a detailed analysis tomorrow to test this." Notified R4DO (D. Powers) and FSME EO (J. Holonich) * * * UPDATE PROVIDED BY MIKE BRODERICK TO JEFF ROTTON VIA EMAIL AT 1723 EST ON 02/27/07 * * * "The results for the dosimeter that was exposed to the Cesium source at one inch for 3 minutes 35 seconds were reported from Landauer this afternoon. Deep dose was 16,106 mrem and shallow dose was 15,374 mrem. This works out to about 4.4 R/minute or 264 R/hour skin dose. "The package containing the blood sample from 'A' was shipped to England via overnight delivery this afternoon. Results are expected in the first half of next week." The results of the examination of 'A' by an OUHSC radiologist have been received and will be combined with the ER records from the weekend and faxed to the NRC on 02/28/07. The results were not substantially different from the verbal report on 02/26/07 and described in the update on the afternoon of 02/26/07. Notified R4DO (Powers) and FSME EO (Mohseni). * * * UPDATE PROVIDED BY MIKE BRODERICK TO BILL HUFFMAN AT 0030 EST ON 03/01/07 * * * OK DEQ provided corrections to the previous report information. Specifically, the well logging source was originally reported to be a directional source. DEQ states that the source was not a directional source. In addition, the update on 2/27/07 reported a dose rate of 4.4 mrem/minute. This should have been 4.4 Rem/minute. The text of the previous report information has been corrected accordingly. Notified R4DO (Powers) and FSME EO (Davis). * * * UPDATE PROVIDED BY MIKE BRODERICK TO HUFFMAN AT 1000 EST ON 03/01/07 VIA E-MAIL * * * The blood sample for chromosomal analysis has arrived in England and been received in good condition. They advise us they expect results on Tuesday. Notified R4DO (Powers) and FSME EO (Morell). * * * UPDATE PROVIDED BY MIKE BRODERICK TO JASON KOZAL AT 1524 EST ON 03/01/07 VIA E-MAIL * * * "This morning the DEQ investigators visited the facility. We met with corporate management. They briefed us on their investigation and steps so far. They are doing root cause analysis of the incident. They will be doing several equipment upgrades to reduce exposure and increase certainty in handling sources. As a temporary measure they have removed the sources of the type in the incident (which did not have positive engagement of the source with the handling stick) from service until the handling sticks can be upgraded. They are doing additional staff training and will be seeking to change the safety culture at the company. As a temporary measure, they have a policy that a member of management must be present during all source handling at the shop. We explained our enforcement process to them. We informed management that based on calculations by NRC and DEQ, it appeared that a coworker of 'A' may have exceeded the dose limit for non-radiation workers, with a calculated dose of 140 mrem. We met with the coworker and explained his potential exposure, setting it in context by comparing it to the dose rate from natural background and the dose limits for radiation workers. As a precautionary measure, the company expects to do medical follow-up for this worker's exposure. We met with 'A' to follow up on his visit with a radiologist on Monday. He complained of nervous stress, but stated he had experienced no sensitivity or evidence of burns in the affected areas. We urged him to contact the radiologist immediately if he experienced any of the expected radiation symptoms. We asked 'A' some questions to clarify his interactions when he unknowingly had the source with him off-site. It does not appear that there was anyone off-site who had enough potential exposure to warrant follow-up." Notified R4DO (Powers) and FSME EO (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-02-28
43182 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2007-02-23 13:36 | 2007-02-23 15:55 | 2007-02-23 | SMALL NATURAL GAS LEAK AT GAS METER "On Friday 2/23/07 at approximately 13:36 EST the Ontario, NY Volunteer Fire Department arrived on site at the Ginna Training Center in response to a report of natural gas leak The report was made to the local gas utility by an employee of the facility. This report was not made through the normal channel of control room communications. Per the local gas utility response procedure, they notify the 911 Emergency call center, if their response time is greater than 30 minutes. The local television media responded to the site based on the 911 radio transmission. The Fire Department left site at 13:57 hours. The gas utility found a minor leak on the gas meter outside the building." The licensee notified the NRC Resident Inspector and is expected to discuss this incident with the media. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-02-23
43181 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2007-02-22 06:57 | 2007-02-22 08:36 | 2007-02-22 | EMERGENCY RESPONSE DATA SYSTEM INOPERABLE The licensee reported the loss of the Emergency Response Data System (ERDS) due to an Emergency Response Facility Computer System (ERFCS) failure at 0757 EST. The loss of the host computer was determined to be the cause of this unplanned outage. An unrelated planned outage of ERDS is scheduled to commence today following the troubleshooting. The planned outage duration will be 10 hours. The licensee will make an update notification when ERDS is restored. The licensee notified the NRC Resident Inspector. *** UPDATE FROM F. GIANNONE TO KNOKE AT 1846 ON 02/22/07 *** The licensee reported the Emergency Response Data System (ERDS) has been restored to normal operation. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-22
43180 | -1 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2007-02-21 21:02 | 2007-02-21 23:50 | 2007-03-02 | MISSING SAFEGUARDS INFORMATION The licensee has determined that some safeguards information is unaccounted for. There is no evidence that the material has been compromised. Compensatory actions have been taken. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. * * * RETRACTION RECEIVED FROM RUSSEL STROUD TO JOE O'HARA AT 1910 ON 3/2/07 * * * "This notification is being made to retract the February 21, 2007 Event Notification made by Arizona Public Service Company (APS) wherein it was reported that certain safeguards information, normally maintained in a locked and alarmed safeguards repository (vault), could not be accounted for. "APS has subsequently recovered evidence and developed information that provides reasonable assurance that the information was destroyed, and not unaccounted for, as originally reported." The licensee will notify the NRC Resident Inspector. Notified R4DO (Powers) and 73.71 Group via e-mail | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-02-22
43179 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2007-02-21 19:15 | 2007-02-21 22:11 | 2007-02-21 | AUTOMATIC REACTOR TRIP ON HIGH RCS PRESSURE FOLLOWING A FEEDWATER TRANSIENT "At 1915 on February 21, 2007, Crystal River Unit 3 was at reduced power (71%) for planned maintenance on one of four condenser waterboxes when the Integrated Control System (ICS) for Main Feedwater became erratic causing a feedwater transient that underfed the once thru steam generators. The reactor protection system (RPS) actuated on high Reactor Coolant System pressure causing a reactor trip. CR3 also received an Emergency Feedwater Actuation (EFIC) on low steam generator levels. This event is reportable as a 4-Hour Non-Emergency Notification per 10CFR50.72 (b)(2)(iv)(B) for Reactor Protection System Actuation and as an 8-Hour Non-Emergency Notification per 10CFR50.72 (b)(3)(iv)(A) for Emergency Feedwater Actuation and for Reactor Protection System actuation. All systems responded as designed and the plant remains stable with Emergency Feedwater in MODE 3." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 71 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-02-21
43178 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-02-21 13:30 | 2007-02-21 20:37 | 2007-02-21 | ALTERNATE EOF UNAVAILABLE "While the normal Emergency Operations Facility (EOF) was unavailable due to modification, the space that is utilized for the Alternate EOF was in a locked condition and it is normally not locked. This condition was discovered during the dayshift and was readily corrected. However, had the facility been required during off hours it would have delayed activation of the Alternate EOF. "Additionally, activation of the Alternate EOF would have been hampered by key availability to the facility storage room and supply cabinet. "Access to Alternate EOF and equipment has been restored." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-21
43177 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2007-02-20 17:20 | 2007-02-20 19:52 | 2007-03-05 | HPCI DECLARED INOPERABLE DUE TO AN APPARENT EQUIPMENT MALFUNCTION "On February 20, 2007 at 1720 hours, the High Pressure Coolant Injection (HPCI) system was declared inoperable. During a system walkdown the HPCI Motor Speed Changer (MSC) was discovered energized. The MSC controls HPCI turbine speed during system startup and shutdown, and should not have been energized at the time of the walkdown. Additional troubleshooting determined the MSC was not functioning properly, rendering the HPCI system inoperable. This event is being reported as a condition that could have prevented fulfillment of a safety function in accordance with 10CFR50.72(b)(3)(v)(D) because the HPCI system is a single train system and the loss of HPCI could impact the plant's ability to mitigate the consequences of an accident. In accordance with Technical Specification Action 3.5.1.F, the Reactor Core Isolation Cooling (RCIC) system was confirmed operable. Further troubleshooting and engineering evaluations are continuing." The licensee informed the NRC Resident Inspector. * * * RETRACTION AT 1146 ON 3/5/2007 FROM ERIK MARKS TO MARK ABRAMOVITZ * * * "The purpose of this report is to retract the ENS report made on February 20, 2007 at 1720 hours (ENS #43177) under 10CFR50.72(b)(3)(v)(D), a condition that could have prevented fulfillment of a safety function. The initial report was made when the Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable following a system walkdown that discovered the HPCI Motor Speed Changer (MSC) was energized. The MSC controls HPCI turbine speed during system initiation, and should not have been energized at the time of the walkdown since the system was not in operation. During troubleshooting the MSC responded slower than expected. Due to this unexpected behavior, it was not certain if HPCI could have met its design basis requirements. However, a subsequent engineering evaluation has determined that at the time of discovery, the HPCI system injection time would have been sufficient to meet its safety function. Repairs to HPCI were completed and the system was declared operable on February 22, 2007 at 0036 hours." The licensee notified the NRC Resident Inspector. Notified the R3DO (Orth). | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-02-20
43176 | 0 | ENVIRONMENTAL PROTECTION AGENCY |  |  |  |  | 2006-12-18 | 2007-02-20 17:30 | 2007-02-21 | DEVICE CONTAINING RADIOACTIVE SOURCES INADVERTENTLY SENT TO RECYCLING FACILITY "The U.S. Environmental Protection Agency's Region 2 is reporting that an X-ray fluorescence analyzer (model X-Met 880) bought by an EPA contractor in 1990 intended for handing over to EPA REAC/ERT, a headquarters facility in 1995, was inadvertently picked up on December 18, 2006 from the EPA Region 2 facility in Edison, NJ. EPA Region 2 health & safety personnel were notified on Friday afternoon, February 16, 2007, that the analyzer sent with other equipment to a Canadian recycling facility was screened, found to contain a radioactive component, and set aside under lock and key. This was inconsistent with information that sources were removed from any equipment sent. Contact was successfully made with the recycling facility on Tuesday after President's Day, February 20, 2007, confirming that the facility had detected the sources in the analyzer. Region 2 staff has also endeavored to contact EPA headquarters personnel thought to have responsibility for this analyzer, but as of this writing have not received a response. "The analyzer, containing 100 mCi of Cm-244 and 30 mCi of Am-241 is intact, in its original case and is secured by the company awaiting return to EPA. If Region 2 EPA is the party that must take this back then it plans to have the unit wipe tested before return." * * * UPDATE 1420 EST ON 2/21/07 FROM QWONG CHO TO S. SANDIN * * * The device was purchased by Roy F. Weston Corp. while under contract to the U.S. EPA and was stored in a locked warehouse in Edison, NJ since approximately 1995. The Model X-Met 880 S/N is 144216 and the two sealed source S/N's are 2765LX (Am-241) and 1951LM (Cm-244). The device is currently in the custody of Maser Canada, Inc. located in Barrie, Ontario pending arrangements for its return. The Canadian Nuclear Safety Commission is aware of this incident. Notified R1DO (Jackson) and FSME (Morell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-02-21
43175 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2007-02-20 12:30 | 2007-02-20 15:06 | 2007-02-20 | AGREEMENT STATE - STOLEN TROXLER MOISTURE DENSITY GAUGE "The New Hampshire Department of Health and Human Services, Division of Public Health Services' Radiological Health Section was notified at approximately 1:45 p.m. on Tuesday, February 20, 2007, by a representative from John Turner Consulting, Inc., of the theft of a portable soil moisture/density gauge from its vehicle on Tuesday afternoon, February 20, 2007, which was located at the licensee's facility in Dover, New Hampshire. The Licensee reported that a Troxler Model 3430 (Serial # 36724) portable gauge containing 9 millicuries of Cesium-137 and 44 millicuries of Americium-241: Beryllium was stolen from the licensee's vehicle parked at the licensee's facility located in [address deleted] Dover, New Hampshire. The locked gauge was padlocked in its original carrying case, which was attached to the bed of the vehicle with two chains with two separate locks. The State is following the incident. Local law enforcement has been notified by the licensee. Follow-up information will be provided to NRC." NH Event Report ID No.: NH-07-001 * * * UPDATE PROVIDED BY STATE (DENNIS O'DOWD) VIA EMAIL TO JEFF ROTTON AT 1653 EST ON 02/20/2007 * * * The following information was provided by the State via email: "As of approximately 4:35 p.m., Tuesday, February 20, 2007, the portable nuclear gauging device reported by NH Licensee John Turner Consulting, Inc. (License No. 423R) has been recovered and was retrieved by the licensee. The licensee's representative has confirmed that the gauge had been left with the Madbury (NH) Police Department, located near the Dover, New Hampshire city line, and was locked inside of its locked case when recovered. "The New Hampshire Radiological Health Section will be dispatching an inspector or inspectors to the licensee's facility on Wednesday, February 21, 2007, to conduct further investigation into this incident." Notified R1DO (T. Jackson), FSME EO (Moore), ILTAB via email and Canada via fax. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2007-02-23
43174 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-02-20 08:30 | 2007-02-20 12:35 | 2007-02-20 | OFFSITE STATE NOTIFICATION REQUIRED BY NPDES PERMIT "Notification to NRC following notification to the following government agencies on 02/20/2007 at 0830 (CST): State of Minnesota Pollution Control Agency - Water Control Quality, State of Minnesota Department of Emergency Management - State Duty Officer. "Notifications made to above government agencies in accordance with Monticello NPDES permit for a collapse of cooling tower panels which resulted in a diversion of circulating flow overland to the discharge canal, resulting in washing of soil and gravel into the canal." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-02-20
43173 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2007-02-19 14:57 | 2007-02-19 19:14 | 2007-02-19 | UNIT 2 PERFORMED A TS REQUIRED SHUTDOWN "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On 02/19/2007 at approximately 14:57 hours Mountain Standard Time (MST), Palo Verde Nuclear Generating Station (PVNGS) Unit 2 initiated a plant shutdown as required by Condition 'C' of Technical Specification (TS) LCO 3.5.3 to be in Mode 3 with Pressurizer pressure < 1837 psia and Reactor Coolant System (RCS) Tc < 485 degrees F. "Limiting Condition for Operability (LCO) 3.5.3 requires that two ECCS trains be Operable. High Pressure Safety Injection Pump (HPSI) 2A was declared inoperable on 02/16/2007 at 13:01 MST and was not restored to Operable status within the TS 72 hour Completion Time due to pump bearing oil leakage exceeding the allowable leakage limit. Efforts are in progress to correct the oil leakage issue. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." The observed pump bearing oil leakage is approximately 3 drops/hr. Unit 2 completed a normal reactor shutdown with a manual reactor trip at 20% power. All rods fully inserted. Decay heat is currently being removed via the Main Condenser. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-02-19
43172 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-02-19 | 2007-02-19 15:34 | 2007-02-21 | DEGRADED CONDITION - 30% THROUGH WALL INDICATION ON REACTOR RECIRC NOZZLE "Information from a Phased Array UT examination of RRF-F002 (Reactor Recirc 'F' Nozzle to Safe-end weld) indicates that a linear indication approximately 7" long (centered at the bottom of the weld) and approximately 30% through wall extent (ID connected) exists. The Phased Array UT examination of RRF-F002 (Reactor Recirc 'F' Nozzle to Safe-end weld) was performed as part of scheduled outage activities. "TRM LCO 3.7.3 for Structural Integrity, Condition B has been entered for the Recirc nozzle/piping. "This event is reportable under § 50.72(b)(3)(ii), 'Any event or condition that results in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded', when there are welding or material defects in the primary coolant system which cannot be found acceptable under ASME Section XI, IWB-3600, 'Analytical Evaluation of Flaws' or ASME Section XI, Table IWB-3410-1, 'Acceptance Standards.'" The licensee informed the NRC Resident Inspector. * * * UPDATE PROVIDED BY HANS OLSON TO JEFF ROTTON AT 2315 EST ON 02/21/07 * * * "Information from a Phased Array UT examination of RRC-F002 (Reactor Recirc 'C' Nozzle to Safe-end weld) indicates that a linear indication approximately 10" long and approximately 82% through wall extent (Inner Diameter connected) exists. The Phased Array UT examination of RRC-F002 (Reactor Recirc 'C' Nozzle to Safe-end weld) was performed as part of a follow-up activity for an extent of condition evaluation on RRF-F002 (Reactor Recirc 'F' Nozzle to Safe-end weld). "TRM LCO 3.7.3 for Structural Integrity, Condition B has been entered for the Recirc nozzle/piping." Corrected error in original report due to event entry error that identified the affected nozzle as RRF-17002 vice the correct identification of RRF-F002 The licensee notified the NRC Resident Inspector. Notified R3DO (Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2007-02-19
43171 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2007-02-19 08:00 | 2007-02-19 10:14 | 2007-02-23 | EOF NOT AVAILABLE DURING RENOVATION "Fermi 2 commenced an upgrade to the Emergency Operations Facility (EOF) on February 19, 2007 at 0800. The upgrade consists of furniture replacement and rearrangement of the seating layout. During this work, some floor panels will be removed for cable routing and accordingly the facility will not be available for emergency use. Fermi is making this notification in accordance with 10 CFR 50.72(b)(3)(xiii). In the event EOF activation is necessary, the Alternate EOF will be utilized. Activation and use of the alternate EOF is included in Fermi's Radiological Emergency Response Preparedness Plan. Fermi will notify the NRC upon completion of this work, which is scheduled for Friday February 23, 2007." The licensee will notify the NRC Resident Inspector. *** UPDATE FROM KONRAD TO KNOKE AT 17:55 EDT ON 02/23/07 *** "This is a follow-up to NRC Event No. 43171. The upgrades to the Emergency Operations Facility (EOF), which caused it to be unavailable for emergency use, have been completed and the EOF is now available for use." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-19
43170 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-02-19 | 2007-02-19 08:56 | 2007-05-21 | AGREEMENT STATE REPORT INVOLVING STOLEN TROXLER MOISTURE DENSITY GAUGE MODEL 3440 The Arkansas Department of Health reported that one of their licensees, Materials Testing of Arkansas, had a Troxler moisture density gauge stolen from a pickup truck in front of a Wal-Mart in Little Rock, Arkansas between 6:00 a.m. and 6:30 a.m. CST. When the licensee returned to the vehicle, he found that the chain securing the gauge had been cut, and the Troxler and some other personal equipment had been stolen from the back of the vehicle. The Troxler is a Model 3440 S/N 19914 and contains 9 milli Curies of Cs-137 and 44 milli Curies of Am-241. The Little Rock Police Department is investigating the theft under case number 07-18990. The Arkansas Department of Health is preparing a press release on this event. *** UPDATE FROM STEVE MACK TO KNOKE AT 15:28 EDT ON 5/21/07 *** The State provided the following information via facsimile: "On Friday, May 18, 2007, the moisture density gauge stolen on February 19, 2007, was recovered in a vacant residence in Little Rock, Arkansas. The gauge transport case, as well as, the gauge handle were not locked when found. The gauge appeared to be undamaged and was transported to the licensee's authorized storage facility. Representatives from the Arkansas Radiation Control Program conducted a leak test in the field and the RSO was conducting a leak test for analysis by the licensee's consultant prior to placing the gauge back in service. "The Department [Arkansas Department of Health] considers this event closed." Notified R4DO (Johnson), FSME (Burgess), ILTAB (Via Email) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2007-02-22
43169 | 0 | OCONEE | 1 | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2007-02-15 16:54 | 2007-02-15 19:00 | 2007-02-15 | UNIT 1 AND UNIT 2 REACTOR TRIP "At 1654 EST on 2-15-07, Oconee Units 1 & 2 tripped from 100% power. The cause of the trips is under investigation. Unit 1 experienced a partial loss of 4160 volt power [Non-Safety Related] which resulted in a loss of Main Feedwater. Emergency Feedwater started on Unit 1. Unit 2 remained on Main Feedwater. Reactor Coolant Pump power was not affected by the trip on either Unit. Post trip equipment response on Unit 2 was normal. On Unit 1, a second HPI pump auto-started due to a non-safety low seal flow signal [one normally running for normal RCS makeup]. "Units 1 & 2 have been stabilized in Mode 3. Restoration of 4160 volt loads on Unit 1 is in progress." All Control rods fully inserted on both units. No PORVs or Safety valves lifted during the event for either unit. Both units are removing decay heat by steaming to the Main Condenser via the Turbine Bypass valves. Both units are in a normal shutdown electrical lineup. Unit 3 was not affected by this event. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-02-15
43168 | 0 | MCCALLUM TESTING LABORATORY |  |  |  |  | 2007-02-15 13:50 | 2007-02-15 14:17 | 2007-06-27 | LOST TROXLER MOISTURE DENSITY GAUGE A Troxler Moisture Density Gauge (model 3411, serial number 6957) was lost at a traffic intersection in Chesapeake, VA. The location of the intersection is at Route 17 and George Washington Parkway. The licensee called local police. The radiation safety officer (RSO) is responding to the site to see if the gauge can be found or if any damage to instrument exists. * * * UPDATE AT 1447 ON 2/15/07 FROM P. BERMAN TO P. SNYDER * * * The licensee reports that the gauge has been found and taken to the local fire department. The RSO is going to the location to examine the gauge for damage. * * * UPDATE AT 1147 EDT ON 6/27/07 FROM BERMAN TO HUFFMAN * * * When the RSO arrived at the fire department on 2/15/07, the gauge was determined to be damaged upon examination. Inspection revealed that the source rod was missing. The pickup truck driven by the city worker that found the gauge was still at the fire department. The truck was examined and the source rod was located loose in the bed of the truck. The RSO picked up the source rod and placed it back into the gauge. The source rod apparently fell out of the gauge while it was being transported to the fire department and was not handled by the individual who found the gauge. The extremity and whole body exposure for the RSO that handled the source rod is estimated to be less than annual limits. Subsequent leak testing of the source rod showed no compromise of the source. R1DO (Powell) and FSME EO (Hackett) notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-02-15
43167 | 0 | MAINE DEPARTMENT OF RADIATION CONTR |  |  |  |  | 2007-02-15 | 2007-02-15 11:41 | 2007-02-15 | AGREEMENT STATE REPORT - LEAKING SOURCE The following was provided by the state via facsimile: "On January 30, 2007 it came to [the licensee's] attention that a radioactive source on Paper Machine #3 is leaking. This source is listed on [the] Materials license (25709) under condition 9 : "Sealed Krypton 85 (85 Kr) sources ". The source is an ABB Industrial Systems Model TG-4, 1 Ci, s/n K-1331-R. "The source is used as part of a scanning system on the paper machine. It is in a location not readily accessible to employees working in the area. Radiation levels at one foot around the source head are 0.1 mR/hour. The gas is leaking very slowly, as evidenced by a decrease over time in the process variable that it measures. The source has been labeled well with caution tape and a barricade tag is affixed to the tape. "The plan for remediation is as follows: " - A replacement source (loaner from ABB) is being shipped (2/1/07) and should arrive by overnight delivery (2/2/07). Upon arrival, [the] shipping department has been instructed to secure the new unit in a designated holding area for radioactive sources. The storage location is a heavy metal cabinet which is locked with a padlock to ensure the safety of the unit and of the workers. The cabinet is in an area not readily accessible to employees, in a building away from production areas. " - The damaged source will stay in place in its frame on the paper machine until early next week when a specialist from ABB will arrive, repackage it and ship it back to ABB. The replacement source will be installed at that time. " - A new source is in the process of being purchased. Delivery is expected in 8-12 weeks. At that time, [the state's] department will be notified there is a new source onsite." ME report number: ME070002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2007-02-20
43166 | 0 | CONVAL, INC |  |  |  |  | 2006-12-11 | 2007-02-14 15:05 | 2007-02-14 | PART 21 CONCERNING MATERIAL VERIFICATIONS ON HIGH PRESSURE AND TEMPERATURE STEAM AND WATER GLOBE VALVES During a Nuclear Utilities Group Audit (NUPIC) on December 11, 2006, several problems were identified at CONVAL related to valve material verification. The problems relate to material verification for 1/2 inch to 4 inch forged body high pressure and temperature steam and water valves produced by this vendor. Since the audit, CONVAL has examined the issues and determined that they are reportable under 10 CFR 21. Issue 1: CONVAL states that the pressure boundary material of the valves in question was not procured to ASME Section III, NCA-3800 program. CONVAL states that the valve material was procured as specified with Certified Material Test Reports (CMTRs) and some independent material over-checking and chemical analysis but the formal verification of the material did not meet NCA-3800. Issue 2: CONVAL states that there was also improper material verification of a safety related part within these valves. The split ring, which retains the closure disc to the stem within these valves, had inadequate material verifications performed for those valves that were ordered to Appendix B with upgraded material verifications. In this case, the split rings have CMTRs but no additional over-checks of the material were performed by CONVAL. None of the valves identified in issues 1 or 2 above were ordered with N-Stamps. CONVAL believes that up to 20 nuclear plants may possess these valves. CONVAL noted that their material verification process has remained unchanged for many years so that this is not a new or recent development. Issue 3: While performing the engineering analysis related to the two issues identified above, CONVAL also determined that under a worst case combination of physical properties for the split ring material in combination with worst case stress conditions, that split ring may not perform its function. CONVAL believes that the likelihood of the split ring failing under these extreme conditions is very remote. CONVAL does not believe there is any safety concern associated with these issues. CONVAL is in the process of identifying and notifying the affected customers. CONVAL plans to provide all customers and the NRC formal documentation of the nature of these Part 21 related deficiencies within the next five business days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | CT | OTH | GEN | 21.21 |  |  |  | 0 | 2007-02-14
43165 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2007-02-14 10:05 | 2007-02-14 13:27 | 2007-02-14 | FITNESS FOR DUTY - SUPERVISOR CONFIRMED POSTIVE FOR ALCOHOL An employee supervisor had a confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's access to the plant has been revoked. A work review is in progress. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2007-02-14
43164 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2007-02-13 20:12 | 2007-02-13 23:05 | 2007-02-13 | LOSS OF OFFSITE COMMUNICATIONS CAPABILITY DUE TO A POWER OUTAGE IN TOLEDO, OHIO "Due to a power outage offsite, the Davis-Besse Nuclear Power Station has experienced a loss of offsite communications capability, which is reportable within eight hours under 10 CFR 50.72(b)(3)(xiii). A loss of a minimum of two of three available telephone system pathways constitutes a loss of offsite communications capability under Davis-Besse site specific requirements (DBRM-RC-0001 R01 Attachment 10). As of 2012 on February 13, 2007, two of the three telephone pathways were unavailable. Full telephone service was restored at 2214 on February 13, 2007. "Due to the loss of the telephone systems, the site also lost the capability to page the Emergency Response Organization via the Computerized Automated Notification System (CANS) in the event of an emergency declaration. However, the site retained the ability to group page the Emergency Response Organization via alternate means. In addition, due to an ongoing snow storm, the site has elected to augment on-shift personnel with selected key Emergency Response Organization personnel. "The Emergency Notification System is currently available." The licensee informed the State of Ohio, local authorities and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-13
43163 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-02-12 | 2007-02-13 12:50 | 2007-02-13 | AGREEMENT STATE REPORT INVOLVING MULTIPLE PATIENTS RECEIVING >20% PRESCRIBED DOSE The following information was received via email: "On Tuesday, February 13, 2007, the Agency [Texas Department of Health] was notified of a series of at least five medical events that were discovered when an improper dose rate constant was used in the treatment planning of the therapeutic application of permanent implants. The radioisotope is I-125 and it was used exclusively for the treatment of prostate cancer. The range of misadministrations is 21-36% over that which was prescribed in the written directive. The licensee is investigating the situation that involved some 28 patients treated over the past year but only one patient complication has been reported thus far. The Agency is continuing to investigate the events with the licensee and will provide updated information as it is received." Texas Incident No.: I-8391 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-02-16
43162 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-02-12 11:58 | 2007-02-12 15:47 | 2007-02-12 | FITNESS FOR DUTY - LICENSED EMPLOYEE A licensed employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been revoked. The employee was working in a non-safety related capacity at the time of the testing. A work review is in progress. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 26.73 |  |  |  | 0 | 2007-02-12
43161 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-02-12 10:52 | 2007-02-12 14:58 | 2007-02-12 | BOTH STANDBY FILTER UNITS INOPERABLE "While performing core alterations and moving irradiated fuel assemblies in the secondary containment, both Standby Filter Units (SFUs) have been declared inoperable per Technical Specification 3.7.4 Condition F. This represents a loss of safety function during the mode of applicability. Core alterations and movement of irradiated fuel assemblies in the secondary containment have been suspended. Movement of irradiated fuel assemblies in the secondary containment, core alterations, and operations with a potential for draining the reactor vessel (OPDRVs) have all been prohibited. As a result of the actions taken, the mode of applicability for Technical Specification 3.7.4 Condition F has been exited. "The A SFU became inoperable per Technical Specification 3.7.4 Condition A due to being unable to meet surveillance requirement 3.7.4.4: -verify each SFU subsystem can maintain a positive pressure of >= 0.1 inches water gauge relative to the outside atmosphere during the isolation mode of operation. This was discovered at 10:52 on 2/12/07. "The B SFU was inoperable due to loss of control power from preplanned maintenance per Technical Specification 3.7.4 Condition A. This occurred on 2/9/07 at 00:45. "DAEC continues to investigate [the cause of the inoperability of the A SFU]. "This event is reportable under § 50.72(b)(3)(v) (D), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident'. " The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-02-12
43160 | 0 | TRACERCO |  |  |  |  | 2007-02-10 05:30 | 2007-02-10 13:45 | 2007-02-10 | MISSING TANTALUM-182 SOURCE IN THE GULF OF MEXICO The following information was provided by Tracerco and BP Pipelines of North America: A pipeline from the Atlantis Platform, 5,000 feet down, was being dewatered with a foam pig. During the process the remotely operated vehicle lost control of the pig causing the pig to surface (normally the pig has negative buoyancy). The pig is currently in the Gulf of Mexico and was last seen in the Grand (Green?) Canyon Block 645, with coordinates of: Latitude 27 degrees 14' 4" North and Longitude 90 degrees 14' 4" West. The pig is 16 inches in diameter and 52 inches long. There is a silver wire inside of the pig which has a Tantalum-182 source. The total activity of the Tantalum-182 when new was 6.25 milliCuries. The source is about 30 days old. The instrumentation is used to track the pig from the platform to the Sub C Collection point. BP Pipelines North America are actively searching for the pig. BP Pipelines North America said that the foam pig will be difficult to find because it will be floating just above or below the surface and that the foam pig will eventually sink. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-02-10
43159 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-02-09 12:08 | 2007-02-09 16:32 | 2007-02-09 | REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "At 1208[CST] on 02/09/2007 with Unit 3 at 100% power, an automatic reactor scram (RPS) was received due to lowering water level. Loss of water level was due to lowering condensate flow which in turn caused a reduction in feedwater flow. Reactor water level lowered to -45 Inches. High Pressure Coolant Injection and Reactor Core Isolation Cooling systems initiated as expected. Additionally, the Recirculation Pump breakers tripped as expected. All expected Primary Containment Isolations, Group 2 (RHR Shutdown Cooling), Group 3 (RWCU), Group 6 (Ventilation), and Group 8 (TIP) were received along with the auto start of Control Room Emergency Ventilation (CREV) and 3 Standby Gas Treatment (SBGT) trains. Unit 2 was at 80% power and was unaffected by the event. Investigation has been initiated as to the cause of the lowering condensate flow. "This event is reportable as a 4-hour and 8-hour non-emergency notification in accordance with 10 CFR50.72(b)(2)(iv)(B) as any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical, 10 CFR 5172(b)(3)(Iv)(A) as any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(Iv)(b), and 10 CFR 50.72(b)(2)(Iv)(A) as any event or condition that results or should have resulted In ECCS discharging to the reactor coolant system. "All control rods fully inserted, the electrical grid is stable. Decay heat is being removed via the turbine bypass valves to the main condenser. The licensee has notified the NRC Senior Resident Inspector." There was no excessive cooldown rate during the injection phase as cooldown rate did not exceed 100 degrees Fahrenheit. Total injection time for both HPCI and RCIC systems was approximately 2 minutes which resulted in approximately 13,000 gallons of coolant from the condensate storage tank (CST) entering the reactor vessel. Primary plant temperature and pressure are 531 degrees Fahrenheit and 928 psig, respectively. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2007-02-09
43158 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2007-02-07 17:30 | 2007-02-08 18:49 | 2007-02-08 | OFFSITE NOTIFICATION TO THE STATE OF NEW MEXICO DUE TO AN OVERTURNED CONSTRUCTION VEHICLE ON SITE At approximately 1730 hours on 2/7/07, a Caterpillar Model 623G Wheeled Tractor Scrapper was being moved from a work area on the Louisiana National Enrichment Facility in Eunice, New Mexico to a parking lot when the tractor overturned and caught fire. The equipment operator escaped without serious injury and was taken to a local medical facility for evaluation. Eunice Emergency Services responded and extinguished the fire. The Lea County Sheriffs department and the New Mexico State Police also responded to the site. The fire was extinguished. There is no radioactive material involved in this accident. The accident occurred north of highway 176 approximately one half mile from the Texas /New Mexico border. The licensee reports there is no threat to human health, safety, property, or environmental resources. The quantity of fluids released from the vehicle is less than 25 gallons of transmission fluid and motor oil. The licensee notified the New Mexico Environmental Department and the National Response Center. There is no planned press release. Tim Johnson and Deborah Seymour of the NRC were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2007-02-08
43157 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2007-02-08 13:42 | 2007-02-08 18:40 | 2007-03-15 | RAW WATER PUMPS DECLARED INOPERABLE DUE TO A POTENTIAL FAILURE OF THE PUMP BREAKER LINKAGES "On February 8, 2007 at 10:22 CST, Raw Water Pump AC-10C was declared inoperable when the pump breaker experienced a plunger linkage failure during a scheduled pump start for a scheduled rotation. Due to a similar failure of Raw Water Pump AC-10B two weeks earlier, a condition report was initiated for engineering to review the potential for a common failure mode. Engineering reviewed the number of cycles of the breakers for AC-10A and AC-10D both have greater than 1600 cycles. The breaker for AC-10B had over 1200 cycles at the time of its failure and AC-10C was over 1700 cycles. Based on the similar numbers of cycles, engineering has determined that continued operation of AC-10A and AC-10D without breaker failure could not he assured. All other safeguards associated breakers have been verified to have less than 1000 cycles and are not considered to be susceptible to breaker failure at this time. After discussion with engineering, Raw Water Pumps AC-10A and AC-10D were declared inoperable on February 8, 2007 at 13:42 CST based on the number of breaker cycles for these two components in relation to the two breakers that failed. "With three Raw Water Pumps inoperable, Fort Calhoun Station entered Technical Specification 2.0.1 which requires the plant be placed in hot shutdown within six (6) hours. The potential for a common mode failure of the linkage in the 4160 VAC circuit breakers (ABB Combustion Engineering Model No. 5VKBR-250) could have prevented operation of the Raw Water Pumps to fulfill the required design function to remove residual heat during a design basis accident. "At 15:22 CST, repairs were completed on Raw Water Pump AC-10C breaker and the pump was declared operable. At 15:34 CST, Technical Specification 2.0.1 was exited and Technical Specification 2.4(1)c, 7-day LCO was entered for the inoperability of Raw Water Pumps AC-10A and AC-10D. The repair of the breakers for AC-10A and AC-10D are scheduled for February 9, 2007." The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1632 EST ON 2/12/07 FROM ERICK MATZKE TO S. SANDIN * * * "This communication is meant to supplement the notification of February 8, 2007. The common mode failure of the linkage in the 4160V circuit breaker (ABB Combustion Engineering model number 5VKBR-250) could have prevented the operation of the raw water pumps as required by design. This could have resulted in the inability of the raw water system to remove residual heat during design basis accidents as required." The licensee informed the NRC Resident Inspector. Notified R4DO (Smith). * * * RETRACTION FROM MATZKE TO HUFFMAN AT 1447 EDT ON 3/15/07 * * * "On February 3, 2007, (Event Number 43157) Fort Calhoun Station reported a condition that, at the time, was believed [to be] a possible common mode failure of the 4160V feeder breakers for the Raw Water (RW) System [redacted]. The circuit breakers for two of the four RW pump feeder breakers had failed. Investigation had determined that the failure mechanism was the same for the two failures. On February 8, it was not known if the other two RW pump breakers could fail by this same mechanism. "The component that failed in the circuit breaker was an offset rod that transmitted operation of the circuit breaker to a set of auxiliary switches associated with the circuit breakers. "The offset rods of the A and D RW pumps have subsequently been tested. Non destructive testing determined that the rods had no cracks. Destructive testing determined that the rods would not have failed for several hundred operations of the circuit breakers. As a result, the system was capable of performing its design safety function. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(B) as previously reported and EN 43157 is being retracted. "While no verbal report criteria is applicable to this condition it is reportable as an LER under 10 CFR 50.73(a)(2)(vii)." The licensee notified the NRC Resident Inspector. R4DO ( Shannon) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2007-02-08
43156 | 0 | ALPHA TESTING LABS |  |  |  |  | 2007-02-02 12:00 | 2007-02-08 16:58 | 2007-02-08 | RADIOGRAPHY CAMERA WITH POTENTIALLY DEFECTIVE SOURCE CONTROL CABLES The licensee provided the following information via facsimile: "RE: U.S. Nuclear Regulatory Commission Radioactive Materials License Number 43-29213-01 Reporting to requirement of 10 CFR 21.21 (d)(3)(i): Concerning Identification of a defect or a failure to comply. "1. Description of the equipment problem: "Alpha Testing Labs purchased a new exposure device with new associated equipment and new source from Source Production & Equipment Company (SPEC). Exposure device model No. 150, S/N 1030 Source Model No. G-60, SIN OA 1704 The first use of the new equipment was of a field job site location in Casper, Wyoming February 2, 2007. Source strength - 4995 GBq "The radiographer successfully cranked out the source for 10 exposures. On the 11th exposure, he experienced difficulty retracting the source back into the locked position. They did an inspection of the equipment (guide tubes and crank cable) and found no visible defects. They informed the RSO of the difficulty. They tried another exposure with the same results. Then they checked the drive cable and gear in the crank outs, replaced the safety stop spring on the drive cable and made 108 exposures with no problems. RSO called SPEC and reported the problem. They said they would overnight a new set of controls and related equipment. "Dosimeter readings: Radiographer-40 mr, Assistant radiographer-45 mr, Assistant radiographer- 12 mr "The next day, February 3, 2007, they made 2 exposures and the problem happened again. They informed the RSO and did not use the equipment again. SPEC sent a new set of associated equipment by overnight delivery and there have been no problems. "2. Corrective action taken: The equipment was returned to the manufacturer, Source Production & Equipment Company (SPEC). SPEC personnel will evaluate the equipment problem and submit a written reply. "3. Place, Date and time of incident: Field site location: Toromont Energy Systems (Wyoming) Inc., 2289 Renauna Ave., Casper, WY 82601 Dates: February 2 and 3rd 2007 at approximately 6:30 PM. "4. Qualifications of personnel involved in incident: Contact the HOO for details." The licensee was operating a brand new SPEC Model 150 S/N 1030 radiography camera containing a 147 Curie source of Ir-192 when the operator experienced some binding while retracting the source control cable. The operator suspended the radiography operation, contacted SPEC, and performed an inspection of the guide tube and cables. The licensee operator noticed some raised metal in the guide tube and guide spring. SPEC provided replacement source guide cables and guide tubes and those components were replaced. The licensee replaced the control cables and guide tubes and no further binding problems were noticed. There were no personnel overexposures and the potentially defective cables are being inspected by the manufacturer. The licensee believes this is a manufacturers defect given that the equipment is brand new and being used for the first time. Additionally, the licensee has four other SPEC cameras and has not experienced any difficulties. The licensee has discussed this issue with Mr. Montgomery in Region IV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 | WY | OTH | PAR | 21.21 |  |  |  | 0 | 2007-02-08
43155 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-02-06 11:00 | 2007-02-08 11:57 | 2007-02-08 | AGREEMENT STATE REPORT INVOLVING PERSONNEL EXTREMITY OVEREXPOSURE "[Captech representative] reported an overexposure to a Captech employee. [The individual] received 50.68 rem to her left hand as per her dosimetry report. [The individual] is no longer an employee at Captech [and] left at her own volition as per [the Captech representative]. Incident referred to radioactive materials for investigation." Captech is an independent Nuclear Pharmacy. The individual receiving the overexposure handled various isotopes during the period measured by the dosimetry report. FL Incident No.: FL07-019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-02-13
43154 | 0 | US CUSTOMS AND BORDER PATROL |  |  |  |  | 2007-01-31 15:00 | 2007-02-08 09:30 | 2007-02-08 | POTENTIAL MISSING SOURCE On 1/31/07 the licensee shipped a pig which was assumed to contain a training source (CS-137 with a strength of 7 milliCuries) from the Port of Miami location to the Los Angeles, CA location. When the shipment arrived in Los Angeles no source could be found in the pig. The source was verified by both survey and visual inspection to not be present. The officers in Los Angeles notified the RSO and the Port of Miami of the missing source. A search for the source was conducted in Port of Miami and Los Angeles, the source was not located. No pre-shipment survey was performed in Miami; therefore the source could not be verified, by radiation levels on the pig, to have been present when shipped. During the investigation, several officers involved in the training and that routinely uses the licensee's sources at the Port of Miami, stated that they believe there was never a source in the storage pig. The licensee has contacted the source vendor, International Isotopes, to verify that a source was actually shipped in the pig to Miami. When the licensee attempted to locate the pre-shipment survey, it could not be found. All other sources in the licensees possession have been accounted for. The licensee continues to attempt to locate the source and will update the NRC as new information becomes available. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | FL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-02-08
43153 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2007-02-08 04:32 | 2007-02-08 05:25 | 2007-02-08 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE "During performance HPCI Pump Operability (34SV-E41-002-1), HPCI Steam Supply Valve (1E41-F001) failed to open. When steam supply valve control switch was taken to open position, double indication was observed; however, HPCI turbine speed did not increase. Shortly afterward, HPCI Valve overload alarm was received. When steam supply control switch was taken to close position, a ground indication was received. The steam supply valve breaker tripped and ground indication cleared. Personnel in the field reported that the steam supply valve motor was hot to the touch." All other required safety systems are operable and available. The electrical power system is in a normal configuration with no power sources unavailable. The licensee will notify the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-02-08
43152 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2007-02-07 16:40 | 2007-02-07 18:29 | 2007-02-07 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE "The HPCI minimum flow valve was found to have no position indication. The valve was verified to be in the closed position. Maintenance subsequent investigation found the control power fuse to be blown in the breaker, rendering it inoperable to stroke on low flow as designed. HPCI then declared inoperable." The fuse has been replaced and they position indication for HPCI minimum flow valve. Licensee entered Technical Specification 3.5.1 (14 day limiting condition of operation). All other Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-02-07
43151 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-02-07 04:30 | 2007-02-07 11:10 | 2007-02-07 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "Between 0430 and 0457 on 2-7-2007, the alarm for 'HPCI Inverter Circuit Failure' was received three times. Indications on High Pressure Coolant Injection (HPCI) pressure instruments and the HPCI Flow Controller also showed oscillations. The power indicating light on the HPCI inverter was also observed to extinguish and re-illuminate once. Because of the alarms and changes in indications, the capability of the inverter is questionable, and HPCI may not be capable of performing its required functions. "HPCI was declared inoperable as of 0430, resulting in entry into Tech Spec LCO 3.5.1 Condition C - HPCI System Inoperable and 3.5.1 Condition D - HPCI System Inoperable and Condition A entered. At the time HPCI was declared inoperable, Core Spray Loop A was also Inoperable for planned maintenance, day 2 of a 7 day LCO. Required Actions for Condition D are to restore either HPCI or the low pressure ECCS injection/spray system to operable status within 72 hours. "Troubleshooting activities for HPCI are being planned, and maintenance and testing activities for Core Spray A are continuing. Completion of the maintenance window for Core Spray A is scheduled for later this afternoon, and activities for Core Spray are currently on schedule. "HPCI is a single train system. This report is submitted as a condition that at time of discovery could prevent the fulfillment of the safety function of an SSC needed to mitigate the consequence of an accident." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-02-07
43150 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2007-02-06 18:15 | 2007-02-06 19:25 | 2007-02-06 | MISSING NON-IRRADIATED TRANSVERSING INCORE PROBE (TIP) "During ongoing activities to remove non-fuel material from River Bend Station (RBS), it was identified that a non-irradiated transversing incore probe (TIP) was not in its expected location. TIP detectors are normally used to calibrate incore nuclear instrumentation. This TIP had not been used. "According to the special nuclear material (SNM) inventory sheets, the TIP was expected to have been enclosed in a storage container in the SNM storage area of the radioactive waste building. During an inventory of the container, the TIP could not be located. It is probable that the material was shipped to an authorized disposal facility for burial. A TIP typically contains less than 0.0008 grams Special Nuclear Material (SNM). "This material does not represent a hazard to the public health and safety. This condition is being conservatively reported under 10CFR74.11 (a) and (b). There is no evidence of theft or diversion. The licensee has informed the NRC Resident Inspector of this condition. "Investigation is continuing." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 74.11(a) |  |  |  | 1 | 2007-02-06
43149 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-02-06 14:15 | 2007-02-06 19:08 | 2007-02-06 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM DECLARED INOPERABLE "The Control Room Emergency Filtration System (CREFS) was declared inoperable at 1957 on 02/03/07 due to W-14B, 'F-16 Control Room Charcoal Filter Fan,' being declared inoperable during monthly Technical Specification surveillance testing. Upon subsequent investigation of the inoperability of the W-14B fan, the W-14A fan was declared inoperable at 1415 CST on 02/06/07. The cause of the failure of the fans is under investigation. "These fans are required to be operable to support operability of the CREFS System. This condition is covered by TS 3.7.9 'Control Room Emergency Filtration System' and both units have entered Action Condition A 'CREFS Inoperable,' with a Required Action to 'Restore CREFS to an OPERABLE Status' by 1957 CST on 02/10/07. "Although the W-14 fans are redundant, CREFS is a single train system. Based on the guidance in NUREG-1022 for single train systems that perform safety functions, this condition was determined to be reportable under 10 CFR 50.72(b)(3)(v)(D), 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function.' Additionally, the failure places PBNP CREFS in a degraded condition that significantly affects plant safety under 50.72(b)(3)(ii)(A), 'Degraded or Unanalyzed Condition.'" The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-02-06
43148 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-02-06 10:45 | 2007-02-06 16:08 | 2007-02-06 | FITNESS FOR DUTY REPORT A licensed employee (currently inactive) had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been denied. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0 | 2007-02-06
43147 | -1 | ST. FRANCIS HOSPITAL, HARTFORD, CT |  |  |  |  | 2007-02-06 07:00 | 2007-02-06 13:49 | 2007-03-07 | MEDICAL EVENT A patient was being treated for cancer of the cervix. The planned total dose to the cervix was to be 2046.5 cGy, over a 39 hour time period. The licensee was using an LDR Selectron Afterloader. Nine cesium-137 sources, activity of each source 16.7 millicuries, were used in the afterloader. The patient started treatment on 02/05/07 at 1235 EST. Today, 02/06/07, between the hours of 0630 - 0717 EST the patient pulled the applicator out approximately 4 centimeters. The patient was given the correct dose to the cervix for 16.09 hours for a total dose of 844.5 cGy. The patient was given an incorrect dose to the vaginal area for between 30 - 60 minutes. The total dose to the incorrect area is between 50 - 200 (Max) cGy. This incident was not harmful to the patient. The patient's doctor was notified of this incident. The patient will not be retreated. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION AT 11:50 ON 3/7/2007 BY DR E. WILCOX TO M. ABRAMOVITZ * * * This event is not reportable because of patient intervention. The patient refused continuing treatment. Notified the R1DO (Caruso) and FSME (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-02-12
43146 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2006-12-08 21:43 | 2007-02-06 10:56 | 2007-02-06 | INVALID EFW ACTUATIONS DUE TO AN ISSUE IN SG DRYOUT PROTECTION CIRCUIT "This report is being made per paragraphs 50.73(a)(1) and 50.73(a)(2)(iv)(A) to address two actuations of the Emergency Feedwater (EFW) System on Oconee Unit 1 on 12/8/06 by the Steam Generator (SG) Dry-out Protection Circuit. EFW is a system named in 50.72(b)(3)(iv)(B). "By design, the SG Dry-out Protection Circuit actuates whenever two Extended Start-up level indications (two of two actuation logic) in either SG are lower than the setpoint (i.e. below 21 inches) for more than 30 seconds. This start circuit is not credited in Oconee safety analyses as performing a required safety function, therefore this signal is considered an INVALID signal with respect to 50.73 (a)(2)(iv)(A). Upon actuation, the circuit starts both Motor Driven Emergency Feedwater Pumps (MD EFWPs) on the affected unit. It does not send a start signal to the Turbine Driven Emergency Feedwater Pump. "Per the startup procedure, Condensate Booster Pumps (CBP) feed the SGs until a main Feedwater pump (FDWP) is placed in service. Operators begin startup of a FDWP when the Reactor Coolant System (RCS) temperature is between ~395 degrees to 475 degrees. The Unit is then maintained at ~ 475 degrees RCS temperature and 500 - 550 psig SG pressure until a FDWP is in service. "On 12/8/06, a Unit 1 startup from a refueling outage was in progress. RCS temperature was approximately 475 deg. (Mode 3) when the RCS heat-up was suspended due to issues with the 1A FDWP Turbine which delayed placing it in service. Steam pressure was being maintained approximately 530 psig (in the procedural band of 500-550 psig) per the unit startup procedure. In addition, a 'SG Hot Soak' was in progress. For this evolution, SG level was raised to 75% (Operating Range) then Operators took manual control to individually blow down 1A and the 1B SGs to low levels (25 inches) while attempting to maintain level above 21 inches. "During this evolution, 1B SG levels decreased below minimum level. Operators initiated actions to recover level but at 2143 the 1A and the 1B MD EFW Pumps auto-started on dry-out protection. From their observation of the level displays, the Operators thought that the actuation logic had not been met (i.e. level had not been less that 21 inches for 30 seconds). Therefore they considered the actuation to be spurious. Based on this understanding and concerns about possible overfeeding and RCS overcooling (due to the relatively low decay heat load starting up from a refueling outage), EFW was secured and reset at 2144. "SG Blowdown activities continued per procedure. At 2207, in response to lowering 1A SG levels, the dry-out protection feature again initiated an auto start of the 1 A and 1 B MD EFW Pumps. Based on his review of SG levels, the CR SRO believed that the second EFW actuation was invalid and directed that EFW be secured. EFW was secured and reset at 2208. At 2241 hrs SG outlet pressure was lowered and maintained within a band of 490-520 psig. "Subsequent review of computer data indicated that a dry-out condition (i.e. less than 21 inches SG level for 30 seconds) did exist for both actuations. Therefore both actuations were valid in that actual plant conditions satisfied the initiation criteria, but, as stated above, the SG Dry-out Protection signal is considered an INVALID signal with respect to 50.73 (a)(2)(iv)(A). "Additional review by Mechanical-Civil Engineering personnel determined that the Unit 1 CBPs operate at approximately 15 psig lower discharge pressure than the Unit 2 and 3 CBPs, apparently due to lower discharge pressures on the Unit 1 Hotwell pumps. That being the case, the Unit 2 and 3 CBPs, apparently due to lower discharge pressures on the Unit 1 Hotwell pumps. That being the case, the Unit 1 CBPs in service could not develop sufficient head pressure to maintain adequate flow to the SGs over the full operating operating band of 500 - 550 psig allowed by current operating procedure guidance. As steam pressures approached or exceeded 535 psig, the ability to feed the SGs using the CBPs was reduced, ultimately leading to the dry-out condition. "The issue of these pump discharge pressures being slightly lower than expected had not been recognized previous to this event. The event investigation noted that during past startups, a main FDWP was normally placed into service promptly, which may have avoided using the CBPs to feed the SG above 535 psig. In this case, alignment of a main FDWP was delayed, which led to the event. "Specific Information Required per NUREG 1022: "(a) The specific train(s) and system(s) that were actuated. "The specific train(s) and system(s) that were actuated were the 1 A and 1 B Motor Driven (MD) Emergency Feedwater (EFW) Pumps and the associated A and B trains of EFW. The Turbine Driven EFW pump does not receive this signal and was not challenged by the event. "(b) Whether each train actuation was complete or partial. "Both actuations were considered complete (i.e. all necessary components responded to the start signal and associated control signals to provide EFW to the SG(s)). "(c) Whether or not the system started and functioned successfully. "In both cases, the system started and operated successfully until secured by Operations personnel. "Initial Safety Significance: None, there was no significant transient. "Corrective Action(s): As stated above, EFDW was secured and reset at 2208. At 2241 hrs SG outlet pressure was lowered and maintained within a band of 490-520 psig. Unit 1 continued startup and subsequently reached Mode 1. This event has been entered into the site corrective action program for resolution." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-02-06
43145 | 0 | UNIVERSITY OF VIRGINIA HOSPITAL |  |  |  |  | 2007-02-04 18:00 | 2007-02-05 13:56 | 2007-02-06 | MEDICAL EVENT - PATIENT RECEIVED AN UNDERDOSE "A FS (Tandem and ovoid) device was loaded into a patient for Cs-137 brachytherapy of the cervix on Friday Feb 2, 2007. The written directive was for 3000 cGy to Pt A in 48.5 hours. Upon removal of the device on Sunday Feb 4, 2007 at approximately 5PM it was observed that the plastic tube used to hold the Cs sources in the tandem was not of the standard length: it was short by approximately 4 cm. The consequence of this would be that the tandem sources would not have been in the position planned. The patient received an underdose to Point A of 760 cGy vs. the 3000 cGy that had been prescribed. Follow-up treatment is planned to correct for this underdose. Clinically, according to the physician, the dose the patient received to distal vaginal would not be expected to cause adverse reactions. " * * * UPDATE FROM FLANNERY (FSME) TO HUFFMAN VIA E-MAIL AT 1218 EST ON 2/06/07 * * * This event has been reviewed by the NRC medical review committee and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2007-02-06
43144 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2007-02-05 04:30 | 2007-02-05 12:25 | 2007-02-06 | LOSS OF STACK EFFLUENT MONITORING CAPABILITY "At 0430 on 2/5/07, Nine Mile Point Unit 1 determined that the capability to determine effluent radioactivity going out the stack has been lost. It is postulated that this is likely due to moisture in the primary and auxiliary sampling line which has frozen and blocking the flow of effluent to the sample analysis equipment. "Compensatory actions include monitoring alternate indications of increased radioactivity in the plant effluent steams. A method has been proceduralized to sum systems that input to the stack. Portions of the systems required for monitoring plant effluents are currently out of service for preventive maintenance. It is expected that they will be returned to service by 1700 hours today." The State of New York will be notified of this event. The NRC Resident Inspector was notified of this event by the licensee. See similar event # 43125 reported by Nine Mile Point Unit 1 on 01/26/07 * * * UPDATE ON 02/06/07 AT 1615 EST BY BRIAN FINCH TO MACKINNON * * * "The systems required for compensatory actions using alternate indications for monitoring plant effluents for the backup methodology previously reported out of service for preventative maintenance were returned to service as of 12:00 EST 2/05/07" R1DO (Bill Cook) notified. The NRC Resident Inspector was notified of this update by the licensee. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-05
43143 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2007-02-05 05:25 | 2007-02-05 08:28 | 2007-02-05 | BLOCKED EMERGENCY VEHICLE ACCESS "Ginna Station Site access for emergency vehicles has been unavailable since 0525 this morning due to the inability to lower both the North and South Active Vehicle Barriers." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-05
43142 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2007-02-05 07:07 | 2007-02-05 07:24 | 2007-02-05 | UNUSUAL EVENT DECLARED DUE TO LOW SERVICE WATER INTAKE LEVEL Licensee provided the following details via facsimile on 02/05/05 at 1305 EST: "On February 5, 2007, at approximately 05:30 hours, the control room received an alarm for 'intake structure or traveling screen trouble alarm,' and a nuclear plant operator was dispatched to investigate the condition. At approximately 05:57 hours, the control room was notified that the alarm was due to low screen wash pressure on all traveling water screens as a result of the all screen wash pumps found tripped. Review of the Emergency Plan (EP) determined that Emergency Action Level (EAL) 8.4.3, 'Service Water Level 4 Feet, 5 Inches Below Mean Sea Level, 'was met and entry into an Notification of Unusual Event (NUE) was required. At approximately 07:07 hours, operations entered an NUE for EP EAL 8.4.3. Further investigation and corrective action are in progress. At approximately 07:24 hours, the NRC Emergency Operations Center was notified of the NUE (Jeff Rotton)." Licensee reported entering EAL 8.4.3 - Service Water Bay Level < 4 feet 5 inches below mean sea level. There are presently no other open LCOs that impact Service Water operability. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1058 EST ON 2/5/07 FROM J. HARVEY TO P. SNYDER * * * The licensee terminated the Unusual Event at 1014 based on the fact that: (a) Service Water Bay Levels had increased to 1 ft below mean sea level and were rising, (b) The licensee initiated cleaning of the trash rack for the intake structure, and (c) the time for an unusually low tide was now passed. The licensee notified the NRC Resident Inspector. Notified R1DO (Cahill), IRD Mgr (Leach), NRR EO (Ross-Lee), DHS (T. Barnes), FEMA (C. Liggett), and R4 (L. Howell). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2007-02-05
43141 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2007-02-05 03:07 | 2007-02-05 06:38 | 2007-02-05 | MANUAL REACTOR TRIP DUE TO STEAM LEAK DURING MAIN FEED BOOSTER PUMP STARTUP "While starting D Feedwater Booster pump, a steam leak developed in the Turbine building. The Reactor was manually tripped at 0307 on 02/05/07. Investigation revealed that an orifice (XPS0006D) in the D Feedwater Booster pump recirculation header was the source of the leak. The steam/water leak was isolated at 0500 on 02/05/07. All systems responded normally on the Reactor trip. Emergency Feedwater (AFW) system started on LoLo Steam Generator level. Steam Generator level recovered quickly." All control rods fully inserted on the manual Reactor trip signal. No relief valves or PORVs lifted as a result of the transient. Decay heat is being removed by the main condenser via the steam dump valves. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-02-05
43140 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2007-02-03 12:32 | 2007-02-03 19:51 | 2007-02-03 | TECHNICAL SPECIFICATION 3.0.3 ENTERED DURING ROUTINE SURVEILLANCE TESTING OF CONTROL ELEMENT ASSEMBLIES (CEA'S) "On 2/3/2007 at approximately 12:32 MST, Palo Verde Control Room operators were performing a routine surveillance test. The purpose of this test is to demonstrate the operability of each full strength CEA not fully inserted in the core by verifying freedom of movement (trippability) by moving each individual full strength CEA that is not fully inserted in the core at least 5 inches (SR 3.1.5.3). "While performing this test on Shutdown Group 'B', Subgroup 6, the 4 CEA's in the sub-group failed to withdraw after successfully inserting the CEA's the requisite 5 inches. The CEA's were inserted beyond the limit of 144.75" withdrawn as required per PVNGS TS LCO 3.1.6 to a position of 144" withdrawn. It was determined that this was not an analyzed condition. "On 2/3/2007 at 13:15 MST, the Control Room staff identified the unanalyzed condition and PVNGS Unit 2 entered TS 3.0.3. It was determined that the unanalyzed condition had existed since 12:32 MST. "On 2/3/2007 at 16:16 MST, following corrective maintenance to replace a phase sequence card, the 4 CEA's were recovered above the TS 3.1.6 insertion limit of 144.75", and Unit 2 exited LCO 3.0.3. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. The required offsite power sources are operable and the electrical grid is stable. "The NRC resident inspector has been notified of this event." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-02-03
43139 | -1 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2007-02-02 13:50 | 2007-02-02 21:05 | 2007-03-14 | LOW PRESSURE INJECTION (LPI) NET POSITIVE SUCTION HEAD FLOW REQUIREMENTS NOT MET FOR CERTAIN ACCIDENT SEQUENCES "At 1350 hours on February 2, 2007, with the plant at 100% power, it was determined [that] the low pressure injection (LPI) system net positive suction head calculation does not account for the additional flow through the failed LPI pump recirculation line during certain accident scenarios. The additional flow is upstream of the flow element used by control room operators to throttle system flow to maintain net positive suction head flow requirements. The additional flow could result in net positive suction head below required design limits. The system design is not affected in events where both LPI trains perform as designed. "Emergency operating procedures direct control room operators to open the LPI system discharge flow cross-connect line isolation valves, if accessible, following a LPI pump failure. Operators are then directed to throttle system flow through the operable LPI pump to maintain proceduralized values. These values are designed to provide sufficient design flow and maintain pump NPSH. During a simulator training scenario, operators identified when the discharge cross-connect line isolation valves were opened, the idle Building Spray train indicated flow. Follow-up investigation identified the increased flow was due to back flow through the failed LPI pump minimum flow recirculation line. This additional flow is upstream of the flow element used by operators to maintain adequate net positive suction head for the operable LPI pump. The additional flow could result in not meeting NPSH design requirements. "The licensee entered the 72 hour Technical Specification limiting condition for operation (LCO) for one inoperable LPI train. The licensee is revising calculations and emergency operating procedures to account for the additional flow. "This condition is reportable in accordance with 10CFR 50.72(b)(3)(ii) and (b)(3)(v) as an unanalyzed condition, and a condition that could have prevented the fulfillment of the safety function of the LPI system to mitigate the consequences of an accident, respectively. " The NRC Resident Inspector was notified of this event by the licensee. *** RETRACTION FROM MILLER TO KNOKE AT 11:11 ON 03/14/07 *** "The purpose of this report is to retract the ENS report made on February 2, 2007 at 2105 hours ( ENS #43139) under 10CFR50.72(b)(3)(ii) and (b)(3)(v) as an unanalyzed condition, and a condition that could have prevented the fulfillment of the safety function of the Low Pressure Injection (LPI) system to mitigate the consequences of an accident, respectively. The initial report was made when it was determined that the LPI system net positive suction head (NPSH) calculation does not account for the additional flow through the LPI pump recirculation line during certain accident scenarios. The additional flow could result in net positive suction head below required design limits. Due to this condition, it was not certain if the LPI system could have met its design basis requirements. The licensee entered the 72 hour Technical Specification limiting condition for operation (LCO) for one inoperable LPI train. The LCO was exited on February 3, 2007 at 9:25PM following implementation of a procedure change that accounted for the additional flow and ensured that adequate NPSH was maintained. A subsequent engineering evaluation has determined that sufficient LPI pump NPSH would have been available to perform its design basis function prior to the procedure change. The engineering evaluation shows that the LPI pumps remained capable of performing their design basis functions based on the following three independent assessments: 1) the LPI pumps would have operated well beyond their mission time without significant cavitation damage at the available NPSH 2) proceduralized operator actions would have throttled flow to restore required NPSH if signs of cavitation occurred 3) an evaluation using realistic Reactor Building pressures showed that sufficient NPSH would exist." The licensee notified the NRC Resident Inspector. Notified R1DO (Hott) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-02-02
43138 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-02-01 08:40 | 2007-02-01 13:20 | 2007-03-28 | CONTROLLED SUBSTANCE FOUND IN PROTECTED AREA Pursuant of 10CFR26.73(b), the following 24 hour notification of a significant fitness for duty event as described in 10CFR26.73(a)(i): "On 2/01/07 at approximately 0840 CST, off-site testing of a substance proved positive for a controlled substance. The substance was found by a member of plant staff on the plant grounds within the protected area. The plant staff member took possession of the substance and immediately contacted Security staff personnel for assistance. There were no personnel noted in the immediate area of the substance [at the time of discovery]. After confirming the substance, it was turned over to Linn County Sheriff's Department." The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * *UPDATE FROM SCHWERTFEGER TO HUFFMAN AT 1948 EST ON 2/1/06 * * * The licensee has brought drug dog teams onto the site to assist in locating any other controlled substances that may be present. Contact the Headquarters Operations Officer for additional information. R3DO (Hills) and ILTAB (Hahn) informed. * * * UPDATE AT 1418 EDT ON 3/28/07 FROM JOHN SCHWERTFEGER TO S. SANDIN * * * The licensee is retracting this report based on the following: "Confirmatory analysis performed by State of Iowa Crime Lab has concluded that the substance in question was not a controlled substance and is therefore not reportable under 10CFR26.73(b) as a significant fitness for duty event as described in 10CFR26.73(a)(i)." The licensee will inform the NRC Resident Inspector. Notified R3DO(Lara). | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 26.73 |  |  |  | 0 | 2007-02-01
43137 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-02-01 09:25 | 2007-02-01 12:18 | 2007-02-01 | LOSS OF OFFSITE PHONE CONNECTIONS At approximately 0925 CST, Braidwood lost approximately 85% of phone functionality. The loss of phones has been determined to be an off site issue and the local phone company is investigating the situation. The Emergency Response Organization (ERO) can still activate ERO pagers using cell phones. The Shift Manager has a dedicated cell phone. The licensee notified the NRC Resident Inspector. * * * UPDATE BY KLEVORN TO HUFFMAN AT 2239 EST ON 2/1/07 * * * The licensee declared the ENS and commercial lines operable based on testing and information from the telephone company. The R3DO (Hills) has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-02-01
43136 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-01-31 18:45 | 2007-02-01 00:36 | 2007-02-28 | POTENTIAL FOR PENETRATION RECIRCULATION FILTRATION SYSTEM OVERLOAD "Due to a procedure based line-up of the Penetration Recirculation Filtration (PRF) system, it has been discovered that the system is placed in a configuration that could prevent it from performing its safety function. The PRF System filters airborne radioactive particulates from the area of the fuel pool following a fuel handling accident or ECCS pump rooms and penetration area of the Auxiliary Building following a loss of coolant accident (LOCA). The PRF system is a standby system that upon a receipt of an actuating Engineering Safety Feature Actuation System signal or upon receipt of a high radiation signal or a low air flow signal from the normal spent fuel pool room ventilation system will start the PRF fans and discharge the ventilation air stream through the system's filters. "The standard operating procedure for the PRF system directs the control room staff to place the system in a 'full recirculation' mode of operation following a design bases LOCA if the system can maintain a proper vacuum inside the PRF boundary. The 'full recirculation' mode of operation isolates the Recirculation fan discharge to the atmosphere and fully opens the Recirculation fan recirculation damper. This mode of operation is only an additional defense in depth measure and is not credited in the accident analysis. In this mode of operation, it has been discovered that a degraded PRF boundary which allows in leakage into the boundary which is less than the maximum allowable operational limits, could place the system in a configuration that might cause the Exhaust fan to trip. The trip is caused by an overload condition at the supply breaker due to the increased flow of the Exhaust fan to the atmosphere. With the Recirculation fan discharge isolated to the atmosphere and the Exhaust fan inoperable, the PRF system may not establish an adequate vacuum in the PRF boundary during a Post LOCA accident, thus not meeting its design function. "This condition was discovered on Unit 1, A train PRF system. Since the systems are similar between Units 1 and 2, and the procedure guidance is exactly the same for the 'full recirculation' mode of operation, this condition has the potential to affect both units, both trains of PRF. "Corrective actions have been completed to eliminate this mode of operation from the procedure guidance given to the control room staff for operation. A major contributor to the in leakage into the PRF boundary on Unit 1 has also been repaired which reduced the running load on the Exhaust fan for that train. With the procedure guidance removed, the system should not be placed in a 'full recirculation' mode of operation, thus eliminating the potential for a failure of the designed safety function of the system." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1100 EST ON 2/28/07 FROM LEONARD SMITH TO S. SANDIN * * * The licensee is retracting this event based on the following: "This is an Update / Retraction of EN#43136IAW NUREG-1022 paragraph 4.2.3 "An eight hour report (EN #43136) per 10 CFR 50.72(b)(3)(v) was conservatively reported based on the potential of having the Penetration Room Filtration (PRF) system become inoperable during a LOCA or fuel handling event. It was believed the post accident system alignment could be relying exclusively on the PRF exhaust fan to draw negative pressure on the penetration rooms during post accident conditions. The report was generated when the FNP Unit 1 A-train PRF exhaust fan tripped while the system was being operated in the full recirculation mode, resulting in a loss of the PRF system capability to meet the intended function. "It was concluded at that time the Post LOCA alignment of PRF could result in a similar condition since procedure guidance would have the operator place the PRF system in the full recirculation mode to enhance the cleanup function. Additional investigation, evaluation, and testing has allowed the staff to determine, due to Penetration Room Boundary (PRB) inleakage, the penetration room pressure would not meet the minimum negative pressure of -.5 in. WC in the Post LOCA alignment while in the full recirculation mode. In that case, the procedure would have the operator promptly realign the system to an acceptable configuration. Appropriate operator action would correct the system degraded condition to one that is acceptable for meeting the intended safety function. The PRF is not a fully automatic design system. Proper operation of the system in accident conditions relies on operation actions. "In summary, the potential for loss of PRF systems necessary to fulfill the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident did not exist as a result of this set of conditions and the 10 CFR 50.72(b)(3)(v) report (EN #43136) is retracted." The licensee informed the NRC Resident Inspector. Notified R2DO (Deborah Seymour). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2007-02-01
43135 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-02-01 12:00 | 2007-01-30 16:12 | 2007-01-30 | FLORIDA AGREEMENT STATE REPORT - LOSS GAS CHROMATOGRAPH Following Agreement State Report was received via e-mail "Licensee reported loss of gauge. Last seen during 2/06 inventory. Roof over storage area was replaced in 03/06 and all instruments/equipment had to be moved. Repairs were complete in 5/06. The gauge was noted missing in 8/06 inventory. Licensee reports an extensive search was conducted for several months. The loss was reported to this office 1/30/07. Licensee will submit a written report. Florida is investigating." Device Type: Gas Chromatograph Manufacturer: Hewlett-Packard Model Number: 5890 Serial Number: SN L4479 Isotope(s): Ni-63 Activity: 15.8 millicuries in 1988 (13.2 millicuries now) Material Form: Sealed Source Incident Category: Loss of Control - Lost, Abandoned, or Stolen Materials Location Classification: Controlled Area THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-02-02
43134 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2007-01-30 05:43 | 2007-01-30 10:31 | 2007-01-30 | LOSS OF EMERGENCY RESPONSE FACILITY INFORMATION SYSTEM "At 0543 hours EST, on January 30, 2007, the Emergency Response Facility Information System (ERFIS) computer system became inoperable due to multiplexer (MUX) failure. At this point, it appears that the malfunction is due to a failure of the MUX power supply. Technical support personnel are currently working to restore ERFIS functionality. "The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, and the Inadequate Core Cooling Monitor (ICCM). The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above described functions. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the ERFIS computer system is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remain available to assess plant conditions, make notifications, and accomplish required communications, as necessary. "An update to this message will be provided when the ERFIS is restored." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 01/30/07 AT 1729 EST BY HENRY CURRY TO MACKINNON * * * ERFIS returned to service at 1700 EST. R2DO (M. Ernstes) notified. The NRC Resident Inspector will be notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-30
43133 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-01-30 08:35 | 2007-01-30 10:10 | 2007-01-30 | LOSS OF SPDS DUE TO PLANNED MAINTENANCE "Unit 2 SPDS (Safety Parameter Display System) is OOS (Out-of-Service) for planned Plant Computer replacement. System will be out for several days." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-30
43132 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2007-01-29 23:10 | 2007-01-30 00:49 | 2007-02-01 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR PRESSURE VESSEL (RPV) WATER LEVEL "On 1/29/07 with Hope Creek reactor startup in progress, in mode 1 at 22% Reactor power, Secondary Condensate Pump Minimum Flow Control Valves began to cycle. Reactor water level reached 39" (RPV level 7) and then lowered to 30" (RPV level 4). Manual control of the Reactor Feed pumps was taken, however, RPV water level continued to lower to 15" (Reactor scram on RPV water level is 12.5") at which time the reactor mode switch was locked in shutdown. There were no ECCS injections and all ECCS systems are operable. Initial review of the event indicates that all systems operated as expected with the exception of the Secondary Condensate pump minimum flow valves and the 'A' IRM failed to insert. Current plant conditions as of 1/30/07 at 0010 are: Hope Creek is in mode 3 at 565 psig. The Main Steam Line Isolation valves are open. 'B' and 'C' Primary Condensate Pumps, 'B' and 'C' Secondary Condensate Pumps, and 'A' Rx Feed Pump are feeding the vessel. All control rods have fully inserted on the scram and Main Turbine Bypass valves are removing decay heat." The licensee will inform the LAC (Lower Alloways Creek Township) and has informed the NRC Resident Inspector. * * * UPDATE FROM REED TO HUFFMAN AT 1719 EST ON 2/01/07 * * * "Based on the post-trip review performed by the licensee, it was determined that the in-service Reactor Feed Pump Minimum Flow Recirculation Valve opened in response to the feed flow adjustments. Reactor vessel level reached the low-level trip set point and an automatic reactor scram occurred. During the event analysis it was determined that the operator initiated the manual scram two seconds after the automatic low level scram occurred. A post event equipment performance review concluded that the Secondary Condensate Pump Minimum Flow Recirculation Valves operated as expected." The licensee notified the NRC Resident Inspector. The R1DO (Cahill) notified. | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2007-01-30
43131 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-01-29 11:30 | 2007-01-29 17:33 | 2007-01-29 | LICENSED EMPLOYEE FAILS FITNESS-FOR-DUTY TEST "A licensed operator employee had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2007-01-29
43130 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2007-01-29 04:00 | 2007-01-29 17:05 | 2007-03-02 | ARIZONA AGREEMENT STATE REPORT - STOLEN CPN DENSITY GAUGE Following Agreement State Report was received via facsimile. "At approximately 9:00 AM January 29, 2007, the Agency was informed that the Licensee had a Nuclear Density Gauge stolen from the back of a pickup truck, while the user was at his residence. The missing gauge is a CPN Model MC-3 gauge, SN 8853. The theft occurred between 4 - 6:15 AM on January 29, 2007. The gauge contains 8 mCi (milliCuries) of Cesium-137 and 40 mCi (milliCuries) Am:Be-241. "The Phoenix PD is investigating and issued report number 2007-701-92664. "The Licensee is offering a $500.00 reward for the recovery of the source. A press release is to be made by the licensee. "The Agency continues to investigate. "First Notice: 07-001" The states of CA, NV, CO, UT , NM, and U.S. NRC , FBI and Mexico are being notified of this event. * * * UPDATE PROVIDED BY GODWIN TO KOZAL ON 03/2/07 AT 1303 VIA FACSIMILE * * * "On February 29, 2007, MRM notified this Agency that at 3:15 that afternoon, MRM had received a phone call from a private citizen that some person had tried to sell the gauge to them. The gauge was retrieved in good working condition by the licensee. Local authorities were notified by the licensee." Notified R4DO (Powers), FSME EO (Wastler) and Mexico (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2007-02-01
43129 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2007-01-26 12:00 | 2007-01-29 12:31 | 2007-02-06 | MISSISSIPPI AGREEMENT STATE REPORT - STOLEN TROXLER DENSITY GAUGE Following Agreement State Report was received via e-mail "Description of Incident: DRH received notification on 1-28-07 from Mississippi Emergency Management Agency (MEMA) about a Troxler Model 3411 M/D gauge, Serial # 9533, that had been reported stolen. The gauge belonged to Aquaterra Engineering. The RSO was contacted and he stated that the gauge had been locked in a tool box. The tool box was not big enough to put the shipping container in it also, so the shipping container was in the bed of the truck. The RSO stated that the lock was cut on the tool box allowing the gauge to be removed. He also stated that the gauge's source rod was locked. Issued press release on 1-29-07. "Date of Incident: Sometime between 1-26-07 and 1-28-07 "Isotope(s): Cesium-137, 8 millicuries; & Americium-241:Be, 40 millicuries. "Describe clean-up actions taken by DRH: None required. "List any other actions required of DRH: Licensee will be required to send a written report of stolen gauge within 30 days. "List any actions taken to notify NRC, other Agreement States: Notified Meridian, MS, Police Department. Notified Lauderdale County Emergency Management. Notified NRC by E-mail. Notified Alabama Radiation Control by phone. Mississippi Department of Health issued press release. "Case Closed: No "Record of incident in RAM files: Yes "Enforcement action taken: Investigation ongoing." Incident No. MS 07001 * * * UPDATE ON 02/06/07 AT 1235 EST VIA E-MAIL FROM BOBBY SMITH TO MACKINNON * * * "Gauge found on 2-5-07 by unidentified citizen in a garbage dumpster. Notified Meridian Police Department & DRH was contacted. DRH sent inspector to pick up device. Device was undamaged and still locked. DRH returned device to owner on 2-6-07. "Describe clean-up actions taken by DRH: None required initially. After found device was retrieved by DRH so leak test could be done. No leakage or contamination detected. "List radiation measurements taken by DRH: After found device was surveyed and determined normal readings @ 13 Mr/hr surface. "List any other actions required of DRH: Licensee will be required to send a report of stolen gauge within 30 days. "List any actions taken to notify NRC, other Agreement States: Notified Meridian, MS Police Department. Notified Lauderdale County Emergency Management. Notified NRC by E-mail. Notified Alabama Radiation Control by phone. Mississippi Department of Health issued press release 1-29-07. "Case Closed: No 'Record of incident in RAM files: Yes "Enforcement action taken: Investigation ongoing" R4DO (Nease) & NMSS EO (Greg Morell) notified. E-mailed to ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2007-02-01
43128 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2007-01-27 20:40 | 2007-01-28 00:02 | 2007-01-28 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF LOAD TRANSIENT CAUSED BY EHC PROBLEM "On January 27, 2007 at approximately 2040 hours an automatic reactor trip occurred. The cause of the trip was Over Temperature Delta T (2/4). All systems functioned as designed. All control rods inserted on the trip. Decay heat removal is via condenser steam dump and Auxiliary Feedwater. "The initial cause of the trip appears to be from a loss of load due to a turbine electro-hydraulic system issue. This is still under investigation. "RCS Temperature is 547 Degrees F and stable "RCS Pressure is 2235 psig and stable "Both pressurizer PORVs momentarily opened and then closed during the transient. "For 8Hr Non Emergency 10 CFR 50.72(b)(3) "RPS actuation occurred. "Auxiliary Feed Water actuation occurred." There was no testing or maintenance in progress at the time of the transient. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-01-28
43127 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2007-01-27 09:05 | 2007-01-27 09:10 | 2007-01-27 | ERFIS REMOVED FROM SERVICE FOR PLANNED MODIFICATION "At 0905 hours EST, on January 27, 2007, the Emergency Response Facility Information System (ERFIS) computer system was removed from service to complete a planned modification of the ERFIS power supply system. The expected duration of ERFIS inoperability is approximately 2 hours. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, and the Inadequate Core Cooling Monitor (ICCM). The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above described functions. Therefore, it is expected that appropriate assessment or plant conditions, notifications, and communications could still be made, if required, during the time that the ERFIS computer system is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remain available to assess plant conditions, make notifications, and accomplish required communications, as necessary. An update to this message will be provided when the ERFIS is restored. "This message is similar to the January 6, 2007 event notification number 43081. At that time the ERFIS was being placed on an alternate power supply to allow modification of the normal power supply. This interruption of the ERFIS is due to the completion of that planned modification, which allows restoration of the ERFIS to the normal power supply." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 01/27/07 AT 1347 EST FROM LEONARD WIEGAND TO MACKINNON * * * Emergency Response Facility Information System (ERFIS) returned to service at 1150 EST. The NRC Resident Inspector will be informed of this update by the licensee. R2DO (Brian Bonser) notified | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-27
43126 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2007-01-26 17:15 | 2007-01-26 22:52 | 2007-01-27 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) DECLARED INOPERABLE. "On January 26, 2007 at 0915 hours, the Clinton Power Station Plant Process Computer failed causing a loss of the Safety Parameter Display System. At 1715 hours, troubleshooting is ongoing and the failure has not been corrected and SPDS has not been restored. Since SPDS was not restored within eight hours, this event is reportable due to a major loss of emergency assessment capability per 10CFR50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." * * * UPDATE PROVIDED BY JERAMY ANDERSON TO JEFF ROTTON AT 0704 EST ON 01/27/07 * * * "Plant process computer was restarted at 0405 CST and a 2 hour confidence run has been completed. The Safety Parameter Display System is now operable." The licensee will notify the NRC Resident Inspector. Notified R3DO (Passehl) | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-26
43125 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2007-01-26 13:54 | 2007-01-26 19:26 | 2007-01-27 | CAPABILITY TO DETERMINE STACK EFFLUENT RADIOACTIVITY RELEASE HAS BEEN LOST. "At 1354 on 01/26/07, Nine Mile Point Unit 1 determined that the capability to determine effluent radioactivity going out the stack had been lost. It is postulated that this is likely due to moisture in both the primary and aux sample lines had frozen, blocking the flow of effluent to sample analysis equipment. "Compensatory actions include; monitoring of alternate indications of increased radioactivity in the plant effluent stream and the development of procedures to quantify radioactivity release rate using existing operable instrumentation." The State of New York was notified of this event. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 01/26/07 AT 2137 EST BY ERIC KELSEY TO MACKINNON * * * "The following action is intended to provide stack effluent release rates, temporarily replacing the non-operable stack sampling and analysis system. The method being developed will assess the significant rad and ventilation contributions of each of the plant systems that exhaust to the stack: specifically, the Off Gas, Reactor, Turbine and Radwaste Building ventilation. This summation will be equivalent to the rad release that was provided by the non-operable system. This method will be procedurally based and can be accomplished by the on-shift Chemistry Technician and can be directly input into the NMP dose computer. "Repairs to the inoperable system will commence on day shift 1/27/07" R1DO (Neil Perry) notified. The NRC Resident Inspector and the State of New York were notified of this update by the licensee. * * * UPDATE ON 01/27/07 AT 1905 EST BY KIRSTY DANN TO SNYDER * * * "The stack sample low flow issue has been corrected as of 1/27/07 at 14:55. Stack flow monitoring of stack effluent has been re-established to a normal lineup." The licensee notified the NRC Resident Inspector. Notified R1DO (Neil Perry). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-26
43124 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2007-01-26 09:15 | 2007-01-26 17:55 | 2007-01-28 | CONTROL ROOM EMERGENCY VENTILATION AIR CONDITIONING (CREV AC) SYSTEM DECLARED INOPERABLE On January 26, 2007 at 0915 hours, the Control Room Emergency Ventilation Air Conditioning (CREV AC) system was declared inoperable due to not meeting the surveillance acceptance criteria for the refrigeration condensing unit (RCU) during QCOS 5750-11 (Control Room Emergency Ventilation System Test - performed every 2 years). As result Technical Specification 3.7.5 Condition "A" was entered (30 day Limiting Condition of Operation). "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident. "At this time, additional analysis is underway to determine the impact of the failure to meet the acceptance criteria on the CREV AC safety function." The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION 01/28/07 AT 1651 EST FROM C. KRONICH TO MACKINNON * * * "Further evaluation performed by Quad Cities Station confirms the CREV AC system would have performed its safety function. A revised surveillance (QCOS 5750-11, Control Room Emergency Ventilation System Test) was re-performed successfully, and the CREV AC system was declared operable on January 28, 2007 at 0911 hours. "Based on the subsequent evaluation and surveillance testing, ENS report # 43124 is being retracted." R3DO (Dave Passehl) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 97 | 96 | 0 | 97 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-01-26
43123 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-06-24 07:40 | 2007-01-26 13:36 | 2007-01-26 | CONTRABAND INTRODUCTED INTO PROTECTED AREA. Actual introduction of contraband into protected area. Immediate compensatory measures taken upon discovery. The licensee notified the Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-01-26
43122 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2007-01-25 | 2007-01-25 21:02 | 2007-01-25 | TAMPERING WITH SECURITY EQUIPMENT As a result of an NRC inspection the licensee reported five instances tampering with the security system. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-01-25
43121 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2007-01-25 17:17 | 2007-01-25 20:11 | 2007-01-25 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO DROPPED CONTROL ELEMENT ASSEMBLY (CEA) "Notification of shutdown required by the Technical Specifications per 10CFR50.72(b)(2)(i). Arkansas Nuclear One Unit 2 is shut down in Mode 3 (Hot Standby) due to Control Element Assembly misalignment as required by Technical Specification 3.1.3.1.d (All CEAs shall be OPERABLE with each CEA of a given group positioned within 7 inches, indicated position, of all other CEAs in its group). CEA #35 dropped to the bottom of the core due to power supply breaker trip during maintenance and was unable to be recovered within the allowed time. All rods were verified to trip normally as part of the controlled shutdown." The reactor was manually tripped from approx. 20% power. The reactor trip was preplanned. The NRC Resident Inspector and the county were notified of this event by the licensee. Licensee will also notify the State of this event. | 0 | 0 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2007-01-25
43120 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2007-01-24 12:00 | 2007-01-25 19:27 | 2007-04-24 | AGREEMENT STATE REPORT FROM WASHINGTON - RADIATION MONITORS AT A RECYCLING FACILITY DETECTED RADIOACTIVITY COMING FROM AN INCOMING LOAD OF SCRAP METAL This event was received via e-mail from the Washington State Department of Health, Office of Radiation Protection. "Licensee: Unknown & under investigation. "City and State: Tacoma, Washington "License Number: Unknown & under investigation. "Type of License: Unknown & under investigation. "Date and time of Event: Washington DOH responded to event site 24 January 2007, ~ 11:30 am). "Location of Event: Tacoma, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "WA DOH was notified on 24 January 2007 that radiation monitors at Schnitzer Steel (a metal recycling facility) detected radioactive sources in a load of scrap. The readings referenced by a Schnitzer's representative seemed unusually high so WA DOH staff were immediately sent to do a site investigation. Numerous meter & wipe surveys by WA DOH & Schnitzer's health physics consultant identified no site or source contamination. Four items of various materials, configurations and sizes were separated from the load. Some pieces had been wrapped in sheet lead. WA DOH staff measured from 0.6 to 80 mr/hr with an open beta window, ion-chamber survey meter. A waste disposal company had also been called to assure control of the materials for disposal. The nuclides, origins of the materials, and other details of the event remain under investigation. "Notification Reporting Criteria: Unknown & under investigation; possibly 10 CFR 20.2201 and WAC 246-221-240 'Reports of stolen, lost or missing radiation sources.' "Isotope and Activity involved: Unknown & under investigation. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Unknown & under investigation (none known at this time). "Lost, Stolen or Damaged? (mfg., model, serial number): Unknown & under investigation (none known at this time). "Disposition/recovery: Unknown & under investigation (none known at this time). Orphan unknown radioactive sources are secured and not a radiation hazard. "Leak test? Unknown & under investigation (none known at this time). "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) NA "Release of activity? Unknown & under investigation (none known at this time). Numerous meter & wipe surveys identified no contamination. "Activity and pharmaceutical compound intended: NA "Misadministered activity and/or compound received: NA "Device (HDR, etc.) Mfg., Model; computer program: NA "Exposure (intended/actual); consequences: NA "Was patient or responsible relative notified? NA "Was written report provided to patient? NA "Was referring physician notified? NA "Consultant used? Yes." Washington State Report Number WA-07-005 * * * UPDATE ON 04/24/07 AT 1500 EDT VIA E-MAIL FROM ARDEN C. SCROGGS TO MACKINNON * * * Status: Updated and Closed "Licensee: Unable to determine after extensive investigation. There are many rumors of possible origin, including military. The military asserted that they did not lose control of these items, there is no proof of military origin, and they have established radiation safety programs / procedures / training to prevent these items from being released into the public domain. Even if these items had been used by the military years ago, does not mean that the military last possessed them and released them to the public. Many natural radium items continue to circulate through the public domain through no fault of the military / manufacturers." License Number: Unable to determine after extensive investigation. Type of License: Unable to determine after extensive investigation. "WA DOH was notified on 24 January 2007 that radiation monitors at Schnitzer Steel (a metal recycling facility) detected radioactive sources in a load of scrap. The readings referenced by a Schnitzer's representative seemed unusually high so WA DOH staff was immediately sent on 24 January 2007 to do a site investigation. Numerous meter & wipe surveys by WA DOH & Schnitzer's health physics consultant identified no site or source contamination, and only minor contamination inside the yard box that contained the various items. "Schnizter deserves recognition for their detectors & staff that flagged & separated the unknown abandoned radioactive materials on their way to the shredder feed. It would have been a terrible mess and a serious health hazard if they had reached the shredder. A waste disposal company worked closely with WA DOH to immediately secure the abandoned unknown radioactive materials, to ensure absence of contamination, assess the nuclide and activities, and to promptly arrange for proper disposal. "Four distinct groups of unknown, abandoned radioactive materials, of various configurations and sizes were separated from the load. The estimated total maximum activity was 81 microcuries natural radium (radium-226). There were four distinct groups: group 1, a black coil, ~ 36 microcuries (~ 40 milliR / hr max @ ~ 1 inch, beta window closed); group 2, a hook & cable & 4 guides & cylinder ~ 4 microcuries (~ 400 microrem / hr max @ ~ 1 inch, 4 guides the highest); group 3, a folded steel sheet ~ 1 microcurie (~ 28 microrem / hr max @ ~ 1 inch); & group 4, a large sandwich of asbestos / wood / thick & heavy metal, ~ 40 microcuries (~ 44 microrem / hr max @ ~ 1 inch). All activities were overestimated due to the complicated nature of the materials and inability to directly access the sandwich and the folded sheet interiors. The radium coil was wrapped in sheet lead by Schnitzer Steel staff when separated from the non-radioactive scrap. "The coil has been recognized as one used by military decades ago; but it is not believed to have come recently from a military site. In 1977 all radium items were removed from military use, & all remaining radium items (mainly museum items) are inventoried & tracked by the military (at levels as low as 1 microcurie). Sad news is that many items still remain in public domain (we routinely receive calls / requests for help with such items). Per military scrap metal recycling contract conditions, all military scrap metal sent to recycling is separated from the other non-metal building scrap / debris, so the sandwich would not have left the military site as a sandwich; all metal would have been separated from the non-metal. All metal shipments leaving the military sites are surveyed by their military rad detectors / radiation safety staff. All military staff interviewed had an awareness of asbestos, would recognize that the asbestos needed proper sampling & handling & disposal, & would stop a shipment containing asbestos & follow their procedures to contact their hazmat asbestos abatement team. "The many manufacturers / vendors / service reps / users / radiation professionals contacted were unable to identify these items. The general reply is that radium is not an application used in this country, & has not been for many decades. The orphans look industrial in nature, & the presence of asbestos / acoustical board / heavy metal plates / wood suggests a high-temperature use, possibly steel / metal processing. It is possible that the sandwich radium sources were used with a fill level gauge. However, radium has not been used by most manufacturers in the US, & the last time it was used was decades ago. It is possible that these are not items that originated in the United States; that is consistent with the blatant disregard for proper asbestos handling. There is a small comfort in that current vendors / users are not tossing this mess. It is troubling that there is no definite answer as to origin / generator, & that the owner / generator possibly knowingly shipped these radioactive / asbestos items to a recycling center. It appears that someone knew they were removing the non-radioactive construction sections from around the radioactive sources section. Someone must have known that they were folding the steel plate to cover/ surround the source buried inside the fold. Someone also disregarded the proper asbestos disposal procedures. This indicates a willful disregard for the asbestos / radiation safety regulations, or a lack of awareness that they exist. "Notification Reporting Criteria: Yes, per WAC 246-221-240 Reports of stolen, lost or missing radiation sources . Notification is required immediately for 100 microcuries or more of lost, stolen or missing radium-226. Notification is required within 30 days for 1 microcurie or more of radium-226 that is still lost, stolen or missing. It is unclear whether federal Nuclear Regulatory Commission 10 CFR 20.2201 Reports of theft or loss of licensed material applies, because natural radium is not considered licensed material and is not regulated until very recently. "Isotope and Activity involved: Natural radium (radium-226), 81 microcuries total maximum estimate. Actual activity probably less due to conservative overestimating. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Extensive investigation identified no overexposures. Prompt identification & action by Schnitzer staff prevented the unknown abandoned radioactive / asbestos materials from entering the shredder feed. It would have been a terrible mess & a serious health hazard if they had reached the shredder. "Lost, Stolen or Damaged? (mfg., model, serial number): Extensive investigation identified no licensee /owner / generator. "Disposition/recovery: These abandoned unknown radioactive materials were immediately secured and not a radiation hazard. These abandoned radioactive materials were properly disposed of via a licensed radioactive waste disposal vendor on 28 February 2007. "Leak test? Wipe tests of the abandoned unknown radioactive materials confirmed absence of contamination in public areas of the site, and identified slightly elevated contamination in the yard box (maximum 98 disintegrations per minute per ~ 1,000 square centimeters composite wipe), and on the abandoned radioactive materials (maximum 784 disintegrations per minute per wipe). Because wipe & meter surveys identified contamination levels below regulatory limits (WAC 246-232-140, Schedule D) and not considered a health risk, the Department of Health did not have the site decontaminated. Per its commitment to ALARA, Schnitzer also arranged for proper disposal of the slightly contaminated yard box. "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) NA "Release of activity? Numerous meter & wipe surveys confirmed absence of contamination in public areas of the site, and identified slightly elevated contamination in the yard box, and on the abandoned radioactive materials (please see Leak tests above). "Activity and pharmaceutical compound intended: NA "Misadministered activity and/or compound received: NA "Device (HDR, etc.) Mfg., Model; computer program: NA "Exposure (intended/actual); consequences: NA "Was patient or responsible relative notified? NA "Was written report provided to patient? NA "Was referring physician notified? NA "Consultant used? Yes." FSME (Greg Morell) & R4DO (Linda Smith) notified. E-mailed to ILTAB. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2007-01-30
43119 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2007-01-25 05:42 | 2007-01-25 15:38 | 2007-01-25 | LOSS OF SAFETY PARAMETERS DISPLAY SYSTEM (SPDS) "On 01/25/07 at 05:42am CT, the Wolf Creek Generating Station Nuclear Plant Information System (NPIS) computer 'C' primary and all backup MUX's failed. Subsequent troubleshooting failed to restore all primary MUX's to operation in a short period of time. "The failure to restore the NPIS computer has resulted in a loss of functionality of the SPDS. Due to SPDS being lost for longer than a short period of time, Wolf Creek Nuclear Operating Corporation is making this ENS notification pursuant to the criteria of 10 CFR 50.72(b)(3)(xiii). There was no other loss of emergency assessment capability concurrent with the ongoing loss of SPDS. Plant personnel entered the appropriate Off-Normal procedure and obtained local readings for the equipment that is normally monitored by SPDS and NPIS during the loss of the plant computer. "NPIS was restored to service and declared operable on the primary plant computer at 13:57 CT. The return of the NPIS computer to an operable condition restored the SPDS assessment capability function. "The licensee notified the NRC Resident Inspector" | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-25
43118 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2007-01-24 09:55 | 2007-01-24 18:08 | 2007-01-24 | MISSING PIPE CLAMP BOLT FOUND ON HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM "During a RFO-20 pre-outage inspection of HPCl Injection Line Pipe Support EBB-5-SR-9, it was noted that one of the two pipe clamp bolts (i.e. stud, nuts, and spacer) was missing. This rendered HPCl and Primary Containment inoperable. Technical Specifications 3.5.1 Condition F for HPCl inoperable, and 3.6.1.1 Condition A for Primary Containment inoperable, were entered. Since Primary Containment operability was not restored within one hour, Technical Specification 3.6.1.1 Condition B to be in Mode 3 in 12 hours and Mode 4 in 36 hours was entered. "At 1649 the pipe clamp was restored, HPCl and Primary Containment were declared operable, and Technical Specifications 3.5.1 Condition F and 3.6.1.1 Conditions A and B were exited. "This event is reportable as an 8 hour event under 10 CFR 50.72(b)(3)(ii)(A), Any event or condition that results in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded and 10CFR 50.72(b)(3)(v)(D), Any event or condition that alone at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2007-01-24
43117 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2007-01-13 12:30 | 2007-01-24 14:05 | 2007-01-24 | FAILURE OF RADIOGRAPHY CAMERA SOURCE TO FULLY RETRACT On January 13, 2006, at 12:30 am local time, while performing a radiography at the facility in Kuparuk, Alaska, the radiography camera source failed to fully retract into the shielded position. The radiographer contacted the Level 2 Radiographer who shielded the camera and was able to fully retract the source. No over-exposures occurred. The camera is a INC Model IR-100, serial number 6631 with a source serial number of J744. The typical original Ir-192 source strength of this type of radiography camera is about 100 curies. Kakivik Asset Management has contacted the manufacturer of the camera about this occurrence and other similar occurrences. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2007-01-24
43116 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2007-01-23 15:15 | 2007-01-23 16:27 | 2007-01-23 | UNANALYZED CONDITION "Crystal River 3 has determined that an existing condition in the Decay Heat (DH) System is reportable under 10 CFR 50.72(b)(3)(ii)(B), an Unanalyzed Condition. Two valves in question are in series in the DH System drop leg from the Reactor Coolant System (RCS). They are Appendix R High-Low pressure interface valves, where 3 phase hot shorts from another power cable must be considered. A review of cable routing concluded that one of the valve's power cables and one of the valve's control power cables do not meet required separation criteria. There is a low probability that both could open due to hot shorts under normal operating RCS pressure and temperature conditions, therefore a rupture of the downstream piping in the Reactor Building or Auxiliary Building is possible. The postulated event is a Loss of Coolant Accident (LOCA) in the Auxiliary Building, which is an unanalyzed condition. This condition is similar to the one reported in EN# 43098 on 01/12/2007. Cables in question are for the same valves, however, they are in a different area of the plant." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-01-23
43115 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-01-23 12:44 | 2007-01-23 14:44 | 2007-01-23 | REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE FAILURE "An automatic reactor scram occurred resulting from loop #2 steam generator low level. The main feedwater regulating valve 2-FCV-3-48 failed closed when the air supply line to the valve severed. A significant leak had been identified and efforts to repair had been initiated. All systems responded as designed. The plant is stable on Auxiliary Feed Water (AFW) and steam generator cooling [to the condenser via steam dump valve] while repairs to the failed air line are planned." All control rods fully inserted into the core. No steam generator or pressurizer relief valves lifted during the transient. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-01-23
43114 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-01-23 13:00 | 2007-01-23 14:27 | 2007-01-23 | PRESS RELEASE ISSUED "The purpose of this notification is to inform the NRC that Nuclear Management Company (NMC) will be issuing a press release approximately two hours (CST) after this notification to the NRC on January 23, 2007, concerning an event previously reported to the NRC on January 10, 2007, via EN# 43088. The event in question involved an automatic reactor scram at 3:26 PM on January 10, 2007. As reported in that notification, all safety systems operated correctly. The scram occurred following the unexpected opening of the main turbine control valves. There was no release of radioactivity during the event. The purpose of the press release is to provide information to the media and the public regarding the results of NMC's investigation as to the cause of the January 10 event and the status of remedial actions." The licensee notified the NRC Resident Inspector. The licensee will notify State and Local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-01-23
43113 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2007-01-22 19:00 | 2007-01-22 22:42 | 2007-03-09 | HPCI DECLARED INOPERABLE DUE TO FAULTY FLOW INDICATOR The licensee discovered that the High Pressure Coolant Injection (HPCI) system flow control loop was degraded in such a manner that HPCI would not perform its safety function. The HPCI loop flow indicator indicated 200 GPM with no flow in the loop. The specification for that parameter is <100GPM. With the flow indicator in this condition the HPCI flow controller would perform non-conservatively (less flow into the system than was demanded), and would not perform its intended safety function therefore rendering HPCI inoperable. The licensee declared HPCI inoperable and in accordance with Technical Specification 3.5.E.2 entered a 14 day LCO. The licensee has commenced troubleshooting and will initiate repairs as necessary to return the system to operation. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 03/09/07 AT 1413 EST FROM M. RAMSEY TO MACKINNON * * * "BASIS FOR RETRACTION: "NRC Event Notification 43113 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10CFR50.73 were met pending the evaluation of an atypical condition observed with the High Pressure Coolant Injection (HPCI) Flow Indicator that was observed by Operators during routine monitoring of plant equipment. After comparing the observed flow indication to allowable values for meter uncertainties, it was determined that the initial NRC Notification was not required. The HPCI system was capable of fulfilling all design safety functions. Additional measures to ensure system reliability were completed that included removing and bench testing the recently refurbished 'square root converter' and calibration verification of involved components. No degraded conditions were discovered. "ENS Event Number 43113, made on 01/22/07, is being retracted." R1DO (Neil Perry) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-01-22
43112 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-06-13 12:00 | 2007-01-22 13:26 | 2007-01-22 | AGREEMENT STATE REPORT - MEDICAL EVENT - MISADMINISTRATION OF BRACHTHERAPY SEEDS The State of Florida was notified on 01/11/07 by Florida Agency for Health Care Administration that while performing an audit of the licensee it appeared a misadministration of brachytherapy seeds on June 13, 2006 was not reported to DOH-BRC, nor was there any documentation it was done. The State is planning to visit the licensee in the next few days to obtain details of this medical event from the Radiation Oncologist. The auditor provide the following documentation to the State concerning a prostate seed implant procedure performed on June 13, 2006 at the Surgical Center of Central Florida: "A review of preplanning, live planning and post planning documents was conducted on June 22, 2006, and a wrong site administration (as defined in Florida Administrative Code 64&5. 101, 88-6) was declared by the prescribing radiation oncologist and the Radiation Safety Officer associated with the Cancer Care Center of Sebring. Their conclusion was supported by diagnostic films and the physics calculations. Consistent with the Florida Radiation Safety Guidelines, the patient's referring physician was also contacted by the treating urologist on June 23, 2006 and [the] facility was advised within 24 hours of the finding. Both the patient and his wife have been informed of the post procedure evaluation results and the patient has undergone a diagnostic computed tomography exam and follow-up appointment at the Cancer Care Center in Sebring. "As a result of further assessment, the apparent misadministration incident was determined to be reportable to the State of Florida pursuant to Florida Administrative Code Section 53E-5.345 4A by the license holder and its' Radiation Safety Officer. . . . " The procedure involved the implant of sixty I-125 seeds totaling approximately 20 milliCuries. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR | 35.3045(a)(3) |  |  |  | 0 | 2007-01-28
43111 | 0 | CAMDEN IRON AND METAL |  |  |  |  | 2007-01-22 07:00 | 2007-01-22 09:38 | 2007-01-22 | STOLEN ALLOY ANALYZER A Niton Alloy Analyzer was stolen probably after midnight on 1/22/2007 (it snowed late last night and there were tracks in the snow). The hand-held gun type analyzer was locked in a case similar to a suitcase. To prevent unauthorized use, a code number is also required to use the analyzer. No other material was stolen. The Camden police were notified. Model: XLP818Q Serial number: 6406 Source: 30 milliCurie Cd/Am-241 Camden Police Report Case: 070122-044 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2007-01-22
43110 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2007-01-21 14:00 | 2007-01-21 19:43 | 2007-01-24 | AGREEMENT STATE REPORT - LOST RADIOGRAPHY CAMERA On 1/20/07 at approximately 1400 CST, a licensee radiographer was transiting down a lease road in his vehicle (white 2001 or 2002 Dodge diesel pickup truck with a fiberglass radiographer dark room on the back) with a radiography camera secured in a yellow box in the back. The radiographer attempted to cross moving water. When the radiographer attempted to cross the water the engine was stalled by the flow of water. The water started to flow into the truck over the doors. The radiographer evacuated the truck. The truck was subsequently swept away. Oklahoma Emergency Management, Local Law Enforcement and the Oklahoma State Police were notified and initiated a search for the lost camera. The search was conducted on the ground and in the air via a helicopter. The licensee RSO was notified and is en route to the area. At this time the camera has been not located, but a log jam was discovered down stream of where the truck was swept away and it is not believed that the truck could have passed this log jam. The search has been called off due to darkness. The area that the camera is suspected to be is very remote and lightly populated. It is between the towns of McAlester, OK and Calvin, OK. It is unlikely that the camera could relocate to a populated area. The search will resume on 1/22/07 at 0700 CST. The camera is a new Industrial Nuclear Corporation model Ir-192 camera. The source strength is 100 Ci. Notified NORTHCOM (via e-mail) * * * UPDATE FROM STATE OF OKLAHOMA (BRODERICK) TO HUFFMAN AT 0940 EST ON 1/22/07 * * * The State of Oklahoma representative reports that the pickup truck is believed to have been located downstream of where it was swept into the water. The location is known as "Coal Creek." Only the shell of the truck can be seen but it is the judgment of those at the scene that the shell is still attached to the truck. Local law enforcement is at the site and has secured it from unauthorized entry. The camera was reported to be in an ammo box that was locked and welded to the bed of the pickup truck so it is likely also still attached to the truck. Because of the unsafe conditions in the creek at this time, the site will remain secured and attempts to retrieve the truck will be made when the water flow is reduced and the levels receded. The State estimates that retrieval will not be until sometime in the morning of Tuesday, January 23. The State indicated that there is media interest in this event and that a press release is being prepared. R4DO (Hay), NMSS EO (Burgess), IRD (Cruz), and ILTAB (Sandler) notified. * * * UPDATE FROM STATE OF OKLAHOMA (BRODERICK) TO KOZAL AT 1459 EST ON 1/22/07 * * * The State provided the following information via email: "The search was resumed on the morning of the 22nd, and searchers quickly located the truck. The top of the camper was visible from the bank. This area was impacted by the snow and ice storms of recent weeks, and the creek is high because of runoff of snow melt. The water is fast moving and cold. Searchers felt there was substantial risk in accessing the truck in these conditions. Local sources estimate the creek will return to a more normal level enabling safe access to the source sometime Tuesday. The licensee plans to maintain security on the truck and source, but let it stay where it is until then. DEQ concurred with this decision. "At about 1 PM on the 22nd, the licensee reported that the water level had dropped and about half the camper shell is above water. It looks intact, and the door of the camper appears to still be locked. They still expect to be able to access the truck on the 23rd. "The camper appears intact, and it is assumed that the source is inside the camera inside the locked ammo box in the camper. The ammo box is bolted to the bed of the truck [not welded, as was previously erroneously reported to NRC], and it is assumed that the source is still present. This incident was reported on television and print media. DEQ has prepared a press release in case one is needed, but does not plan to issue it at this time. DEQ staff are en route to the area and will be present tomorrow during recovery. They will also interview the radiographer and assistant involved in the accident." R4DO (Hay), NMSS EO (Burgess), IRD (Cruz), and ILTAB (Sandler) notified. * * * UPDATE FROM STATE OF OKLAHOMA (BRODERICK) TO KOZAL AT 1031 EST ON 1/23/07 * * * The State provided the following information via email: "The water has not gone down enough to allow safe access to the truck this morning, and is not expected to drop enough today to allow it. The licensee is now hoping for access to the truck tomorrow." The licensee will continue to provide security for the truck. R4DO (Hay), NMSS EO (Morell), IRD (Blount), and ILTAB (Sandler) notified. * * * UPDATE FROM STATE OF OKLAHOMA (BRODERICK) TO GOTT AT 1450 EST ON 1/24/07 * * * The State provided the following information via email: "The licensee has recovered the camera. It appears to be intact. As a precautionary measure, DEQ staff will take surveys and wipe tests of the camera and return to the office." Notified R4DO (Hay), NMSS EO (Morell), IRD (Blount), ILTAB (Sandler), DHS (Constantopoulos), FEMA (M. Laforty), DOE (M. Smith), USDA (A. Paris), NORTHCOM (Maj. Martin), and HHS ( M. Dalziel). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-01-24
43109 | -1 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2007-01-20 03:38 | 2007-01-20 16:38 | 2007-02-14 | CREVS AND CRETS INOPERABLE DUE TO 1A AND 2B EDG OOS The licensee discovered two separate issues that required the 1A EDG and 2B EDG to be declared inoperable. It was discovered that the 1A EDG exhaust fan damper had failed which required the 1A EDG to be declared inoperable and 22A Service Water Heat Exchanger Inlet strainer diversion valve was failed which required the 2B EDG to be declared inoperable. With both of the EDG's inoperable the licensee declared the Control Room Emergency Ventilation System (CREVS) and the Control Room Emergency Temperature System (CRETS) systems inoperable. This condition placed the licensee in a 2 hour LCO to place the plant in hot shutdown. At 0432 the 1A EDG was restored to operability and the applicable LCO was exited. The condition existed for 56 minutes. Subsequently the repairs were completed on the 22A Service Water Heat Exchanger Inlet strainer diversion valve and the 2B EDG was returned to service. The licensee notified the NRC Resident Inspector. * * * UPDATED AT 1248 EST ON 2/14/07 FROM JOE GIOFFRE TO S. SANDIN * * * This notification is retracted based on the following: "On January 20, 2007, at 16:38 EST, EN 43109 was made by Calvert Cliffs Nuclear Power Plant in accordance with 10 CFR 50.72(b)(3)(v)(D), 'Event or Condition That Could Have Prevented Fulfillment of Safety Function'. At that time, a condition was believed to exist which, at the time of discovery, could have prevented the fulfillment of a system function that is needed to mitigate the consequences of an accident. Specifically, the onsite emergency power supplies to both trains of the Control Room Emergency Ventilation System (CREVS) and Control Room Emergency Temperature System (CRETS) were declared inoperable due to separate issues on the 1A EDG and the 2B EDG. "After further evaluation, it has been determined that both DG's were operable and, therefore, the CREVS/CRETS safety function was not lost. Significant margin existed to support operability for both DG's. Accordingly, this event is not reportable. EN43109 is, therefore, retracted by this notice." The licensee informed the NRC Resident Inspector. Notified R1DO (White). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2007-01-20
43108 | 0 | CONAM INSPECTION |  |  |  |  | 2007-01-20 05:00 | 2007-01-20 13:41 | 2007-01-20 | POTENTIAL EXTREMITY DOSE IN EXCESS OF 50 REM The licensee was performing radiography at the Sunoco refinery in Philadelphia, PA when a radiographer approached the front of a radiography camera thinking that he had retracted the radiography source and manipulated the source holder to another position and returned to the rear of the camera. When the radiographer attempted to expose the source he thought was retracted, he found the source in the exposed position. The radiographer then retracted the source, secured it, and then reported the incident to the Radiation Safety Officer. The radiographer received a calculated dose of between 44 and 55 Rem to the right hand and fingers due to this event. The length of exposure was approximately 55 sec. The individual was wearing a film badge and dosimeter but no alarming rate dosimeter. Both dosimeters were sent in to be read and determine actual dose received. The radiography camera was a 660 AEA Ir-192 camera with current source strength of 77 Ci. The radiographer has been sent for medical treatment and will continue with treatment until further notice. The licensee has initiated the following corrective actions: radiographer has been relieved of duty; all work has been stopped at the Sunoco refinery; the licensee will require two individuals at the radiography site to ensure source position and securing of the source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2007-01-20
43107 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2007-01-19 14:10 | 2007-01-19 17:22 | 2007-01-19 | OFFSITE NOTIFICATION DUE TO PRESS RELEASE "The licensee issued a news release for closure of the Cesium -137 issue identified in December 2006. Results of the extensive review indicate all sample levels to be within expected ranges for this area. This notification is being made due to heightened public awareness for environmental issues." The licensee notified the NRC Resident Inspector. See related event notification #43053. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-01-19
43106 | -1 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2007-01-18 16:00 | 2007-01-18 21:08 | 2007-01-22 | BATTERY CHARGER ROOM COOLER INOPERABLE "Entered a condition which required TS 3.0.3 entry and an 8 hour report. While the 2B RHR equipment outage was in progress, it was discovered that the 2A Battery Charger room cooler was not operating. The condition was investigated and it was found that the thermal overloads were tripped on the supply breaker. They were reset and the fan was restarted. The shift observed the fan operation for 10 minutes and then decided to check the breaker every 30 minutes until a plan could be implemented to swap trains of battery chargers. During the first 30 minute check, the breaker overloads were found tripped again. See time line below. "This put us in a condition where an LOSF existed on both trains of RHR due to the requirement to evaluate supported systems when opposite train LCO's are entered. 02:00 2B RHR tagged out for equipment outage, entered LCO for RHR. 16:00 2A Battery Charger room cooler found not running. Entered LCO for DC sources. 16:35 Overloads reset on 2A Battery Charger room cooler supply breaker and fan restarted. LCO initially cleared, but now will conservatively be reinstated since the overloads tripped again later. 17:02 2A Battery Charger room cooler breaker thermal overloads found tripped again. 17:26 2B RHR tagged in and made available, but not yet operable (still need to perform surveillance), 17:37 Swing Battery Charger (2C) placed in service for 2A. Exited LCO for DC sources. "LCO 3.0.3 was applicable from 16:00 until 17:37. Condition is reportable under 10CFR50.72(b)(3)(v) 'Event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.'" The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY HUNTER TO KOZAL ON 1/22/07 AT 1457 EST * * * "The eight hour report (EN #43106) per 10 CFR 50.72(b)(3)(v)(b) was conservatively reported based on inconsistent operation of non-TS [Technical Specification] attendant equipment (the room cooler supplying cooling to the A-Train Battery charger) leading to the declaration of the battery charger as inoperable. However, no actual loss of safety function existed for the Unit 2 RHR Subsystem. Therefore, the eight hour report is retracted for the following reasons: "The A-train DC battery was operable, and the A-train DC Battery Charger and DC bus were available. Procedures and training are in place for the door between the battery charger rooms to be opened to ensure sufficient cooling to the A train DC switchgear room. The time for room temperature heat-up allows for operator actions and the rooms and entry/exit pathways are accessible for operators to perform these actions during normal operations and design basis events. The battery charger room temperature was 86F upon discovery which is well within the equipment capability. Therefore, the battery charger room cooler system was available to provide cooling for the long term design basis accident. "Technical specification 3.5.2, Condition A was entered due to the Unit 2 B-Train RHR pump scheduled equipment outage. During the entire time that the Unit 2 B-Train RHR pump was inoperable and out of service, the Unit 2 A-Train RHR pump would have performed its required function to supply sufficient flow during an accident (it was declared inoperable due to an inoperable DC support system, but remained available). Condition A allows one or more ECCS trains to be inoperable provided that 'at least 100% of the ECCS flow equivalent to a single OPERABLE ECCS train' is available. Even with the battery charger room cooler non-functional, the A-Train RHR pump would have performed its safety function and combined with the A-Train charging pump, would have delivered 100% of the ECCS flow equivalent to a single OPERABLE ECCS train. "In summary, a loss of safety function on both trains of RHR did not exist and the 50.72(b)(3)(v)(b) report (EN # 43106) is retracted." Notified R2DO (HAAG). The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2007-01-18
43105 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2007-01-14 10:46 | 2007-01-16 11:15 | 2007-01-18 | AGREEMENT STATE REPORT - MASSACHUSETTS - STOLEN Mo-99 GENERATOR The National Response Center notified the NRC Operations Center that a 6 curie Molybdenum-99 generator was reported stolen in the State of Wisconsin. A representative of the shipment carrier along with the State of Wisconsin Radiation Protection Section provided additional details. The generator had originated at Bristol Myers Squibb in Massachusetts and was stolen from a pickup truck at the Milwaukee, WI Airport en route to Froedtert Hospital in Wisconsin. The theft was reported to the Milwaukee Sheriff's Department. Massachusetts has assigned docket number 01-6787 to track this incident. * * * UPDATE FROM SCHMIDT (WISCONSIN RADIATION PROTECTION) TO KNOKE AT 1330 ON 1/18/07 * * * A representative of the State of Wisconsin Radiation Protection Section called reporting that the material package was not stolen from the truck, but had fallen off the truck while enroute Froedtert Hospital. On 1/14/07 a private citizen had observed this event and took the material package home with him and contacted the carrier company identified on the shipping label. Because this was over the weekend no one was at the company to take the call. On 1/17/07 the citizen turned in the missing package to local police. The police subsequently brought the package to Froedtert Hospital in Wisconsin. On 1/18 the hospital evaluated the container and determined there was no damage and no contamination. The NRC Operations Center conveyed this information to the State of Massachusetts Radiation Control Program (Sumares). Contacted R1DO (Cobey), R3DO (Peterson), NMSS (Wastler), ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2007-01-23
43104 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2007-01-10 09:00 | 2007-01-16 17:54 | 2007-01-16 | RADIOGRAPHY CAMERA MALFUNCTION During an equipment checkout prior to use, the ball of the drive cable broke during hookup of the pigtail to the drive cable. The source was locked in the safe position and no exposure was realized due to this incident. The radiography camera is an INC IR100 Model 32 (Serial # 4813) with a 65.8 curie Ir-192 source (serial # J590). The camera will be sent to the manufacturer for inspection and evaluation of the failure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | AK | MAT | [5 empty] | 0 | 2007-01-16
43103 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2007-01-15 11:00 | 2007-01-16 13:38 | 2007-01-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION At 1100 on 01/15/07, the radiography crew reported a radiography camera malfunction to their Radiation Safety Officer. The crew was using a Model SPEC 150 radiography exposure device with a 71 curie Ir-192 source. The radiography source had become disconnected from the drive cable and was stuck in the guide tube near the collimator. The guide tube was not crimped and the cause of the disconnect is not known. The crew covered the collimator with sand bags to limit access. That afternoon after consulting with SPEC, the crew was able to retract the source using a tong type apparatus. The licensee will return the camera to SPEC for repairs. There were no abnormal exposures. The crew was from Oklahoma and was working near Bonanza, Utah under a reciprocity agreement. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2007-01-19
43102 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-01-14 15:42 | 2007-01-15 20:02 | 2007-01-17 | INFORMATION REGARDING WILDFIRE IN THE VICINITY OF THE PLANT SITE "On January 14, 2007, at 1713 PST licensed plant operators initiated Technical Specification tracking sheet T0058983 documenting a potential trip risk, due to notification of a wild land fire adjacent to the Diablo Canyon Power Plant (DCPP) Units 1 and 2. The fire is located approximately 1 mile north of the plant site on rural agricultural and State of California property at Montana de Oro State Park. "Since the initial notification the fire has expanded to over a section of wild land about 1 mile north of the plant. The fire is being fought by State of California Department of Forestry (CDF), DCPP and local area fire fighting organizations by land and air attack equipment. "On January 15, 2007, at 1530 PST plant management concurred with recommendations to issue an information notice due to local news interest. Pacific Gas and Electric Company (PG&E) is supporting the efforts lead by the CDF to combat the wild land fire, and the staff of DCPP is being fully advised of the fire conditions on an ongoing basis. To date no PG&E facilities or operations are threatened and CDF and DCPP fire fighting personnel are routinely updating plant operators regarding fire fighting activities in the area. "No actual or potential threat to plant operation or equipment has occurred or expected and this report will be updated upon successful control of the wild land fire, currently expected to be early January 16, 2007." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY LARRY PARKER TO JEFF ROTTON AT 1830 EST ON 01/17/07 * * * "On January 17, 2007 the fire was reported as 100% contained by the California Department of Forestry (CDF). CDF personnel will remain on the scene until operations throughout the burn area are complete. The fire burned a little over 320 acres and did not impact the operation of DCPP or its offsite transmission network. No further updates of this notification are required." The licensee notified the NRC Resident Inspector. Notified R4DO (Campbell). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2007-01-15
43101 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2007-01-15 13:21 | 2007-01-15 17:24 | 2007-01-15 | OFFSITE NOTIFICATION - OIL SPILL At 1321 on January 15, 2007, the Point Beach Nuclear Plant asset owner notified the Wisconsin Department of Natural Resources (WDNR) that at about 10:00 a.m. on Sunday, January 14, 2007, approximately 20-25 gallons of vacuum pump hydraulic oil was released to the roof of the Point Beach Nuclear Plant heating boiler room. This event was caused by a failed seal in a vacuum pump. A small amount of this oil entered the rooftop drain system, and from there, it entered the plant's storm water drain system. The plant staff contained and removed the oil from the roof system. Absorbent pads were placed in the storm water system and at the exit of the system near the riprap above the beach. Approximately one gallon of the hydraulic oil was collected in the absorbent material at the exit of the storm water system. No oil discharged to the beach or the surface water. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-01-15
43100 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2007-01-12 19:00 | 2007-01-15 14:18 | 2009-05-21 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via email: "On January 15, 2007, about 10:00 am, the [California] DHS Duty Officer received a call regarding a stolen Troxler, Model 3430 Moisture/Density Gauge (SN 35954), containing a nominal 8 millicuries Cs-137 and 40 millicuries Am-241. The gauge user went to his home, after work on Friday, January 12, 2007, to have dinner, before returning the gauge to the authorized storage location. The gauge was chained in an open-bed pick-up truck. When the user returned to the truck, between 7:00 - 7:30 pm that evening, the chains had been cut, and the gauge was gone. The user did not report this to the licensee's home office until approximately 9:30 am, Monday, January 15, 2007, at which time, the licensee phoned the police, and notified [CA] DHS. RHB will follow-up with the licensee on this issue." State report number: 011507 * * * UPDATE FROM THE STATE OF CALIFORNIA TO JOHN KNOKE VIA EMAIL ON 5/20/09 @ 1848 EDT * * * "Recovered gauge was previously reported stolen on January 15, 2007 from Krazan & Associates (NMED #070031 RH5010 #011507) "At 0830 on Wednesday, May 20, 2009, the Department received a call from the local metal recycler stating the radiation alarm was set off when an individual brought a truck load of metal to recycle. The item that set off the alarm was a nuclear soil density gauge. The individual stated he had found the gauge in the street at the corner of Highland Avenue and Valencia Avenue in San Bernardino, CA. Information was taken from the driver and the gauge was surveyed and secured in SA Recycling's hazardous waste trailer until the Department could arrive. "At 0945, the Department arrived on site to survey the gauge and take identifying information from the gauge. The outer plastic housing of the gauge had been broken off, but the metal casing and handle appeared intact. The source rod was retracted and the Cesium 137 source was in the safe shielded position and the Americium 241:Be source metal housing and shielding was also intact. The surface of the gauge was wiped and there was no external contamination found. "Using a Victoreen, CHP 450 #414, the highest reading found was at the surface of the Americium 241:Be source housing - 18 milliRoentgen per hour (mR/hr) at the surface; 0.68 mR/hr at 1 foot; 0.1 mR/hr at 3 feet; with a background of 0.02 mR/hr. This gauge was a Troxler, model 3430, #35954 with a 40 milliCurie (mCi) Americium 241:Be source #78931 assayed on 8-16-04 and a 8 mCi Cesium 137 source #77-3063 assayed on 10-15-04. We then contacted the manufacturer who identified the gauge as belonging to Krazan & Associates, Ontario, CA. This gauge had been reported stolen on January 15, 2007 (RH5010 #011507, NMED# 070031). The gauge was returned to the Krazan& Associates in Ontario who will send the gauge to the manufacturer for evaluation and repair or disposal as necessary. The Anaheim Police were also notified of the recovery of the gauge." Notified R4DO (Jones), FSME EO (Chang), ILTAB (via email) and Mexico (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-01-18
43099 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2007-01-14 10:46 | 2007-01-14 14:58 | 2007-01-18 | AGREEMENT STATE REPORT - STOLEN Mo-99 SOURCE National Response Center reported that a radioactive material package (Molybdenum-99) was stolen from a pickup truck with a shell. The truck was at the Milwaukee WI Airport enroute from Bristol-Meyers-Squibb in Massachusetts to Froedtert Hospital in Wisconsin. The package was in a Type A box with Yellow II labels. Tradewind Enterprises reported that the package contained 6 Curies of Mo-99. The theft was reported to the Milwaukee Sheriff Department. National Response Center Report #823642 *** UPDATE FROM SCHMIDT TO KNOKE AT 13:30 ON 1/18/07 *** The State called indicating the material package was not stolen from the truck, but had fallen off the truck while enroute. On 1/14/07 a private citizen had observed this event and took the material package home with him and contacted the carrier company identified on the shipping label. Because this was over the weekend no one was at the company to take the call. On 1/17/07 the citizen contacted the local police and they returned it to Froedtert Hospital in Wisconsin. On 1/18 the hospital evaluated the container and determined there was no damage and no contamination. Contacted R3DO (Peterson), NMSS (Wastler), ILTAB (email). See related NRC event report #43105 from the State of Massachusetts. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-01-17
43098 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2007-01-12 16:31 | 2007-01-12 17:19 | 2007-01-12 | UNANALYZED CONDITION OF DECAY HEAT SYSTEM "Crystal River Unit 3 has determined that an existing condition in the Decay Heat (DH) System is reportable under 10 CFR.50.72 (b)(3)(ii)(B), an Unanalyzed Condition. Two valves in question are in series in the Decay Heat (DH) System drop leg from the Reactor Coolant System (RCS). These valves are High-Low pressure interface valves, where three phase hot shorts from another power cable must be considered under Appendix R. A review of cable routing concluded that the two valve's power cables do not meet required Appendix R separation or protection criteria. As such, there is a low probability that both valves could open due to hot shorts under normal operating RCS pressure and temperature conditions, resulting in a rupture of the downstream piping in the Reactor Building or Auxiliary Building. This event could result in a Loss of Coolant Accident (LOCA) in the Auxiliary Building, which is an unanalyzed condition." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2007-01-12
43097 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-11-19 20:28 | 2007-01-12 15:33 | 2007-01-12 | INVALID ACTUATION OF PRIMARY CONTAINMENT ISOLATION SYSTEM "This telephone report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition caused by an invalid signal that resulted in an automatic actuation on November 19, 2006 at 2028 CST of the following Primary Containment Isolation System (PCIS) groups: * Group 2, Primary Containment isolations (partial) including Shutdown Cooling (SDC) valve isolation with no loss of SDC function. * Group 6, Secondary Containment isolation, and initiation of Standby Gas Treatment System and Control Room Emergency Filtration System (complete). "The systems above functioned as designed. Reactor Protection System (RPS) bus 'B' had lost power from its Motor Generator (MG) and was found de-energized which caused the actuations. Power was restored to the RPS bus 'B' from auxiliary power, and plant systems were recovered. "In addition to the actuations reported above, the following actuations also occurred and functioned as designed. * RPS half-scram on B channel (no rods moved); * Half-group isolations of the following PCIS Groups; * Group 1, Main Steam Isolation Valves (valves were already shut), * Group 3, Reactor Water Clean-up (one valve shut), * Group 7, Recirculation Loop Sample Lines (valves were already shut), "The cause of the invalid signal was 'B' RPS MG set high voltage condition produced by a faulty voltage adjust potentiometer in the voltage regulator. This caused a protective relay to trip the RPS MG exciter field which caused the subsequent low voltage and loss of the 'B' RPS bus." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-01-12
43096 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2007-01-12 10:39 | 2007-01-12 12:39 | 2007-01-12 | TURBINE TRIP/REACTOR TRIP "At 1039 Kewaunee Power Station experienced a loss of auto stop oil pressure on the main turbine while performing the monthly Turbine Trip Mechanism Test resulting in a reactor trip. No safeguards equipment was out of service at time of trip. Following the trip one of the moisture separators associated with the main turbine had its associated steam inlet valve fail open, which resulted in RCS temperature decreasing to 536 degrees F. This valve was manually isolated and RCS temperature returned to normal 547 degrees F. Normal heat sink via the condenser was available during the event. Investigation is continuing into the cause of the turbine trip. "This event is being reported under 10CFR50.72(b)(2)(iv)(B) for actuation of the Reactor Protection System and 10CFR50.72(b)(3)(iv)(A) for actuation of the Auxiliary Feedwater System." All rods fully inserted and no primary or secondary PORV's lifted. There was no injection from any safety systems, other than AFW. Decay heat is being dumped to the condenser via steam dumps. The reactor coolant pressure and temperature are stable. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-01-12
43095 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-01-11 17:30 | 2007-01-11 19:09 | 2007-01-11 | OFFSITE NOTIFICATION TO STATE AGENCIES "Notification to NRC following notification to the following government agencies: State of Minnesota Pollution Control Agency State of Minnesota Dept of Natural Resources Enforcement State of Minnesota Dept of Natural Resources Area Fisheries Office State of Minnesota Dept of Natural Resources Local Conservation Office Notifications made to above government agencies in accordance with Monticello Nuclear Plant water appropriations permit for fish kill in Mississippi river following Rx scram on 1-10-07." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2007-01-11
43094 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2007-01-11 07:10 | 2007-01-11 17:40 | 2007-01-11 | FITNESS FOR DUTY A licensed employee had a for cause fitness-for-duty test performed and was determined to be unfit for standing duty. The employee's access to the plant has been restricted pending review. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0 | 2007-01-11
43093 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2007-01-11 10:00 | 2007-01-11 16:59 | 2007-01-11 | FITNESS FOR DUTY A non-licensed contract employee supervisor had a confirmed positive result during the initial fitness-for-duty test. The employee's access to the plant has been denied. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.73 |  |  |  | 0 | 2007-01-11
43092 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2007-01-11 08:16 | 2007-01-11 13:16 | 2007-01-11 | REACTOR SCRAM WHEN TURBINE OUTPUT BREAKERS OPENED "Unit 2 reactor scrammed due to a main turbine trip. PCIS [Primary Containment Isolation Signal] groups 2, 3,and 6 isolated, CREV [Control Room Emergency Ventilation] A, SBGT [Standby Gas Treatment] trains A, B, and C started as expected. All control rods fully inserted, eight main steam relief valves lifted and no ECCS actuations occurred. This event is reportable within four hours according to 10CFR50.72(b)(2)(iv)(B) and eight hours according to 10CFR50.72(b)(3)(iv)(A)." The turbine trip was the result of the 500kV main output breaker opening causing the generator output breaker to open. All relief valves fully seated during the scram recovery. The reactor water level is being maintained using normal feedwater and decay heat is being removed using the steam dumps. The plant is using the startup transformer for electrical power. The cause of the 500kV breaker opening is under investigation. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-01-11
43091 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-12-01 | 2007-01-11 13:09 | 2007-01-11 | AGREEMENT STATE - OHIO - EQUIPMENT MALFUNCTION OF A COBALT TELETHERAPY DEVICE On January 2, 2007, Ohio Bureau of Radiation Protection received a written report that an equipment failure of a Cobalt Teletherapy Device had occurred on December 1st while treating a patient. The sealed source did not return to the closed positron after completing treatment. The therapists immediately entered the room and returned the source to a safe configuration. The department requested additional information from the licensee on January 2 and received the additional information on January 9, 2007. It has been determined that the licensee did not perform a 24 hour notification as required in rule 3701-40-20 of the Administrative Code. The patient was exposed to less that thirty seconds exposure time and a determination was made from the additional information provided that a medical event did not occur. The unit was repaired by Neutron Products on December 8, 2006. The problem identified was an old air cylinder and detent pin which was replaced returning the unit to normal operation. The Department notified the NRC Operations Center on January 11, 2007 after determination of reporting requirements. Teletherapy unit is a Theratron-80, s/n 2640986, which is manufactured by Neutron Products. The Co-60 sealed source is 1690 Ci or 62530 GBq, model number NPTY, s/n T-1444. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2007-01-16
43090 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2007-01-11 11:15 | 2007-01-11 12:13 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * FAILURE OF GAMMA SPECTROMETER WASTE MONITOR "A routine-6-month calibration was performed on the [DELETED] condensate discharge inline monitor system. The calibration identified that the gamma spectrometer. Monitoring system was not functional. The system failed all calibration efforts including a self-check. This piece of equipment is an active engineered IROFS [Item Relied On For Safety] for discharge of low-level condensate waste. The failure of this IROFS leaves only one other IROFS in place but fails to meet the minimum performance criteria. This equipment may have been in a failed state for more than eight hours. The remaining IROFS that remains intact is sampling the waste prior to discharge. "There were no actual safety consequences to the workers, the public, or the environment due to the low level of waste discharged through this system. "All waste discharges have been suspended until equipment functionality can be demonstrated. A complete review of recent discharges through this system is underway to ensure that all discharges have been according to approved discard limits. The receiving tanks are also being sampled to confirm that the uranium concentration is within approved limits. "All waste discharges from other plant facilities having similar monitoring equipment have been suspended until equipment functionality can be demonstrated." * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ONLY ONE SAFETY ITEM AVAILABLE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (a)(5) |  |  |  | 0 | 2008-05-11
43089 | 0 | RANCHO SECO | 1 |  |  | [1] B&W-L-LP | 2007-01-10 12:30 | 2007-01-11 11:05 | 2007-01-11 | UNAUTHORIZED PROTECTED AREA ENTRY Actual entry of an unauthorized person into the protected area around ISFSI. The licensee will notified the Regional Inspector. Contact the NRC Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2007-01-11
43088 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2007-01-10 15:28 | 2007-01-10 19:46 | 2007-01-10 | REACTOR SCRAM WITH STUCK OPEN MAIN TURBINE CONTROL VALVES "At 1528 hours Central Time, a RPS trip occurred, all rods fully inserted. Turbine valve testing was in progress. A group 1 isolation occurred with all MSIVs closing. A partial group 2 occurred due to low reactor water level. All safety systems (valves) operated correctly. Currently reactor pressure/cooldown in progress using HPCI in pressure control, normal condensate and feedwater in service for reactor water level control. Investigation of cause is in progress." Group isolations resulted from low pressure and low reactor water level. During the transient and subsequent cooldown, Operators manually opened the main steam relief valves to maintain pressure control in accordance with the plant EOPs. HPCI was manually started to maintain reactor level. The group 2 isolation has been reset. The group 1 isolation (MSIVs) will not be reset until after the main turbine control valves are shut. The plant is being cooled down to initiate RHR cooling and is in the normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-01-10
43087 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2007-01-09 | 2007-01-10 17:30 | 2007-01-10 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL EVENT - BRACHYTHERAPY The State provided the following information via facsimile: "Licensee has notified State Agency within 24 hours. "A Mick applicator malfunctioned during the planned treatment of a prostate patient. The patient was scheduled to receive I-125 seed implants totaling 11 millicuries at 0.25 millicuries per seed. A total of 8.25 millicuries were implanted when the malfunction occurred. This will most likely result in the total dose delivered differing from prescribed dose by 20 percent or more. The dose information was not currently available but will follow in NMED reporting. The seeds not implanted have all been accounted for and have been placed in storage. The licensee will provide a written report within 15 days. No further information is available at this time." SC Event Report: SC070001 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2007-01-16
43086 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2007-01-10 12:35 | 2007-01-10 16:36 | 2007-01-10 | LOSS OF OFFSITE LANDLINE COMMUNICATIONS CAPABILITY DUE TO CUT FIBER OPTIC CABLE "On 01/10/2007 at 1235 CST, the Unit 1 control room was notified that the offsite fiber cable from Palacios to Port Lavaca was cut at approximately 1155 hours by a building contractor just out of Palacios on Texas Highway 35. Verizon dispatched a crew to repair. Estimated time for repair is about 4 hours. "Offsite communications is lost from both Unit 1 and Unit 2 control rooms including the state and county ring down lines, the NRC ring down line and the ability to transfer information from the Emergency Response Data System (ERDS) to offsite agencies. Satellite phones remain available. "At 1258 CST, the NRC Operations Center was notified via satellite communications of alternate phone numbers to contact the Unit 1 and Unit 2 Control Rooms. This is a follow-up to make the notification of this event to the NRC pursuant to 10 CFR 50.72 (b)(3)(xiii). "The NRC Senior Resident Inspector was notified of this issue." * * * UPDATED AT 1830 EST ON 01/10/07 FROM CHRIS VAN FLEET TO S. SANDIN * * * All offsite lines have been restored as of 1716 CST on 01/10/07. The licensee informed the NRC Resident Inspector. Notified R4DO (Spitzberg). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-10
43085 | 0 | AIR PRODUCTS & CHEMICALS, INC. |  |  |  |  | 2006-12-15 | 2007-01-10 15:17 | 2007-01-10 | MISSING GENERAL LICENSE ELECTRON CAPTURE DETECTOR During an inventory for license transfer, a Delphi Instruments electron capture device, model #4402 S/N 2546, containing 50 mCi Tritium was discovered missing. The device was used to measure contamination in argon gas streams. The licensee received the device at their NY facility in April 2000. Since no wipe test is required the last use of this device is unknown. The licensee conducted two exhaustive searches with negative results. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2007-01-10
43084 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2007-01-09 | 2007-01-09 18:17 | 2007-01-09 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE DISCOVERED AFTER BADGE PROCESSING "The agency [Texas Department of State Health Services (DSHS)] returned a telephone call at 5 p.m. [on 01/09/07] to the licensee, in regards to a voicemail the licensee's RSO left on another program's telephone. The personnel answering the telephone at the facility stated the RSO had just left for the day & gave [the state] partial information that the facility had received the personnel monitoring report for 11/10/06-12/06/06 that showed a radiographer's dose to be 697,408 (mR) -Deep dose. The employee stated that the monitoring processing company was going to repeat the tests again to confirm the dose. The licensee was waiting to hear from DSHS/Radiation Control (RC) on 1/09/07, to decide what to do. They were not sure if they should do blood work, etc. "DSHS/RC advised the employee to 1) Have the RSO call DSHS/RC Incident Investigation (IIP) personnel first thing in the morning on 1/10/07; 2) Have the RSO perform an inquiry with the radiographer to assess the events during the monitoring period in question; 3) Have the RSO look at personnel monitoring records for co-workers on the same job(s) as the radiographer under review to compare their dosage during this time period; 4) Have RSO check utilization logs during this period to assess what specific equipment was used & the job details; 5) DSHS/RC requested a fax copy of the personnel monitoring report [Deleted]. The employee agreed to comply. DSHS/RC will follow-up first thing 1/10/07 with the licensee's RSO to obtain complete information. Additional clarification/corrective information may be submitted by DSHS/RC after interview with licensee's RSO. " Texas Incident number: I-8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2007-01-12
43083 | 0 | BROWNS FERRY | 1 | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-11-10 00:10 | 2007-01-08 15:47 | 2007-03-13 | EDG ACTUATION DUE TO ACCIDENTAL SWITCH MISPOSITIONING "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of any of the equipment specified in paragraph 50.73(a)(2)(iv)(B). In this case, the equipment actuated was the four Unit 1 and 2 emergency diesel generators (EDG) A, B, C, and D. These EDGs are common equipment for Browns Ferry Units 1 and 2. "On November 10, 2006, personnel were performing surveillance requirement (SR) test 0-SR-3.8.1.6, Common Accident Signal Logic. At this time Browns Ferry Unit 1 was shutdown and defueled, and Unit 2 was operating at 100% thermal power. During conduct of this testing, at 0010 hours CST, all four of the common U1/2 EDGs were inadvertently started. This occurred when test personnel (non-licensed) inadvertently placed a keylock switch in the wrong position during the equipment restoration portion of the testing. The SR test step being performed was correct, but it was incorrectly implemented. "All affected equipment operated per the plant design in response to the switch manipulation, with each of the four EDGs properly starting and running in response to the invalid start signal. No loss of normal plant electrical power occurred, and none of the EDGs connected to its associated 4-Kv shutdown board. The EDGs were shutdown in accordance with plant operating procedures approximately 13 minutes after their start. " Since no actual plant condition existed which required the EDGs to start, and since the starts occurred inadvertently as a result of a human error during a test performance, this event is classified as invalid. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for evaluation and resolution. [Reference BFN corrective action document PER 114498]. "The NRC Senior Resident Inspector has been notified." * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC INTERNAL WEBSITE* * * | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-01-08
43082 | 0 | HACKLEY HOSPITAL |  |  |  |  | 2007-01-08 10:30 | 2007-01-08 15:26 | 2007-01-08 | MEDICAL EVENT UNDER DOSE TO INTENDED ORGAN DUE TO IMPROPER SEED IMPLANT During a seed implant procedure for treating prostate cancer with I-125 (41 seeds with 0.32 millicuries each), the patient moved after inserting 2 of the 14 treatment needles. The procedure was delayed for five minutes to allow the patient to be more completely under general anesthesia. The lineup was checked using ultrasound and once the urologist, the radiation oncologist, and the medical physicist were comfortable with the situation, the seed implant was resumed. Once the procedure was completed, the hospital personnel took a film shot to verify the needle placement. It was discovered that the 12 of 14 remaining needles that were inserted were not in the intended location. The patient has been notified of the error. The hospital is in the process of determining the prostate underdose and the overdose to the unintended areas (rectal and urethra). The hospital is still evaluating any patient intervention that needs to be identified and if there is any unintended permanent functional damage to other organs. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | DOSE TO OTHER SITE > SPECIFIED LIMITS | [8 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) | 35.3045(a)(3) |  |  | 0 | 2007-01-14
43081 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2007-01-06 10:00 | 2007-01-06 10:00 | 2007-01-10 | LOSS OF SPDS PARAMETER DISPLAY DUE TO PLANNED MODIFICATION "At 0904 hours EST, on January 6, 2007, the Emergency Response Facility Information System (ERFIS) computer system was removed from service to perform a planned modification of the ERFIS power supply system. The expected duration of ERFIS inoperability is approximately 2 hours. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, and the Inadequate Core Cooling Monitor (ICCM). The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above-described functions. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still be made, if required, during the time that the ERFIS Computer system is inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remained available to assess plant conditions, make notifications, and accomplish required communications, as necessary. An additional message will be provided when the ERFIS is restored." The licensee will notify the NRC Resident Inspector. * * * UPDATE PROVIDED BY HENRY CURRY TO JEFF ROTTON AT 1158 EST ON 01/06/07 * * * ERFIS computer has been returned to operable status at 1146 EST. Licensee notified NRC Resident Inspector. Notified R2DO(Payne) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-06
43080 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-11-08 12:00 | 2007-01-05 17:34 | 2007-01-05 | DEFECT IDENTIFIED IN CRANE BRAKE CALIPER MOUNTING PIN United States Enrichment Corporation (USEC) identified a defect in a Continental Brake Model No. 95400 crane hoist drum hydraulic brake caliper mounting pin (part no. 3954022). The firm that supplied the item was Continental Brake Equipment Company, Longboat Key, Florida. The item is a commercial grade item, dedicated for use as a Basic Component upon receipt inspection. The defect involved errors in the machining of a groove which accepts a retaining ring to hold the caliper mounting pin in place. Specifically, the grooves were machined too shallow and too narrow to properly accept and hold the retaining ring. The result is that during use the retaining ring may dislodge from the pin, allowing the pin to loosen. This happened in the certificate holder's C-315 facility during use. A loose mounting pin can result in the brakes not performing its function as a hoist brake to prevent the uncontrolled lowering of a UF6 cylinder. Per the faxed USEC report: "Failure of the crane hoist resulting in the drop of a cylinder containing liquid UF6 is identified in the PGDP accident analysis as resulting in off-site uranium exposures exceeding the guidelines established for determining a substantial safety hazard." USEC has inspected all subject mounting pins in service and on-hand. All defective mounting pins were removed from service or shelves. USEC has not communicated with other specific purchasers or licensees but they recommend that users of cranes with similar brakes inspect the subject caliper pins for engagement. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 21.21 |  |  |  | 0 | 2007-01-05
43079 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2006-12-21 14:00 | 2007-01-05 15:45 | 2007-01-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS On December 21, 2006 at approximately 2 pm local time the Maine Radiation Control Program received notification from a licensee, the City of Presque Isle, that they had lost 5 tritium exit signs during building renovations. Sometime between August 2006 and December 2006 at the time of the report to the state the licensee noted that 6 tritium exit signs had been disposed of as part of renovations to Building 1309. The signs were manufactured by Safety Light Corporation, Model 2040-50-20. The serial numbers are 0941221, 0941229, 0941223, 0941227, 0941225, and 0941228. While the exact location of the signs is not known they were probably disposed of in the trash. The state estimated the activity per sign to be about 5 Curies. The state is following up on this report. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2007-01-10
43078 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2007-01-04 12:00 | 2007-01-05 13:12 | 2007-03-13 | AGREEMENT STATE REPPORT - MEDICAL DOSE TO WRONG LOCATION "On January 4, St. James' Hospital and Health Center's medical physicist called to report that medical event had occurred involving a patient at their Cancer Center Institute. [The medical physicist] advised that a series of high dose rate (HDR) afterloading fractions using 10 Ci of Ir-192 that had been conducted on 11/29, 12/6, 12/13 and 12/20 had inadvertently caused the irradiation, not of the cancerous target intended but instead, a portion of the patient's inner thighs. The delivered radiation dose to the skin was 2,000 Rad and the dose to the intended treatment area was zero. "[The medical physicist] indicated that the error had been identified as part of a 'chart audit' that was conducted prior to performing the next similar routine treatment of a subsequent patient. Computerized dosimetry planning records showed that although the prescribed treatment was to occur with an automated source travel distance of 120 cm, the actual data point used during the treatment phase was a travel distance of only 100 cm. The patient was asked to come to the hospital on the afternoon of January 4 for a consultation. During that visit the responsible authorized radiation oncologist confirmed reddening of the skin on both inners thighs of approximately 3 square centimeters. [The oncologist] indicated that the skin damage is a 'superficial ulceration with no necrosis of the tissue' and he expected healing to be completed in 2-4 weeks. [The oncologist] has made arrangements to meet with the patient weekly to monitor her progress during that time. HDR afterloader treatments have been rescheduled to occur next week." The state also said that it appears that correct dose was administered to the wrong location because of a human error not an equipment malfunction. Other pertinent data related to this event: Type of procedure: BRACHYTHERAPY, Intended Dose: 2000 RAD, Form of Radioactive Material: SEALED SOURCE, Radionuclide: IR-192, Activity: 10 Ci. Equipment Information: Manufacturer: ALPH-OMEGA SERVICES VARIAN, Model Number: VS2000, Serial Number: 02011368001112006101. The Illinois Emergency Management Agency will be following up on this incident. This report is IL report number 070001. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC PUBLIC WEBSITE* * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2007-01-08
43077 | 0 | 3M CORPORATION ST PAUL |  |  |  |  | 2007-01-05 08:00 | 2007-01-05 10:14 | 2007-01-05 | MISSING TRITIUM SIGN 3M Corporation Office located in Saint Paul, Minnesota, was notified this morning from their office located in Brookings, South Dakota, that during a semi annual sealed source inventory it was discovered that a tritium sign containing 20 curies of tritium, as of May 1998, was found to be missing. The on-site Radiation Safety Officer is starting a plant investigation process to determine to try and find the missing tritium sign. The sign was accounted for during their previous semi annual sealed source inventory in July 2006. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | SD | OTH | GEN |  |  |  |  | 0 | 2007-01-05
43076 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2007-01-04 17:43 | 2007-01-04 23:46 | 2007-01-05 | HIGH RANGE EFFLUENT RADIATION MONITORS DECLARED INOPERABLE DUE TO COMMON CAUSE FAILURE "At 17:43 CST Cooper Nuclear Station declared the three High Range Kaman Effluent radiation monitors inoperable due to a common cause failure mechanism. The affected Kamans monitor the Elevated Release Point exhaust, the Turbine Building ventilation exhaust and the Radwaste/ Augmented Radwaste Building ventilation exhaust during accident conditions. The identified common failure mechanism results in the installed, movable calibration sources spuriously inserting into the monitors, causing them to indicted abnormally high. "This condition is being reported under 50.72 as a loss of Emergency Preparedness Capabilities due to the potentially inaccurate indications of the High Range Building Exhaust radiation monitors and the Elevated Release Point Effluent radiation monitor." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2007-01-05
43075 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 1993-12-31 | 2007-01-04 15:27 | 2007-01-04 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State provided the following information via email: "This Agency [Nebraska Health and Human Services] contacted the general licensee in November 2006 concerning their three NRD Inc. self luminous exit signs (Model T-4001, with 19.8 Curies of H-3 when shipped, Serial Numbers 24921, 24922 and 24923) which where shipped to the licensee in early 1986. The licensee discovered that in 1993 the store moved to a new location within the shopping mall. The signs were left in the original store location. This location went through a major renovation in 1993 at which time a demolition company gutted the entire store. The debris was disposed of by the demolition company. The mall's manager and the new store's representative do not know the name of the demolition company and do not know the current location of the three exit signs." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2007-01-09
43074 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2006-12-27 12:00 | 2007-01-04 11:33 | 2007-01-04 | WISCONSIN AGREEMENT STATE REPORT "Event Location: University of Wisconsin Hospital, 600 Highland Avenue, Madison, Wisconsin 53792 "The event occurred on Wednesday, December 27, 2006. A patient was to receive 4 high dose-rate brachytherapy fractions of 5 Gy each over a 7 cm length of the vaginal mucosa using a vaginal cylinder. "About halfway through the first treatment fraction, the actual dose delivered to part of the target organ, over the inferior 3 cm of the treatment length, exceeded the prescribed dose by more than 50%, (range 1.5 - 2.37 times the prescribed dose). "The biological dose to the patient from this event was under the prescribed dose. The subsequent 3 fractions will be modified to deliver the intended biological dose to the patient, and no adverse health effects are expected to the patient. "Notification, by the licensee, of this event to the Department of Health and Family Services (DHFS) occurred on Thursday, December 28, 2006. DHFS will dispatch a team on Monday, January 8, 2007 to investigate this event." Event Report ID No: WI-07-01 A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2007-01-10
43073 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2006-12-28 07:30 | 2007-01-04 10:47 | 2007-01-04 | AGREEMENT STATE REPORT - FAILURE OF SOURCE TO RETRACT INTO AFTERLOADER UNIT The State provided the following information via facsimile: "Prior to a scheduled patient treatment, the RSO at Methodist Medical Center was performing QA testing on the Nucletron-Oldelft Corp. Model microSelection-HDR remote afterloading device. The device utilizes a sealed source containing 10 curies of Iridium-192 to be used for treatment of cancer in humans. The sealed source would not retract when the RSO tried the emergency retraction button at the control console. Following the emergency procedures, the RSO manually retracted the sealed source into the HDR afterloader unit. The RSO estimated it took three seconds to return the sealed source to its shielded position. Nucletron Corp. was immediately notified of the malfunction by the RSO. Nucletron Corp. called DRH to request reciprocal recognition of its Maryland license and an authorized service person arrived at the licensee's facility on 12/28/06. The circuit board was found to be faulty and was repaired. After repair, the required safety functions of the system were tested and found to be functioning as designed. The licensee will complete a written report and submit to the State." Tennessee report number: TN-06-158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2007-01-09
43072 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2007-01-03 18:03 | 2007-01-03 19:32 | 2007-01-03 | AUTOMATIC REACTOR TRIP DUE TO A CARD FAILURE "A Unit-1 reactor trip was initiated by a Process Rock card failure that caused the 'B' main feed regulation valve to fail closed. The closure of the 'B' main feed regulation valve caused a reactor trip due to a steam flow - feed flow mismatch with a low steam generator water level. The auxiliary feed water system actuated as expected due to the reactor trip. The plant was stabilized with no other issues using the appropriate emergency procedures." All control rods fully inserted on the trip and no relief or safety valves lifted in either the primary or secondary systems. Auxiliary feed water pumps automatically started and injected into the steam generators on a low water level signal. The operators restored normal feedwater flow to the steam generators. Decay heat is via the condenser steam dumps. The plant is aligned to the normal shut down electrical alignment. Card replacement is expected tonight and reactor startup is expected tomorrow. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2007-01-03
43071 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2006-12-28 12:00 | 2007-01-03 10:14 | 2007-01-03 | POTENTIAL DEGRADATION OF HYDRAULIC SNUBBER FLUID "FPL Energy Duane Arnold makes the following notification under 10 CFR 21.21(d)(3)(i) of a defect found during snubber rebuild activities. The specific defect is foreign materials identified in the GE SF 1154 snubber fluid, which was supplied by Shaw A/DE, Inc (now known as Fronek Anchor Darling Enterprises, Inc.) as a basic component in 2003. The fluid has been identified as a part of GE batch number AD965 and was manufactured June 2001. "The foreign material had the appearance and texture of paraffin wax. FPL Energy has postulated that the foreign material could restrict fluid flow through the orifice in the snubber and cause the snubber to remain locked following activation. The resulting locked snubber would prevent the function of allowing for some piping movement associated with normal system movement. "The fluid has been removed from use at the Duane Arnold Energy Center (DAEC) and a portion was sent for analysis. The analysis indicates that the solid contaminate is silicone. Silicone based oils are generally very stable and the analysis does not indicate how, or why, they came out of solution. FPL Energy engineering personnel inquired about the analysis findings to ascertain the likely causes for the silicone separation from solution. The conclusion is that it could have been a bad batch, a contaminant could have been introduced during processing or repackaging or it could have resulted from some form of reaction with the plastic container. "The supplier, Fronek Anchor Darling Enterprises, Inc, was contacted on 12/22/06 to discuss FPL Energy Duane Arnold's findings. "FPL Energy has verified that none of the suspect batch has been installed in snubbers installed at the DAEC. All the suspect fluid has been accounted for." It is unknown if any fluid from this same lot was distributed to any other power reactor sites. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 21.21 |  |  |  | 0 | 2007-01-03
43070 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-11-01 18:23 | 2007-01-02 13:19 | 2007-01-02 | LOSS OF UNIT-2 AUX TRANSFORMER CAUSED UNIT-1 SYSTEM ISOLATIONS AND ACTUATIONS "This report is being made in accordance with 50.73 (a)(1), which states, in part, 'In the case of an invalid actuation reported under 50.73 (a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' These invalid actuations are being reported under 50.73 (a)(2)(iv)(A), NUREG-1022, Rev. 2, states that the report should provide the following information: The specific train(s) and system(s) that were actuated Whether each train actuation was complete or partial Whether or not the system started and functioned successfully. "On November 1, 2006, with Unit 1 operating at 100% of rated thermal power, the loss of the Unit 2 Startup Auxiliary Transformer resulted in loss of power to the isolation logic associated with the common main stack radiation monitor resulting in actuations normally associated with a high radiation signal. This invalid signal resulted in actuation of the Unit 1 Primary Containment Isolation System (PCIS) Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems) valves, a Unit 1 Reactor Building Ventilation System isolation (i.e., Secondary Containment isolation) and the automatic start of both Unit 1 Standby Gas Treatment (SGT) System trains A and B. The actuations of PCIS Group 6 valves and Reactor Building Ventilation System isolation were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open, at the time of the event, closed). Additionally, SGT System trains A and B started and functioned successfully. "Discussion of the causes and corrective actions associated with this event are documented in the corrective action program in Nuclear Condition Report (i.e., NCR) 211237. The resident inspector will be notified." The System Engineer (Leo Kauffel) verified that the Unit 2 actuations resulting from this event were previously submitted in LER 2-2006-001 and are not stated in this event report. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2007-01-02
43069 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2007-01-01 20:30 | 2007-01-02 10:37 | 2007-01-10 | AGREEMENT STATE REPORT - FLORIDA - STOLEN MOISTURE DENSITY GAUGE. A truck belonging to the licensee flipped over on a highway in Polk County, FL on January 1, 2007, at approximately 8 or 9 pm. The truck was carrying a Humboldt Model 5001EZ moisture density gauge (nominal 50 millicuries Am-241/Be and 10 millicuries Cs-137). The driver was unhurt and walked to a local business to report the accident leaving the gauge unattended. The gauge was stolen while the driver was gone. Police were notified and a report filed. The gauge was locked inside of the locked case and chained to the vehicle. FL report #FL07-001 * * * UPDATE FROM STATE OF FLORIDA (FURNACE) TO HUFFMAN AT 0726 EST ON 1/10/07 * * * The State reports that a gauge meeting the description of the missing gauge was found by a Polk County representative on the side of a road. The gauge was not in its case but was intact and did not appear to be damaged. The gauge is being stored by the County (which is licensed to possess and use moisture density gauges) in an authorized safe and secure storage location and will be transferred to the licensee today. The licensee plans to send the gauge to a vendor to have it checked-out, leak tested, and certified for use before returning it to service. R1DO (Bellamy) and NMSS (Morell) have been notified. ILTAB notified by e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2007-01-05
43068 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-12-28 18:30 | 2006-12-29 16:13 | 2013-01-30 | AGREEMENT STATE REPORT - THEFT OF A TROXLER MOISTURE DENSITY GAUGE "On December 29, 2006, at 11:10 am, the licensee contacted the California [Radiologic Health Branch] RHB to report the theft of a Troxler, Model 3430 moisture/density gauge (S/N 38217) containing a nominal 10 millicuries Cs-137 and nominal 40 millicuries Am-241. When the licensee initially reported, they had been informed by their technician that the gauge (secured by two locking cables in the truck bed) had been stolen at 11:00 am on December 29, 2006, while the technician was having lunch at a restaurant in Fontana, CA. Subsequently, during the police investigation, the technician acknowledged that the gauge had actually been stolen out of his truck, sometime the night previously (i.e., between about 6:30 pm December 28, 2006 and 8:00 am December 29, 2006), while the truck was parked in front of his home in San Jacinto, CA. "The licensee prohibits their technicians from taking the gauges home overnight, and intends to take disciplinary action against the technician in this regard. The San Jacinto police have also been contacted, and the licensee intends to place a reward notification in the local press in the San Jacinto area. RHB will continue to follow up on this matter." * * * UPDATE FROM DONELLE KRAJEWSKI TO CHARLES TEAL ON 1/30/13 AT 1351 EST * * * The following was received via email from the State of California via email: "On Monday, January 28, 2013, the Border Patrol notified us, the Texas Department of State Health Services (DSHS), that a trailer had caused the radiation monitor to alarm at its checkpoint in Sierra Blanca, TX (approximately 90 miles east of El Paso on I-10). "The individual pulling the trailer stated he was moving to Texas from California. The source of radiation was identified as being a Troxler moisture/density gauge. [The individual] stated that he had purchased the gauge as a tool for finding underground pipe at a swap-meet in Beaumont, CA, back in late August/early September of 2012 (he paid $125 or $150 for it). He stated he had not used the gauge he had only opened the case and looked at it and then put it in his storage shed where it remained until he packed up to move. The gauge was detained by one of our Agency [DSHS] inspectors and [the individual] willingly surrendered it. "Gauge information: "Troxler Model 3430 "SN: 38217 "It, and the case, are in very good condition. Based on isotope identification by Border Patrol and the DSHS inspector, it appears that the cesium-137 and the americium-241/beryllium sources are still in the gauge." Notified R4DO (Walker), Mexico, and FSME Event Resource via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2007-01-03
43067 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2006-12-28 02:30 | 2006-12-28 11:43 | 2006-12-28 | FAILURE OF RADIOGRAPHY CAMERA SOURCE TO FULLY RETRACT On December 28, 2006, at about 2:30 am local time, while performing a radiography at the pumping facility in Kuparuk, Alaska, the radiography camera source failed to fully retract into the shielded position. The radiographer contacted the Radiation Safety Officer who guided the radiographer in unscrewing the drive cables so that the source was able to be fully retracted. No over-exposures or unplanned exposures occurred. The camera is a INC Model IR-100. The original source strength of the radiography camera Ir-192 source was 100 curies. Kakivik Asset Management plans to contact the manufacturer of the camera about this occurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-12-28
43066 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-12-27 12:37 | 2006-12-27 13:16 | 2006-12-27 | DECLARED UNUSUAL EVENT DUE TO UNIDENTIFIED REACTOR COOLANT LEAKAGE GREATER THAN TECH SPEC LIMIT "Reactor Coolant level and pressure are stable in capacity of normal charging. Reactor Coolant leakage rapidly increased. Large input to Reactor Coolant Drain Tank. Leak diagnostic in progress. Secured 1B NCP [ Reactor Coolant Pump] due to low standpipe level. Leak data to be provided on follow up notification." The NRC Resident Inspector, State, and local Officials were notified of this event by the licensee. * * * UPDATE FROM RUSSELL EDMOND TO JOE O'HARA AT 1417 ON 12/27/06 * * * Reactor coolant leak appears to be isolated. Operators entered containment and found the reactor coolant system "C" loop low point drain valve partially open. The operators closed the valve and isolated the reactor coolant leak. The licensee is in EAL 4.2.U.4. The licensee notified the NRC Resident Inspector. R2DO (Landis), NRR EO (MJ Ross-Lee), and IRD Manager (J. Cruz) * * * UPDATE FROM LARRY SAUNDERS TO JOE O'HARA AT 1613 ON 12/27/06 * * * The licensee reports they have exited the unusual event at 1600 on 12/27/06 due to the leak being terminated. The licensee notified the NRC Resident Inspector. R2DO (Landis), NRR EO (MJ Ross-Lee), IRD Manager (J. Cruz), FEMA(Eaches), and DHS(J. Craig) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-12-27
43065 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-12-23 | 2006-12-27 02:34 | 2006-12-27 | AGREEMENT STATE REPORT - STOLEN AND FOUND TROXLER GAUGE The State provided the following information via email: On Sunday Dec 24 the State of Colorado received notification from the licensee of a missing Troxler Model 3430 portable moisture density gauge SN 21961 (Activity: 8 millicuries Cs-137/ 40 millicuries Am-241/Be). The gauge was being used at a job site at Denver International Airport (DIA). The gauge is presumed to have been stolen from the truck outside the field technician's residence in Douglas County and not at DIA. However, this has not been verified. The time of theft was not determined but is most likely between 8:00 p.m. Fri Dec 22 and 10:00 a.m. Sat Dec 23. The theft was discovered on Saturday Dec 23. The gauge had been properly chained in the back of a pickup truck and both chains had been cut. The gauge was subsequently discovered intact in an alley in Parker, CO on 12/26/06. The address where the gauge was recovered has not yet been reported by local police. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2006-12-29
43064 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2006-12-26 10:30 | 2006-12-26 16:16 | 2006-12-26 | EMERGENCY SIRENS FAIL TO OPERATE FROM COUNTY FACILITIES "EP [Emergency Planning] Personnel were coordinating routine silent testing of the Wayne County Alert Notification System (ANS) per EPIP 4-10. At approximately 0930, Wayne County personnel activated the system from the Wayne County 911 Center activation point. The test was unsuccessful. In accordance with procedure, Wayne County personnel attempted to activate the system from the Wayne County EOC. This test was also unsuccessful. Per procedure guidance, if the alternate activation point is unsuccessful, Ginna EP personnel are to be notified to perform the test from the Ginna TSC. Ginna EP performed the silent test of the system from the Ginna TSC per procedure EPIP 4-8. The test was successful. "Site personnel were notified and the Verizon Phone Company was contacted by Engineering to investigate. Phone line connections from Wayne County to the Brantling Hill transmitter site were functionally tested satisfactorily by Verizon Phone Company. Verizon personnel & Ginna Maintenance personnel were dispatched to the transmitter site to perform troubleshooting. "Although the 70 Wayne County ANS sirens could not be tested from either Wayne County test location, the notification system was functional and continuously capable of being activated from the Ginna TSC is in accordance with the E-Plan. "Silent siren alarm tests for the 26 Monroe County ANS sirens were initiated from both Monroe County activation points (911 Center and Radio Center). All tests initiated from the Monroe County activation points were successful. "Sirens restored to operable at 1552 12/26/06 following communications card repair and testing." The licensee notified the NRC Resident Inspector, State, and local government agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-12-26
43063 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2006-12-24 | 2006-12-26 13:48 | 2006-12-26 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "Portable moisture density gauge was stolen along with vehicle (Jeep Cherokee) on night of December 23 or 24 in Las Vegas, Nevada. Gauge loss may have been incidental to theft of vehicle, however company policy was to return gauge to office. "Troxler model 3411 portable moisture density gauge, s/n 12367" Sources: 40 milliCuries Am-241:Be and 8 milliCuries Cs-137 A police report has been filed with the Las Vegas Metro Police Department. Nevada Event Report: NV-06-008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2006-12-29
43062 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-12-25 05:39 | 2006-12-25 09:27 | 2006-12-25 | REACTOR SCRAM DUE TO TRIP FROM NEUTRON MONITORING SYSTEM "On 12/25/06 at approximately 05:39 an automatic reactor scram occurred on Brunswick Unit 2. The Reactor Protection System (RPS) actuated on Neutron Monitoring System (APRM/OPRM) trip for APRM 2 and 4. All control rods properly inserted when the scram occurred from the RPS signal. Reactor water level reached low level 1 (LL1) and low level 2 (LL2) as a result of the scram. The LL1 signal causes a Group 2 (floor and equipment drain isolation valves), Group 6 (monitoring and sampling isolation valves) and Group 8 (shutdown cooling isolation valves) isolation signal. The LL1 isolations occurred as designed. The LL2 [signal] causes a Reactor Core Isolation Cooling (RCIC) system actuation, High Pressure Coolant Injection (HPCI) system actuation, Group 3 (reactor water cleanup valves) isolation signal, a secondary containment isolation signal, a Standby Gas Treatment (SBGT) initiation signal, a Control Room Emergency Ventilation (CREV) initiation signal, Reactor Recirculation Pump trip and an Alternate Rod Insertion (ARI) actuation signal. The low level 2 condition was reached momentarily and did not affect all instruments due to calibration differences. Initial assessment concludes that the appropriate LL2 isolations and actuations occurred as designed. Further evaluation of LL2 isolation and actuations will be conducted. The RCIC system actuation resulted in injection into the reactor as designed. The HPCI system actuated but did not inject because reactor water level was recovered. The plant is in a stable condition. An investigation is in progress to determine the cause of the Neutron Monitoring System trip." RCIC started momentarily and then was secured. Reactor water level being maintained via normal feedwater system. Decay heat being removed through the bypass valves. Normal electrical lineup for shutdown. EDGs available. Unit 1 not affected by this transient. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 64 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2006-12-25
43061 | 0 | NATIONAL INSTITUTE OF HEALTH |  |  |  |  | 2006-12-01 | 2006-12-22 13:32 | 2006-12-22 | LOST VIAL CONTAINING PHOSPHORUS-32 "This is a report of the loss of licensed material in accordance with 10CFR20.2201. "1. The licensed material consisted of a single packaged vial of Alpha-Adenosine Triphosphate (a-ATP) which contained 250 microcuries (9.25 MBq) of Phosphorus-32 (Half-life=14.3 days). The product is supplied by GE Healthcare, product number PT10160. The volume of the product was 25 microliters. "2. On December 1, 2006 a box containing three separate shielded vials of the product described in (1) above was delivered to a technician in the Clinical Research Center, 5th floor, Room 3288. Some time later, the Authorized User [AU] unpacked the box, but only retrieved two of the three product packages from the dry ice within the Styrofoam chest, because the third package was below the remaining dry ice. The AU then defaced the radioactive materials labels on the delivery box and placed the box containing the remaining vial for pickup as regular trash. The AU did not discover the error until December 4, 2006, too late to attempt retrieval from the regular trash dumpster. "3. The disposition of the material is to the regular trash stream through the Montgomery Country, MD refuse transfer station in Rockville, MD. "4. We have no reason to believe that this loss of licensed material resulted in exposure to anyone. The P-32 labeled ATP is in a very small volume of liquid, shielded by a sturdy Lucite plastic vial shield, encased in a sealed vinyl plastic outer containment. Furthermore, that assembly was in a thick-walled Styrofoam box within the cardboard delivery box. It is highly unlikely that, during the process of transport to, and through the transfer station that the P-32 would have leaked out of containment. "5. No action was taken to recover the material due the circumstances of loss and the time between loss and discovery of the loss. "6. No procedures have been modified as a result of this incident. The package insert clearly delineated to the AU that there were 750 microcuries of Alpha-ATP-32 in the shipment, in accordance with what the AU ordered, indicating that three items should have been retrieved from the dry ice. The loss was the result of human error." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-12-22
43060 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-12-21 14:00 | 2006-12-21 14:46 | 2006-12-21 | INADVERTENT ACTUATION OF EMERGENCY SIRENS "A Press Release will be issued for an inadvertent actuation of the Emergency Sirens during testing. This item is reportable under 10CFR50.72(b)(2)(xi) as an offsite notification of an event of public interest." Following maintenance on a single siren, Columbia County emergency management personnel were requested to test it. The County inadvertently activated all 112 sirens within 10 miles of the plant. The licensee notified the NRC Resident Inspector and the State. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-12-21
43059 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2006-12-21 02:05 | 2006-12-21 09:24 | 2006-12-21 | ACCIDENT MITIGATION - AUXILIARY FEEDWATER SYSTEM "A condition was identified [at 0205 on 12/21/06] involving improper placement of temporary scaffolding that could have resulted in all three Auxiliary Feedwater (AFW) pumps becoming inoperable during a high energy line break (HELB) in the Turbine-Driven Auxiliary Feedwater (TDAFW) pump room. "Scaffolding, erected to perform maintenance on the floor above the TDAFW pump room, had two vertical members placed on the high energy line break blowout panel in the TDAFW pump room roof that could potentially have restricted the ability of the panel to lift during a HELB event in the TDAFW pump room. Failure of the panel to lift during the event may cause the structural limit of the walls separating the TDAFW pump room from the motor driven AFW pump room to be exceeded. This could have resulted in all three AFW pumps becoming inoperable. "At 0530 on 12/21/06, scaffolding removal was complete and AFW operability was restored. "This condition is being conservatively reported, pending further evaluation, per 10CFR50.72(b)(3)(v) as a condition that at the time of discovery could have prevented the fulfillment of a safety function." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-12-21
43058 | -1 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2006-12-20 10:50 | 2006-12-20 11:50 | 2006-12-21 | DISCOVERED VITAL AREA VULNERABILITY Discovered vulnerability in vital area that could allow access to a controlled area. Compensatory measures taken upon discovery. The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM B. PUMPHREY TO HUFFMAN AT 1350 EST ON 12/21/06 * * * Licensee is retracting this event because it did not meet criteria for a one hour notification. This report is only required to be logged. The NRC Resident Inspector will be notified. R1DO(Powell) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MD | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-12-20
43057 | 0 | COOPER HEALTH SYSTEM |  |  |  |  | 2006-11-09 11:00 | 2006-12-19 14:41 | 2006-12-20 | DISCOVERED THAT A PATIENT RECEIVED AN UNDERDOSAGE "During a routine NRC inspection on 12/18/06 Sandra Gabriel Ph.D, Senior Health Physicist from Region I, discovered a medical event that occurred on 11/9/06 involving a HDR (35.600) treatment. "On 11/9/06 an HDR treatment patient received a dose of 1.37 Gy to Point A when the prescribed intended dose was 6.0 Gy. "The following scenario lead to the medical event. "A 6.0 cm tandem was inserted into the patient, however, the Authorized User asked the Authorized Medical Physicist to treat only a length of 4.0 cm to spare excess dose to normal structures. After the patient was treated, the Authorized Medical Physicist told the Authorized User he miscalculated the appropriate treatment length and what he thought was 2.0 cm from the end of the tandem was actually 20 cm from the tip of the tandem. The Authorized User and Authorized Medical Physicist calculated where 20 cm was, and this point was in fact outside of the patient's body, thus the patient only received dose from the ring portion of the applicator, resulting in a dose of 1.37 Gy to point A of the prescription plan. "Since this dose was subtherapeutic, the Authorized User added an extra HDR treatment (during the course of treatments) and the patient received a total dose to point A of 31.37 Gy which was within 20% of the original intended total dose. The patient was made aware of the extra treatment that was necessary because of the under dosage on 11/9/06. "A full written report will follow within 15 days as required by 10 CFR 35.3045." * * UPDATE FROM FLANNERY (FSME) TO KOZAL AT 1213 ON 12/20/06 * * * This event has been reviewed by the NRC medical review committee and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-12-20
43056 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2006-12-18 20:15 | 2006-12-18 21:10 | 2006-12-19 | DISCOVERED VULNERABILITY IN VITAL AREA ACCESS Discovered vulnerability in vital area that could allow access to controlled access area. Compensatory measures taken upon discovery. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION PROVIDED BY G. DORMAN TO J. KOZAL ON 12/19/06 AT 1301 * * * The licensee determined upon review of the event this event was not reportable and should have been entered into the stations safeguards event log pursuant to 10 CFR 73 Appendix G (2)(a). Contact the Headquarters Operations Officer for additional details. Notified R1DO (Powell), ILTAB (Whitney via-email), and 73.71 Group (via e-mail). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-12-18
43055 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-12-18 11:00 | 2006-12-18 13:55 | 2006-12-18 | INADVERTENT ACTUATION OF OFF-SITE EMERGENCY SIRENS "A press release issued for an inadvertent actuation of the emergency sirens. This item is reportable under 50.72(b)(2)(xi) as offsite notification as an event of public interest." The licensee was performing scheduled silent testing of the off-site emergency sirens. During the test a signal for the sirens to sound was sent in error, and the sirens sounded. There was no emergency. Licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-12-18
43054 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2006-12-16 00:50 | 2006-12-16 04:40 | 2006-12-16 | SAFEGUARDS SYSTEM DEGRADATION DUE TO HUMAN ERROR Safeguards system degradation related to monitoring and detection of PA boundary. Compensatory actions taken upon discovery. Call the Headquarters Operations Officer for details. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-12-16
43053 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2006-12-15 17:15 | 2006-12-15 17:47 | 2006-12-15 | PRESS RELEASE FOR LOW LEVELS OF CESIUM-137 CONTAMINATION IDENTIFIED ON SITE "A press release was issued for heightened awareness concerning low levels of Cs-137 found on AmerGen property. Samples indicate slightly elevated levels of Cs-137 that are below any reporting criteria." The licensee will notify the New Jersey Department of Environmental Protection. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-12-15
43052 | 0 | SCIENTECH, LLC |  |  |  |  | 2006-12-14 14:47 | 2006-12-14 14:47 | 2007-01-02 | PART 21 - DEFECT FOUND IN BASIC COMPONENTS (FOXBORO REPLACEMENT MODULES) SUPPLIED TO NUCLEAR POWER PLANT Scientech LLC company manufactures a replacement for obsolete Foxboro 66 R Lead/Lag unit - a TMD500, the time domain module in NUSI's Series 500 line. The Fully model number is of the form TMD500-xx/xx/xx/xx-xx-xx-yy, where xx defines certain input, output, and power options, while 'yy' selects the style of faceplate. Two shipments were made to Ginna, one of five modules and one of nine modules, were made in mid-September of 2006. Ginna performed receipt inspection and tested the modules for proper operation. The tests confirmed that NUSI had configured the modules as required and the modules worked as expected. Ginna Station installed the NUSI TMD500 modules in the reactor protection channels as part of a modification required for an extended power uprate. After further testing twelve modules in total were installed; 4 modules configured for OPDT setpoint calculator, and 8 modules configured as lag units. Two lag modules units were installed in each of the four reactor protection channels on the output side of the Thot R/I modules, to dampen the effects of hot leg streaming. All of these modules were bought under one purchase order and received in September 2006. On 11/2/06, several days after installation and calibration activities were completed, computer monitoring of the OPDT setpoints indicated that Channel 1 OPDT setpoint calculator module was following Tavg as it increased from 550 degrees F. The magnitude was small - approximately 0.3 degrees F change for a 10 degree F change in Tavg. However, the output of the module should have been steady until Tavg reached 574 degrees F. Ginna Station Operations declared reactor protection channel 1 OPDT setpoint inoperable when this condition was identified. The module was replaced, the replacement calibrated, and the channel was declared operable. On 11/6/06, several days later, computer monitoring of the channel 2 OPDT setpoint calculator showed it was exhibiting the same anomalous behavior that has occurred previously on the channel 1 OPDT setpoint calculator. Operations declared channel 2 OPDT setpoint inoperable. Ginna requested a team from NUSI travel to site and address the problem. A team of one engineer, one assembler, and the QA Manager traveled to Ginna to inspect and hopefully correct the problem. Troubleshooting by Ginna Station I&C personnel determined that the zero potentiometer wiper was shorted to the module case. The edge of the mounting fixture for the Lo Lim potentiometer had cut through the insulation of the wire going to the wiper of the Zero potentiometer. The NUSI team arrived on site while Ginna personnel were making repairs, and provided advice. The team inspected the module originally found defective and removed from service; they found that the wire to the wiper of the Zero potentiometer was damaged. They reinsulated the wire with electrical tape in accordance with approved Ginna procedures and tested the module, confirming that it worked correctly. The NUSI team then returned to the Idaho Falls facility on the 11/08/06. NUSI initiated Non-Conformance Report 06N-090 and this 10CFR21 evaluation on 11/10/06. Extent of Condition: There are four module types that use this style of faceplate: TMD500-[options]-01 Time Domain Module, MTH500-[options]-01 Simple Math Module, CMM500-[options]-01 Complex Math Module, and HLS500-[options]-01 High/Low Select Module. Modules in this category were sold to Ginna and Indian Point. These modules were also sold to Westinghouse for resale; the module identifiers were the same with the substitution of "9000" for "500" in the module number. Per Scientech; Ginna, as stated above, is aware of the problem associated with the TMD500 but they have not been officially informed of a Part 21 being issued concerning the TMD500 problem. As for the Indian Point 2 and Westinghouse they have also not been informed of the Part 21 being issued. The major problem will be trying to trace down the where abouts of the "9000s" that were sold to Westinghouse. * * * UPDATE AT 1057 EST ON 12/18/06 FROM MARTIN BOOSKA TO S. SANDIN * * * Scientech confirmed that Ginna, Indian Point 2 and Westinghouse have been informed of this Part 21 notification. Notified R1DO (Powell), R2DO (Moorman), R3DO (Duncan), R4DO (Whitten) and NRR (Hodge, Tabatabai) via email. * * * UPDATE AT 1739 ON 1/2/2007 FROM MARTY BOOSKA TO MARK ABRAMOVITZ * * * NUSI determined that very old TMD500s could not read higher than 10 Meg. This was traced to a noise suppressing zener diode which has been replaced in more recent models with a metal oxide varistor. A new test criteria was suggested for the older versions. Notified the R1DO (Lorson), R2DO Munday), R3DO (Burgess), R4DO (Farnholtz), NRR (Hodge, Tabatabai) via E-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 | ID | OTH | PAR | 21.21 |  |  |  | 0 | 2006-12-14
43051 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-12-13 15:30 | 2006-12-14 12:27 | 2006-12-14 | OHIO AGREEMENT STATE REPORT - LOST/STOLEN MOISTURE DENSITY GAUGE "Lost or stolen Troxler moisture density gauge from Toledo Office of licensee. Last physically seen on 11/28/06 in secure storage area. Was discovered missing when periodic inventory was being performed on 12/13/06. Gauge is not on licensee's premises or in possession of any current employees. Gauge has not been signed out in any utilization log since 11/28/06. Incident has been reported to Toledo Police Department. Licensee is still investigating. Troxler model 3440, S/N 023819, containing 10 mCi (millicuries) Cs-137 and 40 mCi Am-241. Reported to BRP on 12/13/06 at (approx.) 3: 30 PM." Reference Number 2006-103 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2006-12-19
43050 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-12-13 17:48 | 2006-12-13 21:00 | 2006-12-13 | UNIT REACTOR TRIP DUE TO GRID DISTURBANCE "While operating at 100 % power the unit experienced an automatic Reactor trip from Reactor Protection System actuation at 17:48 on 12/13/06. At the time of the trip there was a grid disturbance followed by the unit tripping. The cause of the trip is under investigation. All plant systems functioned as designed. The unit is being maintained in Hot Shutdown conditions using applicable plant procedures." All control rods inserted fully after the reactor trip. S/G safety valves lifted and reset per design during the transient. The S/Gs are being supplied with normal feedwater and decay heat is being removed to the main condenser via the steam dump valves. The electric plant is in a normal shutdown lineup and the EDGs are available. The licensee notified the NRC Resident Inspector, PEMA, the Counties of Dauphin, Cumberland, Lancaster, York, and Lebanon. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-12-13
43049 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-12-13 04:35 | 2006-12-13 05:49 | 2006-12-13 | REACTOR SCRAM - LOSS OF INSTRUMENT AIR RESULTING IN FEEDWATER TRANSIENT AND MANUAL REACTOR SCRAM "A loss of instrument air caused a transient in feed system causing a lowering Hot Surge Tank Level. The Reactor was manually scrammed when Reactor Feed Booster Pumps were cavitating. Control Rod 42-55 did not insert on the initial scram. Control Rod 42-55 did insert when ARI was manually initiated." The loss of instrument air was the result of an air line rupture, and the licensee is steaming to the condenser while maintaining vessel level with feedwater. There was no ECCS injection, and the licensee is investigating the cause of the line rupture. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0814 ON 12/13/2006 FROM MICHAEL BROGAN TO MARK ABRAMOVITZ * * * "This update is being made in accordance with 10CFR50.72(c)(2) to immediately report the results of ensuing evaluations or assessments of plant conditions, the effectiveness of response or protective measures taken, and information related to plant behavior that is not understood. On December 13, 2006, at 0549 hours, the Perry Nuclear Power Plant notified the NRC Operations Center (Event Number 43049) of a manual Reactor Protection System actuation associated with a loss of instrument air. In the initial report, it was stated that control rod 42-55 did not insert on the initial scram, but did insert when Alternate Rod Insertion was manually initiated. Subsequently, reactor engineering review of control rod performance during the event determined that the control rod scram time for control rod 4255 was satisfactory and that the problem was with the control rod indication. The plant remains stable at this time." Control rod indication has two channels. Control rod 42-55 displayed one fully inserted indication and one blinking green indication (i.e. not fully inserted). When the system was reset, all rods indicated fully inserted with a "00" position indication. The licensee notified the NRC Resident Inspector. Notified the R3DO (Lara). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-12-13
43048 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2006-12-12 23:20 | 2006-12-13 02:27 | 2006-12-13 | AGREEMENT STATE REPORT - FIRE INVOLVING A Co-57 FLOOD SCANNER SOURCE The Director of the Oklahoma Department of Environmental Quality Radiation Protection Agency contacted the NRC Operations Center to report a fire involving one of their material licensees. At approximately 2320 CST on 12/12/06, a fire alarm actuated at Oklahoma Cardiovascular, a mobile nuclear medicine business located in Oklahoma City, OK. The Oklahoma City Fire Department and the HAZMAT team responded to the alarm. The fire destroyed a vehicle containing a plastic coated Co-57 source (10 millicuries). The source is used as a "flood source" for sodium iodide scanners to test the function of the scanner by providing an even radiation field for the scanner to produce images. Three vehicles were parked in the garage, each having one Co-57 source inside each vehicle. The destroyed vehicle appears to be the source of the fire, and the fire department has extinguished the fire. The other vehicles don't appear to be significantly damaged. The Oklahoma City Fire Department is reading radiation levels above background. Oklahoma City Police Department is providing security overnight to prevent access to the area. The licensee doesn't know if vandalism or theft was involved. However, there is media interest in this event. The State of Oklahoma representative intends to go to the site in the morning and contact the NRC with any additional information. * * * UPDATE AT 0953 ON 12/13/2006 FROM MIKE BRODERICK TO MARK ABRAMOVITZ * * * The local hazmat team is still in control of the site. An Health Physicist has determined that the source is intact. A contact reading outside the sheath reads 0.2 milliRem/hr. All swipes were negative and readings elsewhere in the building indicated only background radiation. Notified the R4DO (Smith) and NMSS (Morell). * * * UPDATE AT 1120 ON 12/13/2006 FROM MIKE BRODERICK TO JOE O'HARA * * * All Co-57 sources located at the facility are intact, and there is not spread of loose surface contamination. The sources did not melt but remained intact inside their shielding. The source located inside the vehicle which burned had decayed to 2 millicuries. The fire was not deliberately set and originated in a transformer located inside the garage. Notified the R4DO (Smith) and NMSS (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2006-12-15
43047 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-12-12 13:22 | 2006-12-12 16:59 | 2006-12-12 | CIRCULATING WATER PUMP FAILURE CAUSES EXPLOSION IN INTAKE STRUCTURE "On December 12, 2006, at 1322 PST, while conducting power ascension operations with Unit 2 at approximately 25 percent power, an electrical failure occurred in the Unit 2 circulating water pump motor enclosure (CWP) 2-1. A loud bang and explosion was reported to the Unit 2 control room. At 1322 PST, an electrical transient was experienced on Unit 2 12-Kv non-vital bus 'D' which in turn caused reactor coolant pump (RCP) 2-2 and RCP 2-4 motor breakers to trip on 12kV non-vital bus 'D' undervoltage, initiating an automatic reactor trip. The reactor trip signal was initiated when 2 out of 4 RCP motor breakers opened. All control rods fully inserted in response to the reactor trip and all plant systems functioned as required. The auxiliary feedwater system for Unit 2 was manually actuated per plant procedures, before an auto-start signal for this system was generated. At 1356 PST, DCPP Fire Department first responders reported that the fire was out. " At 1340 the licensee declared a Notice of Unusual Event (NUE), number 23, 'Confirmed Explosion Onsite'. Decay heat is being removed via auxiliary feedwater to the steam generators steaming to the atmospheric dump valves. Emergency power is being supplied via offsite power. "The NRC resident inspector has been informed and was onsite at the time of the Unit 2 reactor trip. Diablo Canyon Power Plant [DCPP] Unit 2 is presently in Mode 3. There were no injuries associated with this event. Investigations into the electrical transient are ongoing. DCPP Unit 2 will remain in Mode 3 pending the results of this investigation. An estimated restart of DCPP Unit 2 is not known at this time. DCPP Unit 1 is unaffected and remains in Mode 1 at 100% power." * * * UPDATE AT 1730 EST ON 12/12/06 FROM T. CHITWOOD TO P. SNYDER * * * The licensee terminated the Unusual Event at 1430 PST. The Notice of Unusual Event was terminated due to the fact the licensee assessed the damage to the circulating water pump and determined that the explosion was caused by a breaker in the local area. The licensee fire brigade was satisfied that the fire was extinguished and that the damage was confined to the local area of circulating water pump 2-1. The licensee notified the NRC Resident Inspector. Notified the R4DO (Smith), NRR EO (Highland), IRD (Wilson), DHS (Inzer), and FEMA (Discoe). * * * UPDATE AT 1841 EST ON 12/12/06 FROM T. CHITWOOD TO J. ROTTON * * * The licensee provided an update to make the formal 4 hour notification pursuant to 10 CFR 50.72 (b)(2)(iv)(B) due to the RPS actuation while critical, and the formal 8 hour notification pursuant to 10 CFR 50.72 (b)(3)(iv)(A) due to the actuation of the auxiliary feedwater system. The licensee notified the NRC Resident Inspector. Notified the R4DO (Smith), and NRR EO (Highland). | 0 | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2006-12-12
43046 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2006-12-12 09:07 | 2006-12-12 11:17 | 2006-12-12 | MANUAL REACTOR TRIP DURING TURBINE CONTROL SYSTEM MAINTENANCE "At 0907 Calvert Cliffs Unit 1 experienced a manual reactor trip during turbine control maintenance. Maintenance was being performed on turbine control to replace circuit cards. This system is a two out of three logic system. Only one logic branch was being de-powered at a time. When the first logic branch was de-powered, the control room supervisor noticed a transient on the reactor coolant system and ordered a manual trip. "Decay heat is being removed via normal methods through the Turbine Bypass Valves to the condenser. At the time of the trip, 11 Auxiliary Feedwater (AFW) Pump was being tested but it was not feeding the steam generators. "This was an uncomplicated trip. The plant responded normally to the event. All control rods fully inserted. The plant is stable and operators are maintaining the unit in Hot Standby. "The licensee notified the NRC Resident Inspector." The trip had no effect on Unit 2, The licensee was in no significant safety system LCO action statement at the time (other than for the AFW 11 surveillance that was in progress at the time of the event.) The steam generators remained on normal feed throughout the event. No Porv's or safeties lifted during the transient. All systems functioned as required. The licensee is investigating how de-powering only one control system logic circuits resulted in the transient. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-12-12
43045 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-11-27 | 2006-12-11 16:14 | 2006-12-11 | NEBRASKA AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGN The licensee provided the following information via email: "The licensee discovered a missing self-luminous sign (Safety Light Model 2040, Serial number D76434) upon doing the annual inventory. They believe the sign was removed by the contractor during a remodeling project in the building about four months before. They believe the sign is in the landfill. They will replace all of the self-luminous exit signs with non radioactive exit signs in 2007." Isotope - Tritium, Activity - 25 Curies. Nebraska Event Number: NE060008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-14
43044 | -1 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2006-12-11 10:03 | 2006-12-11 11:02 | 2006-12-11 | ENTRY OF UNAUTHORIZED PERSONNEL INTO PROTECTED AREA The licensee reports the actual entry of two unauthorized contract personnel into the protected area. Contact Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. * * * RETRACTION PROVIDED BY HUTTON TO KOZAL ON 12/11/06 AT 2137 * * * The licensee reports upon review of the event that there was no unauthorized entry. Contact Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. Notified R1DO (Conte) and 73.71 Safeguards Group (via e-mail) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-12-11
43043 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2006-11-13 | 2006-12-11 10:13 | 2006-12-12 | AGREEMENT STATE REPORT - LOST PO-210 SOURCE A 0.5 milliCurie Po-210 static eliminator source was lost by 3M Corporation. 3M was performing an inventory and determined the source to be missing on 11/13/2006. The state will follow up with additional details when supplied by the licensee. * * * UPDATE PROVIDED VIA FAX BY CRAIG VERKE TO JEFF ROTTON AT 1341 EST ON 12/12/06 * * * The State provided the following information via facsimile: " The lost device is a model P2042 Nucleospot nuclear static eliminator, manufactured by NRD Inc. The original activity of the source was five millicuries of Polonium-210 at the time of its manufacture in September of 2005. The current, decayed activity of the source is 0.5 millicuries. The static eliminators are leased by NRD for a one year period and returned to NRD at the expiration of the lease. "3M uses about 40 of these devices in weighing balances in research laboratories at 3M Center, St. Paul MN. Receipt, shipment and annual change outs of the devices at the end of their lease is handled by a member of Corporate Health Physics (CHP). An individual in the laboratory where the device is used is designated as the Radiation Safety Officer (RSO) and is responsible for day-to-day use of the device. The RSOs conducts semiannual physical inventories of their devices, most recently in July 2006. "The device in question was in use in a laboratory of the 3M Pharmaceutical Division in Building 260 on 3M Center. It was not in the balance where it was normally used when CHP attempted to replace it at the end of the lease in November 2006. It was then learned that the RSO for the laboratory had taken a different position at 3M and had not been in the laboratory since the physical inventory in July. " CHP was not notified of the job transfer by the laboratory RSO. Therefore, there was a period of several months when there was no individual specifically responsible for the device. During that time we believe the device was moved to a different 3M laboratory for use there and placed in a drawer or other storage location by an employee who has since left the company. Since 3M announced plans for the sale of the Pharmaceutical Division, many research employees in that division have taken positions with other companies. The device may have been disposed of in the trash, though this seems unlikely as it has a radioactive material label. It also appears likely that it was stolen as it has no intrinsic value and little usefulness outside of a laboratory. " Radiation exposure would not result from this device in an unrestricted area. The emitted alpha radiation is completely shielded by clothing or the dead skin layer on the outside of the body. The radioactive material is sealed in a capsule, which is further enclosed in the body of the device itself, thus preventing inhalation or ingestion. Wipe tests performed by 3M in January and July, 2006 showed no contamination at a minimum detection level of 1 x 10-6 microcuries. " Actions taken to recover the lost device involved interviews with personnel in the laboratory where it was used and searches of that and surrounding laboratories. Emails were sent to persons working in the laboratories asking them to provide any information they had on the location of the device. Flyers with pictures of the device requesting its return were posted in the laboratories. " Measures to ensure against a recurrence are: - Reminders to laboratory RSOs and their management to notify Clip of any change in location of a nuclear static eliminator or in the job status of the RSO. - Reminders were given to those working in the laboratories, during the course of the searches, of the need to leave the nuclear static eliminators in their assigned location." Notified NMSS EO (Morell), R3DO (Lara), and ILTAB (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2006-12-14
43042 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-12-10 16:08 | 2006-12-11 00:31 | 2006-12-14 | RAPID SHUTDOWN AND MANUAL REACTOR TRIP DUE TO HIGH REACTOR COOLANT PUMP STATOR TEMPERATURE "On December 10, 2006, at 1608 PST, operators manually tripped the reactor while it was subcritical. This is an 8 hour notification per 10 CFR 50.72(b)(3)(iv)(A) for actuation of the reactor protection system while subcritical. On December 10, 2006, with Unit 2 operating in Mode 1 at 100% power, operators initiated an unplanned reactor shutdown due to indications of increasing stator temperature on reactor coolant pump 2-2. In accordance with plant procedures, when the reactor coolant pump stator temperature reached 300 degrees Fahrenheit, operators manually tripped the reactor and tripped the coolant pump 2-2. The reactor was subcritical at the time of the reactor trip but all rods had not been fully inserted. "All control rods fully inserted in response to the reactor trip and all systems functioned as required. The auxiliary feedwater system was already in service as part of the shutdown. The grid is stable and with the exception of RCP 2-2, all major equipment including the 3 emergency diesel generators remain operable. Unit 2 electrical loads are being supplied by the normal startup power. The other 3 RCPs are maintaining forced circulation of the reactor coolant system. Investigations into the high RCP stator temperature are ongoing, the unit will remain in Mode 3 pending the results of these investigations. An estimated restart date is not known at this time. The NRC Resident Inspector has been informed and was onsite at the time of the trip. Unit 1 is unaffected and remains in Mode 1." The licensee stated that a press release related to this event is likely. * * * UPDATE TO HUFFMAN DURING PLANT STATUS ON 12/11/06 AT 0419 EST * * * Licensee believes the cause of the high RCP stator temperature was due to a failed RTD. * * * UPDATE FROM L. PARKER TO P. SNYDER AT 1531 ON 12/14/06 * * * "Unit 2 was in Mode 3 (Hot Standby) at 0 percent power at the time of the manual trip. At the time of the Initial notification, all procedural requirements for declaring Mode 3 had not been met, but upon further review, PG&E has verified K effective was less than 0.99." The licensee notified the NRC Resident Inspector. Notified R4DO (Proulx). The original report was modified by this change. The 'RX Crit' field was changed from 'Y' to 'N'. The 'Init Power' field was changed from '5' to '0'. The 'Curr Power' field was changed from 'Startup' to 'Hot Standby'. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-12-11
43041 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-30 05:37 | 2006-12-09 12:55 | 2006-12-09 | INADVERTENT OPENING OF TWO ISOLATION VALVES "This telephone notification to report an invalid actuation is provided in accordance with 10 CFR 50.73(a)(1), which states, 'In the case of an invalid actuation reported under Sec. 50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. The specific reporting requirement in 10 CFR 50.73(a)(2)(iv)(A), states, 'Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).' For this report, the affected system was the Unit 2 Train B Containment Spray System. "On October 30, 2006 at approximately 0600 hours, a Main Control Room (MCR) Senior Reactor Operator identified during a panel walk-down that the containment spray header isolation valve, 2CS007B, and the containment spray eductor NaOH tank suction isolation valve, 2CS019B, were open. This was an unexpected condition, which prompted Operations to investigate. A review of the Alarm computer points revealed that the valves opened at 0537 hours. The investigation determined that the most probable cause of this occurrence was attributed to, during the performance of maintenance inside of the 2PA10J panel, an Electrical Maintenance Department technician inadvertently making contact with the manual latch causing the actuation of the K643B slave relay that led to repositioning of the out-of-position valves. "The following information provides the required details outlined in NUREG 1022 Revision 2: "(a) The relay actuation for the 2B Containment Spray valves was not a valid ESF actuation. The actuation was the result of an inadvertent bump of the K643B relay and not the result of a valid ESF signal from the reactor protection system. "(b) This report is being made under 10CFR50.73(a)(2)(iv)(A). "(c) The specific train and system that actuated was 2B Containment Spray. "(d) The train actuation was a partial actuation for three containment spray valves from the K643B slave relay due to an inadvertent bump of the slave relay manual latching mechanism with the following conditions identified: " 2CS007B, 2B containment spray header isolation valve, changed from closed to open. "2CS010B, 2B containment spray NaOH eductor inlet isolation valve, is normally open and did not change position, but received an open signal. "2CS019B, 2B containment spray eductor NaOH tank suction isolation valve, changed from closed to open. "The 2B containment spray system was in TEST in preparation for changing from Mode 5 to Mode 4. "(e) The containment spray system did not start because the system was in TEST and the containment spray pumps were in lock out while in Mode 5. The three valves functioned as designed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-12-09
43040 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-12-08 18:12 | 2006-12-08 22:42 | 2006-12-28 | CREFS SYSTEM INOPERABLE "Control Room Emergency Filtration System (CREFS) was declared inoperable at 1812 on 12/8/06 because the W-14A, F-16 Control Room Charcoal Filter Fan tripped during performance of the monthly technical specification surveillance test, TS-9. "This fan is required to be operable for operability of the CREFS System. This condition is covered by TS 3.7.9, Control Room Emergency Filtration System and both units have entered action condition A, 'CREFS Inoperable' with a required action to 'Restore CREFS to OPERABLE Status' with a completion time of 7 days. "CREFS is a single train system. Based on the guidance in NUREG-1022 for single train systems that perform safety functions, this condition was determined to be reportable under 10CFR50.72(b)(3)(v), 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function'." * * * RETRACTION PROVIDED BY VANDERWARF TO KOZAL ON 12/28/06 AT 0952 * * * "On December 8, 2006, at 22.42 EST, EN 43040 was made by the Point Beach Nuclear Plant in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition at the time of discovery could have prevented the fulfillment of a system function that is needed to mitigate the consequences of an accident. Control Room Emergency Filtration System (CREFS) fan W-1 4A, F-16 Control Room Charcoal Filter Fan tripped during performance of the monthly Technical Specification surveillance test. CREFS was declared inoperable. "After further evaluation, it was determined that the safety function of CREFS was not lost. Redundant fan W-14B was operable for the duration of the time fan W-14A was out of service. Single train portions of the system were not affected by the W-1 4A fan trip. Accordingly, this event is not reportable. EN 43040 is, therefore, retracted." Notified R2DO (Burgess) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-12-08
43039 | 0 | KENNEDY MEMORIAL HOSPITAL |  |  |  |  | 2006-12-08 | 2006-12-08 15:49 | 2006-12-11 | SHIFT OF I-125 SEEDS AFTER IMPLANTATION On 10/26/06 the licensee implanted a patient with 104 seeds of I-125 (total activity of 42.2 millicuries, manufactured by Bard, Inc.) to treat prostate cancer. The post implant CT performed on 12/08/06 indicated that the distribution of the seeds was inferior to the intended distribution. A percentage of the seeds had shifted approximately 1.5 cm inferior to what was intended. The licensee is still evaluating at this time what percentage of the seeds intended for the prostate were no longer in the prostate . The licensee immediately informed the patient and the prescribing physician. The patient has to this point shown no ill effects from the migration. However, a quantity of the seeds have migrated to the perineum. Due to the unknown quantity of seeds in the perineum the licensee is still investigating the amount of dose received in this area. The licensee is investigating the cause of the migration. After the cause is determined they will put corrective actions in place to prevent reoccurrence. The licensee has performed multiple implants that were close to 100% successful since this occurrence. The licensee intends to supplement the patients treatment with an external bean in order to achieve the intended dose. The licensee notified NRC Region 1 (S. Gabriel, P. Lanzisera) * * * UPDATE TO HUFFMAN FROM TRIPP AT 10:55 EST ON 12/11/06 * * * Based on discussion with NRC Region 1 (S. Gabriel), the licensee provided the following revision to the initial event report: "On October 25, 2006, the licensee implanted 104 I-125 seeds into a patient for the treatment of prostate cancer. The total activity of the implanted seeds was 42.4 mCi. A post-implant CT performed on December 8, 2006, indicated that the seed were misplaced approximately 1.5 cm inferior to the intended position. The licensee is still evaluating the details of the post-implant dosimetry. "Notifications pursuant to 10 CFR 35.3045 were made on December 8, 2006. "The licensee is still evaluating the cause of the misplacement of the iodine seeds. After the cause(s) has been determined, corrective actions will be put in place. "The patient will require will require further treatment of the prostate gland. External beam therapy will be used to supplement the dose to prostate." R1DO (Conte) and NMSS EO (Morell) notified. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-12-11
43038 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-12-07 17:28 | 2006-12-07 21:51 | 2007-02-05 | LOSS OF SAFE SHUTDOWN CAPABILITY "The Unit 2 Spray Additive System was isolated due to an identified crack on a weld at a 'tee' section of pipe upstream of a sample point. The crack was identified during a system release for an unrelated maintenance activity. Isolation of the crack for repairs requires isolation of the Containment Spray Additive system from both Containment Spray headers. This isolation was also completed to comply with ASME (Technical Specification Action Statement) 3.4.11.1. Therefore the Containment Spray Additive system is unable to perform its safety function. Salem Unit 2 remains in TS A/S 3.6.2.2 until repairs are complete." TS A/S 3.6.2.2 is a 72 hour LCO (entered at 0503 on 12/07/06) and requires the plant to be in hot standby within 6 hours of the expiration of the LCO. The licensee will inform the Lower Alloways Creek Township and has informed the NRC Resident Inspector. * * * RETRACTION FROM ABBOTT TO HUFFMAN AT 2146 EST ON 2/05/07 * * * "On December 7, 2006, PSEG made a non-emergency report in accordance with the 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D) (event report 43038) regarding the Salem Unit 2 Spray Additive System. "Upon further investigation, PSEG determined that the identified crack on a weld which resulted in a one drop per minute leak would not have caused a loss of system function. Therefore, based upon the guidance provided in NUREG 1022 that there is reasonable assurance that the weld would have remained intact and would have satisfactorily performed its intended function in the event of a CS system actuation (i.e., there was no loss of system safety function) this event report is being retracted. "The NRC Resident Inspector was notified of this retraction." R1DO (Cook) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2006-12-07
43037 | -1 | ST. JOHNS MERCY MEDICAL CENTER |  |  |  |  | 2006-12-07 07:30 | 2006-12-07 11:25 | 2006-12-08 | EXTERNAL CONTAMINATION ON PACKAGE EXCEEDING SHIPPING LIMITS The RSO for St. Johns Mercy Medical Center reported that a package was received at the facility with external and internal contamination. The package originated from a radiopharmaceutical company, GE- Healthcare, St. Louis and contained 400 microCi of I-123 and 5 milliCi of Tc-99. The package was surveyed upon receipt and found to have contamination levels of approximately 3100 dpm per square centimeter on both external and internal surfaces. This contamination is greater than the limits permitted in 49 CFR 173.443 and are therefore reportable. The contamination was analyzed in a multichannel analyzer and is believed to be Tc-99. The radiopharmaceuticals in the package were not damaged or leaking and the contamination does not appear to be from the contents of the shipment. The GE-Healthcare, St. Louis facility was contacted and informed of the contamination. The driver and the vehicle used to transport the package have been surveyed and no contamination found. No other contamination has been found at the St. Johns Mercy Medical Center. The hospital plans to hold onto the shipping package until the Tc-99 decays before it is returned to GE- St. Louis. * * * RETRACTION FROM TURCO TO HUFFMAN AT 1045 EST ON 12/08/06 * * * Upon further investigation, the RSO for St. Johns has determined that the package was likely contaminated by the technician that performed the receipt inspection at the St. Johns Mercy Medical Center. The gloves of the technician performing the initial survey swipes were apparently contaminated by activities at the facility prior to receiving the package. Therefore, the licensee is retracting this event. NRC Region III (Piskura) was notified by the licensee. R3DO (Lipa) and NMSS EO (Morell) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2006-12-07
43036 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2006-12-06 | 2006-12-06 18:04 | 2006-12-06 | AGREEMENT STATE REPORT - LICENSEE LOST CUSTODY OF TROXLER GAUGE DURING TRANSPORT The State of Utah reported that a member of the general public recovered a Troxler moisture density gauge on a street located near St. George, Utah. Apparently, the licensee was transporting the gauge through this area when it fell off the vehicle. The licensee was not aware that the gauge was no longer in their custody and continued traveling down the road. A member of the general public, a cable company employee, noticed the gauge and its transportation container lying in the street. The individual recovered the gauge, placed it back in the transport container, and contacted the licensee via the phone number on the package. The licensee arrived and took custody of the gauge from the member of the general public. The licensee reported that the source remained in the safe, shielded position. The licensee reported that the gauge was not damaged and is located in their St George, Utah office. The State is expecting additional details regarding the serial number, isotope, or activity of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2006-12-11
43035 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-11-29 | 2006-12-06 16:16 | 2007-01-24 | AGREEMENT STATE REPORT - LOST CANCER THERAPY SEEDS The State provided the following information via email: "Date and time of Event: 29 November 2006 (reported to DOH on 5 December 2006) "Location of Event: Seattle, Washington (main campus operating room) "ABSTRACT: A Central Services employee, who was to only clean bodily fluids from the exterior of a cancer therapy seed applicator post-use, apparently also opened the spring-loaded device displacing the remaining seeds. The remaining seven seeds in the applicator (one was later found in garbage, six are still missing) popped out. The six seeds were apparently flushed down the drain by mistake. Surveys cannot locate the seeds at this time. Cause, contributing factors, and corrective actions have not been determined as of this writing. At this time no consequences are expected and there has been no media attention. "Isotope and Activity involved: Iodine-125, sealed brachytherapy seeds. Six seeds, total of 97.7 MegaBq (2.64 millicuries). "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None noted or expected. "Lost, Stolen or Damaged? (mfg., model, serial number): Lost, mfg/model not yet known. "Disposition/recovery: To be determined. "Leak test? Original, by Manufacturer, within past six months. "Release of activity? The seeds were apparently released to the waste water drain. No contamination was found. "Consequences: None so far, none expected." WA-06-068 * * * UPDATE FROM A. SCROGGS TO W. GOTT AT 1455 ON 01/24/07 * * * The State provided the following information via email: "The actual cause was determined to be inadequate training of the CS employee. The licensee has revised the procedure for handling seed implants. Now only a properly trained scrub nurse or tech will handle the applicator and accessories. At this time no consequences are expected and there has been no media attention." The six missing sources were never recovered. Notified R4DO (M. Hay) and NMSSEO (G. Morell) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-12-11
43034 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-12-05 12:00 | 2006-12-06 14:11 | 2006-12-07 | OHIO AGREEMENT STATE REPORT - MEDICAL EVENT - LOWER DOSE THAN PRESCRIBED "On December 6, 2006 at 9:00 AM the Ohio Bureau of Radiation Protection received a phone call from The Urology Center, LLC Ohio License number 02200310002 reporting a possible medical event that was discovered on December 5, 2006 at approximately 12:00 PM. The licensee reported that the loading of seeds into the prostate gland was not performed properly, resulting in a total shift of the seeds to the intended treatment site. This resulted in a dose to the intended treatment site to be 40 percent less than the prescribed dose. The seeds were delivered to the prostate gland. A preliminary report is expected by 4 PM December 6, 2006. A detailed written report will be due in 15 Days. A Ohio Bureau of Radiation Inspector will perform an inspection the week of December 11." The seeds used for the implant were I-125, curie content not known at this time. It is not known at this time if there will be any deleterious effects due to this treatment. The patient was notified at the time of the treatment. Ohio event number: 2006-100 * * * UPDATE FROM FLANNERY (FSME) TO HUFFMAN AT 0706 ON 12/07/06 * * * This event has been reviewed by the NRC medical review committee and determined to be a reportable medical event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2006-12-09
43033 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS INC. |  |  |  |  | 2006-09-18 | 2006-12-05 17:56 | 2006-12-05 | POTENTIALLY DEFECTIVE PRESSURE TRANSMITTERS SHIPPED TO DIABLO CANYON "Notification under 10 CFR Part 21 for Model 1154 Series H Pressure Transmitters pursuant to 10 CFR Part 21, section 21.21(a), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you that: (a) two Model 1154 Series H pressure transmitters shipped to Pacific Gas & Electric on September 18, 2006, may not conform to RNII's published specification's under accident conditions. "1.0 Name and address of the Individual providing the information: Mr. Jeffrey W. Schmitt, Vice President & General Manager Rosemount Nuclear Instruments, Inc. 8200 Market Blvd Chanhassen, MN 55317 "2.0 Identification of Items supplied: Two Model 1154 Series H pressure transmitters are affected, as shown below: Purchase Order - 130124, Sales Order 1732406, Model Number - 1154DH5RC, Serial Number(s) - 0533268, 0533275 Ship date - 18SEP06, Site - Diablo Canyon "3.0 Identification of firms supplying the item: Rosemount Nuclear Instruments, Inc. 8200 Market Blvd Chanhassen, MN 55317 "4.0 Nature of the failure and potential safety hazard: RNII Model 1154 and Model 1154 Series H transmitters are similar in construction except that the Model 1154 Series H transmitters have a metal shroud, filled with an insulating material, surrounding the sensor module. This feature assures that the Model 1154 Series H transmitter can perform to specifications under certain accident conditions. "When an order for a pressure transmitter is released to production, a travel card is generated by RNII's business operating system. In the production process a specific list of manufacturing and inspection procedures is joined to the travel card based on the transmitter model number pre-printed on the travel card. These procedures are completed in the order listed to produce the specified pressure transmitter. "For the two transmitters in question, a list of procedures pertaining to the Model 1154 was attached to the travel card, rather than the procedures for the Model 1154 Series H transmitter. This error was not detected during the production process, and, as a result, the transmitters were assembled and inspected as Model 1154 transmitters. "5.0 The corrective action which is taken, the name of the individual or organization responsible for that action, and the length of time taken to complete that action: (a) As a precautionary measure, RNII held shipments of all Model 1154 Series H transmitters while production records were reviewed for discrepancies. No additional suspect transmitters were identified. (b) All RNII transmitter travel cards for the prior three years of production were examined for similar discrepancies. No additional suspect transmitters were identified. (c) RNII's field returns history was reviewed for similar nonconformances. None were found. (d) An internal corrective action request was initiated. Corrective actions have been implemented to eliminate the potential for attaching the incorrect list of production procedures. (Completed: Dec 4, 2006) "6.0 Any advice related to the potential failure of the item: The end user is advised to determine the impact of this defect upon its plant's operation and safety, and take action as deemed necessary. RNII recommends that the affected transmitters be returned to RNII for rework. (Arrangements have been made with PG&E to return the affected transmitters.)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2006-12-05
43032 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-12-05 | 2006-12-05 16:27 | 2006-12-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN "On December 5, 2006, the licensee reported that an exit sign, currently containing approximately 5.5 Ci of H-3 was apparently lost or inadvertently disposed during remodeling of the University Library in October 2006. This sign was distributed by 'Self Powered Lighting' in Elmsford, NY (15 Ci in March 1989), Model 710-A, S/N A60. The sign was mounted in the east stairwell of the 4th floor of the University Library, and was present during the quarterly inventory July 31, 2006. During the October inventory, and while the building was being remodeled, the sign was missing. The University staff investigated, but were unable to determine the disposition of the sign. The wall where the sign was mounted was removed by a contractor during the remodeling. The RSO discussed the situation with the Construction Manager and the University's Project Management Staff to avert such occurrences during future remodeling activities. The University will notify RHB if the sign is located. The most likely scenario is that this sign was disposed with other construction debris." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-12-08
43031 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-12-04 13:25 | 2006-12-05 13:52 | 2006-12-05 | POTENTIAL DEFECTIVE WOODWARD GOVERNOR FOR FAIRBANKS MORSE EDG "South Carolina Electric & Gas Company makes the following notification under 10 CFR 21.21(d)(3)(i) of a defect found during pre-installation testing of a Fairbanks Morse Woodward 2301 A/DRU governor. This governor was not installed on the Virgil C. Summer Nuclear Station Emergency Diesel Generators (EDG). "The Fairbanks failure mode effect analysis (FMEA) states that when 125 VDC power is lost to the governor Digital Reference Unit (DRU), the speed reference signal goes to 0 VDC and that the Control Module will respond to drive the EDG to rated speed of 514 rpm. When this failure mode was tested, removal of the 125 VDC power resulted in a speed reference signal of -4 VDC. This would result in the governor Control Module driving the EDG to the low speed set point of 300 rpm. The failure to achieve rated speed would prevent the EDG from performing its safety function. "Following a loss of 125 VDC power, the DRU must be manually reset in order for the Control Module to drive the EDG to rated speed. Users of this governor, that are not aware of this failure mode, may be unaware that the in-service EDG would be unable to meet the Technical Specification requirements unless surveillance tests were performed following the loss of power." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2006-12-05
43030 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2006-12-03 18:04 | 2006-12-05 11:04 | 2006-12-05 | NON-FUNCTIONAL SAFETY PARAMETER DISPLAY SYSTEM "At 1804 on 12/03/2006, both Safety Parameter Display System (SPDS) displays in the Beaver Valley Power Station (BVPS) Unit 1 control room were identified as not functioning. Initial evaluation indicated that the system would be returned in less than a day. However, subsequent evaluation determined that vendor assistance would be needed to return the system to operation. The vendor is currently performing maintenance, with the system anticipated to be returned to service today (12/05/2006). Thus, this is being reported as a loss of emergency assessment capability pursuant to 10 CFR 50.72(b)(3)(xiii). "Other BVPS Unit 1 equipment that remain available to adequately address potential emergent events include the Inadequate Core Cooling Monitor (ICCM), the BVPS Unit 1 Plant Computer and the Control Room alarm system." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM RONALD T. GREEN TO JOE O'HARA AT 1449 ON 12/5/06 * * * " At 1401 on 12/05/2006, the Safety Parameter Display System (SPDS) was repaired and returned to service at Beaver Valley Power Station (BVPS) Unit 1." The licensee notified the NRC Resident Inspector. Notified R1DO (M. Sykes) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-12-05
43029 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-04-21 | 2006-12-04 16:59 | 2006-12-04 | AGREEMENT STATE REPORT - MISSING SELF-ILLUMINATING EXIT SIGNS The State provided the following information via facsimile: "Late last winter and early this spring the general licensee hired a consulting firm to do an inventory of the self-illuminating exit signs in Nebraska. They used the inventory lists of exit signs from the Radiation Control Program in Nebraska and lists from the manufacturers of Isolite (Safety Light) and SRB Technologies to make a comprehensive list of exit signs assigned to Nebraska Licensees. This comprehensive list was taken to each store and compared to the signs that were installed. They made more than one trip to the stores to make sure they had an accurate inventory. They discovered that some signs had been returned to the manufacturer and some signs installed in other Wal-Mart stores in and out of Nebraska. The consultants found 3 missing signs at this location. To help with the inventory in the future, the licensee (1) put a sticker on each tritium exit sign with the 'Item Number' assigned by the State of Nebraska, (2) The sign location was marked on a drawing of the store's floor plan, and (3) The inventory information was compiled and stored in a database. The licensee has discontinued having self illuminating signs installed in their stores in Nebraska. They are also considering replacing the signs with non radioactive material exit signs as they remodel stores in the future. They will continue to do inventories of stores in other states and may find some of the missing signs. The consultants discovered that some contractors took signs from one store to another when they had extra signs left after a construction project. The licensee was unable to determine if the missing signs were installed in this location and then removed during previous remodeling or if the signs were never installed at this location." Source 1: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 325286, 11.5 Curies H-3 Source 2: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 325319, 11.52 Curies H-3 Source 3: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 325320, 11.5 Curies H-3 Nebraska item number: NE060007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43028 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-04-21 | 2006-12-04 16:59 | 2006-12-04 | AGREEMENT STATE REPORT - MISSING SELF-ILLUMINATING EXIT SIGNS The State provided the following information via facsimile: "Late last winter and early this spring the general licensee hired a consulting firm to do an inventory of the self-illuminating exit signs in Nebraska. They used the inventory lists of exit signs from the Radiation Control Program in Nebraska and lists from the manufacturers of Isolite (Safety Light) and SRB Technologies to make a comprehensive list of exit signs assigned to Nebraska Licensees. This comprehensive list was taken to each store and compared to the signs that were installed. They made more than one trip to the stores to make sure they had an accurate inventory. They discovered that some signs had been returned to the manufacturer and some signs installed in other Wal-Mart stores in and out of Nebraska. The consultants found 3 missing signs at this location. To help with the inventory in the future, the licensee (1) put a sticker on each tritium exit sign with the 'Item Number' assigned by the State of Nebraska, (2) The sign location was marked on a drawing of the store's floor plan, and (3) The inventory information was compiled and stored in a database. The licensee has discontinued having self illuminating signs installed in their stores in Nebraska. They are also considering replacing the signs with non radioactive material exit signs as they remodel stores in the future. They will continue to do inventories of stores in other states and may find some of the missing signs. The consultants discovered that some contractors took signs from one store to another when they had extra signs left after a construction project. The licensee was unable to determine if the missing signs were installed in this location and then removed during previous remodeling or if the signs were never installed at this location." Source 1: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 324383, 11.5 Curies H-3 Source 2: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 324384, 11.5 Curies H-3 Source 3: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 424395, 11.5 Curies H-3 Nebraska item number: NE060006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43027 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-04-21 | 2006-12-04 16:59 | 2006-12-04 | AGREEMENT STATE REPORT - MISSING SELF-ILLUMINATING EXIT SIGNS The State provided the following information via facsimile: "Late last winter and early this spring the general licensee hired a consulting firm to do an inventory of the self-illuminating exit signs in Nebraska. They used the inventory lists of exit signs from the Radiation Control Program in Nebraska and lists from the manufacturers of Isolite (Safety Light) and SRB Technologies to make a comprehensive list of exit signs assigned to Nebraska Licensees. This comprehensive list was taken to each store and compared to the signs that were installed. They made more than one trip to the stores to make sure they had an accurate inventory. They discovered that some signs had been returned to the manufacturer and some signs installed in other Wal-Mart stores in and out of Nebraska. The consultants found 2 missing signs at this location. To help with the inventory in the future, the licensee (1) put a sticker on each tritium exit sign with the 'Item Number' assigned by the State of Nebraska, (2) The sign location was marked on a drawing of the store's floor plan, and (3) The inventory information was compiled and stored in a database. The licensee has discontinued having self illuminating signs installed in their stores in Nebraska. They are also considering replacing the signs with non radioactive material exit signs as they remodel stores in the future. They will continue to do inventories of stores in other states and may find some of the missing signs. The consultants discovered that some contractors took signs from one store to another when they had extra signs left after a construction project. The licensee was unable to determine if the missing signs were installed in this location and then removed during previous remodeling or if the signs were never installed at this location." Source 1: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 294689, 11.5 Curies H-3 Source 2: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 294690, 11.5 Curies H-3 Nebraska item number: NE060005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43026 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-04-21 | 2006-12-04 16:59 | 2006-12-04 | AGREEMENT STATE REPORT - MISSING SELF-ILLUMINATING EXIT SIGNS The State provided the following information via facsimile: "Late last winter and early this spring the general licensee hired a consulting firm to do an inventory of the self-illuminating exit signs in Nebraska. They used the inventory lists of exit signs from the Radiation Control Program in Nebraska and lists from the manufacturers of Isolite (Safety Light) and SRB Technologies to make a comprehensive list of exit signs assigned to Nebraska Licensees. This comprehensive list was taken to each store and compared to the signs that were installed. They made more than one trip to the stores to make sure they had an accurate inventory. They discovered that some signs had been returned to the manufacturer and some signs installed in other Wal-Mart stores in and out of Nebraska. The consultants found 3 missing signs at this location. To help with the inventory in the future, the licensee (1) put a sticker on each tritium exit sign with the 'Item Number' assigned by the State of Nebraska, (2) The sign location was marked on a drawing of the store's floor plan, and (3) The inventory information was compiled and stored in a database. The licensee has discontinued having self illuminating signs installed in their stores in Nebraska. They are also considering replacing the signs with non radioactive material exit signs as they remodel stores in the future. They will continue to do inventories of stores in other states and may find some of the missing signs. The consultants discovered that some contractors took signs from one store to another when they had extra signs left after a construction project. The licensee was unable to determine if the missing signs were installed in this location and then removed during previous remodeling or if the signs were never installed at this location." Source 1: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 228132, 11.5 Curies H-3 Source 2: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 228141, 11.5 Curies H-3 Source 3: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 228109, 11.5 Curies H-3 Nebraska item number: NE060004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43025 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-04-21 | 2006-12-04 16:59 | 2006-12-04 | AGREEMENT STATE REPORT - MISSING SELF-ILLUMINATING EXIT SIGNS The State provided the following information via facsimile: "Late last winter and early this spring the general licensee hired a consulting firm to do an inventory of the self-illuminating exit signs in Nebraska. They used the inventory lists of exit signs from the Radiation Control Program in Nebraska and lists from the manufacturers of Isolite (Safety Light) and SRB Technologies to make a comprehensive list of exit signs assigned to Nebraska Licensees. This comprehensive list was taken to each store and compared to the signs that were installed. They made more than one trip to the stores to make sure they had an accurate inventory. They discovered that some signs had been returned to the manufacturer and some signs installed in other Wal-Mart stores in and out of Nebraska. The consultants found 8 missing signs at this location. To help with the inventory in the future, the licensee (1) put a sticker on each tritium exit sign with the 'Item Number' assigned by the State of Nebraska, (2) The sign location was marked on a drawing of the store's floor plan, and (3) The inventory information was compiled and stored in a database. The licensee has discontinued having self illuminating signs installed in their stores in Nebraska. They are also considering replacing the signs with non radioactive material exit signs as they remodel stores in the future. They will continue to do inventories of stores in other states and may find some of the missing signs. The consultants discovered that some contractors took signs from one store to another when they had extra signs left after a construction project. The licensee was unable to determine if the missing signs were installed in this location and then removed during previous remodeling or if the signs were never installed at this location." Source 1: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 271458, 11.5 Curies H-3 Source 2: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 279235, 11.5 Curies H-3 Source 3: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 279236, 11.5 Curies H-3 Source 4: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 279237, 11.5 Curies H-3 Source 5: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 279238, 11.5 Curies H-3 Source 6: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 279239, 11.5 Curies H-3 Source 7: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 279240, 11.5 Curies H-3 Source 8: Manufacturer: Safety Light Corp, Model SLX-60, Serial number: 279243, 11.6 Curies H-3 Nebraska item number: NE060003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43024 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-04-21 | 2006-12-04 16:59 | 2006-12-04 | AGREEMENT STATE REPORT - MISSING SELF-ILLUMINATING EXIT SIGNS The State provided the following information via facsimile: "Late last winter and early this spring the general licensee hired a consulting firm to do an inventory of the self-illuminating exit signs in Nebraska. They used the inventory lists of exit signs from the Radiation Control Program in Nebraska and lists from the manufacturers of Isolite (Safety Light) and SRB Technologies to make a comprehensive list of exit signs assigned to Nebraska Licensees. This comprehensive list was taken to each store and compared to the signs that were installed. They made more than one trip to the stores to make sure they had an accurate inventory. They discovered that some signs had been returned to the manufacturer and some signs installed in other Wal-Mart stores in and out of Nebraska. The consultants found 4 missing signs at this location. To help with the inventory in the future, the licensee (1) put a sticker on each tritium exit sign with the 'Item Number' assigned by the State of Nebraska, (2) The sign location was marked on a drawing of the store's floor plan, and (3) The inventory information was compiled and stored in a database. The licensee has discontinued having self illuminating signs installed in their stores in Nebraska. They are also considering replacing the signs with non radioactive material exit signs as they remodel stores in the future. They will continue to do inventories of stores in other states and may find some of the missing signs. The consultants discovered that some contractors took signs from one store to another when they had extra signs left after a construction project. The licensee was unable to determine if the missing signs were installed in this location and then removed during previous remodeling or if the signs were never installed at this location." Source 1: Manufacturer: SRB Technologies, Model BX-20-GY, Serial number: 310254, 17.51 Curies H-3 Source 2: Manufacturer: SRB Technologies, Model BX-20-GY, Serial number: 310289, 17.51 Curies H-3 Source 3: Manufacturer: SRB Technologies, Model BX-20-GY, Serial number: 310290, 17.51 Curies H-3 Source 4: Manufacturer: SRB Technologies, Model BX-20-GY, Serial number: 310291, 17.51 Curies H-3 Nebraska item number: NE060002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43023 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2006-04-21 | 2006-12-04 16:59 | 2006-12-04 | AGREEMENT STATE REPORT - MISSING SELF-ILLUMINATING EXIT SIGNS The State provided the following information via facsimile: "Late last winter and early this spring the general licensee hired a consulting firm to do an inventory of the self-illuminating exit signs in Nebraska. They used the inventory lists of exit signs from the Radiation Control Program in Nebraska and lists from the manufacturers of Isolite (Safety Light) and SRB Technologies to make a comprehensive list of exit signs assigned to Nebraska Licensees. This comprehensive list was taken to each store and compared to the signs that were installed. They made more than one trip to the stores to make sure they had an accurate inventory. They discovered that some signs had been returned to the manufacturer and some signs installed in other Wal-Mart stores in and out of Nebraska. The consultants found 2 missing signs at this location. To help with the inventory in the future, the licensee (1) put a sticker on each tritium exit sign with the 'Item Number' assigned by the State of Nebraska, (2) The sign location was marked on a drawing of the store's floor plan, and (3) The inventory information was compiled and stored in a database. The licensee has discontinued having self illuminating signs installed in their stores in Nebraska. They are also considering replacing the signs with non radioactive material exit signs as they remodel stores in the future. They will continue to do inventories of stores in other states and may find some of the missing signs. The consultants discovered that some contractors took signs from one store to another when they had extra signs left after a construction project. The licensee was unable to determine if the missing signs were installed in this location and then removed during previous remodeling or if the signs were never installed at this location." Source 1: Manufacturer: SRB Technologies, Model BX-20-GY, Serial number: 27110, 16.51 Curies H-3 Source 2: Manufacturer: SRB Technologies, Model BX-20-GY, Serial number: 270408, 17.51 Curies H-3 Nebraska item number: NE060001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43022 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-12-04 11:46 | 2006-12-04 14:05 | 2006-12-04 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE A truck carrying a CPN Model MCI PRT moisture density gauge (10 millicuries Cs-137; 50 millicuries Am-241:Be) was involved in a transportation accident. The moisture density gauge was thrown from the truck when the truck flipped over. The driver was injured and taken to the hospital. The company RSO responded and reported that the gauge remained in its case and the gauge was not damaged. There was no detectable radiation leakage. The gauge is in the possession of the company's RSO who will send it for a leak test tomorrow, 12/05/06. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-12-07
43021 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2006-12-03 08:58 | 2006-12-03 15:20 | 2006-12-14 | ACCIDENT MITIGATION - HIGH PRESSURE CORE SPRAY (DIVISION 3) EMERGENCY DIESEL INOPERABLE "On December 3, 2006, at 0858 hours, control room operators received a Division 3 Emergency Diesel Generator (EDG) Carbon Dioxide (CO2) (Fire Protection) system initiation signal. The CO2 system for the Division 3 EDG room was out of service at the time and so no CO2 was released into the room. At 0905 hours, a first responder notified the control room operators that there was no indication of a fire in the Division 3 EDG room. A walkdown of the associated EDG room ventilation system confirmed the ventilation system tripped with the CO2 initiation signal locked in. At 0919 hours, the Division 3 EDG was declared inoperable and Technical Specification (TS) LCO 3.8.1 Condition B was entered. The required TS actions were implemented. The Division 3 EDG is available with restoration of the ventilation system using the CO2 Override switch. The CO2 initiation signal is currently locked in, and the Division 3 CO2 Fire Monitoring Panel, with associated equipment has been quarantined for further investigation. "The Division 3 EDG provides emergency AC electrical power to the High Pressure Core Spray system. This event is being reported as a condition that could have prevented the safety function of structures or systems required to mitigate the consequences of an accident. The Resident Inspector has been notified." * * * EVENT RETRACTED AT 1324 ON 12/14/06 FROM C. ELBERFELD TO P. SNYDER * * * "The purpose of this call is to retract Event Number 43021. On December 3, 2006, at 1520 hours, a notification, Event Number 43021, was made to the NRC Operations Center by the Perry Nuclear Power Plant (PNPP) in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. A spurious Carbon Dioxide (CO2) Fire Protection system initiation signal resulted in a tripped condition for the Division 3 Emergency Diesel Generator (EDG) room ventilation system. Operators declared the Division 3 EDG inoperable and took the appropriate Technical Specification actions. The Division 3 EDG provides emergency AC electrical power to the High Pressure Core Spray system. The High Pressure Core Spray system is a single train safety system. "After further evaluation, it was determined that operators could promptly restore the ventilation system, with the CO2 initiation signal locked in, if the Division 3 EDG was needed, and that the safety function of the system could still be fulfilled during the time in question. Because the condition reported in Event Number 43021 would not have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident, the condition is not reportable, and this notification is retracted. The evaluation (i.e., Reportability Review) for this condition is documented in Condition Report 06-10843. "The NRC Resident Inspector has been notified." Notified R3DO (Lara). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-12-03
43020 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2006-12-01 11:42 | 2006-12-01 17:06 | 2006-12-01 | LOSS OF THIRTEEN EMERGENCY SIRENS "A loss of power has disabled thirteen of the fifty EP sirens (26%). The sirens were lost at 11:42 CST and have not been restored. "This meets the threshold of reportability based on the loss of a public notification system. "Restoration of power is being scheduled to occur as soon as reasonably possible with the current winter weather conditions. "Both units remain at full power and are unaffected by the loss of power." The sirens do not have a battery backup. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-12-01
43019 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2006-12-01 | 2006-12-01 16:55 | 2006-12-01 | AGREEMENT STATE REPORT - LOST SOURCE "The licensee reported a lost static air gun containing 10 millicuries of Po-210. The source is approximately 1 year old and the licensee believes the source was disposed of while attached to an air hose which was thrown away." The State is continuing its investigation into this event and will provide updated information when it is available. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2006-12-06
43018 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-12-01 06:30 | 2006-12-01 10:12 | 2006-12-07 | LOSS OF EMERGENCY SIRENS "At approximately 06:30 hours CST on December 1, 2006, it was discovered that greater than 25% of the Clinton Power Station (CPS) offsite sirens were out of service. 31 of 44 sirens are not available due to inclement weather. "The licensee has notified DeWitt County Sheriff, Illinois Emergency Management Agency and the NRC Resident Inspector." ** UPDATE FROM JEANS TO KNOKE AT 17:00 EST ON 12/07/06 ** "As of December 7, 2006, there are less than 25% of the offsite sirens out of service (6 total). Repairs are continuing to restore power to the remaining sirens. "The DeWitt County Sheriff, Illinois Emergency Management Agency, and the NRC Resident have been informed of this updated information. "A press release is planned when all of the sirens have been restored." Notified R3DO (Lipa). | 55 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-12-01
43017 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-12-01 06:30 | 2006-12-01 10:03 | 2006-12-01 | LOSS OF PLANT ACCESS "At 0630 on 12-1-06, due to worsening road conditions from heavy snowfall, a determination was made that there is a loss of plant access for some individuals and some impairment of evacuation routes. This meets criteria for an Immediate Notification (8 Hour) per 10 CFR 50.72 (b)(3)(xiii). There is no impact on plant operation. The weather is improving, road crews are working and access concerns should be alleviated during the day today." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-12-01
43016 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2006-11-30 14:45 | 2006-11-30 19:00 | 2006-12-01 | AUXILIARY FEEDWATER PUMP AUTOMATIC START "On November 30, 2006, at approximately 14:45 hours, an Auxiliary Feed Water (AFW) System actuation signal was generated as a result of maintenance activities on the 21 Main Boiler Feed Pump (MBFP). Both motor driven AFW pumps were running at the time and were not automatically started due to previously being placed in service to provide feed water flow to the steam generators. The actuation signal isolated the Steam Generator blowdown Containment Isolation Valves. Both MBFPs were isolated and not feeding the steam generators at the time the actuation signal was generated. The plant was in Mode 3 (Hot Standby) for a forced outage and 21 MBFP was in a maintenance / test condition. The automatic actuation occurred due to the reset oil pressure lowering below the trip set point and initiating an automatic actuation signal." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 12/01/06 AT 0151 EST BY MR. TROULET TO MACKINNON * * * "At 2100 on 11/30/2006, as a result of continuing work activities on the 21 MBFP an AFW System actuation signal was generated. Both motor driven AFW pumps were running at the time and were not automatically started due to previously being placed in service to provide feed water flow to the steam generators. 21 MBFP has been successfully placed in service." The NRC Resident Inspector was notified of this update by the licensee. Notified R1DO (James Dwyer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-11-30
43015 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2006-11-29 10:40 | 2006-11-29 17:48 | 2006-12-01 | AGREEMENT STATE REPORT INVOLVING A LOST TROXLER GAUGE The following information was provided via fax: On November 29, 2006, the NV Health Division Radiological Heath Section was notified by the Las Vegas Water District that a portable moisture density gauge, a Troxler Model 3440, S/N 33786, was lost from the bed of a pickup truck at 10:40AM in Las Vegas, NV. When the loss occurred the gauge was sitting on the open tailgate of the service truck, out of the shipping container and not secured. However, the handle was locked. The Troxler Model 3440 gauge contains two (2) radioactive sources; 8 millicuries Cs-137 and 40 millicuries Am-241/Be. Licensee corrective actions include additional training for gauge operators. NV Event Report ID: NV-06-007 * * * UPDATE PROVIDED BY NEVADA (VERELLEN) VIA FAX TO KOZAL ON 12/01/06 AT 1409 * * * The missing gauge was recovered and returned to the licensee intact on 12/01/06. Notified R4DO (Bywater), NMSS EO (Wastler), and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2006-12-01
43014 | 0 | GENERAL DYNAMICS LAND SYSTEMS |  |  |  |  | 2006-11-28 12:20 | 2006-11-28 16:37 | 2006-11-28 | FIRE/EXPLOSION DURING SERVICING OF M1 ABRAMS TANK TURRET General Dynamics Land Systems services the M1 Abrams Tank at their Joint Systems Manufacturing Center located in Lima, OH. Following approved procedures, technicians removed the outer side armor followed by welders punching two (2) holes into the depleted uranium armor package. When the technician inserted a hydrogen probe, a detonation occurred causing a flame to eject through the holes. The flame struck the technician on his Tyvek coveralls but did not cause any injury. A rad survey of the area confirmed minor contamination inside the armor cavity and on the floor adjacent to the right side of the turret armor cavity. Decontamination of the floor is ongoing, however, the armor cavity will be resealed as a contaminated volume. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 40.60(b)(4) |  |  |  | 0 | 2006-11-28
43013 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-11-27 13:30 | 2006-11-27 16:47 | 2006-11-27 | MOMENTARY LOSS OF SHUTDOWN COOLING DUE TO RHR ISOLATION SIGNAL "On November 27, 2006 Fort Calhoun Station was on shutdown cooling, while in the process of moving the plant from Mode 3 to Mode 4 to fix a leak on an In-Core Instrument (ICI) Grayloc fitting. At 1327 Reactor Coolant Pump RC-3B was secured. At 1330, the last Reactor Coolant Pump (RC-3A) was secured. Once the reactor coolant pumps were secured, spray to the pressurizer was lost. This loss of pressurizer spray caused pressure in the pressurizer to rise; the systems pressure interlock caused HCV-347, Shutdown Cooling Loop 2 Outboard Isolation Valve, and HCV-348, Loop 2 to Shutdown Cooling Isolation Valve to close due to pressurizer pressure being greater than 250 psia. "At 1330 the Control Room entered AOP-19 for a Loss of Shutdown Cooling. The control room operators initiated auxiliary spray, lowered pressure, reopened HCV-347/348, and started Low Pressure Safety Injection Pump SI-1A. At 1342 shutdown cooling was reestablished. At 1352 all conditions to exit AOP-19 were met and the procedure was exited. During the 12 minutes that shutdown cooling was lost the highest pressure reached in the RCS was 254 psia up from 233 psi and the highest temperature was 135 degrees, up from 134 degrees as read on the core exit thermocouples." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Hot Standby; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-11-27
43012 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2006-09-29 13:33 | 2006-11-27 10:35 | 2006-11-27 | INVALID SPECIFIC SYSTEM ACTUATION "On September 29, 2006, at 1:33 pm CDT, a safety-related 120VAC distribution panel was inadvertently de-energized during a planned shift of its power supply. The plant was operating at 100 percent power at the time. The loss of power resulted in the automatic closure of primary containment isolation valves in the reactor water cleanup and the suppression pool cooling/cleanup systems. This event is being reported in accordance with 10CFR50.73(a)(1) as an invalid actuation of the containment isolation valves affecting more than one system. "This event occurred during a planned shift of the inverters that supply the distribution panel. This shift was being performed to support post-maintenance testing of one of the inverters. The operators performing the shift were utilizing the appropriate procedure. At a certain point in the procedure, the off-going inverter was deenergized, and the operators discussed the expected equipment response. Following that discussion, a step was erroneously performed out of sequence, resulting in the loss of power to the 120VAC distribution panel. The primary containment isolation signal was actuated as designed, and the appropriate valves responded correctly. "Reactor power was not affected by the containment isolation signal. The pertinent response procedures were implemented, and actions were taken to restore the distribution panel to service. This was completed at 5:31 pm CDT that day." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-11-27
43011 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-11-25 20:42 | 2006-11-25 22:48 | 2006-11-25 | REACTOR SCRAM FROM FULL POWER DUE TO GENERATOR LOAD REJECT "At 2042 on 11/25/06, Susquehanna Unit 1 reactor automatically scrammed due to an apparent generator load reject. All rods fully inserted, and both reactor recirculation pumps tripped. Reactor water level lowered to approximately +13" inches causing level 3 (+13") isolations, and was restored to normal level (+35") by the feedwater system. All isolations at this level occurred as expected. Five steam safety relief valves opened then reclosed. Pressure was subsequently controlled via turbine bypass valve operation. All safety systems operated as expected. "The 'A' reactor recirculation pump was restarted to re-establish forced core recirculation. Reactor water cleanup (RWCU) system has been restarted and placed in service. The reactor is currently stable in Mode 3. An investigation is underway. "Unit Two continued power operation. "The NRC resident inspector was notified. A press release will occur." Decay heat is being removed by normal feedwater to the reactor vessel and steaming through the steam bypass valves to the condenser. The licensee intends to notify the State of Pennsylvania EOC. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2006-11-25
43010 | -1 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-11-24 19:45 | 2006-11-25 04:14 | 2007-01-18 | UNANALYZED CONDITION "With Prairie Island Unit 2 core offloaded for the 2R24 refueling outage, it was discovered that a potential common cause failure of the 21 and 22 Residual Heat Removal (RHR) Pumps may exist. A non-safety related 120 VAC motor heater circuit from Panel 2RPA3 Circuit 28 supplies power to 21 and 22 RHR Pumps. Investigation continues. The RHR system is not required by the current operating mode. "The RHR Pumps on the operating unit (Unit 1) are supplied from separate 120 VAC panels so the concern does not exist for the 11 and 12 RHR pumps." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY J. STRICKLAND TO KOZAL ON 1/18/07 AT 1322 EST * * * "Event Number 43010 (reported 11/24/06) reported a potential single failure vulnerability of the Unit 2 residual heat removal (RHR) pumps. NMC identified that power cables for the motor heaters in each pump were powered from the same 120 Volt panel and that the heater power cables were routed for some distance in the same conduit. The concern was that an electrical fault could propagate from one RHR pump motor to the opposite train RHR pump motor. Further engineering evaluation has determined that no credible failure mechanism exists that could cause a fault in one RHR pump motor to propagate to the opposite train RHR pump motor. Since the dielectric strength of insulation on the heaters is greater than the dielectric strength of the air between the motor windings and the motor frame or the stator, any fault in the motor windings would be to ground (and, thus, interrupted by the ground fault protective relaying). Therefore, no potential single failure vulnerability existed in the as-found condition and NMC hereby retracts the event reported on 11/24/06 (Event Number 43010)." The licensee notified the NRC Resident Inspector. Notified the R3DO (H. Peterson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-11-25
43009 | -1 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2006-11-23 09:17 | 2006-11-23 10:14 | 2006-11-28 | LOSS OF CONTROL OF SAFEGUARDS INFORMATION Safeguards information found in inappropriate storage location. Compensatory actions taken upon discovery. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector will be notified of this event by the licensee. * * * EVENT RETRACTION FROM JIM SPEICHER TO JOE O'HARA AT 1639 ON 11/28/06 * * * The licensee has retracted its previous notification of event #43009 dated November 23, 2006. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. Notified R2DO (Ayres) and Safeguards Group via e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-11-23
43008 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-11-16 | 2006-11-22 18:06 | 2006-12-19 | AGREEMENT STATE - WASHINGTON - GAMMA KNIFE OVEREXPOSURE The Washington State Department of Health (DOH) received a preliminary telephone report, November 22, from University of Washington, Harborview Gamma Knife, that a dose of 28 Grays had been administered to a patient. The exposure exceeded the prescribed exposure of 18 Grays by 10 Grays. The cause, thus far, is unknown. DOH is to receive a written report within 15 days. The dose was administered by a Leksell Gamma System Model 24001 Type C gamma knife with 7,236 Curies of Co-60. The patient or responsible relative has been notified. The licensee is required to notify DOH within 24 hours. The notification is apparently several days late. Washington State report number: #WA-06-066 * * * UPDATE PROVIDED VIA EMAIL FROM SCROGGS TO ROTTON AT 1955 EST ON 12/11/06 * * * The State provided the following update information via email: "The cause was stated by the licensee to be human error. The prescribing physician, apparently in a hurry to leave for the day, had prescribed 18 Gy. The physician then entered the Rx value into the computer treatment plan rather than having the medical physicist do it as is the usual procedure. The physician erroneously entered 28 Gy. "The licensee stated the tumor undergoing treatment turned out to be larger than expected consequently the 28 Gy administered remains therapeutic with likely no ill-effects expected as a result of this incident. "The treatment plan has been modified so that a similar event is less likely to occur. The progress of the patient is being closely watched by the licensee. DOH is expecting receipt of a written report from the licensee this week." Notified the R4DO (Smith) and NMSS EO (Janosko). * * * UPDATE PROVIDED VIA EMAIL FROM SCROGGS TO KOZAL AT 1841 EST ON 12/19/06 * * * "The Department has received the licensee's written report of the incident and proposed corrective action. Corrective actions now include a verification process to ensure the correct treatment dose has been transferred from the treatment planning computer to the Gamma Knife computer prior to patient therapy. A plan signed by the treating oncologist, physicist, and neurosurgeon is now required. In addition the treating oncologist and physicist will verify and initial the prescription dose and isodose. Before a patient is treated, the nursing still will confirm: the patient's name/identity; the disease process; the disease site; the prescribed dose; and the prescribed isodose. These actions appear adequate at this time and will be reviewed during the Department's next visit to the facility. "The effect to the individual is unknown at this time. However, it is expected that there will be minimal symptoms related to the larger radiation dose. A longer course of steroids than was initially planned may be prescribed." Notified the R4DO (Whitten) and NMSS EO (Pierson). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-11-28
43007 | 0 | SCHLUMBERGER PTC - NJ |  |  |  |  | 2006-11-22 09:00 | 2006-11-22 14:38 | 2006-11-22 | TRITIUM LOST FROM STORAGE VIAL The licensee reports that while attempting to extract tritium used in manufacturing minatron well-logging tools, it was determined that the tritium supply vial was empty. Four vials of tritium were shipped to the licensee's facility on 9/20/06 and placed in a storage vault until used. The tritium was receipt inspected with no abnormal observation and swiped with no finding of radiological contamination. The vials were also double sealed in plastic bags. The vials are shipped from Ontario Hydro (Canada) and each vial contains approximately 100 curies of tritium. When one of these vials was loaded into the manufacturing process line and the vial opened, no tritium gas was detected. The licensee notes that the vials are shipped at a vacuum relative to atmospheric pressure and the vacuum was still intact in the vial making leakage an unlikely scenario. In addition, the inside of the plastic sealing bags had no evidence of tritium. The licensee is currently trying to contact Ontario Hydro to further its investigation into what happened to the tritium. The licensee has also been in contact with NRC Region 1 (Jackson) concerning this event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-11-22
43006 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-11-22 | 2006-11-22 14:17 | 2006-11-27 | AGREEMENT STATE - COLORADO - LOST CHECK SOURCE The State provided the following information via facsimile: "A licensee, TSA Systems, Ltd., Colorado License #285-01, notified the Department on this date that a 2.1 microcurie Cf-252 source was missing. The source, manufactured by Isotope Products Laboratories, is a Model A3014 with Serial #B2-833. The licensee's representative stated that they continue to search their facility for the source which is used for instrument response checks and calibrations. "No other details are available at this time. The Department has initiated an investigation." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2006-11-27
43005 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-11-21 14:00 | 2006-11-22 11:48 | 2006-11-22 | OUTSIDE OF LICENSE CONDITION FOR INSPECTION OF SERVICE WATER INTAKE STRUCTURE "At 1400 on 11/21/06, V.C. Summer Nuclear Station (VCSNS) determined there was a failure to perform required monitoring of the Service Water intake structure and embankments within the required 5 year frequency. "This is not a requirement of Technical Specifications, but is required by the VCSNS Operating License NPF-12, Section 2.C(5). This license condition requires that the monitoring interval not exceed 5 years. "Monitoring was last performed 12/04/00 with no adverse consequences noted in the evaluation. "Efforts are underway to schedule the required monitoring as soon as practicable. "An extent-of-condition review will be performed to ensure compliance with all aspects of license condition 2.C(5)." The licensee will notify the NRC Resident Inspector. State and local agencies will also be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0 | 2006-11-22
43004 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-11-22 04:26 | 2006-11-22 08:22 | 2006-11-22 | MAIN TURBINE TRIP DUE TO HIGH- HIGH STEAM GENERATOR "B" WATER LEVEL DURING FEEDWATER SWAP OVER. "At 0426 hours on 11/22/06, with the reactor critical and attempting to bring the Main Turbine on-line and shifting from Emergency Feedwater to Main Feedwater, 'B' Steam Generator level increased to the Hi-Hi level (P14) trip set point, resulting in tripping all 3 Main Feed Water Pumps. The reactor did not trip. "All systems functioned as designed and the plant was stabilized." The NRC Resident Inspector was notified of this event by the licensee. | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-11-22
43003 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2006-11-06 | 2006-11-21 14:23 | 2006-12-11 | AGREEMENT STATE REPORT INVOLVING LOST/UNACCOUNTED FOR STATIC ELIMINATORS The State of Minnesota received the following notification from Seagate Technology via letter dated November 6, 2006: "Subject: Loss of Anti-static Nuclear Ionizing Devices [General License Material] "The following anti-static nuclear ionizing devices described below were due for return to the vendor, but could not be found after an extensive search including a written communication requesting assistance from associated work areas across our site. "The devices are: "NRD brand Model P-2063-1200, Nuclear Ionizer Fan Element, 31.5 millicuries of Polonium-210 per device "Serial Numbers A2ER777 thru A2ER785 [nine total], manufactured 9/22/2005." * * * UPDATE ON 12/11/2006 AT 1013 FROM CRAIG VERKE TO MARK ABRAMOVITZ * * * The sources were found on 12/7/2006 in a locked storage cabinet. The sources will be returned to the distributor. Notified the R3DO (Lara), NMSS (Morell), Sandler [ILTAB] THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2006-11-24
43002 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-11-21 06:15 | 2006-11-21 06:31 | 2006-11-21 | UNUSUAL EVENT DECLARED DUE TO UNIDENTIFIED LEAKAGE Licensee reported 20 GPM of unidentified leakage from indication of VCT lowering level. RCS pressure is 50 psig. Source of the leak has not been identified and it is not known at this time where the RCS leakage is going. All air and liquid releases are within specifications and no protective action recommendations are needed at this time. The licensee has notified the State and Local emergency agencies. The licensee will notify the NRC Resident Inspector. * * * UPDATE PROVIDED BY BEN HUNT TO JEFF ROTTON AT 0714 ON 11/21/06 * * * Unidentified leakage is now calculated to be 2 GPM based on inventory balance using charging and letdown flow and VCT level. It is believed that the indication of a leak may be from an incomplete vacuum fill of the S/G after the S/G replacement modification and when the RCS was pressurized, the remaining voids in the S/Gs were filled. There has been no visible leakage found outside of the RCS. Notified NRREO (Wermiel), R2DO (Haag), IRD Manager (Wilson / Leach). * * * UPDATE AT 0756 ON 11/21/2006 FROM BEN HUNT TO MARK ABRAMOVITZ * * * The licensee terminated the Unusual Event (UE) at 0737 due to indicated RCS leakage being less than 2 GPM. The site's emergency action criteria for a UE is 10 GPM unidentified leakage. No water has been found to have leaked outside the RCS. The licensee notified the NRC Resident Inspector. Notified NRREO (Wermiel, Ross-Lee), R2DO (Haag), IRD Manager (Wilson, Leach), DHS SWO (Gray), FEMA (LaForty) * * * UPDATE PROVIDED BY DOUG HOLT TO JEFF ROTTON AT 0959 ON 11/21/06 * * * "The cause of the apparent leakage is under investigation by plant and TVA personnel. No actual leakage is believed to have transpired. Current plant conditions are stable." The licensee notified the NRC Resident Inspector. Notified R2DO (Haag), NRREO (Ross-Lee), IRD Manager (Wilson) * * * UPDATE AT 1215 EST ON 11/21/06 FROM DOUG HOLT TO S. SANDIN * * * "As a result of the declaration of a Notification of Unusual Event earlier today relative to a suspected RCS leak, a News Release is being made. The purpose of the release is to clarify to local officials and residents the nature of the suspected leak and the actions taken by school officials. The cause of the suspected leak remains under investigation." The licensee notified the NRC Resident Inspector. Notified R2DO (Haag). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2006-11-21
43001 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2006-11-17 | 2006-11-20 16:20 | 2006-11-20 | LOSS OF CONTROL OF RADIOACTIVE MATERIAL The State provided the following information via email: "The Radiation Safety Officer (RSO)/owner of Rio Grande Radiological Physics Group, LLC (NM license number RS433-01) reported at 7:51 a.m. on November 20, 2006 that he had lost control of a 108 microCurie Cs-137 sealed source and a Co-57 sealed source (decayed down to background levels of radiation). The RSO/owner is a medical physicist and had returned home late Friday night, November 17, 2006, from a trip in which he had provided radiological services to a contracted facility. As he unloaded his equipment at his residence, he placed the two sealed sources that were in lead containers, on a gate or tailgate and proceeded to move his equipment into his residence. "He apparently left the two sources behind. The sources landed up in the possession of one of his neighbors. On Saturday, November 18, 2006, the neighbor participated in an activity at the state fair grounds in Albuquerque, NM and had the sources in his vehicle. The sources ended up being placed on the ground in a parking lot where they were found. An emergency response was initiated with NM State Police, NM National Guard, and a DOE RAP Team from Sandia National Laboratory responding. DOE Sandia took possession of the sources and safeguarded them. "The RSO contacted the FBI on Sunday, November 19, 2006 and reported the incident. He is meeting with an FBI agent and a Radiation Control Bureau inspector today. New Mexico Radiation Control Bureau personnel are currently investigating the incident and the two sources are in the process of being returned to the licensee by Bureau personnel. Details will be provided as they develop and are made available." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2006-11-23
43000 | 0 | 3-M COMPANY - ST. PAUL, MN |  |  |  |  | 2006-11-01 12:00 | 2006-11-20 15:43 | 2006-11-20 | LOST TRITIUM FOIL SOURCE A licensee representative reported that a 600 milliCurie tritium foil source (SSDR IL8138D802S) has been lost from a static measuring device (Tritium Static Wand). The source was discovered to be missing when the device was determined to not be operating correctly. The licensee is uncertain how the tritium source may have fallen out of the device. When the source is missing the device continues to operate providing a low static reading such that it would not be obvious that the source was no longer present or that the device is not functioning properly. The device is not routinely calibrated. The device was shipped to the facility about 2 months ago from the 3-M St. Paul, MN, facility and was verified to contain the source when shipped. The licensee has searched likely facility locations where the source could be located including trash and scrap. The licensee plans on notifying the State of Indiana and the Region 3 Inspector. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-11-20
42999 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-11-16 | 2006-11-20 12:24 | 2006-11-20 | AGREEMENT STATE - STOLEN TRUCK CONTAINING RADIOPHARMICEUTICALS The State provided the following information via email: "DRH [Department of Radiation Health] received notification on 11-17-06 from Cardinal Health about a delivery vehicle that was car-jacked at a gas station located in Jackson, MS. The driver was driving a Ford Ranger delivery truck that was carrying approximately 540 millicuries of Technetium-99m. The vehicle was delivering radiopharmaceuticals to area hospitals and clinics. At the time of the report to DRH, the doses had already gone through 3 half-lives of decay. As of Monday 11-20-06, the vehicle has not been recovered." The State notified Flowood, MS and Jackson, MS police departments, Mississippi Emergency Management Agency (MEMA), and the FBI. Mississippi State report number: MS 06014 * * * UPDATE FROM MISSISSIPPI (B.J. SMITH) TO HUFFMAN VIA E-MAIL AT 1629 EST ON 11/20/06 * * * "Vehicle recovered by Jackson Police Department 11-20-06 at about 2:00 PM CST. Ammo boxes [shipping containers] were not tampered with and all material recovered. Security seals were still attached." R4DO (Campbell), NMSS EO (Camper) and ILTAB (via e-mail) have been notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2006-11-23
42998 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-11-09 14:44 | 2006-11-17 15:48 | 2006-11-17 | EMERGENCY DIESEL GENERATOR ACTUATION DURING TESTING "At 1444 on 11/09/06, after initial installation of the Alternate AC power source, post modification testing was being performed in accordance with STP-125.021, requiring an abnormal lineup of the 'B' diesel generator (DG). Prior to starting the test, potential unforeseen conditions were discussed, but not documented in STP-125.021. During the test, 'B' DG was secured and returned to the standby mode. As individual loads were manually loaded on the 1 DB bus, bus voltage momentarily decreased. When the 'B' emergency feedwater pump was loaded, an undervoltage condition on 1 DB existed momentarily, starting the 'B' DG. The 'B' Engineered Safety Features Actuation System load sequencer had been de-energized prior to the test as required by STP-125.021. The 'B' DG did not tie onto the 1 DB bus since the load sequencer was de-energized. Voltage on the 1 DB bus was restored by the Alternate AC source, which was supplying the bus for testing. All loads were successfully loaded on the 1 DB bus and the test was satisfactorily completed. "After further review and evaluation, SCE&G considers the actuation of 'B' DG, while undergoing post modification testing of the Alternate AC power source, reportable under 10CFR50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector and will also notify State and local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-11-17
42997 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-11-15 21:30 | 2006-11-16 08:54 | 2006-11-17 | MISSING WELL LOGGING TOOL At 2130 CST on 11/15/06, Schlumberger reported that a well logging tool was missing from the truck transporting the tool. The tool contained 1.5 curies of Tritium in a neutron target. It appears that the tool was lost or fell from the truck along a 50 mile portion of County Road 3169 in Zapata County, TX. A search for the tool is in progress. * * * UPDATE VIA E-MAIL FROM TEXAS (JISHA) TO HUFFMAN AT 1630 EST ON 11/16/06 * * * "At 2130 on Nov 15, 2006, a third party transport driver noted that he was missing a well logging tool that contains a neutron generator. The tool appears to have fallen off the truck along a fifty mile stretch of county road 3169 in Zapata county. The neutron generator contains 1.5 curies of tritium that is impregnated into the target of tube and is sealed within the tube and tool. No radiation is emitted by the generator and no public exposure is expected. "Schlumberger personnel are searching the fifty miles of road and if the tool is not located on the first search, the Zapata county sheriff's office will be contacted. The search will continue at daylight. Additional notifications have been made to the Nuclear Regulatory Commission (NRC), U.S. Department of Transportation (DOT), and State Operations Center (SOC). The tool is a model 7158 manufactured by Schlumberger and is ~10 feet in length with an outside diameter of one and 11/16 inches. The device is made of stainless steel and has few markings on the exterior surface. The external surface of each neutron generator target is engraved with a target assembly I.D. number consisting of year-month-day (date of construction) and target position and the sequential serial number assigned to the neutron generator. After tritiation, the neutron generators have the model number (758, 761, or 762) and 'Radioactive H3' etched or engraved on the annulus of the end Kovar piece at the pinchoff end. The remaining annular space is taken by a second engraving of the serial number. "Specific Item Missing: 1 11/16 inches OD logging tool continuing neutron generator approximately 108 inches (9 feet) long. The tool is made of steel and is cylindrical. Neutron Generator: Schlumberger Model 7158 covered by SSDR NR-316-D-101-S-1 (attached), Serial Number, 5710 Activity and Nuclide: 1.5 curies of tritium "Description: Tritium is impregnated in a metal target contained within a sealed tube. The tube is sealed within an electronic housing (PNG-1032) and this electronic housing is contained with a well logging tool that is sealed and pressure rated to 15,000 psi." The generator only produces neutron radiation when high voltage is applied. R4DO (Johnson) and NMSS EO (Camper) notified. ILTAB notified via e-mail. * * * UPDATE VIA E-MAIL FROM TEXAS (JISHA) TO GOTT AT 0831 EST ON 11/17/06 * * * On 11/16/06, the licensee found the tool with the source intact, and it is reportedly at their Laredo facility. Notified R4DO (C. Johnson) and NMSS (G. Morell) and emailed to ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-11-18
42996 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-11-16 02:26 | 2006-11-16 03:57 | 2006-11-16 | REACTOR TRIP "At 0226, North Anna Power Station Unit 2 automatically tripped on steam flow greater than feed flow with low steam generator water level on 'B' Steam Generator. This was caused by a Steam Flow Channel (Channel 3) Low failure. After the reactor trip, Auxiliary Feedwater Pumps automatically started on Low-Low Steam Generator Level." All control rods fully inserted. RCPs are in operation transferring decay heat to the steam generators. The steam generators are discharging steam to the main condenser using the condenser steam dumps. Main feedwater pumps are running to maintain steam generator water levels. Unit 1 was not affected. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-11-16
42995 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2006-11-16 00:18 | 2006-11-16 03:02 | 2006-11-16 | REACTOR TRIP DUE TO TURBINE TRIP AND DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION OF AN UNSUAL EVENT At 0018 Calvert Cliffs Unit 2 experienced an automatic reactor trip due to a turbine trip. "At the time a clearance order was being performed for upcoming maintenance on P-13000-2 [transformer]. As a result of the turbine trip, RCS pressure rose to approximately 2420 psia causing the PORV's to open. Unexpectedly, a Pressurizer Safety Valve, RV-200 also lifted and reclosed when RCS pressure was lowered to approximately 1500 psia. As a result of the pressure decrease, a Safety Injection Actuation Signal (SIAS) occurred. Once the Pressurizer Safety Valve reclosed, RCS pressure began to rise to return to normal values. "Decay heat is being removed via normal methods through the Turbine Bypass Valves to the Condenser. "Normal Feedwater is being used. No Auxiliary Feedwater actuation occurred. "Two Reactor Coolant Pumps were secured as a result of the SIAS. The plant responded normally to the event. The plant is currently stable and operators are conducting a plant cooldown to mode 5." All control rods fully inserted. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM C. MORGAN TO W. GOTT AT 1039 ON 11/16/06 * * * The automatic trip was due to high RCS pressure from the closure of the Turbine Intercept Valves. Both PORV's opened as designed. One remained open approximately 1.5 minutes causing RCS pressure to reduce to 1500 psia. The PORV should have closed at 2400 psia. Relief Valve 200 (RV-200) did not open as previously reported and was not the cause of the RCS pressure lowering. Acoustic monitoring indication were due to the close proximity of the PORV. Since the SIAS signal did not cause a reportable ECCS actuation, the reported 50.72(b)(2)(iv)(A) ECCS Actuation is retracted. The licensee notified the NRC Resident Inspector. Notified R1DO (P. Henderson). * * * UPDATE FROM C. MORGAN TO W. HUFFMAN AT 1200 EST ON 11/16/06 * * * Upon further review, the licensee has determined that this event met the criteria for Unusual Event Emergency Action Level (EAL A.U.2.2.1) for identified RCS leakage greater than 25 gpm. The licensee met this criteria for the duration that the PORV valve remained open (less than 2 minutes). The licensee did not recognize that it had met the criteria at the time of the event and is reporting this as an after-the-fact emergency condition of unusual event per the guidance in NUREG-1022. The licensee notified the NRC Resident Inspector. Notified R1DO (P. Henderson), NRR EO (Ross-Lee), and IRD Manager (Leach). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-11-16
42994 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-11-16 00:09 | 2006-11-16 01:38 | 2006-11-16 | SPDS UNAVAILIBLE DUE TO PLANNED MAINTENANCE "The Safety Parameter Display System and ERDS will be out of service for approximately 4 hours for scheduled maintenance. SPDS and ERDS parameters will be monitored by Control Board indications. Work will be continuous until SPDS/ERDS are returned to service. Alternate assessment and communication measures are available to compensate for these temporary impairments. "This is an 8-hour reportable event per 10 CFR 50.72(b)(3)(xiii) Major Loss of Assessment Capability. Cooper Nuclear Station is currently in a scheduled refueling outage. The operation of Cooper Nuclear Station is not affected by this planned maintenance." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-11-16
42993 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2006-11-15 14:00 | 2006-11-15 16:26 | 2006-11-15 | AUTOMATIC REACTOR TRIP DURING ELECTRICAL MAIN GENERATOR TROUBLESHOOTING "On November 15, 2006, at 14:00 hours, an automatic reactor trip occurred during troubleshooting of the Main Generator Exciter Generrex power supply, when an electrical spike resulted in a turbine trip which caused a reactor trip. All control rods fully inserted and safety equipment operated as expected. The Auxiliary Feedwater (AFW) System actuated as expected as a result of a low steam generator level from the reactor trip and started the motor driven AFW pumps. The Emergency Diesel Generators did not start as offsite power remained available. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There were no radiation releases. The condition is under investigation and a post trip review is being conducted." No PORVs or SG safety valves lifted during the event. The electrical plant is in a normal shutdown lineup and the EDGs are operable in standby. There was no affect on Unit 3 operation due to this event. The licensee notified the NRC Resident Inspector, and stated that IPEC communications has transmitted an IPEC Status Report which provides a status to local, state, and federal agencies. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-11-15
42992 | 0 | PRINCETON UNIVERSITY |  |  |  |  | 2006-11-13 09:00 | 2006-11-15 13:45 | 2006-11-15 | LEAKING SR 90 SOURCE In the process of conducting the semiannual leak tests for sealed sources, a leaking Sr- 90 source was discovered on 11/13/2006. The Sr-90 source is used by the Physics Department in Room 365 of Jadwin Hall. The Sr-90 source has an activity of 180 microcuries and is normally stored in Room 361 of Jadwin Hall. The source actually consists of a foil on which Sr-90 has been electroplated. The foil is situated in a brass cylinder that consists of two cylindrical pieces - the piece in which the foil sits and a collimator end that is usually screwed onto the end containing the foil. When the leak test was conducted 6 months ago, there was no leakage. But after discovering contamination during the leak test on 11/13/06, it was found that a small hole has been punched through the foil so that the foil's integrity is compromised. The last time the source was used was approximately 6 weeks ago, so the damage occurred sometime between May and the end of September. Contamination (less than 150 dpm) has been found on spots on the floor in Room 361 of Jadwin Hall where the source is usually stored. Contamination has been found on a variety of surfaces on which the brass cylinder was set. A very rough estimate of the amount of missing activity is believed to be approximately 25% of the original activity. No contamination has been found in public spaces. Surveys have been conducted for the two hallways that border the labs in which the source is used (Room 365) and stored (Room 361). Surveys have been conducted in the office of the sole research staff member who uses the source, and the lab in which the source is stored (Room 361). Results from the survey of the hallways and the office show no contamination problem exists in those areas. The wipes from the lab surveyed on 11/14/06 will be available on 11/15/06, but the G-M survey reveals no gross activity other than in the cabinet in which the source is stored and on the floor directly in front of the cabinet. Those areas were readily decontaminated. On 11/15/06, surveys will be conducted in the lab in which the source is actually used (Room 365). Preliminary surveys on 11/14/06 indicated a number of surfaces that are contaminated in that room, and more thorough surveys will be conducted. All suspect areas have been locked and posted. No personal contamination has been discovered. The person who used the source is out of the area and will provided a urine sample when they return. The licensee expects that decontamination will be complete by 11/16/06 and the rooms will have access restored. Licensee has notified NRC R1 (Modes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2006-11-15
42991 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-11-14 16:42 | 2006-11-14 20:02 | 2006-11-14 | EMERGENCY SIREN ACTIVATION CAPABILITY INOPERABLE FOR APPROXIMATELY 15 MINUTES "At 1642 hours on 11/14/06, activation capability was lost to all ENS sirens due to the malfunction of a radio repeater. Plant personnel secured the affected repeater and control was automatically transferred to one of the four remaining functional repeaters. The siren system has been satisfactorily tested. The total siren outage time was approximately 15 minutes. This event has been entered into the station corrective action program for evaluation." State and Local Officials were notified of this event by the licensee. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-11-14
42990 | 0 | NASA AMES RESEARCH CENTER |  |  |  |  | 2006-11-13 12:00 | 2006-11-14 19:15 | 2006-11-14 | MISSING SOURCES While licensee was conducting their semi-annual inventory of sources they discovered that two sources were unable to be located. One source, 13.9 milliCuries of Ni-63, was believed to be a double entry in the inventory log, however, that is not confirmed at this point. A second source, 10.4 microCuries of Am-241, is also missing. The RSO has been notified. The licensee is continuing to search for the missing sources. A meeting was held by the licensee to review their inventory control procedures and see how this can be prevented in the future. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | CA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-11-14
42989 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-11-07 15:26 | 2006-11-14 18:55 | 2006-11-14 | ACTUATION OF AN OFFSITE EMERGENCY SIREN "At 1526 on 11/07/2006 the BFN (Browns Ferry Nuclear) Shift Manager was notified by the Operations Duty Specialist (ODS) that siren 32 in Morgan County had to be disabled due to alarming for no reason. It was later determined that this event was identified by an outside citizen who notified Morgan County personnel and @ 1550 on 11/10/2006 that Corporate TVA personnel notified the State of Alabama of the status of the alarming siren. The late reporting has been entered into the corrective action program and discussed with the NRC Resident. "This event is reportable an a 4-hour Non-Emergency Notification 10CFR50.72 (b)(2)(xi) as 'Any event resulting in notification to other government agencies that has been or will be made.' " The NRC Resident Inspector was notified of this event at 1340 CDST on 11/14/2006. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-11-14
42988 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2006-11-12 12:45 | 2006-11-13 16:03 | 2006-11-17 | AGREEMENT STATE REPORT FROM ALABAMA - STOLEN TROXLER MOISTURE DENSITY GAUGE Information was received via facsimile "SUBJECT: Stolen Gauge Containing Radioactive Material - Alabama Event 06-46 "On the morning of November 13, 2006 at 8:00 am, (deleted) of Building and Earth Sciences, Inc. notified the Alabama Office of Radiation Control Duty Officer that a Troxler Model 3430 moisture density gauge was stolen from the back of pickup truck that was parked at a commercial storage location in Albertville, Alabama. Building and Earth Sciences, Inc. is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 1266. Preliminary information indicates that the gauge was discovered stolen approximately 1:30 pm on the afternoon of November 12, 2006. (Deleted) indicated that the Albertville Police Department had been notified and responded to the incident. The gauge was believed stolen sometime between 12:45 pm and 1:30 pm on November 12, 2006. The stolen gauge was identified as a Troxler model 3430, serial number 37367 with 8 millicuries of Cs-137, and 40 millicuries of Am-241:Be. (Deleted) indicated that a number of other items were stolen from the victim including three motorcycles and an air compressor. "This information is current as of 3:00 pm CDT - November 13, 2006." * * * UPDATE PROVIDED BY ALABAMA (TURBERVILLE) TO KOZAL VIA FAX ON 11/17/06 AT 0848 * * * "On the morning of November 16, 2006, [Deleted] of Building and Earth Sciences,. Inc, notified the Alabama Office of Radiation Control that the Albertville Police Department had found the Troxler model 3430 moisture density gauge that was stolen from the licensee on November 12, 2006. Building and Earth Sciences, Inc is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 1266. The police department was given as anonymous tip and found the device in its transport container located in an abandoned lot in Albertville, Alabama. [Deleted] surveyed the device and found radiation levels were acceptable. An inspection of the device confirmed that this was the device stolen from the licensee on November 12, 2006. It was noted that someone had poured bleach on the unit. This appeared to be the only damage to the unit. [Deleted] took possession of the unit and was advised to perform a leak test of the unit before placing it back in service." Notified R1DO (Henderson), NMSS EO (Camper), R1 (White) via-email and ILTAB (Sandler) via-email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2006-11-16
42987 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-09-20 | 2006-11-13 09:50 | 2006-11-13 | AGREEMENT STATE REPORT - ABANDONED SOURCE The state provided the following information via fax: "Precision Energy Services abandoned a 2 Ci source of Cs-137 (serial number 06926B) down a hole at a depth of 3064 feet. The tool string got stuck on September 20, 2006. The first attempt to retrieve the stuck tool string succeeded in retrieving the Am/Be neutron source but also caused the tools to break apart. The section of the tool string with the Cs-137 source was stuck at a depth of 3064 feet. Red-dyed cement plug was set with open-ended drill pipe at 3060 feet to 2860 feet. Production casing was run and cemented at 2850 feet, with float shoe, 41 feet of cement filled shoe joint, and float collar. The deflection device was dropped on the float collar and 20 feet of red-dyed cement was dumped on the device on November 1, 2006. An identification plaque will be placed on the well." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-11-16
42986 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-11-11 12:43 | 2006-11-11 16:31 | 2006-11-11 | REACTOR SCRAM DUE TO CONDUCTIVITY EXCURSION "At 1243 EST, during startup activities, a manual reactor scram was inserted as a result of high conductivity in the condenser. It is believed that the high conductivity was the result of a condenser tube leak. Upon receipt of the conductivity excursion alarm, abnormal operating procedures were consulted and the manual scram was inserted. Unit 2 was at approximately 1 percent of rated thermal power and reactor pressure was approximately 100 psi. At the time of the conductivity excursion, the condensate system was not in service and, as such, reactor water chemistry was not adversely affected. All safety systems operated per design. No emergency core cooling systems (ECCS) actuated. "Unit 2 will be taken to mode 4 and the necessary repairs will be completed." All control rods inserted as expected. The licensee believes there is no spread of high conductivity to adjacent systems (e.g. CRD and the CST). Confirmatory samples are in progress. Decay heat is being removed by RCIC in the pressure control mode with the intention of placing shutdown cooling in-service. The electrical system is in a normal shutdown lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-11-11
42985 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-11-11 05:30 | 2006-11-11 06:46 | 2006-11-11 | UNUSUAL EVENT DECLARED DUE TO AN ELECTRICAL FIRE INVOLVING HEAT TRACE At 0530 CST, CNS declared an Unusual Event per EAL 5.1.1 "Any fire within the Protected Area which takes longer than 10 minutes to extinguish," due to a fire involving the Standby Liquid Control (SLC) heat tracing. Operators in the control room received a report from the Refueling Floor that heat trace installed on piping of the SLC System in Reactor Building 976 East was "arcing & sparking." Responders on-scene extinguished the fire after de-energizing the heat trace by opening the associated electrical feeder breaker. All personnel are accounted for and there are no reported injuries. The licensee will conduct a comprehensive review to determine the extent of damage. The SLC System is a TS required safety system but is not required for current plant conditions. No other safety-related equipment was affected. The licensee is not augmenting staff in response to this event and no offsite assistance was requested. The licensee informed State and local agencies and the NRC Resident Inspector who is enroute to the site. * * * UPDATE AT 0733 EST ON 11/11/06 FROM STEVEN JOBE TO S. SANDIN * * * The licensee terminated the Unusual Event at 0558 CST on 11/11/06 based on the judgment of Station Management since the extent of condition is well understood, the affected electrical circuit is isolated and that no reflash watch is necessary. The licensee informed State and local agencies and the NRC Resident Inspector. Notified R4DO (Clark), EO (Bateman), IRD (Wilson), DHS (Gomez) and FEMA (Sweetser). * * * UPDATE AT 0942 EST ON 11/11/06 FROM ED McCUTCHEN TO S. SANDIN * * * The licensee will be issuing a press release regarding this incident and has informed the NRC Resident Inspector. Notified R4DO (Clark). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2006-11-11
42984 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-11-10 | 2006-11-10 18:28 | 2006-11-11 | SHIPMENT OF IODINE - 125 SEEDS LOST IN TRANSIT The State provided the following information via email: "On November 10, 2006, [a representative] of Bard Brachytherapy, Inc. (IL-02062-01) called to report that they had been advised by their customer, that a package intended for Milton Hospital, Milton, Massachusetts did not make it to its destination. The package had been offered to their courier, Airnet, the previous evening for next morning delivery. Using the company's package tracking system, it was determined that the shipment (DELETED) had been transferred from Airnet, to the American Airlines' O'Hare Airport Air Freight Hub in Chicago, IL., but no record of its departure existed. Physical searches of the airport facility by the carriers' staff did not immediately locate the package containing the radioactive material. The shipment consisted of 2 leaded pigs of I-125 sealed sources. One pig held 73 'seeds' with an activity of 66 milliCuries, the second held 80 'seeds' with an activity of 72 mCi. The two packages had been combined into an 'over pack' with a total activity of approximately 134 milliCi of I-125. The package was identified as a 'limited quantity' package with a dose rate of less than 0.5 milliR/h at the surface of the container. The box was approximately 15x12x12 inches in size. As of 17:30 CST the package remains missing. "The customer, Milton Hospital, notified their local regulatory authority, the Massachusetts Department of Public Health, Radiation Control Program to advise them of the situation. Due to the quantity of I-125 involved, the U.S. NRC Operations Center was advised of this event. As a result, U.S. NRC event number 42984 was assigned. Bard is continuing to work with their courier and the carrier to locate the package. At this time American Airlines believes it is still in possession of the package as it does not show the airbill tracking number (DELETED) as arriving at any of its domestic hubs. The radioactive material involved is encapsulated in medical grade stainless steel and is approximately the size of a 0.5 cm length of pencil lead. It is used as a permanent implant to treat cancer of the prostate. Due to the energy of I-125, it posses a very limited external exposure hazard, and then only at very close distances of less then a foot. [The Bard representative] promised to keep the Agency informed of developments as they occurred by contacting the Agency's radiation duty officer." Illinois Report No: IL060058 * * * UPDATE AT 1755 ON 11/11/2006 FROM D. PERERRO TO M. ABRAMOVITZ * * * The package has been located at the airport in Boston, MA. The package is intact and is being returned to the originator in Illinois. Notified the R3DO (Cameron), NMSS (McConnell), and ILTAB (English via E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-11-15
42983 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-11-10 14:20 | 2006-11-10 17:33 | 2006-11-10 | AUTOMATIC REACTOR TRIP AT LOW POWER "On 11/10/2006 with a shutdown in progress to repair a degraded bearing on the turbine generator, an automatic reactor trip occurred due to a power range nuclear instrumentation (NI) low range - high flux trip. Reactor power had just been lowered to below 10% power (P-10) where the power range (NI) low range trips become active. The bistable for power range NI N-42 had been tripped due to an unrelated failure on 11/09/2006. When P-10 automatically unblocked, a power range NI low range high flux reactor trip was generated. At the time of the trip, reactor power was well below the trip setpoint of 24.5% power. "Following the trip, Main Feedwater Regulating Valve, FW-7A, did not automatically close as required on the reactor trip coincident with Low Tave (554F). The Reactor Operator reported FW-7A was mid-position and attempted to manually close FW-7A. It did not respond. As a result, levels in steam generator A rose to greater than 67%, which initiated feedwater isolation. The feedwater isolation signal tripped the running feedwater pump. With no feedwater pumps running, both Auxiliary Feedwater Pump A and Auxiliary Feedwater Pump B automatically started as required. The High-High steam generator level also resulted in a second reactor trip initiation signal. The Reactor Operator manually controlled Auxiliary Feedwater flow to steam generator A to restore normal level. Following the feedwater isolation, FW-7A fully closed. "Following the trip, MS-201B1, the steam supply to main steam reheater B1 was locally isolated to limit the RCS cool down. This was a previously discussed contingency action. Main steam isolation valves remained open and normal condenser heat sink remained available. "Further investigation as to the cause of the trip is in progress. Recovery actions per normal operating procedures are in progress." The plant was being shut down at a rate of a half percent power per minute at the time of the trip. All control rods fully inserted on the reactor trip and no safety or relief valves lifted. The plant was aligned for the normal shutdown electrical lineup prior to the trip. The temperature on the generator bearing reached a maximum of 190F with trip guidance set at 225F. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-11-10
42982 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2006-11-10 13:15 | 2006-11-10 14:08 | 2006-11-10 | SAFEGUARDS REPORT Actual entry of a person into the protected area who did not meet access screening criteria. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-11-10
42981 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2006-11-09 15:30 | 2006-11-09 21:28 | 2006-11-09 | HYDROGEN ACCUMULATION DUE TO LOSS OF WATER SEAL "On 11/9/06 at 0210 hours the Dry Conversion facility line 1 began starting up. At 0230 hours the fire alarm actuated in the Dry Conversion facility. Upon investigation, AREVA operations personnel discovered at approximately 0240 hours that the Hydrogen detector in the HF [hydrogen fluoride] Recovery room had tripped. Operations personnel immediately shutdown the process system. Operations personnel discovered that there was no water plug in the drain P-trap from the exhaust. Therefore, H2 from the reactor and calciner offgas leaked through the drain into the room with H2 enough to the point of setting off the H2 detector which has a set point of 20% of the LEL [Low Explosive Limit]. Hand held readings were taken and determined to be approximately 7% of the LEL at the lower elevation in the room to 25% of the LEL near the ceiling of the room. "AREVA operations personnel contacted Environmental Health and Safety to determine the safety significance of the event. After reviewing the ISA for this system, EHS&L personnel deemed at approximately 1530 hours that the analysis of this system configuration meets the 24 Hour Reporting Criteria, 'Any event or condition that results in the facility being in a state that was riot analyzed, was improperly analyzed, or is different from that analyzed in the ISA and which results in failure to meet the performance requirements of 10CFR 70.61.' "Evaluations determined that it is possible that enough H2 gas could have filled the room to cause an explosion in the HF Recovery room potentially causing a rupture of the HF holding tanks and piping. If an operator were present (this room is occupied approximately 5 to 10 times a week for 10 to 15 minutes each time) at the time of the explosion, it would be possible for the operator to receive sufficient injuries from HFA exposure to potentially make this an intermediate or high consequence event. "Although this system has an H2 detector which, actuates a fire alarm, it is not designated as an IROFS. "The process equipment associated with this scenario is still shut down and will remain shut down pending establishment of sufficient IROFS to meet the performance criteria of 10CFR 70.61. All other systems with the potential for H2 gas leaks are being re-evaluated to ensure that the performance criteria of 10CFR 70.61 is met. "The material in the identified system that is in the tanks that could spill onto an operator is HF solution with trace amounts of Uranium. "Safety significance is low. The HF Recovery, room is not normally occupied during operation, and then for only short periods of time (this room is occupied approximately 5 to 10 times a week for 10 to 15 minutes each time). There is no potential of an accidental nuclear criticality in the as found condition. "The process equipment associated with this scenario is shut down and will remain shut down pending establishment of sufficient IROFS to meet the performance criteria of 10CFR 70.61. Related process systems that might have a similar potential are under evaluation to ensure that the same potential does not exist in these areas." The licensee will notify NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2006-11-09
42980 | 0 | DANVILLE REGIONAL MEDICAL CENTER |  |  |  |  | 2006-11-08 10:10 | 2006-11-09 16:02 | 2006-11-09 | POTENTIAL LEAKAGE FROM A I-125 SEED Six cartridges of I-125 seeds were received on 11/6/2006. During the inspection of the cartridges, a bent seed was found and removed from one of the cartridges. One additional cartridge was inspected by removing the seeds and reloading the cartridge. The remaining cartridges were visually inspected. No contamination was found on any of the cartridges. The seeds were implanted in a patient at approximately 10:00 on 11/8/2006. After the procedure, residual activity was found on one of the cartridges. A urine assay on the patient was performed and a low level of activity was found (about four times background). A spectrographic analysis confirmed the activity as I-125. The licensee is performing a dose assessment. The seed manufacturer was notified and stated that they would notify the state of Illinois. Source information: Manufacturer: Bard of Carol Stream, Illinois. Model: STM1251 Lot #I60539B03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | HOS | [5 empty] | 0 | 2006-11-15
42979 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2006-11-09 05:00 | 2006-11-09 14:25 | 2006-11-09 | FAILURE OF WARNING HORNS "At 0500 on 11/09/06, during a routine monthly test of the Criticality Warning System (CWS), a segment of the system covering the Dry Conversion Process (DCP) was found to have no functioning evacuation horns. Appropriate personnel were notified, the DCP processes were shut down, DCP personnel evacuated, and the area cordoned off. The activation of the evacuation horns in the balance of the plant were fully functional. "A follow-up test was immediately scheduled for 0900. The building was evacuated and the emergency organization assembled in accordance with normal procedures. During this test, the DCP horns again failed to function. "The Emergency Director determined that the processes stay shut down and all personnel remain out of the area while investigations and testing were conducted. "The problem was located in the interface between the Data Acquisition Modules (DAM's) and the Auto-Call system that initiates the alarm signals. After a repair was completed, a re-test was completed which confirmed functionality of the DCP process area horns. "Current plans are to resume normal operations beginning with the 1500 (evening) shift. "This event is being reported within 24-hours pursuant to 10CFR70.50(b)(2) as a safety equipment failure." The licensee will notify NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2006-11-09
42978 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-11-09 06:44 | 2006-11-09 13:22 | 2006-11-09 | HIGH PRESSURE CORE SPRAY SYSTEM VALVE INADVERTENTLY DE-ENERGIZED "At 0644 hours (CST), the Main Control Room (MCR) received an alarm that the Division 3 Shutdown Service Water (SX) system was not available. The MCR also received an indication that a Division 3 SX motor operated valve for the plant service water to the SX header isolation valve, 1SX014C, was not available and discovered that there was no light indication for this valve. This valve is required to reposition following a High Pressure Core Spray (HPCS) system initiation. With the loss of power to the valve, this resulted in the Division 3 SX and the HPCS systems being inoperable. Since the HPCS system is a single train safety system, this event is reportable under 10CFR50.72(b)(3)(v)(D). An investigation is underway to determine the cause of the loss of power to the 1SX014C valve, however, preliminary indications are that an individual may have inadvertently bumped the breaker to the 'off' position. "At 0742 hours, the investigation of the 1SX014C breaker indicated that the breaker was in the 'off' position (i.e., not tripped). The cubicle door for the 1SX014C breaker was opened. There were no abnormal or unusual indications in the cubicle. The 1SX014C valve was verified open; then the 1SX014C breaker was closed. The breaker was taken directly to the close position and not reset first. The 1SX014C breaker closed, indication returned to the MCR, and the alarm cleared. The breaker remained closed and HPCS system was returned to an available status. "At 1047 hours, the Division 3 SX pump was started to confirm that operability of Division 3 SX and HPCS were restored by the actions taken to reclose the breaker at 0742 hours. The 1SX014C valve operated normally and Division 3 SX and HPCS were declared operable. "The NRC Resident has been notified." | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-11-09
42977 | 0 | THE VALLEY HOSPITAL |  |  |  |  | 2006-11-08 | 2006-11-09 10:30 | 2006-11-28 | IMPLANTATION SEED FOUND IN MEDICAL WASTE BAG A single Cs-131 implantation seed (2.66 milliCuries as of 9/25/06) was found in a medical waste bag which had not yet left the hospital. All applicable areas were surveyed and no radioactive contamination was found. The licensee is performing a leak test of the seed and will forward the results. The hospital is performing an investigation into the incident. * * * UPDATE FROM K. CHAK TO W. GOTT AT 1037 ON 11/28/06 * * * The licensee completed the leak test - negative results, and properly disposed of the seed. The licensee is taking corrective actions to prevent its recurrence. Notified NMSS (S. Wastler) and R1DO (J. Dwyer) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | NJ | HOS | [5 empty] | 0 | 2006-11-09
42976 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2006-11-08 22:54 | 2006-11-09 04:33 | 2006-11-09 | FAILURE OF CONTROL ROOM HVAC TO MAINTAIN CONTROL ROOM TEMPERATURE "At 22:54 hours on November 8, 2006, the B Control Room HVAC Refrigeration and Condensing Unit (RCU) failed to maintain proper Control Room temperature and cycling excessively. The RCU is a single train system and therefore is reportable per 10CFR50.72(b)(3)(v)(D). The RCU is required to operate during a design basis accident to maintain Main Control Room habitability/temperature. The Air Filtration Unit (AFU) of CREVS remains operable. This places unit 2 in a 30 day LCORA per Tech Spec 3.7.5 Required Action A.1." The licensee notified the NRC Resident Inspector. | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-11-09
42975 | -1 | WILLIAM BEAUMONT HOSPITAL |  |  |  |  | 2006-11-07 13:45 | 2006-11-08 17:39 | 2007-01-12 | MEDICAL EVENT - LESS THAN PRESCRIBED DOSE OF YTTRIUM - 90 The Radiation Safety Office for the licensee reported an event where a patient received less than the prescribed dose during a treatment for liver cancer using Yttrium - 90 microspheres. Specifically, the patient was prescribed 9.8 millicuries to the liver using Yttrium - 90 SirTex Sirspheres using a intrahepatic catheter. The patient only received 6.5 millicuries due to problems in the administration of the dose. After administering about half of the treatment dose, the physician started to encounter injection resistance which is not uncommon with this treatment due to vasculature loading. The physician stopped the treatment and was trying to view the microsphere placement in the liver using fluoroscopy when he noted some unusual "clumping" of the microspheres between the delivery vial and a 3-way stop cock that connects to the catheter. Because of the clumping and the resistance, the physician elected to discontinue the administration of the remainder of the dose. The licensee has contacted SirTex and plans to send the delivery device with the clumped microspheres to SirTex when the Yttrium - 90 has decayed away (in a couple weeks) for further evaluation of the product. The licensee has also contacted the Region 3 NRC inspector (Piskura) about this event. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. *** UPDATE FROM SCHULTZ TO KNOKE AT 14:29 ON 01/11/07 *** The RSO called to indicate this event was reviewed by Region 3 and was determined to not meet the criteria for a reportable event, therefore the event is being retracted. Notified R3DO (Kozak) & NMSS (Janet Schlueter). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-11-10
42974 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-11-08 11:06 | 2006-11-08 14:30 | 2006-11-08 | SPECIFIED SYSTEM ACTUATION - EMERGENCY DIESEL GENERATOR AUTO START "On November 8, 2006, at approximately 11:06 Central Standard Time (CST) a valid actuation of Fort Calhoun station (FCS) Unit 1 Emergency Diesel Generator 2 (DG-2) occurred as a result of undervoltage on its respective safety bus (1A4). DG-2 started as a result from manually deenergizing bus 1A4 during the performance of the Bus Ground Fault Locator Function Test. The DG-2 output breaker was disabled as part of the test and therefore did not close onto the bus. The procedure was deficient in ensuring that DG-2 was not in automatic. "No loads were being supplied from Bus 1A4 at the time and thus no loads were lost. No other Safeguards systems or equipment were actuated. "Fort Calhoun Station is currently in a refueling outage, Mode 5 with the core offloaded to the Spent Fuel Pool. No Technical Specifications were entered as a result of this actuation due to plant being less than 300°F. "Emergency Diesel Generator 2 was taken out of automatic, lockout relays reset and the engine was shutdown." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-11-08
42973 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-11-07 16:07 | 2006-11-08 10:56 | 2006-11-08 | FAILURE OF PROCESS GAS LEAK DETECTION SYSTEM "At 1607 on 11/7/2006, the Plant Shift Superintendent (PSS) was notified of a failure of the C-333 Unit 6 Cell 3 process gas leak detection (PGLD) system. C-333 operators were alerted to the Unit 6 Cell 3 PGLD failure by the receipt of an Area Control Room alarm. The operators responded to the Unit 6 Cell 3 cell panel and discovered that the PGLD system was inoperable. C-333 Unit 6 Cell 3 and associated piping were operating above atmospheric pressure (Cascade Mode 2) at the time of the PGLD failure. The operators initiated a continuous smoke watch of the area with lost PGLD coverage until the associated equipment and piping pressure was reduced below atmospheric pressure in accordance with TSR LCO 2.4.4.1. The PGLD system is required per TSR 2.4.4.1 to be operable when a cascade cell and associated piping is above atmospheric pressure (Cascade Mode 2). "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-06-3679; PGDP Event Report No. PAD-2006-11; NRC Worksheet No. 42973." The licensee stated that the equipment and piping pressure was reduced in order to allow the process to continue operating in a condition where the PGLD system is not required to be operable. The licensee is investigating the cause of the failure but it is preliminarily believed to be a failure of an instrumentation power supply. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-11-08
42972 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-11-07 08:59 | 2006-11-08 08:52 | 2006-11-08 | PROCESS GAS LEAK DETECTOR FAILURE "At 0859 on 11/7/2006, the Plant Shift Superintendent (PSS) was notified of a failure of the C-337A process gas leak detector (PGLD) YE-613-21 to alarm during TSR [Technical Safety Requirements] surveillance 2.2.4.1-1. TSR surveillance 2.2.4.1-1 is a quarterly test to verify that the PGLD will detect a UF6 release, alarm, and alert personnel. PGLD YE-613-21 provides coverage for the north section of the facility UF6 piping trench. Staff review of the failure, suggest that PGLD YE-613-21 may have failed prior to being removed from service to perform the 11/7/06 TSR surveillance. PGLD YE-613-21 was replaced and tested satisfactorily. Additional testing and engineering review of PGLD YE-613-21 is being performed to ensure the operability of the PGLD and to develop any needed corrective actions. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-06-3670; PGDP Event Report No. PAD-2006-10; NRC Worksheet No. 42972." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-11-08
42971 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2006-11-08 08:05 | 2006-11-08 09:19 | 2006-11-17 | PLANT COMPUTER DOWN FOR UPGRADE "Farley Nuclear Plant is replacing the Unit 1 plant computer with an upgraded plant computer. The total time that the plant computer may be down is a maximum of 10 days. The functions for emergency preparedness will be completed within the first 12 hours of the outage. During that first 12 hours a contingency plan is in place to ensure that the TSC would have the required data if an emergency was declared. A 5054Q was written for this and was reviewed by the Region 2 NRC EP staff prior to implementation." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 2045 EST ON 11/17/06 FROM FOREST LERO TO S. SANDIN * * * The licensee successfully completed functional testing earlier today of the SPDS and has returned it to service as of 2045 EST on 11/17/06. The licensee will inform the NRC Resident Inspector. Notified R2DO (Chuck Casto). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-11-08
42970 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-11-07 13:55 | 2006-11-07 15:08 | 2006-11-07 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION ON 11/07/06 AT 2035 EST BY DARON ZAKARIAN TO MACKINNON * * * Upon further review and investigation the licensee is retracting this event. Contact the Headquarters Operation Officer for further details. R1DO (N. Perry) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-11-07
42969 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-09-25 10:34 | 2006-11-07 13:16 | 2006-11-07 | INVALID SYSTEM ACTUATION - PARTIAL PHASE A CONTAINMENT ISOLATION "This 60-day telephone notification is being made under the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation partial containment Phase A isolation affecting more than one system. "On 09/25/2006 at approximately 1034 hours, while in MODE 6, 'Refueling Operations' with no core alterations in progress, a partial Containment Phase 'A' Isolation occurred without a valid initiating signal from the Train 'A' Solid State Protection System. All components responded as designed and Operations verified stable conditions in accordance with plant operating procedures. "The following components were actuated: 1-XCR-100, Containment Air Supply Header No. 2 Containment Isolation Valve, 1-XCR-102, Control Air Supply Header No. 1 Containment Isolation Valve, 1-VCR-11, Glycol to Air Handling Units, 1-VCR-21, Glycol from Air Handling Units, 1-DCR-600, Containment Sumps to Dirty Waste Hold-up Tank Containment Isolation Valve, 1-DCR-610, Ice Condenser Fans Cooler Units Drain to WDS Containment Isolation Valve, 1-CCR-455, CCW to Reactor Support Coolers Containment Isolation Valve, 1-QCR-919, Demin Water to Containment Isolation Valve, 1-QRV-51, Pressurizer Auxiliary Spray Line from CVCS Isolation Valve, 1-QRV-61, Alternate Charging Line to Cold Leg 1 Isolation Valve, 1-QRV-62, Normal Charging Line to Cold Leg 4 Isolation Valve. "All components responded as expected. The remaining Phase 'A' components did not actuate because they had been previously removed from service. "This event was caused by an intermittent electrical connection at Universal Logic Card A313 receptacle and a failed A213 card. The inadequate receptacle spring tension on the A313 card has been corrected, and the failed A213 card has been replaced. There were no safety consequences or impacts on the health and safety of the public. The event has been entered into the Donald C. Cook Nuclear Plant's corrective action program. The NRC Senior Resident was notified of this report, time 1220, 11/7/06." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-11-07
42968 | 0 | RANCHO SECO | 1 |  |  | [1] B&W-L-LP | 2006-11-06 09:30 | 2006-11-06 17:20 | 2006-11-06 | ONE AND POSSIBLY FIVE OTHER CLASS "C" FUEL ASSEMBLIES WERE SINGLED OUT AS HAVING THE POTENTIAL OF HAVING FLAWS ABOVE THE HAIRLINE CRACK OR PINHOLE LEAK CRITERIA. This event is a 24 hour notification per Technical Specification 2.2.1. Based upon the differences in the definition of damaged fuel presented in RSAP-0112, and the commitments made in various licensing documents, it was determined that a potential existed that damaged assemblies may have been placed in a fuel canister licensed only for intact assemblies. A potential problem exists with fuel assemblies, which had been categorized as class "C" assemblies in the RSAP-0112 inspection results, and therefore would not have had any restrictions on the type of canister to be placed. Class "C" assemblies were those assemblies not meeting the requirements of F2 for gross cladding defects, did not have cracks which exceeded dimensional of approx. 0.34 inches across and 0.7 inches high. Based on further review of the RSAP-0112 inspection results, six fuel assemblies were upgraded as potentially damaged fuel assemblies because the written inspection reports indicated the existence of a crack or missing cladding greater than the class "C" limit. With the exception of assembly 2G6, the video portion of the tape is not 100% conclusive that a crack greater than a hairline exists on the other five fuel assemblies. Based upon the images available of assembly 2G6, the crack on this assembly was scaled to be approx. 0.04 inches wide by 0.25 inches long. The film quality of the remaining 5 assemblies is not sufficient to provide such detailed scaling but is estimated for discussion purposes. NRC Project Manager (Randy Hall) was notified of this by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2006-11-06
42967 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2006-09-08 18:28 | 2006-11-06 11:51 | 2006-11-06 | HALF SCRAM SIGNAL DUE TO EQUIPMENT FAILURE "On September 8, 2006 at approximately 1828, with the James A. FitzPatrick Nuclear Power Plant (JAF) operating at 98% reactor power, an equipment malfunction occurred, resulting in the tripping of one of the two 'B' Reactor Protection System (RPS) motor generator Electrical Protection Assembly (EPA) breakers. This caused a corresponding loss of power to the 'B' RPS bus, a half scram and primary containment isolation valve closures. Appropriate actions were taken in accordance with Abnormal Operating Procedure (AOP)-60, 'Loss of RPS Bus B Power.' All equipment operated as designed as a result of the loss of power to the 'B' RPS bus. "At 1859, the 'B' RPS bus was placed on the alternate power supply. At approximately 1905, the RPS half scram and Primary Containment Isolation System (PCIS) isolation signal was reset. Restoration of the various isolated systems commenced shortly thereafter. The reactor remained at 98% power throughout the event and Technical Specifications (TS) Limiting Condition for Operation (LCO) Actions were entered for the affected equipment as required. "The above event meets the reporting criteria of 10 CFR 50.73(a)(2)(iv)(a) since the loss of RPS bus resulted in primary containment isolation signals affecting containment isolation valves in more than one system. The following systems or components isolated as a result of the loss of 'B' RPS bus: Reactor Water Cleanup, Reactor Building Ventilation, 'B' Containment Atmosphere Dilution, Torus Vent and Purge, Drywall Equipment and Floor Drain Sumps, 'B' Drywall Containment Atmospheric Monitors, Recirculation System Sample Line, Main Steam Line Drains, Residual Heat Removal drain valve to radwaste, Standby Gas Treatment (auto initiated). "Since the signal was invalid (the result of loss of power vs. an actual containment isolation condition), this event meets the criteria in 10 CFR 50.73(a)(1) for being reported as a 60 day telephone notification in lieu of a written LER. "The loss of the 'B' RPS bus was caused by the tripping of one of the two in-series 'B' RPS motor generator EPA breakers. A Failure Modes and Effects Analysis was completed for the EPA breaker. Potential failure modes were evaluated and ruled out with the exception of failure of a subcomponent on the EPA breaker logic card. The logic card and breaker were replaced, restoring the 'B' RPS motor generator to service." The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-11-06
42966 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2006-11-06 01:10 | 2006-11-06 04:57 | 2006-11-06 | AUTOMATIC REACTOR SCRAM DURING TURBINE TESTING "On 6 November 2006 at 0110 an automatic reactor scram was received. This report is being made under 10 CFR 50.72 (b)(2)(iv)(B), 'any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical.' The plant also received Group 2, 3 and 4 isolations from the low level signal as reactor water dropped due to the reactor scram. The isolations are being reported under 10 CFR 50.72 (b)(3)(iv)(A), 'any event or condition that results actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section.' The scram is believed to be the result of a turbine trip but is currently being investigated further. Main Turbine surveillance testing was in progress at the time but it is not known if the testing caused the turbine trip and subsequent Reactor Scram. Reactor pressure is currently being controlled by the turbine bypass valves and steamline drains. No actuations of Safety Relief Valves were required or occurred. Both Reactor Recirculation pumps tripped as part of RPT. The 'B' Recirc pump has been restarted. Reactor level dropped following the scram resulting in the isolations but was recovered and is currently being maintained by the normal feedwater systems. All isolations went to completion and have been reset at this time. The plant electrical buses transferred without incident and are currently in a normal shutdown alignment. "The current plan is to remain in Mode 3 while investigations determine the cause of the turbine trip and reactor scram." All control rods fully inserted on the trip. Currently the plant is using offsite power but diesel generators are available. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-11-06
42965 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-11-05 16:00 | 2006-11-05 18:07 | 2006-11-06 | TEXAS AGREEMENT STATE REPORT - MISSING SOURCE Two Radiation Oncologist Residents removed an LDR applicator from a cervical cancer patient. The applicator was supposed to have contained four Cesium-137 sources, 15 millicuries each, but only 3 of the sources were found. The patient's bed sheets had been changed and taken out of the room. Search for missing source is in progress. * * * UPDATE FROM R. JISHA TO P. SNYDER AT 0843 ON 11/6/06 * * * The lost source material was found in the laundry. The state continues to investigate. Further information will be provided later. Notified R4DO (J. Clark) and NMSS EO (M. Burgess). A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-11-11
42964 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2006-11-04 18:10 | 2006-11-04 21:01 | 2006-11-04 | HPCI INOPERABLE "During HPCI testing with reactor pressure at 975 psig, HPCI flow and turbine speed oscillations occurred. The HPCI turbine was run for approximately one minute and was manually tripped by the operator when system conditions did not improve. "A cause investigation is underway. "All other ECCS and RCIC remain operable. "The unit is in a 14 day LCO for this event. "The NRC Resident Inspector has been notified." | 20 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-11-04
42963 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-11-04 16:30 | 2006-11-04 20:37 | 2006-11-04 | AUXILIARY FEEDWATER NOT ALIGNED PROPERLY IN STARTUP MODE "On 11/3/2006 at 1834 hours, it was discovered that, with the Plant in Mode 2, both trains of Auxiliary Feedwater were not in the required pump automatic start configuration. One pump was operating and performing the heat removal function. Both Auxiliary Feedwater train pump controls were immediately placed into the Automatic configuration. It was determined that the pump start controls had been placed in Manual on 11/1/2006 at about 2152 hours. Upon discovery, it was believed that the Auxiliary Feedwater heat removal function was satisfied because one train was operating and had been in operation since before 2152 hours on 11/1/2006. "Subsequently, on 11/4/2006 at 1630 hours it was determined that, with the pump controls in manual, coincident with a postulated Loss of Offsite Power and an Auxiliary Feedwater Actuation Signal, the operating Auxiliary Feedwater pump would trip and neither train pump would automatically start. "This situation would constitute a condition that could have prevented the fulfillment of the safety function to mitigate the consequences of a Loss Of Offsite Power event and is reportable under 50.72(b)(3)(v)D. "Had such an event occurred, the Operators would have restored Auxiliary Feedwater flow in accordance with station procedures." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-11-04
42962 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-11-01 10:20 | 2006-11-03 13:05 | 2007-04-24 | WASHINGTON STATE AGREEMENT STATE REPORT This event was received via e-mail "On November 1, three workers were involved in separating sources, lead pigs (shielded containers) and trash from a barrel. Work was being conducted in a ventilated enclosure within a PEcoS waste processing building. Two workers inside the enclosure were wearing respirators and the supervisor (not wearing a respirator) was immediately outside the enclosure directing the work. At the end of the day, the supervisor noted he was contaminated. The supervisor was scheduled for whole-body counting at the Battelle facility early the next day. An uptake of approximately 11.7 nanocuries of Americium 241 was confirmed. The preliminary dose estimate to the individual's lung was 97.5 Rem CDE. The individual was started on chelation treatment. The other two workers were sent for whole body counting on November 3. "The operation included opening one lead pig that contained three Am-241 sources. Contamination previously had not been detected outside the pig or in the trash. Sources were surveyed for dose rate and separated from the lead pig without contamination smears being taken. No release to the public or the environment occurred. Operations in this and adjacent areas were stopped once the situation was known. An investigation was initiated by PEcoS. The area was evacuated and is currently being ventilated. DOH has an inspector on-site performing an incident investigation. "Media is aware of the incident. "Notification Reporting Criteria: WAC 246-221-250(2) Notification of Incidents (24 hour notification) "Isotope and Activity involved: Am-241 total activity from twelve drums was manifested at 6.8 GigaBq (184 millicuries). Only one drum was open at the time of the incident. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Three workers were involved. One worker has an apparent over exposure of 97.5 Rem CDE to the Lung. No release to public or environment." * * * UPDATE FROM WASHINGTON STATE (FRAZEE) TO HUFFMAN VIA E-MAIL AT 1746 ON 11/16/06 * * * "On November 1, three workers were involved in separating sources, lead pigs (shielded containers) and trash from a barrel. Work was being conducted in a ventilated room, (previously reported as an enclosure within the room) within a PEcoS waste processing building. Two workers inside the room were wearing respirators and the supervisor (not wearing a respirator) was immediately outside the room directing the work. A very high contamination level was detected (greater than 2 million dpm/wipe) in the room at about 10:00, and the building was evacuated shortly after that. At about this time, an air sample that was in the area of the workers was counted and determined to have a very high alpha activity (10 E-9 µCi/ml). The supervisor and the workers were taken to a survey area and found to be contaminated on the face. Contamination was detected on the respirators. The workers were successfully decontaminated by the on site health physics department. The supervisor was scheduled for whole-body counting at the Battelle facility early the next day. An uptake of approximately 11.7 nanocuries of Americium 241 was confirmed. The preliminary dose estimate was 97.5 Rem CDE. The individual was started on chelation treatment. The other two workers were sent for whole body counting on November 3. Subsequent counts on the first individual were lower (about 9nCi), and the subsequent 2 workers follow-up counts decreased from about 6.9nCi to 3.2nCi and from 1.5nCi to 0.5nCi. The final dose received will depend on the efficiency of the chelate treatment and other factors. One additional person who was in the building was analyzed for internal Am-241 contamination, and was found to be <0.092nCi, below the detection limit of the instrument. "The operation included opening one lead pig that contained three Am-241 sources. Contamination previously had not been detected outside the pig or in the trash. Sources were surveyed for dose rate and separated from the lead pig without contamination smears being taken. Operations in this and adjacent areas were stopped once the situation was known. An investigation was initiated by PEcoS. The area was evacuated and is currently being ventilated. DOH has an inspector on-site performing an incident investigation. Update as of 14 November: "The three employees are still being treated with a chelating agent. This week should be the last week. At this time, there is no update on the original activity or the activity left in the body, except that the amount of activity in the lung is decreasing. It will be several weeks before the final dose can be calculated by the licensee's consultants, which will be based on the initial lung count, the bioassay results (urine/fecal), and the effectiveness of the chelate at removing the americium from the body. At this point, we assume there are three individuals who may have exceeded their annual dose limit of 50 Rem to the bone. The final dose received by the three individuals will be calculated when sufficient information is accumulated. The three workers have returned to work exhibiting some emotional stress and slight effects from the medical treatments. Plant Status "The plant is being restarted incrementally after a safety shutdown imposed by the company. After DOH approval, two process lines have been restarted: the super compactor on the mixed waste side of operations and an inspection and sorting process, also on the mixed waste side. The licensee is completing items identified on the mixed waste thermal systems safety evaluation, and expects to restart those processes in the next few days. In addition, they are completing items identified on the low level thermal systems, but a restart date is pending. The low level processes that were affected by this accident are not being restarted, until the contamination in the building is controlled. The building that the material is in is being decontaminated, and continues to be a respirator area. The contaminated room is still inaccessible, however, a plan was completed to re-enter the room to assess the extent of the contamination. This initial entry was conducted on 11-14-06 by senior members of the Health Physics staff. As a result of the surveys conducted during the reentry, the extent of the problem they face is better understood. A plan is being developed to decontaminate the room. "The investigation is continuing, and the actual cause of the event does not appear to be a single cause, but rather compounding mistakes, errors in judgment and complacency for the seriousness of this type material. Corrective actions that are being taken by the licensee at this time, are primarily based on self evaluation, using the workers and technical staff. In addition, at this time DOH is requiring the company to retrain the radiological technicians as well as the workers in the different waste processes prior to restart of any process. DOH is working with the company to identify the root causes of this incident. "No release to public or environment. Air sample analysis results for a particulate sample in the building exhaust stack was 9.2E-3 µCi/ml gross alpha. "The building is being decontaminated, and additional containment tents are being installed around the contaminated room. "Media is aware of the incident. Tri-City Herald (Kennewick Washington) article was published November 4, 2006. "Notification Reporting Criteria: WAC 246-221-250(2) Notification of Incidents (24 hour notification) "Isotope and Activity involved: Am-241 total activity from twelve drums was manifested at 6.8 GigaBq (184 millicuries). Only one drum was open at the time of the incident. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Three workers were involved. The first worker had an initial internal deposition result of 11.7 nCi. Two additional workers have been confirmed as having an internal deposition: initial results were 6.9 nCi and 1.5 nCi. Subsequent counts of all three involved personnel were lower. All three workers were given chelating treatment. The final dose will be calculated by the Battelle internal dosimetry program, following extensive testing. Other workers who were in the area are being tested. The estimated dose to the endosteal (white bone matter) from 11.7nCi is about 95 rem CDE." R4DO (Johnson) and NMSS EO (Camper) notified. Washington State Report # WA-06-063. * * * UPDATE ON 02/06/07 AT 1600 EST VIA E-MAIL FROM MIKEL ELSEN TO MACKINNON * * * "Update as of 5 February, 2007 "From the Department of Health's investigation into this incident, it appears that the root cause of the event was failure to adhere to procedures and plans set forth for the project, and inadequate training. Preliminary corrective actions taken by the licensee to prevent recurrence are disciplinary action to the employees involved for procedure and policy violations, a functional Alpha CAM was put in service, training performed for all staff working with radioactive material, with follow-up testing. Additionally, a reorganization of the facility which relieves the RSO of numerous tasks not related to Radiation Safety has taken place, and the facility has made a new position Special Project Lead who is assigned to work with HP and Operations Staff on special projects and compile lessons etc. The final exposure to the individuals has not yet been assigned. When the DTPA treatments have been determined done then exposures will be able to be assigned. Currently it is anticipated that the final dose calculation will be assigned by the end of February 2007. The amount of Am-241 activity in the involved drum was manifested as 71 millicuries Am-241." R4DO (Nease) & NMSS (Greg Morell) notified. * * * UPDATE ON 04/24/07 AT 1525 EDT VIA E-MAIL FROM MIKE ELSEN TO MACKINNON * * * "Update as of April 23, 2007 "The final intake and internal dose evaluation of the PEcoS employees have been completed. The results are presented below, along with the anticipated dose they would have received if the employees did not receive the DTPA chelating treatments. Employee 1: Intake was estimated at 17 nCi of Am241 The estimate of the actual 50-year committed internal dose equivalents for the respective organs and tissues "Actual 50-year Committed Anticipated Dose "Organ / Tissue Dose Equivalent (rem) Without Therapy (rem) "Effective 3.8 7.3 "Bone Surface 78 150 "Liver 4.6 8.9 "Red Bone Marrow 6.2 12 "Gonads 1.1 2.1 "Lungs 1.7 1.7 "Employee 2: Intake was estimated at 4 nCi of Am241 The estimate of the actual 50-year committed internal dose equivalents for the respective organs and tissues "Actual 50-year Committed Anticipated Dose "Organ / Tissue Dose Equivalent (rem) Without Therapy (rem) "Effective 1.0 1.7 "Bone Surface 22 36 "Liver 1.3 2.1 "Red Bone Marrow 1.7 2.8 "Gonads 0.29 0.48 "Lungs 0.39 0.39 "Employee 3: Intake was estimated at 48 nCi of Am241 The estimate of the actual 50-year committed internal dose equivalents for the respective organs and tissues "Actual 50-year Committed Anticipated Dose "Organ / Tissue Dose Equivalent (rem) Without Therapy (rem) "Effective 4.9 21 'Bone Surface 95 430 "Liver 5.5 25 "Red Bone Marrow 7.5 34 "Gonads 1.3 5.8 "Lungs 4.7 4.7 "The licensee has taken the following corrective actions to help prevent reoccurrence: "A Re-distribution of the RSO's work to other onsite personnel and hiring additional people to ensure adequate coverage. "Management reorganization, to increase the oversight given to the radiation protection program. "Increased training on procedures. 'Increased management interaction and surveillance by the RSO and other health physics staff. 'Inclusion of the engineering staff on all facility changes, such as ventilation changes.'Changes to the procedures for operation of the ventilation system in buildings 1 and 2. "Hazard analysis on the ventilation system in buildings 1 and 2, and the changes that were discussed in the hazard analysis. "Careful analysis of the internal dose received by the affected workers. "Assurance PEcoS personnel will follow all of your procedures. "Disciplinary action for culpable employees. "Greater emphases to ensure that orders and instructions to the workers are clear and understood. "Plant Status "The plant is being restarted incrementally after a safety shutdown imposed by the company. After DOH approval, two process lines have been restarted: the super compactor on the mixed waste side of operations and an inspection and sorting process, also on the mixed waste side. The licensee is completing items identified on the mixed waste thermal systems safety evaluation, and expects to restart those processes in the next few days. In addition, they are completing items identified on the low level thermal systems, but a restart date is pending. The low level processes that were affected by this accident are not being restarted, until the contamination in the building is controlled. The building that the material is in is being decontaminated, and continues to be a respirator area. The contaminated room is still inaccessible, however, a plan was completed to re-enter the room to assess the extent of the contamination. This initial entry was conducted on 11-14-06 by senior members of the Health Physics staff. As a result of the surveys conducted during the reentry, the extent of the problem they face is better understood. A plan is being developed to decontaminate the room. "The investigation is continuing, and the actual cause of the event does not appear to be a single cause, but rather compounding mistakes, errors in judgment and complacency for the seriousness of this type material. Corrective actions that are being taken by the licensee at this time, are primarily based on self evaluation, using the workers and technical staff. In addition, at this time DOH is requiring the company to retrain the radiological technicians as well as the workers in the different waste processes prior to restart of any process. DOH is working with the company to identify the root causes of this incident. "No release to public or environment. Air sample analysis results for a particulate sample in the building exhaust stack was 9.2E-3 µCi/ml gross alpha. "The building is being decontaminated, and additional containment tents are being installed around the contaminated room. "Media is aware of the incident. Tri-City Herald (Kennewick Washington) article was published November 4, 2006. "Notification Reporting Criteria: WAC 246-221-250(2) Notification of Incidents (24 hour notification) "Isotope and Activity involved: Am-241 total activity from twelve drums was manifested at 6.8 GigaBq (184 millicuries). Only one drum was open at the time of the incident. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Three workers were involved. The first worker had an initial internal deposition result of 11.7 nCi. Two additional workers have been confirmed as having an internal deposition: initial results were 6.9 nCi and 1.5 nCi. Subsequent counts of all three involved personnel were lower. All three workers were given chelating treatment. The final dose will be calculated by the Battelle internal dosimetry program, following extensive testing. Other workers who were in the area are being tested. The estimated dose to the endosteal (white bone matter) from 11.7nCi is about 95 rem CDE. "Lost, Stolen or Damaged? (mfg., model, serial number): N/A "Disposition/recovery: N/A "Leak test? N/A "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) N/A "Release of activity? N/A "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: N/A "Exposure (intended/actual); consequences: N/A "Was patient or responsible relative notified? N/A "Was written report provided to patient? N/A "Was referring physician notified? N/A "Consultant used? (deleted) at Battelle in vivo counter facility, (deleted) at Advanced Medical, and (deleted) at Pacific Northwest National Laboratory." FSME (Greg Morell) & R4DO (Linda Smith). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-11-08
42961 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2006-11-03 03:09 | 2006-11-03 12:04 | 2006-11-03 | PROCEDURAL ERROR CAUSED RESIDUAL HEAT REMOVAL SHUTDOWN COOLING INBOARD CONTAINMENT ISOLATION VALVE TO CLOSE. "This event notification is being made to report an event that could have prevented the fulfillment of the safety function to remove residual heat. On November 3, 2006, the plant was shutdown in Mode 4 (Cold Shutdown) with the reactor vessel level being maintained between 60-80 'inches' and temperature was being maintained 110-120F. Operators were performing a procedure to transfer RPS B to its alternate power supply. During the procedure, RHR-V-9 (RHR shutdown cooling inboard containment isolation valve) closed and shutdown cooling was interrupted. Reactor Recirculation Pump A remained in service providing forced flow through the core. Operators reopened RHR-V-9 and restored shutdown cooling. Reactor temperature reached 148F and vessel level reached 95 'inches' (bottom of main steam lines is 116 inches) while shutdown cooling was not in service. Shutdown cooling was restored in 45 minutes (120 minutes time to boil from 120F) after RHR-V-9 went closed. Reactor temperature and level were restored to their previous operating bands by 0451 PST. Initial indications are that RHR-V-9 closed due to an error in the procedure which failed to remove control power from RHR-V-9 during the RPS transfer. Without removing control power, a motor-closed demand would have been created in the circuit during the transfer and upon restoration of power to the valve motor, the valve would motor close. Further investigation is ongoing." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-11-03
42960 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-11-02 18:53 | 2006-11-02 22:13 | 2006-11-02 | TECHNICAL SPECIFICATION SHUTDOWN "On 11/01/06 at approximately 18:23 (EST) Brunswick Unit 2 experienced a loss of the unit's Startup Auxiliary Transformer (SAT) and a loss of reactor forced circulation. Due to the loss of the SAT and subsequent manual reactor scram of Unit 2, a loss of Offsite Power resulted to the Unit 2 power buses. All four site Emergency Diesel Generators (EDGs) then started as designed. "On 11/02/06 at approximately 0400 (EST) EDG no. 1 tripped on low lube oil pressure due to high differential pressure on the EDG lube oil strainer. The EDG was not loaded at the time of the trip. Due to the loss of one offsite qualified circuit (Unit 2 SAT) and the loss of one EDG (EDG 1), Unit 1 entered Technical Specification (TS) 3.8.1, Condition F, which requires restoration of the inoperable offsite circuit or restoration of the inoperable Diesel Generator within 12 hours. At 1600 on 11/02/06, Brunswick Unit 1 entered TS 3.8.1, Condition H, Required Action H.1 to be in MODE 3 in 12 hours and Required Action H.2 to be in MODE 4 within 36 hours. "On 11/02/06 at 17:54 EDG 2 was declared inoperable due to being placed in manual for a required loaded run due to having been operated at no load for a period of time. Unit 1 entered Technical Specification 3.0.3 due to having EDG 1, EDG 2, and one offsite qualified circuit (Unit 2 SAT) inoperable. Per Technical Specification 3.0.3, action shall be initiated within one hour to place the unit in Mode 2 within 7 hours, Mode 3 within 13 hours, and Mode 4 within 37 hours. Unit 1 began a Technical Specification Required shutdown at 18:53 and is presently at 99% power. "On 11/02/06 at 21:30, EDG 2 was declared operable following the loaded run and is presently in standby in the auto mode. Technical Specification 3.0.3 was exited at that time. Unit 1 remains in Technical Specification 3.8.1 Condition H at the present time. "At 21:59, the NRC resident was notified of this event." | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-11-02
42959 | -1 | PALISADES | 1 |  |  | [1] CE | 2006-11-02 14:36 | 2006-11-02 19:10 | 2006-11-10 | HIGH PRESSURE SAFETY INJECTION (HPSI) PUMPS ALIGNMENT BLOCKS IMPROPERLY INSTALLED "At 1436 hours on November 2, 2006, with the plant in Mode 3, it was determined that less than 100% of the required Emergency Core Cooling System (ECCS) flow was available per Technical Specification (TS) 3.5.2.D. Therefore, TS LCO 3.0.3 was entered. "Each High Pressure Safety Injection (HPSI) pump (one in each ECCS train) is designed with alignment blocks in its mounting, which ensures pump and motor alignment for the thermal expansion experienced by the pump upon initiation of sump recirculation flow. These alignment blocks ( 2 per pump) were discovered to be improperly installed, or missing altogether. In this condition, the HPSI pump could potentially be rendered inoperable upon initiation of sump recirculation. "This condition is reportable in accordance with 10CFR 50.72(b)(3)(ii)(B) and (b)(3)(v)(D) as an unanalyzed condition, and a condition that could have prevented the fulfillment of the safety function of the HPSI pumps to mitigate the consequences of an accident, respectively." The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION FROM MALONE TO HUFFMAN AT 1335 EST ON 11/10/06 * * * "EN # 42959 reported on November 2, 2006 that both Emergency Core Cooling System Trains were inoperable. The reason for that determination involved the observation that the alignment blocks [keys] associated with the mounting of the high pressure safety injection (HPSI) pumps were either incorrectly installed or were missing. The alignment keys were believed to be necessary to ensure appropriate HPSI pump and motor alignment for the thermal expansion experienced upon initiation of sump recirculation flow. The condition was reported as an unanalyzed condition and a condition that could have prevented the fulfillment of the safety function of the HPSI pumps to mitigate the consequences of an accident. "Subsequently, further evaluation of the HPSI pump mounting configuration determined that the alignment keys are not required for pump operability. Therefore, there was no unanalyzed condition and no condition that could have prevented the fulfillment of the safety function of the HPSI pumps to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. R3DO(Cameron) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2006-11-02
42958 | 0 | ANDREWS ENVIRONMENTAL ENGINEERING |  |  |  |  | 2006-11-02 16:00 | 2006-11-02 16:24 | 2006-11-03 | DAMAGED TROXLER MOISTURE DENSITY GAUGE. The outer case and the key pad to a Troxler, Model number 3440, was damaged when a vehicle struck the case. The rod to the gauge still operates properly. The location of the incident occurred at the Newton County landfill near Brook, IN. The RSO will go to the site to take radiation surveys. The serial number of the gauge is 21041. The gauge contains 8 millicuries of Cesium-137 and 40 millicuries of Am-241/Be. * * * UPDATE FROM STEVE REUTER TO JOE O'HARA ON 11/3/06 AT 1152 * * * Licensee reported that radiation surveys of the gauge indicated less than 3 milliRem/hr approximately six inches from the device, and the carry case isn't damaged. The licensee has recovered the gauge and will perform a leak test prior to forwarding it to the vendor via FedEx. Notified R3DO(Monte Phillips) and NMSS ( Sandra Wastler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN |  |  |  |  | 0 | 2006-11-02
42957 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-11-02 13:34 | 2006-11-02 14:53 | 2006-11-03 | AUTOMATIC TURBINE TRIP/ REACTOR TRIP DUE TO INVALID LOW CONDENSER VACUUM SIGNAL "At 1334 on 11-2-06 an Automatic Reactor Trip occurred from 100% power. All systems functioned as required. One safety valve stuck open on both OTSGs. They subsequently re-seated. An employee working on the roof at the time of the trip fell off a ladder and injured his leg. Emergency medical was contacted to assist with the injured worker. Two fire trucks and an ambulance was dispatched to the site to remove the injured worker. The worker was not contaminated. There is no indication of any OTSG tube leaks. Initial investigation indicates the reactor tripped, due to a turbine trip due to an invalid low vacuum signal." State and local officials will be notified of this event by the licensee. I&C Techs were performing maintenance on one of the low pressure vacuum switches. An electrical fault fed to the other two low pressure vacuum switches causing a 2 out of 3 signal which resulted in a turbine trip followed by a reactor trip signal, as expected. All rods fully inserted into the core. One safety valve (9 safety valves on each OTSG) on each Once Through Steam Generator stuck open. OTSG "B" safety relief valve was open less than one minute. There are no leaking OTSG tubes. A condensate relief valve located in the turbine building opened/shut - nobody injured. The ICS (Integrated Control System) operated as expected. All emergency core cooling systems and the emergency diesel generators are fully operable plus the electrical grid is stable. A licensee working on the industrial coolers on top of the industrial building, standing on a ladder, fell off the ladder when OTSG relief valve opened. Licensee either broke or badly sprained his leg. The NRC Resident Inspector was informed of this event by the licensee. * * * UPDATE ON 11/03/06 AT 1607 EST FROM ADAM MILLER TO MACKINNON * * * "Post trip evaluation determined that the Main Steam safety valves were not stuck open. The safety valves were operating within their tolerance band. The "B" OTSG Main Steam safety valve reseated with no operator action as steam pressure decreased. The "A" Main Steam safety valve was reseated when operators lowered OTSG pressure in accordance with Plant Operating Procedures. TMI-1 issued a press release on this event at 15:13 on 11/2/06." R1DO (John White) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) |  |  | 0 | 2006-11-02
42956 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-11-02 13:30 | 2006-11-02 14:06 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * SITE EMPLOYEE ARRESTED Site employee was arrested by law enforcement personnel on 11/02/06. Site access has been terminated pending investigation. The licensee notified the NRC Resident Inspector. Contact Headquarters Operations Officer for additional details. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2008-05-11
42955 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-11-01 18:37 | 2006-11-01 19:10 | 2006-11-02 | UNIT 2 DECLARED AN UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER TO THE 4KV EMERGENCY BUSES At 1823 EST, Unit 2 was manually scrammed due to a loss of offsite power from the Startup Auxiliary Transformer to both 4KV Emergency (E) buses. Both Emergency Diesel Generators (EDGs) 3&4 autostarted and re-energized the affected electrical buses. At 1823 EST, an Unusual Event was declared based on EAL 06.01.01, "Inability to power either 4KV E bus from offsite power." Unit 2 is currently stable in mode 3, Hot Shutdown, with MSIVs closed and HPCI controlling pressure and RPV Water Level. All control rods fully inserted following the manual reactor scram. The licensee determined that no emergency facilities will be activated and that no offsite assistance is needed at this time. The licensee informed both state and local agencies and will inform the NRC Resident Inspector. * * * UPDATE PROVIDED BY JOEL LEVINER TO JEFF ROTTON AT 2214 EST ON 11/01/06 * * * "On 11/01/06 at approximately 18:23 (EST) Brunswick Unit 2 experienced a loss of the unit's Startup Auxiliary Transformer and a loss of reactor forced circulation. A manual reactor scram was performed as required by station Abnormal Operating Procedures. Due to the loss of the Startup Auxiliary Transformer and subsequent manual reactor scram, a loss of Offsite Power resulted to the unit's power buses when unit shutdown was completed. All control rods properly inserted when the manual reactor scram was performed. All four site emergency diesels started and diesels 3 and 4 are supplying the Unit 2 emergency buses. Reactor water level reached low level 1 (LL1) and low level 2 (LL2) as result of the reactor scram and loss of offsite power. The LL1 signal resulted in Group 2 (floor and equipment drain isolation valves), Group 6 (monitoring and sampling isolation valves) and Group 8 (shutdown cooling isolation valves) isolation signals. All low level 1 isolations occurred as designed. The LL2 resulted in a Reactor Core Isolation Cooling (RCIC) system actuation, High Pressure Coolant Injection (HPCI) system actuation, Group 3 (reactor water cleanup valves) isolation signal, a secondary containment isolation signal, a Standby Gas Treatment (SBGT) initiation signal, a Control Room Emergency Ventilation (CREV) initiation signal, and an Alternate Rod Insertion (ARI) actuation signal. All isolation and actuations occurred as designed with the exception the CREV initiation and ARI actuation. CREV initiation and ARI actuations were performed by manual actions. The failure of the CREV and ARI initiation/actuations are under investigation. The RCIC and HPCI systems were used to restore reactor water level to the normal operation band. Reactor vessel pressure is being controlled in the normal band with manual operation of Safety Relief Valves (SRV), and HPCI/RCIC in pressure control mode. The Main Steam Isolation Valves (MSIVs) (Group 1) and the drywell pneumatic isolation valves (Group 10) closed on the loss of power. The plant is a stable condition. Troubleshooting activities are in progress to determine the cause of the event. "At 1910, the NRC was previously notified of the Unusual Event declaration. "Initial Safety Significance Evaluation: The safety significance of this event is minimal and Unit 2 is in a stable condition. All control rods properly inserted when the manual scram was performed. Plant safety systems responded as required with the exception of the CREV and ARI systems which did not automatically initiate but functioned properly when manually actuated. All four emergency diesels started and Unit 2 diesels 3 and 4 are supplying the Unit 2 emergency buses. Reactor pressure and level are being controlled per procedure, with HPCI and RCIC. Actions are in progress to re-establish off site power supply to emergency buses 3 and 4 via backfeed through the Unit Auxiliary Transformer (UAT). "Corrective Actions: Actions are in progress to re-establish offsite power supply to emergency buses 3 and 4 via backfeed through the UAT. Investigations are in progress to determine the cause of the SAT failure and the failure of CREV and ARI to auto-initiate." The licensee has notified the NRC Resident Inspector and the State and local emergency agencies. Update provided also added the following reportable notifications due to the event: 10CFR50.72(b)(2) (iv)(A) and(iv)(B) and 10CFR50.72(b)(3)(iv)(A). Notified R2DO (Evans). * * * UPDATE PROVIDED BY MARK SCHALL TO JEFF ROTTON AT 1805 EST ON 11/02/06 * * * Licensee reported that the Unusual Event was terminated at 1745 EST on 11/02/06 after Offsite power was restored to both 4 KV E Buses from the Unit Auxiliary Transformer (UAT) on Unit 2. The #3 and #4 EDGs have been secured and are in Standby. #1 EDG remains inoperable and #2 EDG is presently being Load Tested. The licensee will be notifying the NRC Resident Inspector and the State and local emergency agencies. Notified R2DO (Evans), NRREO (Richards), IRD Manager (Leach), DHS (Barnes), and FEMA (Kuzia). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | IMode2: Power Operation; FMode2: Hot Shutdown | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 0 | 2006-11-01
42954 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-11-01 18:05 | 2006-11-01 18:40 | 2006-11-01 | UNIT SHUTDOWN REQUIRED DUE TO SERVICE WATER LEAK INVOLVING A CONTAINMENT AIR COOLER "On November 1, 2006, at 1530 hours EST, a service water leak was identified in the cooling coil of Containment Air Cooler VHX-4. While this containment air cooler has no safety function for containment cooling, the breached cooling coil represents an inoperable containment boundary. "In accordance with Technical Specification (T.S.) 3.6.1.B1&2, a shutdown was initiated at 1805 hours EST, following expiration of the completion time of 1 hour for restoring containment to operable per T.S. 3.6.1.A.1." The licensee anticipates having the unit in mode 3 Hot Standby by 2205 hours EST, at which time an evaluation involving extent of condition for the required repairs will be performed. The leak is characterized at this time as 300 ml/minute. The licensee informed the NRC Resident Inspector. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-11-01
42953 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2006-11-01 09:08 | 2006-11-01 15:30 | 2006-11-01 | POTENTIAL DEGRADATION IN THE OFFSITE EMERGENCY SIREN NOTIFICATION SYSTEM "A potential loss of the ENS Siren System occurred on 11/1/2006 due to a degradation of the Radio Transmitter System. A successful siren silent test was performed at 0925 on 11/1/2006 to verify full siren operation. The system was returned to full functionality at 1127 on 11/1/2006 by restoring normal transmission capability." The licensee will inform Calvert, Dorchester and St. Mary's Counties and has informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-11-01
42952 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-10-31 | 2006-10-31 20:14 | 2006-10-31 | CONTRACTOR EMPLOYEE FATALITY "This report is being made pursuant to 10CFR50.72(b)(2)(xi), 4-hour Non-Emergency Report due to potential media interest and offsite notification. At approximately 1130 CST on October 31, 2006, the Callaway Plant control room was notified of a non-work related medical emergency involving a Wackenhut contract employee. Onsite medical personnel responded to the scene and administered first aid for an apparent heart attack. An ambulance was dispatched and the individual was transported offsite to a local hospital. The individual was not contaminated. "At approximately 1545 [CST], Callaway Plant was notified that the individual had passed away. Wackenhut notified OSHA of the fatality at 1745 [CST]. At this time no press release is planned." The licensee stated that the employee was a security officer attending classroom training and was not on duty at the time of the incident. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-10-31
42951 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2006-10-31 06:10 | 2006-10-31 13:14 | 2006-10-31 | OFFSITE EMERGENCY SIRENS INOPERABLE "At 0810, Eastern Standard Time, the Harris Nuclear Plant (HNP) determined that the offsite emergency sirens were not capable of being activated. This event requires an 8-hour non-emergency notification per 10CFR 50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. The NRC Senior Resident Inspector was informed. In the event that the sirens had been needed, the State of North Carolina and all four counties within the 10-mile emergency planning zone would have implemented mobile route alerting, as detailed In the Emergency Plan. Tone Alert Radios for notification of residents within the 5-mile emergency planning zone were also available and operable. "The siren failures began to occur during the regularly scheduled 12-hour test at 0510. The most probable cause was a failed 'B' Repeater which rendered the controller at the microwave tower unable to activate the sirens. The 'B' Repeater was removed from the system and all sirens were operating as designed following a satisfactory system test at 0748. The State of North Carolina and all four counties within the 10-mile emergency planning zone were briefed on this occurrence and notified of system restoration by 1145. The plant continues to troubleshoot to determine the cause of the 'B' Repeater failure. In the interim, HNP is conducting frequent interrogation of the siren system to ensure that the system continues to function correctly. The system is now operating with the 'A' Repeater. The 'B' Repeater will be replaced as a part of the troubleshooting and repair plan. "HNP is responding to local media inquiries." See directly related event EN # 42948 of 10/30/06 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-31
42950 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2006-10-31 04:45 | 2006-10-31 10:04 | 2006-10-31 | REACTOR TRIP FROM TURBINE TRIP ON LOW AUTO STOP OIL PRESSURE "Reactor trip at 0445 following a turbine trip. Initial indication of cause is turbine trip due to low auto stop oil pressure. There were no complications in plant response. Plant is stabilized in mode three, heat removal is being maintained by turbine bypass valves." All control rods fully inserted on the trip, no safety or relief valves lifted during the transient, reactor water level 3 isolations did isolate, and the minimum level attained during the transient was -6 inches. Vessel water level is being maintained with normal feedwater flow and the electrical lineup is the normal shut-down electrical lineup. The cause of the low auto stop oil pressure is under investigation. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (M. HUMMER) TO M. RIPLEY AT 1439 EST ON 10/31/06 * * * "In response to questions raised during this event notification, a verbal response was provided to the NRC that an 8 hour notification in accordance with 50.72(b)(3)(iv)(A) [Specified System Actuation] was required. Upon further review it has been determined by Energy Northwest that this notification was not required because all required reporting was satisfied by 50.72(b)(2)(iv)(B)." The licensee will notify the NRC Resident Inspector. Notified R4 DO (D. POWERS) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-10-31
42949 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2006-10-30 13:04 | 2006-10-30 14:25 | 2006-10-30 | ALERT DECLARATION DUE TO ELECTRICAL FIRE AFFECTING ONE ESF TRAIN At 1304 CT on 10/30/06, the licensee declared an Alert due to a fire in a breaker compartment in safety-related 480 VAC Bus 2B-53. The bus feeder breaker tripped open, resulting in the loss of some safety equipment, including one train of emergency feedwater. The fire was immediately extinguished. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (D. HAWKINS) TO W. GOTT AT 1950 EST ON 10/30/06 * * * "ANO-2 Technical Specification 3.6.3.1 action compliance is in progress which includes plans to commence plant shutdown starting at approximately 1908 hours [CT]. Parallel repair efforts are underway to restore the necessary portions of 2B-53 power to allow exiting the Technical Specification 3.6.3.1 LCO's." The licensee notified the NRC Resident Inspector. Notified R4 DO (D. Powers) and R4 IRC (Kennedy). * * * UPDATE FROM LICENSEE (D. HAWKINS) TO W. GOTT AT 2046 EST ON 10/30/06 * * * "At 1925 hours [CT] on 10/30/06, Shutdown of Unit 2 to Hot Standby was commenced in accordance with Technical Specification 3.6.3.1 Action D. This notification satisfies the requirement of 10CFR50.72(b)(2)." The licensee notified the NRC Resident Inspector. Notified R4 DO (D. Powers) and R4 IRC (Kennedy). * * * UPDATE FROM LICENSEE (D. HAWKINS) TO W. GOTT AT 2110 EST ON 10/30/06 * * * "At 1925 hours [CT], Shutdown of Unit 2 was commenced in accordance with Technical Specification 3.6.3.1. The termination criteria of OP-1903.010, Section 6.3 have been met and the Alert has been terminated [at 2000 CST]. The licensee will notify the NRC Resident Inspector. Notified R4 DO (D. Powers), R4 IRC (Kennedy), NRR EO (Lubinski), NSIR (Leach, Blount, Wilson), HQ PAO (Brenner), Comm TA's (Lee, Brown, Skeen, Hatchett, Piccone), EDO Staff (Lamb - message), DHS SWO (Bozzo), FEMA (Casto), DOE (Foote), NRC (McCrossen), USDA (Giles), HHS (Harris) | 0 | 67 | 0 | 0 | 67 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 4 | AR | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) |  |  | 0 | 2006-10-30
42948 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2006-10-30 07:21 | 2006-10-30 13:47 | 2006-10-30 | OFFSITE EMERGENCY SIRENS INOPERABLE "At approximately 0721, Eastern Standard Time, the Harris Nuclear Plant (HNP) Control Room was informed that the offsite emergency sirens were inoperable. This event requires an 8-hour non-emergency notification per 10CFR 50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. The NRC Senior Resident Inspector was informed. The State of North Carolina and all four counties within the 10-mile emergency planning zone were notified and were standing by to implement mobile route alerting if needed, as detailed in the Emergency Plan. Tone Alert Radios for notification of residents within the 5-mile emergency planning zone were also available and operable. "The most probable cause was a controller malfunction at the microwave tower. This controller was reset at 0600. A successful system interrogation was initiated and restored operability of all sirens following the controller reset. Operability of the offsite emergency sirens was restored at 0922 following two successful silent tests. The State of North Carolina and all four counties within the 10-mile emergency planning zone were notified of system restoration by 1035. The cause of the controller malfunction and required corrective action will be determined in accordance with HNP's Corrective Action Program." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-30
42947 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-10-30 08:48 | 2006-10-30 11:56 | 2006-10-30 | REACTOR TRIP "During power operation, at 92% rated power, an automatic reactor trip occurred. The reactor protection signal that caused the reactor trip was steam generator 'B' steam flow greater than feedwater flow coincident with low water level on steam generator 'B.' The cause of the plant transient that led to the reactor trip was a loss of Instrument Bus 1 (Red Channel). Instrument Bus 1 unexpectedly deenergized during the performance of maintenance on the inverter (BRA-111) that feeds Instrument Bus 1. "Following the reactor trip, the auxiliary feedwater pumps automatically started, as designed, due to a low level in the steam generators. "After the trip, non-safety related 4160 Volt AC Bus 4 de-energized and secondary plant feedwater heater 15B relief valve lifted. The cause of the loss of Bus 4 and 158 feedwater heater relief lifting Is under Investigation. "The plant is currently stable and in the hot shutdown (HSD) mode. Power was restored to Instrument Bus 1 at 1018. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) as any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical because of the automatic reactor trip and under 10 CFR 50.72(b)(3)(iv)(A), any event or condition that results in valid actuation of any of the systems listed below because of the actions of the RPS and the automatic start of the AFW pumps." All control rods fully inserted. Decay heat is being removed by feeding the steam generators with AFW and steaming to the Condenser Dump. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM T. BUNKELMAN TO W. GOTT AT 1332 EST ON 10/30/06 * * * "Due to the loss of Bus 4, the running Circulating Water Pump was lost resulting in a loss of normal heat sink to the condenser. The standby Circulating Water Pump was started at 1002 CST and the condenser heat sink was restored." Until the condenser steam dump was restored, the plant was steaming through the steam generator PORVs (atmospheric steam dumps). There is no steam generator tube leakage. The licensee notified the NRC Resident Inspector. Notified R3DO (M. Phillips) | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-10-30
42946 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-29 20:11 | 2006-10-30 01:10 | 2006-10-31 | AUTOMATIC START OF AUXILIARY FEEDWATER DURING MSIV TESTING "This is an 8 hour notification being made to report that a valid ESF auxiliary feed actuation occurred. Salem Unit 2 is in Mode 4 with RHR providing shutdown cooling. 21, 22, and 23 reactor coolant pumps are in service providing forced circulation. "While performing a main steam isolation valve stroke test for maintenance concurrent with main turbine valve surveillance testing, 22 steam generator narrow range level indication shrunk to 7%, which is below the low level trip setpoint of 14%, causing an automatic start of 21 and 22 auxiliary feedwater pumps. There was no other testing or evolutions in progress at the time of the event that contributed to the automatic start of the auxiliary feedwater pumps. "Steam generator parameters at the time of the event where 0 psig and 223 degrees (T-cold). Main condenser vacuum was established. "23 auxiliary feedwater pump was tagged for maintenance and did not start. "22 steam generator level was restored to normal level and the 21 and 22 auxiliary feedwater pumps secured. "There were no personnel injured." During this event, the main turbine governor valves were off their closed seats when the MSIVs were stroked. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY STRAUBMULLER TO KOZAL ON 10/31/2006 AT 0146 * * * "Subsequent to the initial notification, it has been determined that in addition to reporting the auxiliary feedwater pumps starting on low steam generator level, it is required to report that the reactor protection system opened the reactor trip breakers as designed. The reactor trip breakers were closed for surveillance testing of the main turbine. Actuation of the reactor trip breakers is reportable under [10 CFR] 50.72 (b)(3)(iv)(A) for this event." The licensee notified the NRC Resident Inspector. Informed R2DO (GRAY) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-10-30
42945 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-29 15:20 | 2006-10-29 18:02 | 2006-10-29 | MANUAL TRIP DUE TO LOWERING STEAM GENERATOR LEVEL "Unit 2 was operating in Mode 1 at 80% power following refueling holding for stabilization xenon in preparation for incore - excore calibration. An alarm condition for steam generator 2-03 indicating Steam - Feedwater flow mismatch was observed. Manual control of the feed regulating valve was taken, but operators were unable to control feed flow while steam generator 2-03 level continued to decrease. A manual reactor trip was initiated and the reactor was tripped. Auxiliary feedwater automatically started on low-low level in steam generators. All systems responded normally during and following the trip. Unit 2 is being maintained in Mode 3 pending the event investigation." All control rods fully inserted. RCPs are in operation transferring decay heat to the steam generators. The MSIV's are open with the steam generators discharging steam to the main condensers using the steam dumps. AFW is maintaining steam generator water levels. Unit 1 was not affected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-10-29
42944 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2006-10-29 13:02 | 2006-10-29 13:38 | 2006-10-29 | LOSS OF NOAA TRANSMITTER The facility lost the Ames Hill NOAA transmitter due to weather conditions. Compensatory measures are in place and the vendor has been notified and is enroute to shift the power supply to back up. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM K. MURPHY TO W. GOTT AT 1522 ON 10/29/06 * * * The Ames Hill NOAA transmitter was restored at 1505. The licensee will notify the NRC Resident Inspector. Notified R1DO (J. Noggle) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-29
42943 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2006-10-28 17:09 | 2006-10-28 21:52 | 2006-11-07 | UNANALYZED CONDITION "An 8 hour notification per 10 CFR 50.72(b)(3)(ii)(B) is being made due to discovery of a previously unanalyzed plant condition. The chemical volume control system (CVCS) charging line is a high energy line susceptible, within design space, to a rupture that could result in pipe whip and an impingement condition. The containment penetration (M-3) for the charging line is directly below the high-pressure safety injection (HPSI) header penetrations (M-5 & M-6). Due to this proximity, a failure of the charging line could impact the SI-1503 class HPSI line (M-6) causing damage to the header and rendering it incapable of fulfilling its design function. The two HPSI headers are different class piping with the M-5 penetration being a 2500 psig (SI - 2501 Class) line and the M-6 penetration being a 1500 psig (SI-1503 Class) line. The 2500 psig line is constructed of robust enough piping to not be susceptible to failure, however both HPSI headers are cross connected prior to location of concern. Although both HPSI and CVCS breaks are isolable, operator action would be required to identify and isolate the break location. The possible result of a high energy line break of charging piping could result in all three pipe headers being inoperable until manual action could be taken to isolate leakage on the 1500 psig HPSI line. Plant is currently shutdown for refueling outage with scheduled startup of November 21, 2006." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY ERICK MATZKE TO JEFF ROTTON AT 1119 EST ON 11/07/06 * * * "Additional review of the stations design and licensing basis has determined that the charging and high pressure safety injection systems are correctly designed to the stations high energy line break criteria for lines inside containment. This situation is not reportable and therefore event notification 42943 is being withdrawn." The licensee notified the NRC Resident Inspector. Notified R4DO (Clark) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-10-28
42942 | -1 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-10-28 12:23 | 2006-10-28 16:02 | 2006-11-09 | SPECIFIED SYSTEM ACTUATION "During plant cooldown/depressurization in Mode 3, an Over Temperature (OT) Delta Temperature reactor trip signal was generated. The reactor Trip Breakers opened as designed (all rods were previously inserted). Additionally, a low Tavg/P-4 Feedwater Isolation Signal was generated and all Bypass Feedwater Regulation Valves closed (open for long-cycle recirculation operation). No Feedwater Isolation Valves were open at the time. All systems performed as designed. "Actual loop Delta T's (Th - Tc) never exceeded 3.3 degrees F, well below the calculated OT Delta T setpoint. But plant Delta T calculations are based on narrow range Th and Tc instruments with scaling to low limits. When actual plant temperature was lowered to the lower limits of each instrument, calculated Delta T increased to the OT Delta T setpoint causing the reactor trip signal. Existing procedure guidance did not adequately ensure that the reactor trip breakers are open prior to initiating a partial plant cooldown. "The plant was stabilized. The long-cycle recirculation was re-established and plant cooldown/depressurization was recommenced, as originally planned to 340 degrees F and 925 psig." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 11/9/2006 AT 12:19 FROM THOMAS G. PETRAK TO MARK ABRAMOVITZ * * * "Alvin W. Vogtle, Unit 1, Operating License no. NPF-68, Event Notification #42942 is retracted. The event reported in the notification which occurred during the Unit 1 cooldown in Mode 3 was not representative of the conditions under which the Over Temperature Delta Temperature (OTDT) setpoint is intended to operate. The setpoint is intended to provide protection while the reactor is in Modes 1 and 2. As the cooldown progressed from Normal Operating Pressure and Temperature (NOPT), eventually the Reactor Coolant System (RCS) hot and cold leg temperature indications reached the low end of their ranges or scales. Further reductions of temperature resulted in artificial indications of core power (delta-T) that cannot be relied upon as a valid input to the OTDT protective function. "The actuation of the Reactor Protection System (RPS) is not considered to be a valid actuation. As such, this is not reportable under 10 CFR 50.72(b)(3)(iv)(A). "The Unit 1 Feedwater Isolation caused from the OTDT reactor trip is not a function is listed in 10 CFR 50.72(b) (3)(iv)(B) as a system whose actuation is required to be reported under 10 CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-10-28
42941 | 0 | ST LUKES HOSPITAL |  |  |  |  | 2006-10-26 15:00 | 2006-10-27 13:22 | 2006-10-27 | MEDICAL EVENT "On October 26, 2006 an incident regarding a high-dose rate (HDR) mammosite treatment was discovered. "At approximately 15:00 hours the physicist was verifying source positions and dwell times prior to treatment number eight of ten. The physicist noted that the first (most distal) source position was different from previous treatments (94.5 cm vs. 92.3 cm). When he queried the dosimetrists about the change, he was told that a different value was given for the measurement of the overall catheter length. The measured catheter length for the first seven treatments was 96.6 cm, while the most recent measurement gave 96.75 cm. The dosimetrist entered 95.15 cm (subtracting the 1.6 cm correction factor for the actual position of the most distal source dwell point within the catheter). However, this did not explain a 2.2 cm difference in the first dwell position. "The subsequent investigation into the discrepancy revealed that the usable catheter length entered into the planning computer was 93.0 cm rather than the correct value of 95 cm. This erroneous usable catheter length was used for the first seven treatments, which resulted in an unplanned dose to tissue proximal to the mammosite balloon. It is presently believed that a typographical error occurred in entering the usable catheter length into the treatment planning computer that was the root cause of the unplanned dose. "The referring physician and patient have been notified of the event. The authorized user (radiation oncologist) is currently evaluating the clinical status of the patient. Further treatments are on hold pending a clinical decision." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM C. FLANNERY (FSME) TO W. GOTT AT 1641 ON 10/27/06 * * * This event has been reviewed by the NRC medical review committee and determined to be a reportable medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-10-27
42940 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2006-10-27 09:15 | 2006-10-27 12:03 | 2006-10-27 | EMERGENCY OPERATIONS FACILITY NON OPERATIONAL DUE TO PLANNED MAINTENANCE "The Emergency Operations Facility (EOF) became non operational on October 27, 2006, at 0915 due to planned maintenance on the electrical power distribution for that facility. This call is required due to not being able to promptly restore the facility in the event of an accident as noted in NUREG 1022 Section 3.2.13. The maintenance should be completed by October 28, 2006. "The backup EOF will be used during this maintenance." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-27
42939 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2006-10-27 03:37 | 2006-10-27 10:02 | 2006-11-17 | CONTAINMENT PATHWAY DECLARED INOPERABLE FOLLOWING LOCAL LEAK RATE TESTING "This condition is being reported in accordance with the requirements of 10CFR50.72(b)(3)(ii) as an event or condition that results in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. "During local leak rate testing (LLRT) of the 'B' reactor feed line to the reactor, both primary containment boundary check valves (RF-CV-13CV and RF-CV-14CV) failed LLRT. Efforts to quantify the leak rate were unsuccessful. The maximum leakage indicated on the test equipment used is 424 standard cubic feet per hour (SCFH). The allowable leakage (La) for Primary Containment is 317.41 SCFH. The affected primary containment pathway was declared inoperable. CNS is in MODE 5 for refueling with vessel level greater than 21 feet above the flange and the spent fuel pool gates removed. No fuel movements or operations with the potential to drain the reactor vessel were in progress. Primary containment is not required per CNS Technical Specifications in this mode of operation. "The NRC Senior Resident Inspector has been notified." * * * RETRACTION FROM FLEMING TO HUFFMAN AT 1500 EST ON 11/17/06 * * * "This notification is being made to retract Event Notification #42939 which reported a Primary Containment isolation pathway being declared inoperable following Local Leak Rate Testing (LLRT); specifically, the 'B' reactor feed line containment boundary inboard and outboard check valves. CNS has determined that the LLRT test method established test conditions that were not representative of the conditions under which the check valves would be required to perform their safety function. Inspection, in-situ testing and evaluation demonstrated the reactor feed line check valves would have performed their isolation functions during credible accident conditions. Thus, the condition was not a serious degradation of a principal safety barrier. "During the normal plant shutdown to refueling outage RE23 with gradually decreasing feed flow, the check valve discs had not completely settled into the valve seats. Due to the slow pressurization rate of the LLRT working medium (air), sufficient differential pressure across the valve could not be developed which resulted in failing the test. Inspection of the check valves in their as-found condition revealed that a slight contact between the disc and the top of seat left a crescent shaped gap which, at the maximum (the bottom), was no more than 1/2 inch. An in-situ test measured the force needed to settle the disc into the seat and found it equated to a flow related pressure drop of less than 1 psid. A review of accident sequences concluded that post-accident pressurization of the feed lines would have closed the check valves for all credible accident scenarios. Check valve disc to pivot arm spacing adjustments were made to ensure sufficient disc float to reseat and fully close the valve from any open position. Subsequently, LLRT results were satisfactory." The licensee notified the NRC Resident Inspector. R4DO (Johnson) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-10-27
42938 | 0 | PALO VERDE | 1 |  | 3 | [1] CE,[2] CE,[3] CE | 2006-10-26 23:53 | 2006-10-27 07:03 | 2006-10-27 | LOSS OF POWER TO THE UNIT 1 AND UNIT 3 TRAIN B SAFETY BUSES WITH EMERGENCY DIESEL GENERATOR ACTUATION "The following event description is based on information currently available, if through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 26, 2006, at approximately 23:53 Mountain Standard Time (MST) a valid actuation of the Palo Verde Nuclear Generating Station Unit 1 Train B Emergency Diesel Generator (EDG) and Unit 3 Train B EDG occurred as a result of undervoltage on their respective safety buses. Both EDGs started and loaded as designed. No Emergency Plan declaration was made and none was required. "The loss of power to the two safety buses was the result of an apparent spurious protective relay actuation of Startup Transformer X01 output breakers to Unit 1 NAN-S06 and Unit 3 NAN-S06 busses. Unit 1 NAN-S06 bus was being supplied by its Alternate breaker (1ENANS06F) and Unit 3 NAN-S06 was being supplied by its Normal breaker (3ENANS06C). Prior to the event, maintenance personnel were restoring potential Transformer (PT) fuses at Unit 1 breaker 1ENANS06, Cubicle G. Preliminary information is that the two simultaneous LOP conditions occurred when the outer doors were closed on 1ENANS06, Cubicle G. This condition apparently caused the output breakers of Startup Transformer X01 to open. There was no electrical fault or damage to any electrical components. "Both Units 1 and 3 entered Technical Specification LCO 3.8.1 Condition A for one (of two) required offsite circuits inoperable. [The licensee is] proceeding with restoration of Normal offsite power to each safety bus in Units 1 and 3. Once offsite power is restored, the LCOs will be exited and the Unit 1 and 3 train B EDGs will be returned to standby. "Both Unit 1 and Unit 3 were at approximately 100% power, at normal operating temperature and pressure prior to and following the EDG actuations. Unit 2 was defueled and was not impacted by the electrical disturbance. No other ESF actuations occurred and none were required. No major equipment was inoperable prior to the event that contributed to the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee notified the NRC Resident Inspector. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation |  | Power Operation | Power Operation |  | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-10-27
42937 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-27 03:08 | 2006-10-27 05:06 | 2006-10-27 | MANUAL REACTOR SCRAM DUE TO LOSS OF BOTH MAIN FEED PUMPS The licensee was performing load reject testing on the Unit 2 turbine generator when oscillations were observed on the plant steam dump system. These oscillations caused a high steam generator water level that caused both Main Feed Pumps (MFP) to trip. Upon receiving this indication the licensee manually tripped the reactor. All Auxiliary Feed Water (AFW) pumps started as expected. All rods inserted as expected. Decay heat is being removed using AFW supplying both steam generators and steaming to the steam dumps. The plant is in a normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-10-27
42936 | 0 | AREVA NP INC RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2006-10-23 10:50 | 2006-10-26 21:09 | 2006-10-26 | WORKERS EXPOSED TO HYDROGEN FLORIDE RELEASE "On 10/23/06 at approximately 1050 hours, during a routine area walk-down of Dry Conversion Facility (DCF) 4th level an operator noticed the pungent/repulsive smell of hydrogen fluoride (HF) vapor near the L-3 UF6 to UO2 conversion vessel and back-up filter vessels. [Note: The odor threshold for HF is approximately 0.042 ppm.] He immediately exited the area, placed it on respiratory protection required status and then notified a Health and Safety Technician (HST). "The operator donned respiratory protection equipment and 'Dragered' the suspect area for HF vapor and the results were positive. The HST also pulled samples for airborne radioactivity and none were observed. The operator notified the DCF control room and shutdown of the affected was initiated. "This report is being made because it has the potential for meeting the following two 10 CFR 70 Appendix A, 24 hour reporting Criteria. "1. Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the ISA and which results in an accident sequence with high consequence that is not at least highly unlikely, or an accident sequence with intermediate consequence that is not at least unlikely. "The location of the HF leak was in a Dry Conversion UF6 to UO2 conversion vessel. This major component is in the powder production process system. However, the boundary of UF6 Vaporization process system ends at the conversion vessel inlet. Accident sequence 810-5 for UF6 Vaporization process system, as reported in the ISA Summary, clearly bounds the conditions associated with this event. The protections listed in this accident sequence are also applicable to this event. However, this condition is not specifically covered in the accident evaluation of the powder production process system. Because this condition was not specifically evaluated in the powder production process system accident evaluation, it is not clear that this reportability criterion does not apply. "3. An acute chemical exposure to an individual from licensed material or hazardous chemicals produced from licensed material that could: a. Lead to irreversible or other serious, long lasting health effects to a worker b. Cause mild transient health effects to any Individual located outside of the controlled area. "Based on the low odor detection threshold for HF and the operator's response to immediately leave the area until protective equipment had been donned, the subsequent measured HF concentrations, estimated exposure time and the physical evidence of the individual exposed to HF, long lasting serious health effects are not expected. "All other conversion units were shut down at approximately 1300 on 10/26/2006 to further evaluate the other unit's conditions although no leakage of HF or radioactivity has occurred." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | ACUTE CHEMICAL EXPOSURE | [8 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(1) | PART 70 APP A (b)(3) |  |  | 0 | 2006-10-26
42935 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2006-05-25 | 2006-10-26 17:34 | 2006-10-26 | AGREEMENT STATE REPORT The State provided the following information via facsimile: "The SC Department of Health and Environmental Control was notified on Wednesday, October 18, 2006, by letter dated October 9, 2006, that a possible Medical Event involving a fetus took place in May 2006. According to a letter from the RSO at McLeod Regional Medical Center, a female patient was dosed with 14 microcuries of Iodine 131 on May 24, 2006, and 15 millicuries of Technetium 99m on May 25 as a prelude to a Nuclear Medicine Thyroid Therapy Ablation. The patient denied the possibility of pregnancy and signed an informed consent specifically addressing pregnancy and fetal exposure. This was following an explanation by the Radiologist of the exact procedure. A dose of Iodine 131 in the amount of 14.8 millicuries was then given the patient for the thyroid ablation. "The patient's OB/GYN physician notified the radiology department as of October 9, 2006, that the patient is now approximately 32 to 34 weeks pregnant. A calculation is being done to determine the exposure dose to the fetus and fetal thyroid. This information is to be sent to the Department once completed. This is all the information available on this situation and determination has not been made that it is a medical event. The investigation is still ongoing. The incident will be updated once additional material is received." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2006-11-01
42934 | 0 | NAT INST FOR OCC SAFETY AND HEALTH |  |  |  |  | 1996-10-01 | 2006-10-25 15:40 | 2006-10-26 | THREE SEALED TRITIUM SOURCES MISSING FROM INVENTORY The National Institute for Occupational Safety and Health (NIOSH) in Cincinnati, OH reported that three electron capture devices with a total activity of 658 milliCuries of tritium are missing. The devices were last physically verified in inventory in October 1996. The devices were removed from the inventory listing in 1997 and no paperwork related to their disposition can be located. The institute contacted the device manufacturer, excess property listings, past RSO's, past device users, and other universities and institutions with negative results. The devices are now considered lost. The following two sources were in the same Baseline Model 1030A Gas Chromatograph (serial # 232): Valco Industries Model 140 electron capture detector (serial # 158). The initial activity was 1000 mCi. Current activity is approximately 387 mCi. Valco Industries Model 140 electron capture detector (serial # 124) . The initial activity was 1000 mCi. Current activity is approximately 218 mCi. The third source was a Scentex electron capture detector in a Scentor Model Gas Chromatograph (serial # 40K191). Initial activity was 150 mCi. Current activity is approximately 53 mCi. The serial number of the detector is not known. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-10-25
42933 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2006-10-25 02:48 | 2006-10-25 06:32 | 2006-10-25 | MANUAL REACTOR TRIP AFTER A 100% LOAD REJECTION "On October 25, 2006, at approximately 0247 hours (EDT), Main Control Room operators observed indications of a 100% load rejection and manually tripped the reactor at 0248 hours (EDT). During the event, Main Control Room operators received an alarm indicating that one or both pressurizer PORVs lifted briefly. The PORV(s) reclosed as designed. The reactor is currently stable in Mode 3. "During the event, the steam generator PORVs briefly opened and re-closed, as expected. All controls rods indicated fully inserted following the reactor trip. The normal post-trip electrical lineup is providing power to the plant and the electrical system is stable at this time. Decay heat is currently being removed by use of the normal feedwater system and the condenser steam dumps. "The cause of this event is under investigation. Follow-up notifications will be provided if important new information is obtained or plant conditions significantly change." The licensee reported no steam generator tube leakage i.e. no radionuclide release during the brief lifting of the steam generator PORVs. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 10/25/2006 AT 0941 FROM G. SANDERS TO M. ABRAMOVITZ * * * "Subsequent to the initial notification, it has been determined that the automatic initiation of the Auxiliary Feedwater (AFW) System is also reportable under 10 CFR 50.72(b)(3)(iv)(A), Specified System Actuation. The AFW System automatically actuated as expected during the event in response to the secondary plant transient." The licensee notified the NRC Resident Inspector. Notified the R2DO (Ernestes). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-10-25
42932 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-10-23 02:30 | 2006-10-24 14:51 | 2006-10-24 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via e-mail: "At 2:30 a.m. a Smith Emery employee was taking backscatter measurements on Highway 99 North in Stockton, California just south of the Fremont off ramp. One lane was restricted to traffic while the Smith Emery employee took backscatter measurements to determine asphalt density. Shortly thereafter a semi-tractor and trailer crossed the barriers into the restricted lane and ran over the CPN MC3 gauge (#m37107963). The gauge outer case was destroyed and the source rod was broken off and carried away from the gauge down the road. The source rod contained 10 mCi of cesium 137. The 50 mCi americium source remained affixed to the portion of the gauge case that was intact. The licensee quickly notified the California Department of Emergency Services, who notified the Radiological Health Branch. Following the incident, the licensee restricted access to the area where the gauge was ran over and awaited the RSO to arrive. The RSO arrived around 6:30 am and with assistance from the Stockton FD, determined the gauge sources were intact and placed them in their transport case to transport to CPN, the gauge manufacturer. CPN leak tested the sources and there was no leakage or contamination found. "CA Assignment number 102306" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-10-27
42931 | 0 | U.S. AIR FORCE |  |  |  |  | 2006-03-30 12:00 | 2006-10-24 17:42 | 2006-10-24 | LOSS OF TWO AMERICIUM - 241 SOURCES DUE TO AIRCRAFT MISHAP A representative from the Air Force Master Material Licensee reported that a U.S Air Force F-16 aircraft with a LANTIRN (Low Altitude Navigation and Targeting IR for Night) , targeting and ranging device attached to the aircraft, crashed in Utah's Great Salt Lake test range area near Hill AFB. The LANTIRN pod contained two 4 microCurie Am-241sources (a total of 8 micro Curie). The USAF is evaluating whether or not a recovery effort will take place. The licensee discussed this issue with Rachel Browder NRC Region 4. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | UT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-10-24
42930 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-10-24 04:00 | 2006-10-24 15:23 | 2006-10-24 | AGREEMENT STATE REPORT - BOOTH RADIOGRAPHY SOURCE DISCONNECTED AND SUBSEQUENTLY RECONNECTED "N.C. Radiation Protection Section was notified on 24 Oct. 2006 by the RSO for Flowserve US Inc. of a booth radiography source disconnect. The sealed source involved is reported as approximately 4.3 Curies of Ir-192. Discovery of the disconnect and subsequent actions were made in accordance with licensee policy and procedures. The licensee is controlling access to the booth, allowing for a safe and well considered response. The licensee is in contact with the vender of the camera and associated equipment in an effort to determine the best course of action (i.e. source recovery). "The NC Radiation Protection Section is working in conjunction with the licensee and vender and will continue to update NRC as appropriate. "The Flowserve Inc. RSO has reported that by following directions from vendor, the source was successfully retrieved and is in the safe, shielded and secure position. He further reports he is immediately replacing all similar equipment and returning the old equipment (including the specific malfunctioning equipment associated with this incident) to the vendor. Both Flowserve and the equipment vendor are planning after action reports to determine root cause if possible. "North Carolina Ref. NC-06-33." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-10-27
42929 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2006-10-24 01:42 | 2006-10-24 09:08 | 2006-11-10 | HIGH PRESSURE CORE SPRAY (HPCS) DECLARED INOPERABLE FOR APPROX. 3.4 HOURS "At 0142 on October 24, 2006, while aligning the High Pressure Core Spray system for surveillance testing of the Reactor Core Isolation Cooling System Storage Tank Level instrumentation, 1E22-F015, the Suppression Pool suction valve for the High Pressure Core Spray pump, failed to stroke fully open. High Pressure Core Spray was declared inoperable as a result. This event is considered a loss of a single train system needed to mitigate the consequences of an accident. The High Pressure Core Spray system was restored to an operable condition at 0506 on October 24, 2006 after the suction valve was successfully stroked open and the HPCS suction source was aligned to the Suppression Pool in accordance with Technical Specification Limiting Condition for Operation 3.5.1. The cause of the event is currently under investigation." All other Emergency Core Cooling systems were fully operable during the time period HPCS was inoperable. The Senior Resident Inspector has been notified by the licensee. * * * RETRACTION FROM SIMPSON TO HUFFMAN AT 1534 EST ON 11/10/06 * * * "Upon further review of this event, the High Pressure Core Spray (HPCS) system remained operable. Based upon valve motor operator thrust verification testing data and troubleshooting, the cause of the suppression pool suction valve for the HPCS pump stopping in mid-position was determined to be tripping of the open-direction torque switch prior to the open limit switch setpoint. "Normally, the condition of the open-direction torque switch has no safety-related consequence since the torque switch is bypassed during design basis events and the valve's motor gearing capability is sufficient to open the valve when the torque switch is bypassed. "During this event, as directed by the surveillance test procedure, operators placed the HPCS Motor Operated Valve (MOV) test switch to the test position which resulted in the open-direction torque switch not being bypassed (i.e., was in the circuit) during repositioning of the HPCS suppression pool suction valve. Due to placing the HPCS MOV test switch to test, operators entered the action of Operational Requirements Manual section 2.5.2 (Motor Operated Valves Thermal Overload Protection). The action requires operators to return the MOV test switch to normal (removing the torque switch from the circuit) if an emergency condition occurs requiring valve repositioning. "As operators were opening the HPCS suppression pool suction valve for testing, suction for the HPCS pump was aligned from the RCIC storage tank. When the HPCS suction valve from suppression pool stopped in mid-position, the HPCS suction valve from the RCIC storage tank was still fully open (per design, stays full open until the HPCS suppression pool suction valve is full open). Therefore, if an accident occurred requiring HPCS to initiate and inject water into the reactor pressure vessel during this event suction would have initiated from the RCIC storage tank. The HPCS system can take suction from either the RCIC storage tank or the suppression pool, and a HPCS initiation signal does not automatically swap HPCS pump suction from the RCIC storage tank to the suppression pool or vice versa. "The operators immediately recognized the HPCS suppression pool suction valve did not fully open. If an accident condition occurred, operators would reposition the HPCS MOV test switch to Normal (to bypass the open torque switch). In the event a condition requiring a HPCS suction transfer to the suppression pool occurred, the suppression pool suction valve would fully open and the RCIC storage tank suction valve would fully close, completing the required suction shift. "On this basis, the HPCS system was capable of performing its function to mitigate the consequences of an accident and this issue is not reportable under 10 CFR 50.72(b)(3)(v)(D)." The NRC Resident was notified of this retraction. R3DO(Cameron) notified. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-10-24
42928 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-10-22 18:15 | 2006-10-23 14:49 | 2006-11-08 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED TROXLER GAUGE The NRC Operations Center received the following information from the State of Colorado via fax: "The Radiation Management Program of the Colorado Department of Public Health and Environment received telephone notification on Monday 23 October 06 regarding the theft of a portable moisture density gauge. "Radioactive Materials Involved: a Troxler 3430 gauge, serial number 28201 containing 333 MBq (9 mCi) of Cesium 137 and 1.63 GBq (44 mCi) of Am-241/Be. "Event details: The theft occurred at the residence of an employee of the licensee ( DELETED) at 6:15 PM on Sunday 22 Oct 06. The Troxler gauge was reported to be in a locked case, chained and locked in the bed of a Ford Ranger. The employee witnessed the theft of the truck from his garage with the gauge secured in the bed of the truck. "The local police were called at the time of the theft but (DELETED) did not have a police contact name or phone number at the time of this report." Notification was made by licensee RSO to the State of Colorado. CO Incident Number 42928. * * * UPDATE FROM STATE (PENTECOST) TO M. RIPLEY AT 1129 EST ON 11/8/06 * * * The State provided the following information via email: "On 7 Nov 06, the stolen Ford ranger was recovered by Lakewood [CO] police without the gauge. Later that evening, the Thornton [CO] police recovered the gauge within a different stolen vehicle. The gauge and transport case have been returned undamaged and properly functioning to Acura Engineering." Notified R4 DO (J. Clark), NMSS EO (G. Morell) and ILTAB (Email) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2006-10-26
42927 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-10-20 16:00 | 2006-10-23 11:26 | 2006-10-27 | AGREEMENT STATE REPORT FROM OHIO: CONTAMINATION INCIDENT IN SOURCE HANDLING FACILITIES Agreements State report received via e-mail Event Cause: Inadequate Procedure "The Bureau was notified at approximately 4:00 PM on Friday, 10/20/06 that the licensee experienced a contamination incident in their source handling facilities. The licensee stated that a 10 mCi Cesium-137 source had been breached during source disposal operations. The source was breached when a source holder was being cut or drilled to remove the source. Contamination was detected on the individual conducting the source removal operations, throughout the source storage room, and outside in the source handling area. Note that these are all controlled access/restricted areas within the facility. The contamination on the individual was located on the clothing, hair, arms and hands. The individual underwent onsite decontamination and was sent to a local hospital as a precautionary measure. As of today (10/23/06) there is still some residual contamination on the individual's finger tips; however, further scrubbing to remove this contamination may cause breakdown to the skin in that area. The individual is currently wearing gloves in an attempt to sweat out the residual cesium contamination. The individual is scheduled for a whole body scan on Wednesday, 10/25/06. The source handling area was secured and closed to all personnel over the weekend. A decontamination contractor has been retained by the licensee to arrive on site on Monday, 10/23/06. A Bureau of Radiation Protection inspector will arrive on site on Wednesday, 10/25/06 to assess the contractor's decontamination efforts and to further investigate the circumstances that caused the contamination event. This information is current as of 10:00 AM on Monday, 10/23/06." "Corrective Actions: Not Reported Contamination to person: 0.010 Curies, 0.37 GBq of Cs-137 (Personnel Contamination) Surface Contamination: 0.01 curies, 0.37 GBq of Cs-137 (Temporary Rad. Controls) Form of Radioactive: Sealed Source Source Used: Fixed Gauge Reporting Requirement: 20.2203 30 day report - Reports of exposures, radiation levels, and concentrations of radioactive material exceeding the constraints or limits. Mode Reported: Telephone Reference Number: H 2006-092 Entry Date: 10/23/2006 Coder Initials: SMJ Reference Type: Agreement State Event Report. * * * UPDATE FROM OHIO DEPARTMENT OF HEALTH (MICHAEL SNEE) TO JOE O'HARA ON 10/25/06 AT 1036 EDT VIA E-MAIL * * * "Two separate Cs-137 sources were involved in the incident. Both were in TN model 5178/5178A source holders. The licensee's employee could not open the holders to remove the sources for disposal. The employee misunderstood where the sources were located in the holders and cut one holder (containing a 11 mCi source) with a bandsaw while drilling into the other holder (containing a 26 mCi source). The saw cut into the source and the drill bit broke and stuck in the source capsule. The contamination was contained to the secure source handling area. A contractor is on site to perform the facility decontamination." Notified the R3DO (Ring) and NMSS EO (Wastler) * * * UPDATE FROM OHIO DEPARTMENT OF HEALTH (STEVEN JAMES) TO JASON KOZAL ON 10/27/06 AT 1119 EDT * * * The State provided the following information via email: "Bureau staff visited the site on Wednesday, 10/25/06 to meet with the licensee and the decontamination contractor to review the circumstances which led to the contamination of the facility and the licensee's worker, as well as the decontamination efforts taken to date. Further investigation will be conducted by the Bureau. The contaminated employee underwent a whole body count on Thursday, 10/26/06. The results of that scan indicated the presence of 3.61 nanocuries in the lungs. The count will be repeated in two weeks. Note that the individual has been described by the licensee as a 'heavy smoker.' The individual is scheduled to undergo two 24-hour urine collections over the coming weekend for analysis on Monday, 10/30/06. Dose estimates will be prepared by the licensee and their medical consultant after the urine samples have been analyzed." Notified the R3DO (Ring) and NMSS EO (C. Flannery) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2006-10-26
42926 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-10-21 20:12 | 2006-10-21 23:23 | 2006-10-21 | FITNESS FOR DUTY A contract supervisor tested positive for alcohol during a for-cause test. The supervisor's plant access has been suspended. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2006-10-21
42925 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2006-10-21 15:48 | 2006-10-21 21:37 | 2006-10-21 | AUTOMATIC REACTOR TRIP DUE TO CONTROL ELEMENT ASSEMBLY POSITION TRANSMITTER OUTPUT DEVIATIONS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 21, 2006 at approximately 1549 MST Palo Verde Unit 1 experienced a reactor trip (RPS actuation) from 100% rated thermal power due to low departure from nucleate boiling (DNBR) trips on all four channels of the core protection calculators (CPCs). The unit was at normal temperature and pressure prior to the trip. "Several minutes prior to the Reactor Trip, RSPT#1 (Reed Switch Position Transmitter) CEA deviation alarms were received for CEA#29 (Shutdown Group B CEA). Operators observed that the magnitude of the deviation was fluctuating erratically. While investigating the alarms CEAC #1 Sensor Fail alarms were received and at 1549 MST, the Reactor automatically tripped on a CPC generated Lo DNBR trips on all 4 channels of CPCs. The apparent cause is presently suspected to be a failure of RSPT#1. An investigation has commenced to determine the root cause of the reactor trip. "All of the control rods fully inserted into the core. The Steam Bypass Control System operated as designed, directing steam flow to the condenser. No main steam or primary relief valves lifted and none were required. There was no loss of heat removal capability or loss of safety functions associated with the event. Electrical buses transferred to offsite power as designed. The Shift Manager determined this event was an uncomplicated reactor trip. No significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event nor contributed to the event. "Unit 1 is stable at normal operating temperature and pressure in Mode 3. No ESF actuations occurred and none were required. The event did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident was notified at 17:38 MST." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-10-21
42924 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-21 15:58 | 2006-10-21 18:26 | 2006-10-21 | OFFSITE MEDICAL TREATMENT OF POTENTIALLY CONTAMINATED CONTRACT EMPLOYEE "A contract employee experienced heat exhaustion while working in the Reactor Containment Building in a contaminated area and was considered potentially contaminated because the initial survey for radioactive contamination had not been completed prior to transporting the employee offsite for medical treatment." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (B. SCARBOROUGH) TO M. RIPLEY AT 1912 EDT ON 10/21/06 * * * At 1758 CDT on 10/21/06, the licensee was notified by their Health Physics Dept. that the contract employee was transported to the Matagorda Hospital in Bay City, TX and was found not to be contaminated. Additionally, all instruments and equipment used in the incident were surveyed and no contamination was found. The licensee notified the NRC Resident Inspector. Notified R4 DO (D. Powers). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2006-10-21
42923 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2006-10-21 07:35 | 2006-10-21 10:15 | 2006-10-21 | NOTIFICATION TO STATE OF CHEMICAL AND SEWAGE RELEASE "Notification of the State [Maryland Department of the Environment] per the NPDES [National Pollution Discharge Elimination System] permit of the release of a maximum of 20 gallons of sewage and chemicals from a portable toilet to the bay through a storm drain." A portable toilet was blown-over by high winds at the site. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-10-21
42922 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-10-20 09:25 | 2006-10-20 11:17 | 2006-10-20 | PLANNED MAINTENANCE FOR HATCH EMERGENCY HVAC HEALTH PHYSICS CONTROL POINT/CHEMISTRY LAB AREA "On 10/20/2006, the emergency HVAC for the Hatch Nuclear Plant's Health Physics (HP) Control Point /Chemistry Lab area was removed from service for planned corrective maintenance and inspections and testing activities. The HP emergency HVAC is required for functionality of the Operations Support Center (OSC). This area is normally utilized by HP/Chem personnel for analysis of samples during normal as well as emergency conditions. These work activities are planned to be performed and completed within a 12 hour work shift. During the time these activities are being performed, the HP emergency HVAC and filter train will not be available for operation for approximately four (4) hours. As such, the HP emergency HVAC will be rendered non-functional during the performance of this work activity. The OSC working area itself, however, does not lose EP functionality throughout this evolution. "The HP emergency HVAC provides climate control for Health Physics control point and Chemistry Lab areas. If an emergency condition requiring activation of the OSC occurs during the time these work activities are being performed, then contingency plans call for utilization of the HP Control Point/Chemistry Lab areas as long as radiological conditions allow. Respiratory protection equipment will be utilized as appropriate for emergency responders until the HP emergency HVAC is returned to service. This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the evolution." The NRC Resident Inspector was notified of this event by the licensee. | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-20
42921 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2006-10-19 17:56 | 2006-10-19 22:35 | 2006-10-20 | AUTOMATIC SCRAM FOLLOWING SPONTANEOUS FEEDWATER VALVE CLOSURE "At 1756 CDT with the plant operating at 100% power, a reactor scram occurred in response to a reactor water level 3 signal from an apparent loss of feedwater. Both feedwater injection lines isolated when isolation valves were inadvertently closed, The cause of the isolation valve closure is under investigation. "When reactor water level lowered to level 2, high pressure core spray (HPCS) initiated automatically and recovered water level. The reactor core isolation cooling system (RCIC) was tagged out for maintenance at the time of the event. "Following the scram, main steam isolation valves isolated on low main steam header pressure. As a result, reactor pressure control was being controlled with the safety relief valves. SRV pressure control in turn led to EOP entry conditions on containment pressure and suppression pool level. "Both feedwater lines were opened, and normal reactor level control was restored. The MSIV's were opened and pressure control was returned to the turbine bypass valves and the main condenser. "Initial indications are that all plant equipment functioned as designed with the exception of the 'B' feed pump which experienced an apparent seal failure. The plant is stable in Mode 3. All plant conditions are understood. "This event is being reported in accordance with 10CRF50.72(b)(2) as an RPS actuation and an injection of HPCS into the reactor vessel, and in accordance with 10CRF50.72(b)(3) as a loss of safety function of HPCS, as it was manually disabled during recovery from the event. The HPCS Injection valve was manually overridden closed for 76 minutes. In addition,' containment isolation valves in multiple systems actuated in response to the RPV level 2 signal." Reactor vessel water level lowered to below level 2. Decay heat is being removed by normal feedwater to the reactor vessel steaming to the main condenser. Offsite power is available and stable. Emergency Diesel Generators are available. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (D. WILLIAMSON) TO M. RIPLEY 1740 EDT ON 10/20/06 * * * "The closure signal to the main feedwater header isolation valves occurred when part of a chart recorder above the isolation valve control switches was dropped by an operator. The operator was attempting to adjust the paper drive mechanism in the recorder, and accidentally dropped the paper cartridge, which struck the 'CLOSE' pushbuttons on the isolation valve control switches. "Following the scram, there was a delay in placing the reactor mode switch in the 'SHUTDOWN' position, which is an immediate action required by procedure. Placing the mode switch to 'SHUTDOWN' bypasses the reactor low steam pressure MSIV Isolation. Reactor steam pressure began dropping after the scram, until it reached the MSIV automatic closure setpoint, and the MSIVs isolated," In addition the licensee corrected one of the 10 CFR Section entries from "50.72(b)(3)(v)(A) POT UNABLE TO SAFE SD" to "50.72(b)(3)(v)(D) ACCIDENT MITIGATION." The licensee notified the NRC Resident Inspector. Notified R4 DO (D. Powers) and NRR EO (N. Chokshi) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) | 0 | 2006-10-19
42920 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2006-10-19 11:47 | 2006-10-19 17:27 | 2006-10-19 | MANUAL REACTOR TRIP FOLLOWING THE TRIP OF SECONDARY CONDENSATE PUMPS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 19, 2006, at approximately 1147 Mountain Standard Time (MST) Palo Verde Unit 3 plant operators manually tripped the reactor from approximately 100% rated thermal power. The reactor was tripped when lowering hotwell levels caused two condensate pumps to trip. The preliminary cause for the lowering hotwell level was the hotwell draw-off valve spuriously failing open. Unit 3 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. There was no loss of normal heat removal capabilities, or loss of any safety functions associated with this event. No major equipment was inoperable prior to the event that contributed to the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The Resident Inspector was informed of the Unit 3 reactor trip and this notification." The current decay heat removal path is auxiliary feedwater supplying water to the steam generators steaming to the condenser. Emergency Diesel Generators are available. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-10-19
42919 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-10-19 09:21 | 2006-10-19 11:17 | 2006-10-19 | NON-LICENSED SUPERVISOR FAILED FOLLOW-UP TESTING "A non-licensed employee supervisor had a confirmed positive test for alcohol during a follow up fitness for duty test. The employee's access to the plant has been put on administrative hold, and the individual has been escorted offsite." The NRC Resident Inspector was notified of this by the licensee. Contact the Headquarter Operations Officer for further details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2006-10-19
42918 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-10-18 09:38 | 2006-10-18 15:27 | 2006-10-18 | FITNESS FOR DUTY - LICENSED REACTOR OPERATOR FAILS CHEMICAL DEPENDENCY EVALUATION A licensed reactor operator has his access to the plant blocked based upon an adverse, chemical dependency evaluation and interview performed through the licensee's Employee Assistance Program (EAP). The individual was not scheduled to work when the evaluation interview was performed. The individual was referred to the licensee by concerned colleagues via the licensee's Human Resources Office and is still employed by the licensee pending senior management review. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2006-10-18
42917 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-10-17 21:00 | 2006-10-18 00:19 | 2006-10-18 | REACTOR VESSEL HEAD NOZZLE WELD AREA FLAW "During the performance of NDE examinations of the Beaver Valley Unit 2 (BV-2) reactor pressure vessel (RPV) closure head Alloy 600 Control Rod Drive Mechanism (CRDM) penetrations required by NRC Order (EA-03-009), indications were identified in penetrations #16, #56, and #61. The ultrasonic examination (UT) signal for the three (3) penetrations were in the J-groove weld area and extend into the CRDM tube base material. "Confirmatory eddy current testing (ECT) was performed on penetrations #16, #56 and #61. Liquid Penetrant (PT) examinations were performed on penetrations #56 and #61 and displayed indications that required further investigation. Following minor excavation of the weld surface in the area of the indications on both penetrations (#56 and #61), additional PT examinations were performed. The result of these examinations on 10/17/06 at 2100 confirmed the presence of flaws in the weld that do not meet acceptance criteria. Penetration #16 is in the state of discovery at this time through PT examination techniques. "Based upon the preliminary analysis, it is expected that these indications would not be acceptable under ASME standards. Although this condition does not exceed the specific 10 CFR 50.72(b)(3)(ii)(A) criteria since there was no leakage as addressed in ASME Table IWB-3410-1 acceptance criteria and the component structures defined in the ASME IWB-3600 acceptance guidance do not address the J-groove weld configuration, reporting under voluntary considerations is appropriate. "BV-2 is planning to repair penetrations #56 and #61. Penetration #16 will also be repaired if warranted through the discovery process. All repairs will be completed prior to returning the RPV head to service." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2006-10-18
42916 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-17 14:30 | 2006-10-17 18:07 | 2006-10-17 | DEGRADED TECHNICAL SUPPORT CENTER VENTILATION SUPPLY FAN "At 1430 CDST on 10/17/2006 the Control Room was notified by the Site HVAC engineer that a condition existing in the Technical Support Center (TSC) HVAC called into question the habitability of the TSC under accident conditions. Specifically, the TSC HVAC Supply fan was noted on the previous shift to be putting out less air than normal. Engineering was asked to look into it and discovered that the fan belts were slipping and that the fan was currently running at approximately half normal speed. While this was sufficient to maintain the required positive pressure in the TSC at the present time, they were not confident of it's ability to maintain it long-term under accident conditions. Receipt of this information and consultation with Southern Nuclear Company Emergency Preparedness employees has led the Control Room staff to the decision to make this notification under 10CFR50.72(b)(3)(xiii), for a major loss of emergency assessment capability due to the uncertainty of the long-term habitability of the TSC. Preparations are underway for the repair of the affected fan, which is expected to be completed tonight." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-17
42915 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-10-17 14:15 | 2006-10-17 17:50 | 2006-11-04 | PRESSURE BOUNDARY LEAKAGE IDENTIFIED DURING AN OUTAGE "On October 14th V.C. Summer Nuclear Station shut down for a routine refueling outage. At 1415 on October 17, 2006 during an inspection of the reactor vessel upper head, personnel identified a small leak in a weld in the Reactor Vessel Level Instrumentation System (RVLIS). This weld is located in a 3/4 inch stainless steel instrumentation line. The line is attached to, and is approximately three feet from the reactor vessel head. This leak resulted in a small amount of boron accumulation in an isolated area. There is no indication that any safety systems were affected." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY ARNIE CRIBB TO JEFF ROTTON AT 1521 ON 11/04/06 * * * "EN #42915 was submitted by South Carolina Electric & Gas Company based on the initial indication of a pressure boundary leak in the Reactor Vessel Level Instrumentation System (RVLIS). South Carolina Electric & Gas Company retracts EN #42915 based on the following discussion. "During subsequent cleaning and inspection of the suspect weld, which was preserved in its as-found condition for root cause analysis, no flaw in the analyzed RVLIS piping or pipe coupling was found. Further investigation was conducted of the area under the Control Rod Drive Mechanism (CRDM) shroud near the RVLIS line. The source was determined to be leakage through the lower canopy seal weld of CRDM No. 25, which resulted in accumulation of boric acid on the suspect RVLIS line. "Since the RVLIS line was not leaking and the CRDM canopy connection is a mechanical (screwed) fitting with a seal weld, there has been no pressure boundary leakage as defined by Technical Specifications. The canopy seal weld is neither a structural weld nor a pressure retaining weld comprising the reactor coolant system pressure boundary. A permanent plant design was developed and the canopy seal was repaired using a standard canopy seal clamping process. "A 100 % bare metal visual inspection of the reactor vessel head was completed during this refueling outage. The results confirmed that there has been no degradation." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Evans) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-10-17
42914 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-10-17 10:21 | 2006-10-17 17:02 | 2006-11-16 | ACCIDENT MITIGATION - HPCI SYSTEM INOPERABLE "Unit HPCI system declared inoperable. During performance of the quarterly surveillance, HPCI pump operability, the HPCI system was secured when the "HPCI Turbine Oil Pressure Low" alarm was received and confirmed. Turbine governor end bearing oil pressure was 2 PSIG. The alarm setpoint is 6 PSIG and procedure limit is 10-12 PSIG. Pressure adjust valve was throttled open to raise pressure to 11 PSIG. The HPCI system was not immediately declared inoperable since an evaluation was being performed to determine if 2 PSIG turbine bearing oil pressure was adequate. Evaluation by the vendor will not be complete until 10/18/06. At 1655 hours, HPCI declared operable after a successful run with adequate oil pressure. HPCI is a single train system." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY NRC ON 11/06/06 AT 1106 EST DUE TO EVENT ENTRY ERROR * * * Original report was entered in error on 10/17/06 with Unit 2 versus Unit 1. Changed EN #42914 to accurately reflect the affected unit (Unit 1). * * * RETRACTION PROVIDED BY E. BURKETT TO KOZAL ON 11/16/06 AT 1039 * * * "EN #42914 was submitted by Southern Nuclear Operating Company based upon a conservative decision to declare the HPCI system inoperable pending further evaluation to support its operability. Southern Nuclear Operating Company retracts EN #42914 based on the following discussion. "During a subsequent review of the parameters by the HPCI Turbine Vendor, Dresser-Rand, and site engineering it was concluded that the HPCI system would have been capable of performing its intended safety function with the lower turbine governor end bearing oil pressure. "During the operation of the system, the visual local indication was approximately 2.5 PSIG oil pressure at the governor end bearing. A review of the data showed that with a governor end oil pressure of the procedural minimal of 10 PSIG, the predicted oil flow rate would be 1.08 gpm with a minimum film thickness of 0.48 mils and a maximum bearing temperature of 228 deg F. With a degraded oil pressure of 2.5 PSIG, the predicted oil flow rate would be 0.54 gpm with a minimum film thickness of 0.46 mils and a maximum bearing temperature of 233 deg F. "Based on the calculated data, the turbine governor end bearing would have performed satisfactorily for at least 8 hours at an oil pressure of 2.5 PSIG. Using the design basis success criteria, HPCI operation is successful if the system can inject water through the core Feedwater line for a total of 4 hours over a 24 hour period. The 4 hour mission time for HPCI is based on the design basis - if HPCI fails, it is backed up by the Automatic Depressurization System (ADS) in combination with Core Spray and Low Pressure Coolant Injection. The HPCI system is not credited for long term injection or late injection. "Although the oil flow rate was reduced by 50% and the minimum film thickness reduced by 4%, the bearing temperatures were predicted to only increase a maximum of 5 deg F. Supporting this conclusion is the fact that the bearing was not damaged during the operation with low oil pressure when the turbine was run for 9 minutes at 2.5 PSIG governor end bearing oil pressure." The licensee will notify the NRC Resident Inspector. Notified R2DO (Haag) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-10-18
42913 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-10-17 08:32 | 2006-10-17 10:22 | 2006-10-17 | OFFSITE NOTIFICATION - PRESS RELEASE "On 10/17/06 at 0832 Nuclear Management Company, LLC issued press release concerning the Unusual Event at Point Beach Nuclear Plant that was declared on 10/16/06 at 21:26 CDT. The Unusual Event was previously reported via EN# 42912 and occurred as a result of a momentary loss of power to the power-operated relief valve (PORV) instrumentation which caused the valve to open. The valve opening resulted in reactor coolant leakage into the pressurizer relief tank. The tank is located in the Unit 2 containment building and is designed to collect water flow from the PORV's. At no time was reactor coolant released outside of the piping systems. The NRC Resident Inspector has been informed of the press release and this subsequent notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-10-17
42912 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-10-16 21:26 | 2006-10-16 23:15 | 2006-10-17 | UNUSUAL EVENT - IDENTIFIED LEAKAGE GREATER THAN 25 GPM "At 2126, PBNP Unit 2 had a inadvertent PORV (431C) lift. This was a momentary event, however, a PRT level change of 60 gallons was noticed. This event is classifiable per C.U.1.2 identified leakage greater than 25 GPM on Unit 2." "This event has been terminated at 2139. "This event was caused by a momentary loss of power to the PORV controller. Power was immediately restored." The event was caused when a manually operated breaker (MOB) was inadvertently operated while the licensee was working inside the panels on the "B" train RHR system. The licensee notified the NRC Resident Inspector, State and local officials. * * * UPDATE FROM R. RODE TO P. SNYDER ON 10/17/06 AT 1544 * * * "Unit 2 was in Mode 5 at ~150 psig, ~112 degrees F and the pressurizer (PZR) was in a water-solid condition per plant procedures. The following is a timeline of the event for clarification: "20:47:49 A manually operated breaker (MOB-281) inadvertently opened while removing a caution tag resulting in an increase of flow in the RHR system. "20:48:43 MOB-281 was reclosed correcting the RHR flow perturbation, however the adjacent breaker (MOB-282) inadvertently opened due to the vibration of MOB-281 being manipulated. This resulted in the loss of power to the RCS pressure instrumentation providing an input to a power-operated relief valve (PORV) causing the affected PORV to open. The PORV opening provided a flow path from the PZR to the Pressurizer Relief Tank (PRT). "20:49:06 MOB-282 was reclosed resulting In the PORV shutting and isolating the flow path from the PZR to the PRT. "20:55 The PRT level indication was checked on the Main Control Board, no change in level was observed as compared to prior to the event. "While additional actions to stabilize the plant were being taken, the Shift Manager directed additional data to be obtained from the Plant Process Computer System (PPCS) regarding PRT parameters as the amount of water transferred was not large enough to be identified on the control board level Indication due to meter resolution. "21:26 Analysis of the PPCS data indicated that 62.5 gallons of RCS inventory had been transferred from the PZR to the PRT while the PORV was open. It was identified that this exceeded allowable RCS leakage limits, and the Emergency Plan was implemented. "21:32 An Unusual Event was declared per EAL CU 1.2, identified leakage greater than 25 gpm. It was recognized that this was a transient event and would be promptly terminated as the leakage flow path had been secured. "21:39 The Unusual Event was terminated. "21:43 State and County agencies were notified. "21:50 NRC Resident notified. "22:15 1 hour ENS Notification for Unusual Event and subsequent termination completed." The licensee notified the NRC Resident Inspector. Notified R3DO (Skokowski). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-10-16
42911 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2006-10-16 20:15 | 2006-10-16 21:15 | 2006-10-23 | "Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Inspector. Contact the Headquarters Operations Officer for additional details." * * * RETRACTION UPDATE FROM LICENSEE (B. NICHOLS) TO M. RIPLEY 1427 EDT 10/23/06 * * * The licensee has determined that the event is not reportable in accordance with 10CFR73.71. The NRC Resident Inspector has been notified. Contact the Headquarters Operations Officer for additional details. Notified R1 DO (J. Noggle), 73.71 Group (Email) and ILTAB DO (Email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-10-16
42910 | 0 | PETOSKEY CARDIOLOGY |  |  |  |  | 2006-10-16 08:30 | 2006-10-16 14:38 | 2006-10-16 | Tc-99m MEDICAL SOURCE LOST PRIOR TO USE Seven pairs of Tc-99m sources were received in syringes in lead shielding, placed in their holders, and inventoried at 0800. At 0830 one source (15 milliCuries) was found missing. A search was conducted visually and with a radiac. The missing source was not found. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-10-16
42909 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2006-10-16 05:20 | 2006-10-16 11:00 | 2006-10-16 | FAILURE OF CONTAINMENT VENTILATION ISOLATION INSTRUMENTATION "At 0520 hours on 10/16/06 with the plant in Mode 6, with containment shutdown purge system in operation and core alterations in progress, a Control Room Operator noted that Main Control Board annunciator L-4 'Safeguard DC Failure [Containment Isolation] CI and [Containment Ventilation Isolation] CVI Logic' was illuminated. "ITS LCO 3.9.3 c. 2. requires that 'Each penetration providing direct access from the containment atmosphere to the outside atmosphere shall be either (1) closed by a manual or automatic isolation valve, blind flange, or equivalent, or (2) capable of being closed by an operable Containment Ventilation Isolation System.' "ITS LCO 3.3.5 Containment Ventilation Isolation Instrumentation Table 3.3.5-1 requires that Function 1, 'Automatic Actuation Logic and Actuation Relays' be operable during core alterations and movement of irradiated fuel assemblies within containment. "Contrary to the requirements DC power was removed from the Containment Ventilation Logic and Actuation Relays on Friday 10/13/06. On Saturday 10/14/06 reactor vessel head lift was performed. Between Sunday 10/15/06 from 1559 until Monday at 0514 the movement of fuel and core alterations in containment were conducted. All fuel movement and core alterations were stopped at 0514 on 10/16/06." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2006-10-16
42908 | 0 | LACROSSE | 1 |  |  | [1] AC (ALLIS CHAMBERS) | 2006-10-16 07:16 | 2006-10-16 09:13 | 2006-10-17 | UNUSUAL EVENT - HIGH AIRBORNE PARTICULATE IN THE REACTOR BUILDING Even though there have been no operations on going over the weekend, airborne activities have increased to above ten times the normal levels. Activity levels were increasing during work processes last week but did not reach abnormally high levels. The licensee is taking air samples and swipe surveys to determine the source. The element of interest is Americium. Workers entering the building are required to wear filter masks. * * * UPDATE VIA FAX FROM LICENSEE AT 1250 ON 10/16/06 TO M. ABRAMOVITZ * * * "Conditions at time of incident: SAFSTOR, decommissioning work in progress involving saw-cutting of Upper Control Rod Drive Mechanism (UCRDM) seal inject supply and effluent lines, plasma arc cutting of metal in Reactor Vessel upper cavity, and welding of lifting lugs on Reactor Vessel upper cavity expansion joint structure. "Description: Thursday afternoon October 12, 2006, air samples of Reactor Building indicated higher levels of Americium-241 (Am-241) than normal. As of Monday morning October 16, 2006, Reactor Building ventilation through HEPA filters had not reduced the level of Am-241 as expected. Unusual Event was declared and investigations commenced to identify source of contamination. "Immediate evaluation/corrective actions: Upper cavity work was halted Thursday afternoon following the air sample results. It was believed that welding or plasma arc cutting in the upper cavity had created the airborne problem. Air sampling on Friday October 13, 2006, indicated Am-241 levels still remained higher than normal. At that time, all personnel entering the Reactor Building were required to wear respirators. Air sampling continued through the weekend. When Am-241 levels had not decreased to acceptable levels by Monday morning, October 16, 2006, an Unusual Event was declared due to the unexpected nature of the airborne activity, lack of identification of the source of the activity, and activity level being greater than 10 times normal for the nuclide Am-241. Following declaration, the Operations Review Committee (ORC) was convened. Various strategies for identifying the source of the contamination were discussed and established. Surveys were conducted in the Reactor Building basement and the source of the contamination was tentatively identified as effluent from the UCRDM draining that occurred on Thursday morning October 12, 2006. Further analysis and clean-up is in progress." Notified the R3DO (Skokowski). * * * UPDATE FROM DAN TESAR TO W GOTT AT 0837 ON 10/17/06 * * * The licensee secured from their Unusual Event at 0727 CDT. The licensee determined the source of the airborne activity, completed decontamination procedures and ventilated though a HEPA filter. Airborne samples are satisfactory. Notified R3DO (R. Skokowski), NMSS (M. Burgess), IRD (M. Leach), DHS (G. Gray), FEMA (K. Biscoe), and NORAD-NC (Hardaway). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-10-16
42907 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-10-15 08:46 | 2006-10-15 15:44 | 2006-10-15 | HPCI INOPERABLE "During routine testing of the Unit 2 High Pressure Coolant Injection (HPCI) Turbine Hydraulic Control System, the HPCI Turbine Control Valve failed to Open as expected. The Unit 2 HPC1 system was declared Inoperable per T/S 3.5.1 [14 day LCO]. This report made pursuant to 10CFR 50.72 (b)(3)(v)(D) for the inability of single train system to mitigate the consequences of an accident." All other ECCS systems are operable. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-10-15
42906 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-10-13 13:57 | 2006-10-13 16:55 | 2006-12-05 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE DUE TO POTENTIAL TURBINE EXHAUST DIAPHRAGM FAILURE "On October 13, 2006 at 1357 (EST) Unit 2 HPCI system was declared inoperable due to indications of a leaking rupture diaphragm in the turbine steam exhaust line. "This determination was made when water was discovered in the E41-PSH-N012A and E41-PSH-N012C instrument lines during the performance of 0MST- HPCI23Q (HPCI Turbine Exhaust Diaphragm High Pressure Instrument Channel Calibration). "TS LCO 3.5.1. 'ECCS - Operating,' Condition D was entered for the HPCI system being declared inoperable. The Reactor Core Isolation Cooling (RCIC) system was verified operable per Required Action D.1. Required Action D.2 of TS LCO 3.5.1 requires the HPCI system to be returned to operable status within 14 days. "The initial safety significance of this condition is considered to be minimal. The RCIC system and all other required ECCS, are operable at this time. "HPCI has been isolated and will be placed under clearance to allow the turbine exhaust diaphragm to be inspected and replaced if necessary " The [NRC] Resident Inspector has been notified." * * * RETRACTION FROM M. TURKAL TO P. SNYDER ON 12/05/06 * * * "Upon further review, it has been determined that the HPCI system was not rendered inoperable as a result of the condition identified on October 13, 2006. "The HPCI system is equipped with two rupture diaphragms on the steam exhaust line installed in series. Between the rupture discs are four instrument lines leading to pressure switches (i.e., E41-PSH-N012A, N012B, N012C, and N012D) and a header vent line that vents to the HPCI room atmosphere. The HPCI Turbine Exhaust Diaphragm Pressure - High signals are initiated from these pressure switches; which are required to be operable per Technical Specification 3.3.6.1, 'Primary Containment Isolation Instrumentation,' to isolate the HPCI exhaust line in the event of a degraded inner rupture disc, before the redundant outer disc is significantly challenged. This isolation provides equipment protection and [is] not assumed in any transient or accident analysis. "The suspected leaking inner rupture diaphragm was confirmed to be fully intact and, as such, not a source of the water (i.e., approximately 1.125 quarts) in the E41-PSH-N012A and E41-PSH-N012C instrument lines. The most likely source of this water is residual water remaining from a rupture disc failure that occurred in November 2003. Engineering has evaluated the potential impact of the residual water and determined that both the HPCI system and the HPCI Turbine Exhaust Diaphragm Pressure - High isolation function remained operable. There was not sufficient water in the lines to affect the function of the HPCI rupture diaphragms if required. In addition, the quantity of water discovered would not have prevented a HPCI initiation, if required, as evidenced by successful operation of the Unit 2 HPCI system on at least 10 occasions since November 2003. The Technical Specification required function of the pressure switches was not impacted by the presence of residual water. Investigation of this condition is documented in the corrective action program is Nuclear Condition Report (NCR) 209265. "On this basis, the HPCI system was capable of performing its function to mitigate the consequences of an accident and the issue is not reportable under 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector was notified of this retraction." Notified R2DO (Landis). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-10-13
42905 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-09-21 | 2006-10-13 16:05 | 2006-10-13 | AGREEMENT STATE REPORT INVOLVING ABANDONMENT OF TWO SEALED WELL LOGGING SOURCES The following information was received via fax: "Event Report ID No.: LA060019 "Event Date and Time: September 21, 2006 "Event Location: East Baton Rouge Parish "Event Type: Abandonment down hole "Notifications: LA DEQ "Event Description: Schlumberger abandoned two sealed radioactive sources down hole. The AEA 63 GBq Cs-137 source, serial number A2371, was abandoned at a depth of 18,887 feet. The Gamatron 592 GBq Am-241:Be source, serial number G4040, was abandoned at a depth of 18,855 feet. Many attempts were made to retrieve the sealed sources from 9/7-21/06. The sealed sources are covered with Premium cement and a cement retainer was set at 18,246 feet. A whipstock was placed on top of the cement retainer at 18,246 feet. An abandonment plaque will be placed on the well. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-10-18
42904 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2006-10-13 10:34 | 2006-10-13 11:46 | 2006-10-13 | INITIATION OF REACTOR SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATION 3.1.7, ACTION C.1 "On October 13, 2006, at 1034 hours, a Reactor Shutdown was initiated in response to Technical Specification 3.1.7, Action C.1. "At 2236 hours on October 12, 2006, it was determined that the Standby Liquid Control tank had a pinhole leak. In accordance with ASME Code requirements for Class 2 pressure boundaries, the SLC tank was declared inoperable, rendering the SLC system inoperable. TS Action 3.1.7, Action B.1, was entered at 2236 hours on October 12, 2006 and TS Action 3.1.7, Action C.1, was entered at 0636 hours on October 13, 2006. "The SLC tank and system remain available. The pinhole leak does not affect the structural integrity of the tank, and the level, temperature and concentration of the boron solution are being maintained per requirements." All ECCS and EDGs are operable and available and the electrical grid is stable. The licensee informed the NRC Resident Inspector. At 1130 CDT, the licensee received a 72 hour extension in getting to Mode 3 (Hot Shutdown). The licensee is currently holding reactor power at 82% in anticipation of bringing the reactor to 100% full power while in parallel performing the necessary repairs to the Standby Liquid Control tank. | 89 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-10-13
42903 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2006-10-12 15:40 | 2006-10-13 10:34 | 2006-10-13 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "The SC Department of Health and Environmental Control was notified on Thursday, October 12, 2006, at 3:45 p.m., that a CPN Model MC-1-DRP had been damaged at 3:40 p.m., on October 12, 2006. The RSO stated that the gauge had been run over by a dump truck during a soil compaction test. The SC Department of Health and Environmental Control Duty Officer responded to the scene and arrived at 5:15 p.m. and found the area properly roped off. The source rod was extended and the gauge had sustained considerable damage. The inspector and licensee personnel were able to retract the source rod to the shielded position and place the gauge in the transport container. The inspector advised the RSO to return the gauge to the storage location, secure it from further use, and to contact the gauge manufacturer for further instruction regarding disposal." A typical CPN Model MC-1-DRP moisture density gauge contains 10 millicuries Cs-137 and 50 millicuries Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2006-10-18
42902 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2006-10-12 17:30 | 2006-10-12 19:26 | 2006-11-07 | STEAM GENERATOR INSTRUMENTATION NONCONFORMANCE "During a review of two nonconformances documented in the station's corrective action system, an unanalyzed condition which could significantly degrade plant safety was noted. The steam generator level instrumentation was not installed as documented in the UFSAR. Letdown valves and piping inside containment was not installed as described in the UFSAR. An unacceptable scenario is a postulated design basis accident in one of the steam generators and a single failure of the letdown piping in the vicinity of the instrumentation piping of the other steam generator, which could, produce conditions that would mislead the operator as to the condition of the plant during the accident." This condition was discovered during steam generator replacement when the old steam generators were removed and the instrumentation piping became visible. The replacement piping will be routed in accordance with approved drawings. This piping is not required in the current mode. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 11/07/06 AT 1152 EST FROM ERICK MATZKE TO MACKINNON * * * "Additional review of the situation previously reported has determined that there are no unanalyzed interactions between the SG level instrumentation tubing and the letdown system. The review determined that the previous determination was incorrectly postulating the occurrence of simultaneous accidents. This observation was not readily apparent during the initial review. Therefore this event is not reportable under 10CFR50.72. Event number 42902 is being withdrawn. "However, the continuing review has identified a failure which will require reporting under part 50.73, but not 50.72." R4DO (Jeffrey Clark) notified. The NRC Resident Inspector was notified of the retraction of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-10-12
42901 | 0 | R & M ENGINEERING INC |  |  |  |  | 2006-08-18 | 2006-10-12 16:00 | 2006-10-13 | MOISTURE DENSITY GAUGE FELL FROM TRANSPORT VEHICLE A portable Troxler moisture density gauge was properly secured in its case with the case and handle locked in place. However, the case was not properly secured in the back of the transport pickup truck. The gauge fell from the back of the truck in front of the business office and was noticed immediately by a public official. This official then brought the gauge to the company office. The gauge was out of the company's possession for approximately 90 seconds. Troxler model 3450 S/N 363 Sources: Am-241 S/N 47-3052 40 milliCuries Cs-137 S/N 750-5849 8 milliCuries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | AK | OTH | GEN |  |  |  |  | 0 | 2006-10-12
42900 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-10-11 17:25 | 2006-10-11 17:55 | 2006-10-11 | SAFEGUARDS REPORT "Unescorted access granted inappropriately. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details." See related EN# 42899 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-10-11
42899 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-11 15:25 | 2006-10-11 16:05 | 2006-10-11 | SAFEGUARDS REPORT "Unescorted access granted inappropriately. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details." See related EN# 42900 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-10-11
42898 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2006-10-11 14:39 | 2006-10-11 15:47 | 2006-10-12 | SPDS OUT OF SERVICE "The Safety Parameter Display System [SPDS] will be removed from service for approximately 6 hours for planned maintenance." Appropriate compensatory actions have been put in place by the licensee to ensure remote indication of SPDS parameters are available when needed. The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 10/12/06 AT 0043 EDT BY CHUCK OLSON TO MACKINNON * * * Safety Parameter Display System place back in service at 0043 EDT. R4DO (J. Whitten) notified. The NRC Resident Inspector will be notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-11
42897 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2006-10-11 12:40 | 2006-10-11 15:05 | 2006-10-11 | UNANALYZED CONDITION - INDICATIONS ON PRESSURIZER NOZZLE TO SAFE END WELDS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "On October 11, 2006, at approximately 12:40 Central Standard Time (CST), engineering personnel performing preplanned in-service examination of the Pressurizer nozzle to safe end welds notified the Control Room that five circumferential indications had been discovered that cannot be found acceptable under ASME Section XI. "Since the indications cannot be found acceptable under ASME Section XI the condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(A). "Three indications are located on the surge line, one indication is on the safety nozzle, and one indication is on the relief nozzle. The locations are part of the Reactor Coolant System (RCS) pressure boundary. There is no evidence of RCS pressure boundary leakage. "WCGS is currently shutdown for its 15th refueling outage and is in Mode 6. Weld overlay of the safe ends is an activity scheduled for the current outage. "An investigation of this event will be conducted in accordance with the WCGS corrective action program." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-10-11
42896 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-10-10 15:00 | 2006-10-10 23:57 | 2006-10-11 | CONTAINMENT SPRAY VALVE MISPOSITIONED "While performing maintenance on one of two installed Containment Spray Header valves, HCV-345, the System Engineer determined that the valve disk was installed backwards [ball valve]. Actual valve positioning would be opposite of remote indication. The resulting affect would be that an accident signal to open HCV-345 would have closed the valve rendering one header inoperable. This condition is presumed to have existed, since the last maintenance activity on the valve during Refueling Outage May 2005, and through Cycle 23." This system is not required to be operable in the current mode. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-10-11
42895 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-10-10 07:35 | 2006-10-10 20:27 | 2006-10-10 | AGREEMENT STATE REPORT - IR-192 BRACHYTHERAPY SEED FOUND AT WASTE TRANSFER STATION The State provided the following information via email: "On Tuesday, October 10, 2006, at 7:35 A.M., [DELETED] of Waste Management/ Orange Transfer Station, contacted RHB South about a transfer truck that set off their radiation alarm (208.9 kcpm, 4.6 kcpm background). The transfer station knew the waste had been picked up at Chapman Memorial Hospital, who was then contacted. The readings that were taken by [DELETED] were 5 millirem/hour at 1 ft., 1 millirem/hour at 3ft and 0.01 millirem/hour background. They were instructed not to sort or segregate the waste before RHB staff's arrival. At 11:20 A.M., RHB staff met [DELETED] and [DELETED] of Chapman Memorial Hospital at Waste Management to identify the waste. Prior to RHB staff arrival, [DELETED] had surveyed and searched through the waste and found a seed of Ir-192 and placed it inside a clear plastic box. According to [DELETED], he was wearing gloves at the time and had spent about 15 minutes searching for the seed (approximately within 2 feet of the source) and was in direct contact with the source with the thumb and forefinger for about 15 seconds. He then proceeded to place the seed back into the trash can that it was contained in. RHB staff surveyed and identified the waste as a 1.4 - 2.1 millicurie Ir-192 brachytherapy seed. A DOT Exemption (CA-CA-06-41) was issued to [DELETED] to transport the trash can back to Chapman Memorial Hospital and to make sure that the RSO is able to supervise the removal of the seed from the trash bag. The licensee will be evaluating the dose to [DELETED], and providing a full report in that regard." California event number 101006 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-10-13
42894 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-10-09 11:24 | 2006-10-09 14:17 | 2006-10-09 | POTENTIAL VIOLATION OF VIRGINIA POLLUTANT DISCHARGE ELIMINATION SYSTEM PERMIT "As a result of heavy rains, influent flows to the Surry Sewage Treatment Plant (STP) were in excess of 193,349 gallons on Saturday, October 7. Road conditions prevented normal pumping service from coming onsite to remove this excess water. "Resultant analysis showed a loss of 54%, 39% and 10% solids in STP aeration tanks 1, 2 and 3, respectively. These 'solid' parameters are normally an indication that the STP is able to maintain effective treatment. At 1124 on 10/09/06, the Virginia Department of Environmental Quality (DEQ) was notified that the loss of solids may indicate that the treatment capability of the STP is impacted, which may cause a violation of one of the parameters of Surry's Virginia Pollutant Discharge Elimination System (VPDES) Permit. "This event is being reported in accordance with 10CFR50.72(b)(2)(xi) due to the fact that the Virginia Department of Environmental Quality was notified at 1124 hours." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-10-09
42893 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-01-02 | 2006-10-09 11:35 | 2006-10-09 | PART 21 NOTIFICATION - VOIDS IN PLATE STEEL "Facility Reporting: Oconee Nuclear Station, Duke Power Company "Basic component: 3/4 in thick, 32 sq ft (4 ft by 8 ft) A36 steel plate manufactured in accordance with ASTM/ASME Section II; manufactured by CORUS; supplied by CONSOLIDATED POWER SUPPLY Purchase Order ON 46703, Heat number A2WT; Duke QC receipt inspection on 9/25/2001. "192 sq-ft of plate was ordered on this Purchase Order, of this, 128 square feet of plate had the applicable heat number "Nature of the defect or failure to comply and the safety hazard: "During fabrication of hangers for use during a modification, pieces were cut from a sheet of 3/4 inch steel plate for use as hanger support base plates. Personnel noted that a base plate contained a lamination, resulting in the hanger strut being welded to only a thin layer of material. The piece was examined by engineering and a Ultrasonic Test examination of the remainder of the original 4 foot by 8 foot sheet found that the lamination area was approximately 15 inches by 36 inches and approximately 1/32 to 3/32 inches deep. This area was cut out and discarded and the remainder of the sheet was considered acceptable for use. "The issue was entered into the Duke corrective action program and an evaluation for Part 21 reportability was initiated. "The Part 21 evaluation concluded that, if the deflective material had been used for hangers as initially intended, the hangers may have failed during a design basis transient or accident due to failure of the thin lamination layer. "Duke hanger designs are typically conservative such that failure of a single hanger will not result in the failure of the supported system/component, but within the rules for evaluation of a Part 21 defect, it must be assumed that this defective material may have resulted in a significant safety hazard and therefore must be reported under Part 21. The material known to be defective was not actually installed; therefore, this event is not reportable under 10 CFR 50.72 or 50.73. "At this time Duke has no information to determine if this defect could extend to other material of the same heat or same manufacturer. Duke has no information on other possible customers. "Duke did use the remaining sheets from the same purchase order in various applications, and is creating corrective actions to inspect the material with the same heat number for additional lamination areas: However due to the fact that no similar deficiencies were observed during fabrication and installation of the components made from this material or in use of similar materials, Duke considers this an isolated instance and does not consider this to be a current operability issue. "Additional details will be provided in the required 30 day report." A sheet (4'x8') of this heat of plate steel was shipped to Catawba. Catawba has been notified and will investigate their use. The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2006-10-09
42892 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2006-10-09 04:00 | 2006-10-09 10:52 | 2006-10-09 | CONTAINMENT SUMP INOPERABLE WHEN REQUIRED BY TECHNICAL SPECIFICATIONS "On October 9, 2006 at or about 0400 EDT it was discovered that the containment Sump B grating had been covered with temporary lead shielding. The shielding was placed as part of refueling outage activities in containment. Investigation has revealed that the lead shielding was put in place at about 0230 hours. All lead was removed from the grating. This was confirmed by the Outage Control Center at 0930. At the time of discovery the plant was in MODE 4 with RCS pressure of 315 psig, RCS Temperature of 337 °F. "The plant entered MODE 5 at 08:15 hours on 10/9/06." The B containment sump is the suction point for the A and B RHR pumps. When required, the RHR pumps also provide suction flow to the Safety Injection pumps. The containment sump is require to be operable in modes 1-4. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-10-09
42891 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-10-07 09:30 | 2006-10-08 15:00 | 2006-10-08 | AGREEMENT STATE REPORT - WELL LOGGING SOURCE DAMAGED The NRC received the following information from the State of California via e-mail: "At about 945 am October 6, 2006, [Deleted] from Schlumberger's Houston office contacted the RHB South ICE RM office to notify RHB that a well-logging tool with two sources (1.7 Ci Cs-137 and 16 Ci Am-Be) had become stuck the day before yesterday near the bottom of the hole. They worked over the last two days, 'fishing' for the sources, and recovered the Am-Be source when the tool broke. Neither of the sources have been compromised. They have not yet determined that the remaining source must be abandoned, but expect to make that determination over the weekend, and requested approval to abandon it, if additional retrieval attempts fail. Approval was granted, and Schlumberger was provided an emergency contact number to provide information over the weekend, if any health and safety concerns arise (e.g., if the source is compromised). The well is in Kern Co., CA at Chevron USA, well no. Amber 235 in the Midway-Sunset Field (Section 26, Township 31-S, Range 22-E). "At 9:30 PDT on October 7, 2006, [Deleted] called again to report that they had reason to believe the Cesium-137 source had ruptured down-hole. Chevron had commenced a cut and thread fishing operation for the stuck logging tool late Wednesday evening, October 4th. On the first trip into the hole the logging tool was engaged into the grapple, when the rig started to pull out of the hole the drill pipe was stuck, the drill pipe would not move up or down. The decision was made to gently reverse rotate the pipe in an attempt to free the logging tool from the grapple. Once the tool was released from the grapple, the drill pipe was pulled out of the hole and the fishing assembly removed and replaced with wash over pipe. During the second trip in the hole with the wash over pipe the tool was engaged and part of the tool came out of the hole. This part of the tool contained the 592 GBq Am241Be source. The 63 GBq Cs-137 source remained down hole in another tool. Several more trips were made with the wash over pipe in an attempt to recover the remaining tools. It was during an attempt with the wash over pipe when Schlumberger personnel who were monitoring the mud returns notice a substantial increase on their survey meter from 0.4 mrem/hr to 7.0 mrem/hr. Since an increase such as this could indicate a potentially ruptured source all operations and circulation were immediately stopped with all personnel removed from the rig and the immediate area. "At this time the area around the rig, mud pit and shale shaker were cordoned off. Schlumberger personnel are conducting further surveys of all personnel and the area at this time. RHB is continuing to follow up with the licensee on this." The state also reported that Schlumberger is sending additional people to the site to conduct further surveys and determine their future course of action. The state was notified of the event on 10/7/06 at 2130. CA Report Number: 100706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-10-11
42890 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2006-10-07 17:11 | 2006-10-08 10:13 | 2006-10-08 | DISCOVERY OF AFTER-THE-FACT-EMERGENCY CONDITION - UNUSUAL EVENT "At 09:20 [EDT] on 10/8/06, it was discovered that a NOUE had not been declared on 10/7/06 as required by Surry EPIP-1.01, EAL Tab H-3. At 17:11 [EDT] on 10/7/06 Surry Power Station experienced a loss of offsite power to unit 1 Transfer Buses (both D & F), therefore in accordance with tab H-3, a Notification of Unusual Event [NOUE] should have been declared. Subsequent to this event, an Alert was declared [on Unit 2] at 18:01 [EDT] due to tab K-11 and the Alert was exited at 05:40 [EDT] on 10/8/06. This notification is for the discovery of an undeclared event that exceeded an Emergency Action Level (EAL) as specified in EPIP-1.01." The licensee notified the NRC Resident Inspector. See EN # 42888 for details regarding Alert declared on Unit 2. | 75 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2006-10-08
42889 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2006-10-07 17:50 | 2006-10-07 23:49 | 2006-10-08 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF PRIMARY CONTAINMENT INTEGRITY "At 17:50, on 10/07/2006, the Peach Bottom Atomic Power Station identified a crack approximately 4 inches long on a Unit 2, Reactor Core Isolation Cooling (RCIC) test line, as the line penetrates the Suppression Pool of Primary Containment. The degraded piping represents a loss of primary containment integrity, placing one of the principle safety barriers in a 'Seriously Degraded' condition as defined by 10CFR50.72 (b)(3)(ii)(A). This condition required a Reactor Shutdown per the plants Technical Specifications (TS) [TS 3.6.1.1]. Unit 2 was manually scrammed, at 20:16, in order to shutdown the reactor and place the unit in Mode 3 per the Technical Specifications. The TS required shutdown is reportable per 10CFR50.72(b)(2)(i). The unplanned reactor scram is reportable per 10CFR50.72(b)(2)(iv)(B). The reactor scram and resultant Emergency Safety Feature actuations were completed as required. In addition, the loss of primary containment integrity represents a condition that 'could have prevented the fulfillment of a safety function of a structure required to control the release of radioactive material' and/or 'mitigate the consequences of an accident.' This is reportable per 10CFR50.72(b)(3)(v)(C) and (D). Unit 2 is currently shutdown, Mode 3, with an RPV cooldown in progress, with plans to Enter Mode 4 by 02:00 on 10/08/06." All control rods fully inserted on the Manual Reactor Scram. The reactor is currently being fed from the condensate system with decay heat being removed to the condenser via the MSL drains. The electric plant is in a normal shutdown lineup. See EN # 42887 for related NOTICE OF UNUSUAL EVENT. Additional 10 CFR Section not listed above: 50.72(b)(3)(v)(D) ACCIDENT MITIGATION The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL | DEGRADED CONDITION | POT UNCNTRL RAD REL | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) | 0 | 2006-10-08
42888 | -1 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-10-07 18:01 | 2006-10-07 18:27 | 2006-10-16 | MANUAL SCRAM DUE TO UNUSUAL NOISE IN TURBINE BUILDING The main turbine cross-under safety relief valves lifted for no known reason and blew siding off the side of the Unit 2 Turbine building. This siding hit the feeder lines to the A & C Reserve Station Service Transformers (RSSTs). The operator manually scrammed the plant due to swings in steam generator level and unusual noise coming from the turbine building . Unit 2 shutdown currently de-energized A & C Reserve Station Transformers, which effects D & E transfer buses. This also effects 1J bus, which is de-energized, and 1H & 2J buses which are energized with #1 diesel and #3 diesel. Decay heat removal is being performed thru the SG PORV's and auxiliary feedwater system, with forced cooling from the "B" RCP. Safety related systems are available if required. Notified USDA (A. Jimenez) in addition to the other agencies already identified. The licensee notified the NRC Resident Inspector, as well as State and local agencies. * * * UPDATE ON 10/8/2006 AT 05:45 FROM MIKE CHRIS TO ABRAMOVITZ * * * The site terminated the Alert at 05:40 due to having the "A" RSST in service with bus 1J being powered from its normal power supply. No damage was found from the displaced siding with the exception of the "C" RSST (which should be repaired around noon). The "C" RSST is currently tagged out for maintenance. The licensee notified the NRC Resident Inspector, state, and local governments. Notified: R2DO (Decker), R4DO (Pick), NRR (Dyer, Weber, Quay), IRD (Blount, Wilson), R2 (McCree), DHS (Gray), FEMA (Dunker), DOE (Steve Bailey), EPA (Allison), USDA (Dean Giles), and HHS (Lt. Smith). * * * RETRACTION ON 10/16/06 AT 1724 FROM L. WHEELER TO M. ABRAMOVITZ * * * "At 1827 hours on 10/07/06, an Emergency Notification System (ENS) notification was made for an Alert declaration at Surry Power station. The steam discharge from the turbine system safety valves that had lifted caused pieces of siding from the turbine building to dislodge and come in contact with two phases of the overhead bus for the 'A' and 'C' reserve station service transformers (RSST). The basis for the declaration was the Emergency Action Level (EAL) Tab K-11: 'Notification of missile impact causing damage to safety-related equipment or structures'. Upon further review, the RSSTs were determined not to be safely-related equipment. Therefore, the conditions for an Alert emergency did not exist and the notification is being retracted. A notification will be made to the Virginia Department of Emergency Management. This is being reported In accordance with 10 CFR50.72, (b) (2) (xi). "As noted in EN# 42890, conditions for a Notification of Unusual Event (NOUE) did exist at the time of the Alert notification." The licensee notified the NRC Resident Inspector. Notified the R2DO (Henson). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | ALERT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-10-07
42887 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2006-10-07 18:02 | 2006-10-07 18:14 | 2006-10-08 | UNUSUAL EVENT - LOSS OF CONTAINMENT INTEGRITY During testing, a small crack (3"- 4" axial crack) was identified on a return line to the torus for both HPCI and RCIC (steam driven ECCS systems). The valve upstream of the leak has been closed, however, the leak is still unisolable between that valve and the torus. This plant condition does not threaten public safety. The licensee notified the NRC Resident Inspector, as well as State and local agencies. * * * UPDATE PROVIDED BY ROBERT STEIGERWALD TO JEFF ROTTON AT 0555 EDT ON 10/08/06 * * * "This is a follow up notification to EN# 42887. Peach Bottom Atomic Power Station Terminated the Unusual Event at 0513 [EDT] on 10/08/06. Unit 2 is currently shutdown in Mode 4." In Mode 4, Primary Containment is no longer required. The licensee notified the NRC Resident Inspector, State and Local agencies. Notified R1DO (Krohn), R1 (Dapas), NRREO (Quay), NRR (Dyer, Weber), IRD (Blount), DHS (Gray), FEMA (Dunker). | 22 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-10-07
42886 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2006-10-07 11:40 | 2006-10-07 16:33 | 2006-10-07 | AXIAL INDICATIONS IDENTIFIED ON PRESSURE BOUNDRY "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 7, 2006, at approximately 11:40 Mountain Standard Time (MST), Engineering personnel performing preplanned in-service examination of the reactor vessel head vent piping notified the Unit 2 Control Room that two axial indications had been discovered. The indications are located on the inner diameter surface of the pipe adjacent to the J-weld to the reactor head and are part of the Reactor Coolant System (RCS) pressure boundary. The indications are characterized as axial, estimated 0.020 to 0.030 inches deep, and approximately 0.2 inches long. The indications do not appear to be through wall and there is no evidence of RCS pressure boundary leakage. "Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.4.14 permits no RCS pressure boundary leakage and there is no evidence of pressure boundary leakage. Nevertheless, the indications are being conservatively identified as abnormal degradation of the RCS pressure boundary and will necessitate taking corrective action to restore the barrier's capability. Therefore, the ENS notification of this event is in accordance with 10CFR50.72(b)(3)(ii)(A). Unit 2 is currently shutdown for its 13th refueling outage and is in Mode 6. "No ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result In the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "An investigation of this event will be conducted in accordance with the PVNGS corrective action program." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-10-07
42885 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-10-07 13:40 | 2006-10-07 14:31 | 2006-10-07 | SITE ACCESS ROAD FLOODED "At 1340 on 10/7/06; normal road access to Surry Power Station became flooded and impassable due to sustained heavy rainstorms. This flooding compromised the Surry off-site response capability. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability (e.g., offsite response capability)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-07
42884 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-10-07 07:53 | 2006-10-07 14:16 | 2006-10-07 | FITNESS FOR DUTY - CONFIRMED POSITIVE FOR NON-LICENSED SUPERVISOR A non-licensed supervisor had a confirmed positive for alcohol. The supervisor's access to the plant has been denied while a review of this matter is performed. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2006-10-07
42883 | -1 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-10-07 06:57 | 2006-10-07 11:05 | 2006-12-04 | HPCI DECLARED INOPERABLE "A division 2 Primary Containment Isolation Instrument System component inoperable required the manual isolation of High Pressure Coolant Injection (HPCI) outboard Primary Containment Isolation valves (PCIV). This isolation was required by T/S action 3.3.2.b.1. "This report made pursuant to 10CFR 50,72 (b)(3)(v)(D) for the inability of single train system to mitigate the consequences of an accident." At approximately midnight on 10/7/06, Control Room Operators received a Div 2 Steam Leak Detection Trouble Alarm. Troubleshooting identified the failure as associated with the GE NUMAC drawer where temperature inputs are processed. The applicable 14-day T/S LCO Action Statement requires completion of repairs within 6 hours or isolation of HPCI 1 hour later. HPCI was isolated at 0657 EDT. There was no I&C work in progress at the time of the failure. Repair parts are available and onsite. The licensee informed the NRC Resident Inspector. * * * RETRACTION RECEIVED FROM EDWARD DENNIN TO JOE O'HARA AT 1500 ON 12/04/06 * * * "This is a retraction of the event notification made on 10/07/06 at 11:05 hours. This event (#42883) was initially reported as a safety system functional failure under the requirement of 10CFR50.72(b)(3)(v)(D). Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable due to a manual closure of the HPCI steam line outboard primary containment isolation valve (PCIV). The PCIV was closed to support the maintenance on an inoperable steam leak detection (SLD) channel and to satisfy the Technical Specification (TS) 3.3.2 Isolation Actuation Instrumentation action statement. "The event was initiated at 00:06 hours by a trouble alarm due to a 'self test fault' condition on the Division 2 SLD instrument channel. Troubleshooting determined that the instrument channel was inoperable. TS 3.3.2 Action 'b.1' requires the channel to be restored to operable status within 6 hours. Since this action could not be completed Table 3.3.2-1 Action 23 was applicable. Action 23 required the affected system isolation valves to be closed within one hour and the system (HPCI) to be declared inoperable. This action was completed at 06:57 hours. "Two modules were replaced in the SLD instrument chassis. The instrument channel was tested satisfactorily and returned to service, Unit 2 HPCI was restored to operable status at 23:48 hours. "The system was removed from service as part of a planned evolution to conduct maintenance in accordance with an approved procedure and the plant's Technical Specifications. The system was secured for the purpose of conducting maintenance on an inoperable SLD instrument channel and completing the TS action. The failed instrument did not adversely affect the HPCI system's capability of performing its safety function. HPCI remained capable of automatic initiation until the PCIV was manually closed to support maintenance by completing the TS actions. "A condition did not exist at the time of discovery that could have prevented the fulfillment of the HPCI safety function." The licensee notified the NRC Resident Inspector. Notified R1DO(Sykes). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-10-07
42882 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2006-10-07 01:51 | 2006-10-07 03:49 | 2006-10-07 | SCAFFOLD PREVENTS MAIN STEAM ISOLATION VALVE CLOSURE Temporary scaffolding was constructed near the loop-1 Main Steam Isolation Valve (MSIV) on 8/30/2006 while the Unit was in Mode 1. On 10/7/2006 surveillance testing on the MSIVs was conducted in Mode 3 and the loop-1 MSIV failed to fully stroke closed. It was determined that temporary scaffolding was interfering with full valve travel. The scaffolding was removed and the surveillance test verified full valve motion. The licensee notified the NRC Resident Inspector and will notify state and local officials. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-10-07
42881 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2006-10-06 14:00 | 2006-10-06 14:55 | 2006-10-06 | SAFEGUARDS REPORT Discovered vulnerability in a safeguards system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-10-06
42880 | 0 | SOUTHERN TESTING SERVICES |  |  |  |  | 2006-10-05 | 2006-10-05 19:20 | 2006-11-10 | POTENTIAL DEFECT IN OTEK PANEL METERS Southern Testing Services (STS) provided information on a potential defect in OTEK Panel Meters. The information applies to 90-265 Volt AC / 10- 32 Volt DC, OTEK Part Numbers: HI-Q114, HI-Q116, HI-Q117, HI-Q118, and HI-Q119. "STS has identified a potential failure cause for the HI-Q class meters that would result in a frozen indicator with no indication that the failure has occurred. The specific failure mode is a failure of the main processor (only) that freezes the display processor. The frozen display inhibits the detection of the main processor failure except by cycling power to the Panel Meter. This failure mode was previously addressed in the Failure Mode Effects Analysis (FMEA) conducted by STS in Test Report S4000-RP-03; however, no credible causes for the failure beyond infant mortality were postulated or had been experienced at the time. Infant mortality failures are minimized by the dedication process that verifies operation of the units prior to shipment to the client. "STS has just learned from OTEK that of one (1) OTEK Panel Meter had experienced a main processor failure which resulted in a frozen display indicator. This Panel Meter was reportedly in a non-nuclear application. OTEK determined that the likely cause of this failure was a high frequency spike on the power lines caused by running the meter off of a DC generator. "The STS EMI/RFI qualification program for the OTEK meters qualified them with an anomaly, limiting the surge protection to 500 [Volts peak to peak] for DC powered units. Additionally, high frequency susceptibility testing was successfully completed with a continuous signal of 3.5 [Volts RMS] on the power lines (both AC and DC powered units) from 10 kHz to 200 MHz. Additional testing was done on AC powered units at 7 [Volts RMS]. Testing was conducted in accordance with EPRI TR-102323 to the methods specified in EN 61000-46. The units passed the susceptibility testing at the limits specified, as reported in Test Report S4000-RP-03. "Based on the successful surge and high frequency susceptibility testing conducted by STS, it is concluded that the single known failure noted by OTEK was related to operating outside of the parameters tested during qualification of these OTEK meters. The likelihood of such a failure in a nuclear safety related application is considered to be remote." STS determined that 294 units were provided to nuclear plants in potentially safety related applications where EMI/RFI requirements were imposed. The following plants were effected purchasers: Vermont Yankee, Pilgrim, St. Lucie, and Brown's Ferry. "OTEK is currently in the process of updating the display board processor programming to detect a failure of the main processor, and provide an indication on the display that a main processor failure has occurred. STS will coordinate with the above utilities when this update becomes available." * * * UPDATE FROM SOUTHERN TESTING SERVICES (W. WILLIS) TO M. RIPLEY 0840 EST 11/10/06 * * * The following information was provided via facsimile: "The date on which the information of such defect or failure to comply was obtained: OTEK notified STS via email on September 18, 2006 following in-person conversations on September 12, 2006 with Southern Testing Services and TVA personnel. "In case of a basic component which contains a defect or fails to comply, the number and location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part. "A total of 294 units have been provided to Nuclear Plants in potentially safety-related applications where EMI/RFI requirements were imposed. The following Effected Purchasers have been identified: Vermont Yankee, St. Lucie, Pilgrim, Brown's Ferry "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action, and the length of time that has been or will be taken to complete the action: OTEK has provided a prototype meter with the display processor code modified to detect failure of the main processor and provide an indication on the meter by generating a full scale bargraph colored amber. STS has successfully performed testing on the unit to confirm proper operation of the modified display processor code. STS will coordinate with the above utilities when testing of this update is complete to upgrade or replace the existing units if required by the utilities. OTEK will include the modified software in the HI-Q series meters in all new orders, starting immediately. "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: STS and Otek acknowledge the definition of 'Defect' within 10 CFR, Part 21 but believe the issue is more accurately described as an absence of a specific failure mode indication that was not previously required." Notified R1 DO (N. Perry), R2 DO (P. Fredrickson), and NRR Part 21 (EMAIL & FAX) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21 |  |  |  | 0 | 2006-10-05
42879 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2006-10-05 16:45 | 2006-10-05 17:42 | 2006-10-05 | SAFEGUARDS REPORT Discovered vulnerability in a safeguards system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-10-05
42878 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-08-19 20:02 | 2006-10-05 14:18 | 2006-10-05 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of multiple main steam isolation valves. "On August 19, 2006, at 2002 hours CDT, with Unit 3 shutdown in Mode 3 following an earlier manual scram of Unit 3 (reference Event Number 42787), the EHC System along with the turbine bypass valves was being used to cool down/depressurize the reactor. The EHC system is used to supervise the turbine control valves and turbine bypass valves to control reactor pressure. The EHC system was subsequently removed from service for the repair of a previously identified system fluid leak. "Following the shutdown of EHC system, reactor pressure and temperature were allowed to slowly increase. At 2240 hours CDT upon completion of the leak repair, operations personnel placed an EHC pump back in service in accordance with the system operating instruction to support post-maintenance testing activities. However, when the EHC system was returned to service, the pressure control set point was lower than the reactor pressure. The significance of the delta between the EHC setpoint and the actual reactor pressure was not recognized by operations. Because the actual reactor pressure was higher than the existing control set point, the EHC system responded by opening turbine bypass valves to lower the reactor pressure. Operations personnel observed the bypass valve response, identified the cause, and raised the pressure control set point. This action caused the bypass valves to rapidly close. The abrupt cessation of steam flow caused by the rapid closure of the bypass valves initiated a reactor pressure transient that affected the reactor water level instrumentation. The affected level instruments' output signals exhibited a ringing effect of a magnitude sufficient to reach the low level set point for primary containment isolation system (PCIS) Group 1 actuation. The Group 1 isolation logic actuated in accordance with its design, and the main steam isolation valves and the main steam line drain valves automatically closed. "Designed time delays in other logic circuits affected by these water level signals prevented additional equipment actuation during this event. Actual reactor water level did not change, remaining within the normal level band; therefore, the isolation signal is considered invalid. "All equipment responded in accordance with the plant design. Upon verification that no actual water level anomaly existed and that the transient instrumentation response had stabilized, the affected PCIS logic was reset, and equipment was realigned as appropriate. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for evaluation and resolution. "The NRC senior resident inspector has been notified of this report. "Reference corrective action document PER 109118." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-10-05
42877 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-08-18 19:58 | 2006-10-05 14:18 | 2006-10-05 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of general containment isolation signals affecting more than one system. "On August 18, 2006, at 1958 hours CDT, with Unit 2 operating at 100% thermal power, the electrical power to reactor protection system (RPS) bus 2B was interrupted during the performance of surveillance testing on RPS circuit protectors 2B1 and 2B2. The RPS buses 2A and 2B are normally powered from motor-generator (MG) sets 2A and 2B, respectively. During testing or maintenance intervals affecting either the MG set or the normal supply circuit protectors, the affected RPS bus is powered from a transformer supply through alternate power circuit protectors 2C1 and 2C2. Power to RPS bus 2B, which was being powered through the alternate power circuit protectors via a temporary transformer, was interrupted when circuit protector 2C1 actuated on a sensed under voltage condition. The Primary Containment Isolation System (PCIS) logic circuits powered from RPS bus 2B were de-energized, and PCIS logic Groups 2, 3, 6, and 8 were actuated. None of the plant conditions which require PCIS Groups 2, 3, 6, or 8 actuation (e.g., low reactor water level, high drywell pressure, abnormal area radiation levels, high area temperature, etc.) existed; therefore, these actuations are considered invalid. "The following actuations/isolations occurred: "Group 2: Isolation of the Pressure Suppression Chamber head tank pumps and Drywell Floor and Equipment Drains Isolation; "Group 3: Isolation of the reactor water clean-up system; "Group 6: Initiation of the Standby Gas Treatment System, Initiation of Control Room Emergency Ventilation, and Isolation of the reactor zone and refuel zone normal ventilation systems; "Group 8: This logic isolates the Traversing In-core Probes (TIP) if they are inserted. The TIPs were not inserted at the time of this event. "All equipment responded in accordance with the plant design. At the time of the loss of power from the alternate source, the surveillance testing had already been completed and activities were in progress to transfer the RPS bus back to its normal supply. These actions were completed and RPS Bus 2B was re-energized from RPS MG set 2B. The affected logic was reset, and equipment was realigned as appropriate. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for evaluation and resolution. "The NRC Senior Resident Inspector has been notified of this report. "Reference corrective action document PER 109090." Also see similar NRC event number 42837. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-10-05
42876 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-10-04 06:30 | 2006-10-04 21:02 | 2006-10-26 | WASHINGTON AGREEMENT STATE REPORT - TWO DAMAGED SHIPPING PACKAGES CONTAINING CESIUM-131 CANCER THERAPY SEEDS. Event sent to NRC Headquarters Operation Center via e-mail. "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "At 6:30 am, 4 October, the Spokane FedEx Terminal Manager discovered a flattened lead cap. A partial label on the cap indicated it came from one of two packages containing IsoRay, Cesium 131, therapy seeds. A second package was found crushed but essentially intact; the seeds in this package were all present and apparently undamaged. Scraps from the first box were found on the runway and other pieces on the floor of a tug (airport vehicle used to move cargo). It is thought the damage was caused when the boxes were caught between moving pieces of the cargo loading equipment. The actual incident appears to have happened 12 hours earlier (about 6 pm, 3 October). Dayshift FedEx staff had apparently placed the damaged packages on the floor on the passenger side of the tug cab. "Four WA Department of Health, Health Physicists responded to the scene at about 8:00 am, 4 October. IsoRay also dispatched a team of three HP technicians arriving at noon with equipment including a decontamination kit. WA Department of Health staff were able to retrieved three of the sixty-three seeds that were in the one shredded package. Several areas of contamination were also found. "Measurement on the floor of the tug's passenger side was reading 150 Mr/hour with an Eberline RO2 ion chamber. Radiation measurements on the crushed pig lid were about 25 Mr/hour with an RO2 and a contamination measurement of about 400 cpm with a GM instrument. Contamination reading on the crushed box was about 300 cpm with the GM instrument. A spot on the tarmac was found reading about 12 Mr/hour with an RO2. "The undamaged stainless steel pig reads about 5 Mr/hour with an RO2. "Night shift personnel were asked to return to the facility. No personnel contamination had been found at the writing of this report. "WA Dept of Health and IsoRay staff continue to look for the remainder of the packaging and seeds. "No news media attention yet. "Notification Reporting Criteria: 10 CFR 30.50(b)(1) "Isotope and Activity involved: 330 mCi, 12.2 Gigabecqerals of Cesium 131. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Exposures to be determined. "Lost, Stolen or Damaged? (mfg., model, serial number): 3 of 63 missing seeds recovered, contamination found in tug, packaging and on the runway. The remainder of the activity is still being sought. "Sealed Source and Device Registry: WA-1220-S-101-S "Disposition/recovery: WA Dept of Health and the manufacturer staff are still on the scene to assist in recovery of seeds. "Leak test? The seeds are leak tested prior to packaging and were within limits. "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) Airport tug, N/N FedEx air bill # 730 235 322 954. "Release of activity? Three seeds found in the tug. Contamination found in the tug, on packaging and on the runway. "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: N/A "Exposure (intended/actual); consequences: N/A "Was patient or responsible relative notified? N/A "Was written report provided? Not yet "Was referring physician notified? N/A "Consultant used? No." Washington Incident Report - WA-06-053 * * * UPDATE FROM A. SCROGGS TO W. GOTT AT 1421 ON 10/26/06 * * * The State provided the following update in the text of their original report via email: "This is notification of an event in Washington State as reported to and investigated by the WA Department of Health, Office of Radiation Protection. "STATUS: update / close "Licensee: IsoRay, City and State: Facility in Richland, Washington License Number: WN-L0213-1 Type of License: Manufacturer and Distributor (of cancer therapy seeds) "Date of Event: 3 October 2006 (reported 4 October 06). Location of Event: Spokane International Airport, FedEx Terminal, Spokane Washington. "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "At 6:30 am, 4 October, the Spokane FedEx Terminal Manager discovered a flattened lead cap in the plane loading area. A partial label on the cap indicated it came from one of two packages containing IsoRay, Cesium 131, cancer therapy seeds. A second package was found crushed but essentially intact; the seeds in this package were all present and found to be undamaged. Scraps from the first box were found on the runway and other pieces on the passenger side floor of a 'tug' (airport vehicle used to move cargo containers). It is thought the damage was caused when the boxes were caught between moving pieces of the cargo loading equipment. The actual incident appears to have happened 12 hours earlier (about 6 pm, 3 October 06). Dayshift FedEx staff had apparently placed the damaged packages on the floor on the passenger side of the 'tug' cab but this was unable to be verified. "Four WA Department of Health, Health Physicists responded to the scene at about 8:00 am, 4 October. IsoRay also dispatched a team of three HP technicians arriving at noon with equipment including a decontamination kit. WA Department of Health staff returned Thursday, Friday and Monday to continue the investigation. WA DOH was not able to find any additional material except that found October 4. These finds amounted to three seeds and a minor amount of contamination in the tug and on the loading surface. WA DOH spent 16 FTE days looking for the material and interviewing FedEx staff. Night shift personnel were asked to return to the facility. No personnel contamination was found. All parts of the complex within the FedEx secured area (buildings and property) and public areas adjacent to the FedEx secured property were searched. "IsoRay personnel decontaminated the tug and loading surface. Took control of the three recovered seeds found in the tug and took all of the damaged packaging including the second package (damaged but intact) and its contents. "Measurement on the floor of the 'tug's' passenger side was reading 150 mR/hour with an Eberline RO2 ion chamber. Radiation measurements on the crushed pig lid were about 25 mR/hour with an RO2 and a contamination measurement of about 400 cpm with a GM instrument. Contamination reading on the crushed box was about 300 cpm with the GM instrument. A spot on the tarmac was found reading about 12 mR/hour with an RO2. "The outside of the undamaged stainless steel pig measurers about 5 mR/hour with an RO2. Some product is transported in a lead container and some in stainless steel. The missing material was in lead; the material in the damaged second package was in stainless steel. "WA Dept of Health and IsoRay staff were on site for a total of 4 days. WA DOH spent approximately 16 FTE days looking for the remainder of the packaging and material. Nothing additional was able to be located. "There was a local television media news story. "Notification Reporting Criteria: 10 CFR 30.50(b)(1) "Isotope and Activity involved: 330 mCi, 12.2 Gigabecqerals of Cesium 131. Cesium 131 has about a 9.2 day half-life. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): The investigation indicates it unlikely that personnel received any significant radiation exposure. However, this could not be substantiated since facility individuals were not forthcoming with information that could be used to make an exposure determination. "Lost, Stolen or Damaged? (mfg., model, serial number): 3 of 63 missing seeds recovered, contamination found in tug, packaging and on the runway. The remainder of the material was not able to be located. "Sealed Source and Device Registry: WA-1220-S-101-S "Disposition/recovery: WA DOH has indicated to FedEx management that hazardous materials transportation handling procedures should be revised and staff refresher training should be performed. "Leak test? The seeds are leak tested prior to packaging and were within limits. Seeds from the damaged second package were found to be undamaged. "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) Airport tug, N/N FedEx air bill # 730 235 322 954. "Release of activity? Three seeds found in the tug. Contamination found in the tug, on packaging and on the loading runway. "Activity and pharmaceutical compound intended: N/A Misadministered activity and/or compound received: N/A Device (HDR, etc.) Mfg., Model; computer program: N/A Exposure (intended/actual); consequences: N/A Was patient or responsible relative notified? N/A " THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-10-09
42875 | 0 | UNIVERSITY OF MISSOURI |  |  |  |  | 2006-10-04 10:50 | 2006-10-04 16:50 | 2006-10-04 | ACCIDENTAL DISPOSAL OF RADIOACTIVE MATERIAL At 10:50 CDT on 10/04/06, the RSO was notified that a custodian accidentally picked up some radioactive trash which contained 4 milliCuries of P-32. This is a beta emitter with a 14 day half-life. The incident occurred during business hours on 10/03/06 at Stadler Hall (Room S402) on the University of Missouri campus. The licensee traced the event and found out the custodian took the trash to the dumpster, which was then picked up by Allied Waste System, who then transferred it to their landfill site in Roxanna, IL. The operator at the landfill indicated no alarms were activated when this trash truck entered the landfill. The RSO stated the trash in the research lab (S402) was put into a container marked "radioactive material", although the double bagged waste material (P-32) was not marked. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-10-04
42874 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-09-27 | 2006-10-04 11:01 | 2006-10-04 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE "A technician was performing radiography operations at an off site facility. The technician had completed an exposure and had returned the source to the camera. The technician noted the survey meter setting about six [feet] in front of the camera was going towards zero. Was setting up for the next exposure. The technician disconnected the guide tube from the camera and relocated it to the new location. Upon returning to pick up the camera, the technician noticed the source hanging out of the camera. The technician cranked the source into the camera. The technician notified his supervisor of the event. The supervisor instructed the technician to cease all work and to bring his film badge, alarming dosimeter, and dosimeter to the office. The film badge was overnighted to the licensee's processor. On 10/3/06, the processor reported the exposure for the film badge to be 16543 mrem DDE. The workers total for the year is reported as 19538 mrem DDE. A safety meeting was held for all radiographers at the licensee facility on October 3, 2006 to discuss proper performance of surveys when conducting radiography operations. It appears at this time that no other persons were exposed to the high dose rates." Texas Incident #: I-8365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-10-09
42873 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-08-08 16:17 | 2006-10-03 15:40 | 2006-10-03 | 60 DAY REPORT - INVALID ACTUATION OF AUXILIARY FEED PUMP 2B "This 60-day report as allowed by 10 CFR 50.73 (a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Auxiliary Feedwater System (AFW). This event involved an invalid actuation of the Motor Driven Auxiliary Feedwater pump 2B during routine Unit 2 Auxiliary Safeguards Testing on 8/8/06. The system was properly aligned and did inject water into Steam Generators 2C and 2D as designed to perform a complete actuation of AFW pump 2B. "The motor driven auxiliary feedwater pumps will automatically start and provide the minimum required feedwater flow within one minute following any of these conditions: "1. Two out of four low-low level alarms in any one of the four steam generators. "2. Loss of both main feedwater pumps "3. Initiation of safety injection signal "4. Loss of station normal auxiliary electric power "5. AMSAC signal "Since none of the five auto-start parameters were met at the time of the system actuation the signal was determined to be invalid. "Engineering reviewed the CA Pump Start circuit to determine which equipment failures could cause the switchgear breaker for the AFW Pump 2B to close and start the pump. These included reviewing sequencer start signals, manual pushbuttons, and associated contacts and breakers. The failure of the fluke meter used during the testing was considered, also. In addition, the Operations Test Group performed an analysis of the human performance aspects of this testing. Based on these investigations potential equipment failures have been ruled out and based on the correspondence in time with when the inadvertent start occurred and when the meter reading was taken, it is believed that the inadvertent start is due to an anomaly with the Fluke 189 meter or issues when taking the measurement. The measurement is taken across an energized circuit, which can be susceptible to inadvertent actuations. The test procedure has been revised to open links on the circuit to prevent inadvertent operation." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-10-03
42872 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2006-10-03 | 2006-10-03 14:51 | 2006-10-03 | FITNESS FOR DUTY ISSUE - 24 HOUR NOTIFICATION MISSED Notification was to report that on 9/27/06 at 1418 hours a company employee self identified the use of a controlled substance. Access was immediately suspended; employee was mandatory referred to EAP and will require admission into the follow-up testing program. The employee is not involved in any safety related activities and is not licensed. The NRC Resident Inspector was notified of this event by the licensee. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 26.73 |  |  |  | 0 | 2006-10-03
42871 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-10-02 14:26 | 2006-10-02 17:29 | 2006-10-02 | OFFSITE SIRENS INOPERABLE FOR PLANNED MAINTENANCE "Surry Early Warning System (EWS) siren activation system was briefly inoperable from 14:26 hours to 16:28 hours on October 2, 2006, for antenna replacement preventive maintenance due to a degrading connector. "This event is reportable in accordance with 10CFR50.72(b)(3)(xiii), any event that results in a major loss of offsite communications capability, (e.g., offsite notification system). "This preventive maintenance was coordinated in advance with offsite agencies for compensatory measure purposes (backup route alerting within 45 minutes). "Return to service testing has verified 68 of 68 sirens are operable (100 %). The current availability of the EWS no longer constitutes a major loss of off site communication capability pursuant to 10CFR50.72(b)(3)(xiii). "Information related to the return to service of these sirens has been transmitted to the offsite agencies. This is the final report that will be issued relative to siren system restoration efforts following this preventive maintenance. Normal siren system status monitoring practices will remain in effect going forward." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-10-02
42870 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-10-02 08:05 | 2006-10-02 08:47 | 2006-10-02 | SAFEGUARDS REPORT Actual entry of an escorted but unauthorized person into the protected area . The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | NC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-10-02
42869 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-10-01 08:35 | 2006-10-01 15:24 | 2006-10-01 | TEMPORARY SCAFFOLDING FOR UPCOMING OUTAGE RENDERS 'A' AND 'B' MSIV INOPERABLE "Scaffold that was built for upcoming refueling outage work at Beaver Valley Power Station Unit 2 may have prevented two Main Steam Isolation Valves (MSIV) from reaching the full closed position. "Scaffold was built on 9/29/06 and 9/30/06 for refueling outage work on the 'A' and 'B' MSIV's. The 'C' MSIV was not impacted. Some of the seismic bracing for these scaffolds were in the area of travel when closing the MSIV's. There is reasonable assurance these braces would have prevented the 'A' and ' B' MSIV's from reaching the full closed position. During a Steam Generator Tube Rupture accident, this MSIV interference may have prevented accident mitigation by not allowing the MSIV to properly close and cause additional release of radioactive material to the environment beyond that already analyzed in the Updated Final Safety Analysis Report. "On 10/1/06 at 0835 the MSIV inoperability was discovered and Technical Specification 3.7.1.5 (MSIV Operability) and 3.0.3 were entered. The scaffold bracing was moved out of the valve closure path of the 'B' MSIV and at 0915 Technical Specification 3.0.3 was exited. At 0945 the 'A' MSIV was free to close and Technical Specification 3.7.1.5 was exited. This is being reported as a loss of a safety function for a Main Steam Line Isolation Valve which is required to control the release of radioactive material, and which is required to mitigate the consequences of an accident, pursuant to 10 CFR 50.72(b)(3)(v)(C) and 50.72(b)(3)(v)(D). "Unit power remained constant throughout the event and no other safety systems have been compromised." The licensee is currently lowering power for the Unit 2 refueling outage. The licensee notified the NRC Resident Inspector. | 0 | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2006-10-01
42868 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-06-01 | 2006-09-29 15:29 | 2006-09-29 | AGREEMENT STATE REPORT INVOLVING A LOST GAS CHROMATOGRAPH The following information was received via fax: "During an inspection of the Sewerage and Water Board of New Orleans it was discovered that a Hewlett-Packard Gas Chromatograph, model number 18713A, with 15 mCi of Ni-63 foil could not be located. According to the inventory, it was placed into storage in 1995, but it could not be inventoried in December 2005 due to Hurricane damage to the storage facility. The facility tried to locate the GC around June 2006, but could not locate the unit. The facility failed to notify the Louisiana Department of Environmental Quality of the missing GC and has been cited. This incident is under investigation. The NRC will be notified of any additional information once it is received. "Event Report ID No.: LA060018" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-10-04
42867 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-08-09 09:51 | 2006-09-29 15:02 | 2006-09-29 | INVALID EECW PUMP ACTUATION DURING TESTING "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of an emergency service water system component that does not normally run and which provides an ultimate heat sink. "At 0951 hours CDT on August 9, 2006, with Unit 1 defueled and Units 2 and 3 operating at 100% power, the B3 Emergency Equipment Cooling Water (EECW) pump was tripped when an undervoltage relay was manually operated during functional testing of relaying associated with the 1B Core Spray (CS) pump breaker. While operations personnel were responding to the pump trip, but before the testing activity could be halted, performance of subsequent steps in the functional testing activity resulted in an automatic start of this same pump and then another trip when a companion undervoltage relay was manually operated. Auto-starting of associated EECW pumps upon CS pump starts is part of the equipment logic and had been anticipated, and the B3 EECW pump had been placed in service prior to beginning the relay functional testing to avoid an automatic start. The potential for tripping loads other than the 1B Core Spray pump breaker was discussed in the pre job briefing, however, the actual test instruction steps did not provide detail sufficient to ensure only specific undervoltage relay contacts were operated. Rather than operating only specific relay contacts, test personnel operated the entire relay, resulting in the unplanned trip, restart, and trip of the B3 EECW pump. "The logic downstream from the manually operated undervoltage relays and the B3 EECW pump responded in accordance with the plant design. No other plant equipment was affected during this event, though the 2B Core Spray pump would have also tripped had it been running at the time the undervoltage relays were operated. The B3 EECW pump was secured, and the testing activity was suspended. Other operating EECW pumps were not affected and no degradation of EECW system function occurred. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for evaluation and resolution. Reference corrective action document PER 108425." The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-09-29
42866 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-09-28 18:02 | 2006-09-29 14:41 | 2006-09-29 | FAILURE OF AUTOCLAVE HIGH CYLINDER PRESSURE SYSTEM "At 1802 CDT on 09/28/06, the Plant Shift-Superintendent (PSS) was notified of a failure of the C-333A Autoclave 3 South High Cylinder Pressure System (HCPS). During a normal cylinder heating cycle the operator noted that the cylinder pressure, as read on a local digital pressure indicator and on a digital recorder in the Operations Monitoring Room (OMR), unexpectedly fell from a steady 65 psia to a negative value on both instruments. A 14 ton cylinder containing 0.4019% U235 assay uranium hexafluoride had been heating (TSR Mode 5) for approximately 2.2 hours when the failure occurred. The PSS declared the HCPS inoperable and TSR LCO 2.2.4.14B actions were implemented to place the autoclave in Mode 2, 'Autoclave Open and Out-of-Service'. The HCPS is a TSR system designed to minimize the potential of primary system integrity failure (cylinder rupture) during a pressure increase event by tripping the steam supply to the autoclave prior to reaching the Maximum Allowable Working Pressure (MAWP) of the cylinder. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident, b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. There was no release of radioactive material. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-09-29
42865 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-09-27 02:47 | 2006-09-27 04:26 | 2006-09-29 | TECHNICAL SUPPORT CENTER HVAC REMOVED FROM SERVICE FOR MAINTENANCE "On 9/27/2006, the HVAC for the Hatch Nuclear Plant's Technical Support Center (TSC) was removed from service for planned preventive maintenance and inspections and testing activities. These work activities are planned to be performed and completed within a 12 hour work shift. During the time these activities are being performed, the TSC air handling unit, TSC condensing unit, TSC filter train and the fan unit for the TSC filter train will not be available for operation. As such, the TSC HVAC will be rendered non-functional during the performance of this work activity. "If an emergency condition requiring activation of the TSC occurs during the time these work activities are being performed, then contingency plans call for utilization of the TSC as long as radiological conditions allow. The site Technical Support Center activation procedure provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity affects an emergency response facility for the duration of the evolution." The licensee will notify the NRC Resident Inspector. * * * UPDATE RECEIVED FROM ANDY DISMUKE TO JOE O'HARA AT 1014 ON 9/28/06 * * * "The maintenance outage affecting the normal power supply for the TSC HVAC was not completed yesterday (September 27, 2006) as originally scheduled. The work schedule called for the normal power supply to the TSC HVAC to be returned to service within 12 hours; however, problems occurred in the functional test of the associated bus that provides the normal power supply to the TSC HVAC. During the functional test, the bus successfully swapped from normal supply to alternate supply, however the swap back to normal was unsuccessful. When the alternate breaker was tripped per procedure, the normal breaker indicated closed (green and amber lights extinguish, red light illuminated as expected, but the motor control center (MCC) was not energized. Maintenance has subsequently reenergized the MCC from alternate supply and TSC HVAC is now functional as of 0808 today (September 28, 2006). The total out of service time for the TSC HVAC was approximately 29 hours, 21 minutes. "A repair plan is being developed to make necessary repairs to the breaker for the normal supply. Once repairs are completed, the breaker will be re-installed so that the MCC can be re-energized from the normal supply. This repair activity will require the TSC HVAC to be removed from service again in order to switch back to the normal power supply. An update will be provided when this evolution is expected to occur. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022 Rev 2 since this work activity affects an emergency response facility for the duration of the evolution." The licensee will notify the NRC Resident Inspector. The R2DO(Collins) has been notified. * * * UPDATE ON 9/28/06 AT 15:02 FROM HATCH (DISMUKE) TO ABRAMOVITZ "On 9/28/06, the HVAC for the Hatch Nuclear Plant's Technical Support Center (TSC) is being removed from service to install the normal supply breaker in the MCC that supplies power to the TSC HVAC following breaker repairs. Estimated time for the TSC HVAC being out of service is 6 -8 hours. An update will be provided when the TSC HVAC is returned to service." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Collins). * * * UPDATE 9/29/06 AT 0004 ET FROM HATCH (F. GORLEY) TO M. RIPLEY "On 09/28/06 at 2329 ET, the HVAC System for the TSC was returned to functional status following the replacement of the normal supply breaker to the MCC and energizing the MCC that supplies the TSC HVAC. Walk-down of the HVAC System for proper operation was completed at 2335 ET." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Ayres). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-09-27
42864 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-09-26 15:13 | 2006-09-26 17:18 | 2006-09-26 | MANUAL REACTOR TRIP DUE TO REACTOR COOLANT PUMP SEAL LEAKAGE. Salem Unit 2 was manually tripped from 94.1 percent reactor power due to Reactor Coolant Pump "21" number 1 seal leakoff exceeding 6 gpm in accordance with abnormal operating procedure. Reactor Coolant Pump "21" was subsequently stopped upon reactor trip verification in accordance with the Abnormal Operating Procedures. Forced reactor coolant system circulation is via the remaining 3 reactor coolant pumps. All safety systems functioned as designed. Auxiliary feedwater pumps started as expected, offsite power is available, Emergency Diesel Generators are available but not required at this time. Decay heat removal is via steam dumps to the main condenser. Salem Unit 2 is currently stable in Mode 3 (Hot Standby). There is no equipment out of service that contributed to this event. There were no personnel injuries or radiological occurrences associated with this event. The licensee is investigating to determine the cause of the abnormal reactor coolant pump seal leakoff flow rate. The licensee notified local government officials. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-09-26
42863 | 0 | HERITAGE VALLEY HEALTH SYSTEM |  |  |  |  | 2006-09-01 | 2006-09-26 16:14 | 2006-09-27 | MEDICAL EVENT - ONLY ONE CAPSULE OF A TWO CAPSULE DOSE ADMINISTERED "On 9/1/06 at Sewickley Valley Hospital, a technician removed a vial of I-131 therapy capsules and measured the dose in the dose calibrator to ensure that the dose measured the expected amount of 100 millicuries. The dose was administered to the patient by emptying the contents of the vial into the patient's hand. Only one of the I-131 capsules came out of the vial instead of two. The vial was placed back into the shipping container and returned to the pharmacy. "On 9/26/06, the pharmacy notified Sewickley Valley Hospital's RSO that the technicians at SVH had returned one of the two capsules to the pharmacy. The notification occurred during the RSO's investigation into a separate medical event that had occurred on 9/21/06 under similar circumstances. The pharmacy had discovered the second capsule on 9/11/06 but there are no records of the pharmacy contacting the hospital about it. The pharmacist who would have made the call is on vacation and not available for questioning until next week. "One of the two capsules had apparently remained in the vial during the administration to the patient. The RSO reported that the dose to the patient was approximately 35 millicuries instead of the 100 millicurie prescribed dose. The hospital has already contacted the referring physician and plans on contacting the patient to make arrangements to administer the rest of the prescribed dose. The hospital will also institute changes in their procedures requiring the vial to be visually inspected and checked in the dose calibrator following use to prevent this from happening in the future." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM LICENSEE (PERNA) TO HUFFMAN AT 11:17 EDT ON 9/27/06 * * * The licensee provided an e-mail edit to the original event report to correct some inaccuracies in the information originally reported to the NRC. R1DO (Hott) and NMSS (Wastler) notified. * * * UPDATE FROM CYNTHIA FLANNERY (NRC) TO GERRY WAIG ON 9/27/06 AT 1532 * * * Then NRC Medical Radiation Safety reviewed this event and determined it to be a reportable medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-09-27
42862 | 0 | HERITAGE VALLEY HEALTH SYSTEM |  |  |  |  | 2006-09-21 | 2006-09-26 09:42 | 2006-09-27 | MEDICAL EVENT - ONLY ONE CAPSULE OF A TWO CAPSULE DOSE ADMINISTERED The licensee provided the following information via email: "On 9/21/06 at Sewickley Valley Hospital, a technician removed a vial of I-131 therapy capsules and measured the dose in the dose calibrator to ensure that the dose measured the expected amount of 25 millicuries. The dose was administered to the patient by emptying the contents of the vial into the patient's hand. Only one of the I-131 capsules came out of the vial instead of two. The vial was placed back into the shipping container and returned to the pharmacy. "On 9/25/06, the pharmacy notified Sewickley Valley Hospital that they had returned one of the two capsules to the pharmacy. One of the two capsules had apparently remained in the vial during the administration to the patient. The RSO reported that the dose to the patient was approximately 5 millicuries instead of the 25 millicurie prescribed dose. The hospital has already contacted the referring physician and plans on contacting the patient to make arrangements to administer the rest of the prescribed dose. The hospital will also institute changes in their procedures requiring the vial to be visually inspected and checked in the dose calibrator following use to prevent this from happening in the future." A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM LICENSEE (PERNA) TO HUFFMAN AT 11:17 EDT ON 9/27/06 * * * The licensee provided an e-mail edit to the original event report to correct some inaccuracies in the information originally reported to the NRC. R1DO (Hott) and NMSS (Wastler) notified. * * * UPDATE FROM CYNTHIA FLANNERY (NRC) TO GERRY WAIG ON 9/27/06 AT 1532 * * * Then NRC Medical Radiation Safety reviewed this event and determined it to be a reportable medical event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2006-09-27
42861 | 0 | WEAVER BOOS CONSULTANTS |  |  |  |  | 2006-09-25 13:00 | 2006-09-25 15:08 | 2006-09-25 | TROXLER MOISTURE DENSITY GAUGE LOST DURING SHIPMENT On 09/20/06 Troxler Naperville, IL office sent a Troxler Model # 3430 to Weaver Boos Consultant office located at 5677 DTC Blvd, Suite 102, Greenwood Village, CO. The gauge was to have arrived at the Weaver Boos Consultant, Greenwood Village, CO office on 09/22/06. Licensee contacted the shipper, FedEx. FedEx is looking for the gauge. The gauge contains 8 millicuries of Cesium-137 and 40 millicuries of Am-241/Be. The serial number of the gauge is 29815. The licensee reported this incident to NRC Region III office. *** UPDATE FROM WARD TO KNOKE AT 10:25 ON 09/27/06 *** Notified by licensee that FedEx has located the missing Troxler gauge, Model # 3430, and has delivered it to the licensee's office in Greenwood Village, CO. Notified R3DO (Burgess), NMSS (Wastler) and Emailed ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | IN | MAT | [5 empty] | 0 | 2006-09-25
42860 | 0 | WATERFORD | 3 |  |  | [3] CE | 2006-09-07 07:50 | 2006-09-25 14:33 | 2006-09-25 | INVALID SYSTEM ACTUATION "On September 7, 2006 at about 0750 CDT, an invalid actuation of B train Engineered Safety Features Actuation System (ESFAS) occurred during maintenance on ESFAS relay K110 B. The following B train Engineered Safety Features Actuation System (ESFAS) relays de-energized: K101, K102, K103, K108 and K109. "The event is reportable per 10CFR 50.73(a)(2)(iv)(A) as a 60 day notification and is being reported to the NRC by phone within 60 days. "The invalid actuations did not occur when the systems had already been properly removed from service nor after the safety function had already been completed. "The 32B buss de-energized which resulted in loss of pressurizer heaters Bank B and Containment Fan Coolers B and D actuated by shifting to slow speed. There was no actual Emergency Core Cooling System (ECCS) system flows actuated. "All of the affected equipment functioned as designed when the relays deenergized "The NRC Senior Resident was informed of the event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-09-25
42859 | 0 | MEDICAL PHYSICS CONSULTANTS |  |  |  |  | 2006-06-28 13:20 | 2006-09-25 13:25 | 2006-09-25 | INCORRECT INITIAL PRESCRIBED DOSE On 6/23/06, a physician prescribed a dose of 10 microcuries of iodine-131 for a patient with Graves' disease. The physician meant to have written the prescribed dose to be 10 millicuries. On 06/28/06, the dose was placed in a calibrator and measured at 10 millicuries with the physician present. After the dose was calibrated at 10 millicuries the physician signed, but forgot to date it, for the patient to receive the 10 millicurie dose. The patient received the 10 millicurie dose. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-10-01
42858 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-09-22 06:00 | 2006-09-25 12:19 | 2006-09-25 | AGREEMENT STATE REPORT - TRAFFIC ACCIDENT INVOLVING A TRUCK CARRYING RADIOACTIVE MATERIAL The State provided the following information via email: "The Division of Radiation Health (DRH) received notification on 9-22-06 from Mississippi Emergency Management Agency about a traffic accident that occurred at 6:00 AM on Highway 43 North of Picayune, MS. The vehicle was delivering radiopharmaceuticals to area hospitals and clinics. The road was wet due to rain and the driver lost control of vehicle and collided with 2 other vehicles. Several of the shipping containers were ejected from the vehicle and some of the contents were deposited outside the shipping containers. Local sheriff department and fire departments responded to the accident scene. DRH responded to the scene of the accident as well as Cardinal Health personnel. Cardinal Health personnel discovered that no contamination had leaked from the containers and no personnel were contaminated. Vehicle was transporting 6 boxes (ammo boxes used as shipping containers) containing a total of 892 millicuries of Technetium-99m and Xenon-133. Some boxes contained used doses that had already decayed to near background radiation levels." Mississippi Incident Report number: MS 06011 See Louisiana Agreement State Report: Event Number 42855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-09-28
42857 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-09-24 04:30 | 2006-09-24 10:15 | 2006-09-24 | EMERGENCY NOTIFICATION SYSTEM AND COMMERCIAL TELEPHONE LINE PROBLEMS "On 9/24/06 at approximately 0430 EST, the NRC Duty Officer attempted to contact the plant via the ENS (Emergency Notification System) phone for the daily plant status. Communications via the ENS phone had apparently failed, and attempts by NRC to use the commercial lines for Unit 1, Unit 2 and the Shift Manager were also unsuccessful. The plant was notified at approximately 0650 by the TVA ODS (Operations Duty Specialist) that the NRC was apparently unable to communicate with Sequoyah via the ENS phone and commercial lines. Sequoyah staff was able to communicate with the NRC Duty Officer with a commercial line, however, the ENS phone line was not functional at that time. At approximately 0700, the ENS phone was successfully utilized to communicate with the NRC Duty Officer. This event is being reported under 10CFR50,72(b)(3)(xiii), Loss of Emergency Preparedness Capabilities. An investigation will follow to determine the cause and required corrective actions." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-09-24
42856 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2006-09-22 | 2006-09-22 16:13 | 2006-09-22 | AGREEMENT STATE REPORT - OVEREXPOSURE This event involves a mis-administration of a therapeutic dose of Sm-153. The written directive was to administer 74 millicuries of Sm-153. This dose was exceeded by at least 58%. The state will provide updated information as it becomes available. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2006-09-28
42855 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-09-22 | 2006-09-22 14:44 | 2006-09-22 | AGREEMENT STATE REPORT "A Cardinal Health vehicle from the Slidell, LA location was carrying 1214 mCi of Tc-99 and 40 mCi of Xe-133 to a Mississippi facility when it was involved in an accident on Highway 43 in Mississippi. Cardinal Health notified the appropriate authorities in Mississippi. Emergency Response in Mississippi took control of the vehicle." Louisiana event report ID number: LA060017 See Mississippi Agreement State Report: Event Number 42858. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-09-27
42854 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-09-21 18:15 | 2006-09-21 20:13 | 2006-09-21 | OSCILLATION POWER RANGE MONITORS (OPRMS) INOPERABLE "On September 14, 2006, the Plant Staff was notified by General Electric (GE) via a draft Safety Communication SC06-010 of a potential non-conservative setting of the OPRM Enabled Region Drive Flow Setpoint when the plant is in Single Reactor Recirculation Loop Operations. On September 21, 2006, at 1815 hours, based on available information, it was conservatively determined that all four OPRM channels were inoperable due to their current flow setpoint settings and uncertainties associated with OPRM enabling. "The OPRM instrumentation provides inputs to the Reactor Protection System. The OPRM instrumentation is relied upon for providing a safe shutdown safety function when operating during an unstable power to flow condition. Operations personnel entered Technical Specification LCO 3.3.1.3 Action B.1 to initiate an alternate method to detect and suppress thermal hydraulic instability oscillations. "This event is being reported as a condition that could have prevented the safety function of structures or systems required to shut down the reactor and maintain it in a safe shutdown condition. These actions and this report are based on preliminary information. Updates will be provided as necessary as additional information becomes available." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2006-09-21
42853 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-09-21 12:00 | 2006-09-21 14:05 | 2006-09-21 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE Troxler Gauge model 3440, Serial number 24024, was stolen from the locked box in the back of the work truck at 1200 EDT on 09/21/06. The work truck was located at 1090 NW North River Drive, Miami during the theft. The lock on the storage box was cut with bolt cutters and the box remains in the vehicle. Miami-Dade Police have been notified and a police report is pending. The gauge contained a Cs-137 8 millicurie source, serial number 75-6012, and an Am-241 40 millicurie source, serial number 47-20055. Florida Incident Number: FL06-119 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-09-26
42852 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-09-08 10:15 | 2006-09-21 12:20 | 2006-09-21 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION: INAPPRORIATE CHANGE MADE TO EMERGENCY ACTION LEVEL 3J BACK IN 1997 CAUSED AN EMERGENCY, ALERT, NOT TO BE DECLARED. "On 9/08/2006 at 1015 during painting activities in a safety-related area the Methanol Short Term Exposure Limit was exceeded. In accordance with Callaway Plant procedures the location was determined to contain a Hazardous ATMOSPHERE. Subsequently, Callaway Plant Emergency Action Levels (EAL) were reviewed and it was determined that the event did not meet the EAL criteria for Callaway Plant EAL 3J related to release of flammable or toxic gases in a safety - related area. "On 9/21/2006 following a debrief that was conducted by Region IV NRC personnel, it was determined at 1025 that an inappropriate change to the intent of EAL 3J was made in 1997. As a result of this discussion, it was determined that an Alert should have been declared in accordance with plant EAL 3J. "Per guidance given in NUREG 1022, Revision 2, Section 3.1.1. "Immediate Notifications", an ENS notification is being made within one hour of discovery of the event. No actual declaration of the emergency class will be made since the event has been concluded and the basis for the emergency no longer exists. "The NRC Resident Inspector has been notified." Licensee also notified State, Local Officials and other government agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW | [5 empty] | 0 | 2006-09-21
42851 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2006-09-20 | 2006-09-20 17:17 | 2006-09-21 | IRRADIATOR SOURCE TEMPORARILY STUCK IN THE EXPOSED POSITION On the night of 8/28- 8/29/2006 the large irradiator was being used for an all night procedure. The principle investigator for the irradiator was present to conclude the operation on the morning of August 29. At the time designated for source retraction, the irradiator source in fact did not retract to the stowed position. The source actuation system uses air pressure to expose the source and spring force to stow the source. The principle investigator tried to house the source by operating the "override" button. The source remained exposed. After approximately 15 minutes the source returned to the housed condition with no operator action. The irradiator will not be used until J.L. Shepard [the manufacturer] is contacted and the cause identified and corrected. The source is currently stowed. The irradiator is an 8800 Curie Cs-137 self shielded irradiator. Iowa event number I806004 The state notified Region 3 (Lynch). * * * Update on 09/21/06 at 1510 ET from Randy D' Ahlin to MacKinnon * * * The following updated information was called in by the State of Iowa Department of Public Health: The irradiator type is an open beam irradiator. The irradiator has been repaired, tested and placed back in service on 09/21/06. R3DO (Julio Lara) and NMSS EO (Cindy Flannery) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2006-09-25
42850 | 0 | PENNSYLVANIA HOSPITAL |  |  |  |  | 2006-05-19 | 2006-09-20 12:56 | 2006-09-20 | MEDICAL EVENT INVOLVING UNDERDOSE DUE TO POSSIBLE PATIENT INTERVENTION On May 19, 2006 an elderly patient was framed and imaged for the treatment of a single large metastatic lesion. The measurements indicated that there would be a "collision" between the anterior left post and the gamma knife helmet. The neurosurgeon who was responsible for the patient decided that it would be in the best interest of the patient to remove the anterior left pin and post rather than having to re-frame and re-image the patient. After the left post was removed the other pins were checked to confirm that the frame was still firmly attached to the patient. In the middle of the first of nine shots, the patient became very agitated and her body was observed to shift. The patient's head is not observable with either of the closed circuit TV cameras when the patient is in treatment position. The treatment was halted after the first shot to examine the patient and found that she was not held in place by the pins. The patient's neurosurgeon immediately spoke with the patient's daughter to explain what had happened and they decided to reschedule the treatment for the following week. On May 26, 2006, the patient was treated to a dose of 18 Gy to a volume of about 6.5 cc. If the patient was in one position during the shot delivered on May 19, the delivered dose is estimated to be 6 Gy to a volume of about 0.6 cc. There is no way of knowing the exact position of the patient's head during this 3.86 minute treatment. At the end of the shot, it was observed that her head was at the correct level but that her head may have dropped down. This would have resulted in a dose delivered anterior to the lesion. Since dose homogeneity is not important for gamma knife treatment and the volume in question is a small fraction of the volume prescribed treatment volume and the position was uncertain, the dose from May 19 was not considered for the treatment of May 26. The area of the patient's brain that could have received unintended incorrect dose did not include an area that would be detrimentally affected by the dose given. A "Medical Event" may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-09-26
42849 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2006-09-19 12:08 | 2006-09-19 16:08 | 2006-09-19 | LOSS OF ALL EMERGENCY SIRENS FOR GREATER THAN ONE HOUR "On September 19, 2006, at approximately 1208 hours, the Emergency Planning Department in conjunction with the Indian Point Energy Center (IPEC) Information Technology (IT) Department determined that all of the 156 sirens in the IPEC Emergency Planning Zone were unavailable due to an inability to activate the sirens through the siren computer operating system. The siren computer operating system was unavailable due to its Oracle Database not responding to a restart command during a routine bi-weekly reboot and preventive maintenance activity. Actions were initiated to recover the siren computer operating system and at approximately 1310 hours, the system was determined to be recovered and a test verified that all 156 sirens could be activated. In accordance with the IPEC reporting procedure, the loss of 16 or more sirens that can not be returned to service in one hour, constitutes a major loss of the offsite notification capability that requires an 8-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(xiii). The Emergency plan has route alerting and public radio announcement available as necessary to notify the public during the time the sirens were not capable of being activated. The condition was recorded in the IPEC corrective action program and actions initiated to investigate and correct the condition. The cause of the failure of the Oracle Database not responding is unknown at this time." The licensee notified the NRC Resident Inspector and the State and Local Emergency Planning organizations. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-09-19
42848 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2006-09-19 10:00 | 2006-09-19 13:09 | 2006-09-19 | AUTOMATIC REACTOR TRIP DUE TO GENERATOR LOCKOUT SIGNAL "At approximately 1000 EDT on September 19, 2006, with the reactor at 100 percent power in Mode 1, the reactor was automatically tripped from a turbine trip due to a generator lockout signal. The cause of this signal is under investigation. The auxiliary feedwater system actuated as expected to stabilize steam generator levels. All systems functioned as required and no other safety systems were actuated. All control rods inserted [fully] on the reactor trip. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load reactor coolant system temperature and pressure following the reactor trip. Steam generator water levels are being maintained using normal feedwater. All emergency core cooling system equipment is available. The plant electrical system is available and in a normal configuration. "This condition is being reported as an unplanned reactor protection system actuation and specified system actuation in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The MSIVs are open with the steam generators discharging steam to the main condenser using the steam dump valves. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-09-19
42847 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2006-09-19 01:05 | 2006-09-19 04:08 | 2006-09-19 | PRESSURIZER HEATER CAPACITY LESS THAN TECH SPEC LIMIT "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On September 19, 2006, at approximately 01:05 hours Mountain Standard Time (MST), Palo Verde Nuclear Generating Station (PVNGS) Unit 1 commenced a reactor shutdown required by Technical Specification 3.0.3. "Limiting Condition for Operability (LCO) 3.0.3 requires the unit shall be placed in a Mode or other specified condition in which the LCO is not applicable when an LCO is not met and the associated ACTIONS are not met, an associated ACTION is not provided, or if directed by the associated ACTIONS. "LCO 3.4.9 Pressurizer, requires two groups of pressurizer heaters OPERABLE with the capacity of each group > [greater than] 125 Kw and capable of being powered from an emergency power supply. TS LCO 3.0.3 and 3.4.9.B were entered at 22:35 hours an 09/18/06 when the Pressurizer Class Heaters were declared INOPERABLE. Engineering personnel with input from the heater manufacturer informed the Unit 1 SM [Shift Manager] and STA that reasonable assurance of OPERABILITY no longer exists. Prompt Operability Determination research to date concludes that the Heaters will not perform their design function for the specified mission time." The heaters were meggered and showed low resistance. There is no affect on Units 2 and 3. LCO 3.4.9.B is in affect for modes 1-3. The licensee intends to go to mode 3 and will evaluate continuing to mode 5. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2006-09-19
42846 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2006-09-18 15:00 | 2006-09-18 22:23 | 2006-11-10 | LOSS OF SPENT FUEL POOL (SFP) COOLING "At 1500 on 9/18/06, the 'A' SFP pump was declared inoperable due to abnormal noise. The 'B' SFP pump had previously been declared inoperable at 2330 on 9/12/06 [due to a vibration problem]. These events have resulted in a loss of SFP cooling. Current SFP temperature if 89°F. Per the Technical Requirements Manual, SFP temperature is being verified within limits of less than or equal to 150 °F once per 4 hours, and actions have been initiated to restore one SFP cooling system to OPERABLE status prior to the SFP exceeding 120 °F." The licensee is attempting to repair both SFP pumps in parallel efforts. In addition, a skid mounted SFP cooling system is being prepared for service. The spent fuel pool temperature was at 80 °F when cooling was lost and has increased to 89 °F at the time this report was made. The licensee has calculated that the SFP cooling will have to be out of service for 48 hours to reach the 150 °F limit. The licensee notified the NRC Resident Inspector. * * *RETRACTION FROM D. DUTTON TO J. KOZAL ON 11/10/2006 AT 1355 * * * "The purpose of this notification is to retract the ENS report made on 9/18/2006 at 2223 EDT (Event # 42846). The initial report was conservatively made when both trains of spent fuel pool cooling were lost. Ginna reported the situation as an event or condition that could have prevented the fulfillment of a safety function per 10 CFR 50.72 (b)(3)(v)(D). "The spent fuel pool cooling system is not credited to mitigate any design basis event, and is not required by the Technical Specifications. The Ginna UFSAR credits the volume of water in the spent fuel pool for providing cooling should forced spent fuel pool cooling be lost." "Based on this, ENS report (# 42846) is being retracted." The licensee notified the NRC Resident Inspector. Notified R1DO (Perry). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-09-18
42845 | 0 | FLEIS & VANDENBRINK |  |  |  |  | 2006-09-18 14:25 | 2006-09-18 16:36 | 2006-09-18 | DAMAGED TROXLER GAUGE The licensee reported that a Troxler Model 3430 nuclear density gauge was damaged at a work site when a road grader backed over the device. The gauge operator was present but was unable to stop the grader. The source was in the shielded position when the accident occurred and appears to be undamaged. A survey shows no contamination or unusual radiation levels. A leak test is in progress and the licensee plans to ship the gauge back to Troxler for repairs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-09-18
42844 | 0 | TYCO VALVES AND CONTROLS LP |  |  |  |  | 2006-09-15 | 2006-09-15 19:38 | 2006-09-15 | IMPROPER VALVE SPRINGS IN PRESSURE RELIEF VALVES LeBoeuf, Lamb, Green and MacRae LLP provided the following information on behalf of the licensee via facsimile: Tyco Valves & Controls LP (TVC) manufactures, sells, and services Pressure Relief Valves (PRVs) to NRC licensees for use in NRC licensed facilities. There is a potential problem with one series of those PRVs, but TVC's analysis to date leads TVC to believe that there is not an imminent safety problem with the PRVs that would require the immediate shutdown of licensed nuclear facilities. Rather, TVC believes that there is adequate assurance that the public health and safety can and will be adequately protected until such time as it is possible to replace the spring(s) at issue. The background of this matter is as follows: "The National Board of Boiler and Pressure Vessel Inspectors performed certification testing on PRVs manufactured by the TVC plant located in India (Tyco Sanmar Ltd). The valves tested by the National Board (NB) were the Crosby series JLT pressure relief valves. These valves are spring-loaded PRVs which are used to provide over-pressure protection for liquid applications. The Series JLT are certified to be in compliance with ASME Boiler and Pressure Vessel Code Sections III and VIII. The certification testing performed by the National Board indicated that these JLT valves did not meet ASME standards and so notified TVC. Thereafter, TVC performed its own testing on the JLT valves and confirmed the NB findings. "TVC performed a root-cause analysis and determined that the Spring Selection Tables were inaccurate in that the Tables specified a spring with a spring rate which was too high for the adjusted set pressure. It was further determined that, in most cases, the Spring Selection Table specified the correct spring for the higher portion of the tabulated set pressure range; however, the Table specified a spring too strong for the lower portion of the range. "The corrective action which has been taken by TVC is as follows: 1. The Spring Selection Tables are being revised and will take effect by 9/23/2006; 2. All of the safety-related PRVs which were affected by the Spring Selection Table have been identified; 3. A list of all nuclear facilities has been compiled; 4. A Product Safety Advisory is being drafted and will be forwarded to all nuclear facilities as identified in Exhibit A; and 5. The Product Safety Advisory recommends replacement of the spring. "[TVC] believes that, while not in compliance with ASME, these PRVs do not pose a safety hazard inasmuch as there are many levels of conservatism built into the design of pressurized equipment and selection of PRVs such as: 1. These valves will open at the specified set pressure and will flow some capacity at the ASME specified overpressure of 10%. Further, based on our testing, these valves will flow the ASME certified capacity at an overpressure of not more than 20%. Most equipment will have been designed with a safety factor above the set pressure of at least 200%. 2. In sizing a PRV for an application, the 'required capacity' is determined by the user and the next largest PRV is selected to assure that the ASME certified capacity of the ARV is always greater than the 'required capacity' adding additional conservatism. 3. These valves have been supplied to the industry using these same spring selections for over 21 years without incident. TVC has notified the affected NRC licensees: Arkansas Nuclear One, Beaver Valley, Calvert Cliffs, Clinton Nuclear Station, Columbia Generating Station, Davis-Besse, Fort Calhoun, Millstone Nuclear Power Station, Nine Mile Point, Oconee Nuclear Station, Peach Bottom, Salem Station, Seabrook Station, Wolf Creek Generating Station. * * * UPDATE ON 9/27/06 1150 ET VIA FAX FROM MICHAEL MCBRIDE TO MACKINNON * * * TVC has notified the additional NRC licensees: Crystal River, Farley, Indian Point, La Salle, McGuire, Robinson, St. Lucie and Turkey Point. R1DO (Chris Hott), R2DO (David Ayers), R3DO (Sonia Burgess) , R4DO (Zach Dunham) notified and e-mailed to NRR Vern Hodge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21 |  |  |  | 0 | 2006-09-15
42843 | 0 | BURLE INDUSTRIES |  |  |  |  | 2006-09-05 12:00 | 2006-09-15 12:34 | 2006-09-15 | MISSING TRITIUM SOURCE One tritium source (27 - 47 milliCuries) was determined to be missing, during an inventory being conducted to return the sources to the manufacturer, one of the tritium sources (27 - 47 milliCuries) was determined to be missing. Because the source is about the size of a grain of rice, the source is normally mounted in a lucite block. A hole is drilled in the lucite block and a set screw holds the source in place. The sources are stored in a locked cabinet. During the inventory on September 6, 2006, the RSO noted that even though the set screw was in place the tritium source was not in the lucite block. The sources have not been used in over a year and the last inventory was conducted on May 1, 2006. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-09-15
42842 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-01-18 | 2006-09-15 09:33 | 2006-09-15 | AGREEMENT STATE REPORT OF DAMAGED ALLOY ANALYZER CONTAINING A CADMIUM-109 SOURCE The State provided the following information via email: "DRH [Mississippi Division of Radiological Health] received notification on 8-7-06 from Metal Processors, Inc. that on 1-18-06 a Niton XL 309 Alloy Analyzer containing a 10mCi Cadmium-109 source (Serial # U3278NR6620) was accidentally run over by a company vehicle. Metal Processors personnel collected the device and contacted the manufacturer. The gauge was subsequently leak tested and showed no leakage. The device was sent back to the manufacturer for disposal." Mississippi Report # MS-06010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2006-09-20
42841 | 0 | AGILENT TECHNOLOGIES |  |  |  |  | 2006-09-14 | 2006-09-14 17:02 | 2006-09-20 | MISSING SOURCES In February 2006 the licensee shipped 60 Ni-63 (15 millicuries each) sources to Isotope Products Labs in California. The licensee determined today that the shipment never made it to its destination. The licensee has commenced an investigation. * * * UPDATE ON 9/15/2006 AT 1010 FROM AGILENT (RSO) TO ABRAMOVITZ * * * The RSO was able to locate Fed Ex tracking numbers and the tracking information confirms that Isotope Products Labs received the sources on February 1, 2006. The initial number of 60 sources has been revised to 65 sources. Notified NMSS (Wastler), the R1DO (Cobey) and the R4DO (Johnson). * * * UPDATE ON 9/20/2006 AT 1200 FROM AGILENT (DAVID BENNETT, RSO) TO KOZAL * * * Isotope Products have located the 65 returned sources. These were shipped back on Jan. 31, 2006 via FedEx. Received & Signed for by Isotope Products, Feb. 1, 2006. Notified NMSS (Flannery), the R1DO (Trapp) and the R4DO (Spitzberg). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-09-14
42840 | 0 | US AIR FORCE |  |  |  |  | 2006-09-14 09:45 | 2006-09-14 10:15 | 2006-09-14 | LOSS OF TWO AMERICIUM-241 NAVIGATION SYSTEM SOURCES A representative for the Air Force Master Material License reported that two 4 microCurie Am-241 sources (8 microCuries total) were lost during shipment from Eglin AFB in Florida to Robins AFB in GA. The sources are used in aircraft LANTIRN (Low Altitude Navigation and Targeting IR for Night) Pods. The shipment was made on August 30, 2006, using a commercial shipping company and was assigned a tracking number. The shipment never arrived at the destination and efforts by the shipper to locate the package have not been successful. The SSDR for the sources is FL-1116-D-01-01S. The Air Force has requested a formal letter of the circumstances of the loss and effort by the shipper to locate the missing sources. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-09-14
42839 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-09-13 09:45 | 2006-09-13 12:00 | 2006-09-16 | AGREEMENT STATE REPORT INVOLVING A STOLEN RADIOGRAPHY CAMERA The following information was received via email from Texas Department of State Health: "At approximately 0920hrs on 09/13/06, while parked at a Texaco Station located at the corner of Miller Street and 1935 Jupiter, Garland, TX 75042, a radiography truck belonging to Bonded Inspection, Inc. was stolen. The driver was in the store talking with his supervisor while the keys were reportedly left on the floorboard. This vehicle had a large dark room style camper which contained a 95-100 Ci, Ir-192 source (s/n J254) inside a model Ir 100, INC camera (s/n 4189). The first contact to TX DSHS came [redacted] at 0950 hrs. [Redacted] the situation was also reported to local law enforcement authorities (LLEA), Garland PD. GPD response time was within 10 minutes and all Dallas Fort Worth (DFW) area LLEAs have been notified also. The JTTF coordinator for the DFW area FBI was notified as was the NRC, local DSHS inspectors and the TX State Operations Center. No malicious of suspicious intent is suspected at this time. The truck is described as a white Ford F350 pick-up conspicuously posted with Bonded Inspections, Inc. and it has flames as decals on the front. The TX license number is 5YL T51." TX Incident No.: I-8362 Notified DHS (Alex Constantopoulos), DOE (Mike Wyatt), EPA (Peter Menk), USDA (Chuck Brown), HHS (Mark McKinnon) and FEMA (Chris Liggett). * * * UPDATE FROM ILTAB (ENGLISH) TO W. GOTT ON 15 SEPT 06 * * * "According to the Texas LLEA and the Texas Department of Health, the stolen truck and radiography camera were discovered at a business park in Dallas, TX approximately 3 miles from where they were taken. The source was found intact in the vehicle, and is in the possession of LLEA while they continue to investigate to find the person(s) responsible for the theft of the vehicle." Notified R4DO (Johnson), NMSS (Flanders), NRR (Case), DHS (Cassandra), DOE (Carolyn Lawson & Ronnie), EPA (Crews), USDA (Dean Giles), HHS (Smith), FEMA (Irwin Casto) and Mexico (via E-mail). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-09-18
42838 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-09-11 06:30 | 2006-09-12 15:36 | 2006-09-12 | AGREEMENT STATE REPORT - FIRE IN A LABORATORY CONTAINING NUCLEAR MATERIALS The State provided the following information via facsimile: "Duke police reported a fire on the 2nd floor of the Nanaline Duke Building at 6:30 AM September 11, 2006. OESO-Radiation Safety Division On Call staff were notified by Duke Police and responded on scene shortly after 7 AM, along with representatives of other OESO Divisions. By 7:15 AM, the Fire Department had the fire out. "Radiation Safety staff immediately obtained the inventory of the Principal Investigator whose lab the fire damaged, verifying the lab's current holdings at less than 0.8 mCi S-35, 0.6 mCi P-32, and 0.005 mCi I-125. All of these amounts are below the ingestion and inhalation ALIs , and would have presented no real health risk even if ingested in their entirety. In the unlikely event that these radioactive materials were to be involved in the fire and dispersed, atmospheric dilution would reduce the hazard to zero outside the building. "Radiation Safety staff surveyed the firefighter's gloves and boot soles as they exited the building. These surveys indicated no evidence of any radioactive contamination. Radiation survey staff surveyed the burnt lab area later that morning, again finding no indication of contamination. Radiation Safety staff also verified that the research radioactive materials had not breached their containment (dry waste containers in a room adjacent to the fire damaged lab and stock solutions in a sealed freezer in the lab). These actions and observations provide concrete assurance that this fire presented no radiation exposure to the emergency responders, Duke employees, the public, or the environment, and none of the material was lost or dispersed." The licensee informed Region I Duncan White. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-09-15
42837 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-07-18 04:47 | 2006-09-12 11:47 | 2006-09-12 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO LOSS OF POWER TO ONE REACTOR PROTECTION SYSTEM BUS "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of general containment isolation signals affecting more than one system. "On July 18, 2006, at 0447 hours CDT, with Unit 2 operating at 100% thermal power, the electrical power to reactor protection system (RPS) bus 2A was interrupted during the performance of surveillance testing on RPS circuit protectors 2A1 and 2A2. The RPS buses 2A and 2B are normally powered from motor-generator (MG) sets 2A and 2B, respectively. During testing or maintenance intervals affecting either the MG set or the normal supply circuit protectors, the affected RPS bus is powered from a transformer supply through alternate power circuit protectors 2C1 and 2C2. Power to RPS bus 2A, which was being powered through the alternate power circuit protectors via a temporary transformer, was interrupted when circuit protector 2C1 actuated on a sensed undervoltage condition. The Primary Containment Isolation System (PCIS) logic circuits powered from RPS bus 2A were de energized, and PCIS logic Groups 2, 3, 6, and 8 were actuated. None of the plant conditions which require PCIS Groups 2, 3, 6, or 8 actuation (e.g., low reactor water level, high drywell pressure, abnormal area radiation levels, high area temperature, etc.) existed, therefore these actuations are considered invalid. "The following actuations/isolations occurred: "Group 2: Isolation of the Pressure Suppression Chamber head tank pumps; and Drywell Floor and Equipment Drains Isolation "Group 3: Isolation of the reactor water clean-up system "Group 6: Initiation of the Standby Gas Treatment System; Initiation of Control Room Emergency Ventilation; and Isolation of the reactor zone and refuel zone normal ventilation systems. "Group 8: This logic isolates the Traversing Incore Probes (TIP) if they are inserted. The TIPs were not inserted at the time of this event. "All equipment responded in accordance with the plant design. Upon loss of power from the alternate source, the surveillance testing was suspended, and RPS Bus 2A was re energized from RPS MG set 2A. The affected logic was reset, and equipment was realigned as appropriate. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for evaluation and resolution. "The NRC senior resident inspector has been notified of this report. Reference corrective action document PER 106999." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-09-12
42836 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2006-09-10 15:30 | 2006-09-11 14:39 | 2006-09-11 | LOSS OF MOTOR CONTROL CENTER DUE TO ELECTRICAL SHORT "An electrical short to the wiring of a Nash vacuum pump caused failure of required operating equipment by shorting out the motor control center and blowing a fuse that supplies power to the Nash vacuum pump, health physics vacuum pumps which provide flow for building air samplers, floor high airborne radioactivity warning lights, and other support equipment and instrumentation. The UF6 processes were shut down and announcements were made to require any personnel who entered any floor in the feed materials building to wear a respirator. There was no release of radioactivity to the environment and power was restored in approximately thirty minutes and process operations were resumed. Air samples were counted on all floors in the Feed Materials Building and no high airborne radioactivity was detected. The floor air samples were counted again in approximately four hours and no airborne radioactivity was detected. An investigation is being conducted and the results will be included in the 30 day written report." The licensee informed NRC Region II John Pelchat of the event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2006-09-11
42835 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2006-09-08 04:01 | 2006-09-08 10:30 | 2006-09-08 | CONTAINMENT ATMOSPHERIC DILUTION (CAD) SYSTEM INOPERABLE "On September 8, 2006 at 04:01, DAEC declared CAD inoperable after determining SV-4332B, UPPER DRYWELL SPRAY CAD N2 OUTBOARD ISOLATION was inoperable while SV-4331B, LOWER DRYWELL SPRAY CAD N2 OUTBOARD ISOLATION was also inoperable. Actions to isolate both of these injection pathways as required by Technical Specifications made CAD injection into the Drywell unavailable. Day 1 of a 7 day LCO for Technical Specification 3.6.3.1 Condition A was entered. Per DAEC Technical Specifications bases, CAD is considered to be inoperable when both injection pathways into either the drywell or torus are not available. Since CAD is a single train safety system, this event is reportable as an 8 hour non-emergency event under 50.72(b)(3)(v)(D), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-09-08
42834 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2006-09-07 21:57 | 2006-09-07 23:23 | 2006-09-07 | AUTOMATIC REACTOR TRIP FOLLOWING SPURIOUS OPENING OF A REACTOR TRIP BREAKER "On September 7, 2006 at 2157 hours, Beaver Valley Power Station Unit No. 1 was operating at 100% when an automatic reactor trip occurred following a spurious opening of the 'B' Reactor Trip Breaker. The first-out indication for the reactor trip was turbine trip due to reactor trip. Control room personnel entered Emergency Operating Procedure E-0, 'Response to Reactor Trip and Safety Injection.' Safety systems and equipment functioned as designed following the automatic reactor trip. Reactor pressure and temperature have been stabilized following the reactor trip without requiring a Safety Injection. The plant was stabilized in Mode 3 utilizing the normal heat sink (main condenser) with steam generator levels restored to post shutdown values by the Auxiliary Feedwater System. All normal and emergency busses are energized from offsite power. "The cause of the reactor trip is being investigated." All rods fully inserted, all ESF systems remain operable, and the electrical grid is stable. The licensee notified the NRC Resident Inspector and plans to issue a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-09-07
42833 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2006-09-07 | 2006-09-07 17:45 | 2006-09-07 | AGREEMENT STATE REPORT INVOLVING A TEXAS NUCLEAR GAUGE FOUND IN A SHIPMENT OF SCRAP STEEL Cascade Steel located in McMinnville, OR received a rail shipment of scrap steel which triggered a portal alarm. During the investigation, a Texas Nuclear Gauge Model 5193, S/N B1207, containing 500 mCuries Cs-137, dated October 1978, was recovered. Thermomeasure Electronics, formerly Texas Nuclear, was contacted and confirmed that the last owner on record was Astaris of Pocatello, ID which may be out-of-business. Thermomeasure Electronics collected and disposed of sources at this location in 2002. Thermomeasure Electronic records identify the source S/N is MA5033 and that a total of eight (8) devices and one (1) gauge associated with Astaris are unaccounted for. The State of Oregon is enroute to the Cascade Steel facility to recover the source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2006-09-12
42832 | 0 | ALASKA INDUSTRIAL X-RAY INC. |  |  |  |  | 2006-08-01 | 2006-09-07 07:15 | 2006-09-07 | FAILURE OF A RADIOGRAPHIC CAMERA LOCKING MECHANISM The following information is from a letter that was sent to the NRC: "During an NRC inspection it was brought to our attention that we are required by 10CFR 34.101 to notify the Nuclear Regulatory Commission of any failure of a radiographic device or a component critical to the safe operation of the device to properly perform its intended function. The following is the information requested in 10CFR 34.101. "1. The key mechanism would not lock on a 660B Tech Ops Camera. "2. The failure of the locking mechanism is not known by us. "3. The manufacture of the equipment is AEA Technology QSA, Inc., Burlington, MA. "4. The place was Anchorage, Alaska and the date 7/23/2003. "5. The action taken to establish normal operations is ship the camera back to AEA Technology QSA and have them fix the lock mechanism when we need and additional camera. The iridium source was transferred to a IN Model IR-50 source changer and shipped to Industrial Nuclear for disposal. The camera at this time is empty and awaiting a time when we would need an additional camera. We have four operational cameras and do not have a need for this camera anytime in the foreseeable future. "6. We plan to have AEA Technology QSA repair the lock mechanism. "7. (Deleted) President of Alaska Industrial X-ray a former RSO and radiographer took the above action to prevent any over exposure to our personnel." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-09-07
42831 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2006-09-06 22:00 | 2006-09-06 23:24 | 2006-09-06 | HISTORICAL UNANALYZED CONDITION IDENTIFIED "On September 6, 2006, an unanalyzed condition was identified during the review of a previous issue discovered on April 18, 2005. The current review was being performed in response to NRC inspection questions regarding the previous issue. "On April 18, 2005, while at 100% power, both trains of standby auxiliary feed water (AFW) flow transmitters were found isolated. The plant had entered Mode 3 on April 8, 2005 for a routine startup after a refueling outage. The transmitters were restored to their normal operational alignment promptly when the condition was identified. "These two standby AFW trains are in addition to the typical safety-related AFW motor driven pump trains and turbine driven pump train, for a total of five safety-related AFW pump trains at the site. The two standby AFW trains are designed to address a high energy line break (HELB) event which would disable the other three AFW pump trains. "Both of the flow transmitters perform several functions including control room indication of standby AFW discharge flow and valve control functions for the pump discharge valve and pump recirculation valve. "With the flow transmitters isolated in both trains of the standby AFW system, an unanalyzed condition existed due to the following: During a postulated HELB, the inoperable flow transmitters would result in the recirculation valve and the pump discharge valve being both full open. Under a steam generator low pressure condition, (as a result of the HELB) with flow through both the open discharge valve and the open recirculation valve, the pump would be in a high flow rate condition until the steam generator level was recovered. The operators would have no indication of flow through the discharge valves and would be operating the system based on steam generator level. During the time assumed for the intact steam generator level recovery, the breaker for the pump motor could be expected to exceed it's time delayed current protection setpoint and trip the motor, preventing delivery of feed water to the steam generator. "Both trains of the standby AFW system are allowed by Technical Specifications to be concurrently inoperable for a period of up to 7 days. The actual inoperability occurred over 10 days while the flow transmitters were isolated. "Ginna did not report the event at the time the isolated transmitters were discovered because the transmitters' control function was not recognized to interact in an unanalyzed manner with the resulting unavailable control room indication, concurrent with the low pressure steam generator condition associated with the HELB event." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-09-06
42830 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-07-09 18:49 | 2006-09-06 16:23 | 2006-09-06 | INVALID ACTUATION OF THE B ESW PUMP "This 60-day ENS report is being made per 10CFR 50.73(a)(2)(iv)(A) and 10CFR50.73(a)(1) to report an invalid automatic actuation of systems listed in paragraph (a)(2)(iv)(B), namely emergency service water (ESW). "On Sunday July 9, 2006, at 18:49 hours, an invalid actuation of the B ESW pump occurred. The B ESW loop start was a partial actuation and the loop functioned successfully following the invalid actuation. The A ESW loop was not affected. "An investigation identified that corrosion on the D12 emergency diesel generator (EDG) jacket water pump discharge pressure switch caused the invalid partial actuation. The cause of the pressure switch failure was due to a cracked supply tube, which allowed moisture to enter the cabinet causing the corrosion. EDG jacket water pump discharge pressure is utilized to initiate logic that starts the ESW pump when the EDG is running. ESW is the cooling medium for the EDG. The switch failure also caused inoperability of D12 EDG since it defeated the capability for the EDG to start. The failed pressure switch and associated tubing were replaced and successfully tested. D12 EDG was declared operable on Monday July 10, 2006 at 12:46 hours. "An inspection of the other seven EDGs identified that the D11 EDG pressure switch was also corroded. The D11 EDG pressure switch was replaced. The inspection determined that the jacket water pressure switches on the other six EDGs were not degraded. "This event is reportable per 10CFR50.73(a)(2)(iv)(A) since B ESW pump automatically actuated on an invalid signal. "Component data: "Equipment number: PSH-GA-110B "Manufacturer: A160 Allen-Bradley Co. "Model number: 636-C3" The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-09-06
42829 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-09-06 10:15 | 2006-09-06 12:17 | 2006-09-06 | NON LICENSED SUPERVISOR FAILS A RANDOM FITNESS FOR DUTY TEST A non- licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2006-09-06
42828 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2006-09-06 02:31 | 2006-09-06 05:33 | 2006-09-06 | MANUAL REACTOR TRIP ON LOSS OF CONDENSER VACUUM "Observed degrading condenser pressure. Entered abnormal procedure DB-OP-02518, High Condenser Pressure and reduced reactor power. At <280 Mwe and > 5 inches Hg (mercury) A (absolute) , manually tripped the reactor at approximately 45% power in accordance with procedure. Normal post-trip response. Condenser pressure is slowly recovering. Still trying to determine the source of the condenser air in-leakage. "Notified Ottawa County Sheriff of main steam safety / atmospheric vent valve operation at 0231 hours per procedure." All control rods fully inserted on the trip. Decay heat is being removed using the turbine bypass valves and the motor driven feed pump. There is no steam generator tube leakage. The atmospheric vent valves / main steam safety valves lifted for a few seconds following the trip and fully reseated after the initial lifting. Plant electrical power if from the grid backfeeding to the station. The electric grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-09-06
42827 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2006-09-05 16:00 | 2006-09-05 16:37 | 2006-09-05 | OFFSITE NOTIFICATION RELATED TO JELLYFISH INFLUX On 9/4/06 at approximately 1633, the licensee secured circulating water pump no. 26 due to a significant influx of jellyfish. Per the licensee's NPDES (National Pollution Discharge Elimination System) permit, the licensee is required to notify the Maryland Department of Environment of any significant aquatic impact on plant operation. The licensee remained at 100% power throughout. On 9/4/06 at approximately 1703, the licensee restarted the no. 26 circulating water pump. The licensee notified the NRC Resident Inspector. See similar Event Notifications 42699, 42700, 42702, and 42704. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-09-05
42826 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-08-29 | 2006-09-01 13:51 | 2006-09-01 | AGREEMENT STATE - TEMPORARILY MISSING TROXLER The State provided the following information via email: "Washington State DOH was notified of a missing gauge 31 August 2006 by the licensee's radiation safety officer (RSO). "A portable gauge (Troxler model 3440, serial number 14393), had been checked out by an authorized gauge user on 29 August for transport to a temporary job-site. The gauge user had secured the gauge in a personal vehicle that day. As of the morning of 31 August, the user had not been heard from or seen since 29 August. Phone calls were made to the user's emergency contact numbers by the company RSO on 29 & 30 August trying to locate the user and gauge. The calls were unsuccessful with locating the person or gauge. "The licensee had issued the user a corporate cell phone upon hiring. Previous attempts to call the cell phone had failed. On 31 August, attempts to call the cell phone confirmed it was in service. The RSO was able to trace the location of the cell phone via its GPS (global positioning system) feature. Both the job supervisor and RSO went to the cell phone's location and found the vehicle, the gauge & the user. The gauge was locked inside the transport container, and had been locked, at all times, inside the vehicle's trunk. The gauge had been secured and in possession of the user at all times even though the user had been out of touch. "Corrective actions can be difficult when personnel choose to disregard established policies / procedures. The user was properly trained, approved & had a satisfactory work-history. Corrective actions will include refresher training and discussions with all staff about following state and company rules. "The incident was successfully concluded due to the powerful GPS resource in the cell phone. Decisive action by the licensee & the employee's job service supervisor allowed for the retrieval of the gauge. Requesting law enforcement involvement was done but played no part in recovery since the gauge was found relatively quickly. "No known media attention. "Notification Reporting Criteria: Immediate notification per WAC 246-221-240. "Isotope and Activity involved: 1 portable gauge, containing 2 sealed sources: one gamma source containing 8 millicuries cesium-137, and one neutron source containing 40 millicuries americium-241 / beryllium." Washington State event number WA-06-052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-09-06
42825 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-31 14:00 | 2006-09-01 12:23 | 2006-09-01 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "On 8/31/06, the Geosyntec RSO contacted the Radiologic Health Branch (RHB), Richmond office to notify that one of their Troxler gauges, Model 3430, S/N 28743 containing 8 mCi of Cs-137 and 40 mCi of [Am]-241 had been run over by a compactor at a job site in South San Francisco (333 Oyster Point Blvd.) around 2:00 pm. The RSO stated that the gauge operator tried to stop the compactor backing up towards the gauge but it was unsuccessful due to the noise. The gauge was severely damaged with the source rod in an unshielded position. The RSO contacted Troxler to have the unshielded source transported for disposal. Troxler was not able to provide transportation on 08/31/06. Per RSO, the gauge is secured on the job site inside a locked storage container and the unshielded rod is placed in a 5 gallon bucket of soil. They expect to transport the damaged gauge as soon as assistance from a local gauge manufacturer is received. The RHB will investigate this incident for any items of non-compliance." The State has indicated that the licensee intends to contact Campbell Pacific Nuclear (CPN) to transport the damaged gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-09-06
42824 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-09-01 11:15 | 2006-09-01 12:01 | 2006-09-01 | SHIPMENT EXERNAL RADIATION LEVELS IN EXCESS OF LIMITS "At 1115 EDT on 9/01/2006, Susquehanna LLC personnel became aware that a shipment received from another site exceeded the 10CFR71.47(b)(2) limit of 200 mr/hr contact dose rate. Contact dose rates on the bottom of the shipment are 820 mr/hr, and therefore reportable per the requirements of 10CFR20.1906(d)(2). "There is no identified surface contamination on the shipment, and the shipment only exceeded the dose rate limit on the bottom once it was lifted off the transport trailer. Doses under the trailer prior to lifting the shipment did not exceed the limit" "The transport company and the originating site have been notified. The transport vehicle left the Vermont Yankee facility on 8/31/06 and was received by SSES on 9/1/06 at 0805." . . . The driver has been contacted by the transport company. "The vehicle made two stops during transport. The first was at the first rest stop traveling west on the Massachusetts Turnpike. The second was at the first rest stop on I-87 south after exiting I-90. No one to the knowledge of the driver came in contact with the shipment. The driver arrived at Susquehanna on 8/31/06 at 2045, and slept in the truck. The driver was wearing dosimetry [TLD]." The licensee will notify State of Pennsylvania Emergency Management and has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2006-09-01
42823 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-29 13:00 | 2006-08-31 20:29 | 2006-08-31 | AGREEMENT STATE REPORT - INAPPROPRIATE DISPOSAL OF SOURCE The State provided the following information via email: "A truck carrying waste materials from Adams Steel in Anaheim set off the radiation alarm at the Simi Valley Landfill on 8/29/06. The landfill monitor reading was approximately 600K (bkg 4K). LA County [DELETED] responded to the landfill on 8/30/06 and identified the nuclide as Cs-137, with radiation levels of 13 mR/hr on the side of the truck, 1.2 mR/hr at 3 feet from the side of the truck, and background in the cab of truck. Based on these radiation readings, it appears the source is located approximately 1 foot inside of the truck and is approximately 10 milliCi in activity. A DOT exemption form was completed by LA County and the truck returned to the Adams Steel yard late on 8/30/06, and parked in a remote location. LAC completed their own 5010 (082906) on the response to Simi Valley. "RHB responded to Adams Steel on 8/31/06, and located an approximate 7 milliCi Cs-137 bare source, located approximately 3 feet from the top of the trailer load and approximately 1 foot in from the side of the trailer. The source was taken by RHB to hold until Adams Steel can arrange for disposal of the source." California incident #083006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-09-05
42822 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-08-31 14:09 | 2006-08-31 18:42 | 2006-08-31 | TECHNICAL SPECIFICATION REQUIRED SHUDOWN DUE TO RCS LEAKAGE "On August 31, 2006, licensed plant operators identified that Technical Specification 3.4.13 was not met due to a one to two gallon per minute unidentified reactor coolant system (RCS) leak. Plant Operators initiated a ramp of reactor power to take Unit 2 to mode 3, Hot Standby, at 1409 PDT. A containment entry has been initiated to identify the source of the RCS leak. The estimated restart date is preliminary, pending investigation of the leakage location. The Unit is currently ramping off line at 4-5 MW/min. Current reactor power level is 90% and 937 MW electric." The licensee stated that the suspected source of the leak is the seal table room where radiation levels have risen consistent with the containment leakage. Current unidentified leak rate is 1.3 gpm. The TS limit is 1 gpm. Current coolant activity is 1.88 microCi/ml. A press release is planned to be issued on 9/1/2006. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY D. PATTY TO O'HARA ON 08/31/06 AT 2254 EST * * * "This is a follow up to the 4 hour notification that was initiated due to initiating a Technical Specification (TS) required shutdown when Technical Specification 3.4.13 was not met. "Plant Operators entered containment and identified RCS leakage from one of the thimble tubes in the seal table 10 path. At 1622 on 8/31/06 the leakage was classified as identified leakage. The TS required shut down was stopped at 1623 as the leak rate is less than the TS leak rate limit for identified leakage. Operators have isolated the 10 path by closing the valve and the RCS leakage has stopped." Notified R4DO (Cain), NRR EO (McGinty) via e-mail, IRD MOC (Leach) via e-mail. | 0 | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-08-31
42821 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-30 15:00 | 2006-08-31 15:33 | 2006-09-01 | AGREEMENT STATE REPORT - LOST OR STOLEN HUMBOLDT GAUGE The State provided the following information via facsimile: "On 8/31/06 the licensee contacted the Radiological Health Branch (RHB) and the Operations Emergency Services (OES) to notify them that one of their Humboldt Scientific gauges, Model 5001C, S/N 1758 containing 10 milli Ci of Cs-137 and 40 milli Ci of [Am]-241 had fallen off from a truck during transportation. The RHB Richmond office contacted the ARSO on 08/31/06 and learned the following: "On 8/30/06 the gauge operator finished a job in Tulare, CA, and left the jobsite around 3:00 p.m. to go to another jobsite in Fresno, CA. When he arrived at the jobsite in Fresno, the operator noticed that the gauge was missing. He had not made any stops on his way to Fresno from Tulare. According to the ARSO, the operator had placed the gauge in the back of the truck without storing it in a type A container and it was not blocked and braced during transportation. When the operator learned that the gauge was missing, he failed to notify the RSO/ARSO. The ARSO was notified of the incident by the operator around 7:30 am on 8/31/06. They immediately contacted the RHB and OES. The ARSO also notified the Fresno CHP and the police departments in the cities of Tulare, Visalia, Kingston, Selma, Sower, and Fresno. The Fresno CHP had notified Caltrans. The RHB advised him to post a reward for $1000.00 in local newspapers for safe return of the gauge. RHB will be investigating the items of non-compliance associated with this incident." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-09-06
42820 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2006-08-31 15:30 | 2006-08-31 16:35 | 2006-08-31 | PLANT REQUIRED SHUTDOWN DUE TO 'A' AND 'B' EDG INOPERABLE. "On August 31, 2006 at 1530 EST Seabrook Station initiated a plant shutdown in accordance with TS 3.8.1.1 Action (f). On August 28, 2006 the Train 'A' Emergency Diesel Generator (EDG) was removed from service for planned maintenance. During the planned maintenance, an emergent issue [suspected diode failure on the control circuitry] was discovered. That required starting the Train 'B' EDG in accordance with the provisions of TS 3.8.1.1 Action (b). During the start of the Train 'B' EDG a voltage control anomaly was discovered that required the Train 'B' EDG to also be declared inoperable. "With two EDG's inoperable, TS 3.8.1.1 requires a plant shutdown. This event is reportable pursuant to 10CFR50.72(b)(2)(i) as the initiation of plant shutdown required by the plant's Technical Specifications. The Station currently has all three offsite power supplies and the Supplemental Emergency Power System operable." The licensee is in the process of shutting down and is currently at 60% power at a 20%/hr ramp rate with the intention of entering Mode 3. The licensee notified the NRC Resident Inspector. | 60 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-08-31
42819 | 0 | ALASKA INDUSTRIAL X-RAY, INC |  |  |  |  | 2006-08-31 10:30 | 2006-08-31 14:36 | 2007-03-20 | LOST RADIOGRAPHY CAMERA ON WAKE ISLAND The licensee reported a loss of a 10 Ci [based on source decay starting December of 2005] IR-192 radiography camera on Wake Island. In preparation for evacuation of the island on 8/29/2006 the camera was loaded in a type B(U) storage container. On 8/30/2006 Super Typhoon Yoke made land fall on Wake Island producing 150 mph winds and 30 - 40 ft storm surge. The status of the camera is unknown due to the uncertain condition of Wake Island. There currently is no information of the habitability of Wake Island and thus it is uncertain when a search can be conducted. The licensee will update the status of the material as more information becomes available. * * * UPDATE ON 09/25/06 AT 1300 ET BY PETE MILLAR TO MACKINNON * * * Per Pete Millar the US NAVY landed on Wake Island and the CONEX shipping container, in which the Industrial Nuclear Radiography Camera is stored, is still on the island and it has not been opened. In about 2 weeks a barge will leave Wake Island to ship the CONEX shipping container back to Alaska Industrial X-Ray. Mr. Millar said that they should have Industrial radiography camera back in their possession in about 3 weeks. R4DO (Zach Dunham) & NMSS EO (Greg Morell) notified. * * * UPDATE ON 03/20/07 AT 1346 EDT FROM PETE MILLAR TO MACKINNON * * * Alaska Industrial X-Ray, regained possession of their radiography camera on 12/15/06. R4DO (Greg Pick) & FSME (Greg Morell) notified. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-08-31
42818 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-31 09:00 | 2006-08-31 14:06 | 2006-09-01 | AGREEMENT STATE REPORT OF A STOLEN TROXLER MOISTURE DENSITY GAUGE The licensee, GEOCON Inc., license number 3924, reports that a Troxler Moisture Density Gauge Model No. 3440, S/N 33526 was stolen on 8/31/06. The gauge was secured in its case in a locked storage container in the rear of a locked pickup truck parked in front of the employees residence. When the employee went to his vehicle this morning at approximately 0900, he discovered that the vehicle was missing. The gauge contained 8 milli curies of Cs-137 and 40 milli Curies of Am-241/Be. The employee filed a report with the City of San Diego Police Department. The case number is 0630914N and the incident number is 66956. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-09-06
42817 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-08-31 11:11 | 2006-08-31 14:26 | 2006-08-31 | HPCI DECLARED INOPERABLE DUE TO STOP VALVE INDICATION ISSUE "At 1111, on August 31, 2006, during performance of SO-152-006 HPCI was declared inoperable when the HPCI Turbine Stop Valve FV-15612 had dual position indication. Local observation of the stop valve by plant operators and a report from the system engineer verified the valve was closed, and the problem appears to be a limit switch problem. With the lower limit switch not responding correctly the system engineer informed the control room the HPCI Ramp Generator is not reset, which will result in an over speed condition of the HPCI turbine if an actuation signal is received. "To prevent possible damage to the HPCI turbine, control room personnel overrode HPCI injection in accordance with plant operating procedures. "Plans are being developed to investigate the problem, and adjust the limit switch if required. "This is being reported as an event or condition that could have prevented fulfillment of a safety function required to mitigate the consequences of an accident in accordance with 10CFR50.72(b)(3)(v)(D)." The licensee has entered the provisions of TS 3.5.1 for this condition. No other accident mitigation systems are currently inoperable. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-08-31
42816 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2006-08-30 14:47 | 2006-08-30 17:04 | 2006-08-31 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED TO A HOSPITAL "While performing work on the refuel floor, an operator received a hand injury. The first aid team responded and the injured hand was covered. Radiation Protection personnel verified that the individual was free of contamination with the exception of the injured hand that had been covered by the first aid team. The individual was transported to an offsite medical facility for treatment as a potentially contaminated injured man." The licensee notified the NRC Resident Inspector and will notify the state. * * * UPDATE PROVIDED BY COSTEDIO TO KOZAL ON 8/31/2006 AT 1402 EDT * * * "Two site Radiation Protection (RP) technicians accompanied the injured man to the hospital. These technicians collected the materials that came into contact with the injured hand that had not been surveyed prior to transport. At the hospital, the bandage that had been applied by the first aid team was removed and no contamination was found on the bandage. The cotton glove liner, that had been left on the hand when the first aid team removed the rubber outer glove, was surveyed and found to have low level contamination on it (100 - 250 Counts per minute above background (CPM)). The cotton glove liner was removed and the hand was surveyed and found to be free of contamination. Prior to leaving the hospital the RP technicians and the hospital radiation safety officer surveyed the patient, the areas of the hospital facility where the patient had been, and the ambulance. The results of these surveys showed no radiological contamination. "The contamination of the cotton glove liner is believed to be due to leaching or transference from the rubber glove, that was being worn by the individual as he was working on the refuel bridge mast, when it was removed by the first aid team." The licensee notified the NRC Resident Inspector. Notified R1DO (Dwyer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2006-08-30
42815 | 0 | SITE BLAUVELT ENGINEERS |  |  |  |  | 2006-08-30 14:20 | 2006-08-30 14:41 | 2006-08-30 | STOLEN MOISTURE DENSITY GAUGE A Troxler moisture density gauge was stolen from a job site in Monroe County. Also stolen were tools and another moisture density gauge (see EN #42814). The gauge was locked in its transportation container, which was inside a locked gang box, which was inside a locked storage shed. The Pennsylvania Police in Swift Water were notified. The licensee notified R1 (Beardsley). The following information was provided: Troxler Model 3440 S/N 35144 Cs-137 source: 8 milliCurie Am-241:Be: 40 milliCurie THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-08-30
42814 | 0 | JBC ASSOCIATES INC |  |  |  |  | 2006-08-30 13:47 | 2006-08-30 14:28 | 2006-08-30 | STOLEN MOISTURE DENSITY GAUGE A Humboldt moisture density gauge was stolen from a job site in Monroe County. Also stolen were tools and another moisture density gauge (see EN #42815). The gauge was locked in its transportation container, which was chained to the building inside a locked storage shed. The Pennsylvania Police in Swift Water were notified. The following information was provided: Humboldt Model HS5001EZ, S/N 3541 Cs-137 source: 10 milliCurie Am-241:Be source: 40 milliCurie THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-08-30
42813 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-08-29 22:25 | 2006-08-30 02:52 | 2006-08-30 | MANUAL REACTOR SCRAM DUE TO ELECTRO-HYDRAULIC OIL LEAK "On 8/29/06 at 2225 CDT, Browns Ferry Unit 3 initiated a Manual reactor SCRAM due to EHC (Electro-Hydraulic Control) System Reservoir level lowering due to a EHC system leak. The leak was from #2 Main Turbine Control Valve. All Systems responded as required to the manual SCRAM signal. No ECCS (Emergency Core Cooling Systems) initiations occurred as a result of the manual SCRAM signal. Groups 2 (floor drains, etc.), 3 (Reactor Water Cleanup), 6 (Ventilation), & 8 (TIPs) PCIS isolations occurred at + 2 [inches] as expected as a result of the manual SCRAM with all systems isolating as required. The EHC leak rate lowered to approximately zero upon turbine trip. No indications existed of main steam relief valves (MSRVs) opening. Bypass valves controlled reactor pressure due to EHC system staying in service. Repair of the EHC leak is in progress. "This event is reportable under 10CFR50.72(b)(2)(iv)(B), 'any event or condition that results in a valid actuation of the Reactor Protection System'; 10CFR50.72(b)(3)(iv)(A), 'Any event that results in an actuation of the specified systems'. This event also requires a 60 day written report in accordance with 10CFR50.73(a)(2)(iv)(A)." Reactor Power was reduced to 78% before the reactor was manually scrammed and all rods fully inserted. The EHC oil is being cleaned up and the oil does not pose a fire threat. All ECCS and the EDGs are fully operable if needed and the electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-08-30
42812 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-29 12:30 | 2006-08-30 | 2006-08-30 | AGREEMENT STATE REPORT INVOLVING A POTENTIALLY DAMAGED TROXLER The State provided the following information via facsimile: "[The] Alternate Radiation Safety Officer called RHB to report their Troxler 3430, serial # 31984 (containing 8 mCi of Cesium-137 and 40 mCi of Americium-241) had just been run over by a water truck on a construction site in Lincoln, CA. [The Alternate RSO] stated the source rod was still intact. The gauge was taken to the Troxler facility in Rancho Cordova, CA. Troxler performed a leak test with negative results. The gauge is to be sent to Troxler headquarters in Research Triangle Park, NC for repair or eventual disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-09-01
42811 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-08-22 | 2006-08-29 10:35 | 2006-08-29 | AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via email: "Yesterday [name deleted] the medical physicist for this Aurora, IL based licensee (IL-01207-01) called to report a medical event which had come to her attention. While preparing a 'Mammosite' treatment plan for an upcoming patient, she had found that two previously administered therapy treatments were not as intended (on 7/28/06 and 8/22/06). Both treatment plans called for a dose of 3400 cGy to be administered to each of the patients over 10 fractions at 340 cGy per fraction with two fractions delivered each of 5 days. However, due to confusion and misunderstanding of the data entry into the treatment planning software, an error occurred and the dose per fraction delivered was only 34 cGy for a total treatment dose of only 340 cGy. Thus, both patients received only 10% of the dose they should have received for their cancer treatments. "The treatment planning software, named Eclipse, developed by Varian Medical Systems had a known issue with regards to 'fractionated doses'. A company technical bulletin, (CTB-BV-318) had been generated by the company in March of 2003 and provided to its customers alerting them to the appropriate method for data entry for fractionated doses. The technical bulletin for the treatment planning software contains a warning that 'incorrect use could possibly cause a misadministration.' However, Rush Copley did not acquire its high dose rate afterloading system and treatment planning software until August of 2005 and although the treatment planning software had been updated to a newer version, the same issue remained in the new version. According to the authorized user and the medical physicist, there was no training provided on this aspect of use of the treatment planning software when they had attended the manufacturer's training last year. "The hospital has administered only these two fractionated doses since they acquired the unit. Both patients have been contacted by the authorized user and the patients are considering the available options for additional treatment if necessary. Considering the treatment regimen is designed for post surgical lumpectomies of the breast, the physician believes the effect of the under dose on the patients will be minimal. The licensee has been advised of the need to file the appropriate report in the next 15 days including its corrective action. "Because the dose to the patient differs by more than 20% from that originally prescribed, the Agency must notify the U.S. NRC Operations Center with this event. "Patient Information: "Patient Number: 1; Patient Informed: Y; Date Informed: 08/28/2006 "Therapeutic: BRACHY, REMOTE AFTERLOADER, HDR "Organ: BREAST, RIGHT "Dose: 340 rad 3.4 Gy; % Dose is Less Than Prescribed: 90 "Effect on Patient: OTHER Administered By: PHYSICIAN "Patient Number: 2; Patient Informed: Y; Date Informed: 08/28/2006 "Therapeutic: BRACHY, REMOTE AFTERLOADER, HDR "Organ: BREAST, RIGHT "Dose: 340 rad 3.4 Gy; % Dose is Less Than Prescribed: 90 "Effect on Patient: OTHER "Administered By: PHYSICIAN "Source of Radiation: "Form of Radioactive: SEALED SOURCE; Radionuclide or Voltage (kVp/MeV): IR-192 "Source Use: BRACHYTHERAPY; Activity: 10.2 Ci 377.4 GBq; Manufacturer: ALPH-OMEGA SERVICES "Model Number: VS2000; Serial Number: 02-01-0699-001-062106-10250-03 "Device/Associated Equipment: "Device Name: REMOTE AFTERLOADER HDR Model Number: VARISOURCE "Manufacturer: VARIAN Serial Number: VS60037 "Reporting Requirements: "Reporting Requirement: 32 IAC 335.1080 - Any administration of radioactive materials that results in a 'reportable event' (misadministration), licensee shall notify the agency by telephone NLT next day after licensee ascertains and confirms that a reportable event has occurred. Mode Reported: Telephone" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-09-01
42810 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2006-08-28 13:00 | 2006-08-28 18:39 | 2006-09-29 | HIGH PRESSURE COOLANT INJECTION OVERSPEED TRIP MECHANISM FAILED TO RESET "The High Pressure Coolant Injection system (HPCI) over-speed trip tappet did not reset as expected during the trip tappet test after securing from a successful HPCI operability run, thereby preventing a re-start of the HPCI system. The Automatic Depressurization System (ADS), Core Spray sub-systems, Low Pressure Coolant Injection (LPCI) and the Reactor Core Isolation Cooling (RCIC) systems are operable." The unit is in a 14 day LCO for this event. The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM MIKE PLETCHER TO JOE O'HARA AT 1130 ON 9/28/06 * * * "NRC Notification 42810 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10CFR50.72 were met pending the evaluation of condition observed with the High Pressure Coolant Injection (HPCI) Overspeed Trip reset feature that was discovered while performing scheduled testing for the HPCI System. "During surveillance testing on 08/28/06, the HPCI System was started and satisfied the Technical Specification requirements designed to demonstrate HPCI System Operability. Subsequently, while testing the specific components of the system, the HPCI Overspeed Trip functioned as expected, but would not reset when manually depressed (locally). The Shift Manager declared the system inoperable and remained in the Limited Condition of Operation (LCO) that was entered prior to commencing the testing activities. "Subsequent investigation determined that the reset function of the HPCI turbine overspeed trip device is not required to support HPCI from performing the system safety functions as described in the station design and licensing basis. "ENS Event Number 42810, made on 08/28/06, is being retracted." The licensee notified the NRC Resident Inspector. The R1DO(Hott) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-08-28
42809 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-08-14 | 2006-08-28 12:59 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * TECHNETIUM-99 CONTAMINATION DISCOVERED ONSITE "In a letter dated August 14, 2006, BWX Technologies, Inc. (BWXT) made a notification to the NRC Region Il, as required by license SNM-42, Section 9.4.2, that low levels of Tc-99 contamination had been discovered in two shallow groundwater-monitoring wells (FEP-1 and FEP-2) adjacent to the Final Effluent Ponds. The levels detected exceeded the license action level for beta activity." The Tc-99 levels identified were 1,408 and 6,206 picocuries/liter for the wells FEP-1 and FEP-2 respectively. These exceeded the NRC licensed action level for beta activity. Additionally, the gross beta levels are above the gross beta screening level for groundwater and surface water. BWXT indicated that as a result of their initial investigation the contamination is contained on the BWXT site and there is no potential for contamination to migrate to offsite groundwater or to affect drinking water at the site. "This concurrent report is being made as the result of an August 25, 2006 notification letter that is being submitted to the Virginia Department of Environmental Quality. "BWXT has initiated an investigation and will provide the results to the Senior NRC Resident Inspector when complete. The Senior NRC Resident Inspector has been briefed of the event and the current status of the investigation." * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
42808 | -1 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2006-08-27 23:45 | 2006-08-28 00:47 | 2006-10-26 | SAFEGUARDS REPORT The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures were not employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. *** UPDATE FROM WARD TO KNOKE AT 1450 ON 10/26/06 *** This event is not reportable and FPL downgraded this event to a loggable event in the security log. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes), ILTAB (Danis), 73.71 Group (Email) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-08-28
42807 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-08-27 17:05 | 2006-08-27 21:35 | 2006-08-27 | REACTOR TRIP DUE TO REACTOR HIGH WATER LEVEL "At 1705 CDT on August 27, 2006, a high water level trip occurred resulting in a reactor scram. All control rods fully inserted on the scram signal. Reactor water level is being controlled in the normal operating band and reactor pressure is being controlled in a normal band. "The apparent cause of the high level trip was a High Pressure Core Spray (HPCS) system initiation. There is no indication that the HPCS initiation was caused by an actual parameter reaching a trip setpoint. Division four nuclear system protection system (NSPS) is the current focus of troubleshooting activities. "The Reactor Core Isolation Cooling (RCIC) system isolated after the scram. Troubleshooting is in progress to determine the cause. Both offsite power sources are operable and emergency diesel generators are operable and available if required. All safety related systems are available if required." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-08-27
42806 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-08-27 06:31 | 2006-08-27 09:20 | 2006-08-27 | AUTOMATIC REACTOR TRIP DUE TO REACTOR COOLANT PUMP TRIP "On Sunday, August 27, 2006 at 0631 EDST, Unit Two was at 99.7% RTP when RCP #4 tripped generating a Low Flow Reactor Trip. All systems functioned as required. AFWAS [Aux Feedwater Actuation Signal] was actuated as expected due to lo-lo Steam Generators levels. RCS Letdown isolated on a momentary low level signal on one channel of Pressurizer level, and has since been restored. The reactor is currently stable in Mode 3 while the cause of the trip of the RCP is investigated." Decay heat is being rejected to the condenser via the steam dumps. ESF systems remain operable and the electrical grid is stable. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-08-27
42805 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-08-26 09:45 | 2006-08-26 13:38 | 2006-08-26 | ELECTRICIAN FLASH BURNED IN SWITCHGEAR ROOM "Offsite Notifications have been made to Blair Rescue Squad due to an OPPD electrician suffering second and third degree burns to arms, face and torso while working on switchgear. The employee has been transported via life flight helicopter to Creighton University Hospital. The flash actuated the Switchgear Room Halon system. Operations verified that there was no fire in the Switchgear Rooms. Recovery efforts are under way. "A media release is expected." A continuous fire watch has been established in the Switchgear Room as a compensatory measure. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-26
42804 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2006-08-25 15:30 | 2006-08-25 17:57 | 2006-08-25 | TRITIUM FOUND IN AN ONSITE SETTLING POND "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) due to notification of other government agencies at 15:30 on 8-25-06. "Florida Power & Light Company (PPL) has identified a small amount of tritium in a settling pond at its St. Lucie Nuclear Plant Site. The level of tritium detected in the settling pond, 3.0 E-6 microCuries per milliliter (uCi/ml), is well below the Environmental Protection Agency's (EPA) drinking water standards of 2.0 E-5 uCi/ml and is less than two per cent of the Nuclear Regulatory Commission's (NRC) safe standards for tritium that apply to water in an unrestricted area. "The source of the tritium is under investigation. The most likely source was from a leaking drain valve off a recirculating line associated with the Refueling Water Storage Tank. The leak has been stopped. "This discovery presents no health or safety risk to employees or the public. The St. Lucie Plant does not have drinking water wells on site and the plant does not impact drinking water off site. The settling pond is a part of the normal drainage process at St. Lucie. Any water that is released from the settling pond is sampled for radioactivity and the results of any findings are included in a Radioactive Effluent Release Report that is filed annually with the NRC. Monitoring of the settling pond is conducted on a monthly basis. The previous measurements of the pond water on July 20, 2006 indicated that there was no tritium present. "Notification to the State of Florida and St. Lucie and Martin county agencies has been reported in accordance with the Nuclear Energy Institute's voluntary reporting initiative." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-25
42803 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2006-08-07 | 2006-08-25 10:52 | 2006-08-25 | AGREEMENT STATE REPORT - LOST OR MISSING RADIOACTIVE MATERIAL The State provided the following information via facsimile: "On 8/7/06, licensee reports being unable to locate two NRD Model P-2021 In-Line Ionizers (S/N A2EJ536 and S/N A2EJ538) each containing up to 10 millicuries of Polonium-210 (138-day half-life). These stainless steel cylindrical items measure 0.5 inches in diameter and just under 3 inches in length. The items were purchased from NRD LLC of Grand Island, NY, in April 2005 (see Sealed Source Registry No. NY-502-D-107-G). The last known location of the items was in a stock storage area at the licensee's former facility in Woburn, MA. The licensee relocated operations from Woburn to Wilmington, MA, in September 2005. "The licensee assumes the items were lost, and possibly disposed, during the Woburn facility cleanup and relocation effort. The licensee does not believe the items were stolen. "In order to prevent recurrence, the licensee implemented a specific device use log and assigned an employee to be responsible for device inventory. "The licensee's search and investigation is ongoing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-30
42802 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-08-25 10:30 | 2006-08-25 10:36 | 2006-09-26 | EMERGENCY RESPONSE DATA SYSTEM AND SAFETY PARAMETER DISPLAY SYSTEM WILL BE UNAVAILABLE "The BVPS Unit 2 Plant Computer System (PCS) will be taken out of service for approximately 5 weeks (8/25/06 to 9/26/06) to implement a planned modification. The current PCS is being replaced and a computer outage is required to allow for the installation of a new PCS. During this time period the Emergency Response Data System (ERDS) and Safety Parameter Display System (SPDS) will not be available at BVPS Unit 2. ERDS and SPDS parameters will be monitored by control board indications and a temporary computer system (with limited analog inputs). Compensatory actions have been developed, which include a revised emergency implementing procedure specifically addressing temporarily unavailable indications and having an extra Operations Communicator respond to the Control Room during any potential Unit 2 emergency to facilitate data transfer while ERDS/SPDS is out of service. Work on replacing the PCS and returning ERDS/SPDS will be ongoing continuously until complete. "This is an 8-hour reportable event per 10 CFR50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of BVPS Unit 1 and Unit 2 plant systems will not be affected due to this planned action. BVPS Unit 1 ERDS and SPDS will not be affected by these modifications. "The NRC resident inspector has been notified." * * * UPDATE ON 09/26/06 AT 1706 EDT FROM KEN TIEFENTHAL TO GERRY WAIG * * * "Work on replacing the PCS and returning ERD/SPDS remains continuously ongoing. However, minor hindrances have caused the scheduled completion of this function to now be October 1, 2006. Previously described compensatory actions remain in effect." The licensee has notified the NRC resident inspector. Notified R1DO (Chris Hott). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-08-25
42801 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-08-25 07:54 | 2006-08-25 09:39 | 2006-08-25 | ATTEMPTED INTRODUCTION OF CONTRABAND Attempted introduction of contraband into the Protected Area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-08-25
42800 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2006-08-24 11:35 | 2006-08-24 15:08 | 2006-08-24 | MAIN FEEDWATER PUMP TRIP DURING STARTUP "On August 24, 2006, at approximately 1135 hours, during startup from a reactor trip on August 23, 2006, a trip of Main Boiler Feedwater Pump (MBFP) 21 sent an actuation signal to automatically start both motor driven Auxiliary Feedwater Pumps (AFPs) as well as isolate steam generator blowdown, and close MBFP discharge valve BFD-2-21. At the time, the plant was at about 1% power and both motor driven AFPs were in operation. All plant responses were as expected. The cause of the MBFP trip is under evaluation. "Offsite power is normal and emergency diesel generators are operable." The plant is currently at 8% power. The licensee notified the NRC Resident Inspector. | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-08-24
42799 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2006-02-24 | 2006-08-23 19:35 | 2006-08-23 | OREGON AGREEMENT STATE REPORT - VIAL CONTAINING IODINE-125 THROWN IN TRASH DUMPSTER The State provided the following information via facsimile: Event Description: "A researcher reported that a vial containing I-125 labeled hormones is missing. They had received a shipment from another university that was supposed to have had 3 vials. The person who checked in the package did not realize there were supposed to be three vials. The material was packaged with dry-ice. Only two vials were removed from the package and the package was placed in the trash. When it was discovered that they were supposed to be three vials, the trash had already been removed and the dumpster taken away. The estimated amount is 237 microCuries of I-125. Corrective Actions: "Licensee will double check inventory of each box during unloading. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2006-08-28
42798 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2005-10-03 | 2006-08-23 19:35 | 2006-08-23 | OREGON AGREEMENT STATE REPORT - GAMMA KNIFE TREATMENT TO THE INCORRECT AREA OF THE PATIENT The State provided the following information via facsimile: "Doctor treated wrong Trigeminal nerve. Patient received 32 Gray before error was noted. Doctor informed patient of error then proceeded to treat correct nerve. "In order to prevent a reoccurrence of this mistake, there will be three different double checks undertaken on the day of treatment. Prior to being sedated, the patient will be asked which side his or her pain is on. When the patient, is framed the nurse shall ask the neurosurgeon which side is to be treated. This will be verified with the patient. Lastly, just prior to treatment, both the neurosurgeon and the radiation oncologist will be once again asked which side is to be treated on the patient. This triple check system should prevent this mistake from happening again." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2006-08-28
42797 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2006-08-23 10:35 | 2006-08-23 13:19 | 2006-08-23 | MANUAL SCRAM DUE TO MISMATCH OF PRIMARY POWER AND SECONDARY LOAD INDICATIONS "On August 23, 2006, at 1035 hours, the Reactor Protection System was manually actuated while at reduced load of approximately 68 percent reactor power upon indication of an apparent disparity in net electric load. It was determined that the cyclic operation of the condenser steam dumps varied steam to the turbine resulting in the indicated drop in electrical output power from about 500 Mwe to 150 Mwe. The manual trip is reportable under 10 CFR 50.72(b)(2)(iv). The event started when heater drain tank pumps 21 and 22 tripped, apparently due to a failure of the automatic heater drain level control valves that could not be manually corrected from the single controller. Reactor operators reduced load in accordance with station procedures to respond to the trip of the heater drain tank pumps and stabilized reactor power at 77%. As a result of the required load reduction delta flux was outside of the operational limit envelope specified at 77% reactor power. This required a further load reduction to less than 50 percent as per Technical Specification 3.2.3. At approximately 68% percent power the reactor was manually tripped due to the mismatch of primary power and secondary load indications. The Auxiliary Feedwater System actuated following the manual trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). A high-high water level signal was received on the 22 Steam Generator. This was due to a feedwater regulating valve that did not fully close. The feedwater isolation valves closed. All other safety systems actuated as required and safety equipment operated as expected. The Emergency Diesel Generators did not start as offsite power remained available and stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal temperature and pressure with residual heat removal using auxiliary feedwater and normal heat removal through the condenser via steam dumps. There was no radiation released. A post trip investigation will be performed prior to restart." The licensee notified the NRC Resident Inspector. *** UPDATE FROM GEORGE DAHL TO JOHN KNOKE AT 1830 EDT ON 08/23/06 *** "This is an update of non-emergency Event Notification 42797 that was previously made on August 23, 2006. Clarification is provided to include reporting of the Event Classification for actuation of a second system (automatic feedwater isolation) as an 8-Hr. Non-Emergency per 10 CFR 50.72(b)(3)(iv)(A). This update revises the wording as follows: "The feedwater isolation valve was manually closed. After receipt of the high-high level trip signal, 21, 23, and 24 feedwater isolation valves automatically closed. This is also reportable under 10 CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector. Notified R1DO (Conte). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-08-23
42796 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2006-08-18 12:30 | 2006-08-23 13:20 | 2006-08-23 | ARIZONA AGREEMENT STATE REPORT - TRASH CONTAINING IODINE -131 TAKEN TO LANDFILL The State provided the following information via e-mail: "At approximately 12:30 PM 8/18/2006 the Agency was informed by the Licensee that a patient receiving Iodine 131 therapy was discharged 8/16/2006. The Radiation Safety Staff proceeded to clean the patient's room. The containment items were placed into a plastic bag. The bag was transported to the waste storage area, where the Staff was unable to unlock the door. Security was called and they were unable to open the door. The Staff then moved the materials to the nuclear medicine preparation room which could be locked. The trash read 1.3mr/hr at the surface. The trash was not marked as being radioactive. "Upon arrival the next day, the Staff discovered that the cleaning crew had removed the trash. The cleaning crew were trained that if the trash is not marked 'Radioactive' they were to remove it. They attempted to catch the trash before removal to the landfill, but they were unsuccessful. The Staff also went to the landfill and attempted to recover the trash but were unsuccessful. "The material represents minimal public health risk if disposed into the landfill. "The Agency continues to investigate the event. "Press coverage is not anticipated." First Notice: 06-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2006-08-28
42795 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2006-08-23 09:40 | 2006-08-23 11:23 | 2006-08-23 | POTENTIAL NEWS WORTHY EVENT "On 08/23/06 at 0940, Turkey Point Nuclear Station was informed of a possible news release concerning the activities of a non-supervisor initial operator student. The initiating activities in question occurred prior to the employment of the individual at Florida Power and Light and have resulted in the recent off site arrest of the student on felony charges. Plant access was suspended immediately upon supervisor notification pending further investigation." Florida Power and Light and Turkey Point were not mentioned in the initial news release. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-23
42794 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2006-08-21 18:00 | 2006-08-23 11:01 | 2006-08-23 | AGREEMENT STATE REPORT - RADIOGRAPHIC CAMERA DISCONNECTED SOURCE The State provided the following information via facsimile: "This event involved a Source Production & Equipment Company radiographic exposure device (model SPEC 150, serial number 948; with sealed source model SPEC G-60, serial number NH0807). The activity contained in the radiographic exposure device at the time of the incident was 4.912 terabecquerels (133 Ci) of Iridium-192. The radiographer noticed that the crank turned out more turns than normal when he exposed the source. He then realized that the guide tube was not connected tightly to the device. The radiographer cranked the source in with the guide tube not connected. The pigtail hit against the radiographic exposure device and disconnected. The radiographer followed the licensee's emergency procedures and controlled the area until the radiation safety officer arrived. The radiation safety officer began and completed the source retrieval procedures without further incident. The licensee contacted the manufacturer regarding the disconnect. The manufacturer informed the licensee that when the source was outside the guide tube, and oriented 90 degrees to the travel direction of the cable, the source can disconnect. "Event Location: Chevron Refinery VGO Unit, 2351 N 1100 W, Salt Lake City, Utah 84116" The Utah Division of Radiation Control was notified by the licensee in a telephone call on August 22, 2006. Utah Event Report ID No.: UT-06-0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2006-08-28
42793 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2006-08-14 | 2006-08-22 12:09 | 2006-08-22 | COMMONWEALTH OF MASSACHUSETTS AGREEMENT STATE REPORT - LOST/MISSING RADIOACTIVE MATERIAL The State provided the following information via facsimile: "As a result of re-labeling effort by Thermo Niton Analyzers LLC (Thermo Niton) to add Am-241 check source information to the device label, the Radiation Safety Officer of Thermo Niton discovered that the device is lost or missing and provided the following information: "With regard to Unit 5213 (Model XLi 848, serial number 5213), we [Thermo Niton] have visited Morris Iron and Steel in person to re-label Unit 5213 and they did not have it in their inventory of devices. An exhaustive review of our [Thermo Niton] records indicate that the last time we [Thermo Niton] were in possession of this device was when we [Thermo Niton] sent it to Morris Iron and Steel at 7345 Milnor Street, Philadelphia, PA 19136 under General License on 9/17/04. The device had 40 mCi (millicuries) Cd-109 source (reference date 4/23/02), a 20 mCi Fe-55 source (reference date 4/20/02), and a 1 microCurie Am-241 Check Shutter source. Morris claims to have sent it back to us but has not been able to produce a tracking number or any other evidence of their shipment. We [Thermo Niton] have contacted Federal Express who is our primary carrier and they have reportedly not maintained records of shipments going back that far. We [Thermo Niton] have also contacted Valley Safety Services who performs leak tests for us and many of our customers and they have not leak tested this device for anyone since prior to 9/14/04. We [Thermo Niton] have put a flag in our database system that will automatically flag us if the device is received here at any time in the future. "As of 8/22/06, the approximate calculated activities of the sources are 3.8 milliCuries for the Cd-109 source; 6.6 millicuries for the Fe-55 source and 1 microCurie for the Am-241 check source." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-25
42792 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2006-08-18 17:30 | 2006-08-21 20:02 | 2006-08-21 | NEW MEXICO AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE. This State provided the following information via e-mail: "This is to notify you that the Density/Moisture Gauge, Seaman C-300 with serial number 21049, was stolen from the back of a pickup, parked at 10216 Andalusian, SW, Albuquerque, NM 87121 sometime between August 18, 5:30 PM and August 20, 3:30PM. The assigned employee, [deleted], the field monitor for A. S. Horner, worked late last Friday, August 18th and instead of taking the gauge to either a project office or the main office and storing it in a locked closet, decided to park the truck backed against the garage door at his residence noted above. The gauge handle was locked, stored in the approved container, that was also locked and the container itself was secured to the bed of the pickup with a chain and a lock. Mr. [deleted] was out of town for the weekend and upon his return at about 3:30 PM on Sunday, he noticed the entire box was gone. Two cut locks were found on the bed of the pickup. There must have been more than one person committing this crime to pickup the heavy box from the rear of the vehicle. "Mr. [deleted] immediately notified the police and the fire department, who cordoned off the area first, then interviewed. Mr. [deleted] and took pictures of the vehicle and the area. Mr. [deleted] searched the nearby dumps and did not find any trace of the gauge. The police report will be available shortly. The fire department, as we understand, has notified the hospitals in the area. "Mr. [deleted] acted in violation of the company policy and we are dealing with this issue. The company has had two moisture/density gauges for more than five years and this is the first incident of this nature. The employees have been instructed to store the gauges in locked closets in the locked buildings inside a fenced area with a locked gate. "I called the 24 hour emergency number and Mr. [deleted] yesterday at about 5 PM and left messages describing the incident. The exact time of the theft is unknown, however, according to the neighbor of Mr. [deleted], it must have happened on Saturday, August 19, between 2 AM and 7 AM, when he noticed that the tool box was open but nothing was missing from the tool box. The neighbor did not notice the box in the back of the vehicle was missing. "Please let me know if there is anything else I need to do other than keep in close contact with the police and fire departments on the status of the recovery of this gauge." Seaman C-300 Moisture Density Gauge contains approximately 10 millicuries of Cesium-137 and 40 millicuries of Americium-241. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2006-08-24
42791 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-08-13 | 2006-08-21 16:13 | 2006-08-21 | MISSISSIPPI AGREEMENT STATE REPORT - SCHLUMBERGER ADANDONS WELL LOGGING TOOL The State provided the following information via e-mail: "Received notification on 8-13-06 from Schlumberger that they had logging tool stuck in the G. B. Boots Smith #1 exploration well located Jones County, Mississippi. Logging tool containing 1.7 curie Cesium-137 source (Serial # GSR-J-5031) and a 16 curie American-241: Be source (Serial # NSR-F-2316) was stuck below 17660 feet. Operating company was fishing for logging tool string. Schlumberger discussed initial procedure of abandoning sources with DRH. Fishing operations for logging tool containing sources was unsuccessful and decision was made to abandon tool string in hole. Licensee stated that tool would be cemented in hole with cement plug set at 17100 feet. Operator set approximately 300 feet of cement used on top of 10 bars of 0.75 inch/ 10 foot joints of solid steel rods with the top at 16782 feet. Well was to be completed at a shallower depth. "Isotope(s) : Cesium-137 & American-241:Be "Activity: 1.7 Ci Abandoned, 16 Ci Abandoned. "Date of Incident: 8-8-06 "Date Reported to DRH: 8-13-06 "Were any other licensees involved, if so identify below: None others involved. "Describe clean-up actions taken by DRH: None taken "List radiation measurements taken by DRH: No survey reading taken by DRH. Schlumberger surveyed drilling mud during fishing operations and did not observe any reading out of the normal readings. "List any other actions required of DRH: 30 written report required from licensee. Licensee must also place plaque on well bore signifying that abandoned source is in well bore. DRH will inspect plaque on well head after it is installed. "List any actions taken to notify NRC, other Agreement States: Notify NRC by e-mail 8-21-06. Notified NMED on 8-21-06 by e-mail. "Case Closed: No "Record of incident in RAM files: Yes "Enforcement action taken: None taken. Abandonment of sources not licensee's fault. No corrective actions required." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2006-08-24
42790 | 0 | PENNONI ASSOCIATES |  |  |  |  | 2006-08-19 23:00 | 2006-08-21 09:47 | 2006-08-23 | LOST MOISTURE DENSITY GAUGE On Saturday August 19, 2006 at approximately 11:00 p.m., an employee of Pennoni Associates loaned his private, passenger vehicle to his sister to perform a short errand. Inside the trunk, the vehicle contained a Humboldt Model 5001 moisture density gauge, serial number 4746, with 10 milli Curies of Cs-137 and 40 milli Curies of Am-241/Be. The employee has not seen his vehicle since and contacted the Bethlehem City Police Department. The licensee is continuing the investigation as to the whereabouts of the gauge and the vehicle. The licensee contacted the NRC Region I office. *** UPDATE FROM CHARLES SNYDER TO KNOKE AT 13:07 EDT ON 8/23/06 *** The RSO (Snyder) indicated that the lost density gauge (sn 4746) was found. The employee, who lent his car to his sister-in-law, retrieved the gauge and returned it to Pennoni Associates. There was no damage to the gauge and the sources were not tampered with. The RSO stated that the sister-in-law emptied the contents out of the car, including the gauge, and then took off with the car without permission. She notified the employee where she dumped the contents, and he came and retrieved it. LLEA is following up on the stolen vehicle. Contacted the R1DO (Conte) and NMSS ( Burgess) and emailed ILTAB (Danis) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-08-21
42789 | 0 | SUPERIOR WELL SERVICES, INC. |  |  |  |  | 2006-08-18 | 2006-08-20 18:30 | 2007-10-30 | GENERAL LICENSE DENSITY GAUGE DISCOVERED MISSING On 8/18/06 the Superior Well Services crew at a temporary worksite approximately 2 hours drive from Vernal, UT discovered that their Thermo MeasureTech Density Gauge was missing. The device, a Model #5192 - S/N B7000 containing a 200 mCi Cs-137 source, is normally stored in the back of their vehicle and was last used the day before on 8/17/06. The licensee is continuing their investigation to determine whether the device was stolen or fell off the back of the vehicle. The device itself weighs 150 pounds and is in a metal housing 36 inches in length (Sealed Source Registry No. TX0634D105B). The licensee contacted the Utah Highway Patrol, the Vernal County Sheriff's Office and will contact the Utah Radiation Control Office. Also, a press release offering a $10,000.00 reward for return of the device will be issued. * * * UPDATE FROM CRAIG JONES TO J. KNOKE AT 12:06 ON 10/30/07 * * * Craig Jones from the state of Utah called to say that on 10/19/07 a member of the public located the Thermo MeasureTech Density Gauge South of Duchesne, UT along State Road 191. The licensee's RSO was notified and responded to the site. A leak test and survey was performed on the equipment and area, and the results were negative. The licensee indicated the person who found the gauge will be given the reward. Licensee now has the Thermo MeasureTech Density Gauge in their possession. The state of Utah will be conducting a follow-up meeting with the licensee in the near future. Notified R1DO (Dentel), R4DO (Powers), FSME (M. Burgess), ILTAB (email) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-08-20
42788 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2006-08-19 18:49 | 2006-08-19 23:10 | 2006-09-22 | RADIATION MONITOR ELECTRICAL SPIKE CAUSES SECONDARY CONTAINMENT ISOLATION "The 'B' fuel pool radiation monitor spiked high causing an actuation of the secondary containment relays. 'A' SBGTS [Standby Gas Treatment System] train started, reactor building, turbine building, and rad waste building ventilation isolated. The Drywell Continuous Air Monitor (DW CAM) and O2 analyzer containment valves isolated. The control room ventilation system transferred to the high radiation mode. "At the time of the occurrence the 'A' Fuel Pool radiation monitor was reading normal (0.5 mr/hr). The 'B' Fuel Pool radiation monitor was reading 80 mr/hr. The 'B Fuel Pool radiation monitor, soon after lowered to 30-40 mr/hr and then back to normal (10 mr/hr). The trip setpoint is 50 mr/hr. The trip was reset. The secondary containment isolation and all ventilation trips were restored to normal. The DW CAM and control room ventilation were restored to normal. A local survey was performed on the refuel floor, readings obtained were < 5 mr/hr at the detector and < 2 mr/hr in surrounding areas. The 'B' fuel pool radiation monitor high level trips were placed in the trip/bypass position. The 'B' fuel pool radiation monitor was placed in downscale trip condition to comply with Technical Specification Table 3.2.4. A team is being established to investigate the cause of the trip." The licensee notified the NRC Resident Inspector. * * * Update on 09/22/06 at 1456 ET from Dave Burnett to MacKinnon * * * "This report is being reclassified from a 50.72 (b)(3)(iv)(A) [valid system actuation] to 50.73(a)(2)(iv)(A) [invalid system actuation]. "Based on further investigation, Monticello has determined that the actuation signal was an invalid spurious signal since other radiation monitors in the area did not indicate any change in value. The cause of the spurious signal was determined to be inducted noise through an unshielded cable which resulted in an increased output current to the instrument. Because the actuation signal was not valid, Monticello is reclassifying the initial event report as an unplanned system actuation under 50.73(a)(2)(iv)(A). This report will be made in lieu of reporting the event as an LER. "In accordance with 50.73(a)(2)(iv)(A): "This report is not considered an LER and the report is being made under 50.73(a)(2)(iv)(A). The original event report (ENS #42788) detailed the system affected, whether the actuation was complete or partial, and whether each affected system started and functioned successfully. "The licensee has notified the NRC Resident Inspector.' NRC R3DO (Julio Lara) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-08-19
42787 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-08-19 11:05 | 2006-08-19 15:15 | 2006-08-19 | MANUAL REACTOR SCRAM Of UNIT 3 DUE TO THE LOSS OF BOTH REACTOR RECIRCULATION PUMPS "At 1105 CST both Reactor Recirculation pumps tripped on Unit 3. In accordance with procedure 3-AOI-68-1, a manual scram was initiated. Reactor water level lowered to Reactor Pressure Vessel Level 3, resulting in the automatic actuation of the Primary Containment Isolation System as expected: Group 2 (RHR Shutdown Cooling), Group 3 (Reactor Water (Clean Up), Group 6 (Ventilation), and Group 8 (Traversing Incore Probe) along with the automatic start of Control Room Emergency Ventilation and all 3 trains of the Standby Gas Treatment System. Reactor water level was recovered to normal levels with the reactor feedwater system. "During this time Unit 2 was at 100% power and was unaffected by the event. "This event is reportable as a 4-hour and 8-hour notification along with a 60-day written report in accordance with 10 CFR 50.72(b)(2)(iv)(B), 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(A)." All control rods fully inserted on the scram. Decay heat is being removed with normal feedwater and the turbine bypass valves. No relief valves lifted during this event. Electrical power to the plant is aligned for the normal shutdown lineup. The cause of this event is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-08-19
42786 | 0 | DEFENSE DISTRIBUTION CENTER |  |  |  |  | 2006-08-18 14:00 | 2006-08-18 15:25 | 2006-10-02 | TRITIUM SOURCES MISSING DURING ANNUAL INVENTORY BUT SUBSEQUENTLY FOUND An inventory of the tritium sources at the Defense Logistics Agency in Aniston, AL was performed. "Initial results of Annual Inventory indicates a loss of the following items: 4 ea NSN 1240001508886 Telescopic panoramic at 3.8 Curies each 5 ea NSN 1240001508890 Mount Telescope at 0.15 Curies each 2 ea NSN 1240003321780 Collimator at 10 Curies each Causative research is currently being conducted and results will be reported in follow up letter to NRC. Total loss would equal 35.95 Curies of H3." The last annual inventory was completed 10/11/2005. * * * UPDATE RECEIVED FROM DAVID COLLINS TO JOE O'HARA AT 0955 ON 10/02/06 * * * The Defense Distribution Center Depot has accounted for all items previously reported as being missing. The items were located in a proper radiological storage area. However, they were not located in the same area as the licensee had documented in their computer system. After performing a full inspection of the radiological storage area, the items were accounted for and properly documented in a report issued 9/28/06. Notified R1DO(Krohn) and NMSS(Burgess) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-08-18
42785 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-17 | 2006-08-18 15:40 | 2006-08-25 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "A Troxler 3430, serial # 35800 was stolen out of the back of a pickup truck parked at the RSO's residence on the evening of 8/17/06. The lock securing the gauge was cut. The gauge was found three blocks away from the RSO's residence on the morning of 8/18/06 in a ditch. A leak test of the gauge is being performed this same date. An inspection of Raney Geotechnical will be performed on 8/22/06." A Troxler 3430 typically contains: 8 mCuries Cs-137 40 mCuries Am-241:Be * * * UPDATE FROM K. FUREY TO P. SNYDER AT 1532 ON 8/25/06 * * * The State provided information stating that the original incident happened between 9pm and 6am the evening of August 17, 2006 and confirmed that the gauge contained 8 mCi of Cesium 137 and 40 mCi of Americium 241. Notified R4DO (T. Pruet) and NMSS EO (C. Reamer). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-08-23
42784 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-14 | 2006-08-18 15:17 | 2006-08-18 | AGREEMENT STATE - STUCK SOURCE The State provided the following information via email: "Problems were encountered during a Varian HDR source exchange during the evening of 8/14/06. While attempting to replace the source on a Varian Medical System's VariSource HDR unit, the new active source (Ir-192, 9 curies) got stuck in a transfer tube. Following placement of shielding, the source was freed and placed in the transport pig by noon on 8/15/06. A new source was delivered, and was successfully installed during the evening of 8/16/06." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-08-23
42783 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-08-17 19:00 | 2006-08-18 01:00 | 2006-08-18 | EMERGENCY DIESEL GENERATORS INOPERABLE DUE TO UNDERSIZED BREAKER CONTROL TRANSFORMERS "At 1900 hrs on 8/17/06, all four Emergency Diesel Generators (EDGs) were declared INOPERABLE. The inoperability is a result of undersized control transformers for each of the Emergency Diesel Generator Service Water (DGSW) Pumps. The concern is that the DGSW pump contactors will not receive adequate voltage at the starters to ensure the starters pickup under degraded voltage conditions. A 2 hour Limiting Condition for Operability (LCO) was entered per LCO 3.8.1 to restore both EDGs in one division to OPERABLE status. At 2100 hours on 8/17/06 the two hour time requirement expired and a 12 hour LCO to place the plant in Mode 3 (Hot Shutdown) was entered. "At 0042 hrs on 8/18/06, compensatory measures have been put in place to restore operability to both division 2 EDGs. The compensatory measures include placing the local control switch for both division 2 DGSW Pumps in run. Placing the local control switches in run ensures sufficient voltage will be available at the starters to ensure the starters pickup following a loss of offsite power, load shed, and restoration of power to the applicable busses. With operability restored to division 2 EDGs, the new expiration time for the LCO has been revised to 72 hours based on discovery of one or both EDGs in one division inoperable concurrent with CTG 11-1 [station blackout Combustion Turbine Generator 11-1] not available. After 72 hours, if operability is not restored to either CTG 11-1 or both division 1 EDGs, the plant will be required to enter Mode 3 within the following 12 hours. "This report is being made pursuant to 10CFR50.72.(b)(3)(v) as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove Residual Heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. The NRC resident inspector has been notified." The licensee stated that the current 72 hour LCO will expire at 1900 EDT 08/20/06. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2006-08-18
42782 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-08-17 10:44 | 2006-08-17 17:33 | 2006-08-17 | MAIN TURBINE BYPASS VALVES INOPERABLE "At 1044 on August 17, 2006, operators received main control room annunciator alarm 'CONDENSER VACUUM LOW' and status lights 'COND VACUUM TRIP' and 'COND VACUUM LOW.' All other indications for main condenser vacuum indicated normal ~ 26.6 [inches Hg]. In response to the alarm, initial troubleshooting determined that the main turbine bypass system was inoperable. This was due to concluding that with the low condenser signal present, the bypass valves were prohibited from opening upon demand. Therefore at 1110, Technical Specifications 3.7.6, 'Main Turbine Bypass System,' Condition 'A' was entered. "This is reportable as an 8 hour report in accordance with 10 CFR 50.72 (b)(3)(v)(D) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident.' "The devices that cause the annunciator are 1PY-ES063 and 1PY-ES066. A visual inspection of the device cards revealed that on the 1PY-ES066 card the 'DC CURRENT ALARM' upper and lower lights were lit. These same lights were not lit on the 1PY-ES063. "At 1212 on August 17,2006, a lead was lifted to remove the low vacuum inhibit input from 1PY-ES066 for the bypass valves. The main control room alarm cleared and the low vacuum light went out as expected. At 1215 the low vacuum inhibit was reset restoring the bypass valves to operable." The licensee will notify the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-08-17
42781 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-08-17 09:00 | 2006-08-17 11:22 | 2006-08-17 | PHONE LINES OUT OF SERVICE FOR MAINTENANCE "Phone line maintenance is occurring today 8/17/06. Maintenance starting at 0900 and is planned until 1600 hours. Line maintenance may impact ENS, HPN, and ERDS capabilities. An 8 hour notification per 10CFR50.72(b)(3)(xiii) is being made due to expected failures during line interruptions. Affected communications will be verified subsequent to completion of line maintenance." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1725 ON 8/17/06 * * * The ENS and HPN lines were tested and declared operable at 16:55 CDT. The ERDS line was verified operable at 17:25 by sending plant data to the NRC. The licensee notified the NRC Resident Inspector. R4DO (Blair Spitzberg) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-08-17
42780 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-10-13 | 2006-08-16 09:58 | 2006-08-16 | MASSACHUSETTES AGREEMENT STATE REPORT OF LEAKING FE-55 The State provided the following information regarding a previously unreported event via facsimile: "On October 15, 2004, Niton Corporation provided a report of a leaking sealed source that was discovered by Niton on October 13, 2004, during routine maintenance of a customer's model Xli 868p XRF device, S/N 5043. The sealed source is AEA Technology model IEC.A1, S/N 8765LG containing 10.3 mCi of Fe-55. The estimated leakage was 700,000 dpm or 0.3 microcuries. "The source and a few contaminated device components were removed from the device and placed into a waste storage container. The area where the source removal was performed was surveyed and no contamination was found. The source manufacturer, AEA Technology, was notified of the leaking source. The source manufacturer, AEA Technology, has re-designed the source." The cause and corrective action were determined and this event is considered closed by the Agency. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-21
42779 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2006-08-15 18:14 | 2006-08-15 18:47 | 2006-08-15 | UNUSUAL EVENT DUE TO FIRE ON ROOF OF EDG BUILDING "During a 24 hour endurance run of the E3 Emergency Diesel Generator (EDG), a small fire occurred on the roof of the E3 EDG Building. Fire reported at 1759, UE declared at 1814. E3 was approximately 19 hours into the full load run. E3 was immediately shut down. As of 1835 the fire was reported out and no offsite assistance was required." The licensee is investigating the cause of the fire. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM L. KEENER TO W. GOTT AT 2044 ON 08/15/06 * * * Licensee terminated the Unusual Event at 2040. Conditions to secure were that the fire was out and overhauled and the E3 EDG fuel racks tripped. The E3 EDG is considered inoperable and not available (14 day shutdown LCO). The licensee will notify the NRC Resident Inspector. Notified R1DO (R. Lorson), NRR EO (P.T. Kuo), IRD (P. Wilson), DHS (M. Charter), FEMA (D. Barden) * * * UPDATE FROM SULLIVAN TO HUFFMAN AT 0010 ON 8/16/06 * * * The licensee will be issuing a press release about the Unusual Event. R1DO( Lorson) notified. | 98 | 100 | 0 | 98 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-08-15
42778 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-08-15 10:20 | 2006-08-15 18:21 | 2006-08-15 | IMPORTANT ENVIRONMENTAL EVENT "The following is being reported in accordance with the Diablo Canyon Power Plant (DCPP) Environmental Protection Plan (EPP) section 4.1 as an 'unusual or important environmental event' requiring NRC notification within 24-hours: "During diving operations to clean the intake bar racks, the diver discovered 50 to 100 dead Cormorants. Cormorants are diving sea birds and are common in the DCPP intake cove. They have recently started nesting in larger numbers on a large rock at the southern end of the intake cove, and feed in the intake cove. "The event did not impact plant operations. It is believed that the birds died of natural causes and collected on the bar racks due to the water currents. To help determine the cause of death, some birds are being saved for testing and analysis. "DCPP will submit a written report within 30 days in accordance with section 5.4.2 of the EPP." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2006-08-15
42777 | 0 | UNIVERSITY OF HAWAII |  |  |  |  | 2006-07-13 19:20 | 2006-08-15 16:56 | 2006-08-15 | RESEARCH SAMPLE OF C-14 WAS LOST AT SEA. The RSO (Irene Sakimoto) for the licensee notified us that while conducting an experiment on a boat at sea (22 degrees 43.48 N and 158 degrees 4.77 W) a sealed source of C-14 (1.8 milliCi) was attached to a line and lowered into the ocean to a depth of 4800 meters. The line became ensnared in the propeller and broke. The sample fell to the bottom of the ocean. The licensee will not be making efforts to retrieve this sealed source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-08-15
42776 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2006-08-15 13:45 | 2006-08-15 16:36 | 2006-08-15 | 24-HOUR REPORT OF SIGNIFICANT ENVIRONMENTAL EVENT INVOLVING UNUSUAL FISH KILL "Unusual fish kill on both unit's intake trash racks. Approximately 50 Cow Nosed Rays were found dead on the trash racks. The apparent cause was low oxygen levels in the bay water. This event is reportable per Tech Spec Appendix B, Section. 4.1 for significant environmental events." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW | [5 empty] | 0 | 2006-08-15
42775 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2006-08-08 | 2006-08-15 14:33 | 2006-08-15 | AGREEMENT STATE REPORT - SURFACE CONTAMINATION The State provided the following information via email: "Licensee received an 'empty' lead pod with exterior contamination of 1.3 E-5 microCi/cm2. Contamination identified as Cs-137. Shipment came from Thermo Electron, 1410 Gillingham Lane, Sugarland, Texas via Conway Trucking." "Licensee informed Conway Trucking of the contamination." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-18
42774 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2003-05-12 | 2006-08-15 13:24 | 2006-08-15 | AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information regarding a previously unreported event via facsimile: "The Agency [MA Radiation Control Program] received a report on 6/23/03 of a misadministration; ie., The wrong area of the scalp was treated during a treatment for a superficial scalp cancer. The wrong area of the scalp was treated because of a malfunction with the source position simulator. The misadministration was not noticed during the treatment period of May 12, 2003, thru June 5, 2003. It was discovered on June 23, 2003 while doing a similar procedure. After the source position simulator malfunction was detected, all cases that used this same device were reviewed and it was determined that only the last patient treatment was affected by this malfunction. Corrective actions were implemented to ensure this event will not happen again. "Corrective action 1. Licensee reviewed all cases that involved the same device and determined that the only patient affected by this malfunction was the last one treated before discovery. 2. All HDR treatments involving variable length catheters will have the length of the catheters measured by 2 independent means. 3. The HDR manufacturer was notified of the problem encountered with the catheter measuring device." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-18
42773 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2006-01-30 | 2006-08-15 13:24 | 2006-08-15 | AGREEMENT STATE REPORT - LOST SULFUR - 35 SHIPMENT The State provided the following information regarding a previously unreported event via facsimile: "S-35 (7 mCi) package was shipped via FedEx, from PerkinElmer in Boston, MA on 1/30/06. "FedEx tracking indicates 1) the package was picked up from PerkinElmer in Boston, MA; 2) the package left the FedEx South Boston station; 3) the package arrived at FedEx Hub in Memphis, TN; 4) the package had an In-transit scan to Montreal on 1/31/06. There were no package scans after that. "PerkinElmer Canadian Customer Service reported the customer did not receive the package. PerkinElmer asked FedEx several times to locate the package. PerkinElmer receiving department did not receive the package as a return and verified with the customer, again, that the package was not received. FedEx was unable to locate the package. "PerkinElmer declared the package as lost on February 12, 2006, and reported to the Agency [MA Radiation Control Program] by phone on March 10, 2006. A written report was received to the Agency on April 10, 2006. "Corrective action: PerkinElmer advised FedEx that all radioactive shipments require a Proof of Delivery; this issue has been escalated to FedEx Dangerous Goods Administrator; and a letter was sent to FedEx explaining the requirements of delivering radioactive packages." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-18
42772 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-12-15 | 2006-08-15 10:01 | 2006-08-15 | AGREEMENT STATE REPORT - LOST GENERAL LICENSED DEVICE The State provided the following information regarding a previously unreported event via facsimile: "By letter dated 1/28/03, Level 1, Inc. notified the Agency [MA Radiation Control Program] of the loss of a GL device. "The device was an NRD air deionizer model number P-2021-0101, serial number 109646 which was shipped to the licensee on March 3, 1999. The device was used to de-ionize air during their clean-room assembly process. The device was taken out of service in March of 2002. When units are taken out of service the licensee stated that the devices are stored in a cabinet. The licensee discovered that the device was lost when they sent back all devices (30) in the program that were beyond their usefulness. They had 31 and could not account for one device when they were going to send the devices back. The device was discovered to be lost in December 2002. They have tried unsuccessfully to locate the device. They believe that it may still be in their facility and will continue to locate it. "In order to prevent future losses, the licensee has implemented a Preventive Maintenance (PM) Program and have included all air deionizers as part of the PM program. The PM program will consist of a computer program that tracks all devices that are to be accounted for in the company for maintenance. The GL devices will be added to the list. "The devices had 10 millicuries of Po-210 loaded in March of 1999. With the 138.38 day half life of Po-210, the device contains about 6 microCuries at this time. The safety significance is low for this lost device. "Corrective action "In order to prevent future losses, the licensee has implemented a Preventive Maintenance Program and have included all air deionizers as part of the PM program. The PM program will consist of a computer program that tracks all devices that are to be accounted for in the company for maintenance. The GL devices will be added to the list. EVENT CLOSED BY STATE." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-18
42771 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2006-08-15 10:15 | 2006-08-15 13:23 | 2006-08-17 | LOSS OF ERDADS COMMUNICATION "On 08/15/2006 during performance of the quarterly ERDADS functional communications test, the ERDADS communication link from the U1 Control Room to the NRC Operations Center was determined to be unavailable. Initial notification was made to the NRC Operations Center and the communications vendor was contacted to investigate the source of the problem. Subsequent notification was made by the vendor to the Site identifying that the communications failure was occurring within the portion of the system under control of the Site. Troubleshooting by the Site is in progress. Note: the U2 ERDADS communication link tested satisfactory. This non emergency notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii) regarding loss of communications capability." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 14:50 ON 8/17/06 FROM JOHN BRADY TO ABRAMOVITZ * * * "Subsequent troubleshooting of the failed ERDADS communication link identified a faulty wiring connection in onsite communications equipment. Repairs were performed and a successful ERDADS functional communications test was completed at 1137 on 08/17/06. The U1 ERDADS comm link is back in service and communications capability has been restored." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-08-15
42770 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-06-04 | 2006-08-15 10:01 | 2006-08-15 | AGREEMENT STATE REPORT - DEFECTIVE PACKAGING OF RADIOACTIVE MATERIAL SHIPMENT The State provided the following information regarding a previously unreported event via facsimile: "On June 4, 2002, the surface and 1 meter radiation dose rates from a package containing 8 curies of phosphorus-32 (P-32) was found to be 1 R/hr at the surface and 4 milliR/hr at 1 meter. The package had a Yellow II label affixed which has a surface dose rate limit of 50 milliR/hr and a dose rate at 1 meter of 1 milliR/hr per Massachusetts regulation 120.775(A)(1). There was no removable contamination on the package hence the inner container appeared to be intact. However, the inner container appeared to be loose in the packaging rather than in the fixed geometry as evidenced in other similar packages in the same shipment. "The package dose rate at the surface is greater than 0.2 R/hr but less than 0.01 R/hr at 1 meter hence the package exceeded the requirements of a Yellow III. "In summary the defective packaging resulted in a radiation field at the surface of the package in excess of the limit for a common carrier and the Yellow II label on the package. "The licensee has suspended all shipments from this supplier until the investigation of the package failure is complete. "The root cause investigation of this event by the licensee has been postponed until September with the approval of the Massachusetts Radiation Control program pending decay of the radioactive material and adherence to the Perkin Elmer Life Sciences ALARA policy. A preliminary investigation concluded that persons handling the package during shipment would not have received a significant radiation dose because of the limited area of the package in excess of Yellow Il limits and the limited time of handling package by transportation personnel. "UPDATE "Excessive radiation field is due to seepage of radioactive material from cracked glass vial. There is a metal cap used to seal the vial. The metal cap is fastened using a hand operated crank. This tool can be mishandled resulting in over-tightening of the cap and causing the glass to crack. This vial, cap and tool are provided by Perkin Elmer and the firm is familiar with this potential failure mode. Root cause: improper training or supervision of operator of capping tool. "Licensee informed vendor that supplies the glass vial and have discontinued using this vendor. This event is closed by the state" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-18
42769 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2002-08-07 | 2006-08-15 10:01 | 2006-08-15 | AGREEMENT STATE REPORT - NUCLEAR GAUGE DAMAGED BY FIRE The State provided the following information regarding a previously unreported event via facsimile: "A fire, which started in garage/storage facility, at a golf course construction site near the summit of a former city landfill was allowed to burn for two days by the local fire department. However, during the fire and immediately after the proximity of the device storage shed was disclosed by the licensee to the local authorities, the City of Quincy Fire Department summoned the Agency [MA Radiation Control Program] to the scene. At the scene the Agency representative was able to overview the situation, to take measurements and to advise the fire officials that the radiological device in the nearby stage shed was neither an immediate or imminent health or safety hazard. On the third day, the Agency representative [and] the licensee Radiation Safety Officer (RSO) were allowed by the Fire Chief to enter the separate device shed with instrumentation and to retrieve the device. The device was located with appropriate instrumentation, separated from the rubble and stored securely elsewhere on-site. Surveys were subsequently conducted to release the remains of the storage shed. The manufacturer of the device was engaged by the licensee to come to the job site to confirm recovery of both Cesium-137 and Am-241:Be sealed sources; to conduct appropriate leak testing and leak test analyses; and to package, mark and label the 55 gallon drum for shipment to the manufacturer's headquarters. Leak test results disclosed no apparent leakage of material from either sealed source. These sources were packaged on August 22, 2002, and the shipment was secured on-site in a vault pending completion of attendant paperwork, obtaining the certificate of compliance for the shipping container, and arranging for the transportation pickup of the hauler. Event closed by state." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-18
42768 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-09 | 2006-08-14 19:19 | 2006-08-14 | AGREEMENT STATE - MEDICAL EVENT The State provided the following information via email: "On August 11, 2006, RHB received notification from North Oaks Radiation Center of a potential medical event. On August 9, 2006, a patient was undergoing the third of three fractional doses from a Nucletron Model MicroSelectron-HDR Classic Afterloader, using Ir-192. The first two fractions had been delivered properly. When this fraction was delivered, the medical physicist inadvertently selected the wrong delivery tube. There are two delivery tubes available depending upon the treatment plan. In this case, the longer tube was incorrectly selected for this fraction, and the source remained outside the patient for the entire fraction. The preliminary estimate of the highest dose in this configuration was approximately 100 - 125 rads to the perineum, which was not the intended treatment site, and which would have received less than 50 rads with the intended configuration. The patient has been notified. The California Radiologic Health Branch will investigate this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-08-17
42767 | 0 | SAN ONOFRE | 1 |  |  | [1] W-3-LP,[2] CE,[3] CE | 2006-08-07 | 2006-08-14 15:08 | 2006-08-14 | INFORMATION NOTIFICATION FOR DETECTION OF TRITIUM IN WATER SAMPLE "On Monday, August 14, 2006, Southern California Edison (SCE) made a voluntary communication to California State and Local government agencies regarding water samples taken during on-going Unit 1 decommissioning activities. During the week of August 7, 2006, water samples were found to have tritium levels ranging from 50,000 -- 330,000 picoCuries/liter. No permits were violated. "It was thought that the contamination may be attributed to historical events during Unit 1 operation (Unit 1 ceased commercial operation in 1992). SCE is investigating the source of the tritium and, as part of decommissioning, will remediate the contamination. The groundwater beneath SONGS is not a source of drinking water. "The NRC Resident Inspectors have been notified of this occurrence and will be provided with a copy of this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2006-08-14
42766 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2006-08-13 21:30 | 2006-08-14 00:30 | 2006-08-14 | OFFSITE NOTIFICATION MADE DUE TO AN OIL SPILL AT TURKEY POINT "There has been a fuel oil spill at the Turkey Point - Fossil plant of approximately 200 gal at 21:30 on 8/13/06. Turkey Point Nuclear control room was contacted at 00:02 on 8/14/06. The Control Room was notified that the spill had been contained and clean-up was in progress. DERM (Department of Environmental Resource Management) had been contacted at 23:05, and a vacuum truck from SWS Environmental had been dispatched to the site to assist in clean-up. The spill was contained on-site, with no chance of release off-site." The NRC Resident Inspector will be notified of this notification by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-14
42765 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-11 | 2006-08-11 14:36 | 2006-08-11 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via email: "The RSO called RHB this morning to report a missing gauge that he believes was stolen. He personally had placed the gauge in the locked storage location in Vista, CA on Wednesday, August 2, 2006. The gauge user that normally uses this gauge states he used a different one on August 3 - 4, 2006, but did not sign the in and out log on those two days. That user was on vacation Monday and Tuesday. On Wednesday and Thursday August 9 - 10, he did sign out a different gauge. On August 9, that user asked the RSO what had happened to the gauge he normally used. The RSO said it was either in the storage locker, or someone else had checked it out. The RSO decided to perform a full inventory of the gauges on Friday morning, the 11th. It was at this point that the RSO discovered that gauge was missing. The storage location is locked, and the gauges are stored in a locked area within that location. Nothing else was apparently taken, although there are several other gauges stored there. The RSO reported this to the San Diego County Sheriff's Office, who will be investigating. The RSO also stated he would post a reward in a local paper. The RSO has contacted all the gauge users, and they state they have no information about the whereabouts of this gauge. The gauge is a Troxler, Model 3440, with a nominal 9 mCi Cs-137 and 44 mCi Am-241. RHB will follow up with the licensee." The licensee will post reward in either San Diego Union Tribune or North County Times. * * *UPDATE PROVIDED BY HAMERICK TO KOZAL VIA E-MAIL ON 8/11/06 AT 1808* * * "Earlier today the California Radiologic Health Branch (RHB) provided a report regarding a stolen moisture-density gauge from Geo Tek, Inc. The RSO from Geo Tek just called, and the gauge had been taken out three days ago by an authorized technician who failed to record it being checked out on the daily log. As of now, all gauges owned by Geo Tek are accounted for and in their locked storage area. RHB will follow up with the licensee regarding the potential procedural violations." Notified R4DO (Gody), NMSS (Holahan), ILTAB (e-mail), Mexico (via fax) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-08-16
42764 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-08-11 09:55 | 2006-08-11 13:28 | 2006-08-11 | INADVERTENT OCA SIREN ACTIVATON "At 0955 EST, the Security Secondary Alarm Station (SAS) operator, in preparation for activity on the site firing range, proceeded to activate the Owner Control Area (OCA) Public Address system to make a site page announcement informing station personnel of range activity. During this process, the SAS operator inadvertently depressed the OCA Siren pushbutton instead of the Public Address pushbutton activating the onsite emergency sirens. The OCA siren system also activates an automatic prerecorded page address which informs non-essential personnel to evacuate the Owner Controlled Area. Approximately 50 to 75 nonessential personnel left the Salem and Hope Creek site, prior to the siren being secured and a page announcement made informing personnel of the inadvertent siren activation. Due to the common OCA, the inadvertent siren actuation affected both Salem and Hope Creek. The siren activation was inadvertent and there was not an actual event requiring site evacuation. Local, County and State agencies were informed of the inadvertent siren actuation. This event is being reported in accordance with 10CFR50.72(b)(2)(xi), Notification of Other Government Agencies." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-11
42763 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-08-10 17:05 | 2006-08-11 12:12 | 2006-08-11 | INOPERABLE HIGH PRESSURE FIRE WATER SYSTEM "At 1705, on 08-10-06, the Plant Shift Superintendent was notified of a large water leak on High Pressure Fire Water system A-5. This system provides water for fire suppression to a portion of the C-337 process building. The system was immediately isolated and TSR [2445] required hourly fire patrols were initiated for the affected area. The leak was located on an underground eight inch header immediately adjacent to the south wall of the building. Engineering has reviewed this incident and determined that due to the size of the leak, the system could not have performed the intended safety function. "This is being reported as an event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and no redundant equipment is available. "PGDP Problem Report No. ATRC -06-2592; PGDP Event Report No. PAD-2006-07; Worksheet No. Responsible Division: Operations. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-08-11
42762 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-08-10 | 2006-08-10 16:40 | 2006-08-11 | ELEVATED TRITIUM LEVELS IN ONSITE SAMPLE LOCATIONS "At 1400 on 8/10/06 KPS [made] a notification to the State and Local Government that samples taken at settling plugs in the basement of the Auxiliary Building and Turbine Building show elevated tritium levels. Detected tritium levels were between 6,000 and 103,000 pico curies per liter. The Radiological Effluent Program has not detected any elevated tritium levels outside the plant. RCS leakage is .19 gpm, stable and within Technical Specification limits and there is currently no identified leakage from the Spent Fuel Pool. Investigation is continuing to identify the reason for the increase in tritium levels." The licensee notified the following agencies: State of Wisconsin: Department of Emergency Management and Department of Natural Resources Regional Office County governments: Kewaunee County Emergency Director and Manitowoc County Emergency Director The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY KARST TO KOZAL ON 8/10/2006 AT 1839 * * * The licensee is planning a press release concerning the elevated tritium levels. This press release will be issued the morning of 8/11/2006. Notified R3DO (Kozak), NRR EO (Nieh), IRD (Wilson), R3 OPA (Mitlyng), HQ OPA (Hayden) * * * UPDATE PROVIDED BY KARST TO KOZAL ON 8/11/2006 AT 1820 * * * "In the initial notification, KPS personnel stated that there was currently no identified leakage from the spent fuel pool. For clarification, there is no indication of gross leakage from the spent fuel pool. However, KPS personnel will be continuing an investigation by collecting and analyzing water droplets from the Spent Fuel Pool leakage detection telltale drains to determine if the water droplets are from the spent fuel pool." The licensee notified the NRC Resident Inspector. Notified R3DO (Kozak) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-10
42761 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-08-09 22:30 | 2006-08-10 15:33 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * PROCESS UNIT 3 ALARM THRESHOLD EXCEEDED "In accordance with 10CFR74.57(f)(2), a report to NRC is required for the following event. On August 9, 2006 the Alarm Threshold Limit was exceeded for [DELETED] Extraction (Column Based) System. This was reported to the Measurement Control Unit Manager on August 10, 2006 at approximately 07:30. The time in which the alarm was initially reported was approximately 22:30 on August 9, 2006. The initial test difference exceeded the Alarm Threshold Limit. No new feed material is being added to the process until the alarm is resolved. An internal investigation is underway. Per E41-116 and the Fundamental Nuclear Material Control Plan (FNMCP), an Alarm Investigation Team was established since a process monitoring test exceeded its alarm threshold limit." Licensee notified Resident Inspector and HQ NRC. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 74.57 |  |  |  | 0 | 2008-05-11
42760 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-08-09 16:00 | 2006-08-10 11:07 | 2006-08-10 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The State provided the following information via email: "A Moister density gauge ( Troxler 3440 - Ser # 19048) was stolen on 8/9/06 at about 1600 in El Paso Texas. The gauge was stolen from the storage area at the facility. There appears to be no signs of forced entry to the area. A Police report was filed. The EPPD was to coordinate with the jurisdictional police department to visit the prime suspect (former PSI employee) yesterday evening (8/9/06). Locks at the facility are being changed. The local scrap yards and the Texas Association of Pawnbrokers have been notified. The source information is 1 Cs-137 source serial # 50-8685 8 mCi, and AmBe serial # 4714512 40 mCi. The licensee will provide a written report as soon as all the information is gathered." Texas incident # I - 8354 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-08-15
42759 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-08-09 | 2006-08-09 15:41 | 2007-01-03 | AGREEMENT STATE REPORT - STOLEN RADIOGRAPHY CAMERA The State provided the following information via email: "This is notification of an event in Washington State as reported to and being investigated by the WA Department of Health, Office of Radiation Protection. Date of Event: Wednesday, August 9, 2006 Location of Event: Everett Washington ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): At some time between 10:00 p.m. Tuesday, August 8 and 6:00 a.m. Wednesday August 9, 2006, a radiography truck was stolen from the parking lot of the Extended Stay America hotel on 8410 Broadway in Everett, Washington. The truck was discovered missing at 6:00 am as the radiographer was about to leave for work. The truck contained an AEA (QSA Global) model 880 radiography device, Serial Number D2720. The device contained an Iridium-192 75 curie source, serial number 28772B. The device was reported to be locked and secured in the truck. The truck was reported to be equipped with an alarm and truck disabling device but was not used. The keys to the vehicle were reported to have been left in the door of the truck. The truck is a white 2006 Chevrolet 2500HD extended cab with a dark room shell in the bed. It has a Texas license plate number [DELETED]. A report was made by the radiography company to the Everett police department upon discovery of the missing truck. Notification Reporting Criteria: WAC 246-221-240. Isotope and Activity involved: Iridium 192, 75 curies. Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None. Lost, Stolen or Damaged? (mfg., model, serial number): Stolen model AEA (QSA Global) model 880 radiography device, s/n D2720. It contained a 75 curie source, s/n 28772B. Disposition/recovery: None. Leak test? May 25, 2006. Vehicle: (description; placards; Shipper; package type; Pkg. ID number) The truck is a white 2006 Chevrolet 2500HD extended cab with a dark room shell in the bed. It has a Texas license plate number [DELETED]. Release of activity? None. Activity and pharmaceutical compound intended: N/A Misadministered activity and/or compound received: N/A Device (HDR, etc.) Mfg., Model; computer program: N/A Exposure (intended/actual); consequences: N/A Was patient or responsible relative notified? N/A Was written report provided? N/A Was referring physician notified? N/A Consultant used? N/A" Washington Event Number : WA-06-051 Other agencies notified: USDA - Krisher-Clive * * *UPDATE PROVIDED BY SCROGGS TO KOZAL VIA E-MAIL ON 8/10/06 AT 1712 EDT* * * "The truck was found by police at 4 pm [PDT], August 9. It had been abandoned in a strip-mall parking lot near Everett. DOH staff were at the scene, making measurements and assured radiation safety for police and fire personnel during the recovery effort. It appears the dark room had not been entered. The radiography device was still in its stowed position. After the police had finished conducting their criminal investigation at the scene, the truck and device were returned to WeldSonix IR personnel. DOH staff are continuing to investigate the incident. Corrective actions are to be determined." Notified R4DO (Bywater), NMSS(Holahan), ILTAB(Hahn), IRD(Wilson), DHS(Craig), DOE(Watt), EPA Region X(Sibley), Canada via e-mail, HHS(Dalziel), FEMA (Bagwell), USDA(Parks) * * * UPDATE AT 18:54 ON 1/3/2007 FROM ARDEN SCROGGS TO MARK ABRAMOVITZ * * * "At approximately 3:40 P.M. Wednesday August 9, 2006 Snohomish County Sheriff's officers found the missing radiography truck in the parking lot of an apartment complex south of the City of Everett, Washington. A DOH Health Physicist had been dispatched to Everett that day to begin an investigation and was at the Everett police department when the vehicle was reported found. The Health Physicist went to the site of the recovered truck and performed surveys of the area. The Snohomish County Sheriff's officer was able to gain access to the truck darkroom by opening the lock and allowing the HP to perform surveys inside the vehicle's storage area. The radiography device appears to have remained in the truck and was undisturbed. "The inspection of the stolen truck and the radiography device prompted a broader investigation resulting in the inspections of all the licensee's trucks, equipment and area operations. These inspections found several items of noncompliance that were ultimately addressed by the license. "These items were: control licensed material at all times, assure proper key control, physically secure exposure devices inside the vehicle to prevent unauthorized removal, and block and brace the transported package to prevent movement. These items were corrected and verified by DOH follow-up, field-site inspections." Notified the R4DO (Pruett), NMSS (Giitter), IRD (Wilson), ILTAB (English, via E-mail) and Canada (via E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-08-14
42758 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-09 | 2006-08-09 14:55 | 2006-08-09 | AGREEMENT STATE REPORT - DAMAGED MOISTURE-DENSITY GAUGE The State provided the following information via e-mail: "At about 8:45 am, [DELETED] with California OES notified RHB that he had received a call regarding a damaged moisture-density gauge. [DELETED], Alternate RSO for Southland Geotechnical (also dba Landmark Consultants), called to report that a Troxler, Model 3430 moisture-density gauge (S/N 29144), with a nominal 8 mCi Cs-137 and a nominal 40 mCi Am-241 source was run over by a loader at a temporary job-site in Heber, CA. The guide bar was broken, but the source rod was not. They were able to fully retract the source, but could not lock it in the shielded position. They took a leak test of the source, which is being analyzed, and they used duct tape to maintain the source in the shielded position. The source is currently secured in its case at the authorized, permanent storage location. After the results of the leak test are returned, if it is negative, the gauge will be returned to Troxler for repair." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-08-14
42757 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-08-08 15:43 | 2006-08-08 18:39 | 2006-08-08 | INADVERTENT EMERGENCY NOTIFICATION SIREN ACTIVATION "At approximately 15:43 [CDT] on 8/8/2006, all STP Emergency Notification System (ENS) sirens inadvertently/spuriously activated. The sirens automatically secured after approximately 3 minutes. All sirens except one at El Maton have subsequently been polled operable. STPNOC is investigating the cause of the activation. "STPNOC has notified Matagorda County Sheriff Department and radio station KZRC. Inquiries from the public have been received. "This notification is being made under 10CFR50.72(b)(2)(xi) as an event where other government agencies were notified." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-08
42756 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-08-08 05:00 | 2006-08-08 18:17 | 2006-08-09 | STOLEN MOISTURE DENSITY GAUGE After picking up the CPN Model MC-3 Moisture Density Gauge (s/n M38128625 10 millicuries Cs-137 and 50 millicuries Am-241:Be) at the company's office in Chino, CA, the gauge operator stopped at his residence in Victorville, CA, for 20 to 30 minutes. The operator's residence is on the way to the job site. The gauge was chained to the bed of the company truck which was parked in the operator's personal stall. When the operator returned to his truck the two chains that secured the gauge case to the truck were cut, and the gauge and case were gone. The San Bernardino Sheriff's Office was notified and investigated. The Radiation Safety Officer is preparing a reward offer. The gauge was within its leak test interval, and the last test was satisfactory. * * * UPDATE ON 8/9/2006 AT 0001 FROM BARBARA HAMRICK TO ABRAMOVITZ * * * The State provided the following information via email: "Today at about 6:15 pm, the California Radiologic Health Branch reported that a moisture-density gauge had been stolen in Victorville, CA this morning. The gauge belonged to RMA Geoscience. We are happy to report, the gauge was found tonight intact, in an abandoned field in Victorville, by the Victorville Fire Department. The RSO was contacted, and will be retrieving the gauge tonight, and returning it to the authorized permanent storage location in Chino, CA." Notified NMSS (Holahan), ILTAB, R1DO (Bywater) and Mexico (via E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-08-11
42755 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2006-08-08 16:45 | 2006-08-08 17:40 | 2006-08-08 | LOSS OF EMERGENCY RESPONSE RADIO ALERT SYSTEM TRANSMITTER Licensee has experienced a loss of emergency response capability due to loss of the Ames Hill NOAA transmitter. This transmitter is used to transmit information to the radio alert system (weather alert) for the site. Contract vendor has been contacted for troubleshooting and repair and is enroute to investigate the problem. The site has the ability to use the local radio stations if necessary. The licensee has notified the NRC Resident Inspector. The licensee will be notifying the VT, NH, and MA State Police, the VT Department of Public Service, and the VT Emergency Management Office. * * * UPDATE FROM J. BROOKS TO W. GOTT AT 1905 ON 08/08/06 * * * At 1840, Vermont Yankee was notified that the Ames Hill NOAA transmitter was operational. The cause of the failure was due to a possible lightning strike. The licensee notified the NRC Resident Inspector. The licensee will be notifying the VT, NH, and MA State Police, the VT Department of Public Service, and the VT Emergency Management Office. Notified R1DO (J Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-08-08
42754 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-08-05 16:31 | 2006-08-07 21:20 | 2006-08-07 | NOTIFICATION OF ONSITE TRITIUM RELEASE BELOW EPA GUIDELINES "While performing routine annual maintenance on the plant heating boiler, water that is normally discharged to the turbine building sump was redirected through a drain to gravel just outside the turbine building. This water contained low levels of tritium. This is a voluntary notification even though the tritium levels were below the EPA guidelines for drinking water and no permits were violated. No follow up action is necessary and monitoring will continue. On July 31 [2006] the site joined the industry initiative regarding lower thresholds for reporting tritium and the ground water reassessments being completed at all nuclear plants in the industry." Tritium level in the water was 1.91E-5 microCuries/ml. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW | [5 empty] | 0 | 2006-08-07
42753 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2006-08-03 10:00 | 2006-08-04 09:43 | 2006-08-06 | AGREEMENT STATE REPORT FROM SOUTH CAROLINA ON DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via email: "The SC Department of Health and Environmental Control was notified on Thursday, August 3, 2006, at 10:00 a.m., that a Humboldt Scientific Model 5001 portable moisture density gauge had been damaged on a job site in Mauldin, South Carolina. The gauge contained 11 millicuries maximum of Cesium 137 and 44 millicuries maximum of Americium 241:Be. [The licensee's representative] with QORE, Inc, made the report. The gauge was reportedly run over by a bulldozer while in use on the job site. [The licensee's representative] was present at the job site at the time of the event. [The licensee's representative] informed SC DHEC that the area had been roped off with both the gauge in its original position and the bulldozer inside the contained area. No individual had approached the gauge following the incident. [The licensee's representative] was advised to maintain surveillance of the device until DHEC personnel could respond. Once on site, DHEC personnel determined there was no release of material and no contamination of the bulldozer, the personnel involved or the roped area. The source was able to be retracted into the shielded position and the gauge placed in its transport container. The licensee secured the container in a locked storage box until disposition by the manufacturer could be accomplished. Departmental investigation is ongoing and updates will be made through the national NMED system." SC Report No.: SC060010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2006-08-09
42752 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2006-08-02 16:00 | 2006-08-02 18:10 | 2006-08-02 | HAZARDOUS MATERIAL DISPOSED FROM OWNER CONTROLLED AREA "[On] 08/02/06 at 1600 hrs. EST, Plant Security officers discovered a canister marked: 'Flammable Contains Phosphorus Notify Military or Law Enforcement if Found,' on plant owner-controlled property, outside the protected area. St. Lucie County Sheriffs Office (SLCSO) was contacted for determination of hazard posed. According to Plant Security supervision, the canister did not, and does not pose a threat to plant personnel, the public, or plant operations. SLCSO has asked other local experts to examine the canister and arrange for satisfactory disposal." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-02
42751 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2006-08-02 11:27 | 2006-08-02 18:41 | 2006-12-20 | POST CONTINGENCY LOW VOLTAGE ALARM "The Rochester Gas and Electric (RG&E) Energy Control Center (ECC) notified Ginna Operations that the Post Contingency Low Voltage Alarm was received for the off site power system. Ginna Operations entered procedure O-6.9, operating Limits for Ginna Station Transmission, and declared the offsite power inoperable per ITS 3.8.1[72 hour LCO]. Per NUREG-1022, section 3.2.7, if either offsite power or onsite emergency power is unavailable to the plant, it is reportable per 50.72(b)(3)(v)(A) regardless of whether the other system is available. "The RG&E Energy Control Center (ECC) monitors 115 Kv voltage using their State Estimation and Contingency Analysis System. The State Estimation portion of the system evaluates real time system power flow and voltages on the 115 and 345 Kv transmission systems. The Contingency Analysis portion analyzes the voltage effect of a Ginna main generator trip concurrent with worst case accident loading. If the Station 13A voltage would drop below the minimum required voltage for offsite power alignment a Ginna Post Contingency Low Voltage Alarm occurs. "If the main generator should trip, then the absence of a Post Contingency Low Voltage Alarm on the RG&E State Estimation and Contingency Analysis System will ensure that the subsequent offsite 115kV system voltage transient will not result in Ginna Station experiencing an under voltage condition on the 480V Safeguard Busses. "The RG&E ECC notified Ginna operations that the Post Contingency Low Voltage Alarm cleared at 1408 EDST on 08/02/2006 and the LCO for ITS 3.8.1 was exited at 1704 after observation of grid stability. The plant was maintained at 100% steady state conditions throughout the event." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM KYLE GARNISH TO W. GOTT AT 1430 ON 08/03/06 * * * "This is an additional notification for EN #42751 that was reported on 8/2/06 for offsite power being declared inoperable. A subsequent investigation revealed that offsite power was also inoperable on 7/17/2006 from 1427 to 1448 and on 8/1/2006 from 1022 to 1843 for which a notification was not completed." The licensee notified the NRC Resident Inspector. Notified R1DO P. Finney * * * RETRACTION OF JULY 17, 2006 PORTION OF EVENT FROM D. DEAN TO MACKINNON ON 12/20/06 AT 1435 EST * * * "The purpose of this report is to retract one of the events discussed in ENS report #42751 (August 2 and 3, 2006). The ENS report covered three separate off site power related events which occurred on July 17, 2006, August 1, 2006 and August 2, 2006. For each of the events, both sources of off-site power were declared inoperable following notification to R.E. Ginna Nuclear Power Plant that the calculated post contingency off-site system voltage was below the required value necessary to ensure that off-site power would remain available following a design basis accident. "Since the ENS report, an engineering analysis of the July 17, 2006 event has been completed. The analysis determined that the off site power system was actually operable at all times on July 17, 2006, The 'post contingency low voltage alarm (PCLVA)' computer model that is being utilized by Rochester Gas & Electric to calculate the post contingency off site system voltage is inherently conservative in that many of the automatic voltage regulators associated with the other generating units are assumed to be in the manual mode. The computer simulation that resulted in the alarm was repeated and by 'turning on' the voltage regulators for four of the nearby generator units, the post contingency voltage improved to above the alarm set point. The four voltage regulators that were turned on in the computer simulation were confirmed to be in the automatic mode on July 17, 2006. As such, the July 17, 2006 event is being retracted. "The licensee notified the NRC Resident Inspector." NRC R1DO (Ray Powell) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2006-08-02
42750 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2006-08-02 05:45 | 2006-08-02 08:30 | 2006-08-02 | MOTOR VEHICLE FATALITY OF PLANT EMPLOYEE "On Wednesday, August 2, 2006, at approximately 0545 EDT, a motor vehicle accident occurred at the entrance to the Owner Controlled Area that resulted in the fatality of a plant employee. The employee was reporting to work. Local law enforcement and emergency medical personnel were called and responded to the scene. "An investigation by local law enforcement and plant security is ongoing. "No formal press release is anticipated. "This event presented no risk to public health and safety." The NRC Resident Inspector was notified of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-08-02
42749 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2006-08-02 00:06 | 2006-08-02 04:49 | 2006-08-02 | LOSS OF ALL OFF SITE EMERGENCY NOTIFICATION SIRENS "On August 2, 2006 at approximately 0006 hours, the Emergency Planning Department determined that all of the 156 sirens in the Indian Point Energy Center, Emergency Planning Zone were unavailable due to, an inability to activate the sirens through the computer operating system. In accordance with the Indian Point reporting criteria, the loss of 16 or more sirens that cannot be returned to service in one hour, constitutes a major loss of the offsite notification capability that requires an 8-hour non-emergency notification in accordance with 10CFR 50.72(b)(3)(xiii). "The Emergency Plan has route alerting and public radio announcement available as necessary to notify the public in lieu of the non-operational sirens. "The condition was recorded in the IPEC Corrective Action Program as CR# 1P2-2006-04625 and actions have been initiated to investigate and correct the condition. "Troubleshooting continues. The cause of failure is still unknown at this time." The licensee notified the NRC Resident Inspector, state, and local agencies of this event. * * * UPDATE ON 08/02/06 AT 1417 EDT FROM BRIAN ROKES TO MIKE RIPLEY * * * "Update to the initial notification provided at 0449 hours on August 2, 2006, regarding the inability to activate the 156 sirens of the Indian Point Entergy Center (IPEC) offsite Emergency Notification System (ENS) through its computer operating system. The capability to activate the IPEC ENS was returned to service at 0635 hours. The total time the ENS sirens were unavailable was approximately 6 1/2 hours. During the event, route alerting and public radio announcement was available as necessary to notify the public. Troubleshooting identified two problems; a hardware problem with drive failures, and a problem with the computer system where the Oracle database control file synchronism failed. These failures resulted in the inability of the ENS computer system to connect to the Oracle database which prevented ENS from being activated. The computer drives were replaced and operating system data file error corrected. Troubleshooting is continuing to identify the cause. The IPEC Corrective Action Program recorded the event as CR-IP2-2006-04625 and will identify any additional corrective actions to prevent recurrence." The licensee notified the NRC Resident Inspector, state, and local agencies of this event. Notified R1 DO (P. Finney), DRP (N. Mamish) and OPA (D. McIntyre). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-08-02
42748 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2006-06-19 | 2006-08-01 14:55 | 2007-03-13 | UTAH AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via facsimile: "On July 11, 2006, the licensee indicated to a Division inspector that a 'misadministration' had occurred. "The licensee sent a letter dated July 17, 2006, to the Division indicating that a 'medical event' had occurred. The letter did not contain sufficient information to determine if the incident was an actual medical event. Multiple attempts were made to contact the RSO who reported the incident to verify that it was a medical event. The RSO was on vacation during most of July 2006. "The RSO contacted the Division by telephone on August 1, 2006, and confirmed that a medical event had occurred. "Event Description: On June 19, 2006, two patients were scheduled at the same time for radioactive treatment of hyperthyroidism. One patient was scheduled for 15 mCi of I-131, and the other patient was scheduled for 29 mCi of 1-131. The patient who was scheduled for 15 mCi of 1-131 ingested 29.0 mCi of 1-131. The error was identified by the licensee prior to the administration of I-131 to the other patient. The other patient's dose was corrected, and the patients' physicians were informed of the incident." Utah Event Report ID: UT-06-0002 * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC PUBLIC WEBSITE* * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2006-08-04
42747 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2006-08-01 05:00 | 2006-08-01 15:16 | 2006-08-01 | AUDIBLE HORN SYSTEM MALFUNCTION "During a routine monthly test of the Criticality Warning System (CWS), a segment of that system (DCP & DOP Warehouse) was found to have no audible horns functioning. Processes were shutdown, the personnel evacuated and the emergency organization assembled. "The preliminary investigation found that an Uninterruptible Power Supply (UPS) that supplies power to the CWS horn amplifiers was not functioning. "After a retest verified that the horns in the balance of the plant were functioning, those areas were allowed to resume operations. At the same time, the UPS for the DCP/DOP Warehouse segment of the system was replaced with a new unit and allowed to charge. Once charged, the system was tested and verified to have audible horn coverage. Operations were then allowed to restart in these areas. "As of approximately 1210 PM the CWS horns were fully operational and the facility was returned to normal operational status. Investigation of the incident is continuing including an attempt to determine the root cause of the UPS malfunction." The licensee notified Region II (J. Pelchat) and will notify State and local organizations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2006-08-01
42746 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-08-01 03:35 | 2006-08-01 11:32 | 2006-08-01 | RCS PRESSURE BOUNDARY LEAKAGE "At approximately 0335 EDT, LCO 3.4.13, RCS Operational Leakage, Action C was entered due to the identification of a pressure boundary leak. Reactor Coolant System (RCS) leak is believed to be a small pinhole on the weld on the downstream side of the check valve on Loop 1 Cold Leg Safety Injection Line. The estimated RCS leak rate is 0.1 gallons per minute. The Unit was in Mode 3 at the time of discovery. This event is being reported under 10 CFR 50.72(b)(3)(ii)(A). "The plant is currently evaluating the appropriate repair method for this condition." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-08-01
42745 | 0 | ACUREN INSPECTION, INC. |  |  |  |  | 2006-07-09 20:50 | 2006-07-31 16:13 | 2006-07-31 | RADIOGRAPHY CAMERA SOURCE UNABLE TO RETRACT Acuren Inspection, Inc, a Texas corporation doing inspection work in Michigan, provided the following information via email: "Description of Equipment Problem: The RT crew was using a 'pill stand' (a vertical metal pipe inserted into a coupling on a magnetic tripod with the source guide tube attached to a horizontal cross pipe) used to set up for an exposure. The 'pill stand' fell over during the exposure, thus crimping the source guide tube. "Cause of Incident: The 'pill stand' was not stabilized on a flat and clean surface prior to exposure. "Equipment: INC Exposure Device, Model IR-100, SN #4339, loaded with an 83 curie Iridium-192 source (Model 87703, SN #27923B). "Place, Date, and Time of Incident: Filer City, Michigan, 8:50 PM CST, July 09,2006." The technicians tried to retract the source assembly into the exposure device, but could not get the drive cable to move either way. Lead blankets were placed over the collimator and part of the guide tube. The technician located the crimp in the source tube and cut approximately a 1 1/2 inch piece of source tube out and freed up the drive cable and slowly cranked the source back in slowly. At 3:10 am, the source was back in the camera. The three licensee technicians involved in the retrieval received 181 mR, 60 mR, and 95 mR respectively by pocket dosimeter. The RSO stated that results for July film badge readings for the technicians will be available in early August. The RSO also stated that there was no damage to the camera or source, and that the guide tube has been replaced. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-07-31
42744 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-07-31 12:13 | 2006-07-31 14:13 | 2006-07-31 | AUTOMATIC REACTOR TRIP DUE TO MAIN GENERATOR TRIP "At approximately 1213 hours on July 31, 2006, with Watts Bar Nuclear Plant Unit 1 operating normally at 100% power, the main generator tripped resulting in a reactor trip per design. "All control rods inserted [fully] and the auxiliary feedwater system [AFW] automatically actuated per design and the reactor was stabilized in mode 3. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip (4-hour report) and under 10 CFR 50.72(b)(3)(iv)(A ) for the RPS [reactor protection system] and AFW actuations (8-hour report). "The cause of the generator trip is currently under investigation." Steam is being released via steam dump to the condenser and all systems functioned as required. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-07-31
42743 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-07-31 13:26 | 2006-07-31 14:04 | 2006-07-31 | UNUSUAL EVENT DECLARED DUE TO CO2 DISCHARGE TO THE CABLE TRAY ROOM "At 1326 on 7/31/06 there was a discharge of CO2 to the cable tray room. This is not a normally accessible room. Plant personnel verified no smoke, no fire. At 1340 the order was given to evacuate all personnel from the Reactor and Auxiliary Buildings as a precautionary measure. An Unusual Event was declared (HU3) at 1344 due to the affect on normal operation of the plant. The CO2 has been isolated, the buildings are being walked down and atmospheric testing is underway in the affected areas." The licensee notified the NRC Resident Inspector, Canada, State and County officials. * * * UPDATE ON 07/31/06 AT 15:17 FROM B. WALLAND TO A. COSTA * * * "At 1344 an Unusual Event was declared due to a toxic release into the Auxiliary Building (HU3). Release was due to a CO2 initiation, and has been isolated. Reactor building and Auxiliary building have been evacuated. Air sampling of the affected areas is underway." Notified R3 DO (O'Brien). * * * UPDATE ON 07/31/06 AT21:44 FROM N. MAJOR TO M. RIPLEY * * * "Walk downs for atmospheric conditions are complete and satisfactory for all areas of the Auxiliary Building. Normal access to Auxiliary building has been restored. This restores access to all affected areas. "Unusual Event is terminated at 2133." Notified IRD (T. Blount), R3 DO (K. O'Brien), NRR EO (M. Tschiltz), DHS (Biasco) and FEMA (Kimbrell). | 6 | 0 | 0 | 6 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Startup; FMode1: Startup | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-07-31
42742 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-07-30 | 2006-07-31 12:51 | 2006-10-23 | OHIO AGREEMENT STATE REPORT - STOLEN AND RECOVERED MOISTURE DENSITY GAUGE The State provided the following information via email: "The Bureau was informed by the RSO of the H.C. Nutting Company (Ohio license # 31210310024) on July 31, 2006 that a moisture density gauge (Troxler model 3430, serial # 23699) was stolen from the back of a truck parked in a closed garage at a residence in Columbus, Ohio. A lock and chain were cut to gain access to the gauge. The theft occurred between 2:30 PM and 8:30 PM on July 30, 2006. A report was filed with the Columbus Police Department. The [Ohio] Bureau is investigating." The gauge contains two sealed sources: Cs-137 (9 millicuries) and Am-241:Be (44 millicuries). OH Incident Number: OH2006-061. * * * UPDATE FROM STATE TO M. RIPLEY 1140 EDT ON 10/23/06 * * * The State provided the following update information via email: "UPDATE 10/23/06: The gauge has been recovered through a local pawn shop." Notified R3DO (M. Ring), NMSS EO (S. Wastler) and ILTAB (Email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2006-08-03
42741 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2006-06-14 | 2006-07-31 08:56 | 2006-08-03 | AGREEMENT STATE REPORT - MISSING SHIPMENT OF NI-63 The State provided the following information via facsimile: "On 7/13/06, licensee reported [ to State of MA] that a Raid-M-100 Hand-Held Chemical Agent Monitor (S/N 22653301851) containing up to 100 Mbq (2.7 mCi) of Nickel-63, shipped by licensee employee on 6/5/06 from Anchorage, AK, via United Parcel Service was reported as being not yet received at the licensee's Billerica, MA, site on 6/14/05. A second package, containing work related non-radioactive items, that had been shipped at the same time was received on 6/8/06. The device was in the custody of UPS at the time of the loss. UPS tracking system indicates the package was scanned in AK. Per the licensee, UPS reported on 6/19/06 and on 6/29/06 that its internal investigation had not yet found the missing item. Licensee filed incident report with Anchorage Police Department. The UPS missing package investigation is ongoing." The site of the event and last known location was UPS, 200 West 34th Avenue, Anchorage, AK. MA Report 7/31/06, Docket # 07-6484 * * * UPDATE ON 8/3/06 AT 1000 EST BY J KOZAL * * * Informed the Canadian government of above event via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-08-03
42740 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2006-07-30 17:30 | 2006-07-31 00:11 | 2006-08-08 | SECONDARY CONTAINMENT ISOLATION DUE TO 'B' SPENT FUEL RAD MONITOR FAILURE "At 1730 on 7/30/06 the 'B' Spent Fuel Pool Radiation Monitor spiked high, which resulted in the closure of the DW CAM (Continuous Air Monitor) and the Oxygen analyzer primary containment isolation valves. The spikes (2) of approximately 50 Mr/hour occurred during this event. Only 1 automatic isolation occurred. The Spent Fuel Pool Radiation Monitor High Rad signal also resulted in a Reactor Bldg Isolation (Secondary Containment), start of 'A' Standby Gas Treatment, and transfer of the Control Room Ventilation to the High Rad Mode. The 'A' Spent Fuel Pool Monitor remained constant at its background radiation level. No activities were in progress on the Refuel Floor at the time of the trips. Rad Protection Tech surveyed the area with no abnormal readings noted. The 'B' Spent Fuel Pool Radiation Monitor was declared inoperable. All automatic isolation valves have been reset, Rx Bldg Ventilation, Control Room Ventilation have been reset and SBGT (Standby Gas Treatment) has been secured. Normal trip setpoint is 50 Mr/ hour." The licensee has taken the actions of LCO 3.2.E The licensee notified the NRC Resident Inspector. * * * UPDATE FROM R. SCHREIFELS TO W. GOTT AT 1544 ON 8/8/06 * * * "This report is being reclassified from a 50.72(b)(3)(iv)(A) (valid system actuation) to 50.73(a)(2)(iv)(A) (invalid system actuation). "Based on further investigation, Monticello has determined that the actuation signal was due to a failed micro switch and therefore was not a valid signal. Because the actuation signal was not valid, Monticello is reclassifying the initial event report as an unplanned system actuation under 50.73(a)(2)(iv)(A). This report will be made in lieu of reporting the event as an LER. "In accordance with 50.73(a)(2)(iv)(A): '"This report is not considered an LER and the report is being made under 50.73(a)(2)(iv)(A). The original event report (EN #42740) [see above] detailed the systems affected, whether the actuation was complete or partial, and whether each affected system started and functioned successfully. "The cause of the invalid signal was the failure of the trip check pushbutton micro switch due to age related degradation. The switch has been replaced, and the 'B' Spent Fuel Pool Radiation Monitor was returned to service. "The licensee has notified the NRC Resident Inspector." Notified R3DO T. Kozak. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-07-31
42739 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-07-30 07:30 | 2006-07-30 11:15 | 2006-07-30 | TECHNICAL SPECIFICATION SHUTDOWN FOR HIGH CONTAINMENT AIR TEMPERATURE "On July 30, 2006, at 0730, a plant shutdown was initiated in accordance with Technical Specification (TS) Action 3.6.5.B.1. This action requires that the unit be placed in Mode 3 within six hours if containment air temperature is not restored to within limits during the previous eight hours. "On July 29, 2006, at 2026 TS Action 3.6.5.A was entered due to containment lower compartment average air temperature exceeding the TS Limiting Condition for Operation 3.6.5.B limit of 120 degrees Fahrenheit. Efforts to reduce the containment temperature during the eight hour completion time of Action 3.6.5.A were unsuccessful. "In accordance with normal plant operating procedures, the unit shutdown was completed by initiating a manual reactor trip from 16.5% Reactor Power following a controlled plant shutdown on July 20, 2006, at 1014. All safety systems and plant equipment used in the shutdown functioned as designed." All rods inserted fully without incident. No PORV/safety valves lifted. Decay heat is being removed with AFW. Unit 2 containment air temperature is 117 degrees Fahrenheit. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-07-30
42738 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-07-29 15:50 | 2006-07-29 19:19 | 2006-07-31 | REACTOR SCRAM AND ECCS INJECTION DUE TO LOSS OF FEEDWATER "At 15:50 EDT on 7/29/06, a Level 3 reactor scram occurred due to a loss of feedwater. The loss of feedwater was caused by a loss of Division 1 electrical power. All control rods fully inserted into the core. The lowest reactor vessel water level reached was 110 inches. HPCI and RCIC auto initiated on Level 2 and injected into the reactor pressure vessel. The Division 1 Emergency Diesel Generators auto initiated and supplied the Division 1 ESF buses. Level 3 and Level 2 isolations occurred as expected. Reactor water level is now being controlled in the normal water level band using Standby Feedwater. No SRVs lifted and RPV pressure is being controlled by the Turbine Pressure Regulator with the main condenser available as the heat sink. "At the time of the scram, work was being performed on the 120kV mat which resulted in a loss of Bus 101. "Group 13 (Drywell Sumps) isolated on Reactor Water Level 3. Group 10 (Reactor Water Cleanup Inboard), Group 11 (Reactor Water Cleanup Outboard), Group 12 (Torus Water Management System), Group 17 ( Reactor Recirc Pump Seals and Primary Containment Radiation Monitoring), and Group 18 (Primary Containment Pneumatic Supply) isolated on Reactor Water Level 2." The licensee notified the NRC Resident Inspector. The licensee stated that HPCI injected for 2 minutes and was then secured as Standby Feedwater was started. At the time of the notification, Bus 101 had been re-energized, and preparations were being made to restore normal power to the Division 1 buses and return the Emergency Diesel Generators to standby. The licensee is investigating the exact cause of the loss of power. * * * UPDATE FROM R. JOHNSON TO M. RIPLEY 1821 EDT 07/31/06 * * * "The purpose of this report is to update the information provided at 19:19 ET on 7/29/2006. "This event was originally reported under reporting criteria 50.72(b)(2)(iv)(A) as an ECCS injection. It has subsequently been determined that both the HPCI and RCIC systems auto-started in response to a reactor low water level 2 (Level 2) injection signal, however, only the RCIC system injected into the vessel. The Level 2 signal was only present for about 2.7 seconds until reactor water level recovered above Level 2. The HPCI injection logic is such that the Level 2 signal must be present until HPCI startup has completed. This includes time for the hydraulic pressure from the HPCI Auxiliary Oil Pump to develop enough pressure to open the HPCI turbine steam isolation valve (E4100F067) and time to stroke open the motor operated HPCI turbine steam isolation valve (E4100F001). It took about 12 seconds before steam was admitted to the HPCI turbine. Thus, the HPCI main pump outlet valve (E4150F006) did not open due to the short duration of the Level 2 signal. This is consistent with the HPCI system design. Therefore the event was not reportable as an event that resulted in or should have resulted in an ECCS injection into the reactor vessel. The event remains reportable under criteria 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A). "Additional clarification of the cause of the scram is also provided. The loss of bus 101 resulted in the loss of power to the operating south reactor feed pump (SRFP) turbine lube oil pump resulting in a loss of feedwater flow from the SRFP. The north reactor feed pump continued to operate. The plant is designed with an automatic runback of the recirculation system to allow continued operation following the loss of a single feed pump. However, the loss of bus 101 also resulted in the locking of the reactor recirculation pump speeds (scoop tube lock), disabling the runback feature. This led to a reactor scram on reactor low water level 3 (Level 3) since a single feed pump is not able to maintain reactor water level at 100% power operation. When south reactor feed pump lubrication pressure recovered, feedwater flow from the SRFP recovered. Recovering feedwater injection from the SRFP following the scram caused a rapid increase in reactor water level and a high reactor water level 8 (Level 8) shutdown of the HPCI, RCIC and reactor feedwater pumps. The standby feedwater system was subsequently started and used to maintain reactor level. "The plant is restarting, and is in Mode 2 with reactor temperature at approximately 508°F and reactor pressure at approximately 817 psi at the time of this report." Based on this update, ECCS injection was removed from CFR Section of the report. The licensee notified the NRC Resident Inspector. Notified R3 DO (K. O'Brien) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-07-29
42737 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2006-06-04 04:19 | 2006-07-27 21:00 | 2006-07-27 | INVALID RPS BUS 'B' AND DIVISION 2 PCIS ACTUATIONS "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1) to report an invalid actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). "On June 4, 2006, at 0419 [CST], with Unit 1 in Mode 1 'Run' at approximately 100% power, the 1B Reactor Protection System (RPS) bus unexpectedly de-energized. As a result, an RPS Bus B half-scram and Division 2 Primary Containment Isolation System (PCIS) isolations were received. All affected containment isolation valves closed as designed. RPS Bus B was transferred to its alternate feed, and restoration activities were begun. "A walkdown found that the 1B RPS MG set output breaker had opened. Troubleshooting identified that the cause was a failure of the 1B RPS MG set voltage regulator. The voltage regulator was replaced and successfully tested, and the 1B RPS MG set was returned to service. "Laboratory testing of the failed voltage regulator found that the stability potentiometer had failed, with excessive vibration identified as the apparent cause. Although the vibration levels at the MG set are considered to be normal, the voltage regulator is mounted in a control cabinet that sits directly on the generator end of the MG set. The normal vertical vibration on the 1B MG set was measured at greater than 2g, which could be sufficient over time to degrade the voltage regulator potentiometers. A design change has been initiated for both Units to isolate the voltage regulators from the RPS MG set vibrations. "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an invalid actuation of containment isolation valves in more than one system." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-07-27
42736 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-07-24 | 2006-07-27 18:45 | 2006-07-27 | ILLINOIS AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via email: "On July 26, the RSO at a broad-scope medical facility contacted the agency to report a possible medical event involving I-131. He stated that on July 24, a 5 microCurie Na-I thyroid uptake diagnostic study was ordered by an endocrinologist at the facility; however, instead of 5 microCuries, the doctor ordered a 2 millicurie dose. The nuclear technologist did not question the request and the dose was drawn and administered to the 16-year old male patient. When the authorized user listed on the license came in to do the imaging on July 25, he noted the error. It appears the authorized user was not directly involved in ordering the study. The licensee estimated the whole body dose as 1.89 Rem and the dose to the thyroid of 4,140 Rem based on 59.2% uptake. Using the same assumptions, the intended dose for 5 microCurie I-131 would be 10.4 Rem. The licensee anticipates some depletion of thyroid function as a result of this administration of 2 millicuries. The RSO continues to investigate the matter and more information will be provided." Illinois Item Number: IL-060036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-08-01
42735 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-07-27 | 2006-07-27 16:50 | 2006-07-27 | LOUISIANA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The State provided the following information via facsimile: "Non-Destructive & Visual Inspection (NVI) reported an excessive exposure to an industrial radiographer on July 27, 2006. [NAME DELETED], RSO, was called by Landauer [dosimetry service] with an exposure of 11,792 mrem for the month of June 2006 for [NAME DELETED]. [The RSO] is conducting an investigation into the excessive exposure and will supply further information once it is available. [The radiographer] told [the RSO] that he could not remember when he would have received such a high dose. Additional information will be provided to the NRC from the State of Louisiana as it becomes available." Louisiana Event Report ID No.: LA-060016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-08-01
42734 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2006-06-05 18:44 | 2006-07-27 14:04 | 2006-07-27 | INVALID EMERGENCY DIESEL GENERATOR START 'The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This report is being made under 50.73 (a)(2)(iv)(A). "On June 5, 2006, at approximately 1844 Mountain Standard Time (MST), Palo Verde Nuclear Generating Station Unit 1 experienced an invalid 'A' train emergency diesel generator (EDG) start in the emergency mode. The EDG had been stopped at 1835 MST following completion of troubleshooting steps related to the balance of plant engineered safety features actuation system (BOP-ESFAS) sequencer. The start occurred as additional troubleshooting steps progressed. The related 4160 VAC class 1E bus, PBA-S03, remained energized by off-site power during the event. The EDG started successfully and remained unloaded until it was stopped at 2014 MST. No other engineered safety feature (ESF) equipment in the 'A' train actuated. "(a) The specific train(s) and system(s) that were actuated: Unit 1 'A' train EDG started in the emergency mode. "(b) Whether each train actuation was complete or partial: Only EDG 'A' started as a single component and remained unloaded until it was stopped. No other ESF equipment actuated or was required. Essential spray pond pump 'A' was already running to provide EDG 'A' cooling water, from the previous EDG run. Bus PBA-S03 remained energized by off-site power throughout the duration of the event. (c) Whether or not the system started and functioned successfully: EDG 'A' started successfully and reached required speed, frequency, and voltage. Loading onto bus PBA-S03 was not required. Operations noted the EDG started with no anomalies. "The exact cause of the invalid start was not known at the time of this report. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-07-27
42733 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-07-27 08:12 | 2006-07-27 11:27 | 2006-07-27 | FOR CAUSE FITNESS FOR DUTY TEST POSITIVE "On July 27, 2006 a licensee [DELETED] supervisor tested positive for alcohol on a for-cause fitness for duty test. The individual's unescorted access was suspended [pending review by the Medical Review Officer and the Employee Assistance Program supervisor]. This notification is being made in accordance with 10CFR26.73(a)(2)(ii). A work investigation is in progress." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2006-07-27
42732 | -1 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2006-07-26 19:00 | 2006-07-27 03:07 | 2006-08-29 | LIMITING CONDITION FOR OPERATION 3.7.4 DEEMED TO BE NONCONSERVATIVE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "Palo Verde Nuclear Generating Station Technical Specification Limiting Condition for Operation (LCO) 3.7.4 requires only one of two atmospheric dump valves (ADV) per steam generator (SG) to be operable. Palo Verde Unit 3 currently has one ADV inoperable on the #2 SG. All other ADVs in Unit 3 (and all ADVs in Units 1 and 2) are OPERABLE. On July 26, 2006 at approximately 19:00 MST, Palo Verde Engineering personnel determined that this LCO is nonconservative since it does not satisfy the single failure criterion for the safety analyses for the accidents that would render one SG inoperable, specifically steam generator tube rupture (SGTR) with loss of offsite power (LOOP) which utilizes both ADVs on the unaffected SG. In case of one SG inoperable due to the event, and single failure of one ADV fail to open, the plant cannot be brought to safe shutdown condition during those accidents and may result in exceeding the acceptance criteria. This LCO should have required two ADVs per SG to be operable in order to satisfy safety analysis assumptions. "An administrative control in accordance with NUREG-1432, Standard Technical Specifications will be put in place for immediate compensatory action. NUREG-1432 LCO 3.7.4 Condition A, one required ADV line inoperable requires restoration of the ADV line to OPERABLE status within 7 days. Reperformance of the safety analyses is expected to be the long term solution. "The event did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or health and safety of the public." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1727 ON 8/29/2006 FROM RAY BUZARD TO ABRAMOVITZ * * * "The notification is being retracted due to further evaluation by engineering and licensing personnel which has determined that the license basis for Palo Verde Nuclear Generating Station is bounded by a steam generator tube rupture with a stuck open ADV coincident with a loss of offsite power event. The safety analysis for this event relies on one ADV on the unaffected SG which, along with the stuck open ADV on the affected SG, limits the offsite dose consequences to within 10 CFR Part 100 guidelines. "The safety analysis referred to in the initial ENS notification utilizes 2 ADVs on the intact SG to limit radiological doses to 10 per cent of Part 100 guidelines. However, as noted above, this analysis is not the bounding safety analysis for the SG tube rupture event. "The administrative control identified in the initial notification will remain in effect until engineering and licensing personnel determine if a Technical Specification change is required to support ADV single failure criteria. "The Resident Inspector has been notified of this retraction. " Notified the R4DO (Cain). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-07-27
42731 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-07-26 14:05 | 2006-07-26 23:50 | 2006-07-27 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "At approximately 2 P.M., the licensee called the Department to report that one of their moisture density gauges (CPN model MC3, serial # M39099115) had been run over by a large truck at approximately 12:20 P.M. earlier in the day. This happened when the gauge user had his back turned from the gauge and he was standing approximately 15-20 feet from the gauge. The gauge source rod (Cs-137) was in the shielded position at the time. The housing was severely damaged and the source rod handle was broken off near the weld joint where the source rod attaches to the source capsule. Both the 8 mCi Cs-137 and the 50 mCi Am-241:Be sources remained in their shielded positions as determined by subsequent surveys. "The incident happened at a Cal Trans job in Santa Paula, CA on Highway 150 at the 28.12 mile marker. The Cal Trans supervisor immediately shut the job down and sent all of the workers home. The area where the gauge was located was secured and roped off until the sources were verified to still be in the gauge. "The gauge and the broken gauge handle was transported back to the Santa Clarita storage location where a representative from RHB performed the survey to verify that the sources were in the gauge and in their shielded positions. The gauge will be transported to local CPN service representative , Maurer Technical Services in Laguna Hills, where they will do leak tests on the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-07-31
42730 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2006-07-26 07:35 | 2006-07-26 14:20 | 2006-07-26 | VARIABLE OVERPOWER REACTOR TRIP FOLLOWING TURBINE CONTROL VALVE MAINTENANCE "On July 26, 2006, at approximately 07:34 Mountain Standard Time (MST) Palo Verde Unit 2 experienced an automatic reactor scram on Variable Overpower. Unit 2 was operating at 90% power at normal operating temperature and pressure prior to the event. A main turbine control valve (CV02) was being returned to service following maintenance. CV02 initially started to open which caused reactor power to decrease to approximately 89%. During the evolution, six steam bypass control valve opened (three valves opened 100 percent, one opened 60 percent, and two opened 5 percent). Reactor power rapidly increased to 98% which resulted in an auxiliary Variable Power Trip (VOPT). The VOPT trip set point is 8 percent. The main turbine automatically tripped in response to the reactor trip. All rods inserted, as required. No ESF actuations occurred and none were required. "No emergency classification was required per the Emergency Plan. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. The maximum power level during the transient was approximately 98%." "Unit 2 is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The maximum RCS pressure was approximately 2260 psia (normal 2240). The maximum steam generator pressure was approximately 1090 psia (normal 1055). The event did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-07-26
42729 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-07-10 | 2006-07-26 10:48 | 2006-07-26 | AGREEMENT STATE REPORT - MEDICAL OVERDOSE The following information was provided by the state related to prostate brachytherapy which was performed on 7/10/2006 using I-125 seeds. "Prostate seed implant plans are specified in kerma units (U) by default in our computer planning system. However, the ordering of seeds is specified in mCi [milliCuries]. In this instance the default seed strength was not changed to mCi and a plan was developed for [the patient] to receive 111 seeds of an activity of 0.394 U per seed when 0.394 mCi was desired. The order form was completed for 111 seeds of the expected (not planned) activity of 0.394 mCi per seed. The result was an implant with seeds of activity 27% higher than planned." The overdose was noticed by the hospital on 7/12/2006. The physician, the patient, and the State of Ohio were notified on 7/13/2006. The State inspected the facility on 7/18/2006. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2006-07-31
42728 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-07-25 15:41 | 2006-07-25 16:56 | 2006-07-25 | UNUSUAL EVENT DECLARED DUE TO FIRE ALARM Cooper Nuclear Station control room received a fire alarm at 1529 CST indicating a fire in the service water pump room. The licensee responded by dispatching a fire brigade to the service water pump room to investigate. At 1541 CST, the licensee declared an unusual event in accordance with their emergency procedures due to their inability to confirm the validity of the fire alarm within a 10 minute period. The licensee exited the unusual event at 1559 CST after determining that the alarm was a false alarm caused by welding inside the service water pump room. The licensee issued a press release. The licensee notified the NRC Resident Inspector, the Nebraska State Patrol, the Richardson County Sheriff's Office, Nemaha County Sheriff's Office, Missouri Highway Patrol, and the Atchison County 911 Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-07-25
42727 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-07-21 | 2006-07-25 14:52 | 2006-07-25 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL IDENTIFIED IN ARC FURNACE ASH The State provided the following information via email: "On Friday, July 21, 2006, a truck containing electric arc furnace (EAF) dust departed the LeTourneau, Inc. facility at 2400 South McArthur Blvd., Longview, TX. The dust is commonly referred to as K061 waste and is a U.S. Environmental Protection Agency (EPA) Resource Conservation and Recovery Act (RCRA) hazardous waste that is a normal byproduct of steel production. A gate monitor alarmed at the Horsehead Resource Development Company, Inc. (Horsehead) in Rockwood, TN, indicating the possible presence of gamma emitting radioactive elements contained in the truck. An alarm of this type is typically associated with the melting of a volatile radioactive source. "The truck was returned over the weekend of July 22 - 23, 2006 to the LeTourneau facility in Longview, TX, where it was isolated. On Monday July 24, 2006 LeTourneau obtained the services of a consultant to identify the material in the truck. Surveys of the truck by LeTourneau, on the morning of July 25, 2006, indicated the presence of Cesium-137 in the K061 waste. Cs-137 is a byproduct material that is commonly used in sources and devices that are distributed under both general and specific licenses for various industrial applications. "After determining that the K061 in the truck was contaminated with Cs-137 a full survey of the furnace facility was performed and samples collected to quantify the activity of Cs-137. Radiation survey of the facility determined that exposure level in the facility ranged from 50 µR/hr to 3000 µR/hr. Highest readings were in the ash hopper and silo. LeTourneau does not believe that there were any significant doses to their employees or public due to the location of the highest reading. LeTourneau plans to have result for the samples collected before the end of the week. "LeTourneau notified the State immediately after determining that the K061 was contaminated with Cs-137." The state is investigating this incident. Texas Incident No.: I-8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-07-28
42726 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-05-01 | 2006-07-25 14:23 | 2006-08-29 | TEXAS AGREEMENT STATE REPORT - BADGE EXPOSURE The State provided the following information via facsimile: "Dosimetry supplier reported 12 Rem exposure. Licensee determined that employee left badge in truck, in radiation field at several locations [various job sites] during the monitoring period." TX Incident No. I-8348 * * * UPDATE ON 8/29/2006 FROM STATE OF TEXAS TO ABRAMOVITZ * * * The State provided the following information via facsimile: "On June 20, 2006, the Licensee notified the Agency that on June 19, 2006, a courtesy call from their dosimeter processor informed them that a worker's film badge indicated an exposure of 12.355 Rem for the month of May, 2006. The RSO removed the worker from rotation to prevent any further exposure. An investigation by the Licensee indicated no abnormal self reading dosimeter readings. The worker could not think of any reason why he would have received that much exposure. The individual only performed work involving radiation on seven occasions in the month of May. During the investigation, it was revealed that the worker had routinely left his dosimetry in the glove box of their work truck at the end of the day. The RSO stated that all of his trucks are in use supporting radiography operations each day. It is believed that the badge was exposed to the majority of the indicated exposure while in the glove box. Individuals who worked with the individual stated that they were not aware of any reason why this worker would have received any unusual exposure. The Licensee assessed the worker's dose to be 59 mrem for the exposure period based on daily exposure records. No Notice of Violation was issued." Notified the R4DO (Cain) and NMSS EO (Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-07-28
42725 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2006-07-25 09:45 | 2006-07-25 11:41 | 2006-08-14 | REACTOR TRIP BREAKERS OPENED DURING MAINTENANCE ON STEAM GENERATOR WIDE LEVEL CHANNELS The licensee was performing maintenance on "D" Steam Generator Low Level bistables when 4 (four) out of 8 (eight) trip control breakers opened possibly due to a 24 V DC power supply transient to 2 (two) of 4 (four) logic matrix relays. The reactor trip logic was verified to be functional and capable of processing valid reactor trip signals. The actuation was invalid as no plant transient occurred and no process variable was exceeded which would otherwise have required a reactor trip. The licensee notified the State and the NRC Resident Inspector. * * * RETRACTION ON 08/14/06 AT 0947 ET BY M. EWER TO MACKINNON * * * "Upon further review, the initial notification of this event is determined to have been conservative. A review of NUREG 1022, Rev. 2, 'Event Reporting Guidelines, 10 CFR 50.72 and 50.73,' as well as the supporting comments in the notice of final rulemaking for changes to 10 CFR Parts 50 and 72 contained in the Federal Register on October 25, 2000, indicates that these documents stress the need for reporting of system actuations. As stated in NUREG 1022, 'actuation of multichannel actuation systems is defined as actuation of enough channels to complete the minimum actuation logic. Therefore, single channel actuation logic,' Per the final rulemaking, 'the principal reason for reporting an actuation of one of these systems is that it is indicative of an unplanned plant transient that the NRC needs to evaluate to determine if action is necessary to address a safety problem.' "In the event described in CR-06-06880, a portion of the RPS actuation sufficiently to cause four of the eight TCBs to open (i.e, a half trip), but not enough channels actuated to complete the minimum actuation logic for RPS (i.e, insufficient channels to fulfill the safety function of the RPS to deenergized the control rod drive mechanisms to shutdown the reactor). There was no unplanned plant transient as a result of the half trip. "Determination "Based on the above assessment, this condition in NOT reportable per 10 CFR 50.73(a)(2)(iv)(A) as an actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B). "Accordingly, the report of a 4 hour non-emergency event under 10 CFR 50.72(b)(2)(iv)(b) for a half RPS trip actuation should be withdrawn." R1DO (Lorson) notified. The NRC Resident Inspector will be notified by the licensee of this retraction. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-07-25
42724 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-07-24 17:00 | 2006-07-25 00:37 | 2006-07-25 | LOSS AND RESTORATION OF SPDS SYSTEM "On 7/24/06, Brunswick Unit 2 experienced a loss of Safety Parameter Display System (SPDS) capability for 12 hours and 54 minutes. Operations was informed of the loss [and restoration] of SPDS at 1700 7/24/06. "Unit 2 remained at 100 percent power, steady state operation, throughout the time that SPDS was inoperable. "The cause of the SPDS failure is under investigation. "Note that all other emergency assessment equipment was operable during the time Unit 2 was without SPDS." SPDS was restored at 1330, 7/24/06. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-07-25
42723 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-07-21 17:00 | 2006-07-24 11:38 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * MEDIA INQUIRY This report is being made to the NRC as a result of a media inquiry from the Lynchburg News and Advance. [The reporter] was asking about the Society of Concerned Scientists report on a leak that occurred at the BWXT site in 2000. She asked what BWXT does to prevent such things from occurring. The Manager of Communications indicated that BWXT follows regulatory guidelines given to us so that our systems function safely and in compliance. The licensee will notify the NRC Resident Inspector. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
42722 | 0 | TEAM INDUSTRIAL SERVICES |  |  |  |  | 2006-07-22 12:00 | 2006-07-22 15:24 | 2006-07-22 | RADIOGRAPHY CAMERA SOURCE UNABLE TO RETRACT While performing radiography on a new tank located in the northeast corner of the Milford Power Plant, 55 Shelland Lane, Milford, CT, the magnetic stand fell on the guide tube and crimped the tube and the source cannot be properly retracted into the shielded position. The radiography camera is a model AEA 60B, serial number - B3562 containing a 62 Curie Ir-192 source, serial number - 28814B. The radiography crew established a boundary around the source at a distance where the exposure rate is less than 2 mrem/hr. Access to the boundary is being controlled by the radiography crew through visual surveillance. QSA-Global in Burlington, MA has been contacted to assist in retrieving the source and should be onsite at approximately 1930 EDT on 07/22/06. There are no indications of any abnormal radiation exposures due to this event at this time. * * * UPDATE ON 7/22/06 AT 2012 EDT FROM C. SMITH TO A. COSTA * * * QSA-Global personnel were able to remove the kinks from the guide tube and then manually return the source to the device's shielded position. The highest dose received during the procedure, which was complete at 1940 hrs, was 65 mrem to the whole body as measured by pocket dosimetry. Extremity dose measurement will be available after finger dosimetry is processed. The radiography camera will be sent to QSA-Global for evaluation, repairs and leak test. Notified R1 (J. Kinneman) and NMSS (L. Kokajko). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-07-22
42721 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-07-21 | 2006-07-21 18:31 | 2006-07-21 | FLORIDA AGREEMENT STATE NOTIFICATION OF MEDICAL EVENT The State provided the following information via email: "The RSO [Deleted] of Florida Hospital called. Florida Hospital in Ormond Beach (873 Sterthaus Ave, Ormond Beach, FL 32174) had a medical misadministration. "They were using a HDR (Nucleotron Microselectron Classic, 8 Ci Ir-192 activity) to deliver vaginal treatment of 500 cGy per fraction. A typical patient gets 3-5 fractions. The delivery tube was 18.5 cm too long resulting in the source being outside the patient. The RSO indicated that the dose to the prescribed area was zero. [Due to the patients position, it was determined that] the dose to the skin is probably not too high. "The Medical Physicist [MP] [deleted] has not yet determined what the skin dose estimate would be. "[The MP] discovered the mistake after observing a treatment. The mistake happened because two different types of applicators are used. One has a longer tube than the other. The tubes were mixed up, which resulted in the misadministration. At least one patient is affected by this and maybe as many as 4 others. The MP believes that using film recorded for each treatment, the hospital can determine how many and which patients are affected. "The treating physician has been notified, the referring physician and the patient have not. "The State of Florida Bureau of Radiation Control will investigate." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-07-26
42720 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2006-07-21 10:30 | 2006-07-21 11:06 | 2006-07-21 | MANUAL REACTOR TRIP DUE TO SPARKS FROM UNDER MAIN GENERATOR "At 1031 hours on July 21, 2006, the reactor operator manually tripped the reactor from 100% power resulting in turbine trip and actuation of auxiliary feedwater. This is reportable under 10 CFR 50.72(b)(2)(iv)(B). 31 Reactor Coolant Pump tripped after the reactor trip. All other systems operated as expected. Steam is being condensed by the condenser. The reactor was tripped due to an abnormal condition under the main generator; electrical arcing/sparking was observed. The reactor will remain shutdown until the cause of the arcing/sparking is identified and corrected." There was no indication of fire but the fire brigade was called out. The observed arcing and sparking from underneath the main generator secured after the turbine trip. All control rods fully inserted on the reactor trip. The electric plant is in a normal shutdown lineup and the EDGs are operable. The unit is stable and Unit 2 was not affected. The licensee notified the NRC Resident Inspector and the New York Public Service Commission. * * * UPDATE PROVIDED BY DON CROULET TO JEFF ROTTON AT 1416 EDT ON 07/21/06 * * * Licensee reported the AFW actuation as a Specified System Actuation per 10 CFR 50.72(b)(3)(iv)(A). The licensee notified the NRC Resident Inspector. Notified the R1DO (Kinneman) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-07-21
42719 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-07-20 18:30 | 2006-07-21 10:02 | 2006-07-21 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE A technician who works for the licensee left his vehicle at his residence and then went to have dinner about 30 minutes away. Upon returning to his home and vehicle, the technician found that all equipment had been stolen, including the Troxler moisture/density gauge, model 3430, s/n 32187. The gauge contained 40 milliCi of Am-241/Be and 8 milliCi Cs-137. The licensee had the Troxler chained and locked to the truck bed. The licensee filed a police report with the Opelousas State Police, and will be offering a reward. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-07-26
42718 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-07-20 17:10 | 2006-07-20 17:22 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * MEDIA INQUIRY REGARDING TRITIUM LEAK FROM YEAR 2000 "This concurrent report is being made to the NRC as a result of a media inquiry from [a reporter] at the Richmond Times Dispatch. The inquiry was specific to a tritium leak from a spent storage fuel pool and underground piping in 2000. [The reporter] indicated that NRC had provided specific information concerning sites in Virginia that had been reported by the Society of Concerned Scientists. The BWXT Manager of Communications confirmed that BWXT had a leak of material from the pool and that the leak was repaired." The licensee will be notifying the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
42717 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-07-17 15:29 | 2006-07-20 17:18 | 2008-05-13 | MEDIA INQUIRY REGARDING BWXT REORGANIZATION *********************************************************************************************************************************** THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. *********************************************************************************************************************************** "This concurrent report is being made to the NRC as a result of a 'media inquiry only' statements that were released to the following organizations: WDBJ 7, WSET 13, and The News & Advance. All of these entities are local news agencies in the Central Virginia area. The press release that was provided is attached. The media inquiry is the result of a recent press release concerning BWXT's reorganization. Licensee Press Release Text: "(Lynchburg, Va) - BWX Technologies, Inc. (BWXT) recently announced the consolidation of its two nuclear manufacturing facilities, the Nuclear Products Division (NPD, Lynchburg, Va.) and the Nuclear Equipment Division (NED, Barberton, Ohio and Mount Vernon, Ind.), into one organization named the Nuclear Operations Division (NOD). The consolidation is designed to facilitate stronger efficiencies in management and overhead functions in executing the work BWXT performs in manufacturing nuclear components for the U.S. Department of Energy. The restructuring also positions BWXT to be more cost competitive in emerging nuclear markets. "As a result of the consolidation, BWXT will reduce its salaried workforce at NPD, NED and BWXT Services, Inc, by approximately 100 people during the months of August and September 2006. "To help mitigate any need for an involuntary reduction, a Voluntary Reduction in Force (VRIF) program, which includes an enhanced severance package, has been offered to all salaried employees at the three sites." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 05/13/08 BY J.KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. *********************************************************************************************************************************** | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-13
42716 | 0 | UNIVERSITY OF VIRGINIA MEDICAL CENT |  |  |  |  | 2006-07-11 | 2006-07-20 16:45 | 2006-07-20 | MEDICAL EVENT INVOLVING SOURCE CAPSULE EGRESS FROM PATIENT On 7/11/06, the licensee administered an I-131 source (54.6 millicuries) to an elderly female for Goiter treatment and subsequently released her. On 7/20/06, the patient went with her daughter to another medical center in West Virginia, and it was related to the staff that a capsule was under the patient's pillow. The staff requested and the capsule was brought to the center, which was confirmed to be the source intended for the patient's treatment at the University of Virginia Medical Center. The West Virginia medical center contacted the licensee and has possession of the source capsule in their hot lab. This incident is being monitored by the licensee who is continuing with an investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PATIENT INTERVENTION DAMAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(b) |  |  |  | 0 | 2006-07-20
42715 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-07-18 22:00 | 2006-07-19 01:07 | 2006-07-21 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER "48 of 165 offsite sirens are not functioning due to loss of power/equipment problems because of recent storm. Efforts are in progress to restore power to the affected sirens." The affected sirens are located in Chester County. Compensatory measures are in effect to alert the public should the need arise. The licensee informed the NRC Resident Inspector. *** UPDATE FROM C. PEAKS TO J. KNOKE AT 08:40 EDT ON 07/21/06 *** The licensee reported that only 22 of 165 sirens are now inoperable. This is less than the reportable (25%) amount of 41 sirens. The licensee notified the NRC Resident Inspector. Notified R1DO (Kinneman). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-07-19
42714 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-07-18 17:15 | 2006-07-18 22:30 | 2006-08-10 | POTENTIAL FLOODING COMMON MODE FAILURE OF SERVICE WATER PUMPS "At 1715, it was determined that current plant configuration does not match the assumptions of the Service Water Pump House flooding design calculation. The calculation assumes that a leak developing in the discharge valve bay would cause the water level to rise to the level of the system piping and then stabilize due to leakage out of the valve bay through the area where the piping penetrated the wall. This level is below any electrical equipment and therefore would have no adverse impact on the system. The area around the piping where it was assumed the water would escape was found to be sealed with a fire barrier material. Since the water could not escape, it would continue to rise until it impacted the pump discharge valve (motor operated valve). This would potentially render the Service Water train inoperable. "A second issue with the design calculation was discovered in that it assumed the pump discharge bays for the other two pumps were physically isolated from each other. This is not the case. The discharge piping for the three pumps are cross-connected via a line which penetrates all three bays. The area between the cross connect piping and the bay walls is not sealed. Any leakage in one bay will be communicated to all three bays. This results in the potential for a leak in any of the bays to possibly impact the operability of both trains of Service Water." The licensee has put compensatory measures in place to maintain equipment operability. The licensee has determined that by putting either of the two following compensatory measures in place equipment operability will be maintained: 1. They will provide a continuous watch of the areas to detect water leakage that may cause a flooding concern and close service water pump discharge valves within 15 minutes and secure the affected service water pump, or 2. They will remove the fire seals causing the potential flooding concern in rooms 25-01, 25-02 and 25-03 of the service water pump house. The licensee notified the NRC Resident Inspector. *** UPDATE F. LUCAS TO J. KNOKE AT 17:40 EDT ON 08/10/06 *** The following retraction was submitted by licensee: "EN #42714 was submitted by South Carolina Electric & Gas Company based on the potential loss of both trains of V.C. Summer Nuclear Station Service Water due to leakage/flooding in the pump discharge valve bays (pits). South Carolina Electric & Gas company retracts EN #42714 based on the following discussion. "Engineering has performed a more rigorous evaluation of the subject scenario utilizing existing calculations and analyses. Any flood or spray event in the Service Water Pump House operating floor or any one discharge valve pit will eventually propagate to all three pits through the open areas around the pipe penetrations. The pits will fill up to the pipe level and would conceivably continue to fill to the operating floor level. The discharge motor operated valve and the control panel above the floor of each valve pit in this scenario would be submerged and would become disabled. The control panels would be shorted to ground, and would fail the discharge motor operated valves in the as-is open position which would not affect the service water supply of either train. "Since the motor operated valves fail as-is, this subject scenario would not result in the loss of both trains of service water." The licensee will notify the NRC Resident Inspector. Contacted R2DO (K. Landis) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-07-18
42713 | 0 | US ARMY |  |  |  |  | 2006-07-06 | 2006-07-18 13:58 | 2006-07-18 | UNPLANNED TRITIUM CONTAMINATION DURING MAINTENANCE "On July 6, 2006 a range indicator SSDR no. NR-155-S-116-S containing [four] 0.8 Ci [curies] tritium lamps [3.2 curies total] was broken during a maintenance procedure at Ft. Bragg, NC Special OPS, 3rd Group Direct Support weapons room, Bldg E-1978. The Ft. Bragg RSO was notified on 7 July 2006 of the incident. Improper maintenance procedure was the reason for the breakage of the tritium sealed source. Two persons were involved in the incident. One tritium bioassay was taken of one individual. The second individual did not have a bioassay taken due to the fact he went on TDY [Temporary Duty] before the discovery of the accident. Leak test of the broken range indicator showed removable contamination of 0.95 microcuries. An area survey of the weapons room by the Ft. Bragg RSO showed a maximum contamination of 0.3 micro curies (64,944 dpm). The Ft. Bragg RSO closed and secured the arms room from re-entry of personnel. The Ft Bragg RSO performed decontamination of the weapons room and brought the tritium removable contamination below regulatory concerns (<10,000 dpm). The licensee was notified of the incident on July 12, 2006." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2006-07-18
42712 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-07-17 21:46 | 2006-07-17 23:56 | 2006-07-18 | EMERGENCY EVACUATION SIREN FAILURES DUE TO THUNDERSTORMS "Greater than 25% of the emergency sirens have failed due to a severe thunderstorm in the area." The licensee stated that 30 sirens had failed and that restoration activities were currently in progress. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM J. KOEPLIN TO M. RIPLEY 0503 ET 07/18/06 * * * As of 2317 CDT 07/18/06, the number of inoperable sirens fell below 25% of all sirens with 23 failed sirens not restored to service. Restoration activities remain in progress. The licensee will notify the NRC Resident Inspector. Notified R3 DO (Cameron) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-07-18
42711 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2006-07-17 15:47 | 2006-07-17 21:38 | 2006-07-27 | CONTROL ROOM VENTILATION FLOW BELOW LIMITS "During review of instrumentation calibration, it was determined that a faulty flow instrument was used for determination of CREFS (Control Room Emergency Filtration System) flow. Due to the error of the flow instrumentation previous test results were deemed to be high outside acceptance criteria. These tests were performed in October of 2005. The CREFS was declared inoperable and preparation was made to rerun the surveillance. At 1900 the surveillance was completed. The results of the surveillance determined that CREFS flow was below the allowable limit. The minimum flow for CREFS is a requirement for post DBA dose calculation for Control Room personnel. With minimum flow not maintained, the Control Room post accident dose calculations may be violated. "CREFS remains inoperable pending adjustments of ventilation dampers and successful performance of surveillance testing. "Resident inspector has been notified." The licensee has entered Technical Specification LCO 3.7.4, Condition A, which is a 7 day LCO. * * * UPDATE AT 1725 EDT ON 7/27/06 FROM DAVID VAN DER KAMP TO S. SANDIN * * * The licensee is retracting this report based on the following: "This notification is being made to retract Event Notification #42711 which reported a loss of safety function due to the unplanned inoperability of the Control Room Emergency Filtration System (CREFS). CREFS was declared inoperable due to flow below the acceptance criteria required per surveillance testing. Upon further evaluation, CNS has determined that CREFS satisfies the Technical Specifications (TS) surveillance requirements and that the safety function was not lost. "The surveillance procedure acceptance criteria for CREFS minimum flow is not required by the TS and is not a direct indicator of system operability. The procedure has been revised to remove the minimum flow acceptance criteria. It has been determined that CREFS, at the flow conditions documented on July 17, 2006 and during a past surveillance in 2005, satisfied TS and USAR requirements and was capable of performing its safety function." The licensee will inform the NRC Resident Inspector. Notified R4DO (Farnholtz). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-07-17
42710 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-07-17 04:00 | 2006-07-17 16:43 | 2007-01-17 | WASHINGTON AGREEMENT STATE REPORT OF STOLEN TROXLER GAUGE The State provided the following information via email: "The licensee reported that a Troxler portable moisture/density gauge, model 3430, serial number 25598, was stolen between 4:00 a.m. and 6:00 a.m. today. The gauge was in a 1987 Toyota Camry when the car itself was stolen from the residence of an employee living in Renton, Washington. The gauge was in the trunk of the car at the time of the theft. The licensee reported that the trunk was locked, the transport box was locked and the gauge was locked. The licensee did not have a required second outer level of security in place to keep an unauthorized individual from removing the locked box with the gauge. The licensee did not keep the gauge stored at the licensed storage location as required by license condition. The user retrieved the gauge Sunday night (July 16, 2006) from the licensed storage location located several miles north of his residence for use today at a temporary jobsite several miles south of his residence. The theft was reported to the Renton Police Department (police report #4626) and was assigned Case #06-7698. " Washington Event Report # WA-06-050 * * * UPDATE PROVIDED VIA EMAIL FROM ARDEN SCROGGS TO JEFF ROTTON AT 1232 EST ON 01/17/07 * * * "[State of Washington, Radioactive Materials Section] received a written report on January 11, 2007, from Professional Service Industries, Inc., (PSI) that the portable moisture/density gauge had been found and recovered on August 22, 2006. The gauge was discovered in the front yard of a residence in Kent, Washington. This is approximately 1 mile from where the vehicle had been stolen. The King County, Washington, Sheriff's Department was notified of the find by the resident at the Kent location. The Sheriff's Office notified PSI of the find. PSI went to the residence, inspected the gauge and determined that it was undamaged. The source rod was locked in the shielded position but the transportation box appeared to have been opened because the locking hasp had been broken. The gauge was placed back into secure storage at a PSI licensed storage location. The gauge was later leak tested [in August 2006]. The test was negative. "Corrective actions included: 1) The gauge user was required to provide the department with a written report of events that lead to the gauge becoming uncontrolled gauge. In the report the gauge user gave reasons for violating license requirements, 2) The user was required to attend a re-training session that included maintaining proper security for portable gauges. The user was required to make written confirmation of the requirements, and 3) The user was required to assist in providing similar training to other PSI gauge users. During that training session, the gauge user gave a lessons learned summary of the incident." Notified R4DO (Campbell) and NMSS EO (Burgess). Notified ILTAB (via email) and Canada (via fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-07-20
42709 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-07-15 | 2006-07-17 15:31 | 2006-07-17 | LOUISIANA AGREEMENT STATE REPORT OF RADIOACTIVE SOURCE FOUND AT OLD TEXACO SITE The State provided the following information via facsimile: "While performing NORM [naturally occurring radioactive material] remediation at an old Texaco site at the end of Hwy 23 in Venice, LA, a radioactive source was uncovered. Production Management Industries (PMI) was dipping out mud out of a canal when, the scoop of mud had a high reading. The scoop was set aside in a restricted area. It was thought to be NORM pipe until the survey meter used on NORM material pegged. They also noticed that the piece of metal giving off radiation was about two inches long. Then it was believed to be a sealed source. Mr. [Redacted] was called about the situation. Mr. [Redacted] told them to set it aside until he got there. Once Mr. [Redacted] was on site they took a survey of the source with a different survey meter. The reading at contact was 30 mR/hr. It was 100 microR/hr at 3 feet and 20 microR/hr at 10 feet. Mr. [Redacted] performed a wipe test on the source and it did not appear to be leaking. Mr. [Redacted] then put the source in a 5 gallon drum and put dry cement around the source. The reading at the drum after this was 1.9 mR/hr. He then put the drum in the generator room where it could be locked up and secure. American Radiation Services is going to pick up the source from Venice on July 17 for disposal. All the employees that were around the source are radiation workers and were wearing personnel monitoring. No excessive exposures are expected. No one picked up the source by hand." Louisiana Report Number LA0600014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-07-20
42708 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2006-07-17 | 2006-07-17 14:34 | 2006-07-17 | ALABAMA AGREEMENT STATE REPORT OF FOUND MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "On the morning of July 17, 2006, the Alabama Office of Radiation Control was contacted by Madison County Emergency Management Agency concerning a container found in the middle of a street in Huntsville, Alabama. The incident was originally reported by a passerby to the Huntsville Police Department. The Huntsville Police Department, Huntsville Fire and Rescue Department, and Huntsville HAZMAT unit responded to the call. Also, local news media was at the scene. The item was determined to be a CPN Model MC-3 moisture density gauge (Serial No. M350402559) containing 10 millicuries of Cesium-137 and 50 millicuries of Americium-241/Beryllium. An investigation found that the device was the property of OMI, Inc. of Huntsville, Alabama. OMI Inc. has an Alabama Radioactive Material License No. 1171 to possess and use the device. The licensee was notified by the Alabama Office of Radiation Control of the found gauge and they returned to the scene to pick it up. Preliminary findings indicate that the licensee failed to secure the device by two independent means in the back of the pickup truck and failed to properly block and brace the device during transport. It does not appear that the device suffered any significant damage but the licensee was advised to perform a leak test of the device before placing the unit back in service." Alabama Event 06-36. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2006-07-20
42707 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2006-07-03 | 2006-07-17 14:55 | 2006-07-18 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION USING HIGH DOSE RATE AFTERLOADER On 7/17/06 the State of Maryland received a report from the Anne Arundel Medical Center in Annapolis, Maryland of a potential medical misadministration using a high dose rate afterloader. Approximately two to three weeks ago a patient was administered a dose using a Varian VariSource 200 HDR brachytherapy afterloader to treat a lung tumor. During the dose administration the catheter was determined to be about ten centimeters short of the planned location for the dose. Because of the mispositioning or the catheter, an unintended dose of less than 100 centigray was given to patient's vocal chord area. The lungs received a dose of 5 gray. The licensee notified the patient of the issue. A licensee physician examined the patient today and determined that there was no erythema and that there would be no adverse medical effects in the unintended dose area. The licensee reported that a human error not a device error resulted in the misadministration. The State will be conducting follow-up investigations into this incident to include reviewing the licensee's determination of the cause, as well as, determining why the event was not reported until 2 to 3 weeks after it had occurred. Typically a 10 curie Iridium-192 source is used in this type of instrument. * * * UPDATE AT 1100 EDT ON 07/18/06 FROM RAY MANLEY TO S. SANDIN * * * The patient did not receive a dose of 5 gray to the lungs as described above. This was the prescribed dose. Also, the information is preliminary pending completion of the follow-up investigation. Notified R1DO (Kinneman) and NMSS (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2006-07-20
42706 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-07-14 15:24 | 2006-07-14 15:32 | 2006-07-14 | AGREEMENT STATE REPORT OF RADIOACTIVE MATERIAL SHIPMENT EXCEEDING EXTERNAL RADIATION LIMITS A control rod drive mechanism was shipped to Global Nuclear from Mexico's Laguna Verde Nuclear Power Plant with package external radiation levels exceeding transportation limits. The package arrived at Global Nuclear with a surface radiation level of 245 millirem per hour which exceeds the limit of 200 millirem hour. There was no external contamination on the package and all other aspects of the shipment were within regulatory limits. The shipment was transported by Tri-State Motor Transport as an exclusive use shipment. Although Global Nuclear is an NRC licensee, the activity being performed by Global Nuclear for Laguna Verde is being conducted under its North Carolina State licensee and not under its NRC license. The NC report number for this incident is 06-22. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-07-19
42705 | 0 | CONSTRUCTION ENGINEERING CONSULTANT |  |  |  |  | 2006-07-08 14:00 | 2006-07-14 14:23 | 2006-07-14 | DAMAGED TROXLER MOISTURE DENSITY GAUGE The Radiation Safety Officer (RSO) of Construction Engineering Consultants Inc. called to report a damaged Troxler gauge. The damage occurred on 7/8/06 as a backhoe's bucket bent the handle of the gauge. At the time the gauge was retracted and not actively in-use. The individual at the site called the RSO who retrieved the device. The RSO surveyed the gauge. No leakage was found. The RSO returned the instrument to the storage vault. He resurveyed again later and still could find no leakage. With the damaged handle the gauge cannot function so the RSO is going to send the damage gage to the manufacturer for repair. The gauge is a Troxler Model 3411B, Serial Number 13844. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-07-14
42704 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2006-07-13 18:26 | 2006-07-13 20:08 | 2006-07-13 | OFFSITE NOTIFICATION RELATED TO JELLYFISH INFLUX The licensee was required to secure circulating water pump 26 due to a significant influx of jellyfish. Per the licensee's NPDES (National Pollution Discharge Elimination System) permit, the licensee is required to notify the Maryland Department of Environment of any significant aquatic impact on plant operation. The licensee remained at 100% power throughout. The licensee has not yet restarted the 26 circ water pump pending evaluation of a long term strategy related to the recent jellyfish events. The licensee notified the NRC Resident Inspector. See similar Event Notifications 42699, 42700. and 42702. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-07-13
42703 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2006-07-12 | 2006-07-12 17:33 | 2006-07-13 | LOSS OF OFFSITE POWER AT A DECOMMISSIONED FACILITY The licensee reported a loss of ENS and commercial telephone lines due to a loss of power to the phone switch located offsite from the facility. The call was provided as a courtesy notification and the licensee indicated that cell phone and satellite phone communication were still available. These methods of communication were tested and verified to be working satisfactorily. During the initial notification, it was not made clear to the NRC Operations Center that the facility had lost all offsite power and was operating on backup propane generators. The licensee stated that there were no operability problems onsite and that power was expected to be returned to the phone system within approximately 1 hour. Update calls were placed to the licensee by the Headquarters Operations Officer at 1930 EDT and again at 2200 EDT to determine phone status. At the 2200 EDT call, it became clear that the site had also experienced a loss of offsite power. The loss of power was due to a tree that had fallen on a power line away from the site and that the licensee did not have any information on when it would be restored. The licensee stated that all onsite power requirements were being met by a backup propane generator and all facility systems (other than the phones) were operable. The licensee stated that the loss of offsite power was not reportable and the loss of the ENS and commercial lines was reportable as information only. The licensee still did not have information on when the power would be restored. R1DO (Meyer), NMSS EO (Ruland), R1 (Miller) were provided the updated information on the offsite power loss at the site when this information was clarified by the licensee. * * * RECEIVED AN UPDATE FROM CHRIS POULOS TO JOE O'HARA ON 7/13/06 AT 0155 * * * The licensee reports that power has been restored to the site and both ENS and commercial phones lines are operating properly. R1DO (Meyer), NMSS EO (Ruland), R1 (Miller) notified. * * * UPDATE FROM RALPH COX TO PETE SNYDER ON 7/13/06 AT 1652 * * * The licensee reexamined the circumstances about this event when it was originally reported and decided to reclassify the original event as a 10 CFR 50.72 (b)(3)(xiii) Loss of Communications / Assessment / Response Capability. The heading information of this report was updated to reflect the licensee's reclassification. R1DO (Meyer), NMSS EO (Ruland) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-07-12
42702 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2006-07-12 16:06 | 2006-07-12 17:17 | 2006-07-12 | OFFSITE NOTIFICATION RELATED TO JELLYFISH INFLUX The licensee was required to secure circulating water pump 26 due to a significant influx of jellyfish. Per the licensee's NPDES (National Pollution Discharge Elimination System) permit, the licensee is required to notify the Maryland Department of Environment of any significant aquatic impact on plant operation. The licensee remained at 100% power throughout and has already restarted the secured circ pump. The licensee notified the NRC Resident Inspector. See similar Event Notifications 42699 and 42700. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-07-12
42701 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2006-07-12 07:30 | 2006-07-12 16:37 | 2006-07-12 | ONE SIREN IN EP ZONE IS OUT OF SERVICE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On July 12, 2006 at approximately 07:30 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Department reported siren (#23) out of service. Siren #23 is estimated to impact approximately 119 members of population in the emergency planning zone (EPZ) within 5 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles. This call is being placed due to the relatively large segment of the population affected. During an event, the Palo Verde Emergency Plan has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren 23 being out of service and this ENS call." The total population within the 5 mile EPZ is 2120. | 90 | 100 | 100 | 90 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-07-12
42700 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2006-07-11 09:30 | 2006-07-11 11:28 | 2006-07-11 | 24-HOUR REPORT OF SIGNIFICANT ENVIRONMENTAL EVENT INVOLVING UNUSUAL FISH KILL "Unusual fish kill on both unit's intake trash racks. Approximately 150-200 Cow Nosed Rays died on the intake racks. The apparent cause was low oxygen levels in the bay water. This event is reportable per Tech Spec Appendix 13, Section. 4.1 for significant environmental events. "The licensee contacted the Maryland Department of the environment as a courtesy. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW | [5 empty] | 0 | 2006-07-11
42699 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2006-07-06 16:35 | 2006-07-11 11:28 | 2006-07-11 | OFFSITE NOTIFICATION REQUIRED BY NPDES TO STATE OF MARYLAND DUE TO SIGNIFICANT JELLYFISH INFLUX "On 7/6/06 a significant jelly fish influx required securing 11 Circulating Water Pump on Unit 1 and 26 Circulating Water Pump on Unit 2. Both Units remained at 100 % power, "On 7/7/06 Unit 1 was downpowered to 41 % due to similar jelly fish influx and subsequently returned to 100 % power. NPDES permit requires state notification of any significant aquatic impact on the plant. "NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-07-11
42698 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-07-04 16:05 | 2006-07-10 17:20 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * SAFEGUARDS REPORT Discovered vulnerability in a [DELETED] that could allow access to a [DELETED] for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2008-05-11
42697 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-07-09 21:45 | 2006-07-10 14:11 | 2006-07-13 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The State provided the following information via email: "Received notification on 7-9-06 from Mississippi Emergency Management (MEMA) that a Troxler 3440 moisture/density gauge, Serial # 31576, had been involved in a fire at a residential location. The gauge was chained and locked in its approved DOT transportation container to the bed of the pick-up truck. A neighbor had seen the fire and called 911. Ridgeland Fire Department extinguished the truck fire and secured the area. DRH responded to the incident and removed the melted gauge from the truck bed. Survey readings were taken at the truck after the gauge was removed and determined to be background (9 microR/hr). "DRH responded to the scene and removed the gauge from the bed of the pickup. Gauge was secured in a plastic garbage bag and placed in DRH vehicle. Cesium-137 source rod was shielded with a lead pig. Gauge was brought to DRH office where leak tests were performed and gauge was stored until pick-up by disposal contractor. "Isotopes: Cesium-137 (9 mCi) and Americium-241/Be (40 mCi) "Survey readings were 95 mR/hr near the end of the Cesium-137 source rod. Survey readings of the Americium-241/Be source were 5 mR/hr. Survey readings of the sources in the bed of the DRH vehicle after shielding them were 15 mR/hr. Sources were leak tested by DRH and appear not to be leaking." * * * UPDATE FROM S. SMITH TO W. GOTT AT 1006 ON 7/13/06 * * * Updated to correct units of the background radiation levels and the survey readings. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2006-07-13
42696 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-04-20 | 2006-07-10 09:30 | 2006-07-10 | AGREEMENT STATE REPORT - LOST BRACHYTHERAPY SEED The licensee provided the following information via email: "As a result of a recent routine inspection, the licensee made report on June 12, 2006, of a lost/missing Pd-103 brachytherapy seed originally containing 3.39 millicuries of Pd-103 on April 20, 2004 and discovered lost/missing on the same date (April 20, 2004) "The seed was never found and was believed to have been disposed of as non-radioactive trash within a cartridge on April 20, 2004. The Pd-103 contained in the seed has a short half-life of 17 days. "A nurse handling the cartridge with one remaining seed in the operating room likely disposed of the cartridge and seed into non-radioactive trash. The licensee concluded that such disposal of the single seed contained in the cartridge would not generate any noticeable radiation exposure to the general public. "The licensee provided additional training to nurses who handle cartridges in the operating room." Report number 06-6414 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-07-13
42695 | 0 | READING SITE CONTRACTORS |  |  |  |  | 2006-07-10 09:41 | 2006-07-10 10:23 | 2006-07-10 | DAMAGED MOISTURE DENSITY GAUGE A Troxler Model 4640B moisture density gauge was damaged when it was run over by an asphalt roller at a construction site located approximately 150 feet south of the intersection of Route 10 (Morgantown Road) and Upland Avenue in Reading, PA. A perimeter has been established around the gauge and the licensee's RSO has been notified and is enroute to the site. The gauge contains a Cs-137 source with a 8 millicurie activity level. Subsequent discussions with a Berks County Emergency Management official indicates that radiation levels are normal and that the source is intact inside the gauge. Berks County Emergency Management is awaiting authorization from PEMA to remove the gauge from the earth and perform surveys underneath the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2006-07-10
42694 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-07-08 05:00 | 2006-07-08 22:00 | 2006-07-10 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via fax: "Licensee: APAC Atlantic, Inc, Asheville Division / Hickory Branch "Event Date &Time: 08 July 2006 between 02:00 and 05:00 am "Report Date & Time: 08 July 2006, 15:00 "Event Location: Hickory, NC "Event Type: Stolen Portable Nuclear Gauge "Notifications: The following organizations have been notified, the FBI, the N.C Highway Patrol, Iredale County Sheriff, N.C. Division of Emergency Management. "Event Description: N.C. Radiation Protection Section was notified on 08 July 2006 by the designee RSO for APAC Atlantic, Inc Asheville Division / Hickory Branch of the theft of a Troxler Electronics Model 4640 B portable moisture density gauge (Serial No. 765). The gauge contained one sealed source: Cesium-137, 9 millicuries. "The device was stored in a locked steel transport box attached to the bed of a White 2006 Dodge Dakota, license plate no. VV2525, with 'APAC' signage on the doors. In addition to being locked in the steel over-pack, the gauge is locked in the required transportation container and the operating mechanism is locked. However, keys to all three locks are in the truck. The truck was stolen in the early morning hours from the licensee's gated and locked facility. "The Radiation Protection Section is working with the licensee and local law enforcement to recover the gauge. "Media Attention: N.C. Radiation Protection has not received any media attention as of this report. A potential news release is pending." NC Incident No. 06-20. * * * UPDATE AT 0415 ON 07/10/06 FROM LEE COX TO W. GOTT * * * In the evening of 07/09/06 the abandoned gauge was found undamaged and in its case in a parking lot in Hickory NC. The source rod was still locked in the stowed position. Notified R1DO (P. Henderson), NMSS EO (Brach) and emailed to ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-07-12
42693 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-07-08 09:18 | 2006-07-08 09:22 | 2006-07-11 | OFFSITE NOTIFICATION - EXCEEDED LIMIT FOR SUSPENDED SOLIDS IN DISCHARGE "On 6/29/06 at 1630 Neutralization Basin A was pumped to Lake Erie. On 7/7/06 the analysis of suspended solids for this discharge was completed with results outside of the daily limit. Results for the suspended solids for the basin discharge was 142 ppm with a limit of 100 ppm. State of Ohio EPA was notified for this non-compliance. This 4 hour notification is being made due to the notification to the State of Ohio EPA. Notification to the Ohio EPA was made at 0918 on 7/08/06. Specific. Reporting details required by Part 12.A are as follows: "Discharge occurred- 6/29/06 at 16:30; Discovered 7/7/06 at 14:38 (analysis reported by First Energy Beta Drive Lab) Approximate amount 18,300 gallons; 7.94 Ph; 142 ppm Total Suspended Solids [backup sample 148 ppm]" The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1007 EDT ON 7/11/06 FROM JIM CASE TO S. SANDIN * * * "This 4 hour notification is being made due to the additional notification to the State of Ohio EPA. "This was follow-up information regarding event number 42693 ('Offsite Notification - exceeded limit for suspended solids in discharge'). On 7/10/06 final data analysis for NPDES Monthly Report was obtained and the 6/29/06 exceedance resulted in an exceedance in the monthly average of total suspended solids (TSS). Results for monthly average suspended solids were 44.2 ppm with a limit of 30 ppm. State of Ohio EPA was notified of this non-compliance at 0925 on 7/11/06." The licensee informed the NRC Resident Inspector. Notified R3DO (Steve Orth). | 66 | 0 | 0 | 66 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-07-08
42692 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-07-07 17:00 | 2006-07-07 19:56 | 2006-07-07 | AUXILIARY FEEDWATER PUMP RECIRCULATION VALVE INOPERABLE "At 1700 CDT, Fort Calhoun Station determined that one of the two safety related auxiliary feedwater pumps may not provide sufficient flow to the steam generators during certain design basis events. The circuitry for the minimum flow recirculation valve for the electric motor driven auxiliary feedwater pump contains some components which were not designed as critical quality components. Since these components are not critical quality components, they are assumed to fail in a manner such that the minimum flow recirculation valve would fail open during a design basis event. If this valve should fail open, flow to the steam generators from the electric motor driven auxiliary feedwater pump may not provide adequate flow to cool the steam generators. The station has entered the appropriate technical specification action statement which requires the plant to be in Mode 2 (hot standby) within 30 hours of declaring the pump inoperable. The electric motor driven auxiliary feedwater pump was declared inoperable at 1700 CDT today." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-07-07
42691 | 0 | SOUTHEAST MISSOURI STATE UNIVERSITY |  |  |  |  | 2006-07-07 10:00 | 2006-07-07 16:31 | 2006-07-07 | DISCOVERY OF ADDITIONAL CONTAMINATION ASSOCIATED WITH AM-241 SPILL At 1000 CDT on 7/7/06, additional Am-241 contamination was discovered in Magill Hall Room 215. An area of approximately 10-12 sq. ft. was identified having gross contamination levels of approximately 10 nanocuries with 0.05 nanocuries removable (alpha emitters) underneath cabinets being moved . The room has been posted as a contaminated area with access controls in place. A Radiation Work Permit will address decontamination on Monday morning, 7/10. A cabinet was taken from Room 215 by two (2) movers and loaded onto a truck. A radiation survey found contamination on the truck lift gate and the truck bed which have been decontaminated. The truck will be rechecked for contamination before being released. The source of the contamination is an Am-241 spill referenced in previous Event Notifications #'s 37282 and 37298. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2006-07-07
42690 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-07-07 14:45 | 2006-07-07 15:43 | 2006-07-07 | ALTERNATIVE REPORT FOR NON-DECLARED EMERGENCY CONDITION IN ACCORDANCE WITH NUREG-1022 "On July 7, 2006, at 1445 hours with Watts Bar Unit 1 at 100% power, operations were underway to prepare to sluice resin to the spent resin storage tank. Due to a suspected valve alignment anomaly, approximately 60 gpm from the CVCS volume control tank transferred thru the cation vessel to the tritiated drain collector tank. This is considered identified leakage in accordance with EAL 2.6 RCS Leakage greater than 25 gpm. "This condition was immediately corrected within about 3.5 minutes but could have met the conditions for a NOUE had the event continued. Accordingly a NOUE was not declared, but this NRC ENS notification is being made in accordance with NUREG-1022 as an acceptable alternative to the immediate notification requirement of 50.72(a)(1)(i)." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2006-07-07
42689 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-06-18 04:40 | 2006-07-07 15:43 | 2006-07-07 | AGREEMENT STATE - MISPLACED SOURCE "At 0634 hrs on June 20, 2006, [the Director of the Texas Department of Health] received a call on the way to the office from the Director of Radiology for Ben Taub General Hospital in Houston, TX. He relayed brief details of a recovered source that was either taken out of a patient or never placed in an after loading appliance utilized for the treatment of a cervical cancer patient. In the words of the Radiation Safety Officer with proper names redacted: "On Sunday, June 18, 2006 at 4:40 am a Cesium-137 source, 3M model 6501(6D6C-CA), serial # 06965, with an activity of approximately 17 mCi [milliCuries] was noted to be missing from a patient who was undergoing a tandem and ovoid implant for cervical cancer. The patient had applicator placement (uterine tandem and two Fletcher ovoids) at Ben Taub General Hospital (BTGH), on Friday 6/16/2006. The Cesium sources (4 in all; 2 in the tandem and 1 each in the ovoid) had been placed in the patient by the Radiation Oncologist at 3:40 pm for a 37 hour implant. When the right ovoid source was noted to be missing at the time of unloading; the patient, room, Nursing Unit 6B of the hospital, and the route of transport of the sources from the BTGH Radiotherapy Department to the patient's room were surveyed using both a sodium iodide detector and a conventional air-ionization type survey meter by both the Radiation Oncologist and Medical Physicist. The BTGH Radiation Safety Officer was notified at 8:20 am Sunday morning of the apparent missing source. Upon further investigation, it was learned that the bed sheets of the patient had been changed at 3 pm on Saturday, 6/17/2006, and this dirty linen was placed in the linen cart on 6B. It was subsequently taken to a truck at the BTGH loading dock and transported to the Texas Medical Center Laundry facility. On Monday morning, 6/19/06, the director of this facility was contacted and subsequently the facility was surveyed. The Cs-137 source was recovered at 10:30 a.m., from the third floor and transported back to the BTGH Radiotherapy Department using an appropriately shielded container. "The names of all the persons who potentially may have come into contact with the Cesium source were obtained and notified. This list included thirty-five [35] individuals of both hospital and laundry services personnel. "Upon further review by staff in assembling the documents for the incident file, the attachments to the June 26, 2006 e-mail was examined at 1400hrs on July 7, 2006. At that time DSHS staff realized that this was a lost/found source with quantities >1,000 X Appendix C value requiring immediate reporting to NMED. However, staff reviewed the operational setting and in the absence of the licensee's report demonstrating an exposure exceeding of 100mrem to a member of the public, the incident may not be reportable. Further investigation is on-going." Texas Incident: I-8350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-07-12
42688 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-06-12 | 2006-07-06 15:15 | 2006-07-06 | AGREEMENT STATE - RADIOGRAPHY SOURCE DISCONNECTED FROM CAMERA The State provided the following information via facsimile: "Global X-Ray had a source disconnect at the McDermott Fabrication Facility in Amelia, LA on June 12, 2006. The radiographers were performing routine radiography on some welded pipe sections. After several exposures, the radiographers began having trouble with the crankout. The radiographers realized that the source had not come back to the shielded position at the end of the exposure. The radiographers followed Global X-Ray & Testing Operating and Emergency Procedures. The radiographers reset their boundaries to a 2 mR/hr level and maintained surveillance and called the office. The source was found in the source guide tube. The source was retrieved and returned to the exposure device with minimal exposure during retrieval. Both the exposure device and controls were sent to SPEC for evaluation. It appears that there was enough wear on the control adapter and the drive cable connector to allow a disconnect. Global ruled out a source misconnect being the problem due to the fact that the film that was exposed prior to the crank out trouble was developed and came out just as it should. There were no excessive exposures to the radiographers. The radiographers dosimeters read 10-12 mR and 35-40 mR. The retrieval process produced an exposure of 85 mR. The device that was involved with the disconnect is a SPEC 150 camera with serial number 139. The source in the camera was an 82 Ci [Curie] source of Ir-192 manufactured by SPEC with model number G-60 and serial number ND-1002." LA Event Report Number: LA060012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-07-11
42687 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2006-07-06 03:52 | 2006-07-06 04:25 | 2006-07-06 | REACTOR TRIP DUE TO GENERATOR DIFFERENTIAL "Indian Point Unit 3 tripped on Generator Differential (Direct Generator Trip). Current conditions are stable, mode 3 operation with all automatic actions occurring properly. Steam Generators levels are stable on aux. feed water. "Unit 2 was unaffected by the trip." All control rods inserted fully and decay heat is being removed via steam dump to the condenser. All required safety related systems are working properly and the electrical buses and diesel generators are in their normal alignment. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 0938 ON 07/06/08 B. ROKES TO W. GOTT * * * "The Auxiliary Feedwater System actuated and the Auxiliary Feedwater Pump started as designed due to the reactor trip. The actuation of the Auxiliary Feedwater System was the result of Steam Generator shrink/swell effect due to the reactor trip at full power. The actuation of the Auxiliary Feedwater System is an eight-hour non-emergency event reportable under 10 CFR 50.72(b)(3)(iv)." The licensee will notify the NRC Resident Inspector. Notified R1DO (P. Henderson) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-07-06
42686 | 0 | ADVANTAGE ENGINEERING |  |  |  |  | 2006-07-01 14:20 | 2006-07-05 15:12 | 2006-07-05 | DAMAGED MOISTURE DENSITY GAUGE A Troxler Model 3411 moisture density gauge was damaged when it was run over by a bulldozer at the Rydal-Waters construction site on Brooke Road in Abington Township, Montgomery County, PA. The gauge was left unattended and uncontrolled while the gauge operator went to retrieve a vehicle to transport the gauge. While left unattended, the gauge was run over by a bulldozer resulting in the gauge being broken and the instrument case being damaged. The sources remained in place in their rods. The rods were placed back inside the gauge, and the gauge was placed back inside its case. Soil surveys resulted in no spread of contamination. Radiation levels taken were not abnormal. There are two sealed sources inside the gauge Cs-137, serial number 40-8387, 5.4 millicuries and Am-241/Be, serial number 47-6341, 38.8 millicuries. The licensee notified NRC (Sattar Lodhi, Region I ), Troxler, and local authorities: Abington Township Emergency Responders and Montgomery County Emergency Management. The gauge has been removed from the Rydal-Waters site to Advantage Engineering's Allentown, PA. office. Troxler is leak testing the gauge and evaluating a transportation plan to return the gauge to Troxler's corporate location. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2006-07-05
42685 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2006-07-04 02:59 | 2006-07-04 05:21 | 2006-07-04 | REACTOR SCRAM ON GROUP 1 ISOLATION "On 7/04/06 at approximately 0259, Unit 2 received a Group 1 isolation on Main Steam Line High Flow. All Group 1 valves closed as required and the reactor scrammed. The Isolation Condenser was manually initiated to control reactor pressure. Group 2 and 3 Containment Isolations occurred as expected. Investigation into the cause of the Group 1 isolation is in progress. All systems responded as required with no abnormalities noted." All rods fully inserted. Water level is being maintained with normal feed and reactor heat removal and pressure control is being controlled via the isolation condenser within normal range. The licensee was in no significant tech spec LCO at the time of the event and all safety related equipment was available if needed. The scram had no impact on Unit 3 operation. The licensee stated that there was no evidence of any main steam system leak or actual condition that could account for the main steam high flow signal. The licensee notified the NRC Resident Inspector. The licensee also notified the State Inspector. | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-07-04
42684 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2006-06-30 19:49 | 2006-07-03 16:23 | 2006-07-03 | 24 HOUR LICENSE CONDITION REPORT - MAIN STEAM ISOLATION VALVE INOPERABLE GREATER THAN 4 HOURS "FPL Energy Seabrook has discovered a condition that was prohibited by the Technical Specifications. This report is being made pursuant to License Condition 2.G of the Seabrook Station Operating License. "On July 3 at 0615, it was determined that a MSIV had been inoperable for a period of time longer than allowed by the Technical Specifications. On June 30 at 1949, an alarm was received indicating a problem with the MSIV. A troubleshooting and repair plan was developed and the MSIV repaired on July 1 at 1559. "Subsequent examination of the failed control module found that it was nonfunctional and that the MSIV had been inoperable since receipt of the alarm on June 30 at 1949. Since the Technical Specification allowed outage time for an inoperable MSVI is 4 hours, the MSIV being inoperable for approximately 20 hours constitutes a violation of the Technical Specifications. "The Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2006-07-03
42683 | 0 | ST JOSEPH HEALTH CENTER |  |  |  |  | 2006-06-28 13:30 | 2006-07-03 15:32 | 2006-07-03 | MEDICAL MISADMINISTRATION FOR THYROID TREATMENT A female patient went to the St Joseph Health Center for medical treatment on her thyroid. The treatment prescribed for this patient was 15 microCuries I-131 uptake, and 5 milliCuries I-131 therapy. The technician did not follow procedure and administered only the 5 milliCuries I-131 therapy dose. The 15 microCuries I-131 uptake dose was not administered. The licensee talked to the patient and her physician about the misadministration and the doctor said he will evaluate the patient to see if any more thyroid treatments are required. This misadministration did not physically harm the patient. The RSO was notified and will be following up with a written report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-07-03
42682 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2006-03-08 | 2006-07-03 10:30 | 2006-07-03 | RADIOGRAPHY SOURCE PIGTAIL DISCONNECTED FROM DRIVE CABLE On the evening of March 8, 2006, while performing radiography at an Alpine Oilfield, North Slope Alaska location, Kakivik Asset Management had a source pigtail disconnect from its drive cable on its radiography camera (INC Model IR100 #6621 using an Iridium-192 source). The disconnect occurred after a series of approximately 30 exposures where taken. There where no overexposures. The exposure device (with source) was sent to the manufacturer for an evaluation and disposal. The connector on the drive cable was removed and replaced with a new one. After an examination of the connection by both the RSO and the manufacturer, there appeared to be no obvious conclusion as to why it failed to stay connected. The licensee issued a detailed 30 day report of the incident under 10 CFR 34.101 to Region 4 on April 11, 2006. However, a 24 hour notification under 10 CFR 30.50 to the NRC Headquarter's Operations Center was never made. This report constitutes the licensee's telephone notification of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-07-03
42681 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2006-07-01 19:28 | 2006-07-02 01:23 | 2006-07-02 | MANUAL REACTOR TRIP FOLLOWING LARGE LEAK IN CONDENSATE SYSTEM "On July 1, 2006, at approximately 19:28 MST Palo Verde Unit 3 experienced a manual reactor trip from approximately 100% rated thermal power due to a large leak in the condensate system. The sight glass for the 'A' condensate demin vessel blew out of the vessel creating an approximate 6 inch diameter hole. Several thousand gallons of condensate were discharged to the Turbine Building and the environment. Radiation Protection has sampled the condensate water and have verified no activity is present. Unit 3 was at normal operating temperature and pressure prior to the trip. The 'A' Main feedwater pump tripped on low suction pressure and a Reactor Power Cutback Signal was received. Condenser hotwell levels continued to decrease. When the main control board annunciator for the 'B' Main Feedwater Pump Trip Circuit Energized was received the reactor was manually tripped. All CEAs fully inserted into the reactor core. The event was diagnosed as an uncomplicated reactor trip. No ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. There was no loss of normal heat removal capabilities, or loss of any safety functions associated with this event. No major equipment was inoperable prior to the event that contributed to the event. No primary or secondary safety valves lifted during the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "Unit 3 is stable at normal operating temperature and pressure in Mode 3. There is no estimated time and date for the Unit 3 restart at the time this call is being made." AFW is being used to feed the steam generators and is discharging steam to the main condenser. The licensee stated that the leak has been secured and that there is no significant standing water in the turbine building lower levels. All the water has drained into sumps or out doors. There does not appear to be any electrical or personnel safety hazards as a result of the water leak. The licensee notified the NRC Resident Inspector. *** UPDATE FROM RAY BUZZARD TO JOHN KNOKE AT 17:28 ON 07/03/06 *** "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This notification is a follow-up to the manually initiated reactor trip event reported on July 1, 2006 (ENS 42681). The notification indicated that the reactor was manually tripped from approximately 100% rated thermal power due to a large leak in the condensate system. Prior to the transient the unit was operating at approximately 100 % rated thermal power, however, the manual trip was actually initiated from approximately 55% rated thermal power following a reactor power cutback caused by the loss of the A train main feedwater pump on low suction pressure. "In addition, the ENS report stated that Radiation Protection had sampled the condensate water and verified no activity is present. The condensate actually was found to contain tritium at a concentration of 1.22E-5 uCi/ml. The water from the spill flowed to the onsite storm drains, was captured behind dams, and transferred to the onsite retention basins. Samples of resin from the spill were also collected, analyzed by gamma spectroscopy, and found to not contain licensed radioactive material." The licensee notified the NRC Resident Inspector. Notified R4DO (Shannon) | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-07-02
42680 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2006-06-30 23:37 | 2006-07-01 01:39 | 2006-07-01 | COMMON CAUSE DEGRADATION TO RHR SERVICE WATER PUMP MOTOR COOLING COILS "At 2337 of 06/30/2006, it was determined that 3 out of 4 Residual Heat Removal Service Water (RHRSW) pumps were inoperable due to a common cause. Each of the 3 affected RHRSW pumps contained motor cooling coils that had experienced flow induced erosion which had significantly reduced the wall thickness of the cooling coil material. In some cases, the thinning was sufficient to cause through wall leakage of water into the upper motor bearing oil reservoir and subsequently displace oil out of the reservoir. Currently, 2 of the 3 affected RHRSW pumps have been removed from service for repairs. 1 of those pumps is expected to be returned to service shortly. The 3rd affected pump remains available for use, but has been conservatively declared inoperable based on Engineering evaluation that indicates a common cause failure mechanism likely exists, based on common fabrication methods used for all RHRSW pump motor cooling coils. The 4th (unaffected) RHRSW pump remains Operable because its cooling coil was replaced approximately 1 month ago. Under these conditions, sufficient confidence that the affected RHRSW pumps could perform their post LOCA mission does not exist. With only 1 of the 4 RHRSW pumps remaining Operable, the RHRSW System is not capable of performing its safety function. This event is reportable under 10CFR50.72(b)(3)(v)(B) and 50.73(a)(2)(v)(B)." With 3 out of the 4 RHRSW pumps considered inoperable, the licensee is currently in an 8 hour Tech Spec LCO action statement. However, with expected the return of one of these pumps to operable status within the next hour, the LCO will convert to a 7 day action statement. The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-07-01
42679 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2006-06-30 15:00 | 2006-06-30 22:22 | 2006-06-30 | AGREEMENT STATE REPORT - LOSS OF SEVEN Pd-103 PROSTATE IMPLANT SEEDS "At 1853 hrs CST on June 30, 2006, University of Minnesota Medical Center, Fairview Riverside Hospital notified the Minnesota Department of Health that seven Palladium-103 seeds had been lost. "At approximately 1500 hrs on June 30, 2005, the licensee completed a seed implant for prostate cancer. At the completion of that procedure, a scrub tech removed the tray from the area. The physicist reported 39 unused seeds ten of which were most probably on a partially used ribbon. (The licensee was using a MIC applicator.) When the nuclear medicine technologist inventoried the sources, only 29 were present. The facility located two seeds in a sink and a third in the drain of that sink. The Radiation Safety Officer believes that the seven lost sources are in the sewer system. "Each seed is 1.2 mCi of Palladium-103." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2006-07-05
42678 | 0 | THERMO ELECTRON CORPORATION |  |  |  |  | 2006-06-30 | 2006-06-30 22:13 | 2006-07-03 | PART 21 - DEFECTIVE PAPERLESS DATA ACQUISATION RECORDERS "On May 3, 2006, Progress Energy (CP&L) Brunswick Nuclear Plant notified Thermo Electron that, during preventive maintenance on a Safety Related CSVC recorder, the rechargeable backup battery was found to have separated. Progress Energy also indicated that a similar failure had been found on a Non-Safety Related recorder prior to this incident. Neither recorder had failed while in service. Both are believed to have been in service approximately six (6) years with the original backup batteries installed. "Progress Energy requested that Thermo Electron evaluate the failures to determine a recommended course of action and determine whether or not a Part 21 Notification was appropriate. Thermo Electron organized an engineering team to immediately begin an investigation of the failures. Thermo engineers solicited the services of the battery manufacturer in their investigation. "The backup battery installed on the CSVC is a NiCad sealed package. As the batteries age, the potential exists whereby if the batteries were fully discharged, which could occur during an outage or a shut down condition, a reverse charging situation may occur when the recorders are brought back on-line. If a reverse charging condition occur, the byproduct is hydrogen gas which could be sufficient to cause the battery to split open. This is not a normal condition, but could occur in batteries that have been in service for a number of years. There is no apparent hazardous condition within the recorder as a result of this failure and the recorder would continue to function properly while under power. "There have been no failures reported in any nuclear safety-related application of CSVC recorders while in operating mode. Should the battery fail, it will not cause the recorder to present or record any erroneous data. However, should a recorder lose power after such a battery failure has occurred, the system configuration would be lost. "Corrective Action : Thermo Electron has determined that a recommended replacement interval for the rechargeable battery should be documented to prevent the potential for this condition to occur in the future. The battery packs as originally installed on the CSVC are no longer available. A replacement has been identified which has been tested and verified to be suitable for the backup battery application. This replacement does not compromise the original qualifications of the CSVC recorder. The battery pack (Thermo Part Number 1063-0200-001, Revision A) should be available for purchase within thirty (30) days. Thermo Electron recommends that utilities with CSVC recorders that have been in service greater than three (3) years with original batteries installed consider replacing the batteries at the next maintenance interval. The recommended replacement cycle for the replacement battery pack shall be three (3) years from the date the recorder is placed in service or the battery was replaced. "Utilities have the option of purchasing batteries for replacement at their facility or returning the CSVC recorders to Thermo Electron for battery replacement. Customers may contact Thermo Electron for spare parts or to request return for service." * * * UPDATED BY SNYDER ON 7/03/06 * * * Updated to correct typographical errors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0 | 2006-06-30
42677 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-06-30 15:18 | 2006-06-30 17:55 | 2006-06-30 | NON-CREDIBLE SECURITY THREAT MADE AGAINST PLANT "Notified by Security Shift Supervisor of a report by the Ashtabula County Sheriff that a 92 year old individual has been checked into the Ashtabula Clinic at 14:57 EDT, claiming to have an explosive device at his Kingsville home and at the Perry Power Plant. This is being considered as a non-credible security threat, based on his never having access to the site, ONI-P56-2 is not applicable, based on this report and assessment. Law enforcement officers are obtaining a warrant to access his home to investigate. The FBI and Lake County Sheriff's offices have been notified by the Security Shift Supervisor. This is an off site report from the Perry Plant to a government agency about the status of the Perry Plant." The Lake County Sheriff's office completed their search of individual's residence and found no bombs or related material. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-30
42676 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-06-30 13:00 | 2006-06-30 14:59 | 2006-06-30 | LOW LEVELS OF TRITIUM FOUND ALONG PLANT DISCHARGE LINE "This report is being made pursuant to 10CFR50.72(b)(2)(xi), 4-hour Non-Emergency Report due to a press release being issued by Callaway Plant reporting that its monitoring program recently detected small amounts of tritium and other radionuclides along the plant discharge pipeline. The concentrations of radioactive material in water sampled from manholes on the discharge line range from less than 1% to about 20% of the NRC effluent release concentration limits. This radioactive material is contained on plant owned property. "All known wells in the vicinity of the plant, as well as drinking water at the plant and in the nearby town of Portland, have been tested and shown to have no detectable radionuclides above background. Further testing of drinking water supplies and in areas around the discharge line is taking place to assure that no migration of the contaminated water occurs. Sampling results of the monitoring program have been provided to the NRC and the Missouri Department of Natural Resources (DNR) and a plan to remediate the contaminated manholes will be coordinated with the DNR. "No Offsite Dose Calculation Manual (ODCM) and no federal effluent limits have been exceeded. Callaway Plant has not identified any health or safety risk to the public or onsite personnel. The DNR, Missouri Department of Health and Social Services, and local County Officials have been notified of the press release." The licensee notified the NRC Resident Inspector, and other State and local agencies are being notified via the press release. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-30
42675 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2006-06-29 20:30 | 2006-06-30 14:18 | 2006-06-30 | MAXIMUM POWER LEVEL EXCEEDED AS ALLOWED BY OPERATING LICENSE "On Thursday, June 29, 2006, at approximately 20:30 the Engineering Department notified the Plant Management that St. Lucie Unit 2 had exceeded the maximum power level allowed by the facility's Operating License (License Condition 3.A). The overpower condition was determined to be approximately 0.5%. This equates to 13.5 MWth reactor core power above the Rated Thermal Power Limit of 2700 MWth. Preliminary data indicates that the overpower condition could have been present between June 20, 2006 and June 29, 2006. This telephone notification is made in accordance with Renewed Facility Operating License No. NPF-16, License Condition 3.H. A written follow-up report will be submitted within 14 days. "A Distributed Control System (DCS) software error was responsible for the overpower condition. The DCS calculated a slightly lower feedwater flow value which was used as input into the calorimetric power calculation. The error resulted in a non-conservative indicated power in the control room. "When the feedwater flow calculation error was identified, it was apparent that an overpower condition may have occurred. Therefore, a controlled power reduction to approximately 98% was performed in accordance with plant procedures. St. Lucie Unit 2 will remain at a reduced power level until the software error is corrected. The software error is understood and is in the process of being resolved within the corrective action process. An extent of condition review has determined that St. Lucie Unit 1 does not have the same problem." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2006-06-30
42674 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2006-06-30 08:19 | 2006-06-30 09:43 | 2006-06-30 | MAIN STEAM ISOLATION VALVE STUCK DURING TESTING "[On June 30, 2006 the licensee initiated] a plant shutdown required by Technical Specifications. [The licensee] discovered during surveillance testing, that the Unit 1 Main Steam Isolation Valve (MSIV-3370B) for the B-loop, would not return to the fully open condition after the partial stroke test. The valve appeared to stroke smoothly to the test position. Trouble shooting of the condition has not determined the exact cause however it appears that there is possible binding." The licensee has tried reasonable methods to free the valve but was unable to do so. The licensee declared the MSIV inoperable. The plant's Technical Specifications require a shutdown within 72 hours with one MSIV inoperable. The licensee has no other safety significant limiting conditions for operation in effect. The safety related electrical buses are powered from offsite power and the grid is stable in the area. The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-06-30
42673 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-05-24 18:25 | 2006-06-29 08:41 | 2006-06-29 | LA AGREEMENT STATE REPORT - DISCONNECTED RADIOGRAPHY SOURCE The State provided the following information via facsimile: "Incident: A Metco crew was working at the PPG facility [Lake Charles, LA] the evening of May 24, 2006, when they reported a disconnected source [to the LA Department of Environmental Quality on May 26, 2006]. "Timeline of events: "1. 6:25 pm - Crew set up to make three exposures in PPG at the area known as the loading dock. "2. 6:45 pm - Crew makes their first exposure. "3. 6:48 pm - The crew retracts the source but the camera does not lock and the survey meter is still giving high readings. "4. 6:50 pm - [Worker 1] and [Worker 2] were notified of the disconnect. "5. 7:05 pm - [Worker 1] and [Worker 2] meet at the Metco shop and leave to go to PPG facility. "6. 7:13 pm - [Worker 1] and [Worker 2] arrive at PPG. "7. 7:20 pm - The source is retrieved. "8. 7:21 pm - The camera and equipment were examined to see where the malfunction occurred and the investigation began. "Investigation: After further review of the incident, it was determined that the source was never connected to the drive cable before making an exposure. The crew had performed only one shot when they realized the source did not retract fully. "Key Points: "1. A perimeter of 150' was maintained after the disconnect occurred. This was inside of a building that had 1.5' concrete walls. "2. The barrier was kept at 2 mrem/hr after the disconnect occurred. "3. The source remained in the collimator and laid facing the floor until [Worker 1] and [Worker 2] arrived onsite. "4. None of the radiographers present on site received a dose of more than 15 mrem. "5. [Worker 1], who performed the source retrieval, received a total dose of 365 mrem." Exposure Device Manufacturer: Amersham Model No.880 Sigma S/N S1712 Isotope: Ir-192 Source Activity: 91 Ci LA Report ID No.LA060013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-07-04
42672 | 0 | WATERFORD | 3 |  |  | [3] CE | 2006-06-28 14:15 | 2006-06-28 20:11 | 2006-06-28 | LOSS AND SUBSEQUENT RESTORATION OF ELECTRICAL POWER TO THE EMERGENCY OPERATIONS FACILITY "On June 28, 2006 at approximately 1415 [CDT], power was lost to the Waterford 3 SES Emergency Operations Facility (EOF) when a tree fell onto the power line feeding the EOF. Power was automatically restored to the EOF from the EOF backup diesel generator. Several minutes later, power was lost to the EOF again when the EOF backup diesel tripped. [Normal] power was restored to the facility at approximately 1550, and the EOF is operable. The backup EOF facility was available during this event. The NRC Senior Resident has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-06-28
42671 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2006-06-27 | 2006-06-28 17:54 | 2006-06-28 | NEVADA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via email: "Event Report ID No. NV-006-04 "License name, address, license No.: Acclaim Material Testing and Inspection, 720 Susanna Way, Henderson, Nevada; License No. 00-11-0470-01 [phone number deleted] " Date and time of occurrence June 7, 2006, approx. 6:30 pm [Determined by review of secured storage room card reader access records] "Date notified of event by licensee or non-licensee: June 28, 2006, 2:30 pm. The missing gauge was discovered during a routine radiation safety audit by the Radiological Health Section on June 27, 2006. "Radionuclide, activity: Cs-137, approximately 10 mCi; Am-241:Be, 50 mCi "Any exposures (indicate short and long-term effects): None known "Sealed source, device, etc. (make, model #, serial #): Campbell Pacific Nuclear Model MCDRP s/n MD60108156 "Leak test information, If applicable: unknown "Persons involved, consequences: [name deleted] . "Cause and contributing factors: Gauge was removed from its permanent storage site. It appears that the gauge was properly secured. " Licensee corrective actions: Unknown at this point "Notifications: Local Law enforcement. " Enforcement Actions. None contemplated pending licensee's final report." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2006-07-03
42670 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2006-06-27 11:30 | 2006-06-28 10:40 | 2006-06-28 | SC AGREEMENT STATE REPORT - SHEARED END OF Pd-103 SEED The State provided the following information via facsimile: "The SC Department of Health and Environmental Control was notified on Tuesday, June 27, 2006, at 5:18 p.m., that a Pd-103 [1.33 mCi] seed had jammed in a Mick applicator at 11:30 a.m., on June 27, 2006. Medical Physicist [Name Deleted] stated that the Mick cartridge was unscrewed to release spring pressure, which subsequently sheared the end of the seed off. The cartridge was removed and placed in a lead container, the applicator was flushed out and the seed was placed in a lead container. All remaining seeds were then placed in a shielded container and the implant was completed. [The Medical Physicist] stated that the area was surveyed with a Ludlum Model 3A utilizing a scintillation probe. One towel and water drained in a basin indicated contamination. These items were bagged and taken to the hot lab for decay in storage. "[The Medical Physicist] was advised by Mark L. Windham to submit a written report detailing this event to the Department within 30 days. The event is considered closed and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system." SC Report ID No.SC060009 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2006-07-03
42669 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2006-06-05 | 2006-06-27 09:57 | 2006-06-27 | IRON DISCHARGE ABOVE NPDES LIMIT "A discharge to the canal on June 5, 2006 had an Iron result above the NPDES limit. A sample of the discharge was analyzed on site using a non-approved method, which showed the result was well below the NPDES limit. Off-site lab results were received on June 16, 2006, which showed the Iron was above the NPDES limit, 650 ppb. The lab results were re-analyzed and the re-analysis on June 22, 2006 verified it was above the permitted limit. In the past, the onsite testing were comparable to the offsite lab tests." The lab results were 720 and 950 ppb. This information was transmitted to the Department of Environmental Protection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-27
42668 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-06-27 04:33 | 2006-06-27 07:16 | 2006-06-27 | LOSS OF ENS COMMUNICATIONS WITH THE SITE "At 0433, NRC notified Hatch that ENS phone line was out of service. Additionally, Baxley commercial phone lines are out of service. "Vidalia commercial phone line and ENN were confirmed to be in service. "Southern Company Information Resources were contacted and have initiated repair activities." The failure was determined to be a broken fiber optic cable. A test at 0716 confirmed the circuit had returned to operation. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-06-27
42667 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2006-06-26 12:30 | 2006-06-26 17:48 | 2006-06-26 | MINNESOTA AGREEMENT STATE REPORT - ANALYZER MISSING IN TRANSIT On 06/26/06 at 1230 CDT, the State was notified that a package shipped by Dayton's Bluff Neighborhood Services arrived empty at Thermo Electron, Corp. in Billerica, MA. The package was shipped on 06/23/06 and was scheduled for delivery on 06/26/06. When shipped, the package contained a NITON X-ray Florescent Paint Analyzer containing a 3.0 milliCurie Cd-109 source which was being returned to Thermo Electron for source replenishment. Thermo Electron and the RSO at FedEx were notified and it was determined that the analyzer must have come out of the package at some point during shipment. FedEx is currently searching for the analyzer (FedEx Tracking No. 854260375661) . * * * UPDATE PROVIDED BY MR. JOHNS TO JEFF ROTTON AT 2107 EDT ON 06/26/06 * * * FedEx RSO notified licensee at 1950 CDT on 06/26/06 that the analyzer was found at the Indianapolis FedEx facility and will be shipped to Thermo Electron, Corp. tomorrow. It was reported by FedEx that there was no damage to the analyzer. Notified R3DO (Madera) and NMSS EO (Flanders) Emailed update to ILTAB and Canada CNSC. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2006-06-29
42666 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-06-26 13:35 | 2006-06-26 14:05 | 2006-07-27 | SAFEGUARDS REPORT "Control Room informed of vulnerability in a safeguard system. Compensatory measures have been taken. Call the Headquarters Operations Officer for additional details." Related event: EN # 42663 At the time of the report all functions had been fully restored. The licensee notified the NRC Resident Inspector and the PA State Police. * * * RETRACTION AT 09:58 ON 7/27/2006 FROM TOM ILIADIS TO ABRAMOVITZ * * * The licensee has determined that this event did not meet the reporting criteria. Contact the Headquarters Operations Officer for additional details. Notified the R1DO (Gray) and the 73.71 group (via E-mail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | SAFEGUARDS REPORTS |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) | 73.71(b)(1) |  |  | 1 | 2006-06-26
42665 | 0 | CARDINAL HEALTH NUCLEAR PHARMACY |  |  |  |  | 2006-06-25 18:00 | 2006-06-26 13:53 | 2006-06-26 | FLOOD DAMAGE TO NUCLEAR PHARMACY On the evening of 06/25/06, the Regional Director arrived at the facility and determined that the pharmacy had been under at least six feet of water at some time during the day. The Regional Director notified the building landlord and the company RSO. After their arrival and the flood waters receded, they conducted a physical inspection of the pharmacy and the radioactive materials. Initial inspection discovered no missing or damaged radioactive material. The licensee is presently completing a detailed inventory. Several doors and windows have been replaced to provide security to the facility. The licensee will update this report when it determines if any specific 10 CFR reporting criteria have been met. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | DE | MAT | [5 empty] | 0 | 2006-06-26
42664 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2006-06-23 16:05 | 2006-06-26 11:45 | 2006-06-26 | SOUTH CAROLINA AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "The SC Department of Health and Environmental Control was notified on Friday, June 23, 2006, at 4:05 p.m. that a Troxler Model 3440 portable moisture density gauge had been damaged on a job site at the Anderson County Airport. F&R Construction [name deleted], made the report. The gauge was reportedly run over by a roller on the job site. [F&R Construction] responded to the notice, as did an Anderson County HazMat team. Both [F&R Construction] and the HazMat team had survey meters in their possession. Following survey of the damaged gauge, the source could be retracted into its housing and the source shield was closed. A survey of the exterior of the gauge showed no readings above 10 mR/hr and a survey of the area the gauge had been used in produced background readings. Anderson County HAZMAT Team [name deleted] took a wipe of the bottom of the gauge. It produced no reading above background. The gauge was placed in its case and then inside an over pack container. The Licensee was then instructed by DHEC BRH to transport the gauge to their storage location and secure it until Monday. DHEC BRH was kept updated throughout this entire time via cell phone communication with both [F&R Construction] and [Anderson County HazMat team]. "A follow-up phone call made to [F&R Construction] on Monday, June 26, 2006, confirmed that the gauge was secured and awaiting transport on Tuesday to the manufacturer or a licensed service provider to attempt repair. The licensee was advised to submit a written report detailing this event to the Department within 15 days. All corrective action to prevent such an incident in the future was requested to be included. No indication of internal uptake at this point. The event is considered closed and pending the licensee's investigation and report to the Department, updates will be made through the national NMED system." South Carolina Event Report # SC060008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2006-06-29
42663 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-06-26 01:56 | 2006-06-26 02:51 | 2006-07-27 | SECURITY EVENT Discovered vulnerability in a safeguard system that could allow access to a controlled access area. Compensatory measures have been taken. Call the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM M. LICHTNER TO W. GOTT AT 0344 ON 06/26/06 * * * "All functions were fully restored." The licensee notified the NRC Resident Inspector. Notified R1DO (M. Sykes) and emailed to 73.71 group. * * * RETRACTION AT 09:58 ON 7/27/2006 FROM TOM ILLIADIS TO ABRAMOVITZ * * * The licensee has determined that this event did not meet the reporting criteria. Contact the Headquarters Operations Officer for additional details. Notified the R1DO (Gray) and the 73.71 group (via E-mail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 1 | 2006-06-26
42662 | 0 | US AIR FORCE |  |  |  |  | 2006-06-23 14:10 | 2006-06-23 14:15 | 2006-06-23 | LOSS OF TWO AMERICIUM-241 DETECTOR SOURCES A representative for the Air Force Master Material License reported that two Americium-241 sources (SSDR NR-1129-D0102-S; Model M43A1) each with a curie content of less than 300 microCuries (less than 600 microCuries total) were determined to be missing from a storage location at the Tyndall Air Force Base in Florida. The sources are used in Chemical Agent Detectors. The date of last confirmed inventory of the sources was December of 2005. The RSO at Tyndall AFB recently changed and a new inventory was conducted at which time the sources were determined to be unaccounted for. The licensee states that there is information that indicates the sources have been transferred to another AFB but that this has not yet been confirmed. Investigation into the current location of the sources is still in progress. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-06-23
42661 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2006-05-26 15:25 | 2006-06-23 12:50 | 2006-06-26 | POTENTIAL LOSS OF LICENSED NUCLEAR MATERIAL "In Event Notifications 42597and 42599 on May 22, and 23, 2006, respectively, as updated on May 26, 2006 Pilgrim Nuclear Power Station notified the NRC that during ongoing activities to remove non-fuel material from the Pilgrim Spent Fuel Pool it had been identified that nine (9) irradiated neutron detectors containing very small quantities (less than 0.003 grams each) of special nuclear material were not in their expected locations. Per the inventory sheets, the neutron detectors were expected to be enclosed in "dry tubes" in the Spent Fuel Pool. Processing of the "dry tubes" identified that the neutron detectors are not in their expected locations. "Subsequent investigation has determined that an error in the records was introduced in 1996 when the current base inventory sheets were developed. During the 1996 inventory, the assumption was made that these nine (9) "dry tubes" contained neutron detectors. The investigation has determined that the detectors, although moved to the spent fuel pool, were removed from the "dry tubes" prior to the "dry tubes" removal from the reactor vessel in 1987. "This affected the validity of the 1996 base inventory. A written report will be submitted consistent with 10 CFR 20.2201(b)." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY MICHAEL MCDONNELL TO JEFF ROTTON AT 1459 ON 06/26/06 * * * "Worst case isotope totals for the 9 detectors combined would be the following (all other isotopes would be an order of magnitude or more lower): U 235 - 5.382E-08 Curies, Pu 239 - 2.376E-07 Curies, Pu-238 - 3.510E-08 Curies, Pu 241 - 4.572E-08 Curies" The licensee notified the NRC Resident Inspector. Notified R1DO (Perry) and NRR EO (MJ Ross-Lee). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-06-23
42660 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2006-06-22 06:20 | 2006-06-22 14:28 | 2006-06-22 | 24 HOUR LICENSE CONDITION REPORT OF OPERATION IN A CONDITION PROHIBITED BY TECHNICAL SPECIFICATION "At 0620 today, FPL Energy Seabrook discovered that the plant was in it condition prohibited by the technical specifications. At approximately 1900 yesterday, June 21, one of the two train-B vital battery chargers was removed from service, rendering the charger inoperable. This condition went unrecognized until 0620 this morning (June 22). Seabrook Station Technical Specification 3.8.2.1 permits two hours to restore a battery charger to operable status, otherwise, the plant must shutdown to hot standby within the next 6 hours and cold shutdown within the following 30 hours. In this event, the train-B full-capacity battery charger was inoperable for approximately 12.5 hours, exceeding the time permitted by the technical specifications. During the period the charger was inoperable, the redundant battery charger in train B and both train-A battery chargers remained in service and operable. This notification is being made as a 24-hour report in accordance with license condition 2.G of the Seabrook Station operating license." Investigation into the circumstances of the event are ongoing. The normal battery charger had been removed from service for normal maintenance and testing. A backup battery charger was placed on the battery which permitted the licensee to continue normal plant operations without entering the two hour TS LCO for 3.8.2.1. During the maintenance and testing of the primary battery charger, the backup battery charger was also rendered inoperable resulting in no battery charger for the affected battery bank. The licensee stated that at 0726 EDT on 6/22/06, the battery charger was restored to service and the technical specification exited. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2006-06-22
42659 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-06-21 17:10 | 2006-06-21 20:50 | 2006-06-21 | CHEMICAL SPILL TO THE DELAWARE RIVER "A notification was made to the New Jersey Department of Environmental Protection of a discharge of approximately 6-10 gallons of Sodium Hypochlorite with a 15% chlorine concentration. The discharge occurred while returning the chlorination system to service following maintenance. The solution was discharged into the intake bay of an out-of-service circulating water pump that communicates with the Delaware River. A portable screen wash pump, that takes a suction on that bay, transported the chlorine to the intake pump traveling water screens and discharged to the Delaware River via the screen debris trough. Neither of these locations are New Jersey Department of Environmental Protection permitted outfalls. "There was no out-of-service safety related equipment that contributed to this event. No one was injured as a result of this event." This event was caused when a floor drain plug was knocked loose during maintenance. This plug is being replaced. 8-10 fish were killed in the trough. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-21
42658 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-06-19 16:00 | 2006-06-21 10:02 | 2006-06-22 | INITIAL PART 21 NOTIFICATION - PRIME MEASUREMENT PRODUCTS, MODELS 763 AND 763A GAGE PRESSURE TRANSMITTERS AND MODEL 764 DIFFERENTIAL PRESSURE TRANSMITTERS "This report is made per 10CFR21.21 Notification of failure to comply or existence of a defect and its evaluation. "Callaway Plant received a notification dated May 18, 2006, from PRIME Measurement Products (formerly ITT Barton) stating Barton Model 763 and 763A Gage Pressure Transmitters and Model 764 Differential Pressure Transmitters may have defective external lead-wire connectors, which could affect their performance during an accident. The notification provided by PRIME stated the affected transmitters were manufactured after May 1982 and shipped from the factory prior to April 1, 2006. "The potential defect is characterized as follows: The transmitters' external lead wires enter the electronics enclosure through a hermetic seal called a connector assembly. The external lead wires are soldered to the glass sealed pins of the hermetic seal. Epoxy potting is used to structurally support the soldered wire connections and establish a seal to protect the solder connections from shorting, which could be caused by an electrically conductive accident environment. The defect is that the insulated portions of the wires in the connectors, manufactured after May 1982, may not be embedded deeply enough into the epoxy potting to provide an electrical connection that would not be affected in an accident environment. "The notification also states that actual transmitter installation may preclude shorting of exposed conductors due to the existence of conduit, conduit seals, and special wire connectors which could protect the exposed wires at a defective connector from conductive moisture. "Callaway Plant identified thirty applicable Barton transmitters and connector assemblies in warehouse stock. Inspections of these operational spare parts identified three connectors, which had exposed conductors external to their seal. One connector had this defect on one lead wire and two connectors had this defect on both lead wires. "Callaway has also identified that thirty-nine potentially affected transmitters are installed in the plant. An inspection plan has been developed to perform the required inspections, based on safety significance, ALARA considerations, and potential accident environmental conditions. Additional reporting requirements associated with the installed components will be evaluated under 10CFR50.72 as required. "On 06/19/06, Callaway Plant personnel completed evaluations and determined the defective connections constitute a defect per 10CFR21 require initial NRC notification within two days. "The NRC resident inspectors have been notified of this issue." * * * UPDATE FROM LICENSEE (D. GRIFFITH) TO M. RIPLEY 1515 EDT 06/22/06 * * * "This report is a revision to report EN # 42658 reported on 06/21/2006. Added statement: "The suppliers of the identified transmitters were Prime Measurement Products and Westinghouse Electric Corporation." The licensee notified the NRC Resident Inspector. Notified NRR (O. Tabatabai), R4 DO (D. Graves) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 21.21 |  |  |  | 0 | 2006-06-21
42657 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-06-21 00:15 | 2006-06-21 02:36 | 2006-07-21 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE DUE EXCESSVIE AUX OIL PUMP MOTOR CURRENT "During routine weekly operation of High Pressure Coolant Injection (HPCI) Auxiliary Oil Pump (AOP), 2E41C002-3, the pump displayed indications of excessive motor current after the pump had been inservice for approximately 45 minutes. The pump was secured and, following review of electrical diagrams and consultation with Electrical Maintenance, the operating current of the AOP was checked and determined to be excessive. The AOP was declared inoperable, with the AOP inoperable, the HPCI system cannot be considered operable. The HPCI System is a single train ECCS system. Investigation into the cause of the high motor current is ongoing." All other Emergency Core Cooling Systems are fully operable including Reactor Core Isolation Cooling (RCIC). The NRC Resident Inspector was notified of this event by the licensee. *** UPDATE FROM A. DISMUKE TO J. KNOKE AT 0933 ON 07/21/06 *** "Retraction of NRC Event # 42657: After further review and evaluation it has been determined that the eight hour call made June 21, 2006 per the guidance of 50.72(b)(3)(v)(D) should be retracted. "On 06/21/2006 at approximately 0015 EDT, Unit 2 was at 100 percent Rated Thermal Power. During routine weekly operation of the High Pressure Coolant Injection (HPCI) Auxiliary Oil Pump, 2E41-C002-3, the pump displayed indications of excessive motor current after the pump had been in-service for approximately 45 minutes. Investigation revealed the running amps to be 46 amps with nameplate data running amps shown as 27 amps. "An evaluation was performed for the as-found condition that considered the cause and effects of the increased running amps on the ability of the auxiliary oil pump to perform its design function. Specifically, the effect of a shunt resistor short to open was reviewed. Areas reviewed for impact were motor speed, system over pressurization, motor insulation, Environmental Qualification, and motor service life. The results of the evaluation showed that significant margin existed to ensure the auxiliary oil pump design function was maintained. Therefore, the auxiliary oil pump operability was maintained and HPCI operability was also maintained. The HPCI system was immediately removed from service using normal plant procedures; a work order initiated, and the existing motor was replaced to ensure continued long term reliability." The licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-06-21
42656 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-06-20 16:30 | 2006-06-20 16:54 | 2006-06-20 | UNUSUAL EVENT DECLARED DUE TO A SEISMIC EVENT "Emergency plan unusual event entered due to a seismic event (LU-1). No equipment damage has been identified." The seismic event occurred at 1611hrs and tremors were felt in the Control Room. Unit 1 remained at full power and initial plant walkdown identified no safety equipment damage. Plant instrumentation indicated an acceleration of 0.005 Gs. Per U.S. Geological Survey website the quake was a 3.4 on the Richter scale and occurred NNW of the site. There is a small likelihood of after shocks. No radioactive releases have occurred. * * * UPDATE ON 06/20/06 AT 2019 EDT FROM JEFFREY D. ANDERSON TO M. RIPLEY * * * "Perry Plant has completed walkdowns from the Seismic Event that occurred at 1611. No Plant problems identified from walkdowns. Unusual Event has been terminated at 2000 on 6/20/06." The licensee notified the NRC Resident Inspector, State and local officials. Notified NRR (M. Case), IRD (Wilson), R3DO (O'Brien), DHS (Fite) and FEMA (Casto). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-06-20
42655 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-06-20 16:00 | 2006-06-20 16:45 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * SEWER MANHOLE OVERFLOW TO CATCH BASIN REPRESENTED A BYPASS PER DISCHARGE PERMIT "On June 20, 2006 at approximately 3:00 p.m. it was reported to Environmental Protection Department that a sanitary sewer manhole was observed to be overflowing. It was also reported that the flow was moving over the adjacent pavement to a nearby catch basin. A subsequent inspection by Environmental Engineering confirmed that the sanitary sewer waste was overflowing the manhole and discharging to a nearby catch basin. This catch basin discharges to the storm water system via the once through cooling drain lines. It is estimated that approximately 1-2 gallons entered the catch basin. "Following the above confirmation both Environmental Engineering management and Radiation Protection personnel were notified. In addition, Industrial Engineering was called to effect repairs and/or unclog the sanitary sewer line. "Because the sanitary sewage flow was being directed around the sanitary sewer treatment plant as a result of the overflow, it was concluded that this event represented a 'bypass' as described by the BWXT NPD VPDES Water Discharge Permit (VA0003697). "Section H 'Reports of Unusual or Extraordinary Discharges' of 'Conditions Applicable to all VPDES Permits' requires that this type of event be reported to VADEQ (Virginia Department of Environmental Quality) promptly, but in no case later than 24 hours with a written report to follow in 5 days. "On June 20, 2006 at about 4:00 p.m. a phone call was made to VADEQ South Central Regional Office notifying them of the event." The licensee notified the NRC Resident Inspector and the State. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
42654 | 0 | QUAKER SALES CORPORATION |  |  |  |  | 2006-06-20 14:30 | 2006-06-20 15:05 | 2006-06-20 | DAMAGED MOISTURE DENSITY GAUGE Licensee was performing work on pavement at State Route 22, Indiana County, PA when a Moisture Density Gauge was damaged by compacting equipment. The damage to the gauge was restricted to the casing and the licensee has confirmed that the sources are in their retracted safe positions. The damaged gauge was moved off the pavement and a perimeter was established around it. Contact readings were recorded as 60 millirem/hr. The licensee has contacted Northeast Technical who is the service provider. The gauge will be temporarily transferred to office storage and will be subsequently transported to the service provider for repairs. The density gauge is a Troxler model 3450, serial number 00397 containing 8 millicuries Cs-137, 40 millicuries Am-241/Be (source numbers 750-6096 and 47-28081 respectively). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2006-06-20
42653 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-05-05 | 2006-06-19 15:18 | 2006-06-19 | AGREEMENT STATE REPORT - MISSING TRITIUM SIGNS The State provided the following information via facsimile: "The Radiation Safety Office of Fort James Operating Company notified the department on 23 May 2006 that one Generally licensed tritium exit sign was missing. The exit sign was noted missing on 5 May 2006 during a corporate inventory of all radioactive material possessed at the site. The sign's bracket was also missing. There was no evidence the sign was damaged while being removed. The Radiation Safety Officer interviewed numerous workers to try and locate the sign but was unable to determine what happened. "Isotope and Activity involved: 11.5 Ci (425.5 MBq) H-3. "Tritium Exit Sign, S/N M5099." WA State Report No.WA-06-021 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-06-22
42652 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2006-06-18 23:19 | 2006-06-19 04:06 | 2006-08-03 | RADIATION MONITOR SPIKED THREE TIMES "At 2319 on 06/18/2006, the 'A' Plenum Radiation Monitor spiked high which resulted in the closure of the Drywell CAM (Continuous Air Monitor) and the Oxygen Analyzer Primary Containment Isolation Valves. The spike's (3) of approx. 30 Mr/HR occurred during this event. The valves isolated once, the Reactor Building Ventilation trip was reset once and re-isolation occurred several minutes later from another spike on the Rad Monitor. Trip setpoint is 26 Mr/hr. The Plenum high Rad signal also resulted in Reactor Building isolation (twice), start of 'A' Standby Gas Treatment, and transfer of the Control Room Ventilation to the high Rad Mode. The 'B' Plenum Rad Monitor remained constant at 1.3 Mr/hr. The Reactor Building Ventilation and Control Room Ventilation have been reset and Standby Gas Treatment has been secured. The 'A' Plenum Radiation Monitor has been declared inoperable." Instrument & Control Technicians are currently troubleshooting the problem associated with the 'A' Plenum Radiation Monitor. The NRC Resident Inspector's have been left messages by the licensee. * * * UPDATE AT 10:15 ON 8/3/2006 FROM ROBERT SCHREIFELS TO ABRAMOVITZ * * * This report is being reclassified by the licensee from a 50.72(b)(3)(iv)(A) [valid system actuation] to 50.73(a)(2)(iv)(A) [invalid system actuation]. "Based on further investigation, Monticello has determined that the actuation signal was due to a failed microswitch and therefore was not a valid signal. Because the actuation signal was not valid, Monticello is retracting the initial event report and instead reporting this event as an unplanned system actuation under 50.73(a)(2)(iv)(A). This report will be made in lieu of reporting the event as an LER. "In accordance with 50.73(a)(2)(iv)(A): "This report is not considered an LER and the report is being made under 50.73(a)(2)(iv)(A). The original event report (ENS #42652) detailed the systems affected, whether the actuation was complete or partial and whether each affected system started and functioned successfully. "The cause of the invalid signal was the failure of the trip check pushbutton [micro]switch due to age related degradation. The switch has been replaced and the 'A' Plenum Radiation Monitor was returned to service." The licensee notified the NRC Resident Inspector. Notified the R3DO (O'Brien). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-06-19
42651 | -1 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2006-06-18 14:55 | 2006-06-19 00:29 | 2006-07-05 | LOSS OF ONSITE EMERGENCY SAFETY FUNCTION - "B" EDG FAILED TO START DURING TEST RUN "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On June 18, 2006, at approximately 1455 Mountain Standard Time (MST), Palo Verde Nuclear Generating Station Unit 1 was operating at 0% power in Mode 6 with the 'A' Emergency Diesel Generator (EDG) inoperable for troubleshooting of the train 'A' load sequencer, The 'B' EDG failed to start during a test run resulting in a loss of the onsite emergency power safety function required by General Design Criterion (GDC) 17. The offsite power source safety function remains available to the plant. "The unit entered Technical Specification 3.8.2, AC Sources - Shutdown Condition B for one required DG inoperable. There was no movement of irradiated fuel assemblies, therefore the unit remained in compliance with the Required Actions. The offsite electrical grid is stable. "At 1810 MST the 'A' EDG was declared operable, exiting Technical Specification 3.8.2. With the 'A' EDG operable, the safety function for the onsite emergency power was also restored. "There were no structures, systems or components that were inoperable at the start of event that contributed to the event. This condition did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. This condition did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified of this condition and this ENS notification." * * * RETRACTION RECEIVED VIA E-MAIL FROM DAN HAUTALA TO JOE O'HARA AT 1702 ON 7/5/06 * * * " Further evaluation has determined that this event is not reportable. In the 'test' mode, an 'Incomplete Sequence' trip is enabled and functions on an engine start to trip the engine if starting air is not terminated within 15 seconds. Due to a delay in opening the engine fuel racks by the test mode pneumatic control valve loop, the 'Incomplete Sequence' trip actuated. During an emergency start, the electrically operated emergency fuel solenoids control the operation of the engine fuel racks and the 'Incomplete Sequence' trip function is bypassed. Engineering evaluation found none of the equipment required to operate the 'B' EDG in the emergency mode degraded or malfunctioning. The 'B' EDG was still capable of performing its design function and was 'OPERABLE'. Additionally, it was determined that the 'A' EDG was fully functional and in a standby condition, capable of performing its design function at the time the 'B' EDG test run trip occurred. "Therefore, this condition is not reportable per 10CFR50.72(2)(b)(v)(B) or (2)(b)(v)(D)." The licensee notified the NRC Resident Inspector. R4DO(Pick) has been notified. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION | POT RHR INOP |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(v)(B) |  |  | 0 | 2006-06-19
42650 | 0 | MICHIGAN DEPT OF TRANSPORTATION |  |  |  |  | 2006-06-18 01:00 | 2006-06-18 19:02 | 2006-06-18 | DAMAGED MOISTURE DENSITY GAUGE While performing back-scatter measurements at a construction site on I-75 between Davison Freeway and I-94 in Wayne County, MI, a Model 3440 Troxler moisture density gauge (8 millicuries Cs-137, 40 millicuries Am-241:Be) belonging to the department was damaged when it was run over by a truck. The gauge was returned to the department office and survey results, pending a leak test on Monday 06/19, were negative indicating the sources remained intact. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MI | MAT | [5 empty] | 0 | 2006-06-18
42649 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-06-15 | 2006-06-16 12:44 | 2006-06-16 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via email: "A Troxler 3440 portable gauge serial number 37319 (8 millicuries Cs-137, 40 millicuries Am-241:Be) was damaged when a large earth moving piece of equipment backed over it. The operator was taking density readings about 20 feet behind the equipment when the equipment backed up. The operator ran to safety as the gauge was struck. The operator roped off a 50 foot radius around the gauge and called the RSO. When the RSO arrived at the site, the RSO and the operator took the buried gauge out of the soil and inspected it. The fire department was called and took readings in the area with a Geiger count-rate meter. Radiation levels were determined to be in the normal range. The top outer portion of the gauge was damaged and the source rod bent slightly, but the source areas were intact. The source rod was put back into the gauge by pounding the handle up with a mallet. The gauge was transported back to the licensed storage location and will be sent back to the manufacture for repair or disposal." Location of Event: SeaTac Airport, Port of Seattle, City of SeaTac. Washington State report number: WA-06-044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-06-21
42648 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-06-16 09:00 | 2006-06-16 11:19 | 2006-11-15 | AGREEMENT STATE REPORT - STOLEN NUCLEAR GAUGE The State provided the following information via email: "Radiation Control received a call at 9:15 am from [name deleted] the Radiation Safety Officer (RSO) for QC Testing Laboratories, Inc., 10810 Northwest Freeway, Houston, TX, 77092, License # L04750-003, reporting that a technician was at a jobsite in the Houston suburb of Brookshire, when the technician noticed that the chain and lock bracing a moisture density gauge was cut, and the gauge and its case were subsequently stolen around 9:00 am, 6/16/06. "The Gauge Information is as follows: Manufacturer - Troxler; Model 3430; Serial # 367007. Source information: Cs-137, 8 millicuries, Serial # 751-796; Am-241Be, 40 millicuries, Serial # 78-1538. The last leak test was performed April 26, 2006. "Local police were immediately notified, who in turn have contacted local FBI. The licensee will fax a copy of the police report to Radiation Control as soon as available. Radiation Control was contacted at 10:00 am by the Chief of Police, Brookshire, to confirm the licensee had contacted the agency and to received additional information on the stolen equipment. An email with the device information and a copy of this report was sent to the police chief [email address deleted]. "Radiation Control is continuing to investigate & will transmit any updated information as soon as it is received. Texas Incident # I -8347." * * * UPDATE PROVIDED BY LATISCHA HANSON TO JEFF ROTTON AT 1833 EST ON 11/15/06 * * * The State provided the following information via email: "At 1145 hrs. CST, the TX state Agency was notified by [name Deleted], the Program Director for Alabama that a Troxler moisture density gauge was being sold on E-Bay. Their staff had been surveying the site in hopes of finding a recently stolen gauge in Alabama and the seller was identified as [name Deleted]. At 1230 hrs. TX staffs were dispatched to the pawn shop, where initially, the representative failed to cooperate and show the inspectors the device or even reveal the storage location in a local warehouse. As an Impoundment Order was being drafted and local law enforcement authorities were being notified, the [name Deleted] employee consented to having the device delivered to the shop for identification and confiscation if it contained radioactive material. The device and associated paperwork were transported back to Austin for investigation as to who the owner is and what incident is associated with the recovered gauge. "[At 1500 CST], the gauge was found by serial #, to belong QC Laboratories, Inc., L04750, TX Incident #I-8347/TX-042648. The RSO has been contacted and agreed to make arrangements with DSHS/Radiation Control for pickup; pick up details to be determined during discussion between both parties on 11/16/06." Notified R4DO (Johnson), NMSS EO (Camper), ILTAB (via email) and Mexico (via fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-06-21
42647 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2006-06-15 22:23 | 2006-06-16 02:18 | 2006-06-16 | MANUAL REACTOR TRIP DUE TO DIGITAL ELECTRO-HYDRAULIC LEAK "On 6/15/06 at 2223 hrs an unplanned manual reactor trip was initiated on St. Lucie Unit 2 from 45% power due to severe DEH Leak on the #1 Throttle Valve. DEH Leak ceased upon Turbine Trip. Following the reactor trip, EOP-1, Standard Post Trip Actions, and EOP-2, Reactor Trip Recovery procedures were completed without contingencies and Unit 2 was stabilized in Mode 3. All control rods fully inserted and no S/G Safety Valves Lifted. Feedwater to the S/G was supplied by the main FW Pumps. All safe shutdown equipment operated as expected. There were no major equipment failures." Decay heat is being removed with main feedwater and dumping steam to the condenser. The grid is stable. The fire brigade was activated following the trip and set a fire watch (no fire). The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-06-16
42646 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-06-05 | 2006-06-15 16:39 | 2006-06-15 | MISSISSIPPI AGREEMENT STATE REPORT - STUCK WELL LOGGING SOURCE The State provided the following information via email: "[The State] received notification on 6-5-06 from Schlumberger that they had logging tool stuck in the Patterson #2 exploration well located at Midway Dome, Lamar County, Mississippi. Logging tool containing a 1.7 curie Cesium -137 source and a 16 curie Americium- 241:Be source was stuck below 12,000 feet. Operating company was fishing for logging tool string. Schlumberger discussed initial procedure of abandoning sources with DRH. During fishing operations logging tool containing sources was pushed to a depth of 14,854 feet. The fishing operation was successful in retrieving the tool string containing the Americium-241:Be source but they did not get the density tool skid containing the Cesium-137 source back. Licensee stated that tool would be cemented in hole with 200 feet of cement and whip stock deflection device. Plan was later modified to drill into cement plug and set casing 160 feet above the abandoned source prior to re-drilling the well to the side of the abandoned source. "Schlumberger took survey readings of the recovered source and tool string and did not observe any readings out of the normal readings. Leak tests were also taken of the Americium-241:Be source, with no evidence of leaking. "30 [-day] written report required from licensee. Licensee must also place a plaque on the well bore signifying that abandoned source is in well bore." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2006-06-20
42645 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-06-14 | 2006-06-15 16:29 | 2006-06-15 | CALIFORNIA AGREEMENT STATE REPORT - LOST AND SUBSEQUENTLY FOUND NUCLEAR GAUGE The State provided the following information via email: "On 6/15/06, the RSO at Earth Systems Pacific contacted the RHB-Richmond office to report a nuclear gauge incident that occurred in the evening of 6/14/06. On 6/14/06 one of their moisture density nuclear gauges (CPN, Model MC1DR, S/N M10906353 containing 10 millicuries of Cs-137 and 50 millicuries of Am-241) fell off from a back of a truck onto the highway during transportation. A member of the public picked up the Type A container (with the gauge inside) and transported it into the jobsite. The jobsite personnel immediately contacted the Fire Department. The gauge was then handed over to the Fire Department. The Fire Department inspected the gauge and contacted the licensee. On the same day, the Alternate RSO picked up the gauge from the Fire Department and brought it back to the licensed facility. According to the RSO, the gauge was inside the Type A container during the whole incident and there was no visible damage to the gauge. They have performed a leak test and sent it for analysis. The RSO is expecting a report from the Fire Department. The RHB South RM office is awaiting additional information on the incident, including additional information concerning the Fire Department involved, and will investigate the reason the gauge was apparently unsecured in the licensee's vehicle." California Report # 061506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-06-20
42644 | 0 | SAN ONOFRE | 1 | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2006-06-13 22:05 | 2006-06-15 15:31 | 2006-06-15 | OFFSITE NOTIFICATION - AUTO ACCIDENT FATALITY "On Tuesday, June 13, 2006, at approximately 2205 PDT, an on duty SONGS security officer driving an SCE vehicle struck a pedestrian on a public road outside the Owner Controlled Area. At that time, the officer was performing routine rounds and was driving between the plant and SCE's MESA facility. "SCE notified local authorities including the California Highway Patrol and the Orange County Fire Authority. "The individual sustained serious injuries and was transported to a local hospital. SCE has been notified unofficially that the individual passed away on June 14, 2006. The identity of the individual is unknown by SCE. SCE is reporting this occurrence in accordance with 10CFR50.72(b)(2)(xi). No news release is planned by SCE at this time. "At the time of this report, Units 2 and 3 were operating at about 99 and 100 percent power, respectively. The NRC Resident Inspectors have been notified of this occurrence and will be provided with a copy of this report." | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-15
42643 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-06-15 10:53 | 2006-06-15 13:38 | 2006-06-15 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "At 10:53 on 6/15/06, a reactor scram, occurred due to a Turbine/Generator Trip. All control rods fully inserted into core. The lowest vessel water level reached was 134 inches. Water level is now being controlled in the normal water level band using Condensate/Feedwater system. No SRVs lifted. RPV pressure is being controlled by the Turbine Pressure Regulator. "At the time of the scram, 2B Main Transformer cleaning was taking place. The initial alarm was 'Main Transformer 2B Oil Temp Hi' followed by Generator Differential Relaying and a Turbine Trip. Transformer Deluge also initiated. An investigation is in progress to determine the specific cause for the initiating event. "Group 13 'Drywell Sumps' isolated on Level 3 as expected. At the time of the scram, all ECCS systems and Emergency Diesel Generators were Operable." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-06-15
42642 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-06-15 03:00 | 2006-06-15 05:05 | 2006-06-15 | REACTOR SCRAM WHILE SHIFTING POWER SUPPLIES "At approximately 0300 hours on 15 June, the Susquehanna Unit One reactor automatically scrammed due to an apparent neutron monitoring trip while transferring Reactor Protection System power supplies. All rods [fully] inserted, and both reactor recirculation pumps tripped. Reactor water level lowered to -38" causing level 3 (+13") and level 2 (-38")isolations, and was restored to normal level (+35") by RCIC and subsequently the feedwater system. All isolations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected. "A reactor recirculation pump was restarted to re-establish forced core circulation. The reactor is currently stable in condition 3. An investigation into the cause of the shutdown is underway. Unit Two continued power operation. "The NRC resident inspectors were notified. A press release will occur." After the scram, HPCI automatically started but was manually shut down with RCIC maintaining vessel level. Decay heat removal is being maintained with main feedwater and the turbine steam dumps. The electrical grid is stable. No major LCOs were in affect at the time of the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2006-06-15
42641 | -1 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2006-06-14 14:00 | 2006-06-14 19:08 | 2006-06-16 | LEAKING DECAY HEAT REMOVAL ISOLATION VALVE BYPASS LINE "On 2-21-06, during a tour of containment during normal operation at 100% power, a small leak (one (1) to three (3) drops per second) was noted from a 1/2 inch line connected to the decay heat removal (DHR) drop line. It was identified as being a body-bonnet leak on valve 1LP-167 subject to a TS limit of 10 gpm. "At approximately 1400 hours on 6-14-06 following a shutdown for an unrelated issue, the source was identified as a leak at a weld in a "tee" joint adjacent to 1LP-167. This is considered RCS pressure boundary leakage, subject to a TS limit of zero leakage. The leak was isolated by closing a normally open valve in the 1/2 inch line and the leakage stopped. "Initial Safety Significance: The leak is in a 1/2 inch line which provides over pressure protection from thermal expansion in the volume between 1LP-1 and 1LP-2 (the main pressure boundary isolation valves between the high pressure RCS and the LPI (DHR) system). The leak rate (1 to 3 drops per second) was not significant, except that it was RCS pressure boundary leakage. 1LP-1 is normally closed, but must be opened to establish a DHR path. Valve 1LP-167 is a 1/2 inch check valve which would have limited RCS leakage. Thus, if the leak had grown, it would have been limited to the amount of seat leakage past either 1LP-167 or 1LP-1. It would also have been limited by the 1/2 inch size of the line containing the leak." Technical Specification LCO 3.4.13 applies to RCS leakage in modes 1 to 4. The licensee plans to fix the leak prior to entry into mode 4. The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 00:15 ON 6/16/2006 FROM SAM LARK TO ABRAMOVITZ * * * "On 6-14-06 at 1908 hours Oconee reported an RCS pressure boundary leak in a 1/2 inch line connected to the decay heat removal (DHR) line near valve 1LP-1 inside containment. Oconee has reviewed the event in greater detail and has concluded that the event is not reportable. The Basis for TS 3.4.13 states that RCS LEAKAGE includes leakage from connected systems up to and including the second normally closed valve (or outermost isolation valve for systems penetrating containment). However TS 1.1 contains a definition of LEAKAGE which includes 'Pressure Boundary LEAKAGE: LEAKAGE (except SG LEAKAGE) through a nonisolable fault in an RCS component body, pipe wall, or vessel wall.' The leakage in this event was isolable, and therefore does not meet the definition of Pressure Boundary LEAKAGE. Therefore the zero leakage criterion of TS 3.4.13 does not apply to this leak. The applicable criterion is 10 gpm identified LEAKAGE. Since the leak does not meet the criterion as Pressure Boundary LEAKAGE, the leak was isolable, and the applicable TS LEAKAGE limit was not exceeded, this event does not meet the reportability criteria for 10 CFR 50.72 or 50.73 and event notification 42641 is hereby RETRACTED. "Additional information and clarification: "During normal operation the leak was isolated by one barrier (valves 1LP-167 and 1LP-1, closed in parallel). The leakage observed on 2-21-06 during a containment tour at Mode 1 was recorded as 1 drop per second. As stated in the initial notification, at that time the leak was believed to be a body-bonnet leak. It was observed at Mode 1 again on 5-25-06 and recorded as 3 drops/second. On 6-14-06, the leakage was recorded as one drop/second while at reduced pressure in Mode 4, before the DHR systems was placed in service. At that point, the leak was isolated by closing an additional valve (1LP-166, normally open), and the leak stopped. The Low Pressure Injection system was placed in service for DHR, which opened 1 LP-1. Later, with system pressure at approximately 285 psig in Mode 5 (outside the applicability of TS 3.4.13), 1LP-166 was reopened to allow additional verification of the leak location. At that time the leak was described as a 'spray' but no leak rate was measured before 1LP-166 was reclosed. The leak rate at that time was estimated as well less than 10 GPM. "Corrective Action: The affective section of 1/2 inch pipe and associated fittings have been removed for transfer to a Duke laboratory for analysis. Repairs will be completed prior to return to mode 4." The licensee notified the NRC Resident Inspector. Notified the R2DO (Bonser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-06-14
42640 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-06-14 09:41 | 2006-06-14 17:30 | 2006-06-23 | ERDS INOPERABLE "On June 14, 2006, at 0941 PDT, plant operators declared both Units 1 and 2 Emergency Response Data System (ERDS) inoperable due to the failure to complete scheduled surveillance testing. The in-plant emergency response facility data system (ERFDS) and safety parameter display system (SPDS) are operating as expected, but data transfer could not be accomplished via the digital data transfer to the NRC Event Response Center. "Plant personnel are actively investigating the cause of the data transfer failure, and will update this notice upon completion of troubleshooting, repair, and successful performance of the surveillance test. "Plant management, emergency personnel, and the NRC Resident Inspector(s) will be informed of the condition, planned maintenance actions, and resolution of this condition." * * * UPDATE FROM DAVE BAHNER TO W. GOTT AT 1841 EDT ON 06/16/06 "PG&E restored the ERDS data system to service and satisfactorily completed communication testing with the NRC Incident Response Center." The system was declared operable at 1433 PT. The licensee will notify the NRC Resident Inspector. Notified R4DO (A. Gody) * * * UPDATE FROM MATTHEW COWARD TO HUFFMAN AT 1306 EDT ON 6/23/06 * * * "The following update is provided to clarify the reason for reporting the failure of the Emergency Response Data System (ERDS) on June 14, 2006. On June 14, 2006, at 0941 PDT, plant operators declared both Units 1 and 2 ERDS inoperable when it was discovered during surveillance testing that, although the in-plant emergency response facility data system (ERFDS) and safety parameter display system (SPDS) were operating as expected, the data transfer to the NRC Event Response Center could not be accomplished." This update is to clarify that the ERDS inoperability was discovered during surveillance testing and was not due to a failure to complete scheduled surveillance testing as initially reported. The licensee notified the NRC Resident Inspector. R4DO (Graves) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-06-14
42639 | 0 | BATTLE CREEK HEALTH SYSTEM |  |  |  |  | 2006-06-12 11:00 | 2006-06-14 15:53 | 2006-06-14 | OVERDOSE TO PATIENTS THYROID The patient reported to the hospital for treatment Monday, June 12 at 11 am and was given 2 millicuries of I-131 as a thyroid treatment dose. The patient then returned on June 14, 2006, for a survey. The prescribing physician reviewed and checked the orders as sufficient for a medistatic survey. The survey results revealed that there was a 96 percent uptake to the thyroid. Using the survey results, a discrepancy was discovered. During an initial interview of the patient it was not determined that the patient had no prior history of cancer or any prior history of operations on the thyroid. Since the patient had no prior history it was determined that a dose of 200 microcuries of I-131 should have been used. The results of this overdose could include loss of thyroid function. The consequences and possible remedies have been discussed with the patient. The hospital plans on changing their interview sheet to a checklist type format to help avoid this problem in the future. The hospital also plans on performing a root cause analysis on this issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-06-14
42638 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2006-06-14 13:00 | 2006-06-14 15:01 | 2006-06-14 | STATE NOTIFICATION OF LOW PH RAINWATER DISCHARGE "427 gallons of rainwater was discharged to the canal [onsite] with a pH of 4.2 which [exceeds] the [National Pollutant Discharge Elimination System] permit. This water went through a charcoal bed that contained water which had not been used in a year and a half." The pH discharge limit is 6. The site notified the Connecticut Department of Environmental Protection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-14
42637 | 0 | NAK ENGINEERING INC |  |  |  |  | 2006-06-13 | 2006-06-13 15:29 | 2006-06-13 | 10 CFR PART 21 NOTIFICATION - DEFECTIVE NORDBERG EMERGENCY DIESEL GENERATOR VALVE SEAT INSERTS The manufacturer provided the following information via facsimile: "Significant Safety Hazard regarding the potential of Nordberg Valve Seat Inserts (VSI) to 'drop' from the bore of the cylinder head into the cylinder with probable resulting damage to the cylinder head, power valves, piston, cylinder liner, exhaust manifold and turbocharger which could result in the loss of the intended 'Safety Function' of the EDG. "There exists a potential problem with the original specification for the specified value of interference fit of the inlet and exhaust Valve Seat Insert (VSI) in the area between the cylinder head bore and the VSI." Two sites, Brunswick and McGuire, had the defective parts with Brunswick already having changed out the affected parts. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2006-06-13
42636 | 0 | WATERFORD | 3 |  |  | [3] CE | 2006-06-12 13:00 | 2006-06-12 21:33 | 2006-06-12 | MANUAL ACTIONS DETERMINED UNTIMELY FOR FIRE SAFE SHUTDOWN "As part of an analysis to determine feasibility of manual actions, it was identified that three actions for Fire Area RAB 7 could not be performed within the times prescribed in the Post Shutdown Analysis. The subject fire area is subdivided by part height fire walls. Waterford 3 has an approved Appendix R deviation for the part height fire wall configuration. "Assuming a fire in Fire Area RAB 7 Operator entry into that same fire area is required. Results of the analysis indicate that the conditions in Fire Zone RAB 7B rapidly exceed the habitability threshold and do not moderate before ten minutes, the time at which one of the three manual actions is required, given a fire in Fire Zone RAB 7A. Because the space becomes uninhabitable, the manual action in Fire Zone RAB 7A is not feasible. "A continuous fire watch has been established within Fire Area RAB 7 as a compensatory measure. This condition is reportable within 8 hours pursuant to 10CFR 50.72(b)(3)(v)(A) as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2006-06-12
42635 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2006-06-12 15:56 | 2006-06-12 18:00 | 2006-06-13 | LOSS OF SPDS DURING PLANNED COMPUTER MAINTENANCE "On 6/12/06 at 07:54 am CDT, the Wolf Creek Generating Station removed the Nuclear Plant Information System (NPIS) computer from service for planned maintenance. Following this maintenance, one of the NPIS multiplexers (MTJX 'D') failed to re-establish communications with the computer, and efforts to restore the computer to service have been unsuccessful. The failure to restore the NPIS computer has resulted in a loss of functionality of the Safety Parameters Display System (SPDS). Efforts continue to restore the NPIS computer to service, which will restore SPDS functionality. Due to SPDS being lost for longer than a short period of time, Wolf Creek Nuclear Operating Corporation is making this ENS notification pursuant to the criteria of 10 CFR 50.72(b)(3)(xiii). There is no other loss of emergency assessment capability concurrent with the ongoing loss of SPDS. Plant personnel have entered the appropriate Off-Normal procedure and are obtaining local readings for the equipment that is normally monitored by SPDS and NPIS. It is unknown at this time when NPIS/SPDS will be restored." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM T. DAMASHEK TO P. SNYDER AT 1735 ON 6/13/06 * * * SPDS has been restored as of 1605 CDT. The licensee will notify the NRC Resident Inspector. Notified R4DO (Bywater). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-06-12
42634 | 0 | BAYHEALTH MEDICAL CENTER |  |  |  |  | 2006-06-12 15:00 | 2006-06-12 17:20 | 2006-06-12 | MEDICAL EVENT - HIGHER DOSE THAN PLANNED ADMINISTERED DURING BRACHYTHERAPY TREATMENT A brachytherapy dose for prostate cancer treatment included a planned 145 Gy dose to be accomplished using permanently implanted I-125 seeds. A computer is used as part of the hospital's procedures for determining the quantity of seeds to implant to arrive at the total prescribed dose using the dose per seed. Hospital staff incorrectly entered the dose per seed as 0.27 millicuries instead of 0.34 millicuries into the computer. This resulted in the computer calculating a quantity of 100 seeds to be used and resulted in a 26% higher dose than intended. The error in the calculation was not discovered until after the actual implant was accomplished. The medical consequences of the overdose include possible rectal complications in the future. Remedial actions could include removal of the prostate. The doctors are investigating other treatment options. The patient was being informed of the overdose and treatment options at the time of this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DE | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-06-12
42633 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2006-06-12 13:02 | 2006-06-12 17:25 | 2006-06-12 | HPCI INITITATION SIGNAL DUE TO TURBINE TRIP SIGNAL DURING STARTUP "Feedwater was being place into long path recirculation mode in accordance with N1-OP-16 to support a chemistry sample. During this evolution, reactor water level rose high enough such that the High Level Annunciator (92.2") was received, the turbine tripped [off of the turning gear] and a HPCI [High Pressure Coolant Injection] initiation signal was received as per design. HPCI system did not initiate flow and no pumps started because the Feedwater Booster Pumps were not in service (pull-to-lock). HPCI was reset and Reactor Water level [was] restored to the operating band 65" - 83". "A copy of this Notification Worksheet will be provided to the Resident Inspector. "This event has been captured on Condition Report 2006-2703. A prompt investigation has been performed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-06-12
42632 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2006-06-12 10:56 | 2006-06-12 11:38 | 2006-06-13 | UNUSUAL EVENT DUE TO A POSTING OF HURRICANE WARNING AT THE SITE "Crystal River 3 is in a Hurricane Warning area. The site is evaluating the need for a plant shutdown at this time." The declaration of NOUE is per the licensee's Emergency Action Guidelines due to posting of the hurricane warning. There are currently no significant equipment problems or LCOs that might be impacted by the impending weather conditions. The licensee will provide updates as appropriate if weather conditions change or a decision to shutdown is made. The licensee notified the NRC Resident Inspector, State, and Local authorities. * * * UPDATE FROM M. WOLF TO M. ABRAMOVITZ AT 1530 ON 06/13/06 * * * The hurricane warning necessitating the entrance by the site into the Unusual Event was exited by the state this morning at 11 am. The site waited until high tide passed and exited the Unusual Event at 1511. The licensee notified the NRC Resident Inspector. Notified R2DO (Ayers), NRR EO (Jung), IRD (Blount), DHS (S. York) , and FEMA (E. Casto). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-06-12
42631 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2006-06-11 22:56 | 2006-06-12 02:35 | 2006-06-12 | LOSS OF 20% OF OFFSITE EMERGENCY SIRENS DUE TO SEVERE WEATHER "As of 10:56 P.M. EDT, [on 06/11/06] more than 20% of the offsite emergency sirens were inoperable for greater than one hour due to loss of power caused by severe weather/thunderstorms passing through the area. At 10:56 P.M. 21 of 81 sirens were out of service. At this time, the Harris Plant cannot estimate the time of siren recovery. However, crews are currently in the field surveying the damage and restoring power. This requires an 8-hour non-Emergency notification per 10CFR 50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. As of 01:40 A.M. 6/12/06, 16 of 81 sirens are out of service." The state and local emergency response organizations will implement compensatory measure of route alerting in the areas of the siren malfunction if needed during an emergency. The licensee notified the NRC Resident Inspector. The licensee also notified the North Carolina State EOC and the local counties of Chatham, Lee, Harnett, and Wake. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-06-12
42630 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2006-06-11 01:26 | 2006-06-11 03:51 | 2006-06-11 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO HIGH RCS DRYWELL LEAKAGE "At 01:26 on 6/11/2006 Nine Mile Point Unit 1 experienced a rise in drywell leakage of 2 gallons per minute increase of unidentified leakage in a 24 hour period [placing the Unit in an LCO] per Technical Specification 3.2.5.a.2. Present Drywell leakage is 2.33 gpm. "A normal orderly shutdown commenced at 01:26, per Technical Specification 3.2.5.b, [to] place the reactor in cold shutdown within 24 hours. "Drywell leakage has trended up very slowly over the past several weeks. On 6/10/2006 the plant reduced power, deinerted the primary containment, [and] attempted to repair packing leak on VLV-32-194. [This valve is a 1 inch drain valve on recirculation pump #12]. Following attempts to repair [the] valve, [the] plant inerted the primary containment [and] raised power to approximately 45% while main condenser tube cleaning continued. Unidentified drywell leakage began rising at a faster rate beginning on 6/10/2006 at 17:55." Drywell leakage has stabilized at a little over 2 gpm. The TS shutdown is required because of the 2 gpm increase in leak rate over the last 24 hour period. There are no other equipment operability concerns or TS LCOs that present a challenge to a normal safe plant shutdown. The licensee notified the NRC Resident Inspector. | 25 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-06-11
42629 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-06-08 11:00 | 2006-06-09 11:14 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * SMALL CHEMICAL SPILL INTO ENVIRONMENT "On June 8, 2006 at approximately 11:00 am, during a daily waste line inspection, dampness was observed in a pipe chase near the [DELETED] building. A test indicated that the liquid was acidic. Investigation into the incident revealed that a portion of the concrete chase underneath an onsite railroad spur/roadway had apparently fallen onto a copper nitrate and a pickle acid line. A small pool of blue liquid was seen under the pipes, indicating that the Copper Nitrate Line was damaged. "Area operations were informed, the copper nitrate production was shut down, and preparations have begun to excavate and repair the line. Approximately one gallon of waste solution was released. [The release was terminated by licensee.] "This concurrent report is being made because the event was reported to the following government agencies: EPA Region III - 215/814-3435, and Virginia DEQ - 434/582-5120" The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
42628 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-03-15 | 2006-06-08 18:14 | 2006-06-08 | LOUISIANA AGREEMENT STATE REPORT - EXCESSIVE EXPOSURE Louisiana Agreement State Report was faxed to the NRC Operation Center. "National Inspection Services reported on June 6, 2006 that a trainee, [deleted], received an excessive exposure. The film badge for [deleted] had an exposure of 5.879 Rem for the March 2006 wear period. This individual is no longer working for National Inspection Services. His employment ran from February 23, 2006 to April 26, 2006. The facility is performing an investigation and will report their findings to the Louisiana Department of Environmental Quality. [Deleted], Radiation Safety Officer, stated that the daily pocket dosimeter records do not reflect an excessive exposure." Event Report ID No.: LA060011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-06-13
42627 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-05-30 | 2006-06-08 15:58 | 2006-06-19 | AGREEMENT STATE REPORT - DAMAGED SOURCES The State provided the information via e-mail: "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): A patient received a total of 89 sealed Iodine-125 (half-life of 60 days) seeds implanted on a permanent basis in the prostate, for a total activity of 33.84 millicuries. This was done at Auburn Regional Medical Center (ARMC), Auburn, Washington, on 25 May 2006. "The patient was seen / rechecked by ARMC personnel on 26 May 2006. Sometime after that visit, on the same day, he was taken by family members to Good Samaritan Hospital (GSH) in Puyallup, Washington, where he subsequently died of a myocardial infarction. "The body was released to a funeral home in Buckley, Washington where it was cremated on 30 May 2006 (about 31 millicuries). The cremains were then boxed up on 31 May 2006 and buried that same day. "Although it was reported the patient and the patient's family were given appropriate verbal and written instructions by ARMC; when the patient was treated at GSH it was for the MI only, and had nothing to do with the prior surgical prostate procedure. The family did not, for whatever reason, inform the staff at GSH. The urologists who had treated the patient for the prostate cancer did not work at GSH and had no connection there. "Therefore, once the patient died, personnel at GSH had no idea they were also dealing with a radioactive source problem. Personnel at ARMC had no way of knowing of the treatment or death of the patient since it did not occur at their facility or in their city. "The RSO for Tacoma Radiation Oncology Center (who provides medical physics support and treatment planning for sealed source therapy to clients such as ARMC and GSH) visited the funeral home on 7 June 2006 and surveyed the crematorium using a meter with a NaI probe. Background was noted at approximately 0.4 mR/hr. Readings of approximately 3.0 mR/hr were noted at the entrance to the retort. A filter in the air exhaust system was noted to be reading approximately 1.0 mR/hr so it was removed for decay and ultimate disposal by GSH. "It appears that most retorts operate at 1600 degrees Fahrenheit, or more, and the titanium capsule would melt a few hundred degrees lower than that. The manufacturer confirmed that all seeds had most likely been melted and would not be recovered whole. The crematorium is at this time on standby until the crematorium is declared clean for further use. It appears the most reasonable way to safely handle this cleaning chore is to have a commercial cleaning company, properly informed and equipped, clean and vacuum the retort with ARMC physics personnel in constant attendance to protect workers from any potential radiation hazards and to remove any contaminated material for decay and disposal. This is scheduled to happen 8 June 2006. "Notification Reporting Criteria: WAC 246-221-240 "Isotope and Activity involved: Iodine 125 / 31 millicuries (at time of cremation) "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): to be determined, likely none. "Lost, Stolen or Damaged? (mfg., model, serial number): melted I-125 seeds. "Disposition/recovery: clean and hold material for decay "Leak test? NA "Vehicle: NA "Release of activity? Yes "Activity and pharmaceutical compound intended: NA "Misadministered activity and/or compound received: NA "Device (HDR, etc.) Mfg., Model; computer program: I-125 seeds "Exposure (intended/actual); consequences: minimal, likely no consequences "Was patient or responsible relative notified? Yes "Was written report provided to patient? Yes "Was referring physician notified? Yes "Consultant used? Yes" Event Report No.: WA-06-042 * * * UPDATE ON 06/19/06 AT 1900 FROM ARDEN SCROGGS TO A. COSTA * * * This incident was investigated by the WA Department of Health, Office of Radiation Protection and the Crematorium facility was released for use. Notified R4DO (Graves) and NMSS EO (Collins). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-06-13
42626 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-05-27 | 2006-06-07 09:11 | 2006-06-07 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "The density/moisture gauge was stolen from the West Gate Tavern's parking lot located at 2725 Mississippi in Metairie, Louisiana, which is in Jefferson Parish. The gauge was stolen sometime between the evening of May 27, 2006 and the morning of May 28, 2006. The theft was reported to the Jefferson Police Department on May 28, 2006. "The gauge was a Troxler Model T3440, Serial Number-20980, Source Activity: Cs-137 (8 millicuries, serial # 75-2404; Am-241:Be (40 millicuries), serial # 47-16481. Last leak test was March 17, 2006. "[The gauge operator] stopped to have a drink at the tavern on Saturday after performing a job at the Michoud Canal. He did not return the gauge to the Hahnville storage location before visiting the tavern. [The gauge operator] had to have someone pick him up from the tavern and bring him home; leaving the truck and the chained container with gauge in the Tavern's parking lot. When [the gauge operator] returned to the truck on Sunday, May 28, 2006, the gauge container (with the gauge in it) was cut from its chains and was gone. "The gauge container was chained and locked, and the gauge itself was locked at the time of the theft. The gauge was properly labeled with caution signs and contact phone numbers. The Department was notified immediately after the discovery of the stolen source. The facility spent countless hours trying to find the gauge. "More training was provided to the operator. The facility ordered eight new bolt-in containers to secure the gauges in the bed of the trucks to deter theft. The Radiation Safety Officer stated that he will probably have it put in the newspaper as well. He also stated that he will write a letter to the Department within 30 days with description of the incident including corrective actions." The state generated report number LA060009 for this event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-06-12
42625 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2006-06-07 08:15 | 2006-06-07 09:34 | 2006-06-07 | INADVERTENT RELEASE OF TOOLS WITH FIXED DETECTABLE CONTAMINATION An Earth Probe sampling machine had been free released from Connecticut Yankee and shipped to the Yankee Rowe Nuclear Power Plant site in April. [ Prior to the scheduled return of the machine to Haddam Neck], two items (shackle and pin) were found to have fixed detectable contamination [by Yankee Rowe personnel] in a tool box attached to the Earth Probe sampling machine. This is being conservatively reported and under investigation that [the contaminated tools] could have been placed in there at Yankee Rowe. Fixed contamination level is approximately 6000 dpm/100 square centimeters. The licensee has notified the Connecticut Department of Environmental Protection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-07
42624 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-05-22 | 2006-06-07 08:54 | 2006-06-07 | AGREEMENT STATE REPORT - UNSECURED DELIVERY OF RADIOACTIVE MATERIAL The State provided the following information via facsimile: "On May 22, 2006, a package containing 300 [microcuries] of I-123 in two (2) capsules was prepared for shipment at the Cardinal Health Nuclear Pharmacy Services ('Cardinal Health') facility in Dallas, TX. This package was a Type 7A container and was given a Yellow II label. This package was consigned to a contract courier, Tradewind, Inc., for delivery to Cardinal Health in Shreveport, LA. "Delivery of this package to Cardinal Health Shreveport was attempted sometime after it closed at 5:00 PM. It was discovered by a parking lot cleaning crew at approximately 11:30 PM that evening. The package had been left behind a dumpster outside the pharmacy and covered with a Tradewind jacket. The cleaning crew contacted the police, who arrived at the scene shortly afterwards and contacted the fire department, who dispatched a HazMat team. The police also contacted our pharmacist on call by using the emergency contact number posted on the outer vestibule door to our pharmacy. The fire and/or police departments took control of the material until a representative from Cardinal Health arrived on site. All radioactive material listed on the shipping paper was present and accounted for. "Root Causes: The cause of this event was a failure by the courier, Tradewind, to properly perform their contracted duties. The package in question was left unsecured behind a dumpster. This is not how Tradewind has been instructed to deliver packages to our pharmacy. They have been instructed to deliver radioactive material packages in a designated area (that is appropriately marked) inside the vestibule, in the rear of our building. Tradewind was issued a vestibule key for this sole purpose. "The driver who originally arrived to deliver the package did not have the vestibule key. An interview with him revealed that his intent was for another Tradewind driver to arrive later with the key and deliver the package into [licensee's] secured vestibule. "Actions Taken to Prevent a Recurrence: Cardinal Health will be working with Tradewind to review training documents required by the DOT and to formulate corrective measures taken to prevent reoccurrence of this type of event." LA Event Report ID No.: LA060008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-06-12
42623 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-05-22 04:00 | 2006-06-07 07:31 | 2006-06-07 | AGREEMENT STATE REPORT - ABANDONMENT OF WELL LOGGING SOURCE The State provided the following information via facsimile: "[Pathfinder Energy Services (licensee) notified the State of LA that] during drilling operations on 17 May 2006 the drill string became stuck while making a connection. The hole had packed off around the drill string not allowing circulation, up and down movement or rotation of the drill pipe. All reasonable effort was used to attempt to free the drill string. "[LADEQ Emergency & Radiological Services Division] was notified on 19 May 2006 that there might be a possibility of needing to abandon the sources over the weekend. He gave a verbal approval to abandon the sources and referred me [licensee] to [LADEQ] to follow up on Monday with the status of the abandonment. [LADEQ] was notified Monday 22 May 2006 that the sources were abandoned at 4:00 AM, 22 May 2006 and given details of the abandonment with the agreement that a formal report would be filed within 30 days of the abandonment. E-mail notification was also sent to Mr. Noble. "It became apparent on Sunday 21 May 2006 that the drill string would be lost. A 370 foot cement plug was set above the sources. A total of 22 joints of HWDP (675 feet) were left on top of the radioactive sources to act as a mechanical deflection device to prevent inadvertent intrusion on the sources. "A sidetrack well is planned to be drilled after 7 5/8" casing is set at 10,237' from the shoe to the original depth of 10,265 ft TVD. The sidetrack well is planned not to come within 15 ft of the sources. A liner (casing) will be set at completion of the bypass well and cemented in place. "Description of Sources: One 1.5 Curie, Cs-137, Doubly Encapsulated, Special Form, Well Logging Sealed Source Serial Number, 5080GW AEAT Model CDC.CY6 "One 8 Curie, Am-241/Be, Doubly Encapsulated, Special Form, Well Logging Sealed Source Serial Number: DNS 013 Gammatron Model AN-HP" THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-06-12
42622 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2006-06-06 16:00 | 2006-06-06 23:09 | 2006-06-15 | FAILURE TO MEET EMERGENCY EQUIPMENT SERVICE WATER SURVEILLANCE REQUIREMENT "On June 6, 2006 at 1600 EDT the Division 2 Emergency Equipment Service Water System (EESW) was in service for a planned surveillance test when the system failed to achieve required flows as specified in the surveillance. These flow rates are acceptance criteria and therefore resulted in system inoperability. EESW cools the Emergency Equipment Cooling Water (EECW) System which in turn cools various safety related components including the High Pressure Coolant Injection (HPCI) System Area Cooler. Unplanned HPCI inoperability occurred due to the Division 2 EECW/EESW inoperability based on loss of the HPCI System Area Cooler. A 14 day Limiting Condition for Operation (LCO) was entered for HPCI per LCO 3.5.1. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident, based on loss of a single train safety system." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 08:14 ON 6/15/2006 FROM JEFF GROFF TO ABRAMOVITZ * * * "On June 6, 2006 at 1600 EDT, during the performance of the quarterly pump and valve operability surveillance test on Division 2 of the Emergency Equipment Service Water System (EESW), the minimum pump flow required by the procedure to perform the test could not be established. Because minimum pump flow could not be established, Division 2 of EESW was declared inoperable. EESW cools the Emergency Equipment Cooling Water (EECW) System which in turn cools various safety related components including the High Pressure Coolant Injection (HPCI) System Area Cooler. HPCI was declared inoperable based on loss of the HPCI System Area Cooler due to the Division 2 EECW/EESW inoperability. A 14 day Limiting Condition for Operation (LCO) was entered for HPCI per LCO 3.5.1. A report was made to the NRC pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident, based on loss of a single train safety system. "On June 7, 2006, the test was re-performed with the valve in the bypass line around the heat exchanger Temperature Control Valve (TCV) throttled open. The required pump flow was established and the surveillance was successfully completed at 1815 EDT. "Further Engineering evaluation concluded that minimum pump flow could not be established on June 6, 2006 due to normal pump wear and heat exchanger fouling. The pump flow required for performing the pump and valve operability surveillance test was established to monitor pump degradation and is higher than the flow required for the EESW system to perform its safety function. It has been verified that the measured flow exceeds the system design basis required flow with an adequate margin and that the pump and heat exchanger remain adequate to support the HPCI room cooling operation. The HPCI safety function was maintained throughout this period; therefore, this event is being retracted." The licensee notified the NRC Resident Inspector. Notified the R3DO (Louden). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-06-06
42621 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-06-06 13:39 | 2006-06-06 19:40 | 2006-06-06 | LOSS OF "A" TRAIN OF OFFSITE VITAL POWER DUE TO RELAY TESTING "Callaway plant was in mode 1 at 100 percent power. Work was in progress on calibrating lockout devices on the B switchyard buss. At approximately 1339 CDT during performance of this work, Callaway plant experienced a loss of switchyard buss B. This resulted in loss of A train offsite power, load shed on A train vital 4160 volt buss (NB01), shutdown sequencer actuation for buss NBO1, start on the A train emergency diesel generator, turbine driven auxiliary feedwater pump actuations, [and] steam generator blowdown and sample isolations. B train offsite vital power and both emergency diesel generators were available. These actuations were consistent with loss of 1 vital AC train. Emergency systems responded as expected. "As of 1630 CDT, the plant is at 100 percent power. Power has been restored to the B switchyard buss. The normal offsite supply to bus NBO1 has been restored and the diesel generator secured. Determination of the cause of the lockout device actuation is in progress." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-06-06
42620 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2006-06-05 09:00 | 2006-06-06 18:06 | 2006-06-06 | AGREEMENT STATE REPORT - MEDICAL TREATMENT UNDERDOSE The licensee administered a 66% under dose during one of a series of brachytherapy doses to a patient. On June 6, 2006, during the second fractional dose in the series, the licensee noted that the administration of the dose took a longer time period than the dose administered to the patient on June 5, 2006. This was unexpected so the licensee performed a preliminary investigation. The licensee discovered that the computer used to time the dose incorrectly recorded the time taken for a quality control (QC) check and the dose time to the patient as one period of time. This was a first time use of this equipment by the licensee. The licensee determined that the patient received a dose of 116 centigray instead of 360 centigray during the administration of the first dose on June 5, 2006. A sealed 6 curie Ir-192 brachytherapy source manufactured by Varian was used. The licensee has informed the patient of the dose discrepancy. Additional controls have been implemented by the licensee to ensure that the computer will not record the time taken for the QC check as dose time to the patient in the future. The State of Oklahoma is following up on the report by sending an inspector to the site. *** UPDATE FROM STATE TO KNOKE AT 10:34 EDT ON 06/07/06 *** The State provided the following information via facsimile: "This was the first use of a new HDR modality mammosite treatment. The QC on this instrument was done prior to patient treatment. The treatment plan was sent from dosimetry computer to HDR control computer. Computer (or possibly human, not clear at this writing) chose the plan used from QC. Computer interpreted this to mean that a particular amount of dose had already been given. The computer delivered the remainder of dose, 116 centigrays, out of the prescribed 360 centigrays. Time was noted to be shorter than expected, but no alarm raised at the time. A second fraction was given later that day, and it was noticed that the time to deliver the dose was longer than in first dose. Inspection of computer records showed the dose had been stopped during treatment on the first fraction. It was then realized for sure that there was a problem. "Corrective Action: QC ACTIVITY WILL BE DONE IN A WAY THAT IT CANT BE CONFUSED WITH THERAPY." Notified NMSS (Wastler ) and R4DO (Runyan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2006-06-09
42619 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-06-02 09:30 | 2006-06-06 15:40 | 2006-06-06 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE The State provided the following information via facsimile: On June 1, 2006, a radiographer technician and an assistant from Team Industrial Services, Inc. performed multiple radiography exposures. After the 19th exposure, the radiographers reported "slightly more friction and resistance" when performing exposures at an elevated location. Approximately at 09:30, the final exposure was performed at an elevated location, the source was retracted with the fore noted additional resistance, and the "crank handle was rotated to the shielded position. No abnormal operation was noted and the lock plunger came up to the locked position. However, a survey of the exposure device is required by Team Industrial Services' Operating and Emergency procedures, the NRC and the LA DEQ [Louisiana Department of Environmental Quality]. No survey was performed." The radiographers then had difficulty disconnecting the source tube and control assembly. The camera was placed in the truck. The truck was then driven to the control room, to the OSI trailer, and to the shop. The radiographers then went to lunch. After lunch, the radiographers went to their shop, unloaded the camera and realized the source pigtail was not in the camera. The calculated worst case dose to Control Room personnel was 0.38 milliRem, to OSI trailer personnel was 20.7 milliRem, an inhabited office near the OSI trailer was 10.83 milliRem, and a second inhabited location near the OSI trailer was 29 milliRem. "At no time during the sequence of events did any unmonitored personnel approach the truck." Team Industrial Services, Inc. calculated the worse case dose for the technician as 13 Rem and the actual TLD dose was 1.1 Rem. The calculated worse case dose for the assistant was 14.5 Rem and the actual TLD dose was 2.2 Rem. These TLD doses included previous doses received in May. The licensee is performing radiation blood analysis on the two radiographers. Source: Ir-192, 40.5 Curies. Louisiana Report: LA060010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-06-09
42618 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2006-04-04 08:00 | 2006-06-05 12:32 | 2006-06-05 | AGREEMENT STATE - UNPLANNED EXPOSURE DURING TRAINING The State provided the following information via email: "The Kentucky Radiation Health Branch was notified on April 4, 2006, by [the licensee], Radiation Safety Officer for Varian Medical Systems, 700 Harris Street, Suite 109, Charlottesville, VA, NRC license no. 45-30957-01, of an incident involving an HDR unit at the University of Kentucky Medical Center. A 10.5 Ci [Curie] Ir-192 brachytherapy HDR source assembly (SS&D registry no. CA-1080-S-102-S) on a VariSource Brachytherapy HDR Remote Afterloader (SS&D Registry no. CA-0661-D-103-S) had been extended beyond the shielded source housing by manually turning the over ride handle on the emergency retraction system. The incident occurred during a training exercise simulating an emergency HDR source retraction involving a medical physicist and four (4) medical students. The unit was in the 'Idle' mode which disabled the internal GM and emergency retract system on the HDR unit. The source was recovered by the RSO and two Varian service representatives on April 7, 2006." The state is awaiting official notification of the actual doses received but reported that the highest dose was around 20-30 milliRem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2006-06-08
42617 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2006-06-03 15:45 | 2006-06-03 16:45 | 2006-06-03 | OFFSITE NOTIFICATION OF A FUEL OIL SPILL "At 1545, Turkey Point Unit 2, a Fossil Plant, reported a leaking fuel coil heater gasket which leaked approximately 500 gallons of #6 Fuel Oil. This leak occurred at 1100 this morning. Most of this fuel oil was captured in a berm. However, approximately 200 gallons of the oil drained into the cooling canals. "Miami-Dade DERM (Department of Environmental Resources Management) was notified at approximately 1430 and the State Warning Point was notified at approximately 1500." The licensee stated that the leak posed no threat to the operation or safety of Units 3 and 4. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-06-03
42616 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-06-02 10:00 | 2006-06-02 14:17 | 2006-06-02 | AGREEMENT STATE REPORT - ILLINOIS - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via email: "On June 2, 2006, [the] Radiation Safety Officer [for] STATE Testing, LLC, (Radioactive Material License No. IL-1015-01), called to report that a CPN moisture density gauge, Model MC-1, serial no. MD 10900497, was stolen from one of their marked construction vehicles sometime after midnight before six in the morning. The theft occurred while the device was at the operator's home [redacted]. The operator discovered the Ford Ranger truck had been broken into this morning when he was preparing to go to the jobsite. The gauge was reportedly secured in the back of the truck under a locked truck cap by means of a padlock and chain. The operator indicated that the gauge had been further padlocked in the 'off' position. Additional construction equipment that had been locked in the truck was also stolen during the break in. Chicago Police have been contacted and are investigating. "An inspector was sent to the company's 570 Rock Road, East Dundee offices this morning to conduct interviews and gather additional information." Illinois Report Number IL-060029 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [10 empty] | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-06-07
42615 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-06-02 09:52 | 2006-06-02 12:41 | 2006-06-02 | FITNESS FOR DUTY REPORT INVOLVING LICENSED OPERATOR "At approximately 0952 CDT a licensed operator failed a random fitness for duty test administered by the station. The individual tested positive for alcohol. The individual was not performing license activities today. The individual's access to the site has been blocked." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2006-06-02
42614 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-06-01 11:55 | 2006-06-01 16:50 | 2006-06-02 | AGREEMENT STATE REPORT - CALIFORNIA - STOLEN MOISTURE DENSITY GAUGE The State of California reported that a moisture density gauge (make, model, and serial number unknown at this time) was stolen from a vehicle used by the licensee. The details and circumstances of the theft are not presently known by the State. An inspector will be sent to the licensee tomorrow to conduct a detailed investigation. The licensee has notified the San Francisco Police Department. * * * UPDATE FROM CALIFORNIA (HEWADIKARAM) TO HUFFMAN AT 1355 EDT ON 6/02/06 * * * The State provided the following information via facsimile: "On 06/01/06, the RSO at Treadwell & Rollo called the RHB (California Radiologic Health Branch) -Sacramento office to report that one of their CPN moisture, density gauges was stolen from a vehicle parked in San Francisco. The NRC operational center was informed of the Incident via telephone on the same day of the incident by RHB. On 06/02/06 RHB-Richmond office contacted the RSO and learned the following: "The CPN gauge Model MC3, S/N M340107275 containing 10 mCi of Cs-137 and 50 mCi of Am-241 was stolen from a vehicle (SUV) parked in San Francisco near the resident of a Treadwell & Rollo employee. The location was in the vicinity of 7th and Natoma streets in San Francisco. On 05/31/06, the employee returned home from a job site around 10:00 pm and left the gauge in the back of the vehicle without returning it back to their storage location in San Francisco. He noticed that the gauge was stolen when he returned to the vehicle around 7:00 am on 06/01/06. The gauge was stored in the back of the SUV with two locks on the Type A container and covered with a tarp. It was not clear whether the gauge was chained to the vehicle. The vehicle was broken into through the window and the gauge was stolen by cutting the two clasps of the Type A container above the locks. RSO will be providing photographs of the Type A container. RSO immediately notified SFPD of this incident. He had posted a reward for $ 1000.00 on the Craig's list and this reward will also appear In the San Francisco Chronicle on 06/03/06. The RHB will be investigating this incident and a notice of violation will be issued to the licensee for the items of non compliance." The R4DO (Whitten) and NMSS EO (Morell) were notified. The update was also sent to ILTAB and Mexico via E-mail. CA Report Number 06/01/06. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-06-06
42613 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-06-01 09:43 | 2006-06-01 12:33 | 2006-06-01 | TECHNICAL SUPPORT CENTER HVAC INOPERABLE "During surveillance testing of 1R43S001B Emergency Diesel Generator 1B (swing EDG) from Unit 2 controls, 1R24S026 EDG 1 B Motor Control Center (MCC) did not transfer from Unit 1 power supply to Unit 2 power supply resulting in 1R24S026 being de-energized. MCC 1R24S026 provides power to Technical Support Center (TSC) HVAC which resulted in TSC HVAC being inoperable. Corrective work activities are in progress to expeditiously return the TSC HVAC back to service. "If an emergency condition requiring activation of the Technical Support Center (TSC) occurs during the time the HVAC is inoperable, then contingency plans call for utilization of the TSC as long as radiological conditions allow. The Technical Support Center Activation procedure provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the TSC so that TSC functions can be continued." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-06-01
42612 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2006-05-31 11:30 | 2006-06-01 11:25 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * CRITICALITY EVACUATION ALARM FAILURE On Wednesday, May 31, 2006, at 1130 hours, it was determined that the criticality accident alarm system (CAAS) was not capable of providing a [DELETED] Complex site-wide evacuation alarm in the event of a criticality. There were no indications on the system control panel indicating a problem with the system. Specifically, the power light was on and there were no trouble alarms at the panel. Preliminary troubleshooting indicates a short in one of the cards in the central panel. The local control panels in each of the buildings appear to be operating normally. However, an alarm at the local control panel will not initiate the [DELETED] Complex site-wide evacuation alarm. This condition may have existed since May 1, 2006. No actual safety consequences occurred as a result of this event; however, there was a risk of potential health and safety consequences to the occupational workforce, involving significant radiation exposure from an accidental criticality event with no warning alarm to initiate prompt [DELETED] Complex site-wide evacuation. The potential risk was significantly lessened after May 15 when all licensed activities at the [DELETED] Complex stopped except for the operation of the Effluent Processing Building, which contains negligible amounts of uranium. On May 20, 2006, a severe thunderstorm passed over the [DELETED] Complex, and a lightning strike caused some electronic components throughout the plant to stop working or function erratically. On May 24, 2006, an indication of a communication system failure in the CAAS was identified. There are two circuits in the system, one is for communications between the individual detectors in each of the buildings and the other circuit is for the alarms. There was no indication of the general system failure that was later observed on May 31. The communication system was repaired and tested successfully. Between May 24 and May 31, instrument technicians were performing regular calibrations of instruments throughout the plant and identified a few instruments that appeared to be affected by the lightning strike. Based on this evidence, and knowledge of the design of the CAAS, the [DELETED] Complex Maintenance Manager recommended to the Plant Manager that the criticality system be tested to ensure it was not affected prior to performing any licensed activities, although there was no direct evidence at that time that the system was affected. It was decided that this testing should take place on May 31. [DELETED] Complex operations are in safe standby condition and will not be resumed until the CAAS is fully functional. The licensee notified the NRC Resident Inspector and Region 2. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-11
42611 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-05-30 09:23 | 2006-05-31 14:15 | 2006-05-31 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM INOPERABLE "Control Room Emergency Filtration System (CREFS) was declared Inoperable at 0923 on 5/30/2006 per TS 5.5.10.c 'Ventilation Filter Testing Program'. Laboratory testing results of a sample of the charcoal adsorber taken on 5/2/2006 did not meet the methyl iodide penetration percentage acceptance criteria of less than or equal to 1.0%. This condition is covered by TS 3.7.9 and both Unit 1 and Unit 2 entered Condition A, 'CREFS Inoperable' with a Required Action of 'Restore CREFS to OPERABLE status' with a Completion Time of 7 Days. "CREFS is a single train system. Based on the guidance in NUREG-1022 for single train systems that perform safety functions, this condition was determined to be reportable under 10 CFR 50.72(b)(3)(v), 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function'. Technical Specifications allow this system to be inoperable for a period of seven days. "This condition was not reported within the 8 Hour Non-Emergency reporting requirements." The charcoal has been replaced and the licensee estimates testing at approximately 17:00. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-05-31
42610 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-05-30 17:00 | 2006-05-30 20:02 | 2006-06-02 | MANUAL REACTOR TRIP ON HIGH TURBINE VIBRATION "At approximately 1700 hours on May 30, 2006, with Watts Bar Nuclear Plant Unit 1 operating normally at 100% power, main turbine vibration increased to a value above the procedure limit and reactor operators manually tripped the reactor in accordance with site procedure requirements. All control rods inserted and the auxiliary feedwater system automatically actuated per design. No other significant equipment issues were identified and the reactor was stabilized in mode 3. "This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) for the manual reactor trip (4-hour report) and under 10 CFR 50.72(b)(3)(iv)(A) for the RPS and AFW actuations (8-hour report). "Watts Bar had been monitoring indications of slightly elevated turbine vibration on the main turbine, but the reason for the increase above the procedure limit of 14 mils is not known at this time. TVA will be investigating the cause of the increased vibration to make necessary repairs before turbine startup." Decay heat is being removed by dumping steam to the main condenser. No safety or relief valves lifted. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (R. CREWS) TO M. RIPLEY 0020 EDT 06/02/06 * * * "As a result of the initial assessment of the turbine vibration discussed above, TVA has identified damage to the turbine end of the 'C' low pressure turbine. This is consistent with the initial indications of high vibration on the number 7, 8 and 9 bearings and not thought to be associated with previous condition monitoring of the number 11 bearing. Assessment and repair of secondary plant components damaged in the transient are in progress." The licensee will notify the NRC Resident Inspector. Notified R2DO (C. Ogle) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-05-30
42609 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2006-05-30 08:13 | 2006-05-30 16:14 | 2006-05-30 | LOSS OF POWER TO TRAIN "A" 4 KV SAFETY BUS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR50.73. "On May 30, 2006, at approximately 08:13 Mountain Standard Time, Palo Verde Nuclear Generating Station, Unit 1 experienced a Loss Of Power (LOP) to Train 'A' (PBAS03) 4 KV safety bus. At the time of the LOP the 'A' Emergency Diesel Generator (EDG) had just been manually removed from the PBAS03 bus following a maintenance surveillance run and was still operating in a post run cool down mode. The PBAS03 bus was still powered from the off site power source and was at rated voltage. An invalid Load Shed signal was received from the Train 'A' Load Sequencer, which opened the normal off site supply breaker to PBAS03 bus, and stripped all of the Ioads off the bus. Next, a valid LOP signal developed, since the PBAS03 bus was de-energized. The EDG 'A' received a valid emergency run mode signal and returned to rated frequency and voltage; however its output breaker did not reclose on bus PBAS03. This reclosure was blocked by the Train 'A' Load Sequencer which had 'stalled' and was not able to provide the permissive for the DG output breaker to close. The failure of the load sequencer is currently under investigation by the PVNGS engineering department. "Offsite power was available to both safety buses throughout the event; however the invalid Load Shed signal blocked immediate restoration of off site power to the Train 'A' bus. The other (Train 'B') safety bus is being supplied by offsite power; however Train 'B' EDG is not available due to planned outage related maintenance. The offsite electrical grid is stable. Efforts are currently in progress to restore the Train 'B' DG for a redundant power source. In addition, efforts are in progress to clear the Load Shed signal off the Train 'A' bus to allow restoration of power from the off site power source. "Palo Verde Unit 1 is shutdown and Defueled in a mid-cycle repair outage. The entire core is off loaded to the Spent Fuel Pool and is currently being maintained with inventory and cooling by the Train 'B' components powered from off site power. No other ESF actuations occurred and none were required. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." At 13:04 MST the 'B' EDG was restored and operable. The licensee also indicated that Train 'A' offsite power is expected to be restored within about 1 hour, or 16:20 EDT. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-05-30
42608 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-05-30 02:45 | 2006-05-30 05:10 | 2006-05-30 | OFFSITE NOTIFICATION MADE DUE TO INADVERTENT EMERGENCY SIREN ACTIVATION "On May 30, 2006, at approximately 0245 CDT, Fort Calhoun Station was notified of inadvertent single siren activation by a Washington County Sheriff Deputy. No actual Emergency exists and no testing is in progress. Local radio station KFAB was notified to broadcast an inadvertent siren activation message. Siren number 27, which is located 5.5 miles South of Blair, NE on State Highway 133, was activated as a result of adverse weather conditions. Crews have been dispatched to repair the failed siren." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-05-30
42607 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2006-05-27 17:14 | 2006-05-28 01:10 | 2006-05-28 | EXCESS TEMPERATURE IN ROOM HOUSING SAFETY FUNCTION SYSTEMS "At 1714 the Division II electrical buses were declared inoperable due to room temperatures greater than 104 F. The appropriate 24 hour LCO was entered. The C.4 abnormal procedure for loss of ventilation was entered. The procedure stated to consider opening doors in the area to provide additional ventilation. Doors were opened for additional cooling. The procedure states to declare ALL Division I 4KV equipment inoperable. At that time both 15 and 16 emergency buses were inoperable. At this time, this condition could have been prevented the fulfillment for Safety Function Systems needed to remove residual heat and mitigate the consequence of an accident. At 1745 the ventilation was re-adjusted and temperature returned the less than 104 F. All doors were closed and the 24 hour LCO exited." The licensee will notify this incident to the NRC Resident Inspector and the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2006-05-28
42606 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2006-05-26 14:15 | 2006-05-26 17:27 | 2006-05-27 | SOLID STATE PROTECTION SYSTEM TRAIN INOPERABLE "Beaver Valley Unit 1 commenced a Technical Specification required shutdown at 1415 hours due to Train B Solid State Protection System inoperable. The condition was discovered during testing and the Unit is required to be in Mode 3 by 1846 hours. Train A of Solid State Protection System remains operable and in service. Investigation of the Solid State Protection problem is in progress." The licensee believes that the problem is caused by a faulty memory card. They are continuing to investigate the problem. The unit was at 18% power at 1727 EDT on the way to mode 3. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/27/06 AT 0114 EDT FROM R. GREEN TO A. COSTA * * * "Beaver Valley Unit 1 entered mode 3 at 1831 hours on 5/26/06. Train B Solid State Protection was repaired and tested satisfactorily. It was returned to OPERABLE status at 1915 hours on 5/26/06. The failure was in the memory portion of the universal logic card in the low power trip block circuitry. A root cause investigation is ongoing. All technical specifications action statements were exited when Train B Solid State Protection was declared OPERABLE. Reactor start up is planned for 0500 on 5/27/06." The licensee will notify the NRC Resident Inspector. Notified R1DO (M. Gray). | 18 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-05-26
42605 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2006-05-24 21:02 | 2006-05-24 21:52 | 2006-05-24 | UNUSUAL EVENT FOR A FIRE LASTING GREATER THAN TEN MINUTES Licensee declared an Unusual Event due to a fire that was not extinguished within 10 minutes - EAL U4A. There were no flames, only smoke. Control Room received a Bus 2 ground alarm, reduced power, secured the B Main Feedwater Pump, inserted control rods below the Maximum Extended Load Limit Analysis (MELLA) line, and then secured the C Condensate Pump. The ground alarm cleared after securing the C Condensate Pump. CO2 discharged automatically into the switchgear room due to the smoke in the switchgear room. The switchgear room has been ventilated, site personnel have entered and no other damage to the switchgear has been identified other than the C Condensate pump breaker. Offsite Fire (Vernon Fire Department) responded to the site and is assisting with ventilation. One ambulance is responding to transport a Fire Brigade member that is not feeling well due to heat. The licensee has notified the NRC Resident Inspector, and State and Local emergency response organizations. Notified R1 PAO (Screnci). * * * UPDATE PROVIDED BY KELLY ROBINSON TO JEFF ROTTON AT 2239 ON 05/24/06 * * * Licensee called to terminate the Unusual Event. The plant is in a stable condition with no other outstanding problems. Ventilation of the switchgear room is continuing and air samples are being analyzed. The licensee has notified the NRC Resident Inspector, and State and Local emergency response organizations. Notified R1 (Holian, Powell, Bores), IRD (Blount), NRR EO (Haney), R1DO (Gray), DHS (Lee) and FEMA (Casto) | 56 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | VT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-05-24
42604 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-05-24 | 2006-05-24 21:00 | 2006-05-24 | AGREEMENT STATE REPORT - SOURCE FOUND ON BEACH "The NC Radiation Protection Section was notified of an event involving the discovery of an item labeled 'US Radium Corp.' in the Onslow Beach area (jurisdiction unknown at this time). This item is described as approximately 2 inches in diameter, ¼ inch thick and silver in color. Preliminary radiation surveys are reported as 7 mR/hr with a background of 1.5 mR/hr. These surveys were reported by Camp Lejeune firefighters. Reported by the Base firefighters, three people associated with the discovery of the item were taken to the Base hospital as a precaution after being 'decontaminated.' The Base RSO is responding and will be in contact with the NC Radiation Protection Section which has offered full assistance." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-05-29
42603 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2006-05-24 10:38 | 2006-05-24 16:46 | 2006-05-24 | UNANALYZED CONDITION DISCOVERED DURING POST-FIRE SAFE SHUTDOWN AREA REVIEW "While performing a post-fire safe shutdown area review for fire area C-35, it was discovered that a design basis fire in this area could prevent operation of both Class 1E Electrical Equipment air-conditioning units (SGK05A and SGK05B). The Class 1E Electrical Equipment air conditioning units provide temperature control for equipment required for safe shutdown in the Class 1E switchgear rooms (ESF switchgear rooms, DC switchgear rooms, and NK battery rooms). A fire in fire area C-35 could impact fire protection panel KC230 and cables associated with the automatic shutdown feature for the air conditioning units. The automatic shutdown feature normally operates whenever a fire occurs in any of the Class 1E switchgear rooms prior to Halon fire suppression operation. A fire in fire area C-35 could result in the inability to operate the air conditioning units and provide the necessary temperature control for equipment required for safe shutdown. "Compensatory measures: a continuous fire watch was established for fire area C-35, a temporary procedure change will be completed to allow use of a jumper to restore Class 1E air conditioning unit (SGK05A) to service, if required, at which time the continuous fire watch will be changed to an hourly watch." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-05-24
42602 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-05-24 15:00 | 2006-05-24 15:52 | 2006-05-24 | FLORIDA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE While licensee employees were eating at a restaurant located at 8363 W. Flagler Street, Miami, FL, the licensee's Troxler moisture density gauge was stolen from the bed of the pickup truck. The licensee reported that the gauge sources were in the stored position, the handle for the gauge was locked and the transport case was locked and chained to the bed of the truck. The chain had been cut and the gauge was missing after returning to the truck after eating. The Troxler was a model 3440, Serial number 24153 containing 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be. The licensee notified the Miami Police Department, but they had not arrived at the scene at the time of this report. The State of Florida will be conducting an investigation into this incident. Florida Incident Number: FL06-75 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-05-29
42601 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2006-05-24 08:05 | 2006-05-24 09:35 | 2006-05-24 | OFFSITE NOTIFICATION " [An] inadvertent release of radioactive contaminated material, specifically three items/tools had fixed contamination, [was reported to the Connecticut State Police and Department of Environmental Protection]. The tools were located on a truck which had left the site previous to the discovery of contamination. The maximum [fixed] contamination level is 1400 corrected counts per minute (ccpm) (approximately 14,000 disintegrations per minute per 100 square cm)." The incident occurred on May 18, 2006. It was discovered when personnel were observed passing tools across a boundary line. Further investigations determined that the truck had left the site with the tools. All tools were accounted for, labeled as radioactive material and stored in a radioactive material area. Surveys of the truck indicate that there was no spread of contamination and there was no personnel contamination. The licensee notified the NRC Resident Inspector and NRC Region 1. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-05-24
42600 | 0 | MUNSON MEDICAL CENTER |  |  |  |  | 2006-05-22 14:00 | 2006-05-23 10:23 | 2006-05-23 | HOSPITAL INFORMED OF PREGNANCY AFTER DOSE On 5/3/06 Munson Medical Center administered a 150 mCi oblation dose of I-131 for thyroid cancer to a patient. Before the dose was administered the patient signed a form indicating that she was not pregnant. The dose was dispensed to the patient around 10 am. On 5/22/06 the patient called Munson Medical Center indicating that she had discovered that she was pregnant at the time of the dose. The licensee determined a calculated dose to the unborn child of 40 Rem. The patient was not yet informed of the dose to the unborn child at the time of the report. Expected medical effects of the dose are either immediate abortion or no harm since at the time of the dose organ development was not expected to have occurred. The licensee is reviewing their current policy to determine actions to prevent recurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3047(a) |  |  |  | 0 | 2006-05-23
42599 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2006-05-23 10:08 | 2006-05-23 10:25 | 2006-05-23 | LOST SPECIAL NUCLEAR MATERIAL "In Event Notification 42597 on May 22, 2006 Pilgrim Nuclear Power Station notified the NRC that during ongoing activities to remove non-fuel material from the Pilgrim Spent Fuel Pool it had been identified that an irradiated neutron detector containing a very small quantity (less than 0.003 grams) of special nuclear material is not in its expected location. Per the inventory sheets the neutron detector should have been enclosed in a 'dry tube' in the Spent Fuel Pool. Processing of the 'dry tube' for shipment identified that the neutron detector is not in its expected location. "There were a total of twelve (12) 'dry tubes' that our records show enclosed neutron detectors. Four (4) of these 'dry tubes' have been processed and a second 'dry tube' in which no neutron detector was stored has been found. This irradiated neutron detector would have contained a very small quantity (less than 0.003 grams) of special nuclear material. "This condition is being conservatively reported under 10CFR74.11. There is no evidence of theft or diversion. "Investigation is continuing." The licensee notified the NRC Resident Inspector. SEE UPDATED EN#42597 ON 5/26/06. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 74.11(a) |  |  |  | 0 | 2006-05-23
42598 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-05-23 08:00 | 2006-05-23 09:47 | 2006-05-23 | TSC VENTILATION TAKEN OUT OF SERVICE FOR MAINTENANCE "Planned preventive and corrective maintenance activities are being performed today (May 23, 2006) on the Hatch Nuclear Plant's Technical Support Center (TSC). These work activities are planned to be completed today within the (12) hour day shift. These maintenance activities include the performance of preventive maintenance on the TSC air handling unit and the TSC condensing unit, replacement of the door seal on the TSC west entry door, replacement of the existing electro-mechanical timer for the TSC condensing unit with a digital timer and replacement of the contactors on the TSC condensing unit. During the time these activities are being performed, the TSC air handling unit, TSC condensing unit, TSC filter train and the fan unit for the TSC filter train will not be available for operation. As such, the TSC HVAC will be rendered non-functional during the performance of this work activity. "If an emergency condition requiring activation of the TSC occurs during the time these work activities are being performed, then contingency plans call for, utilization of the TSC as long as radiological conditions allow. Procedure 73EP-EIP-063-0, Technical Support Center Activation, provides instructions to direct TSC management to the Control Room and TSC support personnel to the Simulator Building to continue TSC activities if it is necessary to relocate from the TSC so that TSC functions can be continued. "This event is reportable per 10CFR50.72(b)(3)(xiii) as described in NUREG-1022, Rev. 1 since this work activity affects an emergency response facility for the duration of the evolution." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-05-23
42597 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2006-05-22 22:00 | 2006-05-22 22:05 | 2006-05-26 | SPECIAL NUCLEAR MATERIAL (.003 GRAMS) LOST During ongoing activities to remove non-fuel material from the Pilgrim Spent Fuel Pool it has been identified that an irradiated neutron detector containing a very small quantity (less than 0.003 grams) of special nuclear material is not in its expected location. Per the inventory sheets the neutron detector should have been enclosed in a "dry tube" in the Spent Fuel Pool. Processing of the "dry tube" for shipment identified that the neutron detector is not in its expected location. This condition is being conservatively reported under 10CFR74.11. There is no evidence of theft or diversion. Investigation is continuing. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/26/2006 AT 15:25 FROM MICHAEL McDONNELL TO ABRAMOVITZ * * * "In Event Notifications 42597 and 42599 on May 22 and May 23, 2006, respectively, Pilgrim Nuclear Power Station notified the NRC that during ongoing activities to remove non-fuel material from the Pilgrim Spent Fuel Pool it had been identified that 2 irradiated neutron detectors containing very small quantities (less than 0.003 grams each) of special nuclear material were not in their expected locations. Per the inventory sheets the neutron detectors should have been enclosed in 'dry tubes' in the Spent Fuel Pool. Processing of the 'dry tubes' identified that the neutron detectors are not in their expected locations. "There were a total of twelve (12) 'dry tubes' that our records show enclosed neutron detectors. As part of the investigation associated with Event Notification 42597, all twelve (12) of these 'dry tubes' have been inspected. Three (3) of the 'dry tubes' were found to contain neutron detectors consistent with plant records. Nine (9) of the 'dry tubes' were found to contain no neutron detector which is not consistent with the plant records. The irradiated neutron detectors would have each contained a very small quantity (less than 0.003 grams each) of special nuclear material. "This condition is being conservatively reported under 10CFR74.11. There is no evidence of theft or diversion. "Investigation is continuing." The licensee notified the NRC Resident Inspector. Notified IRD (Blount and Leach), R1DO (Gray), NRR (Haney), ILTAB (English), DHS SWO (Cassandra), FEMA (S. Kimbrell), DOE (Ronnie), EPA (Crews), USDA (Margaret), and HHS (Marcy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 74.11(a) |  |  |  | 0 | 2006-05-22
42596 | 0 | NDT REPAIR SERVICE, INC. |  |  |  |  | 2006-04-18 | 2006-05-22 16:32 | 2006-05-22 | PART 21 NOTIFICATION - NDT EQUIPMENT FAILURE The State provided the following information via facsimile: "Per the requirements of 10 CFR Part 21 this letter has been written to inform you of a reportable condition in regards to a Crankout Assembly Failure Reported by Team Industrial Services on April 18, 2006, Event# 42508, and on May 08, 2006, Event# 42561. "On May 8, 2006, NDT Repair Service was notified, by Team Industrial Services, of an equipment failure during radiographic operations using one of our Control Assemblies (PN# RT1117 25ft Control Assembly For Use with AEA-QSA 6608 Exposure Device). It was noted to us that the Control Assembly could be connected to the exposure device without connecting the drive cable to the source assembly. The Exposure Device could then be put into the operation mode and the source could then be cranked out therefore causing a misconnect; which violates the ANSI N432-1981, Section 6.1.4, as required by 10 CFR Part 34. "NDT Repair Service immediately halted distribution of Control Assemblies for the AEA-QSA 6608 Exposure Device pending investigation of the probable cause of the failure. After further investigating into the cause of the failure it was found, that, the basic component that caused the failure was the Control Adapter, which is part of the Control Assembly that connects to the Exposure Device. "Through further internal investigation, NDT Repair Service was able to limit the potential problem to 1 lot of 25 Control Adapters that we took delivery of on November 13, 2003 and it was noted that 9 of the 25 adapters were out of tolerance and needed rework. The Root Cause of the defect in the control adapter was found to be that back stops for the drive cables were drilled too deep allowing the adapter to hook up to the exposure device without connecting to the source assembly, therefore allowing the source to be cranked out and causing a misconnect." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | LA | OTH | PAR | 21.21 |  |  |  | 0 | 2006-05-22
42595 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-03-26 03:47 | 2006-05-22 13:11 | 2006-05-22 | 60 DAY NOTIFICATION - INVALID ACTUATION OF HIGH PRESSURE CORE SPRAY PUMP "The following 60-day report is being made under 50.73 (a)(2)(iv)(A) for an invalid actuation of the High Pressure Cory Spray pump that occurred at 0347 hours on March 26, 2006. As allowed by 10CFR50.73(a)(1) this notification is being made via telephone. NUREG-1022, Revision 2 identifies the information that needs to be reported as follows: "(a) The specific train(s) and system(s) that were actuated. "On March 26, 2006 at 0347, the Division 4 Nuclear System Protection System (NSPS) power was lost due to a loss of the Division 4 NSPS inverter. The High Pressure Core Spray (HPCS) pump started automatically as a result of this failure. This response is identified in the Operations bus outage procedure as a potential impact of the loss of Division 4 NSPS and was considered expected. Immediate actions were taken to secure HPCS and declare it inoperable. "An Apparent Cause Evaluation was performed. The apparent cause of the loss of Division 4 NSPS Inverter was determined to be the age related failure of the Z111 voltage regulator on the 12 Static Switch logic card. "(b) Whether each train actuation was complete or partial. "The automatic start of High Pressure Core Spray was partial since the 1E22-F004 HPCS Injection Valve does not receive an open permissive when the Division 4 NSPS Inverter is deenergized. "(c) Whether or not the system started and functioned successfully. "The start of High Pressure Core Spray pump was successful and functioned properly in the minimum recirculation flow mode." The licensee notified the NRC Resident Inspector. | 80 | 0 | 0 | 80 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-05-22
42594 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-05-22 07:01 | 2006-05-22 10:13 | 2006-05-22 | MANUAL REACTOR SCRAM AS A MITIGATING ACTION DUE TO LOWERING SERVICE AIR PRESSURE "CNS was operating at 100% power at 06:51 CDT on May 22, 2006 when Plant Service Air pressure began lowering due to an unknown cause. Additional Service Air Compressors could not be started in time to recover Service Air pressure. A rapid power reduction was performed and at 07:01 the reactor was manually scrammed as a mitigating action due to lowering Plant Service Air pressure. All control rods fully inserted and a Group 2 Isolation occurred due to low Reactor Vessel level as expected following the manual scram. Minimum Reactor level was -20 inches Wide Range. The reactor is currently shutdown and stable with level maintained at 35 inches in the green band on the Narrow Range Indicators with the Feedwater System. Reactor pressure following the scram was stabilized at approximately 900 psig using the Main Condenser Bypass Valves and is slowly lowering. "This report is made in accordance with 10CFR50.72 as a 4 Hour Report due to a valid RPS actuation and as an 8 Hour Report due to a valid Group 2 Isolation actuation. All automatic actions functioned as expected. The plant is being maintained in Hot Shutdown while the cause of the Plant Service Air Pressure lowering is being investigated. The NRC Senior Resident inspector has been informed of the event." The scram was characterized as uncomplicated. The licensee is not in any significant tech spec LCO and all systems functioned as required. It was noted that there are 3 service air compressors available and only one of the compressors was running at the time of the event. The licensee does not yet know the cause of the service air pressure loss or why the backup compressors did not autostart. Instrument air pressure was maintained during the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-05-22
42593 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-05-21 | 2006-05-21 18:38 | 2006-05-22 | AGREEMENT STATE REPORT - STOLEN I-131 CAPSULE The licensee (IsoRx) reported to the State of California that their vehicle was broken into at Modesto, CA and a 2 milliCurie capsule of I-131 was taken. IsoRx is a Nuclear Pharmaceutical company operating in San Francisco, CA. The owner and RSO is on his way to Modesto to investigate this matter. The State of CA told licensee to contact the Modesto police and fill out a report. * * * UPDATE PROVIDED FROM KENT PRENDERGAST TO JEFF ROTTON AT 1616 EDT ON 05/22/06 * * * The initial report from the State of California claimed that the vehicle was broken into in Modesto, CA. That was reported incorrectly and is being revised by the update provided below. The State provided the following information via email: "On 5/21/06, the RSO at IsoRx called Kent Prendergast [State of California] to report a theft of about 2 mCi of I-131 capsule from a trunk of a IsoRX vehicle that was parked at Myrtle Street between Park and Larkin in San Francisco. Immediately after the incident, the RSO and [Deleted] (CHP) surveyed a four block area around the theft site with a Ludlum Model 3, (S/N 197096, PR 207476) micro R meter. A thorough survey of the vehicle was also performed. None of the surveys indicated any elevated readings above background. The RSO also conducted a ground search of the area with the pharmacy personnel and spoke with local 'street people' to uncover any information. A reward was also offered for the capsule. RSO filed reports with OES and SFPD. The RSO will be sending a formal report to the RHB regarding the incident." Notified R4DO(Shaffer) and NMSS EO (Burgess) and ILTAB(via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injured someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-05-24
42592 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-05-20 14:21 | 2006-05-20 16:15 | 2006-05-21 | UNUSUAL EVENT - REACTOR TRIP OF BOTH UNITS DUE TO LOSS OF ALL OFFSITE POWER The licensee experienced a reactor trip to Units 1 & 2 due to loss of all offsite power. This anomaly was believed to be from an overcurrent condition in a relay, and limited to the Catawba switchyard. The reactor tripped due to actuation of the reactor protection system (RPS), and all rods for both Units fully inserted as designed. The Unit 1 Pressurizer PORV did lift momentarily. The decay heat is being released through the secondary PORV's, and steam generator level is being maintained with the auxiliary feedwater system (AFW). Presently, Units 1 & 2 are in EAL 4.5.U.1 (Loss of Offsite Power to Essential Busses for greater than 15 minutes). The licensee indicated there are no steam generator tube leaks in either unit. The licensee activated the TSC at 15:50 EDT. The licensee notified the NRC Resident Inspector, as well as State and local government. * * * UPDATE FROM SI BILLENGER TO HUFFMAN AT 0152 EDT ON 5/21/06 * * * The licensee terminated from the Unusual Event at 0140 EDT on 5/21/06 based on restoration of offsite power to all essential buses. The licensee is no longer in a Tech Spec cooldown LCO and both units have secured from further cooldown and have stabilized conditions in Mode 3. Both units are still on natural circulation with AFW cooling and decay heat removal through secondary PORVs. The licensee will notify the NRC Resident Inspector. R2DO (Widmann), NRR (Ross-Lee), IRD (Blount), FEMA (Kimbrell) and DHS(York) have been notified | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-05-20
42591 | 0 | SULZER PUMPS, INC |  |  |  |  | 2006-05-20 | 2006-05-20 12:44 | 2006-05-20 | PART 21 - SULZER PUMPS, INC. The licensee provided the following information via facsimile: "Pursuant to Title 10, Code of Federal Regulations, Part 21, reporting requirements, Sulzer Pumps (US), Inc. is reporting a deviation from technical requirements for components to be used in nuclear safety related applications. "Sulzer Pumps (US) Inc. owns and operates a centrifugal pump repair and manufacturing facility at 4126 Caine Lane, Chattanooga, TN 37421. On May 7, 2006 during manufacturing we became aware of what appeared to be weld repairs to two pump bowl castings to be used in a replacement Essential Service Water Pump we are manufacturing for the J. M. Farley Nuclear Power plant. The supplier for these castings is Stainless Steel Foundry and Engineering, 5110 North 35 th St., Milwaukee, WI 53209, (414) 462-7400. "The Sulzer Pumps (US) procurement documents to the foundry required weld repairs to the castings be preceded by notification to us, submission for approval of both the proposed weld procedure (WPS) to be used, and the weld procedure qualification record (PQR). Weld maps are also required by our procurement documents. "In the case of our PO # 08407520, we received material certifications from Stainless Foundry and Engineering which certified no welding was performed to the castings. During our inspection processes we discovered what appeared to be weld repairs not traceable to us or to the above named Stainless Foundry. Subsequent investigation by Sulzer Pumps (US) and foundry representatives concluded that undocumented and unapproved weld repairs were performed by the foundry. "Additional research by Sulzer Pumps (US) identified other castings supplied by Stainless Foundry and Engineering which were used in orders previously processed and shipped by Sulzer. The documentation supplied by Stainless Foundry stated none of these castings had required weld repair by the foundry. Our records indicate the castings that have been supplied are impellers. However, based on the aforementioned discoveries they too may contain undocumented weld repairs. We have reviewed and identified the nuclear power plants where pumps using these castings were shipped which are listed below. They are: Indian Point, Cust PO# 4500533843, our job number 04JC1423; and E.I. Hatch, Cust PO# 6057240, our job number 04JC1505. "All other castings from Stainless Foundry and Engineering that we received have been placed on hold and will be returned to the foundry. We are in the process of evaluating our options to obtain replacement castings." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21 |  |  |  | 0 | 2006-05-20
42590 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-05-20 07:15 | 2006-05-20 11:51 | 2006-05-20 | HIGH PRESSURE TRANSMITTER FAILURE "At 0715 CDT on 05120/06, the Plant Shift Superintendent (PSS) was notified of a failure of the C-333A Autoclave 2 North High Cylinder Pressure System (HCPS). During a normal cylinder heating cycle the operator noted that the cylinder pressure, as read on a local digital pressure Indicator and on a digital recorder in the Operations Monitoring Room (OMR), unexpectedly fell from 55 psia to a negative value on both instruments. A 14 ton cylinder containing [deleted] U235 assay uranium hexafluoride had been heating (TSR Mode 5) for approximately 8 hours when the failure occurred. The PSS declared the HCPS inoperable and TSR LCO 2.2.4.14B actions were implemented to place the autoclave in Mode 2, 'Autoclave Open and Out-of-Service'. The HCPS is a TSR system designed to minimize the potential of primary system integrity failure (cylinder rupture) during a pressure increase event by tripping the steam supply to the autoclave prior to reaching the Maximum Allowable Working Pressure (MAWP) of the cylinder. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "Work Request #5087574" submitted to troubleshoot and repair. "PGDP Problem Report No. ATRC-06-1655; PGDP Event Report No. PAD-2006-06; NRC Worksheet No. 42,590" "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-05-20
42589 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-05-18 13:23 | 2006-05-18 21:22 | 2006-05-18 | POSTULATED FLOODING THAT COULD IMPACT BOTH TRAINS OF THE RESIDUAL HEAT REMOVAL (RHR) SYSTEM "At 1323 the Shift Manger was notified of a flooding concern that could impact both trains of the Residual Heat Removal (RHR) System. At this time both trains of RHR were declared inoperable and actions were taken to isolate the lines that could flood the RHR Pump Pits, The lines in question were from the Spent Fuel Pool Cleanup system specifically associated with the Spent Fuel Pool Dernineralizers and the Pre-filters and Post-filters. These lines were Isolated at 1345. Spent Fuel Pool cooling remained in service following isolation of the Spent Fuel Pool Cleanup system. Both RHR trains were returned to service at 1345. "Initial piping analysis determined that these lines would have remained intact during and following a seismic event. The final evaluation s expected to be completed within two weeks." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2006-05-18
42588 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2006-05-18 15:00 | 2006-05-18 19:40 | 2006-05-18 | UNEVALUATED FAILURE OF CHARGING PUMP IN FIRE SCENARIO "On May 18, 2006, it was determined that a previously unevaluated failure mode of charging pumps during a certain 10 CFR 50 Appendix R fire scenarios existed. Charging pumps are credited for specific fire scenarios to be available to make up inventory and provide reactivity control in the reactor coolant system. The engineering evaluation determined that an Appendix R fire scenario could potentially result in the failure of a circuit which would cause the credited charging pump to be tripped and held tripped by the undervoltage protection circuitry. The postulated failure would require diagnosis and manual actions to operate the charging pump. "A preliminary analysis of the core damage risk associated with this condition was performed, taking into account the frequency of fires in all of the affected areas, the potential failure of fixed and/or manual fire suppression systems, and the required manual operator actions (with assumed failure likelihoods). The results indicate that the additional core damage frequency (CDF) associated with this condition is approximately 1.2E-07/yr. "Procedures changes to address this issue are being developed." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-05-18
42587 | -1 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2006-05-18 17:12 | 2006-05-18 18:00 | 2006-07-06 | SAFEGUARD REPORT INVOLVING MODIFICATION OF SECURITY PATROLS Due to a safety hazard in the Unit 4 Power Block, access has been secured with compensatory measures in place. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE PROVIDED FROM EDWARD TREMBLAY TO JEFF ROTTON AT 1923 ON 05/18/06 * * * "Update to EN 42587 concerning suspended security patrols. This also results in a deviation from licensed condition 3E which addresses the approved Security Plan. PTN Unit 4 is operating under 10CFR50.54(x) due to suspended security patrols." This licensee notified the NRC Resident Inspector. Notified R2DO (Widmann) * * * UPDATE ON 5/19/06 AT 0056 EDT FROM C. MONTGOMERY TO A. COSTA * * * "Update to EN 42587 concerning suspended security patrols. Unit 4 is in Mode 3, and the area requiring evacuation has been significantly reduced. As of 2315 EDT on 5/18/06, the security plan has been reinstated. PTN has resumed compliance with licensed condition 3E, which addresses the approved Security Plan and has exited 10CFR50.54(x)." This licensee notified the NRC Resident Inspector. Notified R2DO (Widmann) * * * RETRACTION ON 07/06/06 AT 1135 FROM GRANT MELIN TO W. GOTT * * * "This update retracts the 10 CFR 73.71and 10 CFR 50.72(6)(1) notification. A subsequent review of security force deployment was performed for the time that access to the affected area of the Unit 4 power block was limited. The review indicated that Physical Security Plan requirements were met. Required patrols were reinstated in time to assure compliance with the Physical Security Plan." "A follow-up written report, is not required." The licensee will notify the NRC Resident Inspector. Notified R2DO (P. Fredrickson) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | DEVIATION FROM T SPEC |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) | 50.72(b)(1) |  |  | 1 | 2006-05-18
42586 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-05-18 15:00 | 2006-05-18 15:36 | 2006-05-18 | FLORIDA AGREEMENT STATE - DAMAGED TROXLER GAUGE "Truck belonging to licensee flipped over on interstate, driver is unhurt. Gauge container crushed, gauge handle broken. Licensee performed leak test at scene and transported gauge back to licensed storage facility. Further action is referred to [Florida] Radioactive Materials." Gauge was a Troxler model number - 3430, serial number 26308. Isotopes - Cs-137, 8 millicuries and Am-241/Be, 40 millicuries. Accident occurred on Interstate 75 at North Bonita Beach Road, Lee County, Florida. Florida Incident Number: FL06-072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-05-23
42585 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2006-05-17 12:30 | 2006-05-18 15:26 | 2006-05-18 | POSTULATED CRITICALITY DUE TO BACKFLOW TO AN UNFAVORABLE GEOMETRY VESSEL "During a regularly scheduled review of the ISA for a process system in the ELO building, the ISA team postulated where fissile solution could backflow into an unfavorable geometry vessel (55-gallon drum). This system configuration did not have sufficient IROFS designated to ensure that the performance criteria of 10 CFR 70.61 were met. The process system was immediately shut down, the potential for back flow to the unfavorable geometry vessel was removed, and the potential for similar accident sequences in this and related process systems was evaluated. This evaluation found one additional system configuration in the same process system where fissile solution could backflow into an unfavorable geometry vessel. The details of this condition are still undergoing internal investigation. This configuration does not have sufficient IROFS designated to ensure that the performance criteria of 10 CFR 70.61 are met. The process equipment associated with this scenario is also shut down and will remain shut down pending establishment of sufficient IROFS to meet the performance criteria of 10 CFR 70.61 "The material in the identified system sources that is normally in the tanks that could back flow to the unfavorable geometry vessel is uranyl nitrate solution with a range of [deleted] g U/liter. However on certain rare occasions, there is the potential for uranyl nitrate solution with up to [deleted] U/liter to be present in these tanks. This is the highest concentration observed by veteran system operators. "The 95/95 upper limit of keff for a single 55 gallon drum containing uranyl nitrate solution with [deleted] U/liter, sitting on a 30 cm thick concrete slab and with [deleted] cm of water tight fitted water reflector is approximately [deleted]. At [deleted] U/liter the 95/95 upper limit of keff is approximately [deleted]. The allowed 95/95 upper limit on keff for normal conditions is [deleted] and [deleted] for abnormal conditions. "SAFETY SIGNIFICANCE "Safety significance is low. The potential of accidental nuclear criticality in the as found condition remained unlikely. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: "The potential criticality pathway involves having more than [deleted] U/liter uranyl nitrate solution in the system tanks, an improper valve line up and then pumping the solution back through an air powered double diaphragm pump into the 55-gallon drum. "CONTROLLED PARAMETERS (Mass, Moderation, Geometry Concentration etc.): "The controlled parameter on the 55 gallon drum of feed material was concentration. The maximum allowed concentration is [deleted] U/1 UNH solution. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (Include process limit and % worst case critical mass: "The facility is limited by NRC license to an enrichment of [deleted] wt.% U-235. The maximum amount of material that could potentially back flow into the 55-gallon drum is approximately [deleted] liters and the maximum expected concentration would be [deleted] U "The normally expected concentration is less than [deleted] U/liter. According to ARH-600 page III.B6-3, the minimum critical spherical mass of UN solution is in excess of [deleted] kg. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "The back flow potential was eliminated and the system tagged out of service pending a complete re-analysis of the process system and the establishment of sufficient IROFS to meet the performance requirements of 10 CFR 70.61. "Related process systems that might have a similar potential were also shut down pending completion of an evaluation to ensure that the same potential does not exist in these areas." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2006-05-18
42584 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-05-18 02:00 | 2006-05-18 08:57 | 2006-05-18 | COLORADO AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The licensee left a paving job site and while driving to another job site noticed that the truck's tailgate was down. The driver stopped and noticed that the gauge was missing and the licensee contacted the State Colorado Department of Health and Environment who responded to incident site. It appears that the gauge was not secured in its casing and most likely was run over on the highway as it fell from the truck bed. Pieces of the gauge (handle and push rod) were found in the proximity of the intersection of Interstate 25 with Academy Boulevard, Colorado Springs, Colorado. The moisture density gauge was a Troxler Model 3401 serial number 30-1031 containing two sources: 8 millicuries of Cs-137 and 40 millicuries of Am/Be. The sources have not yet been found. The State and Highway Patrol are at the incident area and will continue to investigate this occurrence. At 1155 on 05/18/06, Tim Bonzer from the Colorado Department of Health reported that both sources had been recovered and packed in a sand filled cooler and will be transported to the state office where the sources will be leak checked prior to shipping to Troxler. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2006-05-23
42583 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-05-17 08:30 | 2006-05-17 20:28 | 2006-05-17 | CALIFORNIA AGREEMENT STATE REPORT- MOISTURE DENSITY GAUGE RUN OVER Eberhart/United Consultants, Inc. located in Placentia, CA reported to the State of California at 1000 PDT on 05/17/06 that one of their CPN MC3 (serial number M390304918) moisture density gauge was run over at a work site; Fontana Speedway, 9300 Cherry Avenue, CA; at 0830 PDT. When the gauge was run over the gauge was in backscatter mode of operation. The casing of the gauge was destroyed. The area was cordoned off and the RSO for Eberhart/United Consultants, Inc. was contacted. CPN Maurer Technical Services came out to the site and took possession of the gauge and took it back to their facility located in Laguna Hills. Wipe test of the sources are clean and the sources will be leak tested. Maurer Technical Services reported that the shielding for the Cesium-137 source had been compromised. State of California representative stated the highest radiation reading from the gauge at one foot was 18 milliRem per hour. The gauge contains a 10 milliCurie Cesium-137 source and a 50 millicurie Am-241/Be source. The RSO will be giving retraining to all staff to cover the emergency procedures for this type of incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-05-22
42582 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-05-17 15:03 | 2006-05-17 16:45 | 2006-05-17 | NEWS RELEASE AND NOTIFICATION TO OTHER GOVERNMENT AGENCIES - PLANNED PLANT SHUTDOWN "This 4-hour phone call is being made to the NRC per 10CFR50.72(b)(2)(xi), news release or notification to other government agencies. This call is to inform the NRC that a Notification was made to the Missouri Public Service Commission (MPSC) at 1503 on 5/17/2006, and a press release reporting that the Callaway Plant is shutting down on May 17, 2006, for an outage expected to last longer than 72 hours. The below information was presented to the MPSC. "The following is a report to the Missouri Public Service Commission (MPSC), to notify the MPSC of a forced outage at the Callaway Nuclear Plant. This notification is reportable under 4CSR240-3.1903(3)(B) because the outage is expected to last longer than 72 hours. "At 1130, May 17, 2006, the Callaway Plant started shutting down to determine the cause of a valve problem in the non-nuclear part of the plant that is preventing the plant from operating at full power. "The NRC Senior Resident Inspector has been notified." | 70 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-05-17
42581 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-05-16 16:15 | 2006-05-16 22:49 | 2007-11-29 | AGREEMENT STATE REPORT INVOLVING A LOST MOISTURE DENSITY GAUGE The licensee while transporting a Campbell Moisture Density Gauge S/N MC1391 from one jobsite to another in El Paso, TX, discovered upon arrival that the tailgate of the truck was down and the transport case with gauge were missing. The loss occurred within a sixteen (16) mile radius of the intersection of Hawkins Blvd. and Montana Ave. The licensee acknowledged to the TX Department of Health representative that the instrument had not been properly secured prior to transport. The gauge contains two (2) sources, i.e., 50 millicuries Am-241/Be and 10 millicuries Cs-137. The licensee informed local law enforcement and the TX Department of Health. TX Incident No. I-8338 **** UPDATE ON 5/17/06 AT 2250 EDT VIA E-MAIL FROM LATISCHA HANSON TO SANDIN **** Incident # correction: It should be I-8337. **** UPDATE ON 5/29/06 AT 2057 EDT FROM LATISCHA HANSON TO KNOKE **** The licensee (RSO) contacted the TX Department of Health representative to indicate that a trucker who is presently in Chicago, IL., found the instrument. The RSO requested the trucker FedEx the gauge back to the licensee. When the State tried the trucker's phone number they received a message that the number is disconnected. No other identification concerning the trucker was available. Contacted NMSS (Janosko) and R4DO (Cain). Emailed ILTAB and Mexico. * * * UPDATE PROVIDED FROM LATISCHA HANSON TO JEFF ROTTON AT 2110 EST ON 11/29/07 * * * The State provided the following information via email: "On November 24, 2007 at 3:08 pm CST, the Incident Investigation Program (IIP) was contacted by the local El Paso, Texas FBI during the State holiday office closure, that the [moisture density] gauge had been recovered by the local police department and retained for evidence. The individual had made a call to the local fire department reporting that his family may have been exposed to radiation from a piece of equipment on his property. The local fire department in turn contacted the local police department, who discovered it was the reported stolen gauge in May 2006. The local police department contacted the local FBI. The individual was questioned thoroughly by the FBI and finally admitted to having picked up the gauge over a year ago. The FBI asked if it was ok to return the gauge to the owner; IIP gave the ok. The FBI will contact the licensee owner to retrieve the gauge from them. The FBI agent reported the gauge was intact. It is still being decided if the individual will be prosecuted. "On November 27, 2007 at 3:38 pm CST, IIP received a telephone call from the licensee asking if they could take possession of the gauge and asked if they had any more reporting requirements. They were given permission to take possession, asked to submit in writing to the licensing program that the gauge was found and to give information that gauge was checked and found to be intact. The licensee agreed." Notified R4DO(Pick), FSME EO (Rathbun), ILTAB (via email), and Mexico (via Fax). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injured someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-05-19
42580 | 0 | CHEMTURA CORPORATION |  |  |  |  | 2005-12-15 | 2006-05-16 16:18 | 2006-05-16 | LOST ELECTRON CAPTURE DETECTOR CONTAINING NI-63 SOURCE The licensee reported that a electron capture detector (Perkin Elmer model # 0330-0119, serial # 2161) is declared lost as of 05/16/06. The detector contains a sealed 10 milliCi Ni-63 source (Ni-63 plated foil). The detector was being stored in a lab area used by the previous RSO and was thought at one time to have been returned to the manufacturer due to obsolescence of the detector. The detector was discovered missing in December 2005 and is believed to have been discarded in general waste in Spring 2005 during a reorganization of the facility. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-05-16
42579 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-05-16 09:45 | 2006-05-16 15:41 | 2006-05-16 | DISRUPTION OF INCOMING AND OUTGOING TELEPHONE COMMUNCIATION CAPABILITY "On 05/16/2006 at 0945 CDT, the control room was notified that problems with Bell South and Verizon phone services had occurred which disrupted incoming and outgoing telephone communications capability for both Unit 1 and Unit 2. Subsequent attempts from the control room confirmed that the State and County ringdown line was dead as well as the Emergency Notification System line. It was also determined that although outgoing calls from the control room and Emergency Operations Facility via land line were possible, incoming calls could not be received. The NRC Operations Center was contacted via land line at 09:50 CDT to inform the NRC of the issue. Alternate communication via cell phone and satellite phone was established to allow incoming calls from the NRC, State and County. The NRC Senior Resident Inspector was notified of the issue. "Telephone service was restored at 13:50 CDT which re-established all normal and emergency telephone communications capability." | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-05-16
42578 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-05-16 09:38 | 2006-05-16 11:37 | 2006-05-16 | HPCI INOPERABLE DUE TO HPCI DISCHARGE CHECK VALVE BODY LEAK "The Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable due to a leak occurring in the pump discharge check valve (2E41-F005). Specifically, the HPCI system was started as part of a planned surveillance. Personnel observing the HPCI surveillance locally saw water discharging from underneath the insulation on the check valve. The individual, being in constant communication with the Main Control Room personnel, immediately notified the Reactor Operator of the leak. The operator subsequently secured HPCI and isolated the leak. "The leak was later estimated to be approximately 20 gpm. The water is supplied from the Condensate Storage Tank. All water was contained in the HPCI room and processed by the room sump system. "Investigations are continuing into the nature and cause of the leak." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-05-16
42577 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-05-16 06:30 | 2006-05-16 10:48 | 2006-05-16 | OFFSITE NOTIFICATION DUE TO EMPLOYEE DEATH "This report is being made pursuant to 10CFR50.72(b)(2)(xi), 4-hour Non-Emergency Report due to potential media interest and the offsite notification of the Callaway County Sheriff's Office of the apparent suicide death of a plant employee on AmerenUE property approximately a half mile outside the Callaway Plant Owner Controlled Area. "At approximately 0630 on 5/16/06 a contractor employee arriving to work at Callaway Plant reported having seen an automobile parked near the plant. The Callaway County Sheriff's Department was notified and verified the automobile was registered in the name of a plant employee. A Sheriff's Deputy arrived on location and requested a Security Supervisor meet him at the location of the vehicle. At this time it was confirmed that the employee was deceased. "Callaway Plant Security conducted an initial investigation reviewing a note left by the employee, work areas, and plant access records. The results of the investigation did not indicate anything suspicious or malevolent. "The licensee has notified the NRC Resident Inspector." | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-05-16
42576 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2006-05-15 10:59 | 2006-05-15 13:48 | 2006-05-15 | MOMENTARY LOSS OF DHR DUE TO AUTOMATIC ACTUATION OF THE KEOWEE EMERGENCY POWER SUPPLY "Event: At 10:59 hours on 5-15-06, while in Mode 6 following completion of refueling activities, Oconee Unit 3 experienced a lockout of CT-3, the transformer for the Startup power source, which was in service at the time. This resulted in a momentary loss of AC power to the unit. Keowee Hydro Station, the Oconee emergency power source received an automatic emergency start signal, started, and closed in to supply power via the Underground Emergency Power path within approximately 40 seconds. "Initial Safety Significance: Initial conditions of significant systems: Normal power via backcharge of main transformer was not available. The Fuel Transfer Canal was full and valves open connecting it to the Spent Fuel Pool. Time to core boil was 58 minutes per procedure. The Equipment Hatch was open. The initial loss of power resulted in interruption of Decay Heat Removal (DHR) Cooling, Spent Fuel Pool Cooling, and other support systems. Power was automatically restored and the affected systems returned to service promptly. Therefore there was no safety significance to this event. Reactor Coolant System heated up from approximately 80F to approximately 89.5F during this event. "Corrective Action(s): As stated, Keowee started and supplied power automatically. The appropriate Abnormal Procedures were entered to restore power and restart these systems. DHR was restored at 11:13. Actions were initiated to achieve Containment Closure due to the loss of DHR. The Equipment Hatch was closed by 11:40. Backup power is available from Central Switchyard via CT-5. The cause of the initiating transformer lock out is under investigation." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-05-15
42575 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-05-14 23:20 | 2006-05-15 01:37 | 2006-05-15 | SODIUM HYPOCHLORITE LEAK INTO THE DELAWARE RIVER "This 4-Hour notification is being made in accordance with 10CFR50.72 (B)(2)(xi). "A notification was made to the New Jersey Department of Environmental Protection of a discharge of approximately 1000 gallons of water containing 3000 parts per million Sodium Hypochlorite to the Delaware river, via a permitted outfall. The source of the water was a leak on the chlorination injection line in the Unit One Service Water Bay. The water was pumped to the river via the building sump pump. On discovery the leak was isolated and the building sumps turned off to prevent further discharge. Follow up investigation to determine the cause of the leak is in progress. "There was no equipment out of service that contributed to this event and there were no personnel injuries or radiological occurrences associated with this event." The leak occurred when changing the pump in service. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-05-15
42574 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2006-05-14 09:57 | 2006-05-14 16:53 | 2006-05-14 | EMERGENCY DIESEL GENERATOR AUTOMATIC START "During restoration from a scheduled LCO, the Unit 1 EDG auto started when its control switch was placed in the auto position. The auto start occurred as a result of a 4KV Bus Feed Breaker being open. This breaker was in the open position as part of scheduled maintenance. This notification is being made in accordance with 10CFR50.72(b)(3)(iv)(A) due to an actuation that was the result of a valid signal." The 4KV Bus was subsequently restored and the EDG was returned to standby. The licensee notified the NRC Resident Inspector. | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-05-14
42573 | 0 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2006-04-24 | 2006-05-12 22:36 | 2006-10-10 | PART 21 NOTIFICATION - BWR CORE SHROUD TIE ROD UPPER SUPPORT CRACKING "Summary: GE Energy, Nuclear (GE) has provided core shroud repairs using tie rods to the US BWR plants identified in Attachment 1 [of the Part 21 notification]. Recently it was discovered during an in-vessel visual inspection (IVVI) that tie rod upper supports at Hatch Unit 1 experienced cracking. The apparent root cause is Intergranular Stress Corrosion Cracking (IGSCC) in the Alloy X-750 tie rod upper support material. Alloy X-750 material is susceptible to IGSCC if subjected to sustained, large peak stress conditions. GE opened an internal evaluation to determine if the potential IGSCC in the X-750 tie rod structural components of other BWR shroud repairs designed by GE could be a reportable condition under 10CFR21. "GE used the criterion provided in the BWR Vessels & Internals Project (BWRVIP-84) for the IGSCC susceptibility assessment of the X-750 components in the tie rod vertical load path. GE has concluded that it is not a reportable condition for the plants that were found to be within or not significantly exceed the BWRVIP-84 criterion. These US plants are identified as 'NR' in Attachment 2 [of the Part 21 notification]. GE determined that two US plants exceed the BWRVIP-84 criterion for the upper supports (in addition to the Hatch Unit 1 as-found condition). GE has not completed the evaluation for these plants to assess if a substantial safety hazard (SSH) exists. These plants have been provided a 60-Day Interim Report Notification under §21.21(a)(2) and are identified as '60-Day' in Attachment 2 [of the Part 21 notification]. "Safety Basis: Cracking in the tie rod components made of X-750 may render the tie rod ineffective in maintaining core shroud configuration integrity during postulated accident conditions. Loss of core shroud integrity could impact the ability to maintain adequate core cooling for postulated design basis accident conditions. This condition would be reportable under 10 CFR 21 as a substantial safety hazard. "Corrective Action: The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action (note, these are actions specifically associated with the identified deviation or failure to comply): 1. A preliminary cause evaluation has been performed. The apparent cause of the cracking is Intergranular Stress Corrosion Cracking (IGSCC). A material sample is being shipped to the GE Vallecitos Nuclear Center for examination to confirm the apparent cause. GE will report the results of the examination by August 21, 2006. 2. The issue has been communicated to the industry through the BWR Owners' Group and the Electric Power Research Institute (EPRI)/BWR Vessel and Internals Project (BWRVIP). The NRC was informed in a NRC management meeting with EPRI and the BWRVIP Executive Oversight Committee at the NRC offices, Rockville, on March 15, 2006. 3. GE has completed an evaluation of the susceptibility to IGSCC using the BWRVIP-84 criterion. Determination of whether any possible cracking could lead to a substantial safety hazard (i.e., loss of core shroud configuration integrity during a design basis accident condition) depends upon many factors, including the actual extent of cracking in the repair components. Until inspections are completed, the actual extent of cracking is not known. GE is developing a model to predict the postulated extent of tie rod upper support cracking for tie rods with upper supports made of Alloy X-750. For upper supports that exceed the BWRVIP-84 criteria significantly, the model will be used to postulate the extent of cracking. This prediction will be used to determine if a substantial safety hazard could exist. GE will report the results of the evaluation by October 9, 2006. 4. The original design basis stress reports will be reviewed to assess the available margin in the primary membrane + bending stress intensities of the upper supports with respect to ASME code allowable values. Where reasonable margin exists in the original design basis code evaluation (an existing margin of approximately 25 % will be considered as reasonable margin), the existing margin is deemed adequate to offset any engineering assumptions or judgments used in the original analysis. Where the original margin is less than 25%, further review will be performed (including finite element analysis, if necessary) to confirm that the upper support remains qualified. This review will be completed by October 9, 2006." Affected US Plants per Attachments 1 and 2 of the Part 21 notification: Clinton, Nine Mile Point 1, Pilgrim, Dresden 2 & 3, Quad Cities 1 & 2, Hatch 1 & 2. ***** UPDATE ON 8/21/06 AT 1614 ET VIA E-MAIL FROM JASON POST TO MACKINNON **** "GE Energy, Nuclear (GE) has completed the failure evaluation of the cracking discovered in the Hatch Unit 1 core shroud repair tie rod upper supports as committed in Reference 2, (GE Part 21 60-Day Interim Report Notification: Core Shroud Repair Tie Rod Upper Support Cracking, MFN 06-133, May 12, 2006). A preliminary cause evaluation had concluded that the apparent cause of the cracking is Intergranular Stress Corrosion Cracking (IGSCC). A material sample was shipped to the GE Vallecitos Nuclear Center for examination to confirm the apparent cause. GE committed to report the results of the examination by August 21, 2006. "The fracture was examined by metallographic and scanning electron microscope (SEM) techniques including an analysis of the fracture surface. The examinations revealed the cracking mechanism to be IGSCC. Scanning electron microscopy (SEM) showed the fracture surface had a "rock candy" like appearance, consistent with an IGSCC mechanism. Images of the cross-section of the fracture surface further verified the IGSCC mechanism by showing the path of the crack following the grain boundaries. No hardness or microstrutural anomalies were observed. "GE continues to work on the other action items that were committed in Reference 2. If you have any questions, on this information, please call me . . . " R2DO (Mark Lesser) notified. E-mailed to NRR Part 21 (Omid Tabastabai & Jack Foster). * * * UPDATE ON 10/09/06 AT 2333 EDT VIA E-MAIL FROM JASON POST TO HUFFMAN * * * Summary of Part 21 Notification: Completion of GE Evaluation on Core Shroud Repair Tie Rod Upper Support Cracking Previous correspondence on this subject identified that GE had concluded that this is not a reportable condition for Hatch Unit 1 and for several other US plants that have core shroud repairs designed by GE. However, GE had not completed the evaluation for two other US plants (Pilgrim and NMP-1). GE committed to complete the evaluation and inform the NRC of the results by October 9, 2006. The purpose of this letter is to inform the NRC of the results of the Pilgrim and NMP-1 evaluations. "The GE evaluation concluded the following: "a. All other major Alloy X-750 components in the tie rod assembly vertical load path besides the previously identified upper support brackets for the plants with GE designed tie rod repairs are within the BWRVIP-84 criterion for IGSCC susceptibility. Furthermore, the upper supports remain qualified with respect to ASME code allowable values per the original design basis stress analyses. "b. It is not a reportable condition for the as found Hatch Unit 1 condition based on the known extent of tie rod upper support cracking. "c. It is not a reportable condition for plants that do not use X-750 material for the tie rod upper support brackets. This is applicable to Clinton. "d. It is not a reportable condition for plants that have margin to the BWRVIP-84 IGSCC criterion for the tie rod upper support brackets (or which exceed the criteria by a very small amount). These plants are Hatch 2, Quad Cities 1/2, and Dresden 2/3. "e. It is not a reportable condition for the plants that exceed the BWRVIP-84 IGSCC criterion for the tie rod upper supports based on a three-pronged composite approach of (1) the shroud repair upper support integrity based on assumed cracking, (2) the shroud horizontal welds integrity, and (3) the previous shroud cracking safety evaluations. These plants are NMP-1 and Pilgrim. "Corrective/Preventive Actions: "GE recommends that NMP-1 and Pilgrim replace the tie rod upper supports with an improved IGSCC-resistant design at the next regular scheduled outage." R1DO (Decker) notified. E-mailed to NRR Part 21 (Vern Hodge, Ian Jung, John Thorp). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2006-05-12
42572 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-03-14 17:40 | 2006-05-12 10:35 | 2006-05-12 | INADVERTANT CORE SPRAY PUMP ACTUATION "The notification is being made pursuant to 10CFR50.73(a)(2) (iv) (A) and is reported per 10CFR50.73(a)(1) "An invalid actuation of the 1 C Core Spray Pump start during D13 LOCA/LOOP Testing. a) The specific train(s) and system(s) that were actuated. The 1C Core Spray Pump actuated automatically on an inadvertent Division 3 LOCA signal during LOCA/LOOP testing. No other ECCS train/system actuated. b) Whether each train actuation was complete or partial. The 1C Core Spray Pump actuated in the minimum flow protection mode. c) Whether or not the system started and functioned successfully. The 1 C Core Spray System started and functioned successfully but did not inject into the vessel. On March 14, 2006 at 5:40 PM during performance of the D13 LOCA/LOOP Test, ST-6-092-117-1, the 1 C Core Spray pump was inadvertently started. The pump started (but did not inject) when an I&C Technician attempted to demonstrate operation of the test switch. He inadvertently picked up the energized test switch which was next to 2 spare test switches and manipulated it which resulted in a Division 3 LOCA signal to the 1C Core Spray Pump. The 1C Core Spray Pump never injected and was running with min-flow protection and functioned as expected. The cause of the event was lack of attention to detail and self check." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-05-12
42571 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-05-12 00:53 | 2006-05-12 05:11 | 2006-05-12 | MANUAL REACTOR TRIP ON HIGH STEAM GENERATOR LEVEL "While lowering turbine load to 45% for planned maintenance to replace an RCS Loop flow transmitter, Callaway Plant experienced high vibration on two main turbine bearings. The main turbine was manually tripped at 0047 in accordance with off-normal procedures. At 0052, received a Steam Generator High-High Level (P-14) on the "A" S/G resulting in a Feed Water Isolation Signal (FWIS) and Auxiliary Feed Water Actuation (AFAS). The reactor was manually tripped at 0053. Emergency Operating Procedures were completed and exited at 0115." After receiving the main turbine high vibration alarm, the plant reduced power to below the reactor trip/turbine trip setpoint and manually tripped the main turbine. Steam generator level rose to the P-14 feedwater isolation setpoint at which time, the reactor was manually tripped. All rods fully inserted on the trip. Decay heat is being removed by condenser steam dumps. Steam generator level is being maintained with the startup feed pump. The electrical grid is stable. No relief valves or safety valves lifted. The cause of the high vibration is being investigated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-05-12
42570 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-05-05 | 2006-05-11 19:54 | 2006-05-11 | AGREEMENT STATE REPORT FROM CALIFORNIA - MISSING SOURCE The following is a summary of information provided by the State via facsimile: The RSO and medical physicist for Century City Doctors Hospital (CCDH) called to report a lost Sr-90 eye applicator, sn 1244, approx 28 mCi (was 63.3 mCi in 1972.) Century City Hospital closed in June 2005. It was reopened under a new entity as CCDH in November 2005. In December 2004 CCDH had sent its old Cs-137 brachytherapy sources to Barnwell. CCDH kept its dose calibrator sources & the Sr-90 eye applicator locked in their hot lab. CCDH is reopening its nuclear medicine department and asked the RSO to determine the status of the dose calibrator sources. When the RSO went to the hot lab on May 5, he noticed the Sr-90 source was missing. The old dose calibrator sources, which had decayed, were still there, and the RSO said it appeared no one had been in the hot lab- it was dusty and dirty. CCDH had a company, Dan York, perform wipe tests in March 2005. The hospital claims to have paperwork that indicates the Sr-90 source was wipe tested, but York says it wasn't. (The RSO will be reviewing that paperwork tomorrow.) Regardless, when York did the next wipe tests in Sept 2005, the eye applicator wasn't there at that time. So it's been missing since at least Sept 2005. The company who brokered the disposal of the Cs-137 sources, New World Technology, has been contacted, and they say they did not remove the eye applicator. The RSO will interview the physician who had used the applicator and everyone who had access to the hot lab. The hospital CEO will send a memo to hospital staff, asking if anyone has seen it. CA report number 051106 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-05-16
42569 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-05-11 15:14 | 2006-05-11 17:35 | 2006-05-11 | MANUAL ACTUATION OF REACTOR PROTECTION SYSTEM DUE TO FAILURE OF CONTROL ROD TO WITHDRAW "Following a startup from a refueling outage with the plant at approximately 24% power, it was determined that one control rod appeared to be fully inserted in the core as determined by both incore and excore flux tilts. The Off Normal Procedure for a dropped control rod was entered. The decision was made to take the plant offline to troubleshoot and correct the apparent condition. The Off Normal Procedure does not allow operation in Mode 2 with a dropped control rod. At 1514 hours EDT the reactor was manually tripped from 8% power. The reactor trip was uncomplicated. "This is reportable under 10 CFR 50.72(b)(2)(iv)(B) as a manual Reactor Protection System actuation while critical." Decay heat is being discharged to the condenser via the turbine bypass valves and cooling is being supplied from AFW. All systems besides the control rod in question functioned as required. It appears that the control rod in question may have been inserted since startup. The rod position indicators were showing a normal rod position. The licensee believes that the rod may not be coupled. This rod has had a previous history of being difficult to couple. The licensee stated that normal rod testing was conducted prior to startup along with low power physics testing which did not indicate anything significantly out of spec. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-05-11
42568 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-05-11 05:11 | 2006-05-11 10:42 | 2006-05-11 | AGREEMENT STATE REPORT - SOURCES FOUND AT ROADSIDE A work crew found an ammo-box on the side of a county road 1788 in the Midland - Odessa area. It contained what are believed to be two (2) sources used for process flow measurement. One source is a Ir-192 source and another as yet unidentified believed at this time to be a Scandium source. The state is following up and will provide additional information on the types and quantities of the sources and licensee data when they receive it. * * * UPDATE FROM STATE (A. TUCKER) TO M. RIPLEY 1824 EDT 05/11/06 * * * The ammo box was found on the side of the road between 6:00 and 6:30 am CDT by a driver for Baker Atlas. The box contained ten empty pigs and two sealed pigs with one labeled Ir-192 (88 mCi) and the other labeled Sc-46 (12 mCi). Initially reported radiation survey results were 5 mrem at 3 feet. The box has Yellow II labeling (radioisotopes) and the sources were thought to be used for tracer studies. The State contacted Protechnics (Core Laboratories) to inquire if they had lost the ammo box, but were subsequently notified that it was not theirs. Later, the licensee, Tracer Tech Services of Midland, TX, was identified as the owner and at 1:10 pm CDT the licensee was on the way to the Baker Atlas facility to pick up the box. The licensee stated that their driver was on his way to New Mexico, got there and then discovered his tailgate was down and the was sources were gone. Baker Atlas and the licensee were instructed by the State not to remove the ammo box until cleared by their inspector. The inspector reached the Baker Atlas facility around 3 pm CDT. Subsequent survey results by the State were 3 mrem/hr at 1 meter and 80 mrem/hr on top. There was no apparent spread of radioactive material. The State will continue to investigate the incident. Texas Incident # I-8335 Notified R4 DO (D. Powers) and NMSS EO (T. Essig) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-05-16
42567 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2006-05-10 16:58 | 2006-05-10 18:41 | 2007-03-13 | MODIFIED SECURITY MEASURES DUE TO INCLEMENT WEATHER "At 1658 Hrs CDT May 10th, 2006, the security measures at GGNS were modified in accordance with the provisions of chapter 19.2 of the physical security plan, due to severe weather conditions (Tornado Warning). These modifications did not result in the reduction of the physical protection of the plant or in a reduction of the required number of security responders. Security measures will be restored as soon as practical after the weather conditions permit. Follow-up notification will be made after security measures are restored to normal." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 5/10/06 AT 1818 CST FROM B. BLANCHE TO A. COSTA * * * The licensee has restored security measures to normal. Notified R4DO (D. Powers). * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC INTERNAL WEBSITE* * * | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-05-10
42566 | 0 | BOZEMAN DEACONESS HOSPITAL |  |  |  |  | 2006-05-09 12:00 | 2006-05-10 17:02 | 2006-05-10 | MEDICAL EVENT - DOSE TO UNINTENDED SITE A medical event was identified during the post-implant CT scan of a prostate implant patient. A total of 88 seeds were implanted (30.3 milliCuries total). The CT scan confirmed that most of the seeds were located in an area surrounding the urethra instead of the prostrate. The patient's physician has been informed. The licensee will continue to investigate this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 4 | MT | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2006-05-10
42565 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2006-05-10 15:45 | 2006-05-10 16:54 | 2006-05-10 | OFFSITE NOTIFICATION AND PRESS RELEASE ISSUED DUE TO DISCOVERY OF ASBESTOS MATERIAL DURING MAINTENANCE "This notification is being made in accordance with 10CFR50.72(b)2(xi) due to a press release being issued. The Nuclear Management Company [NMC] will be issuing a press release regarding maintenance activities on a non-safety related, non-radioactive system that will state: 'During work on a plant equipment modification at Prairie Island Nuclear Plant Unit 1 last week, some gasket material being removed was found to contain asbestos. Prairie Island Unit 1 is in the midst of a refueling outage. 'As soon as site management became aware of the concern for potential asbestos containing material, work on the project was suspended, according to Nuclear Management Co., which operates the plant. The air immediately was monitored and tested according to Minnesota Clean Air requirements. The results were well below regulatory limits. However, results from additional testing on surfaces by a certified lab indicated detectable levels of asbestos on some surfaces in the immediate area. 'Trained asbestos workers are performing a complete clean-up of the affected area. 'NMC and its contractor are taking precautionary actions for any employee with a concern for potential exposure. This includes offering an optional asbestos exposure examination in accordance with federal Occupational Safety and Health Administration (OSHA) guidelines. 'Prairie Island's two reactors near Red Wing, Minn., generate 1,076 megawatts of electricity, enough to power one in five homes and businesses in the Upper Midwest. Xcel Energy owns the plant, which is one of six reactors operated by Nuclear Management Company, headquartered in Hudson, Wis.'" Unit 1 is currently defueled. The licensee informed state/local agencies/nearby tribal entity and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-05-10
42564 | -1 | JAMESON HOSPITAL |  |  |  |  | 2006-05-08 08:36 | 2006-05-10 10:57 | 2006-06-12 | POTENTIAL PERSONNEL OVEREXPOSURE Jameson Hospital in New Castle, PA. reported that one of its physicians had a film badge reading of 9,218 mrem deep dose. The film badge was issued to the physician on 11/5/05 and processed by Global Dosimetry approximately four months after being issued. According to the radiation safety officer, the physician is a licensed anesthesiologist and was exposed to radioactive sources for approximately 3 hours per day providing fluoroscopy imaging procedures to patients spinal cords in a laboratory environment over the four month period. The only recorded dose for the physician this calendar year is 45 mrem from March 2006 to April 2006. There are no other individuals who worked in the same area as the affected physician reporting any high film badge readings. Jameson Hospital has notified the physician, initiated a root cause investigation, and is reprocessing the film badge to determine the root cause. * * * RETRACTION ON 6/12/06 AT 1300 EDT FROM ROBERT ONDO TO A. COSTA * * * The root cause investigation for this incident has been completed and it has been determined that the potential overexposure related to this individual is not from NRC related activities. Furthermore, the potential dose from the overexposure was not determined since the film badge was mishandled. Notified NMSS EO (G. Morell) and RDO (D. Silk). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2202(b)(1) |  |  |  | 0 | 2006-05-10
42563 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-05-10 02:15 | 2006-05-10 04:36 | 2006-05-10 | NOTIFICATION OF OFFSITE AMMONIA AND HYDRAZINE RELEASE "A notification was made to the New Jersey Department of Environmental Protection of a discharge of approximately 2000 gallons of water containing 30 parts per million (ppm) of hydrazine and 200 ppm of ammonia to the Delaware river, via the storm drain system. The source of the water was a relief valve on the Unit 1 Condensate System that resulted in the overflow of the condensate polisher building sump. The water migrated from the building to the storm drain system. The discharge was terminated at the time of discovery. "There was no equipment out of service that contributed to this event and there were no personnel injuries or radiological occurrences associated with this event." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-05-10
42562 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-11-01 | 2006-05-09 08:48 | 2006-05-09 | MASSACHUSETTS AGREEMENT STATE - ABANDONED RA-226 QUANTITY 1000 TIMES GREATER THAN LABELING REQUIREMENTS The following information was received from the state via fax: "Cause Description: During Clean-Out of Deceased Dermatologist, the family discovered a box with Ra-226. "About 11/1/2005: [Deleted] contacted the Boston Regional (Office) of the EPA to dispose of Ra-226 discovered at family home. EPA recommended to [Deleted] that it would be cheaper if he disposed of the Ra-226 directly via a waste broker. EPA suggested Radiac Environmental Services of Brooklyn, NY. "11/17/2005: Radiac (Environmental Services of Brooklyn, NY) visited the Milton, MA residence and estimated that the amount of Ra-226 was about 2.9mCi. In addition, Radiac placed the box of Ra-226 sources into a 5-Gallon DOT Type A steel drum with a ring bolt closure, placed a security seal was placed over the ring, and labeled the drum with yellow/magenta radioactive label. [Deleted] was going to Florida for the winter. "4/27/06: The EPA informed the Mass. Radiation Control Program about the Ra-226 in Milton, MA. "Corrective Actions: Material to be disposed of by licensed broker - Radiac Environmental Services of Brooklyn, NY - during the week of May 8, 2006." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-05-12
42561 | 0 | TEAM INDUSTRIAL SERVICES |  |  |  |  | 2006-04-18 18:27 | 2006-05-08 11:43 | 2006-05-08 | PART 21 NOTIFICATION INVOLVING FAILURE OF AMERSHAM-660B CRANK ASSEMBLY The licensee provided the following information via email: "This report is being submitted by Team Industrial Services, Inc. (TISI), as required by 10CFR Part 21. This report is to serve as notification of a nonconforming condition encountered by TISI, when using crank assemblies, manufactured or serviced by the supplier shown below, with Amersham-660B radiographic exposure devices. "NDT Repair Service and Supply, Inc. 7874 Highway 90 East Morgan City, LA 70380 "An initial failure of these crank assemblies (s/n NDT-267) was noted by TISI personnel performing industrial radiography at a jobsite in Sewaren, NJ on 04/18/06. Specifically, the radiography crew was able to connect the drive cable assembly to the exposure device, without connecting the drive cable to the source connector. As a result, the radiography crew was unable to return the source assembly to the exposure device, and emergency source retrieval was required. Based on our understanding of the specifications established in ANSI N432-1981, section 6.1.4, these controls should not have allowed exposure of the source assembly if the drive cable was not properly connected. "Subsequent evaluation of other crank assemblies purchased from the supplier noted the same failure. As a result, all TISI branches have been directed to identify these assemblies as nonconforming and to remove them from service. A Supplier Corrective Action Request (SCAR) has been issued, per TISI's Quality Assurance Program, against this supplier as a result, requesting a determination of the root cause of this nonconformance, action to correct, and action to prevent recurrence." See related EN#42508. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 21.21 |  |  |  | 0 | 2006-05-08
42560 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-05-08 12:30 | 2006-05-08 14:21 | 2006-05-08 | EARLY WARNING SIREN SYSTEM (EWSS) DECLARED INOPERABLE "Intermittent radio functionality was noticed during routine radio operation at 1203. Radio checks were satisfactorily performed immediately after this occurrence; however, at 1230, the intermittent problem recurred. VCSNS declared that the siren control system would not operate at 1230. Our procedures require notification of the South Carolina Emergency Management Division and the local counties within 1 hour. Informal notifications to Fairfield and surrounding counties, and the State Area Coordinator were completed by 1242. Official notifications were made via the ESSX system at 1321." "This report is being made to the NRC per 10CFR50.72(b)(3)(xiii) due to the loss of >25% of the EWSS. Additionally, this is being reported per 10CFR50.72(b)(2) (xi) due to the notification made to other government agencies." The local counties notified include Fairfield, Newberry, Richland and Lexington. The outage affects the entire EWSS. The licensee informed state/local agencies and the NRC Resident Inspector. * * * UPDATE AT 1723 EDT ON 5/8/06 FROM FRED LUCAS TO S. SANDIN * * * The EWSS has been returned to service. Notified R2DO (Munday) and NSIR (McMurtray) via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2006-05-08
42559 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2006-05-06 16:35 | 2006-05-06 20:30 | 2006-05-06 | VALID ACTUATION OF EMERGENCY DIESEL GENERATOR DUE TO LOW VOLTAGE CONDITION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On May 6, 2006, at approximately 16:35 US Mountain Standard Time (MST) a valid actuation of the Palo Verde Nuclear Generating Station Unit 3 Train 'A' Emergency Diesel Generator (EDG) occurred as a result of an undervoltage condition on its respective safety bus (PBA-S03). EDG 'A' started and loaded as designed to energize PBA-S03. The loss of power to the safety bus occurred during Gas Turbine Generator testing. GTG number 1 was supplying safety bus PBA-S03 at a low voltage when supply breaker PBA-S03L opened unexpectedly. This resulted in the deenergization of the safety bus PBA-S03. "The emergency diesel generator started and all required related safety equipment started as expected. "No Emergency Plan declaration was made and none was required. "Unit 3 was in mode 5 at 50 psia and140 degrees F. Shutdown Cooling Train B was OPERABLE and in service. No other ESF actuations occurred and none were required. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been notified of the ESF actuation and this ENS notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-05-06
42558 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2006-05-06 06:07 | 2006-05-06 12:31 | 2006-05-06 | UNPLANNED MANUAL REACTOR SCRAM DURING SHUTDOWN "A manual reactor scram was inserted to expedite a reactor shutdown. The reactor was subcritical at the time of the manual scram. All control rods inserted to less than or equal to position 02 as required." The unit entered a forced outage for necessary repairs including replacement of the "B" recirc pump motor. All systems functioned as required for the manual reactor scram. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Startup | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-05-06
42557 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-05-05 16:00 | 2006-05-05 22:55 | 2006-05-05 | POTENTIAL LOSS OF RHR "At 1600 CST on May 5, 2006, the Kewaunee Power Station (KPS) declared both trains of Residual Heat Removal (RHR) inoperable due to a vulnerability to internal flooding caused by possible ruptures of non-seismically qualified piping during a seismic event. Since the KPS RHR system is not protected from non-seismically induced piping breaks in the auxiliary building basement KPS does not presently meet the design criteria in the KPS USAR for the RHR system. The specific design criteria is stated in USAR section B.5 'Protection of Class I Items' and states that Class I items are protected against damage from 'Rupture of a pipe or tank resulting in serious flooding or excessive steam release to the extent that the Class I function is impaired.' "With KPS in Intermediate Shutdown and both trains of RHR inoperable, KPS meets the Technical Specification requirement for Decay Heat Removal Capability with two (2) Steam Generators operable to remove decay heat. "This event is being reported under 10CFR50.72(b)(3)(v)(B) for 'Any event that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to remove residual heat.'" The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-05-05
42556 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-03-31 | 2006-05-05 13:49 | 2006-05-05 | AGREEMENT STATE REPORT - MEDICAL EVENT An 80 year old white female undergoing a Mammosite Brachytherapy (Nuclear Tron V2 model 31662) procedure utilizing Ir-192 source received less than 30% of the prescribed dose of 3400 centi-gray (cGy) (accumulated dose). An incorrect figure was entered into the computer causing the source to stay back 6 cm from the intended position and hence dosing an unintended area of approximately 2 cm with 3 times the prescribed dose of 10,000 cGy. The treatment was given 2 times a day for five days from March 31 to April 7, 2006. The patient saw the attending physician for follow-up on May 2, 2006. The physician discovered the patients skin abnormally red. He contacted the Medical Physicist who investigated and discovered the input error. The physician, patient and the patients family were notified. The patient is well and is being treated for erythema. Florida Incident number: FL 06-062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-05-10
42555 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-05-04 17:50 | 2006-05-04 21:54 | 2006-05-04 | UNEXPECTED REACTOR PROTECTION SYSTEM (RPS) ACTUATION DURING TESTING "On May 4, 2006, at 1750 hrs, with the plant in Mode 5, an actuation of the reactor protection system occurred with a single control rod fully withdrawn for testing. The actuation occurred when operators opened the main steam isolation valves (MSIVs) for a separate testing activity, which caused an apparent pressure perturbation with the steam generator level transmitters. The pressure perturbation resulted in the indicated level of 2 of 4 'A' Steam Generator level transmitters oscillating to below the steam generator low level reactor trip setpoint, before returning to the pre-event level. As a result of the reactor protection system actuation, the control rod inserted into the core as expected. "The steam generators were aligned in lay-up condition with a nitrogen blanket present at the time the MSIVs were opened. "The event is reportable in accordance with 10 CFR 50.72(b)(3)(iv), as a valid actuation of the reactor protection system." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-05-04
42554 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2006-05-04 09:11 | 2006-05-04 18:11 | 2006-05-04 | FITNESS FOR DUTY REPORT INVOLVING A CONTRACTOR SUPERVISOR "A random test of a contractor supervisor resulted in a positive fitness-for-duty [test] requiring 24 hour fitness-for-duty notification. There was no impact to the plant as a result of this event. Individual access to the protected area has been revoked." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2006-05-04
42553 | 0 | GEO TECHNICAL CONSULTING AND TESTIN |  |  |  |  | 2006-05-04 16:00 | 2006-05-04 17:45 | 2006-05-04 | DAMAGED MOISTURE DENSITY GAUGE A Troxler Model 3430 (s/n 360840) was run over at the Fort Belvoir, VA construction site. The source rod is in the stowed and locked position. The gauge case is cracked on the bottom. The area has been posted and the RSO is enroute to perform radiation surveys. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2006-05-04
42552 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-05-04 14:30 | 2006-05-04 17:19 | 2006-05-04 | 24-HOUR CONDITION OF LICENSE REPORT INVOLVING FIRE PROTECTION PLAN VIOLATION "The Perry Nuclear Power Plant (PNPP) Operating License requires that a report be made within 24 hours to the NRC operations center via the emergency notification system in the event that a violation of the PNPP Fire Protection Program occurs. On May 2, 2006, it was discovered that a specific set of Division 1 Emergency Diesel Generator (EDG) Control Room Control Switch contacts were not designed to isolate the Control Room from the local Division 1 EDG controls in the event of a control room fire. At 1430 on May 4, 2006 it was determined that this deficiency violated the PNPP fire protection program and could adversely affect plant shutdown in the case of a control room fire. A potential fire induced hot short in the diesel generator logic circuit(s), may result in a failure to start or a spurious trip of the Diesel Generator even if control is transferred to remote control. Although repairs and operator actions could have been taken to restore the Division 1 EDG if the Control Room fire caused a failure to start or a spurious trip of the Diesel Generator, these activities were not specifically identified in the Fire Protection safe shutdown analysis or associated operating procedures. The ability to achieve and maintain safe shutdown in the event of a fire in the Unit 1 Control Room could be adversely affected. Compensatory actions (procedure changes) have been completed to address this issue. A written report will follow in accordance with Technical Specification 5.6.6.a and Operating License Condition 2.F." The licensee discovered this discrepancy while researching a modification. This condition has existed since 1987. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW | [5 empty] | 0 | 2006-05-04
42551 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2006-05-04 | 2006-05-04 13:23 | 2006-05-04 | PART 21 NOTIFICATION INVOLVING POTENTIAL DEFECT IN AEROVOX CAPACITOR The following information was provided via email: "COMPONENT DESCRIPTION: "13uF X 1000V AC capacitors, SCI P/N 07-020139-00, Aerovox P/N H94S1013A0BA, manufactured between January 2004 and December 2004. "Capacitors can be either installed in Ametek Solidstate Controls UPS equipment or provided as a spare part. The components are schematically identified as C805, C815, or C705. "PROBLEM YOU COULD SEE: "The capacitor failures due to this defect will occur early in the operating life of the device. There are no warning signs that a failure is imminent, or detection method for predicting an approaching failure. "CAUSE: "The investigation has revealed that the capacitor failures (date codes 0408 and 0436) were due to manufacturing defects. A failure analysis by Aerovox revealed that a foil tab connecting the capacitor winding to the internal terminal became pinched between the lid and the can during the seaming operation. Within the first year of operation, the insulation covering the connecting tab was cut through. This resulted in terminal to case short. "EFFECT ON SYSTEM PERFORMANCE: "The failures described above, could result in loss of output voltage and transfer of the static switch to the bypass source. The resulting failure could result in a potential damage to the load. "ACTION REQUIRED: "The observed failure rate of this component is very low at 0.06% (2 out of 3336 units manufactured between 1/1/04 and12/31/04.) Aerovox has implemented corrective actions to preclude further failures. "Based upon the Aerovox evaluation, Ametek Solidstate Controls believes if a defect was present in a capacitor, the likelihood of a failure should occur early in the operating life. We feel the failure rate has been extremely low and the risk is minimal. Each operating facility will need to evaluate the potential risk to their operation. "AMETEK SOLIDSTATE CONTROLS CORRECTIVE ACTION: "If you wish to replace the capacitors Ametek Solidstate Controls will work with you to arrange replacements. Please contact Mrs. Jean Falor of our Client Services group at 1-800-222-9079 or 1-614-846-7500 ext. 6230. jean.falor@ametek.com." Rudimentary listing of stations that received this component installed in equipment or as a spare part: - Installed in equipment: Oconee, McGuire, Watts Bar, Browns Ferry, STP, Beaver Valley, San Onofre, Nine Mile Point and TMI. - Spare part: St. Lucie, Palo Verde, Surry, Turkey Point, Diablo Canyon, Harris, Crystal River, Robinson and Comanche Peak. - International: Korea Hydro, Nuklearna Elec Vrbina, China Nuclear, Laguna Verde and Electrobras. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2006-05-04
42550 | -1 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2006-05-04 10:37 | 2006-05-04 11:34 | 2006-05-26 | UNAUTHORIZED CONTROL ROOM ENTRY Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * RETRACTION FROM S. ELLIOTT TO W. GOTT AT 1549 ON 05/26/06 * * * Upon further review of Generic Letter 91-03, it was determined that the event should have been classified as a loggable event. St. Lucie Plant is retracting the event. Notified R2DO (C. Payne) and emailed 73.71 group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-05-04
42549 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2006-05-03 22:30 | 2006-05-04 06:07 | 2006-05-04 | RCIC DECLARED INOPERABLE DUE TO DEGRADED FLOW INSTRUMENT The licensee indicated the Reactor Core Isolation Cooling (RCIC) has been made inoperable by a degraded flow instrument. The deficiency will prevent RCIC from achieving its design flow of 410 gpm. The degraded condition limits the flow to 360 gpm. This condition put the licensee into LCO 3.5.3.A. To exit the LCO an I&C tech will need to perform a venting operation on the flow transmitter. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1252 EDT ON 5/4/06 FROM GENE DORMAN TO S. SANDIN * * * The licensee provided the following additional information: EVENT NOTIFICATION RETRACTION "At 0607 on 05/04/2006 the James A. FitzPatrick Nuclear Power Plant notified the NRC Operations Center that, 'Reactor Core Isolation Cooling (RCIC) System has been made inoperable by a degraded flow instrument. The deficiency will prevent RCIC from achieving its design flow rate of 410 gpm. Estimated flow rate in the current condition is 360 gpm.' This notification was made pursuant to 10 CFR 50.72(b)(3)(ii)(A) 'Any event or condition that results in: (A) The conditions of the nuclear power plant, including its principal safety barriers, being seriously degraded;' "Subsequent review of this event determined that the degradation of the RCIC System did not result in any of the plant's principal safety barriers (i.e., fuel cladding, reactor coolant pressure boundary, or the primary containment integrity) being degraded therefore, criterion 10 CFR 50.72(b)(3)(ii)(A) is not applicable to the event. Additionally the guidance contained in Regulatory Issue Summary (RIS) 2001-14, 'Position on Reportability Requirements for Reactor Core Isolation Cooling System Failure' was reviewed and it was confirmed that the RCIC System is not credited in the UFSAR for mitigating the consequences of a rod ejection accident, so the 10 CFR 50.72(b)(3)(v)(D) accident mitigation criterion does not apply. Consequently this notification is being retracted." The licensee informed the NRC Resident Inspector. Notified R1DO (Bellamy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-05-04
42548 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-05-03 07:00 | 2006-05-03 13:55 | 2006-05-03 | LOSS OF RESPONSE CAPABILITY - TECHNICAL SUPPORT CENTER (TSC) "This report is being made pursuant to 10CFR50.72(b)(3)(xiii), 8-hour Non-Emergency Report due to the loss of off-site response capability. As of 0700 Central Daylight Savings Time on 5/03/2006 the TSC was declared non-functional due to the discovery of non-conservative surveillance acceptance criteria for the TSC ventilation system flow balance. The acceptance criteria allow for a higher percentage of pressurization flow from filtered outside air and lower recirculation flow than is supported by the radiological consequences analysis for the TSC. This condition is complicated by the fact that the radiological consequences analysis has not been updated to incorporate changes to plant operation and radiological source term derived from the current license basis Loss of Coolant Accident analysis. Preliminary evaluations using current plant configuration, current TSC ventilation flow balance values, and current calculation methodology indicate that post-accident dose to TSC personnel is approximately 31.7 Rem to the thyroid, exceeding the acceptance criterion of 30 Rem. "Activities to revise applicable surveillance acceptance criteria and restore TSC functionality by re-balancing TSC ventilation flows to establish acceptable dose consequences have been initiated and are expected to be complete by 2000 on 5/3/2006. Affected Emergency Response Organization members have been instructed on compensatory measures in place until the TSC is fully functional. "Callaway Plant is currently operating in Mode 1 at 100% power. Normal plant operation is unaffected by the partial loss of TSC function. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM F. BIERMANN TO P. SNYDER AT 2036 ON 5/3/06 * * * "TSC ventilation flow balancing activities to restore TSC functionality have been completed. The TSC was declared functional and restored to service at 1930 CDT on 5/3/06." The licensee will inform the NRC Resident Inspector. Notified R4DO (Bywater). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-05-03
42547 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-05-03 02:14 | 2006-05-03 12:28 | 2006-05-03 | DEGRADED CONDITION "Greater than one percent of steam generator (SG) 2-4 tubes were determined to be defective and require plugging. Diablo Canyon performs 100% bobbin inspection of SG tubes, thus, no expanded bobbin inspection scope was required. "On May 3, 2006, during the Unit 2 thirteenth refueling outage (2R13), final analysis of eddy current data of SG 2-4 indicated that greater than one percent of the total tubes inspected were defective placing them in Category C-3. Thirty four (34) detective tubes in SG 2-4 were detected and are being plugged. Most of the pluggable indications are due to axial outside diameter stress corrosion cracking at the hot leg tube support plates. Diablo Canyon TS 5.5.9, Table 5.5.9-2, requires 'Notification to NRC pursuant to 10 CFR 50.72(b)(2)' (replaced by 10 CFR 50.72(b)(3)(ii), an 8-hour non-emergency ENS report requirement). "An NRC teleconference in accordance with TS 5.6.10.d to report the preliminary SG tube inspection results is scheduled for May 3, 2006, at 1000 PDT. "A Special Report in accordance with TS 5.6.10.a to report the number of tubes plugged in each SG, and TS 5.6.10.c describing the cause of the tube degradation and corrective measures taken to prevent recurrence will be submitted prior to returning Diablo Canyon Unit 2 to power operation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-05-03
42546 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2006-04-26 16:00 | 2006-05-02 16:22 | 2006-05-02 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was provided by the state via facsimile: "Description of event: At [approximately] 1600 hours, a portable moisture density gauge and its user were hit by heavy equipment. The gauge was run over, flattening the gauge. The user was injured and was taken for medical treatment. At the time of the notification, the RSO was enroute to evaluate the condition of the gauge. RCP advised the caller to contact [phone number deleted] if the RSO determines the source to be leaking, or if a response team is needed. Additionally, RCP advised the licensee to provide an update upon determination of gauge condition, as well as specific [information]. [The] gauge was a Troxler moisture density gauge Model 3430, Serial #32478. "Isotope: Am-241 (44 millicuries) and Cs-137 (9 millicuries). "[On] May 1, 2006 [RCP was] notified by [the] RSO that the source was stuck in the out position and it is being stored at their facility shielded by concrete test cylinders. Troxler has been notified and is sending a container to ship the gauge back in. A leak test has been performed. [The licensee] will send [the state] a summary of the event and information on the gauge." Georgia Department of Natural Resources Report ID No. GA-2006-10. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2006-05-05
42545 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-05-02 | 2006-05-02 16:09 | 2006-05-30 | AGREEMENT STATE REPORT - LOST OR STOLEN TROXLER GAUGE The following information was received from the state via e-mail: " [The licensee's] Radiation Safety Officer (RSO), Illinois Dept. of Transportation (Radioactive Material License No. IL-1100-01), called to report [to Illinois Emergency Mgmt. Agency] that a Troxler moisture density gauge, Model 3440, serial no.16550 [Cs-137 Source S/N 50-5822, 8 millicuries; Am-241/Be Source S/N 47-11975, 40 millicuries] was stolen from one of their vehicles assigned to their Edwards subsite (Peoria area). The open bed Dodge Ram truck was at a Peoria asphalt plant when the discovery was made. The user went to use the device this morning at the site and when he opened the back of his vehicle to remove the gauge, he noted the gauge was missing from the transport container although initial appearances suggested the container was still secure and intact. The transport container is bolted and padlocked to the bed of the vehicle. In addition the transport case has a locking hasp which is padlocked. This locking device was damaged and the gauging device subsequently removed. It is not known at this time when the device was actually stolen. It was last used on April 17, 2006. Peoria County Sheriffs personnel have been contacted as well as the Illinois State Police. "[The RSO's] investigation this afternoon showed that no other tools or equipment had been taken from the vehicle although other items contained in the transport case were missing such as the reference block, and cleaning kit. The operator indicated that he could not consciously remember verifying the security of the transport container since the last time the gauge was used in April, only that it appeared to be locked. He was able to confirm that the handle of the gauge had been secured and padlocked following its last use." Illinois Emergency Mgmt. Agency Item No: IL060020 * * * UPDATE AT 16:20 ON 5/30/2006 FROM D. PERRERO TO ABRAMOVITZ * * * "On May 29, 2006 the Agency was contacted by the Peoria Fire Department (PFD). The PFD had responded to a request from the Peoria Police Department to investigate a moisture/density gauge which had been found by a member of the public in Kickapoo Creek. Upon investigation by the PFD, it was determined that the radiation levels from the device were as expected for an intact device with no shielding failure. The device was taken into custody and secured by the Peoria Police Department in a remote portion of their Police Property Division. The information on the identification plate on the device was used to positively determine ownership as the Illinois Department of Transportation (IDOT). On Tuesday morning, the IDOT Radiation Safety Officer was contacted and advised of the situation. Arrangements were immediately made for him to personally go to Peoria to identify the gauge, inspect its condition and safely transport the gauge back to their Springfield, IL offices for further repair and evaluation. Upon his arrival he determined that the gauge handle was still locked in the safe position and there was no structural damage to the gauge. The gauge was field tested with negative results for contamination due to leakage. IDOT intends to have the gauge cleaned, serviced, calibrated and put back into service after replacement of the electrical components. "Pending receipt of the final report from the IDOT RSO which details the correct action taken to prevent a recurrence, we are considering this matter closed." Notified NMSS (Morell), R3DO (Kozak) and ILTAB (via E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-05-05
42543 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-05-01 07:30 | 2006-05-02 11:30 | 2006-05-02 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via email: "The licensee notified [the State of Washington] office via [the] agency hotline phone number at 8:00 a.m. Monday, May 1, 2006 of a theft of a Troxler model 3430 portable moisture/density gauge [Serial Number 27641; 8mCi of Cs-137 and 40 mCi of Am-241/Be]. The theft occurred sometime between Friday (p.m.) April 28, 2006 and Monday (a.m.) May 1, 2006 from a temporary jobsite trailer located at the Wal-Mart construction site on 7110 Bridgeport Way, Lakewood, Washington. The gauge was last seen Friday, April 28, 2006 when the gauge was secured in the jobsite trailer by the licensee's gauge user. The Licensee indicated that the gauge operator employed by the licensee arrived at the job-site and found the padlock on the outside of the trailer had been cut. Once in side, he found the chains securing the gauge case had also been cut and the gauge was missing. Nothing else appeared to be missing from the trailer. The gauge user was not present at the jobsite over the weekend and the licensee can not determine the exact day or time it was stolen. A police report was filed with the Lakewood Police Department and given report number 061210259." Washington Report Number WA-06-020 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-05-05
42542 | -1 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2006-05-01 20:29 | 2006-05-02 02:15 | 2006-06-29 | LOW TEMPERATURE OVERPRESSURE PROTECTION (LTOP) TRAINS INOPERABLE "Event: At 2029 hours, Oconee Unit 3 was in Mode 5 for a refueling outage. The administrative controls which comprise one train of Low Temperature Overpressure Protection (LTOP) were not yet in service, but a dedicated LTOP operator was in place as a Tech Spec required compensatory measure. Instrument Technicians performing a procedure erroneously isolated the low range RCS pressure indication, which removed the Power Operated Relief Valve (PORV) from service while required for LTOP. This placed Unit 3 in a one-hour action statement per Technical Specification 3.4.12, Condition H. "Initial Safety Significance: This is potentially a condition which could have prevented the fulfillment of a safety function (LTOP). Both the automatic PORV train and the Admin Control train were inoperable per Technical Specifications. However, a dedicated LTOP operator was in place meeting the compensatory measures requirement for continued operation per TS 3.4.12, Condition F related to the Admin Control requirement. No event occurred while in this condition which would challenge the LTOP function. "Corrective Action(s): Operator at the controls recognized the loss of indication and contacted the Instrument Technicians. They verified their error and returned the instrument to service within one hour." The licensee will notify the NRC Resident Inspector. *** UPDATE FROM R.P. TODD TO J. KNOKE AT 16:34 ON 06/29/06 *** "At 0215 EDT on 5-2-06, Oconee made an ENS notification to report a condition which could have prevented the fulfillment of a safety function, specifically Low Temperature Overpressure Protection (LTOP). "The LTOP Technical Specification (TS) 3.4.12 requires that a) the Power Operated Relief Valve (PORV) be operable, and b) administrative controls be in place to assure greater than 10 minutes are available for operator action to mitigate an LTOP event. As stated in the initial report, during shutdown for a refueling outage instrument technicians erroneously isolated the low range RCS pressure indication, which made the PORV inoperable for automatic operation while required for LTOP. In addition, the administrative controls were not yet fully established. "However, if a specific sub-set of administrative controls are in place, the TS allows credit for a dedicated LTOP operator as a compensatory measure. Upon further review, Oconee has confirmed that a) the PORV remained available for manual initiation by the dedicated LTOP operator, and b) the dedicated LTOP operator and associated sub-set of administrative controls were in place. This satisfied the required actions of TS 3.4.12 Condition F and assured that an LTOP event could be mitigated. Therefore, Oconee concludes that this event did not constitute a potential loss of safety function. "Actions were taken to restore the instrument alignment to restore automatic actuation capability for the PORV within the required action time per TS 3.4.12. Therefore there was no operation in a condition prohibited by Tech Specs. As a result, the event is not reportable under 50.72 or 50.73 and the ENS notification is hereby retracted. "Corrective Action(s): As stated above, the instrument alignment was restored to return the PORV to an operable status for automatic actuation. Subsequently, the full set of administrative controls were established. As shutdown continued, the unit exited the LTOP region." The licensee notified the NRC Resident Inspector. Notified the R2DO (Decker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-05-02
42541 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-05-01 10:00 | 2006-05-01 18:05 | 2006-05-02 | AGREEMENT STATE REPORT - LEAKY SEALED SOURCE Baylor University identified a leaking Americium-241 sealed source. They were preparing the source for shipment to Los Alamos as part of the lost source recovery program when they identified leakage during a leak test. The state received conflicting information from the licensee who said that the activity of the source was either 1 millicurie or 191 millicuries. No further information was available at the time of the report. The state will follow up on this report with additional information after they gather it. * * * UPDATE FROM A. TUCKER TO P. SNYDER AT 1301 ON 5/2/06 * * * There were no personnel consequences as a result of this incident. No uptakes were reported. The source, ICN serial number 74101, was a one inch diameter check source that was being prepared for shipment to the Los Alamos National Laboratory off-site recovery program on 4/25/06. The source was in storage for some period of time immediately prior to being prepared for shipment. The activity of the source is 0.1909 microcuries of alpha and 0.0234 microcuries beta/gamma. "The [licensee's] radiation safety staff isolated the source in a sealed container and surveyed all areas to ensure that the facility and other articles in contact with the source have not been contaminated. A contractor has been secured to encapsulate the source so that it can be disposed of." This event is being tracked as Texas Incident Number I-8329. Notified R4DO (Bywater) and NMSS (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-05-04
42540 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-05-01 11:00 | 2006-05-01 14:40 | 2006-05-01 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "The licensee's radiation safety officer, [deleted] called the [Illinois Emergency Management Agency Division of Nuclear Safety (IEMA-DNS)] to report that a vehicle used to transport a portable moisture density gauge had been stolen. [The licensee] indicated that a 2004 White Chevy Astro Van with license plate IL 43701F had been stolen from a jobsite at 820 South Damon Street, Chicago, IL at 11:00 hours this morning. "Chicago Police have been called to the scene to investigate and to alert them as to the situation." The Chicago Police has issued a 'be on the lookout' notice for the stolen vehicle. IEMA-DNS indicated that the licensee reported that the gauge was secured to the vehicle. The stolen gauge was a Troxler Moisture Density Gauge Model 3430, Serial Number 23187. The gauge has 2 sealed sources a 8 millicurie Cs-137 source (s/n 75-9797) and a 40 millicurie Am-241/Be source (s/n 47-19015). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-05-04
42539 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-04-26 | 2006-05-01 13:27 | 2006-05-02 | AGREEMENT STATE REPORT - STOLEN SPECTRUM ANALYZER "N.C. Radiation Protection Section was notified on 01 May 2006 by the RSO for Carolina Environmental, Inc. of the theft of a Niton Model XLP 303-A portable Spectrum Analyzer (Serial No. 7225). The gauge contained one sealed source: (1) Cd-109, 40 millicuries, source. The device was stolen from vehicle between 04-26-06 and 04-29-06 (exact date and time unknown). The device was stored in a grey plastic pelican style medium sized suitcase Exterior labeling and security on the case is unknown at this time. The vehicle had been in the Boston, [Massachusetts] area during this time frame. "The NC Radiation Protection Section is investigating compliance issues related to the NC licensee. "N.C. Radiation Protection Section is notifying the regional FBI, the N.C Highway Patrol, the State Bureau of Investigation, Nuclear Regulatory Operations Center, Massachusetts Radiation Control Program, local Massachusetts law enforcement are being informed by the victim of theft." * * * UPDATE FROM L. COX TO P. SNYDER AT 1315 ON 5/2/06 * * * The spectrum analyzer reported as stolen yesterday in Boston, Massachusetts as part of a reciprocity agreement was reported found today. The licensee said that the source was removed from the vehicle by a family member and stored without the custodian's knowledge. The licensee identified this on 5/2/06 and will contact local law enforcement and the state of Massachusetts about the recovery of the anayzer as well. The state of North Carolina will continue to follow this event and report additional information as it becomes available. Notified R1DO (R. Bellamy) and NMSS (G. Morell). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-05-04
42538 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2006-04-29 | 2006-05-01 08:31 | 2006-05-01 | AGREEMENT STATE - DAMAGED MOISTURE DENSITY GAUGE A representative of the State of Ohio Bureau of Radiation Protection reported an incident resulting in a damaged moisture density gauge. A moisture density gauge was run over by a truck at the Port Clinton, Ohio landfill when the State licensee was setting up to use the gauge. The top of the gauge was smashed and the fire department and a consultant for the licensee responded to the scene. There was no indication of contamination or damage to the sources. The gauge was placed back into its container and locked up at the landfill at a secure location. The State is sending inspectors out today to assess the incident and licensee actions. The licensee plans to ship the gauge to a repair facility. The State did not have the make or model of the gauge or source serial numbers at the time this event was reported. The licensee number of the licensee was given as Ohio license 31210-2500-5000. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2006-05-04
42537 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-05-01 04:39 | 2006-05-01 05:17 | 2006-05-01 | UNUSUAL EVENT DECLARED DUE TO A FIRE IN AN ISOPHASE BUS DUCT LASTING 11 MINUTES "The Unusual Event was declared due to a fire lasting greater than 10 minutes (after discovery) within the protected area. The fire was located on the Isophase Bus Duct near the Main Transformer. A load reduction to 80% rated thermal power is in progress on Unit 1. The fire was extinguished at 0450 with dry chemicals extinguishers." The licensee believes the fire was on cabling in the Isophase bus duct due to overheating. The licensee has been monitoring hot spots on the duct cabling for several days. The fire did not apparently impact any other systems and observers are at the location monitoring for any change in conditions. No Tech Spec Limiting Conditions of Operations resulted from the fire and there is no impact on Unit 2 operations (which is currently at 100%). Termination criteria will be based on management judgment and safety assessment. * * * UPDATE FROM P. UNDERWOOD TO M. RIPLEY 0727 EDT 05/01/06 * * * "Unusual Event terminated at 0655 [EDT]. Fire extinguished. Reactor power reduction continuing. Management evaluating continued operation." The unit is currently at 77% power and plans are to reduce power to 60% pending their evaluation of continued operation. The licensee will notify the NRC Resident Inspector. Notified R2 DO (K. Landis), NRR EO (M.J. Ross-Lee), IRD Manager (P. Wilson), DHS (S. York), and FEMA ( M. Roland). | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-05-01
42536 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-04-29 10:56 | 2006-04-29 14:19 | 2006-04-30 | DISCOVERY OF AFTER-THE- FACT EMERGENCY CONDITION - UNUSUAL EVENT DUE TO RCS LINEUP "D.C. Cook Unit 2 was in Mode 4 and heating up after Unit 2 Cycle 16 refueling outage when 2-IMO-340 (East RHR pump to Charging Pump Suction Header) was throttled open. RHR suction was aligned to Loop 2 Hot Leg with wide range RCS pressure at 337 psig and RCS average temperature 280 degrees Fahrenheit. Charging header safety valve 2-SV-56 lifted with a setting of 220 psig and relieved to the Pressurizer Relief Tank (PRT) between 10:56:00 and 10:58:30. 2-IMO-340 was then closed. Approximately, 120 gallons of reactor coolant were directed to the PRT during the approximate 2.5 minutes, resulting in a flow rate of approximately 48 gpm, greater than the 25 gallon per minute identified leak rate limit for an Unusual Event [10 CFR 50.72(a)(1)(i)]. Time of discovery for leakage quantity and reportability was 13:21 on 4/29/06. "Therefore, for approximately 2.5 minutes, D.C. Cook Unit 2 met the conditions for an Unusual Event. However, this fact was discovered after leakage was stopped. Unit 2 is stable in Mode 4 at 340 degrees Fahrenheit and 405 psig RCS pressure. "An Unusual Event was NOT declared, but the conditions for an Unusual Event were met under Emergency Condition Criteria S-8 between 10:56:00 and 10:58:30 on 4/29/06. This ENS notification is being made within one hour of the discovery of the undeclared event." The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 4/30/06 AT 1419 EDT FROM D. TURINETTI TO J. MACKINNON * * * "EN# 42536 reported that D.C. Cook Unit 2 satisfied the conditions for entry into an Unusual Event under Emergency Condition Criteria S-B, identified RCS leakage exceeding 25 GPM. This was identified after system alignment had been restored, ending the event, and was reported as an after the fact declaration that the conditions for an Unusual Event had been satisfied, but not declared. Subsequent review of this event has determined that the conditions for Emergency Condition Criteria S-B were not satisfied in that no identified RCS leakage occurred during this event. The diversion of 120 gallons of CVCS [Chemical Volume and Control System] inventory was the result of plant alignment by Operations personnel which was immediately recognized and terminated. Plant systems and components functioned as designed to terminate this event." The licensee will notify the NRC Resident Inspector. Notified R3DO (H. Peterson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | UNUSUAL EVENT | 3 | MI | POW | [5 empty] | 0 | 2006-04-29
42535 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-04-28 | 2006-04-28 15:05 | 2006-04-28 | AGREEMENT STATE REPORT FROM THE STATE OF FLORIDA - STOLEN TROXLER MOISTURE DENSITY GAUGE Event was received at the NRC Operation Center via e-mail. "This office was notified of the theft of a soil moisture density gauge at a temporary job site. While the tech was inside a building, which is under construction, drilling holes, the locked transportation box was forced open and the gauge was stolen. They did not get the keys to the gauge. The licensee is considering offering a reward for the return the gauge. Florida is investigating." Incident occurred at 3251 NW 103rd Street, Miami, FL. Troxler Model Number 3430, Serial Number 26593. Contains 8 milliCuries of Cesium-137 and 40 millicuries of Am-241/Be. Florida Incident Number: FL06-055 * * * UPDATE VIA E-MAIL FROM CHARLES E. ADAMS TO MACKINNON ON 04/28/06 AT 1610 EDT * * * "Florida Investigator has determined that the transportation case was not locked and was not in view of the tech when the gauge was taken." R1DO (Barkley) & NMSS (Morell) notified and NSIR (ILTAB) e-mailed. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-05-03
42534 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-04-27 19:29 | 2006-04-28 03:25 | 2006-06-16 | TWO TRAINS OF SHIELD BUILDING VENTILATION INOPERABLE At 19:29 on 04/27/2006 the Kewaunee Power Station declared two trains of Shield Building Ventilation (SBV) inoperable. Train B SBV was declared inoperable on 4/25/2006 at 17:25 when SW Train B was declared out of service for a leak that developed on the branch header to Diesel Generator B and TS 3.3.e.2 was entered. On 4/27/2006 at 19:29 QA typing discrepancies in RR-119 were discovered. QA-2 components were used in a QA-1 system, which could potentially cause a failure of some safety related equipment powered from this relay rack. As a result, all safety related equipment powered from RR-119 were declared inoperable and the appropriate technical specifications entered. SBV Train A Damper Control is powered from RR-119 and was declared inoperable at 19:29 on 4/27/2006 resulting in two trains of SBV being inoperable and TS 3.6.c.1 entered. The QA-2 components that may have an adverse affect on QA-1 safety related components in RR-119 have been removed and both trains of SBV were declared operable at 00:29 on 4/28/2006. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM JERRY RISTE TO W. GOTT 1524 EDT ON 6/16/06 * * * "This event was reported on April 27, 2006 (Event Number 42534) for two trains of shield building ventilation (SBV) being declared inoperable. Train B SBV was declared inoperable due to loss of the service water spray system for the SBV charcoal filters and Train A SBV was declared inoperable due to relay rack RR-119 Quality Assurance typing discrepancies (relay rack provides power for SBV Damper Control). Subsequent review of analysis determined that the SBV spray system is not required for post-LOCA operation to control the release of radioactive material. Therefore, Train B of SBV was not required to be declared inoperable when Train B service water was declared out of service. With only one Train of SBV being inoperable, this event is not reportable and is being retracted. "The licensee notified the NRC Resident Inspector." Notified R3DO (P. Louden). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-04-28
42533 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-04-27 22:30 | 2006-04-28 03:20 | 2006-06-21 | BOTH SAFETY INJECTION TRAINS DECLARED INOPERABLE At 22:30 on 04/27/2006 the Kewaunee Power Station declared both trains of Safety Injection (SI) inoperable. SI Pumps A & B were declared out of service per Surveillance Procedure SP 87-125 (Shift Instrument Channel Checks-Operating) due to SI Accumulator B level change of greater than or equal to 3%. SI Accumulator B level indicator (LI-935) indicated 30%. Previous indication recorded for SI Accumulator B was 33%. Per SP-87-125 'If the SI pumps are not vented prior to a level decrease of greater than or equal to 3%, the SI pumps become INOPERABLE.' TS 3.0.c (Standard Shutdown Sequence) was entered. At 0130 on 4/28/2006, venting of both SI Pumps was completed. SI Pump A was returned to service and SI Pump B remains out of service due to SW Train B inoperability. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 6/21/06 AT 0922 EDT FROM JERRY RISTE TO GERRY WAIG * * * "On 4/28/06, with Train B of SI already inoperable for other reasons, EN#42533 was made under 10CFR 50.72(b)(3)(ii)(B) for both trains of Safety Injection (SI) being inoperable due to excessive level drop in an SI Accumulator which had the potential to gas-bind both trains. "Subsequent evaluation has determined that, under the existing plant conditions, an SI train should only be declared inoperable if it is found that gas is actually present in the SI pump. Since venting after the event revealed no gas present, neither SI train was rendered inoperable by the Accumulator level drop, and thus both trains were never inoperable. Therefore, EN#42533 is being retracted." The licensee will notify the NRC Resident Inspector. Notified R3DO (K. O'Brien) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-04-28
42532 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-04-27 | 2006-04-27 10:45 | 2006-07-25 | AGREEMENT STATE REPORT - MISSING TROXLER GAUGE The licensee provided the following information via email: "Arkansas Department of Health and Human Services, announced today that one radioactive gauge is missing from a job site in Jonesboro, Arkansas. The gauge may pose a health risk to persons if handled or carried for an extended period of time. The missing gauge is in a yellow plastic transport case and weighs approximately 90 pounds. "The gauge is described as a Troxler Electronic Laboratory Model 3440 (Serial #36212) soil moisture/density gauge containing 9 millicuries of Cesium-137 and 44 millicuries of Americium-241/ Beryllium. "State police, local government officials and law enforcement agencies, the United States Nuclear Regulatory Commission and the Arkansas Department of Emergency Management have also been notified." The gauge appears to have been missing for at least a week. * * * UPDATE AT 1638 ON 5/4/06 FROM JARED THOMPSON VIA EMAIL * * * The following information was provided via email: "The Arkansas Department of Health and Human Services (DHHS) conducted an investigation in the Jonesboro, Arkansas area for the missing Troxler gauge (Serial Number 36212) on April 27, 2006. DHHS staff talked with licensee staff and the former Radiation Safety Officer. Based on these discussions, it appears that the gauge may have been inadvertently stolen when the portable storage building was stolen in mid-April. The gauge was last known to be inside a homemade, galvanized metal building. "On May 5, 2006, the licensee offered a reward for the return of the gauge. DHHS has been in contact with the scrap metal broker in the Jonesboro area in the event the building is scrapped." Notified R4DO (Bywater), NMSS (Reamer) and ILTAB (email). * * * UPDATE FROM JARED THOMPSON VIA EMAIL AT 1046 EDT ON 7/25/06 * * * The State provided the following information via email: "The Arkansas Department of Health and Human Services (DHHS) received notification on July 17, 2006 that the missing Troxler gauge (Model 3440; Serial Number 36212) was anonymously returned to the licensee's jobsite in Jonesboro, Arkansas on July 14, 2006. The transportation case and source rod were locked and secured. The gauge appeared to be in normal working condition and a leak test was performed by the RSO. The gauge is being shipped to Troxler for routine calibration and maintenance. DHHS considered this event to be closed." Notified R4DO (Farnholtz), NMSS (Morell) and ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2006-05-02
42531 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-04-27 02:07 | 2006-04-27 09:18 | 2006-04-27 | LOW PRESSURE STEAM LINE PRESSURE SAFETY INJECTION SIGNAL INADVERTENTLY INITIATED "On 4/27/06 at 02:00, with D.C. Cook Unit 2 in Mode 5 and the Control Rod Drive System de-energized under clearance and incapable of withdrawal, Instrumentation and Controls Technicians were beginning Instrumentation Channel Operational Test and Trip Actuating Device Operational Tests. The block for Main Steam Line Low Pressure Safety Injection was inadvertently removed. This allowed the existing low steam generator pressure (0 psig) and low RCS temperature (186 degrees F) to initiate a Low Steam Line Pressure Safety Injection and a Steam Line Isolation signal. "At 02:07 Unit 2 had a Main Steam Line Low Pressure Safety Injection signal on both Trains. The following components automatically started: Unit 2 West Centrifugal Charging Pump (on minimum flow recirc path with injection path isolated for LTOP -- no injection to RCS) Unit 2 South Safety Injection Pump (on minimum flow recirc path with injection path isolated for LTOP - no injection to RCS) Unit 2 East Residual Heat Removal Pump Unit 2 East Component Cooling Water Pump Unit 2 CD Emergency Diesel Generator Both Trains of Unit 2 Control Room Pressurization Both Trains of Unit 2 Phase A Containment Isolation signal Both Trains of Unit 2 Containment Ventilation Isolation. Both Trains of Unit 1 Control Room Pressurization Fans Unit 1 West Essential Service Water Pump "All available equipment actuated as expected for this condition. (The Unit 2 Boron Injection Tank was isolated under clearance for LTOP. The Unit 2 East Centrifugal Charging Pump, Unit 2 West Residual Heat Removal Pump, and Unit 2 West Component Cooling Water Pump were already running. The Unit 2 AB Emergency Diesel Generator was under a clearance for maintenance. The Unit 2 North Safety Injection Pump was under an administrative clearance for LTOP. The Unit 1 East Essential Service Water Pump was already running.) "After diagnosing the event, operators manually blocked the Steam Line Isolation and manually reset Safety Injection signals for both trains. Components were returned to normal status for plant conditions." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Cold Shutdown | Cold Shutdown |  | Cold Shutdown | Cold Shutdown |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-04-27
42530 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-04-26 20:49 | 2006-04-26 22:39 | 2006-04-27 | FAILURE OF RPS SIGNAL TO INITIATE REACTOR TRIP "At 2043 [CDT] on 4-26-06, during a plant shutdown with the reactor at approximately 35% power, the operating crew manually initiated a reactor trip. The operating crew had just stopped one of the two condensate pumps and then the remaining feedwater pump tripped unexpectedly. The operating crew recognized the turbine did not trip, as it is expected to automatically trip when no feedwater pumps are running. The automatic turbine trip would have automatically tripped the reactor. Therefore, the operating crew manually initiated a reactor trip. "Because the reactor did not automatically trip (i.e., failure of RPS to initiate and complete a reactor trip), the Shift Manager declared an Alert, at 2049, based on Chart F of Table 2-1 EPIP-AD-02. Therefore, this is a one-hour notification in accordance with 10CFR50.72(a)(1)(i) 'The declaration of any of the emergency classes specified in the licensee's approved Emergency Plan.' "The manual reactor trip is reportable (4-hour) in accordance with 10CFR50.72(b)(2)(iv)(B) 'Any event or condition that results in an actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "All systems functioned as expected following the manual reactor trip. Service Water Train B is inoperable because of a one-gallon per minute leak." All rods inserted fully. Decay heat is being removed with the steam dump and secondary PORVs. The condenser is losing vacuum due to the turbine trip. Auxiliary Feedwater Pumps started as required. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JERRY RISTE TO JOHN KNOKE AT 01:45 EDT ON 04/27/06 * * * "At 2049 on April 26, 2006, Kewaunee Power Station staff declared an Alert emergency classification (reference EN# 42530). The Kewaunee Power Station staff has assessed this event. There was no affect on the health and safety of the general public and no release of radiation. No plant personnel were injured and the only plant equipment problem was with the failure of a trip of both feedwater pumps to cause the main turbine to trip. The Kewaunee Power Plant staff has conducted a preliminary investigation of the control room indications and sequential events recorder, which indicates that before the manual reactor trip there was no automatic reactor trip signal present and a failure of the reactor trip breakers did not occur. The Alert was terminated at 0024 CDT [on 04/27/06]. The unit is currently in the Hot Shutdown Mode with plans to cool the plant to less than 350 degrees Fahrenheit." The licensee notified the NRC Resident Inspector and will be notifying State and local government and issuing a press release. Notified NRR EO (MJ Ross-Lee), IRD Mgr (P. Wilson), R3DO (H. Peterson), DHS (Holz ), FEMA (Steindurf), NRC/EPA (Crews), DOE (Wyatt), USDA (Timmons), HHS (Peagler). * * * UPDATE ON 04/27/06 AT 1718 EDT FROM JERRY RISTE TO ARLON COSTA * * * "When performing a review of the event reported on April 26, 2006 (EN# 42530), the Kewaunee Power Station staff determined another reporting criterion was met. An eight-hour report is required to be made per 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of 10 CFR 50.72 except when the actuation results from and is apart of a pre-planned sequence during testing or reactor operation.' 10 CFR 50.72(b)(3)(iv)(B)(6) is PWR auxiliary or emergency feedwater system. "As described in EN# 42530, a manual reactor trip of the Kewaunee Power Station was initiated at 2043 on April 26, 2006. The manual reactor trip was initiated when the plant experienced a loss of both feedwater pumps. With a loss of both feedwater pumps and a manual reactor trip, the narrow range water level in both steam generators decreased to the actuation setpoint value for starting the Auxiliary Feedwater Pumps, causing all three Auxiliary Feedwater Pumps to start as designed. Because the steam generator water level was below the actuation setpoint, this was a valid actuation of the auxiliary feedwater system. As a valid actuation of the auxiliary feedwater system, this condition is reportable under 10 CFR 50.72(b)(3)(iv). "The untimeliness of the report has been entered into the Kewaunee Power Station's corrective action program." The licensee notified the NRC Resident Inspector. Notified R3DO (H. Peterson). | 0 | 0 | 0 | 35 | 0 | 0 | -1 | 0 | 0 | A | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | ALERT | 3 | WI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2006-04-26
42529 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2006-04-26 18:19 | 2006-04-26 18:55 | 2006-04-26 | FIRE IN ADMINISTRATION BUILDING At approximately 18:19, a fire occurred in the administration building lower level. The fire was in the southeast corner of the building in a communications room (PBX room). The fire department was called and extinguished the fire at 19:04. No injuries were reported. The fire did not affect the ISFSI and backup communications were available if required. Notified the R1DO (Barkley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-04-26
42528 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-04-26 17:00 | 2006-04-26 18:23 | 2006-04-26 | PLANT S/D REQUIRED BY TS DUE TO LEAK IN SERVICE WATER SUPPLY LINE TO "B" EDG "At 1345 on April 26, 2006, a decision to shutdown the plant was made due to an Inoperable service water train. At 1700 on April 26, 2006, the plant shutdown was initiated. "On April 25, 2006, a leak was found on the Service Water supply line to the 'B' emergency diesel generator. At 1725 on April 25, 2006, the 'B' train of service water was declared inoperable and the technical specification limiting condition for operation was entered for one train of service water being inoperable. The end state for exceeding the allowed outage time for the limiting condition for operation for service water is the reactor coolant system Tavg less than 350 degrees Fahrenheit. "During investigation of the leak, an additional small leak was discovered approximately 180 degrees from the first leak on the same section of pipe. Based on this additional leak, a conservative decision was made to shutdown the unit. "It is estimated that the repair to the service water piping would not be completed within the allowed outage time and therefore per 10CFR50.72(b)(2)(i) this event is reportable as the initiation of any nuclear plant shutdown required by plant's technical specifications." All systems are currently functioning as required for the unit shutdown and the "B" EDG is operable and available. The licensee notified the NRC Resident Inspector. | 92 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-04-26
42527 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-04-25 13:30 | 2006-04-25 18:04 | 2006-04-25 | UNANALYZED CONDITION - CONTROL LOGIC ERROR "TMI Issue Report # 482679 identified an issue while performing reviews of fire abnormal operating procedures to assure compliance with the Fire Hazards Analysis Report (FHAR), in that a control logic error was identified in the circuitry elementary drawing for the isolation valves DH-V-6A and DH-V-6B between the Borated Water Storage Tank (BWST) and the Reactor Building (RB) sump. Plant circuitry was verified to be wired as per the elementary drawing. This circuitry design was to prevent a hot short, due to a fire, from opening the valve. "However, the identified control logic error could allow a spurious opening to occur on DH-V-6A or DH-V-6B due to a fire. The FHAR credits these valves as being protected from spuriously opening due to a fire in AB-FZ-5 (Auxiliary Building 281' general area). If this protection is not provided, then spurious opening could result in draining the BWST inventory to the RB sump. This hot short condition would result in the depletion of the BWST inventory and loss of the High Pressure Injection (HPI) makeup capability, resulting in an unanalyzed condition that significantly degrades plant safety. "This condition is reportable under 10 CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' A 60-day LER is also required under 10 CFR 50.73(a)(2)(ii)(B) for the same degraded condition. "An hourly fire-watch has been established in the affected fire zone in the 281' elevation Auxiliary Building as an interim compensatory measure. Additionally, the control circuitry at the 1A and 1B ES MCCs will be modified to prevent the RB sump isolation valves DH-V-6A and DH-V-6B from spuriously opening due to a hot short." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-04-25
42526 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2006-03-04 05:12 | 2006-04-25 16:20 | 2006-04-25 | INVALID EMERGENCY DIESEL GENERATOR START "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1), to report an invalid actuation reportable under 10 CFR 50.73 (a)(2)(iv)(A). "On March 4, 2006, with Unit 1 in Mode 5 'Refuel,' Instrument Maintenance (IM) technicians were installing a Barton level indicator for reactor vessel level indicator 1B21-R452A as part of a system modification. At 0512 hours, momentary 'Reactor Vessel Water Low Level 2' alarms were received in the Main Control Room, and the Unit 1 High Pressure Core Spray (HPCS) Emergency Diesel Generator (1B EDG) auto-started. A Reactor Vessel Water Level Low 2 condition sends a start signal to HPCS and the 1B EDG; however, because the HPCS pump control switch was in pull-to-lock, the pump did not start and did not inject water into the reactor vessel. "The initiating signal was reset, and at 0524 hours the 1B EDG was shutdown with the Maintenance Switch placed in 'Maintenance.' "Investigation determined that the 1B EDG had auto-started approximately 15 minutes after the IM technicians had completed work and placed the 1B21-R452A indicator back in service. The computer point alarm typer data was reviewed, and it was observed that only a single set of alarm points were received. Typically, when an alarm is caused by improperly valving in an instrument, multiple alarm points are received due to 'ringing.' Based on the 15 minute time delay and the lack of ringing, the apparent cause was determined to be an air bubble that was introduced during the modification and then migrated to the level transmitter, resulting in an invalid low level signal and an auto-start of the 1B EDG. Corrective actions included reviewing the remaining Barton installation modification work packages for unusual piping configurations that could contribute to air entrapment, and-for adequate system isolation requirements; i.e., bypassing trip units or removing components from service in order to prevent inadvertent actuations. "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an invalid actuation of an EDG." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-04-25
42525 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2006-04-20 | 2006-04-25 12:45 | 2006-04-25 | AGREEMENT STATE REPORT - LOST PROCESS INSTRUMENT SOURCE On 4/20/06 the licensee Radiation Safety Officer called the State of Georgia to report the loss of a process instrument source. The instrument contained a 100 millicurie Americium-241 source as part of an Industrial Dynamics Model CI-2 case inspector serial number 00224. The source serial number is 3139 and model number is 06765. The instrument was installed in a conveyor system that was removed and salvaged between March 20 and 25 of this year. The licensee contacted the Albany recycling facility to notify them of possible disposal at their facility but the recycling center said that their radiation detectors did not alarm. The recycling company also sends their scrap to IPSCO and ELG recycling operations in Mobile, AL. The licensee continues its search for the lost source. The licensee is currently reviewing their procedures for handling radioactive devices and the entire plant population will be retrained. The Georgia State ERC report number is 38364. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2006-04-28
42524 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2006-04-25 05:00 | 2006-04-25 12:31 | 2006-06-21 | SERVICE WATER PIPING FLOODING CONCERN IMPACTS RHR "At 0500 hours on April 25, 2006 with the plant in mode 5 and RCS loops filled, Operations declared the 21 and 22 Residual Heat Removal (RHR) pumps inoperable (see IP2-CR-2006-2133). This is reportable under 10 CFR 50.72(b)(3)(v)(B) as an event that at the time of discovery could have prevented the RHR pumps from removing residual heat. Residual heat removal is still available through the steam generators. The pumps were declared inoperable, but remained in operation, after a degraded horizontal section of Service Water (SW) line 405 was identified. SW line 405 is a non-ASME Section XI, non-Class A, seismically supported 24 inch return line routed through the Steam Generator Blowdown (SGBD) Tank room in the Plant Auxiliary Building (PAB) about 15 feet above the floor elevation of 51 feet. The ability of the pipe to withstand a seismic event has not currently been demonstrated. The consequence of a failure of this pipe is the flooding of the SGBD Tank room, cascading water down to the pipe case and then to the 15 foot PAB elevation. Water can drain to the transformer yard through a door at that elevation but the bottom of the RHR pump motors is lower than the door sill. "Compensating actions have been implemented. These include provisions to open the door to the transformer yard with a security guard to monitor the open door, install sand bags at the entrance to the RHR pump room to prevent water entry, and install blocking devices to prevent backflow through the RHR pump room floor drains. A 24 hour watch is being provided for implementation of these compensatory measures. The watch will have a sump pump should it be necessary for leaks. The RHR pumps were declared operable at 1200 hours. Corrective action for SWS pipe 405 is being planned." The licensee notified the NRC Resident Inspector. * * * UPDATED ON 6/21/06 AT 0920 EDT BY B. ROKES TO J. ROTTON * * * "Indian Point 2 is withdrawing the 8-hour non-emergency notification made on April 25, 2006, at 1231 hours. (Log No. 42524). "The notification on April 25, 2006, reported an event or condition that could have prevented the Residual Heat Removal pumps from removing residual heat [10CFR54.72{b}(3)(v)(B)]. On April 25, 2006, at approximately 0500 hours, Operations declared the 21 and 22 Residual Heat Removal (RHR) pumps inoperable after a degraded horizontal section of Service Water (SW) line 405 was identified. SW line 405 is a non-ASME Section XI, non-Class A, seismically supported 24 inch return line routed through the Steam Generator Slowdown (SGBD) Tank room in the Plant Auxiliary Building (PAS) about 15 feet above the floor elevation of 51 feet. The ability of the degraded pipe to withstand a seismic event had not been demonstrated. The consequence of a failure of this pipe is the flooding of the SGBD Tank room, cascading water down to the 15 foot PAB elevation where the RHR pumps are located potentially flooding the RHR pump motors. Compensating actions were implemented and the RHR pumps declared operable at 1200 hours. Subsequently, a detailed engineering calculation was performed that included development of a finite element model of the piping using the SAP 2000 software package. The calculational methodology was based on ASME Section XI, Appendix H, Code Case N-513-1 and was augmented with stress intensity factor solutions from API-579. Stresses resulting from pressure, deadweight, and seismic loads were evaluated and found acceptable demonstrating that the overall structural integrity of the piping is maintained for all loading conditions. Based upon the observed pipe leak rate of approximately 15 gallons per hour (gph), an evaluation of the potential flaw size corresponding to this leak for the lower bound internal pressure was performed. It was concluded that the small stress contribution that would result from seismic loading would cause the flaw to have negligible propagation during a seismic event. Since it was determined that the pipe could support stable flaws much larger than the small flaw that corresponded to the observed leak rate, engineering concluded that the through wall flaws that produced the leakage did not threaten the structural integrity of the pipe. The estimated leakage that could have occurred from the pipe during a seismic event is bounded at 26 gph. Because the 26 gph leakage rate is well within the capacity of the two PAB sump pumps (50 gallons per minute each), there was never any threat to flooding the PAB or a challenge to the operability of the RHR pumps." The licensee notified the NRC Resident Inspector and will be notifying the New York Public Service Commission. Notified R1DO (M. Sykes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-04-25
42523 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-04-21 | 2006-04-24 14:11 | 2006-05-10 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The State provided the following information via email: "On April 21, 2006, the Radioactive Materials Program of Arkansas Department of Health and Human Services was notified by Central Arkansas Radiation Therapy Institute, ARK-654-BP-12-08, located in Little Rock, of a possible misadministration (medical event), which had been identified during the post-implant CT of a prostate implant patient. Based upon the CT scan, the facility determined that the I-125 seeds had been implanted in the incorrect area. The post-implant treatment plan generated on April 24, 2006, indicated that a dose greater than 50 Rem had been delivered to an unintended area of tissue. "The licensee and Department will continue to investigate this event. A final written report regarding this misadministration (medical event) will be submitted within 15 days. "NRC Region IV was notified of the potential misadministration on April 21, 2006." * * * UPDATE RECEIVED FROM THE STATE (KIM C. WIEBECK) VIA E-MAIL TO JOE O'HARA ON 5/10/06 AT 0938 * * * "As previously reported, on April 21, 2006 CARTI notified Arkansas Department of Health and Human Services of a misadministration (medical event) that occurred during an I-125 prostate seed implant. The final written report was received on May 9, 2006. "The post-implant dosimetry imaging determined that the 84, I-125 seeds with average activity of 0.219 mCi on March 28, 2006, were misplaced approximately 4 cm inferior to their intended position. The post-implant dose calculation determined that a dose of 108 Gy, which was consistent with the prescribed dose, had been delivered to the incorrect area. "Root cause was determined to be two-fold. First was the inability prior to implant to place a Foley catheter to fill the bladder allowing a clear definition of the base of the prostate gland. Second was the human error in clear delineation of the prostate gland and alignment of the template prior to seed implant. "The patient will require further treatment of the prostate gland via re-implantation in order to deliver the appropriate dose. Any effects from the misadministration (medical event) may not manifest immediately and may be difficult to distinguish from the effects of the external beam IMRT treatment that the patient received prior to the March 2006 implant. "The licensee has implemented a new policy for inexperienced urologists that requires placement of the Foley catheter prior to implanting seeds, thus ensuring clear definition of the base of the prostate and the urethra." Notified R4DO(Powers) & NMSS EO(Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2006-04-27
42522 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-04-23 07:30 | 2006-04-24 10:42 | 2006-05-05 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A Troxler Moisture Density Gauge (sn 25459; 40 millicuries Am-241/Be and 8 millicuries Cs-137) was stolen from the operator's truck which was parked at his home. This was reported to the police and a reward was offered. Texas Incident No.: I-8327 * * * UPDATE FROM S. SIMMONS TO P. SNYDER ON 05/02/06 AT 1315 * * * This update was inadvertently entered as EN 42544 on 05/02/06. EN 42544 has been deleted. The following information was received from the state via e-mail: "On Saturday, April 22, 2006, a technician for Drash Consulting Engineers, Inc., was working a full time project performing density testing services. He stated that upon completion of the work day he felt very sleepy and was worried he might fall asleep at the wheel while driving. He had worked a lot of hours that week (70 hrs). He went home for a shower and a nap before returning the gauge to secured storage. [He] locked the gauge in the cab of the pickup truck with its transport case chained to the steering wheel. He did not lock the transport case. He awoke the next morning, Sunday, April 23, 2006, around 7:30 am and discovered that the side window of his truck was broken and the case that contained the Troxler Gauge Model 3440, was opened and the gauge was stolen. "Root Cause: Technician failed to secure the gauge in the most restrictive fashion possible. "Conclusion: The technician failed to follow company policy that the gauge must be returned to secured storage. "Licensee corrective actions: The technician was given a one day suspension without pay, a written reprimand, and additional training. On April 25, 2006 a Hazardous Materials Transportation handout ( 49 CFR, Part 172, and Subpart H) was given to all gauge users, that included specific discussion on theft of gauges. DCE supervisory staff will closely monitor technicians working long hours to be sure that gauges are being returned to storage in accordance with company policy. "Sealed source, device, etc, (make, model #, serial #): Troxler Moisture Density Gauge Model No. 3440, Serial No. 25459, with Am-241 (40 mCi) and Cs-137 (8 mCi) sources. "Texas Incident No.: I- 8327." The state is following up with the licensee. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-04-27
42521 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-04-20 | 2006-04-24 10:14 | 2006-04-24 | AGREEMENT STATE REPORT - STUCK SOURCE The State provided the following information via facsimile: "On April 20, 2006, Global X-Ray had a source that failed to return to the shielded position. The source is a 105 Ci source of Ir-192 manufactured by SPEC with model #G-60 and serial #NC-1506. The source was in a SPEC 150 radiography camera with serial number 905. The RSO was dispatched to the Lonestar Horizon barge at West Cameron 165 to retrieve the source. The source was retrieved at approximately 11:37AM on April 20, 2006. No excessive exposures were reported. The badges were sent in for processing. The RSO picked up approximately 430 millirem while performing retrieval activity." Event Report number: LA060006 This was reported by Global X-Ray and given NRC Event Number 42516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-04-27
42520 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-04-23 11:25 | 2006-04-23 11:59 | 2006-04-23 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGES RECOVERED The following was received from the state via email: "The duty officer was notified 1125 this morning of the theft and apparent recovery of two soil moisture density gauges in Miami, Fl at about 4 am this morning. Thieves broke into a locked Conex at a FL DOT job location on SR 826 between Bird & Flagler. They broke into the locked cabinet in which the gauges were stored. They then broke into the locked transportation boxes and took two gauges belonging to two licensees. "The first licensee is A Squared Group, license # 3727-2. Gauge was a CPN model MC-3, SN 350808026, Cs-137/AmBe sources 10/50 millicuries. "The second licensee is Metric Engineering, license # 1704-1. Gauge was a Troxler model 3440, SN 37243, Cs-137/AmBe sources 10/40 millicuries. "Miami-Dade PD apprehended the thieves as they were departing the storage site. The licensees believe the gauges are in the vehicle which has been impounded by Miami-Dade PD. They are trying to get access to the car to confirm that the gauges are there, but the PD has denied them access to this point. Licensees will call when they have confirmed the gauges are in the car and when they have been returned to their possession. Licensees will also submit a written report on this occurrence. "Florida continues to investigate this incident." * * * UPDATE FROM ADAMS TO SNYDER AT 1358 ON 4/23/06 * * * The following was received from the state via email: "Both licensees have possession of their gauges. They appear undamaged. The gauges will be leak tested and checked for functionality." Notified R1DO (Holody) and NMSS EO (Janosko). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-04-26
42519 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-04-06 | 2006-04-21 14:31 | 2006-04-21 | AGREEMENT STATE REPORT - TRITIUM EXIT SIGNS DISPOSED OF IN LANDFILL "A licensee, Hazen Research, Inc., Colorado license # 77-02, notified the [Colorado Department of Health] that 4 generally licensed Tritium exit signs were accidentally disposed of in the sanitary landfill during a building repair project. Apparently, an electrical contractor disposed of the exit signs in a dumpster after they were removed and replaced with new signs in February or March of this year. The error was discovered on April 6. The signs, Isolite Model: 2040-50G-10BK, were purchased in May of 2001, and contained about 7.5 Ci of Tritium each. "No other details are available at this time. "The [Colorado Department of Health] has initiated an investigation of this incident." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2006-04-26
42518 | -1 | ST. VINCENT HOSPITAL |  |  |  |  | 2006-04-20 12:10 | 2006-04-20 12:35 | 2006-04-24 | TECHNETIUM 99M SURFACE CONTAMINATION FOUND ON PACKAGE EXTERIOR St. Vincent Hospital received a package with surface contamination levels excess of Department Of Transportation 49 CFR 173.443 required levels. The package was an expected shipment of Iodine 131 for hospital use. The Hospital identified the contaminant via exterior swipe surveys as Technetium 99m at levels in excess of 5200 decays per minute per 100 centimeters squared. The integrity of the package was not compromised. No contamination was found on the interior of the package. The hospital called the shipper, Cardinal Health Systems, to notify them of the contamination found and has isolated the package in a controlled area. * * * UPDATE FROM WROBLEWSKI TO SNYDER AT 1427 ON 4/24/06 * * * The licensee is retracting this event based on the fact that the reported surface contamination levels are not above the DOT limits referenced above. Notified NMSS (Morell), R3DO (Peterson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2006-04-20
42517 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2006-04-19 11:00 | 2006-04-20 09:54 | 2006-04-20 | CONTRACT EMPLOYEE FAILED A RANDOM FITNESS FOR DUTY TEST A non-licensed contract supervisor tested positive for a controlled substance during a random test. The individual's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 26.73 |  |  |  | 0 | 2006-04-20
42516 | 0 | GLOBAL X-RAY & TESTING CORP |  |  |  |  | 2006-04-20 07:00 | 2006-04-20 08:28 | 2006-04-20 | PIPELINE RADIOGRAPHY SOURCE FAILED TO RETRACT Pipeline radiography was being performed offshore aboard the pipe lay barge "Lone Star Horizon" at West Cameron 165 (approximately 25 miles offshore of Louisiana). The source failed to retract into the camera after an exposure. At the time of the report, the Radiation Safety Officer (RSO) was being dispatched to the barge via helicopter to retrieve the source and return it to the camera. Camera: SPEC Model # 150 exposure device (serial number 905) containing 100 Curie Ir-192 source (SPEC # G-60 serial number NC-1506). * * * UPDATE AT 1535 ON 4/20/06 W. JOHNSTON TO P. SNYDER * * * The RSO went to the site and properly recovered the camera source. The RSO also took a new camera to the site and brought the existing camera back to be returned to the manufacturer for inspection. No excessive exposures resulted. Film badges were sent for processing. The RSO received approximately 480 millirem performing the retrieval activity. Notified R4DO (Kennedy) and NMSS (Morell). This was reported by the state of Louisiana and given NRC event number 42521. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-04-20
42515 | 0 | MALLINCKRODT- MARYLAND HEIGHTS |  |  |  |  | 2006-04-19 17:10 | 2006-04-19 18:49 | 2006-04-19 | POTENTIALLY LOST DEPLETED URANIUM SHIPPING SAFES The licensee recently performed a physical inventory of the depleted uranium "safes" used for shipment of Technetium-99m generators. These safes weigh about 45 lbs each and are used to provided shielding during the Tc99m shipments. Of approximately 3200 safes possessed by the licensee, 145 could not be located. The licensee is continuing its investigation and has expanded the search area within other buildings in the 20 acre facility. The licensee is also investigating possible inventory record keeping errors associated with the inventory tracking program. The licensee has informed the NRC R3 (Gattone) of the missing safes. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-04-19
42514 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-04-19 17:50 | 2006-04-19 18:49 | 2006-04-19 | RADIATION READING IN CONTAINMENT READ 100 TIMES ABOVE NORMAL LEVELS "At 0225 hrs on April 19, 2006, a container storing in-core instrument pieces rose to the surface of the flooded reactor cavity under its own buoyancy, causing unexpected high radiation readings in the general vicinity of the reactor cavity for a few seconds before the container returned to the bottom of the reactor cavity. Emergency Action Level RU2.2 was promptly reviewed, and it was determined that the threshold for an unusual event was not exceeded, because the area radiation monitors rose by a factor of approximately 100 versus the EAL setpoint of 1000 over normal levels. "Subsequently, at 1750 hrs, during post event investigation, it was discovered that dose rates indicated by an electronic dosimeter worn by an individual in the area at the time of the event may have exceeded the EAL setpoint of 1000 times the normal radiation levels for that area of containment for a few seconds. The total exposure received by the individual was less than 50 millirem. Therefore, this event is being reported in accordance with NUREG 1022, Revision 2, Section 3, 'Discussion' as a potential event discovered after-the fact." The licensee notified the NRC Resident Inspector, and Al Svilpe, Emergency Management Office in Van Buren County, MI. There is also expected to be some media attention from this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2006-04-19
42513 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-04-18 | 2006-04-19 18:12 | 2006-04-19 | AGREEMENT STATE - LOSS OF 20 TRITIUM FILLED SAFETY MARKERS DURING TRANSPORT The State of North Carolina reported that 20 "Safety Markers" (Model #SM145), each containing 0.53 Curies of Tritium (Serial #s 803205 through 803224) have been lost by United Parcel Service during transport. The markers were shipped from SRB Technologies, Inc of Winston-Salem, NC, on March 22, 2006, to a customer in Houston, TX. On April 10, SRB was notified by the customer that the shipment was never received. SRB contacted UPS for a trace of the package. On April 18, 2006, UPS notified SRB that the shipment was lost. The State did not have information on a UPS tracking number or trace number. No information on a point of contact at UPS was available. In addition, there was no information on the last known location of the package. North Carolina Report #06-14 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-04-24
42512 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2006-04-19 09:45 | 2006-04-19 15:58 | 2006-06-01 | POSTULATED SCENARIO WHERE CONTAINMENT SPRAY SYSTEM MAY BE UNABLE TO FULFILL DESIGN SAFETY FUNCTION "During a review of the operation of the plants emergency cooling system for the containment an unanalyzed single failure was discovered. The identified single failure scenario could result in the containment spray system being unable to fulfill its design safety functions. "In the event of loss of offsite power occurring after the initiation of an accident signal, the 480V undervoltage relays serve to trip open containment spray pump breakers (as well as other ESF breakers) in order to prepare the breakers for resequencing after the diesel generator output breakers have closed onto their associated buses. The undervoltage trip bypass function performed by the sequencer timer relay contacts serves to prevent tripping ESF breakers due to inadvertent actuation of the undervoltage trip circuits and allows ESF breakers to trip only when sequencers have been reset by a loss of voltage at the 4160V bus level. "In situations where a loss of power occurs at the 480 volt level without a coincident loss of power at the associated 4160 volt level, ESF loads supplied from the lost 480 volt bus, such as containment spray pumps, do not receive a trip signal due to the undervoltage blocking feature of the sequencing relays. For most ESF loads, this is not a problem and can be considered part of a single failure scenario affecting only one train of ESF equipment. In the case of containment spray pumps SI-3B and SI-3C, however, the failure of the associated breakers to trip during a single failure of bus 1B4B, results in the operation of a single spray pump, SI-3A with two containment spray valves open. This results in one pump operation to two containment spray headers. "Operating the containment spray system in a one pump, two header configuration creates the possibility of inadequate system performance. This configuration may result in overloading the running pump (due to runout) and inadequate NPSH to the running pump. This condition was intended to be prevented by a modification which installed an interlock between spray pumps SI-3B and SI-3C and spray valve HCV-344. The modification apparently failed to consider the single failure of specific 480 Volt buses. "Spray valve HCV-344 has been disabled in the closed position so that no external signals will allow the valve to be opened. Disabling this valve places the plant in a 24 hour LCO (Technical Specification 2.4.2.d) starting at 0950 CDT." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM MATZKE TO HUFFMAN AT 1439 EDT ON 6/01/06 * * * "On April 19, 2006, Ft. Calhoun station reported that an unacceptable single failure scenario had been identified that could result in the containment spray system being unable to fulfill its design safety functions. The failure scenario required that there be a loss of power at the 480 volt AC level without a coincident loss of power at the associated 4160 volt AC level. This resulted in the potential for one pump operation to two containment spray headers. "Following a review of failures that would cause this it was determined that of all the possible failure mechanisms that could impact the capability of affected 480 volt AC bus, such that both trains of containment spray pump could be adversely affected, the only failure mechanism that has unacceptable consequences is a failure of multiple phases of AC power failing in an open circuited manner without a fault occurring and, consequently, without supply breakers opening. This failure mechanism has been determined not to be credible. Therefore, it is not necessary to assume that this type of failure could occur as part of a design basis event. Therefore, no credible single failure could result in the failure of the containment spray system to perform its intended safety function. The report of April 19, 2006 is being retracted June 1, 2006." The licensee notified the NRC Resident Inspector. R4DO (Spitzberg) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2006-04-19
42511 | 0 | UNITED HOSPITAL CENTER |  |  |  |  | 2006-04-11 11:40 | 2006-04-19 14:13 | 2006-04-19 | MEDICAL EVENT - ADMINISTRATION OF GREATER THAN 50 PERCENT OF PRESCRIBED DOSE TO PATIENTS The RSO of the United Hospital Center called about a misadministration to 2 female patients being treated for cervical cancer. Each patient was to receive a total of 3000 centigrays, distributed via 6 treatments of 500 centigrays each. The treatment was a high dose rate Brachytherapy insertion of a 4.4 Curie Ir-192 sealed source into the cervical area. On their first treatment, patient #1 received 1040 centigrays at 11:40 EDT on 04/11/06, and patient #2 received 1058 centigrays at 11:45 EDT on 4/18/06. The attending physician is now going to alter the remaining treatments to 350 centigrays/treatment for each patient, thereby keeping the original total dose to the required 3000 centigrays/patient. The reason given for the misadministration was human error. The operator did not check the magnification reading on the computer before administrating the dose to each patient. The referring physician will be discussing this error with each patient when they come in for their next treatment on 4/21/06. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | WV | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2006-04-19
42510 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2006-04-19 09:00 | 2006-04-19 11:13 | 2006-05-17 | NON-CONSERVATIVE COLD OVERPRESSURE LIMIT CURVES DISCOVERED DURING ENGINEERING REVIEW "Cold overpressure limit curve utilized in the EMG (Emergency Guidelines) network including EMG F-0, Critical Safety Function Status Trees is incorrect and non-conservative. This could have resulted in some instances where the operator may have diagnosed a green path (no challenge) when a yellow (potential challenge) or orange path (severe challenge) actually existed. The consequence would have been failure to implement the correct functional restoration procedure." This problem was found during an Engineering review. The problem had existed since 1999. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION AT 1308 EDT ON 5/17/2006 FROM Lance Lane TO Steve Sandin * * * "The purpose of this notification is to retract a previous report made on 4/19/06 at 1113 hours (EN# 42510). Further evaluation revealed that a green path would not have been diagnosed instead of an orange path. The evaluation also concluded that this condition does not prevent the fulfillment of a safety function." The licensee informed the NRC Resident Inspector. Notified R4DO (Jones). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-04-19
42509 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2006-04-18 12:00 | 2006-04-18 20:22 | 2006-04-18 | SHIELD BUILDING VENTILLATION SYSTEM DECLARED INOPERABLE "On 4/18/2006, at 1200 hours, while the plant was operating at full power, the plant entered a 12 hour Technical Specification (TS) action statement for both trains of the Shield Building Ventilation (SBV) System being declared inoperable. The SBV System action statement was entered when the plant declared Relay Flacks RR-119 and RR-120 inoperable due to non-qualified fuses and cables being installed in six (6) of the boxes contained in these racks. The instruments associated with the six (6) boxes were not found in Technical Specification required instruments or alarms. The issue was that a downstream failure on the non-qualified Instruments may not have qualified fault protection, therefore a fault could impact safety related equipment. Other Technical Specification equipment affected by the inoperability of RR-119 and RR-120 include both trains of Inadequate Core Cooling Monitoring System (ICCMS), Reactor Vessel Level Indication (RVLIS), Pressurizer Safety Valve Outlet Temperature, and Pressurizer Power Operated Relief Valve Outlet Temperature. "At 1611 actions taken by plant staff returned RR-120 to operable and the 12 hour action statement for SBV was exited. The plant remains in a 7 Day Limiting Condition of Operation (LCO) pending the return of RR-119. Due to the fact that Train B of SBV has been made operable, a plant shutdown was not commenced. "This event is being reported under 10CFR50.72(b)(3)(v)(C) 'Any event that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to control the release of radioactive material'." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2006-04-18
42508 | 0 | TEAM INDUSTRIAL SERVICES |  |  |  |  | 2006-04-18 18:27 | 2006-04-18 19:27 | 2006-04-18 | EQUIPMENT MALFUNCTION CAUSED RADIOACTIVE SOURCE TO BE STUCK IN UNSHIELDED POSITION The licensee reported that there was a stuck source at a temporary job site [Motiva Refinery] in Perth Amboy, NJ. The exposure device involved was an Amersham-660B [Model A424-9] which contained a 17-Curie Iridium-192 source. When the source stuck in the extended position, the crew tried unsuccessfully to retract it. The workers then secured the area of concern and put up a controlled boundary to limit personnel exposure to 2 mr/hr or less. Licensee notified AEA-QSA [aka QSA-Global, Inc.] to come to the work site and repair or replace the defective equipment. It is unknown if any of the workers were overexposed due to this incident, however, licensee suspects they were not. Licensee will be evaluating the workers personal dosimeters, and other instruments, to ensure accurate readings of personnel exposure. * * * UPDATE FROM QSA-GLOBAL TO KNOKE AT 21:03 EDT ON 04/18/06 * * * QSA-Global, Inc. is going to Motiva Refinery in Perth Amboy, NJ, to perform an "emergency source retrieval" on the Amersham-660B [Model A424-9] which contained the 17-Curie Iridium-192 source. This work is being performed for their client Team Cooperheat located in Aston, PA. Notified R1DO (Holody), NMSS EO (Janosko and Pangburn) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-04-18
42507 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2006-04-18 12:45 | 2006-04-18 16:42 | 2006-04-18 | RECEIPT OF PACKAGE WITH SURFACE CONTAMINATION "Licensee called pursuant to 10 CFR 20.1906, to report the receipt of a package of radioactive material with removable surface contamination slightly exceeding the limits of 10 CFR 71.87(i). The package was received at approximately 1245 CT today by the VA Medical Center in Birmingham, AL. "Several wipe tests were performed on the package. The one showing the greatest removable contamination indicated 283 dpm/cm2, slightly exceeding the regulatory limit of 220 dpm/cm2. The package was received from a commercial nuclear radiopharmacy, Birmingham Nuclear Pharmacy, in Birmingham AL. The final delivery carrier has been notified." The radionuclide is Technetium-99m. HOO NOTE: The Department of Veterans Affairs coordinates all reports to the NRC from their NHPP Director's Office located in Little Rock, AR. NRC oversight for the VA Master Materials licensee is assigned to NRC Region III. Permittee: VA Medical Center, 700 South 19th Street, Birmingham, Alabama, 35233, Permit Number 01-00643-02. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2006-04-18
42506 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-04-17 00:26 | 2006-04-17 01:20 | 2006-04-17 | UNIT 1 MANUALLY TRIPPED DUE TO FAILURE OF A MAIN FEED REGULATING VALVE TO CONTROL STEAM GENERATOR LEVEL "Unit 1 reactor was manually tripped from 33% RTP due to the Loop 3 Main Feed Regulating Valve (MFRV) 1LV-0530 not controlling steam generator level in manual or AUTO. "A unit shutdown was in progress at the time of the trip due to concerns with the Loop 3 MFRV. The unit shutdown had commenced from 100% power on 04/16/2006 at 1603 hrs. "All systems functioned as required on the reactor trip including a feedwater isolation and the Loop 3 MFRV closing as expected. The unit is presently in Mode 3 at normal operating temperature and pressure. An investigation team is being assembled concerning the Loop 3 MFRV." All control rods fully inserted. No primary or secondary reliefs/safeties lifted during the transient. Unit 1 is currently in Mode 3 Hot Standby controlling Steam Generator Water Level using Auxiliary Feedwater supplied by both Motor Driven and the Steam Driven pumps. Decay Heat is being removed via the Bypass Valves to the Main Condenser. Offsite power is stable and all EDGs are available, if necessary. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 33 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-04-17
42505 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2006-04-15 16:15 | 2006-04-15 20:52 | 2006-04-16 | REACTOR SCRAM FROM 100% POWER "At 1615 CDT time on April 15th, 2006 with the Reactor at 100% power, River Bend Station experienced a reactor scram resulting from a RPS actuation. All plant systems performed as designed. The reactor is stable with pressure and temperature being controlled by feed water system and main steam bypass valves, respectively. The cause of the scram is not known at this time. The plant is conducting causal investigations to fully understand the cause of the plant scram." All control rods fully inserted, no safety valves lifted, and no Emergency Safety Feature actuations occurred on the scram. The electrical grid is stable. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1033 EDT ON 4/16/06 FROM KENNETH HIGGINBOTHAM TO S. SANDIN * * * "River Bend Station status on 04/16/2006: The unit is in Mode 3, Hot Shutdown, and stable. Investigation of the plant trip found an optical isolator in the control circuit for the end-of-cycle recirculation pump trip failed causing both recirculation pumps to shift to slow speed. The pump downshift placed reactor power and flow into the exclusion region of the power to flow map. The reactor received trip signals from APRM E & H heat flux exceeding their corresponding trip set points. The optical isolator is being replaced. Plant restart will commence pending successful replacement of the optical isolator." The licensee informed the NRC Resident Inspector. Notified R4DO (Pruett). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-04-15
42504 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2006-04-14 14:25 | 2006-04-14 16:07 | 2006-04-14 | MANUAL REACTOR TRIP DUE TO CONDENSATE PUMP AND FEEDWATER PUMP TRIP "At 1425 on April 14, 2006, a lockout trip of 11 Condensate Pump occurred. The condensate pump trip caused an expected lockout trip of 11 Main Feedwater Pump trip. With the loss of 50% of feedwater pump capacity, the Shift Supervisor directed a manual Unit 1 reactor trip. The manual reactor trip was successful and all systems responded as expected. The reactor protection system actuation is reportable under 10CFR 50.72(b)(2). A reactor trip from full power results in an expected steam generator narrow range level shrink to 0%. This resultant narrow range steam generator level caused an expected Auxiliary Feedwater System Actuation. Both 11 and 12 Auxiliary Feedwater Pumps started as expected. Auxiliary feedwater actuation is reportable under10CFR 50.72(b)(3). "Investigation is underway to determine the cause of 11 Condensate Pump lockout. "Plant operations are underway per emergency procedure 1ES-0.1, Reactor Trip Recovery, and 1C1.3, Unit 1 Shutdown, to stabilize the plant in Mode 3, Hot Standby." All control rods fully inserted. Steam generators are discharging steam to the condenser steam dump system. The Auxiliary Feedwater Pumps are maintaining Steam Generator level. The electrical grid is stable. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-04-14
42503 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2005-06-02 | 2006-04-14 15:35 | 2006-04-14 | AGREEMENT STATE REPORT - ABANDONED WELL LOGGING SOURCE The licensee provided the following information via facsimile: "06/03/05: High Bluff Operating, LLC reported The Rosel Company of Liberal, Kansas lost a logging tool downhole in Clark County, Kansas. The logging cable broke, and the tool dropped to a depth of 5866 feet. The tool was 'fished' from the hole, but the density pad broke off the tool and stayed in the hole. An experienced 'fishing tool expert' recommended that cement the possible source in place. "[High Bluff] proposes: 75' of red dyed cement on top of the pad with a 'whipstock' device preventing reentry of the hole. Set 5740 feet of production casing to prevent deepening. Post at the wellhead a plaque noting the required Information. "06/04/05: [Kansas] replied to [High Bluff] and concurred with his plan. "11/01/05: [High Bluff] sent in his final report. Correct the final depth to 5856'. Modified the plan of action to be 5710 feet of casing and 146 feet of red dyed cement by Allied Cement. The plaque was still awaiting production and placement. "11/11/05: [High Bluff] reported the plaque was unacceptable, and a new plaque was being made. "03/22/06: Received cd-rom of digital pictures taken of well site, time stamped 03/13/2006. Plaque meets general requirements. Event considered closed." Source: 2 Curie Cs-137, Serial Number CSV-K98 manufactured by Gulf Nuclear Kansas Report Number: KS050022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2006-04-19
42502 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2006-04-14 15:32 | 2006-04-14 15:32 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * FAILURE OF A FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employees access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.73 |  |  |  | 0 | 2008-05-11
42501 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-04-14 11:45 | 2006-04-14 13:35 | 2006-05-16 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE FROM ERICK MATZKE TO M. RIPLEY 1435 EDT 05/16/06 * * * The licensee provided updated information regarding compensatory measures that have been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R4 DO (W. Jones) and NSIR (D. Dorman) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-04-14
42500 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-04-14 | 2006-04-14 10:10 | 2006-04-14 | AGREEMENT STATE - TWO TRITIUM EXIT SIGNS LOST The State provided the following information via email: "Event type: Lost, two self-luminous, 20 Ci/ea., H-3, exit signs were discovered missing, presumed discarded. "Event description: The manufacturer is SRB Technologies (Canada), Inc. 1) Model: BetaLux-E/Luminexit, SN 272697, Activity: 20 Ci; 2) Model: BetaLux-E/Luminexit, SN 270605, Activity: 20 Ci. "One sign was noted as being discarded by the housekeeping staff and a subsequent inventory investigation showed that another sign was missing from an area that was renovated in August of last year." Texas Incident No.: I- 8325 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-04-19
42499 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2006-04-13 09:30 | 2006-04-14 08:57 | 2006-04-14 | AGREEMENT STATE - DAMAGED TROXLER GAUGE The State provided the following information via facsimile: "On the morning of April 13, 2006 at approximately 9:30 am CDT, a Troxler model 3430 moisture density gauge, serial number 22787 containing 8 millicuries of Cs-137 and 40 millicuries of Am-241:Be was damaged while in use at a temporary job site in Eutaw, Alabama when it was run over by a dump truck. The licensee, Gallet & Associates notified the Alabama Office of Radiation Control at 11:55 am. Gallet & Associates is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 991. The licensee representative stated that they were able to place the sealed source rod in the shielded position and lock the device in the safe position. Radiation levels around the gauge were found to be within the normal range. The gauge was placed back in the transport container and returned to the licensee's facility. The licensee was advised to perform a leak test of the gauge. "This is all the information that this Agency has at this time and is current as of 8:00 am CDT, April 14, 2006." Alabama Incident No 06-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2006-04-19
42498 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-04-06 11:00 | 2006-04-13 15:00 | 2006-04-13 | AGREEMENT STATE REPORT - STOLEN ALLOY ANALYZER An alloy analyzer was stolen between 11:00 and 12:00 on 4/6/2006. The device was in Beaumont, TX and the theft was reported to the local police (case number 069751). Description: Niton model XL 800, serial # U2184 Source: 10 milliCurie Cd-109 (This was the original activity when purchased five years ago), Source model # XFB3205, Serial # NR6244 Texas Incident Number I-8324 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-04-18
42497 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-04-13 07:38 | 2006-04-13 14:25 | 2006-04-13 | LOSS OF EMERGENCY CAPABILITY - TECHNICAL SUPPORT CENTER (TSC) "This report is being made pursuant to 10CFR50.72(b)(3)(xiii), 8-hour Non-Emergency Report due to the loss of emergency assessment capability. The TSC filter absorber unit (FUB7001) and the TSC were declared non-function at 0738 Central Daylight Savings Time on 4/13/2006 for charcoal replacement activities. Charcoal replacement activities have an estimated completion time of 2000 on 4/13/2006. Affected Emergency Response Organization members have been instructed in the event of an emergency to report to designated backup facilities. "Callaway Plant is currently operating in Mode 1 at 100% power. Normal plant operation is unaffected by the loss of ventilation filtration. "The licensee has notified the NRC Resident Inspector." * * * UPDATE AT 1855 ON 4/13/06 FROM D. LANTZ TO W. GOTT * * * "Maintenance and post maintenance testing activities for charcoal replacement in the TSC filter absorber unit have been completed. The TSC filter absorber unit and the TSC were declared functional and restored to service at 1738 CDST on 4/13/06" Notified R4DO (T. Pruett) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-04-13
42496 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2006-04-13 10:30 | 2006-04-13 14:09 | 2006-04-13 | INADVERTANT ACTUATION OF EMERGENCY NOTIFICATION SIRENS "The purpose of this report is to provide a telephone notification under 10CFR50.72(b)(2)(xi) to notify the NRC of the inadvertent actuation of the Oswego County emergency notification sirens at approximately 1030 on 4/13/06. Oswego County is participating in a radiological exercise involving a simulated emergency at the James A. FitzPatrick Nuclear Power Plant. It was during the simulated exercise that the sirens were inadvertently actuated. "The Oswego County Emergency Management Office issued a News Release identifying the inadvertent actuation of the emergency sirens. "The NRC Sr. Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-04-13
42495 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-03-09 | 2006-04-13 09:45 | 2006-04-13 | AGREEMENT STATE REPORT OF DAMAGED RADIOGRAPHY CAMERA The State provided the following information via email: "This is an incident involving a SPEC 150 exposure device with serial number 0288 that contained a 80 Ci source of Ir-192 (SPEC G-60 serial number NA-2006). On March 9, 2006 while radiographing a coupon, the exposure device was placed in contact with a welding lead. When the exposure device was cranked out the crankout cable formed an electrical conductor from the welding lead to the coupon. An arc and smoke was observed. The radiographer immediately returned the source to the shielded position. The radiographer approached the exposure device with a survey meter and determined the source was in the shielded position. The radiographer disconnected the source tube and replaced the safety plug. While attempting to remove the drive cable connector from the source pigtail, the connector came off. The radiographer replaced the dust cover cap, secured the exposure device in the transport container and called the main office. Neither radiographer received an excessive exposure. The exposure device and equipment were sent to SPEC for evaluation. SPEC stated that the integrity of the encapsulated source was not harmed, but the pigtail itself was unusable, and the source had to be disposed. The exposure device operated properly and was cleared for use by SPEC." Louisiana Report LA060005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-04-18
42494 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-04-12 08:13 | 2006-04-12 17:30 | 2006-04-18 | UF6 RELEASE DETECTION SYSTEM FAILED DURING TESTING "At 0813 CDT on 04/12/2006, the Plant Shift Superintendent (PSS) was notified that immediately following routine test firing of the C-333 Unit 4 cell 7 UF6 Release Detection System (TSR surveillance requirement 2.4.4.1-1), smoke and sparks were observed coming from the UF6 Release Detection System control module and the system ready light was extinguished. The Area Control Room alarm locked in and the system was declared inoperable by the PSS. The cell and associated piping were above atmospheric pressure (Cascade Mode 2) at the time of the failure. "The UF6 Release Detection System is a TSR system that is required to be operable per TSR 2.4.4.1, when a cascade cell and associated piping are in Cascade Mode 2. After discovery of failed system condition, a continuous UF6 smoke watch was initiated on the areas affected by the loss of detection capability in accordance with LCO Required Actions 2.4.4.1.B.1 and 2.4.4.C.1. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-06-1197; PGDP Event Report No. PAD-2006-03." There was no release from this event. The failure was shorted contacts in the alarm reset relay. * * * UPDATE FROM WALLACE TO KNOKE AT 19:04 EDT on 04/18/06 * * * "This report is being retracted. Subsequent to the event, Maintenance and System Engineering determined that the alarm disable switch control module faulted when the operator attempted to reset the ACR PGLD alarm. This fault caused the system power supply to fail. Resetting the alarms is the last step in the test procedure being performed when the failure occurred. Only after the alarms are cleared is the PGLD system returned to normal operating condition and testing complete. In this case, the evidence clearly indicated that the failure occurred during the conduct of the surveillance and the successful firing of the detectors and the start of the test provides positive evidence that the failure did not exist prior to the surveillance. Therefore, the in-service safety system failure reporting criteria of 10CFR 76.120(c)(2)(i) is not applicable. "The Senior Resident Inspector has been notified of this retraction." Notified R2DO(Lesser) and NMSS (Janosko). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-04-12
42493 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2006-04-12 13:35 | 2006-04-12 14:48 | 2006-04-12 | UNIT 2 EXPERIENCED AN AUTOMATIC REACTOR TRIP FOLLOWING THE LOSS OF THE "2B2" REACTOR COOLANT PUMP At 1335 EDT the Unit 2 Reactor tripped from 100% power on a Flux/Flow/Imbalance on two (2) RPS Channels "A" and "D." The initiating event was the trip of the "2B2" Reactor Coolant Pump (RCP) for unknown reasons. I & E Techs were working in the RCP Monitoring Cabinets at the time. Immediately following the RCP trip, Unit 2 commenced a runback as expected for approximately six (6) seconds before the RPS actuation occurred. All rods fully inserted with an anomaly noted for CRD [Control Rod Drive] Group 3 Rod 7 API [Absolute Position Indication] indicating approximately 21%, however, the PI [Position Indicating] Panel light was on. The licensee suspects that the problem is related to a reed switch for the API indication and not the actual rod position. Shutdown Margin has confirmed that the Reactor is subcritical. The Pressurizer Code Safeties and PORV did not lift during the transient. Unit 2 is currently stable in Mode 3 discharging steam to the Main Condenser via the Turbine Bypass Valves using Main Feedwater for steam generator level control. Offsite power is available and stable. This event did not impact Units 1 or 3. RCP "2B2" will remain secured until the cause of the trip is identified and corrected. There is no known primary to secondary leakage for Unit 2. The licensee has completed EOP (Emergency Operating Procedure) subsequent actions. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-04-12
42492 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-02-28 02:50 | 2006-04-12 09:38 | 2006-04-12 | INVALID SYSTEM ACTUATION DUE TO WORK INSTRUCTION ERROR "General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves. "The following information is provided as a 60 day telephone notification to NRC under 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of the 10CFR50.73(a)(2)(iv)(B) system checked above. NUREG1022 Revision 2 identifies the information that needs to be reported as discussed below. "(a) The specific train(s) and system(s) that were actuated. "This report is being made under 10CFR50.73(a)(2)(iv)(A). On February 28, 2006 at 02:50 EST the implementation of Work Order 1051442601, to perform a routine replacement of a relay 1C61-K86, called for lifting of wires related to the relay. During the evolution, the lifting of wires at CC-107 in panel 1 H11-P623 resulted in a daisy chain effect and the auto start of all four Standby Gas Treatment (SBGT) fans. Both the Unit One and Unit Two reactor building and refueling floor normal ventilation systems automatically shutdown and isolated. These actuations were a result of the loss of power to relay 1C61-K75. This relay initiates the logic for isolation of the reactor building and refueling floor ventilation and initiation of SBGT. "Subsequent investigation determined that in order to prevent this daisy chain effect the wires should have been lifted at DDD-1 in panel 1H11-P623. This error was the result of inadequate work instructions. "(b) Whether each train actuation was complete or partial. "The four Standby Gas Treatment (SBGT) fans auto started and both Unit One and Unit Two reactor building and refueling floor normal ventilation systems automatically shutdown and isolated. The SBGT initiation and the ventilation system shutdown were both complete actuations. "(c) Whether or not the system started and functioned successfully. "The above systems functioned successfully." The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-04-12
42491 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-04-11 09:24 | 2006-04-11 12:37 | 2006-04-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 0924 Unit 2 experienced multiple Fire Protection System Deluge Valve actuations for the Main Filter Banks, System Station Service Transformers (SSSTs) 2A and 2B, the Main Transformer, Condensate Polishing building ventilation charcoal filter and Decontamination building ventilation charcoal filter. The Transformers were unaffected by the spray actuation and remained operable. "No actual fire occurred or was observed for these components or areas. The Motor driven and Engine Driven Fire Pumps automatically started upon the actuations. These above noted areas and components received water spray down until manually isolated. "It was verified that both of the Charcoal Main Filter Banks (TS 3.7.8.1) had become wetted down by the spray actuation. With the charcoal main filter banks wet, their filtering capability becomes impacted and is being evaluated. These filter components were declared inoperable. "At 0924, Unit 2 entered the actions of Tech. Spec. 3.0.3. The requirements of Tech Spec 3.0.3 are: "Within 1 hour action shall be initiated to place the unit in Hot Standby within the following 6 hours, Hot Shutdown within the following 6 hours, and Cold Shutdown within the subsequent 24 hours. At 1055 Unit 2 commenced shutdown at 20%/hr. "The cause of the multiple actuations is not understood at this time. An Event Response Team has been formed to investigate the issue." All other safety related systems are operable. The action required for the licensee to exit this Tech Spec required shutdown will be to restore the charcoal filter banks to operable status. The licensee estimates the investigation, troubleshooting, and repair efforts to last approximately 40 hours. The licensee notified the NRC Resident Inspector. | 0 | 65 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-04-11
42490 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-04-10 16:25 | 2006-04-11 11:06 | 2006-04-11 | FITNESS FOR DUTY A contract employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2006-04-11
42489 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-03-11 04:32 | 2006-04-11 09:35 | 2006-04-11 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "On 03/11/06 at approximately 0432 hours, with Susquehanna Unit 1 in the Refueling Mode (0% power), the Unit experienced a partial isolation of Primary Containment isolation valves. The actuation occurred when a blown fuse disrupted power to a containment isolation logic relay. The inboard isolation valve to the 'B' Drywell Floor Drain Sump and the Containment Instrument Gas purge supply valve to the TIP indexer both closed. The 'A' Standby Gas Treatment system fan and the 'A' Reactor Building Recirculation fan successfully auto started during the event. "This event constitutes an invalid system actuation and is reportable under 10CFR 50.73(a)(2)(iv)(A). The condition meets the criteria of 10CFR 50.73(a)(2)(iv)(B)(2) because a general containment isolation signal affected containment isolation valves in more than one system. This notification is being provided via a 60-day optional phone call as permitted under 10CFR 50.73(a)(1) in lieu of a written LER. "As stated above, both valves affected by the invalid signal fulfilled their isolation function by successfully closing. At the time of the event, no other Primary Containment isolation valve was being maintained in a manner that required re-positioning. There were no challenges to the Reactor as a result of this event. The plant responded as expected. "Following replacement of the subject fuse, the isolation logic was successfully reset and affected equipment was restored to the desired status." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-04-11
42488 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-04-10 16:30 | 2006-04-10 23:33 | 2006-04-10 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM DECLARED INOPERABLE DUE TO DESIGN DEFICIENCY "EVENT DESCRIPTION: "At 1630 on 4/10/06, plant personnel identified a potential failure mode of the recently modified chlorine detectors. The failure mode has the potential to render the Control Room Emergency Ventilation (CREV) system inoperable following power restoration after a LOOP/LOCA event. Due to this design deficiency, the CREV system was declared inoperable per LCO 3.7.3, Control Room Emergency Ventilation System, which placed both units in LCO 3.7.3 Condition B. Required Actions for this Condition are to be in Hot Shutdown in 12 hours and in Cold Shutdown in 36 hours. In addition TRM [Technical Reference Manual] 3.18, CREV Smoke Protection Mode, is being entered for Condition B. The Plan required by TRM 3.18 Condition B is to remove the Chlorine Tank Car from site AND to disable the Chlorine detectors to prevent them from actuating. These actions were completed at 2100 on 4/10/06 and the CREV System Rad/Smoke Mode was restored to operable. "This situation has been evaluated as reportable to the NRC within 8 hours per 0OI-01.07, Attachment 1. The criteria is 10CFR50.72 (b)(3)(v)(D). The condition at the time of discovery that could have prevented the fulfillment of safety function of structures or systems that are needed to mitigate the consequences of an accident. (Item # 3.4.4 of 0OI-01.07 Attachment1). "INITIAL SAFETY SIGNIFICANCE EVALUATION: "The initial safety significance of this event is considered minimal due to the immediate implementation of Tech Spec and TRM required actions following discovery of the design deficiency. "CORRECTIVE ACTIONS: "The Plan required by TRM 3.18 Condition B is to remove the Chlorine Tank Car from site AND to disable the Chlorine detectors to prevent them from actuating. These actions were completed at 2100 on 4/10106 and the CREV System Rad/Smoke Mode was restored to operable. The Chlorine Tank Car will remain off-site and the Chlorine detectors will remain disabled until the design deficiency is corrected." The deficiency with the chlorine detectors which had been modified in February 2006 was identified using the plant simulator. The licensee informed the NRC Resident Inspector. | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-04-10
42487 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2006-04-10 12:33 | 2006-04-10 15:39 | 2006-04-10 | UNIT 2 ENTERED A TS REQUIRED SHUTDOWN DUE TO INOPERABLE AUXILIARY FEEDWATER PUMPS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On April 10. 2006, at approximately 12:33 hours Mountain Standard Time (MST), Palo Verde Nuclear Generating Station (PVNGS) Unit 2 commenced a reactor shutdown required by Technical Specification [TS] 3.7.5 Condition C. Limiting Condition for Operability (LCO) 3.7.5 requires three AFW trains to be Operable. Condition A of this LCO provides allowance for one steam supply to the turbine driven AFW to be inoperable for a 7 day period. If the inoperable SGAUV138A valve is not restored to an operable condition within 7 days, Unit 2 will be required to shutdown to Mode 3 in 6 hours and to Mode 4 in 12 hours, starting at 10:41 MST on April 10, 2006. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified and is present in the control room." | 0 | 88 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-04-10
42486 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-04-10 10:55 | 2006-04-10 14:24 | 2006-04-10 | PERSONNEL AIR LOCK DOOR EQUALIZING VALVE LEAKING BY "It was reported to the Shift Manager this morning in Condition Report 200601444 that the inner Personnel Air Lock (PAL) door equalizing valve was leaking by. Although the condition was reported this morning, it was actually discovered following a containment entry on Friday, April 7, 2006. Fort Calhoun Station Technical Specification 2.6(1)b,(ii) states that with the PAL inoperable, except as the result of an inoperable air lock door, maintain at least one air lock door closed; restore the inoperable air lock to operable status within 24 hours or be in at least hot shutdown within the next six hours and in cold shutdown within the following thirty hours. The leak by past the inner air lock door is applicable to this Fort Calhoun Station Technical Specification. The Shift Manager determined at 10:00 CDT that Fort Calhoun was in excess of the Limiting Conditions for Operation of Technical Specification 2.6(1)b(ii) and entered Technical Specification 2.0.1 (Motherhood) which requires the unit to be placed in at least hot shutdown within six hours, in at least subcritical and less than 300°F within the next six hours, and at least cold shutdown within the following thirty hours, unless corrective measures are completed that permit operation under the permissible action requirements for the specified time interval as measured from initial discovery or until the reactor is placed in an operating mode in which the specification is not applicable. "At 10:55 CDT on April 10, 2006, a shutdown was commenced and negative reactivity was introduced to the core. At the same time, machinists were dispatched to troubleshoot the situation and found a loose collar on the valve assembly that was preventing full closure of the valve. The collar was adjusted and post-maintenance testing was completed. The inner PAL door equalizing valve was declared operable at 13:10 CDT. Technical Specifications 2.0.1 and 2.6(1)b(ii) were exited, the unit shutdown was ceased at a power level of 96.04% and preparations are being made to return the unit to full power." The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-04-10
42485 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2005-12-31 | 2006-04-10 13:54 | 2006-04-10 | LOSS OF GENERAL LICENSED MATERIAL DUE TO IMPROPER DISPOSAL DURING CONSTRUCTION "My name is Gary Williams with the Department of Veterans Affairs, National Health Physics Program [NHPP]. I am calling to report a loss of radioactive materials. "The loss occurred at a medical permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-2385301VA. The permittee is the Clement J. Zablocki VA Medical Center, Milwaukee, Wisconsin. "The loss occurred in 2005 and was discovered in April 2006. The basis for the report is under 10 CFR 31.5(c)(10) in that radioactive materials obtained under a general license were lost and the reporting requirements in 10 CFR 20.2201 must be followed. "Specifically, the permittee stated one tritium exit sign was apparently disposed or discarded during a facility construction project in 2005. The sign was last seen in 2004. "The sign was either of two models. The first model is a 11.5 Curie sign from Shield Source Incorporated. The second model is a 20 Curie sign from SRB Technology. These types of signs were manufactured circa 1994. "The Department of Veterans Affairs will evaluate the circumstances related to the loss of radioactive materials and submit a written report to NRC, Region III, within 30 days." HOO NOTE: The Department of Veterans Affairs coordinates all reports to the NRC from their NHPP Director's Office located in Little Rock, AR. NRC oversight for the VA Master Materials licensee is assigned to NRC Region III. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-04-10
42484 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2006-04-08 23:42 | 2006-04-09 02:37 | 2006-04-09 | CONTROL ELEMENT ASSEMBLY STUCK DURING PHYSICS TESTING "During the performance of PSTP-2, Low Power Physics Testing on U-1 for Regulating Control Element Assemblies Group 2, CEA #21 was declared untrippable, Technical Specification 3.1.4.F, CEA Alignment, was entered and Plant shutdown to Mode 3 was commenced at 2342 on 4/8/06." The reactor is shutdown in Mode 3. The licensee borated to maintain adequate shutdown margin. The reactor trip breakers were opened but CEA #21 remains not fully inserted into the core. The licensee is currently troubleshooting to determine the cause of the stuck CEA. Offsite power is stable and powers the safety buses. Emergency Diesel Generators are available. The licensee is currently at normal operating pressure and temperature with decay heat being removed by the steam generators steaming to the condenser. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-04-09
42483 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2006-04-07 22:31 | 2006-04-08 01:11 | 2006-04-08 | GROUP STEP COUNTER FAILURE DURING REACTOR STARTUP "While in Mode 3 at 547 degrees and 2235 psig in the Reactor Coolant System, during Rod Control System rod drop testing, the group 2, 'A' shutdown bank step counter failed. The step counter is required to be operable in Modes 3, 4 and 5 per [Technical Requirements Manual requirement] 3.1.3 or the reactor trip breakers must be opened within 15 minutes. The step counter failed at 2217 and at 2231 the reactor trip breakers were opened. This was considered a valid actuation of the [Reactor Protection System] due to the [Technical Requirements Manual] requirements and due to the equipment malfunction." Shutdown margin is adequate and all emergency buses are on offsite power. Emergency Diesel Generators are available. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-04-08
42482 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-04-07 17:07 | 2006-04-07 17:07 | 2006-04-12 | LOSS OF OFFSITE COMMUNICATION CAPABILITY - PLANNED MAINTENANCE ON SPDS AND ERDS SYSTEMS "The Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were removed from service for planned Preventive Maintenance on the Uninterruptible Power Supply (UPS) system. SPDS and ERDS are scheduled to be restored on 4/9/2006. During this period any out of service indication on the SPDS can be obtained from control board indications. The Emergency Notification System will remain operable. These conditions are reportable in accordance with 10CFR50.72(b)(3)(xiii). The NRC Resident Inspector has been notified. The Reactor is currently defueled while in a refuel outage. Reactor Coolant Temperature is 87 degrees and Div 2 RHR is in shutdown cooling." The licensee maintains secondary indication capability via control panel indicators. * * * UPDATE FROM KEVIN DAHM TO HUFFMAN AT 1152 EDT ON 4/12/06 * * * SPDS and ERDS are now fully functional and have been returned to service as of 1130 EDT on 4/12/06. The licensee will notify the NRC Resident Inspector. R3DO (Phillips) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-04-07
42481 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2006-04-06 10:39 | 2006-04-06 14:44 | 2006-04-06 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE At 10:39 AM on 4/6/06, Unit 2 HPCI was declared inoperable due to circuit breaker 16 failure on the ESS bus. Circuit breaker 16 opened as a result of temporarily shorting the power supply lead while installing a new HPCI temperature recorder. Trouble shooting is in progress as a result of the failure and restoration will follow. Since circuit breaker 16 provides ESS power to HPCI flow controller, HPCI was declared inoperable. This event is reportable under 10CFR 5.72(b)(3)(v)(D). The licensee notified the NRC Resident Inspector. | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-04-06
42480 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2006-03-09 23:00 | 2006-04-06 09:21 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * FITNESS FOR DUTY REPORT INVOLVING LICENSEE SUPERVISOR The licensee reports that a facility supervisor has been found to be in violation of the fitness for duty program procedure (NFS-HR-08-001A) due to failure to adhere to a 5 hour alcohol abstinence requirement before reporting to the site The individual's site access has been denied. The licensee notified the NRC Resident Inspector. Contact the HOO for additional details. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.73 |  |  |  | 0 | 2008-05-11
42479 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2006-04-05 18:55 | 2006-04-05 21:23 | 2006-06-01 | ABNORMAL OPERATING PROCEDURE (AOP) FOR STATION BLACKOUT COULD NOT BE PERFORMED IN SPECIFIED TIME PERIOD "DAEC (Duane Arnold Energy Center) abnormal operating procedure AOP 301.1 for Station Blackout specifies that 30 minutes are allowed to establish alternate ventilation for RCIC (Reactor Core Isolation Cooling) /HPCI (High Pressure Coolant Injection) rooms, switchgear rooms, battery rooms, and the Main control room. During validation demonstration conducted on April 5, 2006 for the NRC Components team (from NRC Region 3 Office) the 30 minutes requirement was not met with the control room alternate ventilation taking about 60 minutes and with the other areas also exceeding their time requirements. This event is reportable as an unanalyzed condition that significantly degraded plant safety pursuant to 10 CFR 50.72(b)(3)(ii) reportability notification." The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION FROM MURRELL TO HUFFMAN AT 1442 EDT ON 6/01/06 * * * "Duane Arnold Energy Center is retracting event number 42479 which was reported to the NRC Operations Center on 4/5/06 at 1855. This event is now determined to be not reportable because further evaluation to assess the significance of the delays in establishing alternate control room ventilation determined that the delay did not result in an adverse temperature increase in the affected areas. Specifically, the control room and back panel area temperature rise was evaluated using a detailed mass and heat transfer model of the affected areas. The evaluation confirmed that delays in establishing alternate control room ventilation did not adversely impact station commitments to 10 CFR 50.63 or accident responses outlined in UFSAR Section 15.3.2. Other areas required to have alternate ventilation established within 30 minutes had previously been successfully validated. Therefore, this event is not reportable as an unanalyzed condition that significantly degraded plant safety. The analyses and the bases for this retraction can be found under the plant corrective action program." The licensee notified the NRC Resident Inspector. R3DO (Kozak) notified. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-04-05
42478 | -1 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2006-04-05 16:15 | 2006-04-05 16:43 | 2006-05-11 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE (HPCI) "During performance of a Unit 3 High Pressure Coolant Injection System (HPCI) Logic System Functional Test, the High Pressure Coolant Injection (HPCI) system was found to be inoperable. The inoperability is due to a logic failure that would prevent the automatic opening of MO-3-23-015, 'HPCI TURBINE STEAM LINE INBOARD ISOLATION VAVLE'. MO-3-23-015 is a normally open valve located inside Primary Containment. The HPCI system initiates upon receipt of a reactor low water level (level 3) signal or a high drywell pressure signal. Upon a HPCI system initiation MO-3-23-015 is required to automatically open, if closed, with no isolation signal present. The automatic opening of MO-3-23-015 is required to ensure the design function of HPCI is fulfilled. The design function of HPCI is to assure that the reactor is adequately cooled to limit fuel-clad temperature in the event of a small break in the nuclear system and loss of coolant, which does not result in rapid depressurization of the reactor vessel. HPCI permits the nuclear plant to be shut down while maintaining sufficient reactor vessel water inventory until the reactor vessel is depressurized. "The HPCI system inoperability has no immediate impact on plant operations. The inoperability places Unit 3 in a 14-day shutdown Tech Spec Action Statement. The 14-day shutdown Tech Spec Action Statement commenced on 04/05/06 @ 0824 when the Logic System Function Test was started. "A troubleshooting and repair team has been initiated to determine a cause and repair of the deficiency." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 09:10 ON 5/11/2006 FROM DAVE FOSS TO ABRAMOVITZ * * * "The purpose of this notification is to retract a previous report made on 4/5/06 at 1643 hours (EN# 42478). On 4/5/06, the High Pressure Coolant Injection (HPCI) system was removed from service and declared inoperable for the performance of a Logic System Functional Test (LSFT). During the LSFT, a condition was discovered in the open control logic circuit of the MO-3-23-015 (HPCI Turbine Steam Line Inboard Isolation Valve) that would have inhibited automatic opening of the valve on a HPCI initiation signal. Notification of this issue to the NRC on 4/5/06 was initially made as a result of the belief that the MO-3-23-015 may not have been capable of being opened for design events. It was subsequently determined that a relay contact exhibited high resistance during the LSFT. The relay was replaced on 4/6/06 (IR 475307). "Since the initial report, Engineering has performed an operability review that evaluated the impact that the relay contact high resistance condition had on the ability of the HPCI system to perform its safety function. It was determined that the relay contact degradation did not cause the HPCI system to be inoperable. The MO-3-23-015 is a normally open Primary Containment Isolation Valve. MO-3-23-015 would only isolate for conditions where HPCI would be rendered inoperable. Automatically re-opening the MO-3-23-015 valve is not a safety related function. Therefore, HPCI was capable of performing its safety function with the degraded relay contact." Notified the R1DO (Dimitriadis). The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-04-05
42477 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-02-07 22:59 | 2006-04-05 16:07 | 2006-04-05 | INVALID SYSTEM ACTUATIONS "The following 60-day report is being made under 50.73 (a)(2)(iv)(A) for an invalid actuation of Division 1 containment isolation valves that occurred at 2259 hours on February 7, 2006. As allowed by 10CFR50.73(a)(1) this notification is being made via telephone. NUREG-1022, Revision 2 identifies the information that needs to be reported as follows: "(a) The specific train(s) and system(s) that were actuated. "An unexpected actuation of Division 1 containment isolation relays occurred during performance of WO 416930-02, EM - Agastat Relay 1UAYVG514B Replacement in panel 1H13P861. Momentary, inadvertent contact occurred between the top row R1-M1 pins of the Agastat relay being inserted and the second row T1-B1 contacts of the installed relay base while the Electrical Technician was attempting to align the relay for seating, prior to applying full seating force to the relay. The relay actuations resulted in closure of Division 1 isolation valves in the Fuel Pool Cooling and Cleanup, Suppression Pool Cooling and Cleanup, Component Cooling Water, Service Air, Containment and Drywell Equipment and Floor Drains, and Makeup Condensate systems. "(b) Whether each train actuation was complete or partial. "The actuations were complete for the portions that were enabled while relay testing was in progress. "(c) Whether or not the system started and functioned successfully. "There no system starts associated with this event "The NRC Resident Inspector was notified of this notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-04-05
42476 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-04-05 12:00 | 2006-04-05 15:05 | 2006-04-05 | OFFSITE NOTIFICATION TO STATE AND LOCAL OFFICIALS CONCERNING TRITIUM DETECTION IN DRAIN SYSTEM "This notification is being made in accordance with 10CFR50.72(b)(2)(xi), i.e., notification of a government agency. FENOC provided a courtesy notification to state and local officials based on the detection of very low levels of tritium in the plant underdrain system. "During routine quarterly sampling of the Perry plant's underdrain system on March 28, 2006, very low levels of tritium were detected in an underdrain system manhole. The plant's underdrain system directs water under the plant to the Emergency Service Water Pumphouse, where it is monitored and discharged. "Samples taken off-site show no indications of detectable tritium. No reportable limits have been exceeded." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-04-05
42475 | -1 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-04-05 08:04 | 2006-04-05 14:08 | 2006-06-02 | BOTH TRAINS OF HIGH PRESSURE INJECTION (HPI) DECLARED INOPERABLE DUE TO POTENTIAL AIR BINDING OF PUMPS "TMI declared both High Pressure Injection Trains not operable due to air void in the suction line from the Sodium Hydroxide tank. The postulated issued is that in the event of a small break LOCA where the plant would need to go on HPI piggy back Ops (the Low Pressure Injection supplying suction to the High Pressure Injection pumps) the air could cause the HPI pumps to become air bound. "The Plant entered a shutdown Tech Spec 3.0.1 at 0804 [EDT] and exited the timeclock at 0850 [EDT] when the Sodium Hydroxide tank was isolated, thus isolating the air void from the ECCS (Emergency Core Cooling System) pumps." The licensee is continuing their investigation into root cause and operability. The licensee will inform the NRC Resident Inspector. * * * RETRACTION FROM A. MILLER TO P. SNYDER AT 1301 EDT ON 6/2/06 * * * "The purpose of this call is to retract the notification (Event Number 42475) made by TMI Unit 1, Docket No. 50-289 / License No. DPR-50. On April 5, 2006, at 1408 hours, the Shift Manager made a notification (Event Number 42475) to the NRC Operations Center in accordance with 10 CFR 50.72 (b)(3)(v)(D) (i.e. any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident). The event was reported as 'Both trains of High Pressure Injection (HPI) Declared Inoperable due to potential air binding of Pumps.' "On April 5, 2006, air voids were found in the NaOH tank piping, upstream of the HPI pumps, and the Shift Manager conservatively declared both trains of HPI inoperable due to the air voids. This placed TMI-1 in a 1-hour shutdown Limiting Condition for Operation (LCO). The isolation valves for the NaOH tank line piping were then Closed to eliminate the possibility that the voids could be transported to the HPI pumps. The HPI pumps were then declared operable and TMI-1 entered a 72-hour shutdown LCO. During the 72-hour LCO, the air bubble was vented from the system. An initial extent of condition evaluation was completed and an event response team was established. "Numerical Applications, Inc. (NAI) was retained to perform GOTHIC Model run on the two phase flow conditions and determine the percent air density of the water at the suction to the Low Pressure Injection (LPI) pumps and the HPI pumps. The NAI analysis concluded that the densities of air found at the suction of the LPI and HPI pumps were below the safe operating level as stated by the pump manufacturers. Based on the results of the evaluation, TMI-1 has determined that the LPI and HPI pumps were operable. Past operability of these pumps with the maximum size air bubble found is affirmed. Therefore, this event does not meet the 10 CFR 50.72 or 10 CFR 50.73 reporting criteria and the notification for Event Number 42475 is retracted. The resident inspector has been notified." Notified R1DO (T. Jackson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-04-05
42474 | 0 | COMMUNITY HOSPITALS OF INDIANA |  |  |  |  | 2005-11-08 | 2006-04-05 13:31 | 2006-04-06 | NOTIFICATION OF A MEDICAL EVENT - DOSE TO INCORRECT AREA OF BODY Community Hospitals of Indiana reported that a high dose rate (HDR) remote afterloader treatment field was incorrectly performed. On November 8, 2005, Community Hospital East in Indianapolis, Indiana performed a HDR treatment on a terminally ill lung cancer patient. Community Hospital East applied the correct dose to the patient. However, a catheter used to carry the source into the patients body was inserted into the patients airway without a cap on the end. As a result of the cap not being in its proper place on the catheter, the source was placed approximately 7 mm higher than originally intended per the physicians written directive. As a result, the field which was irradiated was greater by approximately 7 mm. Immediately following the treatment, the error was noted and the physician was informed. The physician noted that the area which was irradiated was within her area of concern and that everything was "o.k." This treatment was conducted to relieve patient symptoms rather than cure the disease. The patient succumbed to the disease approximately two weeks later. The treatment and its results were documented by the licensee in its Radiation Safety Committee Meeting minutes. During a routine inspection of its records on 4/4/06, a Region III NRC Inspector noted that this event appeared to be a medical event and should be reported. As a result of that guidance, the licensee is reporting the event. * * * UPDATE FROM K STEFFEN TO J. KNOKE AT 1610 ON 04/06/06 * * * The licensee provided the doses for the above event. Due to the catheter cap not being in its proper place the airway area above the lung received an actual dose 500 rads, whereas the prescribed dose was to be 200 rads. The area of treatment in the lung received an actual dose 200 rads, whereas the prescribed dose was to be 500 rads. Notified R3DO (Anne-Marie Stone) and NMSS (Greg Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2006-04-05
42473 | 0 | MICHIGAN TECHNOLOGICAL UNIVERSITY |  |  |  |  | 2006-03-16 | 2006-04-05 11:30 | 2006-04-05 | LOST LICENSED MATERIAL In 1967 the Michigan Technological University Physics Department obtained 10 Uranium fuel plates. The plates had a triangular shaped tip on the end that measured about 1 inch at the base, 1 inch high and was 0.1 inch thick. On one of the fuel plates, the tip broke off and the Department's RSO maintained the piece in an envelope in the same locked container where he kept the fuel plates. In 1977 during the course of routine laboratory nuclear training work with the fuel plates, one of the students wanted to look at the structure of the piece microscopically for a course in Metallurgy. The RSO gave the student the tip in an envelope sandwiched between 2 copper sheets. The student returned the piece in the envelope, and the envelope was returned to the safe unopened. On March 16, 2006, the envelope was opened to obtain data on the piece for return to Federal control, and the piece was not in the envelope. Further investigation determined that the tip was too large to be used in the Scanning Electron Microscope (SEM), and a small piece of the tip was removed. It appears that only this small piece was returned to the RSO. Personnel from the Metallurgy laboratory were questioned and it appears that the tip remained in the Metallurgy facility until after 1991 when it is thought that it was disposed of in the regular trash. The uranium fuel plates were 20 weight percent enriched Uranium. The tip contained approximately 1.1 grams enriched uranium or 0.21 gm U-235. It had an activity of 0.3 micro curies U-238 and 0.4 micro curies U-235. On contact measurements for the tip are expected to be less than 1 milli rem per hour on contact. On March 30, 2006, the Director, Occupational Health and Safety conducted a thorough search and survey of the Metallurgy laboratory and could not find the tip. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-04-05
42472 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-04-05 06:35 | 2006-04-05 11:45 | 2006-04-05 | FITNESS FOR DUTY - CONFIRMED POSITIVE FOR NON-LICENSED CONTRACTOR SUPERVISOR A non-licensed contract supervisor had a confirmed positive for alcohol while attempting to gain access the plant this morning. The contractor's access to the plant has been suspended. A review of previous work is being performed. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2006-04-05
42471 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-04-05 00:16 | 2006-04-05 02:22 | 2006-04-05 | REACTOR SCRAM FOLLOWING MAIN TURBINE CONTROL VALVE FAST CLOSURE "Two I & C technicians were performing a 24 month calibration on 2S32R017, Megavar & Voltmeter Recorder in accordance with 57CP-CAL-010-2, Esterline Angus Megavar & KV Recorder. This activity was being performed on Work Order 2042825001. At the approximate time the recorder was being removed from service the shift received a RPS trip from a MTCV [Main Turbine Control Valve] Fast Closure. The control valve fast closure scram was caused by a power load imbalance. Both RFP's [Reactor Feed Pumps] tripped on high reactor water level and RCIC and HPCI were used (for 7 and 2 minutes respectively) to control RWL [Reactor Water Level]. Eight SRV's [Safety Relief Valves] opened momentarily on high reactor pressure. The highest reactor pressure indicated was 1120 psig and the lowest RWL indicated was +7 inches. A main condenser vacuum transient due to loss of seals required use of HPCI and RCIC." The licensee characterized the scram as uncomplicated. All systems functioned as required and nothing unusual or not understood besides what caused the initial power load unbalance signal and resulting MTCV fast closure. All rods fully inserted. The unit is currently at normal pressure and water level for Mode 3. MSIVs remained opened and decay heat is being discharged to the main condenser. The scram had no impact on Unit 1. Offsite on onsite electrical conditions remained normal. The licensee was not in any significant LCO at the time of the event. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) |  |  | 0 | 2006-04-05
42470 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-03-17 | 2006-04-04 17:08 | 2006-04-05 | AGREEMENT STATE REPORT INVOLVING THE POSSIBLE LOSS OF A TROXLER MOISTURE DENSITY GAUGE At 1430 PDT on 4/4/06, the CA Rad Control Program Office was notified by Global Geo Engineering, Inc. that one of their Troxler Moisture Density Gauges, a Model 3430 - S/N 32401 containing 8 mCi Cs-137 and 40 mCi Am-241/Be, was missing and could not be accounted for. The last known log out occurred on 3/17/06 when the gauge had been used by a temporary worker at a jobsite. The licensee, unable to locate the temporary worker for a work assignment, reported the gauge as missing to both the State of CA and their local police department. CA will conduct an investigation into the circumstances involving this incident. * * * UPDATE ON 04/05/06 AT 1548 EDT FROM DONELLE KRAJEWSKI, STATE OF CALIFORNIA, TO MACKINNON * * * Gauge was returned to licensee today, 04/05/06. The temporary worker had the gauge in his possession. R4DO (Linda Smith) and NMSS (Greg Morell). E-mailed to Mexico and ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-04-07
42469 | 0 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2005-01-17 12:00 | 2006-04-03 12:56 | 2006-04-04 | MEDICAL EVENT INVOLVING DELIVERED DOSE LESS THAN THE PRESCRIBED DOSE During a review of patient's records, the licensee identified a patient who received a delivered dose of 6,885 Centigray vice the prescribed dose of 8,196 Centigray using an ovoid applicator. The incident occurred on 1/17/05 and was discovered following a similar incident reported on 03/30/06 (see EN #42453). Both the referring physician and patient have been informed. There is indication or requirement for additional treatment at this time. The licensee discussed this incident with R3 (Gattone). * * * UPDATE AT 11:44 ON 4/4/2006 FROM JEFF MASON TO ABRAMOVITZ * * * The doses are being revised by the System RSO as: prescribed: 2500 centigray actual dose: 1203 centigray Notified NMSS (Morell) and the R3DO (Stone). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-04-03
42468 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2006-04-02 20:54 | 2006-04-03 03:56 | 2006-04-03 | EMERGENCY DIESEL TRIP DURING TESTING "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On April 2, 2006 at approximately 20:54 Mountain Standard Time, Palo Verde Nuclear Generating Station Unit 3 experienced a valid Loss of Power (LOP) actuation on the Train 'B' 4.16 kV safety bus. The event occurred due to personnel error during performance of surveillance test 73ST-9DG02 (Class 1 E Diesel Generator and Integrated Safeguards Test Train B). EDG 'B' had been started In Emergency Mode per the surveillance test by opening the normal supply breaker to the associated 4.16 kV bus and initiating simulated Safety Injection Actuation System (SIAS) and Containment Isolation Actuation System (CIAS) signals. A subsequent portion of the surveillance test was in progress which demonstrates that the EDG 'test mode' trips are bypassed with the EDG operating in Emergency Mode. The step being performed was intended to simulate an Overcurrent (test mode) trip by installing a jumper at the Overcurrent relay. However the jumper was inadvertently installed at the Differential Current relay, which generated an 'Emergency Mode' trip of EDG 'B'. This resulted in the deenergization of the 4.16 kV bus. The operations staff entered Abnormal Operating Procedure (AOP) 40AO-9ZZ12 (Degraded Electrical) and reset EDG 'B'. Upon reset at approximately 21:26 MST, EDG 'B' automatically started in response to a valid Loss of Power (LOP) signal from the deenergized 4.16 kV bus. The EDG 'B' output breaker automatically closed to restore power to the Train 'B' 4.16 kV and equipment sequenced onto the 4.16 kV bus. "Due to the loss of power on the Train 'B' 4.16 kV bus, the Train 'B' Control Room Essential Filtration System (CREFS) and Control Room Emergency Air Temperature Control System (CREATCS) were rendered inoperable and LCOs 3.7.11 Condition 'A' and 3.7.12 Condition 'A' were entered. Operability of Train 'B' CREFS and CREATCS was restored when the Train 'B' 4.16 kV bus was reenergized and these LCO Conditions were exited. "Offsite power remained available to the Train 'A' 4.16 kV bus and EDG 'A' remained operable throughout the event. Shutdown Cooling was unaffected since it was being provided by the Train 'A' safety train, which was supplied by offsite power. The offsite electrical grid is stable. "Palo Verde Unit 3 Is shutdown and in Mode 5 for its 12th refueling outage. No other ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified of the ESF actuation and this ENS notification." The site performed a work stand down to discuss this event and prevent recurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-04-03
42467 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-04-02 14:02 | 2006-04-02 15:46 | 2006-04-02 | AUTOMATIC REACTOR TRIP DUE TO A MAIN GENERATOR TRIP "At 1402 Beaver Valley Unit 2 experienced a reactor trip due to a Main Generator trip. Unit 2 was operating at 100% power at the time of the trip [control rods inserted fully]. All systems functioned as expected. Emergency busses [are] being supplied by offsite power. Auxiliary Feedwater started as expected. Both Emergency Diesel Generators started on momentary undervoltage and remained operating unloaded. "The Control Room Crew entered Emergency Operating procedure E-0, 'Response to Reactor Trip and Safety Injection' and have transitioned as expected to ES-0.1 'Reactor Trip Response.' The plant is stable in Mode 3 with steam generator levels and Reactor Coolant System temperature restored to normal values with Auxiliary Feed System operation. "The cause of the Generator / Reactor trip is being investigated. "No radiological releases ongoing or caused by this event. "Beaver Valley Unit 1 is in Mode 5 for a Steam Generator Replacement outage and was unaffected." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-04-02
42466 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-04-02 14:04 | 2006-04-02 15:21 | 2006-04-02 | UNUSUAL EVENT DECLARED DUE TO ADVERSE WEATHER CONDITIONS An Unusual Event was declared per EAL 7.1.4 at 1404 CDT due to strong winds exceeding 74 mph onsite for 5 minutes between 1355-1400 CDT (peak windspeed measured at 83 mph). The Unit remained at 100% power during the incident. Current plant conditions are stable with windspeed approximately 30 mph. Offsite power is stable with a surveillance of the #1 EDG in progress. After completion of walkdowns the licensee will assess exiting the Unusual Event. A preliminary damage report indicated loose guy wire(s) on the met tower. The licensee informed state/local agencies and the NRC Resident Inspector who is onsite. * * * UPDATE AT 1621 EDT ON 04/02/06 FROM GENE MACE TO S. SANDIN * * * The licensee terminated the Unusual Event at 1500 CDT based on current sustained windspeeds less than 74 mph and passage of the storm front. The licensee is continuing their damage assessment walkdowns. The licensee informed state/local agencies and the NRC Resident Inspector. Notified R4DO (Powers), EO (Gillespie), IRD (Wilson), DHS (Mitchell), and FEMA (Mick Roland). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-04-02
42465 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-04-01 00:39 | 2006-04-01 02:45 | 2006-04-01 | EXCESSIVE CHECK VALVE LEAKAGE AT A CONTAINMENT PENETRATION "At 0039 hours on 4/01/2006, Fermi 2 feed water line check valves, B2100-F010A and B2100-F076A, failed their LLRT test. The leakage rate of the inboard check valve B2100-F010A was 324.21 SCFH and the leakage rate of the outboard check valve, B2100-F076A was above the measurement capability of the leak rate monitor. The combined penetration (X-9A) leakage value was thus 324.21 SCFH which is greater than the allowable containment leakage rate (La) value of 296.3 SCFH per Tech Spec 5.5.12." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-04-01
42464 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2006-03-31 16:00 | 2006-04-01 00:12 | 2006-04-01 | AGREEMENT STATE REPORT: DAMAGED TROXLER A Troxler moisture density gauge was left unattended at a site in Clinton, Maryland and was run over by a bulldozer. The Troxler was broken in two parts. No external contamination was detected and the source was in the shielded position. Troxler Model 3430, serial #23881. Sources: 8 milliCurie Cs-137 40 milliCurie Am-241:Be | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2006-04-05
42463 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2006-03-31 22:20 | 2006-03-31 22:36 | 2006-03-31 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE AFW TURBINE During post maintenance testing of the Auxiliary Feedwater Terry Turbine driven pump, pump problems were discovered related to the turbine governor and pump bearings. The turbine driven pump is inoperable and can not be made operable within the Technical Specification LCO Action time limit of 72 hours. The unit will be commencing a reactor shutdown to Mode 4 and perform maintenance to correct the problems. The licensee notified the NRC Resident Inspector, the Connecticut Department of Environmental Protection, and the Local Waterford Dispatch. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-03-31
42462 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-03-29 12:15 | 2006-03-31 20:14 | 2006-04-03 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO HPSI INOPERABILITY "On 3/29/06 at 1215, the left train High Pressure Safety Injection [HPSI] Pump P-66B subcooling valve CV-3070 was declared inoperable due to valve failing to stroke. Technical Specification Limiting Condition for Operation 3.5.2 ECCS - Operating, Required Action B.1 requires HPSI train to be restored to operable status within 72 hours. This required action expires on 04/01/06 at 1215. It has been determined that it will not be possible to restore operability prior to the expiration of this action statement. "A Technical Specification required shutdown to Primary Coolant system temperature < 325 degrees F will be initiated on March 31, 2006 at 2100. The site will then commence a planned refueling outage that was scheduled to begin on April 01, 2006." The licensee notified the NRC Resident Inspector. * * * * UPDATE from Dan Malone to MacKinnon on 04/03/06 at 1451 EDT * * * * Event date changed from 03/28/06 to 03/29/06. NRC Resident Inspector notified by licensee. R3DO (Anne Marie Stone) notified. | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-03-31
42461 | 0 | WHITING CORPORATION |  |  |  |  | 2006-03-30 | 2006-03-31 17:56 | 2006-04-03 | PART 21 - CRANE OVERSTRESS CONDITIONS The following is a summary of information provided by the manufacturer via email: On March 30, 2006, as part of a crane design analyses and study, Whiting Corporation identified two overstress conditions. One is on the Girder End connection of a low head room bridge and one on a single fastener in a main hoist gear case application. It is recommended that the affected cranes at the facilities listed below be restricted to 50% capacity for the over stressed end connection and 50% or 85 % capacity for the suspected over-stressed bolt until such time as the fastener or end connection can be inspected and evaluated or replaced. The following list identifies the facilities where the bridges and trolleys are suspected to be affected by the Whiting Corporation. Oyster Creek, Three Mile Island, Seabrook Oconee, McGuire, Shearon Harris, St. Lucie, Catawba D. C. Cook Cooper, Waterford, Grand Gulf, San Onofre, Palo Verde, Columbia Generating Station Whiting Corporation is attempting to contact the customers directly to notify them of this circumstance. * * * PART 21 UPDATE - CRANE OVERSTRESS CONDITIONS VIA E-MAIL ON 04/03/06 AT 1800 EDT ENTERED BY MACKINNON* * * The following is a summary update of information provided by the manufacturer via e-mail Indian Point added. R1DO (Finney), R2DO (Tom Decker), R3DO (Anne Marie Stone), R4DO (Linda Smith), NRR Part 21 (Omid Tabatabai) & NRR Part 21 (Jack Foster) notified via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21 |  |  |  | 0 | 2006-03-31
42460 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2006-02-23 09:15 | 2006-03-31 16:27 | 2006-03-31 | AGREEMENT STATE REPORT - MALFUNCTIONING RADIOGRAPHY CAMERA The State provided the following information via facsimile: "This event involved a crank cable for a Source Production & Equipment Company radiographic exposure device (model SPEC 150, serial number 876; with sealed source model SPEC G-60, serial number ML0608). The activity contained in the radiographic exposure device at the time of the incident was 2.66 terabecquerels (72 Ci). A crimped fitting on the crank cable housing came loose when a radiographer was moving the radiographic exposure device. The source was in the shielded position at all times when it was being moved. No source disconnect occurred. The cause of this incident is not known since the equipment had been functioning until this incident. The licensee believes it to be a manufacturing problem. When the incident occurred, radiographic operations were immediately stopped. And the radiography crew (radiographer, radiographer's assistant, and Radiation Safety Officer) returned to the licensee's Utah facilities. The control cable was tagged out of operation until a new housing could be obtained from the manufacturer. "The Utah Division of Radiation Control was notified by the licensee in a letter dated March 23, 2006 (received on March 29, 2006). "The licensee notified the manufacturer and the malfunctioning equipment was returned. It was immediately replaced with a new cable housing. "Event Location: Structural Steel & Plate Fabrication, 555 N. Main, North Salt Lake, Utah 84054" Utah Event Report ID No. : UT-06-0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2006-04-05
42459 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-03-31 11:50 | 2006-03-31 16:01 | 2006-03-31 | DEFECTIVE RHR CHECK VALVE "In accordance with 10 CFR 21.21(d)(1), Pacific Gas and Electric (PG&E) is hereby notifying the NRC of a defective component received from Flowserve, Flow Control Division, in Raleigh, NC, but not installed at Diablo Canyon Power Plant (DCPP). The component is an 8-inch tilting disk check valve that was procured for installation in the Residual Heat Removal (RHR) System during the Unit 2 refueling outage (2R13) scheduled to begin on 04/17/06. "On 03/02/06, the defect was identified at DCPP during post-receipt bench testing and involved incorrect disc dimensions that caused the disc to stick in the valve bonnet (i.e., in the open position). This would have prevented the valve from performing its intended safety function of closing to prevent pump-to-pump interaction when both RHR pumps are running. (These check valves were installed in response to NRC Bulletin 88-04, 'Potential Safety Related Pump Loss.') Failure of this check valve, had it been installed, could have resulted in the loss of one RHR train on Unit 2, which could impact the ability to shut down the reactor and maintain it in a safe shutdown condition. " On 03/08/06, PG&E notified Flowserve of the defect via Supplier Audit Finding Report #060670010 and requested corrective actions be taken. "On 03/13/06, Flowserve concluded that the defect was caused by disc design error and test procedure error. "On 03/16/06, Flowserve initiated Quality Problem Corrective Action Plan #169, in which they concluded a Part 21 evaluation was not required. "On 03/31/06, PG&E Vice President, Diablo Canyon Operations and Station Director, [deleted], determined that the defect met 10 CFR 21.21 reporting requirements. "PG&E initiated purchase of the 600 lb, stainless steel check valve on 06/02/05, and does not know whether any others have been manufactured by Flowserve. The valve was manufactured in accordance with Vendor Assembly Drawing W9023267 and ASME Section III, Subsection NC, 1989 Edition. "PG&E subsequently repaired the check valve in accordance with instructions provided in a Flowserve letter to PG&E, dated 03/16/06. The valve has passed inspection and bench testing and will be installed during 2R13." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 21.21 |  |  |  | 0 | 2006-03-31
42458 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2006-03-31 12:30 | 2006-03-31 15:19 | 2007-03-13 | OFFSITE NOTIFICATION TO THE FBI DUE TO POTENTIAL ACT OF VANDALISM "This notification is to inform the NRCOC [NRC Operations Center] that FPL Security contacted the local Homestead FBI agent at 12:30, and the agent is currently on site to assist in the investigation of the Potential Act of VANDALISM that was reported earlier at 1009 on 3/31/06." The Licensee will notify the NCR Resident Inspector. This event notification is related to EN 42456. * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC INTERNAL WEBSITE* * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 1 | 2006-03-31
42457 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-03-31 13:07 | 2006-03-31 14:07 | 2006-03-31 | LOW TRITIUM CONCENTRATION LEVELS FOUND NEAR UNDERGROUND PIPING "Followup information to the February 15, 2006, notification (ENS #42339 [at Braidwood]) involving the discovery of elevated levels of tritium in several vacuum breaker vaults located along the discharge piping to the Rock River. At that time we indicated we planned to install monitoring wells along this pipeline to determine if tritium has migrated from these vaults. "Fifteen shallow test wells and eight deeper, more permanent wells were drilled on company property to obtain water samples. Of the 23 wells, two had measurable levels of tritium, however they were well below the Environmental Protection Agency's standard for drinking water (20,000 picocuries per liter). "These elevated levels pose no health or safety hazard to the employees or public. Investigation into the source of the elevated tritium levels continues. "A press release is planned for the afternoon of March 31, 2006 regarding the results obtained from these monitoring wells." Incident reported according to 10 CFR 50.72 (c)(2) and the licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2006-03-31
42456 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2006-03-31 09:10 | 2006-03-31 10:09 | 2007-03-13 | SUSPECTED SABOTAGE TO PLANT EQUIPMENT Discovered suspected sabotage to plant piping system. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC INTERNAL WEBSITE* * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-03-31
42455 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2006-03-30 21:00 | 2006-03-31 02:26 | 2006-05-08 | FEEDWATER CHECK VALVE LEAKAGE ABOVE ALLOWABLE LIMITS "At 21:00 hours on 3/30/06, Unit Two feed water header check valves 2-0220-58A and 2-0220-62A LLRT [local leak rate test] results were both indeterminate, as a result both were greater than the allowable La containment leakage rate allowed by Tech Spec 5.5.12." La is defined as the maximum allowable leak rate at a specified pressure. "This is reportable under 10CFR50.72(b)(3)(ii)." The "indeterminate" leak rate was higher than the test equipment could read. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1635 EDT ON 5/8/06 FROM JIM STORTZ TO S. SANDIN * * * The licensee is retracting this report based on the following: "ENS Retraction - Feed Water Header Check Valve Leakage > La Containment Leakage "The purpose of this notification is to retract the ENS report made on 3/31/2006 at 0226 EDT (Event # 42455). The initial report was made when it appeared the Unit 2 feed water header check valves 2-0220-58A and 2-0220-62A LLRT (local leak rate test) results were both indeterminate. As a result, both valves appeared to have had a leakage rate greater than the allowable La containment leakage rate allowed by Tech Spec 5.5.12, where La is defined as the maximum allowable primary containment leak rate at accident pressure. Quad Cities assigned all leakage experienced during this test to the primary containment isolation valves being tested and reported the situation as a condition that seriously degraded the nuclear power plant per 10CFR50.72(b)(3)(ii)(A). "Subsequently, Quad Cities Station performed testing on 4/2/06 utilizing a higher fill rate test methodology. The subsequent test was completed with satisfactory results. "Based on this subsequent testing, ENS report (# 42455) is being retracted." The licensee informed the NRC Resident Inspector. Notified R3DO (Pelke). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-03-31
42454 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-03-30 16:50 | 2006-03-30 21:40 | 2006-05-22 | INADEQUATE OPERATOR RESPONSE TIME FOR COMPONENT COOLING WATER SYSTEM REALIGNMENT DURING A LARGE BREAK LOCA "At 1650 on March 30, 2006, a concern was identified where the operators in the training simulator could not complete realignment of the component cooling water (CCW) flow to the residual heat removal (RHR) heat exchanger in a timely manner under certain accident scenarios. This could result in exceeding the maximum design temperature of the CCW system. In addition, assumptions made in the containment pressure and temperature analysis following a large break loss of coolant accident (LOCA) are non-conservative with respect to when CCW flow to the RHR heat exchangers is manually established in accordance with emergency operating procedures. "Callaway plant FSAR indicates CCW system flow is manually aligned to the RHR heat exchangers prior to the recirculation phase of emergency core cooling system (ECCS). If the automatic transfer of the RHR pumps to cold leg recirculation, which happens at the Lo-Lo-1 level of the refueling water storage tank (RWST), occurs before CCW flow has been manually aligned to the RHR heat exchanger, containment sump water at temperatures up to 270F can be circulated through the RHR heat exchanger without CCW flow on the other side of the heat exchanger. The CCW side of the heat exchanger would contain stagnant water. This water can heat up quickly with no established flow and exceed the design rated temperature of the system. "Recent simulator scenarios of large break LOCAs have shown that the CCW alignment is not reached before the Lo-Lo-1 RWST alarm level is reached. The CCW alignment is completed as part of procedure ES-1.3, Transfer to Cold Leg Recirculation. A review of two large break LOCA scenarios completed on 3-20-06 show that it takes between 1:00 and 1:30 minutes to initiate the step to align CCW to the RHR heat exchangers and takes between 3:00 and 4:30 minutes to complete the alignment. "In addition to CCW system temperature concerns, an assumption that CCW flow is established to the RHR heat exchanger prior to reaching the Lo-Lo-1 level in the RWST is made in the containment temperature and pressure response analyses. As a result, a failure to establish CCW flow to the RHR switchover would result in an adverse impact on the inputs used in the Licensing Bases Containment Analysis. However, preliminary sensitivity runs using containment analyses codes indicate that post-peak temperature and pressure are not significantly affected by this issue. "Actions taken: "1650 Declared both trains of CCW inoperable. Declared both trains of ECCS inoperable and entered Technical Specification 3.0.3 "1710 Both trains of CCW aligned with flow through the RHR heat exchangers "1711 Exited Technical Specification 3.0.3 " The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY GREG BRADLEY TO JEFF ROTTON AT 1747 EDT ON 05/22/06 * * * "The purpose of this notification is to retract a previous notification made on 3/30/06 (EN# 42454). That report was made per 50.72(b)(3)(v)(D) - Accident Mitigation. An engineering evaluation has determined the RHR and CCW systems would have fulfilled their safety functions had they been necessary to respond to an event. Since the safety functions would have been performed there are no applicable reporting criteria under 50.72 or 50.73 and Event Notification 42454 is retracted. "The NRC Resident Inspector will be notified." Notified R4DO (Shaffer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-03-30
42453 | 0 | INDIANA UNIVERSITY MEDICAL CENTER |  |  |  |  | 2006-03-29 15:30 | 2006-03-30 11:41 | 2006-03-30 | DIFFERENT LENGTH BUCKET AND APPLICATOR USED DURING BRACHYTHERAPY DOSE Following a vaginal/cervical/uterine brachytherapy dose it was noted during a side by side comparison that a different length bucket and applicator were used. Because the applicator was shorter than the bucket, the applicator did not reach the end of the bucket during administration of the dose. Review of the x-ray taken to confirm placement during the exam showed that the dose distribution given to the patient was different than originally intended. It is estimated that the dose varied by greater than 20 percent. The dose was lower than the intended dose. The prescribing physician did not note any apparent ill effects to the patient during a follow-up physical examination. The event occurred because the licensee did not do a direct physical comparison of the bucket and applicator prior the exam. The licensee sorted all applicators and buckets following the event to create matched sets. The licensee is considering modifying procedures to include physical comparison of the applicator and bucket in the future. The oncology physician was to inform the patient of the differing dose. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-03-30
42452 | 0 | WISCONSIN DEPT OF HEALTH |  |  |  |  | 2006-03-29 | 2006-03-29 11:46 | 2006-03-29 | AGREEMENT STATE REPORT OF A POSSIBLE RELEASE OF F-18 FDG (FLUORO-2-DEOXYGLUCOSE) The following is a summary of the report received from the Wisconsin Department of Health and Family Services via e-mail: "On March 27, 2006 a vial containing approximately 2.77 Ci of F-18 FDG was not received at the drawing station after the synthesis had been completed. Licensee stated that the monitoring equipment indicated the synthesis had been completed and the F-18 had been delivered to the drawing station. The radiopharmaceutical synthesizers are located in a shielded mini-cell. The mini-cell door was opened to investigate and the delivery line was observed to be disconnected. The mini-cell was then closed and operations were discontinued until the next day allowing for decay. The half-life of F-18 FDG is 1.82 hrs. Radiation and contamination surveys were performed outside the closed mini-cells and surrounding areas. No contamination was found. "On March 28, 2006 the licensee contacted DHFS by telephone to report the incident. The licensee subsequently faxed in a preliminary report to DHFS. "This will be followed up on Friday March 31, 2006 during a reactive inspection by a DHFS inspector." Wisconsin Rpt No.: 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | MAT | [5 empty] | 0 | 2006-03-29
42451 | -1 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2006-03-29 00:01 | 2006-03-29 06:34 | 2006-05-30 | UNIT 3 SHUTDOWN DUE TO POTENTIAL SAFETY INJECTION TANK GASKET ISSUE "On March 27, 2006, with Unit 2 in Mode 4 while starting up from a refueling outage, [Southern California Edison (SCE)] discovered that the gasket used to seal the manway cover for Safety Injection Tank (SIT) T-008 had become partially dislodged. The gasket is a 'flexitalic' type gasket which consists of a long section of crushable wire that is coiled and compressed between the manway cover and the safety injection tank flange. For SIT T-008, the flexitalic gasket had uncoiled and extended down into the SIT and prevented SIT outlet check valve MU040 from fully sealing in the closed position. On March 28, SCE inspected the remaining three SITs (SITs # 007, 009 and 010) and found the flexitalic gaskets degraded but intact and not interfering with other components. "When this condition was discovered at Unit 2, San Onofre Unit 3 was operating at approximately 100 percent power. Similar flexitalic gaskets are also used for the manway covers on the four SITs at Unit 3. At 0001 PST on March 29, 2006, SCE conservatively declared both trains of the emergency core cooling system at Unit 3 inoperable. This placed Unit 3 in a TS 3.0.3 shutdown action statement. Plant Operators began the required Unit 3 shutdown at about 0050 on March 29, 2006. SCE is providing this phone notification to the NRC in accordance with 10 CFR 50.72(b)(2)(i) for the initiation of any nuclear plant shutdown required by the plant's Technical Specifications." The electric grid in the area is stable and Emergency Diesel Generators are available on Unit 3. There is no maintenance being performed on systems required for shutdown on Unit 3. The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 12:14 ON 5/30/2006 FROM L. CONKLIN TO ABRAMOVITZ * * * "On March 29, 2006, SCE reported the initiation of the shutdown to the NRC Operations Center (Event Log No. 42451). "At the time, SCE was concerned that if the gaskets were uncoiled they might have interfered with operation of the ECCS. "After completing the plant shutdown, SCE inspected and found the gaskets degraded but not extending into the SIT and its discharge piping. In addition, subsequent evaluations by the SONGS NSSS vendor Combustion Engineering (now Westinghouse) determined the degraded gaskets (even if uncoiled and interfering with SIT outlet check valve from fully closing) would not have prevented the ECCS from performing its required safety function. "Consequently, SCE was not required to declare Unit 3 ECCS inoperable and SCE is retracting the phone report to the NRC (Event Log No. 42451). SCE will submit a voluntary LER to document this condition. "At the time of this report, Unit 2 and Unit 3 are in Mode 1 at approximately 100% power. The San Onofre Resident Inspector has been notified of this event and will be provided with a copy of this report." Notified the R4DO (Spitzberg). | 0 | 0 | 50 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-03-29
42450 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2006-03-28 13:57 | 2006-03-28 17:29 | 2006-03-29 | UNUSUAL EVENT DUE TO RANGE BRUSH FIRE NEAR PLANT The licensee declared an unusual event due to a range brush fire primarily involving tumbleweeds that is several hundred yards outside of the protected area. The basis for the declaration is EAL 9.4.U.3 for a fire near the plant that threatens to reduce the level of safety. The fire currently is not threatening anything (such as offsite power lines or buildings). The plant is not in any major limiting conditions of operation (LCO). The Hanford Fire Department has responded. The criteria for termination of the UE is when the fire is extinguished. The licensee has notified State and local authorities and the NRC Resident Inspector. * * * UPDATE FROM F. SCHILL TO HUFFMAN AT 1953 EST ON 3/28/06 * * * "At 1640 PST on March 28, 2006, Columbia Generating Station exited Unusual Event status due to the Emergency Action Level condition no longer being valid. The range fire reported earlier no longer has the potential to reduce the level of safety. The range fire is under control after burning approximately 0.4 acres approximately 150 yards southeast of the protected area boundary. Two engines from the Hanford Fire Dept. responded. No offsite power sources were affected or threatened. No press release is planned." The licensee notified the NRC Resident Inspector. R4DO(Powers), NRR EO(Gillespie), IRD(Wilson), DHS(Hill), and FEMA(Liggett) notified. * * * UPDATE FROM M. HEDGES TO HUFFMAN AT 2103 EST ON 3/29/06 * * * "Event Notification 42450 has the statement 'The plant is not in any major limiting conditions of operation (LCO).' "This statement should read 'The plant is not in any major Technical Specification Action Statements due to this event.' Unrelated to the declaration of the Unusual Event, the plant had a 125 V dc battery pilot cell that was inoperable per the requirements of TS 3.8.6. Applicable TS Action Statements were entered. At the time of the NOUE, plant personnel were in the process of restoring the battery to operability. The operability of the battery was restored at 1547 on 03/28/06. The licensee will notify the NRC Resident Inspector. R4DO (Powers) notified. | 60 | 0 | 0 | 60 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | WA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-03-28
42449 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2006-03-28 12:50 | 2006-03-28 15:50 | 2006-03-28 | DISCOVERED SAFEGUARDS DEGRADATION The licensee reported a degradation in the safeguards system that allowed unauthorized individuals to have access to contraband material in the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Hot Standby | Power Operation | Power Operation | Hot Standby | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-03-28
42448 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  |  | 2006-03-27 09:30 | 2006-03-28 09:36 | 2006-04-05 | IRRADIATOR SHUTTER FAILS TO CLOSE The air-actuated shutter mechanism on one of the facility's irradiators (Neutron Products S/N T1497 with 13,500 Curies Co-60) failed to re-close. The irradiator source remained in its shield. A staff scientist entered the irradiator room and isolated the air supply to the shutter allowing the shutter to close. The scientist received less than 2 mrem during the incident. The cause of the shutter failure is being investigated. * * * UPDATED AT 1103 EDT ON 4/5/06 FROM TIMOTHY MENGERS TO S. SANDIN (via email) * * * The licensee identified two (2) additional reporting requirements, i.e., 10CFR36.83(a)(1) and 10CFR30.50(c)(1) [Preparation and Submission of Reports], and provided a chronology of the incident. Contact the Headquarters Operations Officer for additional details. Notified R1DO (Finney) and NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INOP ACCESS CTRL SYS | UNSHIELD STUCK SOURCE | [8 empty] | NON EMERGENCY | 1 | MD | MAT |  | 36.83(a)(5) | 36.83(a)(1) |  |  | 0 | 2006-03-28
42447 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-02-23 14:40 | 2006-03-24 19:10 | 2006-03-24 | AGREEMENT STATE REPORT INVOLVING LOSS AND RECOVERY OF A MOISTURE DENSITY GAUGE The following information is a summary of a report received via fax: On 2/24/06 the Texas Department of State Health Services was notified that a moisture density gauge was left in a motel room and later recovered still in its DOT shipping container. The cause of the incident is attributed to negligence on the part of the authorized user who has been subsequently terminated by the licensee. Local Police, FBI, and other States, as needed, were notified as well as San Antonio Police HazMat. There were no known personnel exposures involved. The license number, make, model and source content of the moisture density gauge were not available at the time of the report. Additional information will be submitted to NMED when available. TX Incident No. I-8310 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-03-29
42446 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-03-23 12:50 | 2006-03-23 18:20 | 2006-04-04 | 24-HOUR CONDITION OF LICENSE REPORT DUE TO THERMAL POWER POTENTIALLY EXCEEDING LICENSED LIMIT "McGuire Unit 1 and Unit 2 may have been operating greater than design thermal power limits of 3411 MW [Megawatt] by approximately 0.08% due to discovery of non-conservative thermal power calculations. Preliminary evaluation of Steam Generator Blow Down inputs into the thermal power calorimetric indicates a non-conservative error resulting in indicated total thermal power being approximately 0.08% lower than actual. Additional evaluations to confirm indicated power are ongoing. Power was reduced as soon as the on duty shift was made aware of the error and both Unit 1 and Unit 2 indicated thermal power is being limited to less than 99.85% to ensure actual reactor power remains less than 3411 MW. "This notification is being made pursuant to the McGuire Facility Operating License Condition 2.C.(1) Maximum Power Level." The licensee will inform the NRC Resident Inspector. * * * UPDATE AT 09:17 ON 4/4/2006 FROM REZA DJALI TO ABRAMOVITZ * * * "McGuire Nuclear Station is retracting event number 42446 which was reported to the NRC Operations Center on 3/23/06 at 1820. This event is now determined to be not reportable because further analyses of plant parameters, engineering margins, and actual plant power operation history indicated that neither Unit 1 nor Unit 2 exceeded 3411 megawatt thermal. The analyses and the bases for this retraction can be found under the plant corrective action program." Notified the R2DO (Bonser). The licensee notified the NRC Resident Inspector. | 99 | 99 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW | [5 empty] | 0 | 2006-03-23
42445 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2006-03-23 10:30 | 2006-03-23 10:25 | 2006-03-23 | MAINTENANCE ON ENS PHONE LINE "At approximately 1030 this morning, the ENS lines for Unit 1, Unit 2, and Technical Support Center will be unreliable and may be unavailable for maintenance on off-site telephone circuitry. The expected duration will be until 1600 on 3/23/06. Commercial telephones will still be available. The loss of the ENS communications is reportable under 10CFR 50.72 (b)(3)(xiii). St Lucie will perform a phone test following ENS restoration." Commercial phone lines to the site are still available. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM J. HESSLING TO W. GOTT AT 1603 ON 03/23/06 * * * ENS lines for Unit 1, Unit 2 and the Technical Support Center have been restored and tested. The licensee notified the NRC Resident Inspector. Notified R2DO (C. Evans) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-03-23
42444 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-03-22 16:24 | 2006-03-22 19:49 | 2006-03-22 | TURBINE TRIP / REACTOR TRIP CAUSED BY MAIN GENERATOR TRIP "This notification fulfills the 4-hr. non-emergency reporting requirement for Reactor Protection System actuation and the 8-hr. non-emergency reporting requirement for an ESF actuation (specifically Auxiliary Feedwater System start). "At 1624 EST, Unit 2 reactor tripped from full power due to main generator trip caused by actuation of the main generator neutral overvoltage relay (the 100% stator ground fault relay also actuated). Safety Injection did not actuate and was not required to actuate. "All automatic actions occurred as designed (e.g., steam dump operation, feedwater system, etc.). "The operating crew responded to the trip using emergency procedures. The unit is being maintained in Mode 3 (Hot Standby) using General Operating Instructions. "No primary steam or steam generator safety valves opened due to this trip. "An investigation has been initiated to determine the cause of this unit trip. A recovery plan will be developed." All control rods fully inserted on the reactor trip. Decay heat is being removed by auxiliary feedwater feeding the steam generators and steaming through the steam dump valves to the main condenser. Offsite power is stable and all emergency busses are being powered via offsite power. All Emergency Diesel Generators are available if required. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-03-22
42443 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-03-22 12:51 | 2006-03-22 18:16 | 2006-03-22 | POTENTIAL LOSS OF COMMUNICATION SIRENS "On March 22, 2006, an unscheduled poll of the North Anna sirens was initiated. During the period from 1251 to 1303 hours, actuation signals were not received at the transmitter and no outgoing signal was transmitted to the sirens. This event is a loss of the Emergency Notification System and is reportable per 10 CFR 50.72 (b)(3)(xiii). "At 1303 hours, telecommunications notified [the plant staff] that the siren system was operational. The cause of the failure is being investigated." The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling Shutdown | Power Operation |  | Refueling Shutdown | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-03-22
42442 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2006-03-22 13:00 | 2006-03-22 17:09 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * PRODUCT MASS DIFFERENT THAN ANALYZED The following was discovered In Building [DELETED] "Accumulation of product in a process vessel was discovered whose mass was different than analyzed in the Integrated Safety Analysis for a health physics related consequence." The licensee is continuing to evaluate the cause. The system involved is shut down and no other similar systems are operating. The licensee will continue to evaluate and determine the cause prior to restarting the process. This is not a criticality safety issue. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM J. WHEELER TO M. RIPLEY 1034 EDT 04/13/06 * * * "On March 22, 2006, Nuclear Fuel Services, Inc. (NFS) made a 24-hour report to the operations center based on 10CFR70, Appendix A, (b)(1). 10CFR70, Appendix A, (b)(1) requires a 24-hour report for a condition that resulted in the facility being in a state that was different from that analyzed in the Integrated Safety Analysis (ISA) and that resulted in failure to meet the performance requirements of Section 70.61. The report was made because it was discovered that product had accumulated in a process vessel whose mass was greater than that analyzed in the Integrated Safety Analysis for a health physics related consequence. "The health physics consequence evaluation assumed that the entire mass of product was respirable. Between March 24, 2006, and April 6, 2006, measurements of the actual product mass were taken, and it was determined that less than 1 percent of the mass was respirable. The actual respirable product mass was 3 percent of the amount that would result in a high health physics consequence assuming a release of material. Substitution of the actual respirable product mass into the health physics consequence evaluation resulted in a low consequence and thus performance requirements were met. Based on this information, it is requested that this event report be retracted. The licensee notified the NRC Resident Inspector. Notified R2 DO (R. Haag) and NMSS EO (G. Morell) * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-05-11
42441 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-03-22 | 2006-03-22 16:10 | 2006-03-22 | AGREEMENT STATE REPORT - RADIATION EXPOSURE The State provided the following information via email: "The Manager Health Physics, Cardinal Health called to report an incident which occurred today out of their Colton, CA pharmacy. A generator was being shipped via contract carrier from Colton to their Palm Springs pharmacy. The wrong shielding was used. Instead of a [Transportation Index] TI 1 which it was shipped as it was actually a TI 20. Upon arriving at the Palm Springs pharmacy it had a surface reading of 1,000 mr/hr. Estimate 4 hours with the driver. [The Manager Health Physics] was not aware if the driver had a personnel exposure device or what type of vehicle was utilized or the distance the generator was from the driver." CA Report Number: 032206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-03-27
42440 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2006-03-03 | 2006-03-22 16:19 | 2006-03-22 | AGREEMENT STATE REPORT - MEDICAL EVENT INVOLVING THE WRONG RADIOPHARMACEUTICAL The following information was received via facsimile: "NH Radiological Health Section 'Agency' was notified on March 7, 2006, by an e-mail from the Radiation Safety Officer (RSO) at Mary Hitchcock Memorial Hospital of the wrong radiopharmaceutical injected into a patient. [The] delay was caused by conflicting information concerning whether the dose administered exceeded the reporting threshold. Four millicuries of Tl-201 Cl [Thallium Chloride] was administered [via] IV to a patient instead of the intended Tc-99 pertechnetate. Due to the error, the administration resulted in a whole body dose of 5.2 Rem. The patient and both the Authorized User and referring physician were notified of the error and the correct radiopharmaceutical was administered. "The Licensee's RSO conducted an investigation and interviewed persons involved with the administration. A written explanation of the event was obtained. [The] cause of [the] incident was identified as inattention to labeling on part of [the] technician. Remedial instruction was given to the technician. NH Report ID No: NH-06-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2006-03-27
42439 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-03-22 09:15 | 2006-03-22 09:27 | 2006-03-22 | ON-SITE FATALITY "On March 22, 2006 at approximately 0341 hours the site medical response team responded to a notification that a Duke employee had collapsed due to personal illness in the Unit 2 Reactor Lower Containment. Unit 2 is currently shutdown in Mode 6 in a refueling outage. The site medical response team called for an ambulance to transport the individual offsite. After the ambulance arrived on site, the ambulance attendants were notified by radiation protection personnel that the individual was considered potentially contaminated because he could not be surveyed. The ambulance left the site at approximately 0459. Radiation Protection personnel accompanied the individual to the medical facility. Upon arrival at the medical facility, a complete survey of the individual was made and no radioactive contamination was found either on the individual or on his clothing. The individual did not survive the personal illness. This situation is determined to be reportable per 10 CPR 50.72 (b)(2)(xi) because this event will be reported to an offsite government agency, OSHA. At this time no press release is planned." The individual was sitting down in containment because he was not feeling well. His co-worker started up a ladder, turned, and noticed the individual was slumped over. He was pronounced dead in the ambulance when it arrived at the hospital. Containment temperature at this time was in the upper 60s. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-22
42438 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS, INC |  |  |  |  | 2006-03-21 | 2006-03-21 16:55 | 2006-03-21 | PART 21 NOTIFICATION CONCERNING ROSEMOUNT TRANSMITTERS The licensee provided the following information via facsimile: "Pursuant to 10 CFR Part 21, section 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) provided information that certain Rosemount Pressure Transmitters may not conform to RNII's published qualified life specification. The specific models affected are: "(a) Certain Model 1153 Series B and 1153 Series D pressure transmitters of all range codes and measuring types (gage, differential, absolute) shipped between 16 December 2005 and 13 January 2006, and "(b) Certain Model 1154 and 1154 Series H pressure transmitters of all range codes and measuring types (gage, differential, sealed reference) shipped between 16 December 2005 and 13 January 2006 "For every RNII Model 1153 and Model 1154 transmitter, four diodes are used on a circuit card assembly which is installed and sealed within the sensor module sub-assembly. The primary function of these diodes is to convert an AC oscillator signal to a DC current that is proportional to the capacitance of the sensor. The diodes (P/N D2911218A) are manufactured by Microsemi Corp (MSG). "Recently during standard receiving inspection, it was noted that the glass packaging on several of the diodes exhibited an unusual 'cloudy' appearance. Upon supplier analysis it was determined that the cloudy appearance was due to interaction between cleaning solution and metallic components of the diode. Cleaning solution was able to penetrate the glass diode package because of a poor hermetic seal. Over time, this condition could degrade the performance and reliability of the diode, particularly at elevated temperatures. The resultant effect on the transmitter might include degraded temperature effect performance and increased drift between calibration cycles. "Through further internal investigation MSC was able to bound the potential problem to two lot codes. These lot codes were traced from MSC through our circuit card supplier and to RNII to identify the shipped transmitters affected by this notification. "RNII built up several test transmitters using diodes having a cloudy appearance and performed thermal aging on the transmitters to simulate typical operating conditions, followed by high temperature testing. Test results suggest that potentially affected transmitters would operate within published performance specifications, including the Nuclear Steam Pressure/Temperature specification. Nonetheless, RNII and MSC were unable to demonstrate the long term reliability of the suspect diodes over the full qualified life of the transmitter. "Therefore, based on analysis of the test results, RNII has established the following qualified life limits for transmitters affected by this notification. This specification supersedes the published qualified life for all pressure transmitters affected by this notification: Interim Qualified Life = 5.1 years @ 120 F Operating Temperature "RNII does not have sufficient information relative to each end use's specific applications to determine the potential safety-related impact of this notification to each end user's plant. Each end user must determine the impact on its plant operations and plant safety and take action as deemed necessary." RNII recommends that "the end user must determine the impact of this potential non-conformance upon its plant's operation and safety, and take action as deemed necessary. RNII recommends that potentially affected transmitters be returned to RNII for replacement of the module at the end user's earliest opportunity and consistent with the abbreviated interim qualified life specification. RNII requests that the end users contact RNII to facilitate the transmitter return process as necessary." Plants which have been supplied these transmitters: Nine Mile Point; Catawba; River Bend; Quad Cities; Braidwood; Dresden; Perry; Turkey Point; Vogtle; Palisades; and Hope Creek. Rosemount is in the process of contacting the end users. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | GEN | 21.21 |  |  |  | 0 | 2006-03-21
42437 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2006-03-21 16:08 | 2006-03-21 17:20 | 2006-03-21 | DEGRADED CONDITION - INDICATION ON PRIMARY COOLANT SYSTEM PRESSURE BOUNDARY WELD "On March 18, 2006, with the Davis-Besse Nuclear Power Station in Mode 6 (Refueling), an axial indication was discovered on the Reactor Coolant Pump 1-1 Cold Leg Drain Line Nozzle to Elbow Weld. At the time of discovery, the indication was determined to be at least 0.25 inches in length, but the through-wall depth of this indication could not be determined. "Further evaluation of this indication is in progress by an offsite engineering organization. Based upon preliminary evaluation, it has been determined that this indication cannot be found acceptable under ASME Section XI. "10CFR50.72(b)(3)(ii)(A) requires reporting of any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. NUREG-1022, 'Event Reporting Guidelines - 10CFR50.72 and 10CFR50.73' lists as an example of such degradation 'Welding or material defects in the primary coolant system which cannot be found acceptable under ASME Section XI, IWB-3600, 'Analytical Evaluation of Flaws' or ASME Section XI, Table IWB-3410-1, 'Acceptance Standards.' "Based upon the preliminary evaluation by the offsite engineering organization, the axial indication is being conservatively reported per 10CFR50.72(b)(3)(ii)(A) as a serious degradation of a principle safety barrier. The plant is currently defueled, and plans are underway to determine the necessary repair [to] this indication." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-03-21
42436 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-03-21 02:29 | 2006-03-21 05:39 | 2006-03-21 | OFFSITE NOTIFICATION DUE TO INADVERTENT EMERGENCY SIREN ACTUATION "At approximately 0238 [EST], received first notification of an actuation of the Early Warning Siren System. This call came from Fairfield County 911 dispatcher after they received numerous calls from area residents. Subsequent calls were received from the State Warning Point, Lexington, Newberry and Richland County's 911 dispatcher as well as calls from the public. The Secondary Alarm Station informed the Control Room that when an attempt was made to silence one individual siren (N-86) that was in alarm, all the sirens were inadvertently actuated. Sirens appear to have alarmed for approximately three minutes and then shut off (per design). Subsequent investigation by the Emergency Preparedness group did not reveal any human error. The investigation into the siren actuation is ongoing. All sirens are operable at this time. SCANA Public Relations has been informed and will be preparing a press release, as will the SC Emergency Management Division. A local television station, WIS TV, will be interviewing SCANA Public Relations personnel at approximately 0630." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-21
42435 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-03-20 17:11 | 2006-03-20 21:36 | 2006-03-20 | OIL SPILL ONSITE "A notification was made to the Wisconsin Department of Natural Resources Spill Response Center by We Energies at 1711 hours on 03/20/06 for a small lube oil spill that occurred on 3/19/06. The spill was initially believed to be very small (less than 5 gallons) and there was no evidence of a release to Lake Michigan. Following a maintenance inspection of the water treatment deaerator vacuum pump, it was conservatively assumed that a maximum quantity of 25 gallons of oil could have been spilled. "The NRC resident inspector has been notified of this event." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-20
42434 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-03-20 13:00 | 2006-03-20 15:51 | 2006-03-20 | PLANT SHUTDOWN DUE TO RCS PRESSURE BOUNDARY LEAKAGE "At 03:56 on 03/20/2006 an intermediate radiation alarm was received on Containment Atmosphere Particulate Radiation Monitor, 2RE-2562A. A review of other containment parameters, such as containment pressure, moisture, temperature, sump levels and other containment radiation monitors were all stable. Chemistry was notified of the increasing particulate radiation levels in containment and immediately pulled the filter paper from radiation monitor 2RE-2562A. A gross count of the filter paper revealed the presence of Na-24 and Co-58. The presence of these two isotopes indicated the possibility of an active RCS leak. An RCS leakrate measurement was initiated. The results of the leakrate measurement showed no measurable change in leakrate. The total leakrate was calculated to be 0.13 gpm. "At 06:03 on 03/20/2006 a high radiation alarm was received on Containment Atmosphere Particulate Radiation Monitor, 2RE-2562A. Preparations were begun to make a containment entry to walkdown outside the bio-shield and to take a robot, equipped with a camera, to inspect inside the bio-shield. "At 13:00 personnel from the Unit 2 containment reported that a leak was visible from inside the bio-shield in the area of RCS Loop #1. Based on reports from personnel in containment, the leakage in containment was determined to be pressure boundary leakage and Tech Spec 3.4.13, "RCS Operational LEAKAGE," was entered. As required by TS 3.4.13, at 13:52 on 03/20/2006 a unit shutdown to Mode 3 was initiated to allow further investigations and repair of the leak inside containment. Abnormal Operating Procedure 18004-C, "RCS Leakage" was also entered at this time due to increasing radiation levels on, radiation monitor 2RE-2562A. Per Tech Spec 3.4.13, Mode 3 entry [is] required by no later than 19:00 on 3/20/2006 and Mode 5 entry no later than 01:00 on 3/22/2006." The Unit shutdown is currently in progress. This is the third shutdown at the Unit for a leak in this vicinity. See similar event reports #42309 dated February 3, 2006, and #42194 dated December 9, 2005. The licensee notified the NRC Resident Inspector. | 0 | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-03-20
42433 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2006-03-20 10:25 | 2006-03-20 15:01 | 2006-03-20 | FITNESS FOR DUTY - CONFIRMED POSITIVE FOR NON-LICENSED SUPERVISOR DURING RANDOM TEST "This report is being made in accordance with 10 CFR 26.73 due to a supervisor testing positive during a random fitness for duty test. The employee was fitness for duty tested on 3/16/06. The Medical Review Officer confirmed a positive test at 10:25 EST on 3/20/06. A review of previous work is being performed. The employee's access to the plant has been denied. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.73 |  |  |  | 0 | 2006-03-20
42432 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2006-03-20 09:00 | 2006-03-20 12:53 | 2006-03-20 | OFFSITE NOTIFICATION TO SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL (DHEC) OF SEWAGE SPILL The licensee reported that an onsite underground line to the sanitary sewage pond broke resulting in back drainage from the pond into the environment of an estimated 60,000 to 70,000 gallons of sewage. The pond sewage has gone into the yard drains and possibly some of the nearby creeks. The licensee provided the following information via facsimile: "Approximately 0800 received first notification of discharge from Sanitary Aeration Pond, outfall # 005. At 0825 an initial notification was made to DHEC. Temporary covers were installed over the yard drains. These covers seem to be holding the remnants of the fluid. At 0900 the control room was notified the discharge had made it to the yard drains and thus to the environment. At 1240 the estimate of discharge was revised to 60,000 to 70,000 gallons, which made this potentially newsworthy. "Suspected cause is a broken underground pipe. No impact on plant operation. "The discharge was not radioactive." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-20
42431 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-03-20 07:56 | 2006-03-20 09:18 | 2006-03-20 | UNUSUAL EVENT DECLARED DUE TO SMALL FIRE INSIDE PROTECTED AREA Fire inside the Protected Area lasting greater than 10 minutes in an electrical conduit between the Ionic trailer and the Water Treatment Building. Power to the electrical feed through the conduit to the Ionic trailer has been secured. No offsite assistance has been requested. The licensee is verifying the status of the fire after securing the power. The licensee notified the NRC Resident Inspector and the State and Local authorities. * * * UPDATE FROM ELDON PLETTNER TO JEFF ROTTON AT 0951 EST ON 03/20/06 * * * Fire was declared out at 0842 CST. Fire was in the EE transformer supplying the Ionic trailer. Fire was extinguished by opening Breaker 48D. The licensee corporate office will be issuing a press release later today. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ELDON PLETTNER TO JEFF ROTTON AT 0959 EST ON 03/20/06 * * * Licensee terminated the Unusual Event due to the fire being out and plant returned to normal operation with the exception of the Ionic trailer power. The licensee notified the NRC Resident Inspector. Notified R4DO (Clark), NRR EO (Benner), IRD Manager (McGinty), DHS (Everette) and FEMA (Liggett) | 82 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2006-03-20
42430 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-03-20 04:53 | 2006-03-20 08:28 | 2006-03-20 | MAIN TURBINE TRIP CAUSED REACTOR SCRAM "At 0453 CST on March 20, 2006, a main turbine trip occurred resulting in a reactor scram. All control rods fully inserted on the scram signal. All systems performed as expected. Reactor water level is being controlled in the normal operating band and reactor pressure is being controlled at 600 psig. "The cause of the turbine trip is under investigation. There is no indication that the turbine trip was caused by an actual parameter reaching a trip setpoint. A turbine Low Vacuum trip alarm is indicated in the Main Control Room and is the current focus of troubleshooting activities. Actual main condenser vacuum is at its normal value." The site is on off-site power, and the EDG's are available if required. All safety related systems are available if required. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-03-20
42429 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2006-03-19 12:40 | 2006-03-19 17:44 | 2006-03-23 | UNIT 2 ERDADS (EMERGENCY RESPONSE DATA ACQUISITION AND DISPLAY SYSTEM) COMPUTER DECLARED INOPERABLE. "On 3/19/06 at approximately 1240, the U2 ERDADS computer failed and stopped providing updated plant data to the Unit 2 and Technical Support Center Operator Consoles, leaving the displays essentially static. Investigation of the failure mode is ongoing and attempts to restore the ERDADS to normal are in progress. A similar event occurred on 3/16/06, EN# 42425. Loss of the ERDADS output for greater than one hour is reportable as a major loss of assessment and communication capability under 10 CFR 50.72(b)(3)(xiii)." The ERDADS computer has been restored but the licensee does not considered it fully operable. Vendor is coming in on 3/20/06 to try to correct the ERDADS computer problem. The NRC Resident Inspector was notified of this by the licensee. * * * UPDATE FROM J. HESSLING TO W. GOTT AT 1603 ON 03/23/06 * * * ERDADS system is restored. The licensee notified the NRC Resident Inspector. Notified R2DO (C. Evans) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-03-19
42428 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-02-10 11:20 | 2006-03-17 14:34 | 2006-03-17 | INVALID SPECIFIED SYSTEM ACTUATIONS "The following information is provided as a 60 day telephone notification to NRC under 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of a 10 CFR 50.73(a)(2)(iv)(B) system. NUREG1022 Revision 2 identifies the information that needs to be reported as discussed below. "(a) The specific train(s) and system(s) that were actuated: "On February 10, 2006, at 1120 EST, a surveillance was in progress to calibrate the Division 2 Fuel Pool Ventilation Exhaust Radiation Monitor D11-K611D. During jumper removal an adjacent terminal was contacted by the jumper while still connected to a 24 VDC power source resulting in a blown power supply fuse. The loss of the power supply resulted in the following automatic actions: Primary Containment Isolation Valve Group 14; Drywell and Suppression Chamber Ventilation System; and Group 16, Nitrogen Inerting System received an isolation signal. All primary containment isolation valves in both groups were previously in their safety function position (closed). "Secondary containment isolated resulting in a trip of the Reactor Building Heating and Ventilation System and Division 2 Standby Gas Treatment System automatically started. The Control Center Heating, Ventilating and Air Conditioning System automatically shifted into the Recirculation mode. The initiation signal was invalid because it did not result in response to an actual high radiation condition, nor did it trip as a result of any other requirement for initiation of the safety function, such as a downscale or inoperable trip, for example. "(b) Whether each train actuation was complete or partial. "The Division 2 Standby Gas Treatment System automatically started, secondary containment fully isolated, Reactor Building Heating and Ventilation System tripped, and the Control Center Heating, Ventilating and Air Conditioning System automatically shifted into the Recirculation mode. These were complete actuations. The primary containment isolation valves Group 14 and 16 remained in their safety function (closed) position. This was a complete actuation. "(c) Whether or not the system started and functioned successfully. "The above systems functioned successfully." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-03-17
42427 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2006-03-17 | 2006-03-17 11:16 | 2006-03-17 | MARYLAND AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE A Troxler model 3430 moisture density gauge was stolen from a locked storage trailer on a temporary jobsite on Reistertown Road in Pikesville, MD. The gauge serial number is #23191 and contained a 8 millicurie Cs-137 source and 40 millicurie Am-241 source. The Maryland State inspectors and the Baltimore City Police are on the scene to conduct their investigation. The Maryland Department of the Environment will be issuing a press release on 3/17/06. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2006-03-22
42426 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-03-17 07:58 | 2006-03-17 10:16 | 2006-03-17 | OFFSITE NOTIFICATION - LOCAL SHERIFF CONTACTED "On March 17 at approximately 0758 Central Standard Time (CST), the remains of a human body were discovered to have washed ashore immediately North of the Unit 2 circulating water discharge canal. The Manitowoc County Sheriff's Department was contacted to investigate. The body is believed to have randomly washed ashore from Lake Michigan." The county is presently on-site to pick up the human remains. The licensee notified the NRC Resident Inspector and expects to issue a press release at a later date. * * * UPDATE ON 03/17/06 AT 1458 EST FROM ERIC SCHULTZ TO MACKINNON * * * "NMC previously reported that on March 17 at approximately 0758 Central Standard Time (CST), the remains of a human body were discovered to have washed ashore immediately North of the Unit 2 circulating water discharge canal. The Manitowoc County Sheriff's Department was contacted to investigate. The body is believed to have randomly washed ashore from Lake Michigan. "The following article has subsequently appeared on the web site of the local newspaper (Herald Times Reporter). "MANITOWOC - Manitowoc County Sheriff's Department investigators responded to the area of the Point Beach Nuclear Plant before 8 a.m. today after a body washed up onto the shore of Lake Michigan there, according to Inspector (Deleted). (Deleted) said the body is that of a 46-year-old man, but said further details are not immediately available. "Sheriff (Deleted) said early indications point to suicide, adding that is still under investigation. "Department personnel were still on the scene, near the Two Creeks boat launch, as of 10 a.m. today. "The County Sheriff and Coroner removed the discovered body and left site at 1008 on 3/17/06." The NRC Resident Inspector and local officials were notified of this event by the licensee. NRC R3DO (Dave Passehl) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-17
42425 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2006-03-16 22:50 | 2006-03-17 01:30 | 2006-03-23 | LOSS OF COMMUNICATION - ERDADS COMPUTER FAILED "On 3/16/2006 at approximately 2010 [EST], the U2 ERDADS computer failed and stopped providing updated plant data to the Unit 2 and Technical Support Center operator consoles, leaving the displays essentially static. Investigation of the failure mode is ongoing and attempts to restore the ERDADS to normal are in progress. "Loss of the ERDADS output for greater than one hour is reportable as a major loss of assessment and communication capability under 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM J. HESSLING TO W. GOTT AT 1603 ON 03/23/06 * * * ERDADS system is restored. The licensee notified the NRC Resident Inspector. Notified R2DO (C. Evans) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-03-17
42424 | 0 | TEXAS A&M UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2006-02-24 | 2006-03-15 12:07 | 2006-03-15 | POTENTIAL EXTREMITY OVEREXPOSURE AT TEXAS A&M RESEARCH REACTOR PER 10CFR20.2202(b)(1)(iii) The licensee reported that an employee at the Texas A&M Nuclear Science Center received 75,800 mREM to the extremities during the month of January 2006. Furthermore, the licensee reported that the individual also received 37,540 mREM to the extremities during the month of February 2006. The licensee reported that the employee was involved in neutron activation analysis work involving contact lenses and that all ALARA procedures were strictly enforced. The licensee stated that there were no changes in general radiation areas levels or processes which would result in an unanalyzed increase in radiation levels. The licensee's investigation is on-going. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | TX | NPR |  | 20.2202(b)(1) |  |  |  | 0 | 2006-03-15
42423 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-03-15 05:57 | 2006-03-15 09:41 | 2006-03-18 | LOSS OF ASSESSMENT CAPABILITY - SAFETY PARAMETER DISPLAY SYSTEM "Unit 1 is currently in Mode 5 for the planned 14th Refuel and Inspection Outage. "At 05:57 on March 15, 2006 the Unit 1 Safety Parameter Display System (SPDS) was deenergized during planned refuel outage activities. It has been determined that it will not be restored within the required eight hours. Currently, restoration is scheduled for March 17, 2006 at 00:01. All required instrumentation is available in the control room. "ERDS will remain operable during the work window but several points will not be available. For example 23 of 58 ERDS points will be unavailable while SPDS is out of service. However, the ERDS system will still be operable and transmit the remaining points. "Loss of Emergency Assessment Capability - A review of the ability of the Emergency organization to function without SPDS was performed. Alternate sources for many of the points in SPDS were identified and are contained on an Emergency Plan format in PICSY (plant integrated computer system). Those points not available from PICSY can be obtained from the control room. With these compensatory actions and the communications in place between the facilities, there will not be a major loss of emergency assessment capability. "Since the Unit 1 SPDS computer system will be unavailable for greater than 8 hours, this is considered reportable under 10CFR50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM J. HUFFORD TO J. KNOKE AT 10:41 EST ON 03/18/06 * * * Licensee has restored the Unit 1 Safety Parameter Display System (SPDS), which was deenergized during planned refuel outage activities for scheduled maintenance. The licensee notified the NRC Resident Inspector. Notified R1DO (Krohn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-03-15
42422 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-03-14 16:59 | 2006-03-14 20:21 | 2006-04-22 | LOSS OF CONTROL ROOM EMERGENCY FILTRATION "On 03/14/06 at 1655 hours, the 'A' Control Room Emergency Filtration (CREF) system was removed from service to address a high oil level and subsequent high bearing drain oil temperatures. The 'A' CREF train was declared inoperable and a 7-day LCO was entered. While placing the 'B' CREF train in-service the chiller did not respond as expected. The chiller failed to properly load and supply cooling. At 1659 hours the 'B' CREF train was declared inoperable. This resulted in both 'A' and 'B' trains of CREF [being] unable to perform their design safety function and thus unable to mitigate the consequences of an accident. This failure placed the Hope Creek Station in a Technical Specification 3.0.3 condition requiring a unit shutdown. Oil level was restored to normal band for the 'A' CREF train at 1732 hours and the 3.0.3 condition was exited prior to any actions being initiated to start reducing reactor power to achieve a Hot Shutdown condition. "A 8 hour report is being made under ECG Section 11.2.2.b, an Event/Condition could have prevented certain safety functions IAW 10.CFR50.72(b)(3)(v). "At the time of event all safety systems were operable. The license has notified the NRC resident inspector." * * * UPDATE FROM ZAKARIAN TO HUFFMAN AT 1359 EDT ON 4/22/06 * * * "This is a retraction of the event notification made on 3/14/06 at 20:21 (ET) hours. This event (#42422) was initially reported as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident per 10CFR50.72(b)(3)(v)(D). The safety function of the system is to ensure that the ambient air temperature does not exceed the allowable temperature for continuous duty rating for the equipment and instrumentation cooled by this system. Further review has determined that the Control Room Emergency Filtration (CREF) chiller system maintained its capability to complete its specified safety function. During the event, the chilled water and affected room temperatures increased only minimally and remained well below the maximum allowable temperatures. The proceduralized in-progress activity to address the 'A' chiller high oil level condition promptly re-established full system cooling prior to approaching any required temperature limits. The procedure was completed in a timely manner with no complications. Therefore, the temperature limits of the Control Room and equipment rooms would not have been challenged had an event occurred during the time 'A' chiller oil level was being adjusted and the safety function of maintaining room ambient air temperature within limits would have been accomplished." The licensee has notified the NRC resident inspector. R1DO(Holody) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-03-14
42421 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-03-14 17:33 | 2006-03-14 18:15 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * Actual introduction of contraband into the protected area. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC INTERNAL WEBSITE* * * * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2008-05-11
42420 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-03-14 16:15 | 2006-03-14 18:08 | 2007-03-13 | PROTECTED AREA BOUNDARY VULNERABILITY Discovered vulnerability in a safeguard system that could allow access to a controlled access area. Compensatory measures have now been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC INTERNAL WEBSITE* * * | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-03-14
42419 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-03-13 | 2006-03-14 11:39 | 2006-03-14 | AGREEMENT STATE REPORT - WELL LOGGING SOURCE ABANDONED The State provided the following information via facsimile: "Baker Hughs Intec abandoned a 2.5 Ci source of Cs-137 and a 5 Ci source of Am-241 down hole on March 13, 2006. The depth of the sources is between 14,423 feet and 14,430 feet. The hole has [been] back filled with cement to a depth of 12,095 feet to prevent reentry into the hole." Louisiana license number: LA060004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-03-17
42418 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-03-05 | 2006-03-14 14:45 | 2006-03-14 | AGREEMENT STATE REPORT - PATIENT RECEIVED IMPROPER MEDICAL DOSE The State provided the following information via facsimile: "On March 5, 2006, a technician at St. Francis North Hospital contacted the Cardinal Health pharmacy to inform them that a scan on a patient had shown lung imaging instead of the expected cardiac imaging after administering a dose labeled Myoview. An investigation revealed that the customer's Tc-99m Myoview dose for cardiac imaging had mistakenly been dispensed as a Tc-99m MAA dose which is for lung imaging. "The cause of this event was a failure by the dispensing pharmacist to follow proper Cardinal Health compounding procedures. The pharmacist pulled the wrong kit from the refrigerator. The pharmacist performed a QC test on the dose, but failed to label the starting point on the QC chromatography strip, which led to a misinterpretation of the failing test as a passing test. "In order to prevent a recurrence of this event, the pharmacy is going to begin requiring all employees performing QC tests to label the starting point of all QC strips. Also, the pharmacy is planning to switch brands of MAA since the Drax MAA vial and the Myoview vials are identical in appearance." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-03-17
42417 | 0 | TRIAD ENGINEERING |  |  |  |  | 2006-03-14 08:00 | 2006-03-14 13:32 | 2006-03-14 | TROXLER MOISTURE DENSITY GAUGE FALLS FROM TRUCK As a licensee employee was leaving the office in Purcellville, VA in his truck, he was stopped at an intersection nearby by bystanders. They informed him that an object (a Troxler gauge in its case) had fallen from the open tailgate of his truck. Local police responded to the incident and contacted the fire marshal who told the officer that the device in its case was designed for that type of an impact. The gauge remained intact and no radiation exposures were reported. The Troxler moisture density gauge is a model # 3411, containing Am-241 (40 millicuries) and Cs-137 (8.7 millicuries). The employee loaded and secured the case containing the gauge and proceeded to the job site. The licensee will perform a leak test on the gauge. The licensee is holding mandatory gauge refresher training for their employees as a corrective action to this incident. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-03-14
42416 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-03-14 09:30 | 2006-03-14 13:42 | 2006-03-14 | LICENSED SRO FAILED RANDOM FITNESS FOR DUTY TEST A licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been put on administrative hold, and the individual has been escorted offsite. Contact the Headquarters Operations Officer for additional details. The licensee has informed the NRC Resident Inspector. * * * * UPDATE ON 3/14/06 AT 1534 FROM S. BRANTLEY TO P. SNYDER * * * * The licensee will be issuing a press release on this event. The licensee has informed the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2006-03-14
42415 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2006-03-13 17:40 | 2006-03-13 21:39 | 2006-03-13 | FAILURE OF ONE EMERGENCY SIREN "The station received a report that a siren was sounding. The station investigated and determined that one siren, EBR#3 was intermittently activating. A communications team was dispatched to remove this siren from service for repairs. The Louisiana Office of Homeland Security and Emergency Preparedness was notified in accordance with station procedures. Responsible personnel at that facility determined that no further action was required since the activation involved only one siren." The siren is in East Baton Rouge Parish and was reported to the site by the Sheriff. The failure is suspected to be a circuit board problem. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-13
42414 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2006-03-13 18:08 | 2006-03-13 21:21 | 2006-03-13 | MANUAL REACTOR SCRAM AFTER OFFGAS SYSTEM FAILURE "During a power ascension, the non-safety Augmented Offgas System experienced a failure which caused a Recombiner high temperature condition. To protect components of the non-safety Augmented Offgas System, station procedures require a manual scram of the reactor when this condition occurs. Station procedures were followed and the reactor was manually scrammed at 18:08. All rods fully inserted and all safety systems performed per design. Primary containment isolation systems responded properly resulting in an automatic isolation of Primary Containment Isolation System Groups 2 and 6 valves and a Reactor Building Isolation due to the transient low reactor water level condition caused by the scram. "The plant is in a stable condition. Investigation is continuing." No safety valves lifted on the scram, decay heat is being removed with the bypass valve, normal feed and condensate are maintaining reactor water level, and the electrical grid is stable on the startup transformer. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 48 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-03-13
42413 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-03-13 11:10 | 2006-03-13 15:35 | 2006-03-13 | TECHNICAL SUPPORT CENTER VENTILATION FAN INOPERABLE "The Technical Support Center ventilation system was discovered to be non-functional at 1110 on March 13, 2006. The cause of the ventilation problem was determined to be damaged drive belts on the supply fan. The belts were replaced and the ventilation system supply fan was returned to service at 1253 on March 13, 2006. This condition is considered a Loss of Offsite Response Capability and is therefore reportable under 10CFR50.72(b)(3)(xiii)." A corrective action request has been generated to follow remedial action. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-03-13
42412 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-03-13 10:01 | 2006-03-13 14:03 | 2006-03-13 | FAILED FITNESS FOR DUTY TEST A licensed employee supervisor had a confirmed positive for alcohol during a re-entry fitness-for-duty test. The employee's access to the plant has been blocked. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2006-03-13
42411 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2006-03-13 11:45 | 2006-03-13 12:54 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * POTENTIAL UNSECURED ACCUMULATION POINT IDENTIFIED "During inspections of the facility, NFS personnel identified an out-of-service equipment elevator and questioned if it contained any potential unsafe accumulation points. The elevator door was later opened and it revealed a pit area that was approximately 8-10 inches below the building floor level. This is considered a 1-hour reportable event because there is no [item relied on for safety or formal controls] in place to prevent a solution leak from entering this location. A solution leak to this area is considered a credible abnormal condition." No actual material accumulation occurred. The licensee currently has compensatory measures in-place to prevent material accumulation in the area. The licensee notified the NRC Resident Inspector. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2008-05-11
42410 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-03-10 15:00 | 2006-03-13 12:40 | 2006-03-13 | STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via fax: "On Friday evening we received a call from the [after-hour phone] service with instructions to call the SOC concerning a lost nuclear gauge. There were instructions to call [the] RSO for Pre-Test Lab [TXRAML02524] a licensee based in Georgetown, TX with authorization to possess and use a variety of moisture/density (M/D) gauges. The RSO explained that around 1500 hrs on Friday, March 10, 2006, one of his trucks was proceeding to a convenience store in the vicinity of Red Bud and County Road 122 in Round Rock, TX when upon arriving at the store it was noticed that the M/D gauge was missing. He admitted that the tailgate may not have been secured and the shipping container was not chained to the bed of the truck. An extensive search of the area traveled was conducted by Pre-Test as well as Round Rock PD and FD without finding the container. The device is a Troxler Model 3411-B serial number (S/N) 10260 with a 9mCi [milliCurie], Cs-137 source model TEL Dwg. #102112 , S/N 40-7662 and a 44mCi, Am-241source model TEL Dwg. #102451, S/N 46-1663." Texas Incident No.: I-8312 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-03-16
42409 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2006-03-09 | 2006-03-13 11:13 | 2006-03-13 | AGREEMENT STATE REPORT - MISSING P-32 On March 9, 2006, Johns Hopkins Medical Institute reported that P-32 was missing from a vial being stored in one of the research facility's freezers. Approximately 10 millicuries is missing. The vial was received on March 2, 2006. Some P-32 (10%) was removed to conduct a research experiment and the vial was replaced in the freezer. When the researcher checked the vial the following day, the vial was empty. The Maryland Department of the Environment and the licensee are conducting investigations. The licensee has performed surveys of the floor that the storage freezer is on, checked for contamination on personnel who work in this area, and water coolers in the facility. All were negative. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2006-03-16
42408 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-03-12 23:45 | 2006-03-13 01:22 | 2006-03-13 | 1-HR REPORT REQUIRED BY PLANT SECURITY PLAN "At 23:45 [CST on] 3/12/06 10CFR50.54(x) is invoked to allow departure from licensee condition requirement in order to provide immediate protection for personnel safety. "It has been invoked due to not able to meet required safety postings due to Tornado Warning for Callaway County. "Required Security postings have been re-established at 00:19 [CST on] 3/13/06." Security Guards posted at selected outside locations were brought inside as a precautionary measure after reports were received that a funnel cloud had formed about 20 miles from the site and was traveling in their direction. The selected outside locations were reposted 34 minutes later. There was no impact on the site. The licensee informed the NRC Resident Inspector. * * * * UPDATE ON 3/13/06 AT 1659 FROM J.R. WEEKLEY TO P. SNYDER * * * * "Section 19.2 of the Callaway Plant Security Plan requires notification of the NRC Operations Center within one hour due to temporary suspension of security measures related to a Tornado warning affecting the plant site. "Upon further review of the events and section 19.2 of the Callaway Plant Security Plan reporting requirement, EN# 42408 is being revised to eliminate the 10CFR50.54(x) reporting criterion and instead list the correct reporting criterion as section 19.2 of the Callaway Plant Security Plan. All dates and times listed are unaffected. "The licensee will notify the NRC Resident Inspector." Notified R4DO (Johnson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW | [5 empty] | 1 | 2006-03-13
42407 | -1 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-03-12 02:17 | 2006-03-12 09:12 | 2006-04-18 | LLRT TEST IDENTIFIED PIPING PENETRATION WITH EXCESSIVE LEAKAGE "While performing local leak rate testing [LLRT] during a planned refueling outage, Susquehanna discovered a Type C penetration on Unit 1 with a leak rate of 12,700 sccm. The limit for this penetration, which can bypass secondary containment, is 4,247 sccm or 9 scfh. Even with this leak rate, the combined leak rate for all penetrations and valves subject to Type B and C tests meets the acceptance criteria of 10CFR50 Appendix J, which is 190,744.7 sccm. This condition seriously degrades the condition of the nuclear power plant, including its principal safety barriers, and is reportable in accordance with 10CFR50.72(b)(3)(ii)." The licensee informed the NRC Resident Inspector. * * * UPDATE AT 1015 EDT ON 4/18/06 FROM JIM HUFFORD TO S. SANDIN * * * "THE FOLLOWING IS A RETRACTION OF ENS NOTIFICATION #42407 "On March 12, 2006, Susquehanna Steam Electric Station reported that a Type C penetration valve on Unit 1 experienced a leak rate of 12,700 sccm during testing. This leakage rate exceeded the TS allowed limit of 4,247 sccm (9 scfh) for Secondary Containment Bypass Leakage (SCBL) valves. Although a non-intrusive investigation determined that a significant amount of the leakage was past a non-Technical Specification test boundary valve, workers were unable to immediately quantify the exact amount of leakage attributable to this valve. Susquehanna conservatively assigned all leakage experienced during the test to the primary containment isolation valve being tested and reported the situation as a condition that seriously degraded the nuclear power plant per 10CFR50.72(b)(3)(ii). Subsequently, Susquehanna successfully re-worked the test boundary valve that was adversely affecting the leak rate test results. With no other changes in test conditions beyond this improvement in the test boundary, the test was re-performed with 464 sccm leakage observed. Total calculated leakage for SCBL amounted to 1306 sccm, well within Tech Spec limits. These results indicate that the excessive leakage was leakage past the test boundary valve and not the tested PCIV. As such, the SCBL limit was never exceeded and the ENS notification (#42407) is, therefore, being retracted." The licensee informed the NRC Resident Inspector. Notified R1DO (Dan Holody). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-03-12
42406 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2006-03-11 01:00 | 2006-03-11 08:35 | 2006-03-11 | UNIT ENTERED A T.S. REQUIRED SHUTDOWN AFTER DECLARING BOTH CONDENSER OFFGAS RADIATION MONITORS INOPERABLE "Condenser offgas radiation monitor flow was blocked. Both Offgas Radiation Monitors were affected and out of service. We entered T.S. 3.0.1 - When a Limiting Condition for Operation is not met, within 1 hour action shall be initiated to place the unit in a condition in which the specification does not apply: "1. Hot Standby within 6 hours. "2. Hot Shutdown with following 6 hours. "3. Cold Shutdown with subsequent 24 hours. "We started to shutdown the Unit at 0100 [hours] on 11 March 2006. Removed blockage from condenser offgas radiation monitors common exhaust and evaluated operability of the condenser offgas radiation monitors. At 0315 [hours] on 11 March 2006, we returned RM-A-5 and RM-A-15 [Condenser Offgas Radiation Monitors] to service and exited T.S. 3.0.1. "We stopped the power reduction at 0251 [hours] on 11 March 2006 while performing the evaluation on the condenser offgas radiation monitors. We stopped the power reduction at 73% reactor power. We started power escalation to 100% at 0338 [hours] on 11 March 2006." The blockage was discovered at 2125 hours on 3/10/2006 during rounds by Secondary Plant Operator who noted that the normal 1 SCFM exhaust flow was reading zero flow. During troubleshooting to discover the cause of the blockage, a bluish foreign material was found in the common exhaust piping. An investigation is underway to identify the source of the foreign material. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-03-11
42405 | -1 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2006-03-11 00:30 | 2006-03-11 06:36 | 2006-03-15 | UNANALYZED CONDITION "This report is being made pursuant to 10CFR50.72(b)(3)(ii)(B), Degraded or Unanalyzed Condition. During Division 1 Core Standby Cooling System (CSCS) valve replacement work, it was discovered that temporary seismic supports required to maintain this piping within the Safe Shutdown Earthquake (SSE) design envelope were not installed. This condition was discovered during the restoration phase of the maintenance and the requirements for the temporary supports no longer exist. At the time of discovery, the required permanent seismic qualified support system had been re-established. The Division 1 CSCS System is common to both units and circulates lake water from the Ultimate Heat Sink (UHS) to the Division 1 Residual Heat Removal (RHR) heat exchangers, Division 1 Diesel Generator cooler, Division 1 Emergency Core Cooling System (ECCS) area room coolers, Division 1 RHR Pump seal coolers, and the Low Pressure Core Spray (LPCS) motor coolers. During the period with the required seismic supports not installed, both Unit 1 and Unit 2 were in an unanalyzed condition due to the inability of the Division 1 CSCS piping to meet its seismic qualification. A postulated structural failure of the Division 1 CSCS piping during an SSE could affect areas containing redundant equipment due to flooding." The licensee is investigating the failure to install the supports. The supports were only needed during the maintenance. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0025 EST ON 3/15/06 FROM T. NANCE TO W. GOTT * * * "On March 11, 2006, it was identified that temporary seismic supports required to maintain the Core Standby Cooling System piping within the Safe Shutdown Earthquake (SSE) envelope during valve replacement activities were not installed. This was reported under 10 CFR 50.72 (b)(3)(ii)(B) as a degraded or unanalyzed condition that significantly degrades plant safety. "Subsequent evaluations have been performed to demonstrate that the piping remained within the SSE envelope with the missing supports. These evaluations have concluded that the remaining supports were sufficient to ensure that piping would remain intact during an SSE. As such, this event notification is being retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (D. Passehl) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-03-11
42404 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-03-10 05:00 | 2006-03-10 14:02 | 2006-03-10 | FAILURE OF EMERGENCY EXHAUST SYSTEM DAMPERS "At 1050 CST on 3/09/2006 the Auxiliary Building ventilation isolation damper, GKD0129, failed a preventive maintenance stroke test as the result of dirt buildup on the damper vanes. The associated Technical Specification action statement, T/S 3.7.13.a, was entered. At 0500 CST on 3/10/2006 mechanical maintenance personnel observed a similar buildup condition on the redundant train damper, GKD0128, which is in series with GKD0129. At 0838 CST on 3/10/2006 approval was given by the Shift Manager to stroke closed GKD0128 to verify Operability. At 0951 CST 3/10/2006 mechanical maintenance personnel observed that GKD0128 damper vanes remained approximately 45 percent open. T/S 3.7.13.b action for two inoperable emergency exhaust system trains inoperable due to inoperable auxiliary building boundary was entered and back dated to 0500 CST 3/10/2006. "Having both trains of auxiliary building ventilation isolation dampers inoperable could prevent the ability to maintain the pressure boundary necessary to control the release of radioactive material. "The licensee will notify the Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2006-03-10
42403 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2006-03-09 22:14 | 2006-03-10 00:58 | 2006-03-14 | AUTOMATIC REACTOR SCRAM DUE TO LOSS OF CONDENSER VACUUM TURBINE TRIP "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) RPS Actuation (scram) for Nine Mile Point Unit 2 which states 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' On 03/09/2006 at 2214 while operating at approximately 85 % reactor power (coast down to refueling) a condenser low vacuum condition resulted in a turbine trip and a subsequent reactor scram. A loss of sealing steam most probably caused the loss of condenser vacuum and an investigation is in progress. Special Operating procedure N2-SOP-101 C was entered. All control rods inserted [fully] as expected. Condenser vacuum has been stabilized and the main steam isolation valves are open. The plant is stable and recovery actions are in progress." Decay heat is being removed via the turbine bypass valves to the main condenser. The condensate and feedwater system is in operation maintaining reactor vessel level. The electric plant is in a normal shutdown lineup and there was no effect from this transient on Unit 1. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0035 EST ON 3/14/06 FROM P. WALSH TO W. GOTT * * * "This update is being made to provide additional information to EN# 42403 which was communicated via ENS on 3/10/06 at 0058 hours. During the scram that occurred at Nine Mile Point Unit 2 on 3/9/06 at 2214 hours, a primary containment isolation signal to RHR Shutdown Cooling, RHR Head Spray and RHR sample valves was received as designed. No components repositioned as the valves are normally closed during plant operations." The licensee will notify the NRC Resident Inspector. Notified R1DO (P. Krohn). | 0 | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-03-10
42402 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-02-28 | 2006-03-09 14:05 | 2006-03-09 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The agreement state submitted the following report via e-mail: "Texas Incident No.: I-8311 "Event date and time: February wear period "Report Received Date: March 9, 2006 "Event location: Brown and Root construction site, 14035 Industrial Road, Houston, TX "Event type: Presumptive badge overexposure "A radiographer trainee was working with a trainer at a construction site in Houston, TX when he noticed that his badge had fallen off approximately 6 feet from a 95 Ci, model G-60 Ir-192 source (S/N NA0502), SPEC model 150 camera (S/N 750). It is uncertain whether the trainee [name deleted] failed to report the incident to the radiographer, supervisor, or RSO. "The incident was thought to have occurred in late February. The trainee is assigned other duties not involving exposure to radiation and the company is considering having cytogenetic testing performed. A second reading of the dosimeter by the company processing the device rendered an inconclusive result. "The radiography company and DSHS staff are performing an investigation although the company is presuming the situation is a badge only exposure since the pocket dosimeters and processed dosimeter worn by the trainer were consistent with their typical monthly exposures of approximately 100 mRem." The film badge read 25.343 Rem. The state will be following up on this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-03-14
42401 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2006-03-03 06:45 | 2006-03-09 15:15 | 2006-03-09 | WISCONSIN AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION EVENT The State provided the following information via email: "On Friday, March 3, 2006 at 6:45 am a vial containing 890 mCi of Tc-99m Cardiolite ruptured while in a heating block. Two employees entered the area immediately, visually confirming the rupture through a window in the heating box and with a survey meter. The employees unplugged the heating box and shut the door. They returned 15 minutes later after the heating box and vial had cooled. The heating box was cleaned and waste was placed in a lead shielded container for decay. No individuals were contaminated. Wipes were taken each day until 3/07/06 when contamination levels were reduced to 2-3 times background. This event will be followed up by DHFS on the next inspection. "Media attention: None" Wisconsin Event Report ID No. 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2006-03-14
42400 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2006-03-09 05:55 | 2006-03-09 09:20 | 2006-03-09 | TECHNICAL SPECIFICATION 3.8.1.1 ENTRY DUE TO LOSS OF UNIT 3 STARTUP TRANSFORMER "While the Unit 3 Startup Transformer was inoperable for planned maintenance, it was discovered that both the 3A and 3B Emergency Diesel Generators were inoperable. The Emergency Diesel Generators were inoperable due to a configuration that resulted in the Emergency Diesel Generators being in the Droop mode versus the Isochronous mode. This configuration was improperly established when offsite power was supplied to Unit 3 via the Main and Auxiliary Transformers (Backfeed). "Upon discovery, jumpers were installed to place both [Unit 3] Emergency Diesel Generators in the proper Isochronous mode correcting this condition at 0615 on March 9, 2006. Unit 4 was identified to be in a condition where one of its required Startup Transformers [from Unit 3] and one of its required Emergency Diesel Generators [from Unit 3] were out of service. Both [Unit 3] Emergency Diesel Generators were restored to an operable condition approximately twenty (20) minutes after discovery." Technical Specification 3.8.1.1 Action c entered due to inoperable Unit 3 Startup Transformer and one inoperable Unit 3 EDG and requires a 4 hour notification report to the NRC. The licensee notified the NRC Resident Inspector. * * * * UPDATE AT 1301 EST ON 3/9/06 FROM M. MURPHY TO P. SNYDER * * * * "As reported in Event Notification # 42400, with Unit 4 at 100% power in Mode 1, and the Unit 3 Startup Transformer out of service for planned maintenance, both the 3A and 3B Emergency Diesel Generators were declared inoperable due to a configuration that placed both Emergency Diesel Generators in the droop mode versus the normal isochronous mode. This placed Unit 4 in a Technical Specification Action Statement for one of its required Startup Transformers and one of its required Emergency Diesel Generators being inoperable. "This EN# 42400 supplement documents that, although the 3A and 3B Emergency Diesel Generators were declared inoperable, the droop mode condition is bounded within previous analyses that demonstrate that the Emergency Diesel Generators and required electrical loads would operate to satisfactorily perform their safety function at the resulting reduced electrical frequency. Refer [to] Turkey Point LER 2004-001-01, dated 10/18/04." The licensee notified the NRC Resident Inspector. Notified R2DO (Fredrickson). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2006-03-09
42399 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2006-03-08 15:53 | 2006-03-08 22:38 | 2006-03-09 | VALID ACTUATION OF EMERGENCY DIESEL GENERATORS "While restoring power to the 3C 480V Load Center following planned maintenance, the 3A safety related 4KV Bus was deenergized by the 3A Sequencer. This resulted in a valid actuation of the emergency diesel generator. The plant was in Mode 5, depressurized, with reactor coolant system level at approximately the vessel flange level. This resulted in a temporary loss of residual heat removal flow which was restored within approximately seven (7) minutes. Reactor coolant system temperature increased from 113 degrees F to 140 degrees F. "Reactor coolant system level and temperature were stabilized at pre-event values." At this time the licensee is preparing to restore off-site power to the 3A Bus and put the emergency diesel generator in standby. The licensee is also investigating the cause of the power loss to the 3A safety related 4KV Bus. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM G. RICHARDSON TO M. RIPLEY 2248 EST 03/09/06 * * * "In response to questions regarding the cause of the loss of the 3A 4KV bus, the following information is provided: "The 3C 480 volt Load Center was de-energized for maintenance and was being restored at the time of the event. One of the maintenance activities associated with the 3C Load Center involved replacement of the 480V feeder breaker for the load center. A rotating cam inside the auxiliary switch for the replacement breaker was misaligned. The misaligned cam caused the switch contacts to operate in reverse, such that normally open contacts would be normally closed and vice versa. One of the auxiliary contacts on the 3C Load Center 480V feeder breaker provides input to the A-train Emergency Diesel Generator (EDG) Load Sequencer. With this contact operation reversed (closed vs. open with the breaker open), the Load Sequencer sensed undervoltage on the 3C Load Center, when the 4kV feeder breaker for the load center was closed. The contact being open would normally block the undervoltage signal, until the 480V feeder breaker was closed and the bus was energized. Once the A-train Load Sequencer sensed the undervoltage condition, the 3A 4kV bus was stripped and then re-energized from the 3A EDG." The licensee notified the NRC Resident Inspector. Notified R2DO (Fredrickson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2006-03-08
42398 | 0 | SABIA, INC |  |  |  |  | 2006-01-11 | 2006-03-08 17:40 | 2006-03-08 | PART 21 NOTIFICATION - DEFECT IN A MATERIAL ANALYZER The RSO provided a report for the failure of a source position indicator on a SABIA, Model XC-series-25 materials analyzer (device per NR-1195-D-103-S) located at Cyprus Creek Mine in Indiana. During a scheduled NRC inspection on 01/11/06 of the shutter for the radioactive source, with the shutter indicating being in the locked out (OFF) position, the source was actually in the open position and the shutter lever appeared to be 180 degrees out of position. During an internal inspection by SABIA on 01/14/06, everything appeared to be in good working order. It was determined that prior to the NRC inspection on 01/11/06, a contractor who was performing a wipe survey of the device retracted the source, but rather than moving the source lever as indicated by the arrows, moved the lever the shortest distance to OFF. This action forced set screws to slip and move the handle to OFF but the sources remained active (ON). In this instance, because the NRC inspector arrived soon after the lever position had been changed, no maintenance was done on the conveyor inside the analyzer while the indication was wrong and no one received any radiation dose resulting from this problem. The unit was repaired by removing the handle and replacing it in the proper position. SABIA will prepare mechanical stops to put on all analyzers that will prevent the source handle from being moved in the wrong direction and will install them as analyzers are routinely serviced. This information represents an interim report, and a final report, together with corrective actions, will be forwarded within 30 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2006-03-08
42397 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2006-03-08 08:00 | 2006-03-08 17:26 | 2006-03-08 | 24-HOUR CONDITION OF LICENSE REPORT DUE TO FAILURE TO SUBMIT TS REQUIRED EXPOSURE REPORT "At 0800 on March 8, 2006, FPL Energy Seabrook discovered a failure to comply with administrative Technical Specification (TS) 6.8.1.2.a. This TS requires submittal of a radiation occupational exposure report by March 1 of each year. On March 8, FPL Energy Seabrook discovered that the report for 2005 had not been submitted and, consequently, failed to meet the March 1st submittal date specified by TS 6.8.1.2.a. This condition is being reported in accordance with the Seabrook Station Facility Operating License, condition 2.G, which requires a 24-hour notification of any violations of section 2.C.(2) of the operating license (FPL Energy Seabrook, LLC shall operate the facility in accordance with the Technical Specifications and the Environmental Protection Plan)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2006-03-08
42396 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2006-03-08 10:30 | 2006-03-08 17:15 | 2006-03-08 | LOSS OF OFFSITE COMMUNICATIONS - SIRENS IN EMERGENCY PLANNING ZONE "On March 8, 2006, at approximately 1030 hours, a full alert siren test was initiated for the sirens in the Indian Point emergency planning zone. Of the 156 sirens, the system initially reported that the activation was underway at 138 sirens. Eighteen of the fifty one sirens in Rockland County (one of the four counties in the 10 mile emergency planning zone) indicated communications failures. One of these, siren R-17, was out of service prior to the test. A final activation report was not available from the system. However, the initial system report was accepted as a basis for the ENS notification since twenty five percent of the sirens had observers who confirmed the initial report results for the sirens they observed. "During the test the siren system computer locked up. None of the 156 sirens could be activated with the computer in this condition. These conditions represent a degraded emergency siren notification system which is reportable under 10 CFR 50.72(b)(3)(xiii). Both Units 2 and 3 were at 100 percent power and remain at 100 percent power. "The siren system was returned to service at approximately 1510 hours on March 8, 2006, with the exception of siren R-17 which remains out of service. All four counties conducted a silent test to confirm functionality. The program application that malfunctioned has been identified and is now functioning properly. The cause of the malfunction is still under investigation. "The counties and State were notified of the loss of sirens. In the event of an emergency, route alerting and outbound calling would have been available to compensate for the siren system loss. Condition report IP2-CR2006-01138 was written for this event." The licensee notified the NRC Resident Inspector and other Government agencies. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-03-08
42395 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-03-08 11:09 | 2006-03-08 14:08 | 2006-03-08 | AUTOMATIC REACTOR TRIP AS A RESULT OF A TURBINE GENERATOR TRIP "This 4-hour notification is being made in accordance with 10CFR50.72(b)(2)(iv)(b). Salem Unit-1 reactor automatically tripped at 1109 (RPS actuation). The trip was initiated due to turbine trip. The cause of the turbine trip is being investigated. "All safety systems functioned as designed with the exception of control rod 1SC1, which did not fully insert. 1SC1 indicates 16 steps. It should indicate zero steps when fully inserted. Auxiliary Feedwater pumps started as expected. Off-site power is available. Emergency diesel generators are available but not required at this time. "During the implementation of the EOP's, a steam leak was reported in the Turbine Building. The Main Steam Isolation Valves (MSIV's) were closed as a conservative measure. This is an 8-hour reportable occurrence in accordance with 10CFR50.72(b)(3)(iv)(a). The leak was subsequently identified as a feedwater leak on the 11CN32 (11 Steam Generator Feed Pump suction valve). The Condensate System was placed in a normal shutdown line-up and the leak is not an impact to personnel safety or plant stability. Decay heat removal is via the atmospheric steam dumps at this time. The MSIV's are being bypassed to restore the main condenser as a heat sink. "Salem Unit-1 is currently in Mode 3 with reactor coolant system temperature at approximately 549 deg F with pressure at 2235 psig. "There was no equipment out of service that contributed to this event and there were no personnel injuries or radiological occurrences associated with this event." The licensee has notified the NRC Resident Inspector and will be making State and local notifications. A press release is expected. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-03-08
42394 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2006-02-24 09:30 | 2006-03-08 11:48 | 2006-03-08 | WISCONSIN AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION EVENT The State provided the following information via facsimile: "On Friday, February 24, 2006 at approximately 9:30 am [CST] a vial of Tc-99m broke in the nuclear pharmacy's dose preparation fume hood. The vial contained about 6 Curies of Tc-99m. The authorized nuclear pharmacist was performing the assay for molybdenum when the vial slipped out of the tongs and fell onto a metal frame that supports the L-block shield. She called over a pharmacy technician who brought absorbent papers to clean up the spill. The papers were placed in a secondary shield for a generator to decay. After clean-up radiation levels were 20 mR/hr in front of the fume hood. Lead sheets were placed on the floor in the immediate vicinity and covered over with cardboard that was taped down to hold the lead in place. The immediate area was posted and access restricted until February 27, 2006. Radiation levels were reduced to 3 mR/hr on February 25, 2006. On Monday, February 27, 2006 radiation levels were background, although a small amount of contamination remained in the hood. Use of the hood resumed on Monday. The lead sheets were taken up from the floor on Tuesday, February 28, 2006. The RSO for the local pharmacy contacted corporate Q & R on Monday, February 27, 2006 to inquire if this event was reportable. Corporate confirmed that a report was required according to HFS 157.13(17)(b)1.b. and also contacted DHFS. Additional information was obtained from the local RSO on March 8, 2006. This event will be followed up by DHFS on the next inspection." WI Event Report ID #: 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2006-03-13
42393 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2006-03-07 17:00 | 2006-03-07 19:41 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * UNANALYZED CONDITION OF CRITICALITY CONTROLS "Approximately 37 liters of High Enriched Uranyl Nitrate (HEUN) solution was inadvertently transferred to a filter enclosure not currently approved for operation. The filter enclosure was equipped with two independent safety-related drains that diverted the solution to the building floor and maintained a safe slab configuration within the enclosure and on the building floor. Upon discovery of this condition, operations in the affected area were terminated and corrective actions were initiated. This condition lead to the determination that the existing safety analysis control flow down was not completed for the operation of this enclosure. "The equipment, which was not approved for use, was connected to a solution transfer line in service. This allowed unattended transfer of solution to a process enclosure. This condition lead to the determination that the existing safety analysis control flow down was not completed for the operation of this enclosure. The safety-related enclosure drains have been inspected by safety personnel and verified to remain free of obstructions to ensure functionality. "Operations in Solvent Extraction Area and all solution transfers to Solvent Extraction were suspended. The unapproved enclosure is being physically disconnected from the Solvent Extraction process prior to releasing the affected Solvent Extraction Area for use. There were no actual or potential safety consequences to the workers, the public, or the environment due to the incomplete control flow down of the safety analysis. "The safety significance of the event is very low, because the system worked as required and maintained a safe slab configuration. "Operations in Solvent Extraction Area and all solution transfers to Solvent Extraction were suspended on March 6, 2006. Starting on March 7, 2006, reviews are being conducted on other out of service equipment to ensure similar conditions don't exist. The unapproved enclosure will be physically disconnected from the Solvent Extraction process prior to releasing the affected Solvent Extraction Area for use." The licensee notified the NRC Resident Inspector. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-05-11
42392 | 0 | US ENGINEERING LABS |  |  |  |  | 2006-03-07 07:00 | 2006-03-07 07:50 | 2006-03-07 | MISSING TROXLER MOISTURE DENSITY GAUGE FOUND In the last week or two during an inventory check at a temporary job site storage building, at the University of Pennsylvania, it was discovered that a Troxler Moisture Density gauge, Model 3411B, serial number 9524, was missing. US Engineering Labs RSO was notified by NRC Region 1 that their gauge had been recovered by a Philadelphia Fire Department located in Northeast Philadelphia. The gauge is stored at a Hazmat storage facility. The RSO said he is going to meet with an NRC Region 1 Inspector and pick up the gauge. The gauge is fully padlocked and still in its case. It does not appear that the case containing the Troxler Moisture gauge had been opened. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-03-07
42391 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-03-01 01:00 | 2006-03-06 20:00 | 2006-03-06 | YELLOW CAKE DRUM EVACUATED INTO ENCLOSED ROOM At approximately 14:00 on 2/28/2006, an employee noticed that a drum of soluble yellow cake had a bulging lid and bottom cap. At 01:00 on 3/1/06, an employee in full protective clothing entered the calciner to release the lid. When the lid was released, approximately half of the barrel's contents evacuated the barrel. Some of the yellow cake went under the employee's hood. The employee will undergo testing 3/7/06. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2006-03-09
42390 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2006-03-06 12:20 | 2006-03-06 14:42 | 2006-03-06 | OFFSITE NOTIFICATION DUE TO LUBE OIL SPILL "On 03/06/06 at 10:40 [EST] a plant operator was dispatched to investigate an unexpected Annunciator D-43, 'TURBINE LUBE OIL RESERVIOR LEVEL HIGH/LOW'. He reported the alarm was a valid low reservoir level [for the main turbine]. A contractor painter had inadvertently bumped open a drain valve on the Kaydon turbine oil filter system. The valve has been closed. "The spilled oil was contained within the Unit 1 Turbine Lube Oil Secondary Containment Structure. The volume of spilled oil has been calculated to be approximately 200 gallons. The Florida Department of Environmental Protection. (DEP) was notified on 3/6/06 at 12:20 EST in accordance with plant procedures for oil spills greater than 25 gallons on a pervious surface. No equipment damage was incurred due to the loss of reservoir level. Actions to retrieve the spilled oil are in progress. "This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(xi.) due to the notification of the Offsite Agency - DEP," The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-06
42389 | 0 | BROWNS FERRY | 1 | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2006-01-13 11:57 | 2006-03-06 12:00 | 2006-03-06 | UNPLANNED, INVALID ACTUATION OF EMERGENCY DIESEL GENERATOR "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of any of the equipment specified in paragraph 50.73(a)(2)(iv)(B). In this case, the equipment actuated was emergency diesel generator (EDG) A. This EDG is common equipment for Units 1 and 2. "On January 13, 2006, troubleshooting was being conducted by maintenance personnel to determine the cause of observed alarm malfunctions on the EDG A local annunciator panel. Browns Ferry Unit 1 was shutdown and defueled and Unit 2 was operating at 100% thermal power. During this troubleshooting activity, at 1157 hours CST, EDG A was inadvertently started. The exact cause of the start could not be conclusively determined. EDG A properly started and ran in response to the invalid start signal. No loss of normal plant electrical power occurred, and the EDG did not connect to its associated shutdown board. The EDG was allowed to run for approximately one hour, and then it was shut down in accordance with plant operating procedures. "Since no actual plant condition existed which required the EDG to start, and since the start occurred inadvertently, most likely as a result of a human error during the electrical circuit troubleshooting effort, this EDG start is classified as invalid. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for evaluation and resolution. [Reference BFN corrective action document PER 96291]." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-03-06
42388 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2006-03-01 12:00 | 2006-03-06 10:30 | 2006-03-06 | INCORRECT DOSE GIVEN TO PROSTATE PATIENT The State provided the following information via facsimile: "The medical physicist for the Via Christi Cancer Center reported that a medical event had occurred the day before. A patient was treated for prostate cancer with I-125 seeds. An activity of 0.4 air kerma units per seed was ordered. The seeds were received with an activity of 0.4 millicuries per seed. The difference in activity units was not detected until after the surgery was completed. The patient received a total dose of 12,850 centigray rather than the prescribed 10,000 centigray; a 28% difference. The radiation oncologist has determined that this larger dose should not cause any untoward harm to the patient. The referring urologist and the patient have been notified of the dose discrepancy. As corrective action, the licensee plans to introduce a new form to be used as part of the procedure followed during permanent implant preparation. This form will be used to record seed activity, including the units, used in treatment planning, listed on the shipping form as well as the seed activity observed at the time of implant." OK Item # - OK060004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2006-03-09
42387 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2006-03-05 07:10 | 2006-03-05 11:12 | 2006-03-05 | AUTOMATIC REACTOR TRIP DUE TO LOW DEPARTURE FROM NUCLEATE BOILING RATIO. "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "On March 5, 2006 at approximately 0710 MST Palo Verde Unit 3 experienced a reactor trip (RPS actuation) from 100% rated thermal power due to low departure from nucleate boiling [ratio] (DNBR) trips on all four channels of the core protection calculators (CPCs). The unit was at normal temperature and pressure prior to the trip. "Prior to the reactor trip, at approximately 0704 MST, a CEAC [Control Element Assembly Calculator] #1 sensor fail alarm was received. While investigating the alarm, at 0710 MST, a control element assembly (CEA) deviation alarm for CEAC #1, all four CPC channel sensor fail alarms, and a CEA withdrawal prohibit alarm were received. The reactor tripped six seconds later. A CEA calculator (CEAC) fail alarm was received on CEAC #1. The apparent cause is presently suspected to be a failure of CEAC #1. An investigation has commenced to determine the root cause of the reactor trip. "All of the control rods fully inserted into the core. Four of eight steam bypass control valves quick opened, per design, directing steam flow to the condenser. No main steam or primary relief valves lifted and none were required. There was no loss of heat removal capability or loss of safety functions associated with the event. Electrical buses transferred to offsite power as designed. The Shift Manager determined this event was an uncomplicated reactor trip. No significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event nor contributed to the event. "Unit 3 is stable at normal operating temperature and pressure in Mode 3. No ESF actuations occurred and none were required. The event did not result in any challenges to the fission product barrier or resulted in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. The event did not adversely affect the safe operation of the plant or health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-03-05
42386 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2006-03-03 18:00 | 2006-03-04 14:51 | 2006-03-28 | REACTOR BUILDING VENTILATION FLOWPATH INOPERABLE "This notification is being made in accordance with License Condition 2.F for Nine Mile Point Unit 2 which states in part 'report any violations of the requirements contained in Section 2.C of this license in the following manner: initial notification shall be made within 24 hours to the NRC Operations Center via the Emergency Notification System, with written follow-up within 30 days in accordance with the procedures described in 10 CFR 50.73(b), ( c), and (e).' License Condition 2.C (2) states in part 'Nine Mile Point Nuclear Station, LLC shall operate the facility in accordance with the Technical Specifications.' This notification describes a licensee identified condition where both redundant Standby Gas Treatment (SGT) trains were apparently inoperable in violation of Technical Specifications. The condition has been corrected. "At 1800 on 3 March 2006, while operating at 91 % power (coast down to refueling), Nine Mile Point Unit 2 identified a condition in which both trains of SGT were apparently rendered inoperable for intermittent time periods of a few hours in length, starting from 17 February 2006 through about 1900 on 28 February 2006. This was not recognized at the time; as such the requirement to initiate a plant shutdown per LCO 3.0.3 was not performed. The condition was caused by use of a heavy-duty tarp and associated cargo net supporting it from underneath, installed across the Unit 2 Reactor Building Hoist Well. Installation of the tarp and net across the hoist well occurred between the above dates, for time periods of a few hours each, in order to support refueling preparations, thereby avoiding spread of contamination during rigging activities. The blockage of the Reactor Building Hoist Well would have obstructed or significantly degraded the design flow paths of both trains of SGT if called upon to perform their safety functions in a design basis accident. Therefore current information indicates this tarp installation configuration renders the SGT system inoperable. "The tarp and net were permanently removed at about 1900 on 28 February 2006 when a supervisor questioned if tarp installation was allowed while the reactor was at power. "Although removal of the tarp and net typically required only a few minutes effort by plant workers, its installation and continued blockage of the ventilation flow path would have resulted in declaration of the [SGT] safety systems to be inoperable if not removed. Workers were not sensitive to the safety function of the open ventilation flow path provided by the hoist well, and no programmatic training or administrative requirements were identified which prohibited the configuration at conditions other than cold shutdown. "Nine Mile Point is in the process of taking compensatory measures to preclude installation of the tarp when SGT is required to be operable by briefing operations, radiation protection and refuel worker crews on ventilation requirements and sensitivity to safety functions. Operations took physical control (lock and key) of the tarp. Corrective actions to provide administrative controls on the tarp installation are in process. Detailed evaluation of the safety significance of the condition is ongoing. "Initial review of plant records indicate that this configuration was also installed intermittently around July 2003. It was recognized as undesirable but was not identified as an operability or reportability issue at the time. Corrective action to prevent its recurrence was not effective. More detailed information on specific dates and durations when this configuration existed will be provided in the 30 day written LER report, after a detailed review. "The instances noted above and any similar conditions identified will be explained in detail in the follow-up LER that will be submitted as required by 10CFR 50.73(a)(2)(i)(B) - 'Any operation or condition which was prohibited by the plants Technical Specifications .'" Unit-1 is not affected since they have a different method to control use of this tarp. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM T. RESTUCCIO TO HUFFMAN AT 2209 ON 3/28/06 * * * "At 1800 on 3 March 2006, while operating at 91% power (coast down to refueling), Nine Mile Point Unit 2 identified a condition in which both trains of the Standby Gas Treatment (SGT) system were apparently inoperable for intermittent time periods of a few hours of length, starting from 17 February 2006 through about 1900 on 28 February 2006. This was not recognized at the time; as such the requirement to initiate a plant shutdown per LCO 3.0.3 was not performed. The condition was caused by use of a heavy-duty tarp and associated cargo net supporting it from underneath, installed across the Unit 2 reactor Building Hoist Well. Installation of the tarp and net across the hoist well occurred between the above dates, for time periods of a few hours each, in order to support refueling preparations, thereby avoiding the spread of contamination during rigging activities. The blockage of the reactor Building Hoist Well would have obstructed or significantly degraded the design flow paths of both trains of SGT if called upon to perform their safety functions in a design basis accident. Review of plant records indicate that this condition was also installed intermittently around July 2003. "A subsequent evaluation of the safety significance of this condition has been performed. This evaluation considered actual area of flow path remaining with the tarp in place, as well as bounding outside temperatures during the times the tarp may have been installed. The evaluation has concluded that the secondary containment function, and therefore the SGT system, remained operable and would have performed its intended safety function during a design basis accident during the time periods the tarp may have been installed during the last three years. This evaluation provides the basis for retraction of the ENS report of March 4, 2006." The licensee notified the NRC Resident Inspector. The R1DO(Cook) has been notified. | 0 | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2006-03-04
42385 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-03-04 05:17 | 2006-03-04 05:34 | 2006-03-04 | CONTROL RODS DECLARED INOPERABLE DURING SHUTDOWN "On 03/03/06, Susquehanna Unit 1 operators began the process of shutting down the unit for the 14th Refueling and Inspection Outage. It was expected that during this evolution, 'slow to settle' control rods would be encountered, and rather than delay the continuance of the shutdown to perform operability testing, it was determined that these control rods would conservatively be declared inoperable. Based on previous testing data and trending analysis of operability testing performed during the cycle, PPL believes that the subject control rods would have passed operability tests. "Accordingly, at 0517 EDT, Technical Specification 3.1.3.f was entered which requires the unit to be taken to Mode 3 in 12 hours when nine or more control rods are inoperable. The inoperable control rods are fully inserted and disarmed, shutdown margin requirements are met, and the control rod system was always fully capable of performing its safety function. "At the time when the ninth control rod was declared inoperable, Unit One was operating at 0% Power. Unit Two is continuing operation at 100% power. "PPL is reporting this event as a Technical Specification Required Shutdown per 10CFR 50.72(b)(2)(i). The NRC Resident Inspector was notified by the licensee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-03-04
42384 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2006-03-03 14:15 | 2006-03-03 16:52 | 2006-03-03 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE A radiography trainee was traversing from one cell to another with the trainer at a fixed radiography facility. Neither individual had a radiation meter. The trainee picked up a guide tube containing a 93 Curie Ir-192 source. The guide tube was held for approximately one minute and the individual was in the vicinity for approximately three minutes. The licensee estimates the individual received a dose of 2-3 rems whole body and 1000 rems to the hand. Rhode Island Department of Health Radiation Control estimates the dose at 8 rems whole body and 18000 rems to the hand. The individual is being transferred to the Emergency Room. The job has been shut down. The state Department of Radiation Control will visit the site on Monday. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2006-03-08
42383 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-09-19 | 2006-03-03 14:30 | 2006-03-03 | AGREEMENT STATE REPORT - LOST NICKEL-63 SOURCES The Commonwealth of Massachusetts submitted the following report via e-mail: "A shipment of 23 devices was scheduled for delivery to a customer in Georgia. AIT Worldwide Logistics, the contract freight forwarder, acknowledged receipt of the 23 devices on September 14, 2005 from GE Ion Track. On Sept. 19th, 2005, when the truck checked into the forwarder's final distribution hub, the shipment was noted to be 2 devices short. The freighter forwarder conducted searches of its distribution centers, and was unable to locate the devices. "GE Ion Track performed a thorough search of their Wilmington, MA facility and the devices were not located. GE Ion Track's and its subcontractor's database showed that the devices had not been transferred to another customer or recipient. "GE Ion Track discovered that these sources were missing on January 24, 2005 and made notification to the Massachusetts Radiation Control Program on January 30, 2006. "The customer in Kuwait and Georgia compared the shipping list to what they received and it was determined that the two missing devices are: "1) Vapor Tracer 2, serial number 120014, source number 09-13171 "2) Itemizer 3, serial number 20566, source number 09-13480 "Each device contained an 8 mCi source of Ni 63 in a foil form, model NER 004 manufactured by Isotope Products Laboratories. "GE Ion Track has concluded that the devices were lost in shipment. As a preventative measure, freight forwarders and transport companies will be asked to verify quantity before accepting shipment from GE Ion Track. "MRCP will be visiting the licensee on Monday March 6, 2006 for investigation." The missing sources were originally reported in a lost voice mail message to the Massachusetts Radiation Control Program on 1/30/2006. The state verified the loss on 3/3/2006. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-03-08
42382 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-01-13 07:45 | 2006-03-03 11:53 | 2007-03-13 | PROTECTED AREA BOUNDARY VULNERABILITY Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * *UPDATED ON 3/13/07 BY KOZAL TO EXPORT TO NRC INTERNAL WEBSITE* * * | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-03-03
42381 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2006-03-02 14:30 | 2006-03-02 18:48 | 2006-03-02 | OFFSITE NOTIFICATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS. "This is a report of a situation, related to the protection of the environment, for which a notification to another government agency has been or will be made, as described in 10CFR50.72(b)(2)(xi). "Specifically, the Palo Verde Nuclear Generating Station (PVNGS) notified the Arizona Department of Environmental Quality (ADEQ) of the possibility of a discharge of non-hazardous material that has the potential to cause groundwater limits to be exceeded "At Palo Verde Unit 3, water was observed in a concrete pipe vault that was abutted against soil. The source of the water appeared to becoming from seals around the pipes and originating from the ground behind the pipe chase. The area behind the pipe chase contains a series of pipes buried in a layer of compacted soil. In order to characterize the water and identify its source, a pothole, approximately 13 feet deep and reinforced with a perforated drain pipe was dug in the radiological controlled area yard so that a sample of the water could be obtained. Initial results from the unit laboratory indicated the presence of tritium. A confirmatory sample was collected and analyzed by the State certified laboratory at Palo Verde that confirmed the presence of tritium at a concentration of approximately 7.14 x 10 -5 microCurie per milliliter. The Aquifer Protection Permit Aquifer Quality Limit for tritium is 2.00 x 10 -5 microCurie per milliliter. "At this time we are working to identify the source. We currently have no evidence that the water has contaminated any aquifer but are continuing with our investigation. Palo Verde's ground-water monitoring program - in place since the unit operations began - has validated that no tritium has been present in any wells or aquifers in any quarterly samples. PVNGS has just finished collecting its quarterly monitoring samples. Analyzed samples have no indication of tritium. The remaining samples will be completed next week. "No Technical Specification effluent limits have been exceeded. No Offsite Dose Calculation Manual (ODCM) effluent limits have been exceeded. No federal effluent limits have been exceeded. Palo Verde has not identified any health or safety risk to the public or onsite personnel. "No source of leakage or release path has been identified, therefore no release rate or total quantity released has been quantified. "Unit 3 is operating at approximately 100% rated thermal power at normal operating temperature and pressure. "This information is also being reported to the Arizona Radiation Regulatory Agency." The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-03-02
42380 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-03-02 13:00 | 2006-03-02 17:07 | 2006-03-02 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE A Troxler Moisture Density gauge was in use when it was run over by a truck. The operator attempted to wave off the truck. The rod was stuck in the extended position. The operator secured an area 25 feet around the damaged gauge. The company's RSO responded, placed a pipe sleeve around the rod, and put the rod in a bucket of sand. A staff member from the Florida Bureau of Radiation observed the recovery. The gauge was transported and then stored in the company's storage facility. The company will notify Troxler. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-03-07
42379 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-03-01 21:27 | 2006-03-01 22:22 | 2006-03-02 | ALERT DECLARED DUE TO HALON DISCHARGE IN SECURITY CONTROL CENTER "At 21:27 on March 1, 2006, a Susquehanna security officer evacuated the security control center and notified the control room of a fire alarm and actuation of the Halon fire suppression system. The actuation of this system resulted in a potential atmosphere immediately dangerous to life and health [IDLH] of personnel in a plant vital area. The fire brigade responded to the event, donning respirators to enter the building, but saw no visible smoke or flames. As a result of an IDLH atmosphere in a plant vital area, Susquehanna entered the emergency plan at the Alert level." The NRC Resident Inspector was informed and responded to the site. The licensee notified state, local and other government agencies. The licensee plans on issuing a press release. Notified DHS (Hill), FEMA (Liggett), DOE (Bailey), EPA (National Response Center, Baumgartner), HHS (Riggs), and USDA (D. Timmons). * * * UPDATE AT 0530 EST ON 3/2/06 FROM RICH KLINEFELTER TO S. SANDIN * * * The licensee terminated the Alert 0433 EST based on the following: Habitability was restored to the security control center by 1. Stopping the Halon discharge 2. Ventilating the affected area 3. Restoring access 4. Isolating Halon sources in the adjacent area to prevent a recurrence and, 5. Posting Fire Watches. The licensee informed State/local agencies and the on-site NRC Resident Inspector. Notified Region I (Perry), NRR EO (Calvo), IRD (Leach), DHS (Hill), FEMA (Liggett), DOE (Pauley), EPA (National Response Center, McCrossen), HHS (H. Peagler), and USDA (D. Timmons). | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | ALERT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2006-03-02
42378 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2006-03-01 14:35 | 2006-03-01 18:13 | 2006-03-01 | MANUAL REACTOR TRIP AS A RESULT OF DROPPED CONTROL RODS "On March 1, 2006, at 1435 hours, the Reactor Protection System was manually actuated while at 100 percent power upon indication of 12 dropped rods. All safety systems actuated as required and safety equipment operated as expected. There were eight control rods that did not indicate full insertion. One control rod had a bad rod bottom light bulb and the other seven control rods require calibration to indicate full insertion. Auxiliary Feedwater started as expected. The Emergency Diesel Generators did not start as offsite power remained available and stable. No primary or secondary relief valves lifted. The plant is in Hot Standby at normal temperature and pressure with residual heat removal using auxiliary feedwater and normal heat removal through the condenser via steam dumps. There was no radiation released. "An investigation revealed that a manual disconnect switch for power control cabinet 1AC was open and scaffold work was being performed in the area. Cabinet 1AC is the power supply for the 12 dropped rods. The event is still under investigation and a post trip review is being conducted." The licensee notified the State and the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-03-01
42377 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2006-02-22 17:00 | 2006-02-28 15:00 | 2006-02-28 | PART 21 NOTIFICATION - DEFECT IN A PORT REDUCER "Honeywell, Metropolis Facility (MTW) mechanics were installing a new BS&B manufactured rupture disc, corresponding safety head, and port reducer on the inlet of the relief valve on the Alternate Primary Cold Trap, E-600. The disc and head were part of an approved change. The safety heads (disc holders) have a port between the disc and relief valve to install a tell-tale indicator. This safety head was for a 1-1/2 in. disc. The normal port size of ½ in. pipe (normal O.D. = 0.84 in.) was reduced to ¼ in. pipe (normal O.D. = 0.54 in.) to allow clearance between the safety head fasteners and the companion flange studs. To facilitate the site requirements of ½ in. pipe size and the clearance needs of the manufacturer, the port reducer was fabricated from a single piece of metal, in this case Monel. MTW had already welded a ½ in. Hex valve to the port and the mechanics had installed the head / disc / port reducer / valve assembly onto the piping. As the tell-tale gauge was installed, the port reducer broke into two pieces. The break was at the machined reduction in the outer diameter. "On inspection a fabrication flaw was found in the port reducer. The large end of the port reducer has an I.D. of 0.55 inches and the small end has an O.D. of 0.54 inches, machined down from the O.D. of 0.84 at the large end. The small O.D. section was specified to be 2.00 inches long. It was improperly machined approximately 2.63 inches long so that the 0.55 I.D. came within a very small distance of the 0.54 O.D. When the gauge was being hand tightened, the port reducer broke at this thin wall point. "MTW reverted to the previous design and all port reducers were collected for investigation. "The licensee notified NRC Region 2 (J. Pelchat)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 21.21 |  |  |  | 0 | 2006-02-28
42376 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-02-27 11:50 | 2006-02-27 15:35 | 2006-02-27 | FALSIFICATION OF ACCESS AUTHORIZATION INFORMATION DURING BACKGROUND REINVESTIGATION. "On 2/27/06 at 1150 (CST) it was discovered that a contractor employee who had been granted unescorted access to the Protected Area had lied to Callaway Plant Access Authorization staff about information obtained during a reinvestigation. This one hour report is being made after discovery of the requirement in NRC Generic Letter 91-03." The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW | [5 empty] | 1 | 2006-02-27
42375 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2006-02-26 02:50 | 2006-02-26 04:32 | 2006-02-26 | MANUAL REACTOR SCRAM DUE TO MSR HIGH LEVEL "This report is being made pursuant to 10CFR50.72 (b) (2) (iv) (B) actuation of RPS when the reactor is critical (4 hour report) and 10CFR50.72 (b) (3) (iv) (A) actuation of PCIS group 2 (8 hour report). "At 0250 on 2/26/06, Central Standard Time, Cooper Nuclear Station was manually scrammed due to main turbine reheat valve remaining closed following testing concurrent with a high level in the moisture separator. Alarm card procedure for this condition required removing the turbine from service. Subsequent to the scram, reactor vessel level lowered to minus 20 inches wide range indication. This corresponds to approximately 140 inches above the top of the fuel. A primary containment isolation system (PCIS) group 2 isolation occurred as expected due to level transient. All automatic actions occurred as expected. "The NRC Senior Resident Inspector has been informed of the event." The reactor scram was uncomplicated, all control rods fully inserted, and no relief or safety valves lifted. The electrical lineup is normal, and the decay heat path is to the main condenser through the turbine bypass valves. | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-02-26
42374 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-02-24 08:54 | 2006-02-24 10:20 | 2006-02-24 | UNUSUAL EVENT DUE TO FIRE IN THE PROTECTED AREA NOT EXTINGUISHED WITHIN 15 MINUTES "At 0836 the control room received a Unit 1B CV/SI pump room fire alarm. An operator reported smoke in the 1B SI pump room at 0840. An unusual event was declared at 0854 due to HU6, fire in the protected area not extinguished within 15 minutes. Sounds of arcing can be heard but flames have not been located. It is suspected that an RWST heater has failed in a pipe tunnel above the 1B SI pump room. The breaker for the RWST heater has been deenergized. The RWST heater pump has been deenergized. Offsite fire department assistance has been requested." The licensee is ventilating the area in order to perform a more thorough inspection of the area and determine the cause of the fire. Both Units1 and 2 remain at 100% reactor power. The NRC Resident Inspector, State and local officials have been notified by the licensee. The NRC has entered the Monitoring Mode at 1036. The NRC Operations Center notified the following organizations: HHS/FDA (V. Howard-King), USDA (Brown), EPA/NRC (Rawls) and DOE (Silva). * * * UPDATE FROM MARCHIONDA TO KNOKE AT 12:49 EST ON 02/24/06 * * * "At 11:09 CST on 02/24/06, Byron terminated an Unusual Event that was declared at 08:54 CST today in accordance with HU6 due to a fire in the Protected Area not extinguished within 15 minutes. The RWST [Refueling Water Storage Tank] heater has been confirmed as the source of the smoke that caused the fire alarm. The heater has been deenergized and the area is being ventilated. The NRC exited the Monitoring Response Mode at 12:52 EST. The NRC Resident Inspector and State officials have been notified by the licensee. NRC made notifications to R3DO(Hills), IRD Managers (Leach, Blount, Wilson), NRR EO (Jung), NRR ET (Dyer), HQ PAO (Brenner), R4DO(Pick), DHS (Carledge), FEMA (Liggett), HHS/FDA( Miller), USDA (Byzustek), EPA/NRC (Rawls, Ribordy), and DOE (Silva). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2006-02-24
42373 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-02-17 | 2006-02-24 01:15 | 2006-02-24 | AGREEMENT STATE - ABANDONED GAUGE The State provided the following information via email: "Based on a July 05 inspection and notification from RML licensing it was determined that Merrvel Engineering had not paid their annual fees and had abandoned their facility. "Based on a 2/17/06 visit to the Engineering Office, it was noted that Merrvel Engineering had been evicted based on the Notice Posted on the front door. RHB contacted the Oakland Police and spoke with an [DELETED] who provided the name of the building owner. RHB contacted the building owner, [DELETED] and set up a time to gain entry to the facility and determine of there were any gauges present. On 2/22/06, RHB visited the facility and met owner at the facility to see if [DELETED] may have left any RAM at this facility. A quick survey indicated that RAM was present in a locked and posted cabinet at the rear of the facility. [DELETED], the owner and party that the property had reverted to, after the 14 day eviction proceedings, removed the hinges from the cabinet and a locked CPN gauge case was observed. According to the case placard, the gauge contained 10 mCi of cesium 137 and 50 mCi of americium 241 on 05/14/84. The serial number of the gauge is M14115815. After removal of the gauge surveys of the facility using a Ludlum Model 19 survey meter indicated that no other gauges were present at this facility. All other readings were background or 9 microrem/hr. A copy of the RHB business card was left with [DELETED] who indicated he would tape it to the door, in case [DELETED], came by and had questions. The inspector noted that [DELETED] had abandoned the facility and had not taken his tools, computers, or equipment. So it is suspected that at some point [DELETED] may contact [DELETED] or RHB regarding the Moisture Gauge. The inspector impounded the gauge because it had been abandoned and will transport the gauge to CPN or storage until release by RHB. RHB will continue to try and locate [DELETED] to retrieve back fees and to determine if he possesses any other portable gauges." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-02-28
42372 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-02-23 18:50 | 2006-02-23 23:37 | 2006-04-21 | DEGRADED CONDITION OF SHROUD TIE RODS "While performing Unit One [In-Vessel Visual Inspection] IVVI examination of the four Shroud Tie Rods (Upper Support Horizontal Support Surface) the following results were reported: "Tie Rod at 135 degree location: Crack-like indications beginning at the inner corner on both sides of the left support and extend to two thirds of the way to the outer corner with full penetration. "Tie Rod at 225 degree location: Crack-like indication beginning at the inner corner on one side of the left support and extending a small portion of the way toward the outer corner. The indication is similar to that described for the shroud tie rod in the 135 degree location except that it is much less pronounced and is only on one side. "Tie Rod at 45 degree location: No apparent indications present. "Tie Rod at 315 degree location: No apparent indications present. "One of the design criteria of the Shroud Tie Rods is to maintain zero separation between the shroud horizontal welds at 100% uprated power, assuming all of the horizontal welds (H1 thru H8) are fully cracked. The Shroud Tie Rods are also designed to maintain structural integrity of the shroud during all design basis accidents and transients. "These findings bring into question the ability of these shroud tie rods to have performed their design function with the reactor in operation. This condition constitutes a serious degradation of a principal safety barrier had the unit been operating. The reactor is presently shutdown and the condition discovered does not represent an immediate safety concern for Unit 1. The extent of this condition is believed to be limited to Unit 1, since Unit 2 core shroud tie rods are made of different materials and installed in a different configuration." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM E. BURKETTE TO M. RIPLEY 0859 EDT 04/21/06 * * * "Retraction of NRC Event # 42372: After further review and evaluation it has been determined that the eight hour call made February 23, 2006 per the guidance of 50.72(b)(3)(ii)(A) should be retracted. "On 02/23/2006 at approximately 2135 EST, Unit 1 was in the refuel mode. During that time routine inspection of the Reactor Vessel Shroud Restraint Tie Rod Assemblies was in progress. The inspections revealed two cracks on the 135 degree assembly and one crack on the 225 degree assembly. In addition the mechanical preload on the 315 degree assembly was found to be below the design value. These assemblies were originally installed as a mechanical replacement of the horizontal shroud welds. "An evaluation was performed of the as-found condition that considered the effects of the cracks on the upper supports and the reduced mechanical preload on the 315 degree assembly. The results of the analysis showed that sufficient compression existed for the tie rod assemblies to be considered operable in the as found condition. Inspection and evaluation of the horizontal shroud welds (original plant design) further determined that sufficient intact weld ligament existed to ensure the shroud design function was maintained without relying on the tie rod assemblies. Therefore, the structural integrity of the shroud was and is maintained for normal operation as well as all design basis accidents and transients." The licensee notified the NRC Resident Inspector. Notified R2 DO (M. Lesser) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2006-02-23
42371 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-02-23 | 2006-02-23 18:23 | 2006-02-23 | AGREEMENT STATE REPORT- STUCK NEUTRON GENERATOR WELL LOGGING SOURCE The State provided the following information via email: A neutron generator well logging source is stuck at 11,000 feet in a well in the Gulf Of Mexico. The location is : long 91degrees 37 min 48.490 sec, and Lat 28 degrees 36 min 26.849 sec. It is in the Gulf of Mexico, Eugene Island. The company is continuing to try and retrieve the stuck source. The radioisotope is H3, but the State does not know the activity level. Texas Incident No: I-8307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-02-28
42370 | 0 | SAN ONOFRE | 1 |  |  | [1] W-3-LP,[2] CE,[3] CE | 2006-02-23 04:00 | 2006-02-23 15:07 | 2006-03-01 | MINOR LEAKAGE OF WASTEWATER FROM TRANSPORT TRUCK "On February 22, 2006, at 1000 PST, two tankers containing wastewater with trace levels of radioactivity departed San Onofre Nuclear Generating Station (SONGS) Unit 1 Industrial Site for Clive, Utah. Each truck contained about 4500 gallons of water. At about 0400 PST February 23, 2006, SCE was notified by the trucking company [Triad Transport Company] that minor leakage from a valve on top of one of the trucks had been observed. The leakage was observed while the truck was stopped in Parawan, Utah approximately 4 hours from its destination. "The driver of the truck immediately notified his management who traveled to the site, identified the origin of the leak as spray from a valve on top of the truck, relieved the tank pressure from a vent valve, and stopped the leak. Dampness was observed on the ground beside the tanker. Unconfirmed measurements indicate radiation levels are near background. "SCE has dispatched a team to the site to coordinate remediation efforts as necessary. The second tanker has arrived at the site in Clive, Utah and no leakage was observed during receipt inspection. The Director of the Utah's Division of Radiation Control and the NRC Resident Inspectors have been notified of this occurrence. At the time of this report, Unit 1 was undergoing decommissioning." The activity from the radionuclides in the entire truck totaled 70.9 mCi, and primarily consisted of Cs-137 (41 mCi), Ni-63 (15 mCi), and Co-60 (5 mCi). The transport company notified the National Response Center. The truck traveled thru 4 States: CA, NV, AZ UT. * * * UPDATE FROM C. WILLIAMS TO M. RIPLEY 1607 EST 03/01/06 * * * "On February 23, 2006, SCE notified the NRC that a small leak had been identified from a tanker that was transporting wastewater with trace levels of radioactivity from SONGS to Clive, Utah. That incident was reported to the NRC in accordance with 10CFR50.72.(b)(2)(xi) and the Utah Division of Radiation Control. "SCE is updating this report to provide the NRC with the following remediation status: "1. SCE has decontaminated the tanker exterior and the leaking flange has been repaired. On February 24, 2006, the tanker completed its trip to the disposal site in Clive, Utah. Enroute, SCE personnel followed the tanker and inspected the flange at planned stops every hour. No leakage was observed and the tanker was received at the disposal facility without further incident. "2. SCE surveyed the truck stop in Parowan and identified two contaminated locations. The first was an asphalt area near the diesel pumps; the second was a gravel area where the truck had parked (about 150 yards from the diesel pumps). All contaminated materials including asphalt, concrete, dirt, and gravel were removed and shipped to the disposal site in Clive, Utah. No detectable levels of licensed material remain at the truck stop. "3. SCE surveyed personnel at the truck stop and determined that one individual had been contaminated. The pants leg of the trucking supervisor who had climbed on top of the truck to stop the leak had been contaminated (SCE took possession of the contaminated garment). There was no contamination on his skin. "4. Approval was obtained from the Utah Division of Radiation Control, the remediated areas of the truck stop were backfilled. "5. SCE is continuing to investigate the cause of the flange leak and will implement appropriate corrective actions. "The NRC resident Inspectors have been notified of this update and will be provided with a copy of this update." Notified R4 DO (J. Whitten) and NMSS EO (S. Flanders) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-02-23
42369 | 0 | FEDERAL AVIATION ADMINISTRATION |  |  |  |  | 1994-01-01 | 2006-02-23 13:50 | 2006-02-23 | LOST STATIC ELIMINATORS Federal Aviation Administration (National Aeronautics Charting Office) was in the process of changing photo processors equipment from a PAKO processor system that used static eliminators (manufactured by NRD LLC, Grand Island, New York) to a coax processor which do not use anti-static bars, in the mid 1990s (1994-1995). Around that time it was possible that six static eliminators left unaccounted with the excessed equipment sent to a NOAA warehouse surplus office. The specific information for these static eliminators are: serial numbers SA2201 and SA2203 (Each: 20.25 mCi, Am-241, bar is 54" long by 1.5" x 1.25"); SA2204 and SA2205 (Each: 18 mCi, Am-241, bar is 48" long by 1.5" x 1.25"); SA2206 and SA2207 (Each: 6.75 mCi, Am-241, bar is 18" long by 1.5" x 1.25"). The Environmental Officer at the Department of Commerce will contact NOAA in an effort to track down the material. Recently the National Aeronautics Charting Office was in the process of moving equipment from the basement of the Department of Commerce building in Washington, DC to a new facility and during the cleanup, two unused static eliminators ended up in a trash compactor and subsequently at the Mosteller Landfill facility in Pennsylvania. The specific information for these static eliminators are: serial numbers SA2200 and SA2202 (Each: 20.25 mCi, Am-241, bar is 54" long by 1.5" x 1.25"). It was reported that one of these static eliminators could be leaking. Arrangements are being made to send these devices from the landfill to the manufacturer for proper disposal. There is one more static eliminator (serial number SA2199 (25.875 mCi, Am-241, bar is 71" long by 1.5" x 1.25") in the basement of the Department of Commerce building in Washington, DC and a survey for low-level contamination is being conducted in response to the static eliminators found at the Mosteller landfill which could possibly be leaking. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-02-23
42368 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-02-20 06:00 | 2006-02-23 12:17 | 2006-02-23 | AGREEMENT STATE REPORT- DELIVERY VEHICLE ACCIDENT WITH UNIT DOSE SHIPPING CONTAINERS ONBOARD The State provided the following information via email: "Received notification on 2-20-06 at 8:00 AM from Cardinal Health Nuclear Pharmacy that one of their delivery vehicles had hit a bridge on Hwy 61 North of Vicksburg, MS, near Cary, MS, located in Sharkey County. The RSO stated that the bridge was covered in ice due to the freezing rain weather conditions. The driver apparently lost control of the pick-up and hit the bridge. The truck rolled over. The camper shell came off in the accident and the unit dose shipping containers were scattered on the roadway. The RSO stated that the driver had stated that the unit doses appeared OK and not leaking. The RSO stated that the driver had removed all the shipping containers from the roadway and secured them at the accident scene. The RSO stated that he had a survey meter with him and was en route to the wreck site. He stated that he would notify DRH if he needed assistance, but thought he would be able to handle situation. "The isotopes involved were Tc-99m, I-131, and F-18. The activity is 75 mCi of FDG (Fluorodeoxyglucose); 12 mCi of I-131; 475 mCi of bulk Tc-99m; 100 mCi/unit doses of Tc-99m. "DRH did not respond to job site. RSO called DRH and stated the shipping containers were secured and not damaged. He said he checked the unit doses for leakage and did not detect any contamination. All doses and shipping containers were put in RSO's vehicle and returned to Flowood facility. RSO stated that after he returned to Flowood facility, he wiped all containers and did not detect an removable contamination." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2006-02-28
42367 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2006-02-23 10:22 | 2006-02-23 11:16 | 2006-02-23 | MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEEDWATER Loss of main feedwater occurred due to an instrument air line failure during a maintenance activity. The reactor was manually tripped and all control rods inserted fully. Auxiliary feedwater received an auto start signal and is providing feedwater to the steam generators. No safety relief valves or PORVs lifted. Decay heat removal is via the turbine bypass valves to the condenser. The plant is in a normal shutdown plant electrical lineup and there was no effect to Unit 3. The licensee notified the State of Connecticut and the city of Waterford. A media press release will be made at a later time. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-02-23
42366 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2006-02-23 08:16 | 2006-02-23 10:54 | 2006-02-23 | FITNESS FOR DUTY EVENT "At approximately 0816 CST a senior licensed operator failed a random fitness-for-duty test administered by the station. The individuals access to the site has been blocked." The licensed employee supervisor had a confirmed positive test for alcohol during a random fitness -for-duty test. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2006-02-23
42365 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2006-02-23 03:31 | 2006-02-23 04:29 | 2006-02-23 | ACCIDENT INVOLVING TRANSPORTATION OF RADIOACTIVE MATERIAL At 0331 EST on 2/23/06, a tractor trailer truck delivering new fuel assemblies backed into the Fuel Handling Building roll up door. The door was 4 feet from the full up position. The upper fuel transport container was pushed into the door but had no visible damage. The truck sustained no damage also. The Fuel Handling Building roll up door had slight damage. This door is only required as a barrier during spent fuel handling which is not in progress. No release of radioactivity occurred. The licensee notified the NRC Resident Inspector. *** UPDATE FROM PRUSSMAN TO KNOKE AT 12:44 EST ON 2/23/06 *** Licensee is retracting this event based on the following information: "At 0429 hours EST, Indian Point 2 reported a tractor trailer truck delivering new fuel assemblies backed into the Fuel Handling Building roll up door. This was event 42365. This event was reported based upon procedural guidance that referenced 49CFR171.15. Indian Point 2 is retracting this notification based on a review of the detailed reporting requirements of 49CFR171.15(b) and a conclusion that none of those reporting requirements was met." The licensee notified the NRC Resident Inspector. Notified R1DO (Henderson) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2006-02-23
42364 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2004-11-05 | 2006-02-22 15:25 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING AN I-131 RADIOPHARMACEUTICAL MISADMINISTRATION The following information was received via facsimile: "NY-06-007 "Radiopharmaceutical therapy misadministration involving Iodine-131 (NYS DOH Internal Tracking Nos. 265 & 342) "Date 11/5/2004 "New York law prohibits the release of any identities in cases of medical events. Therefore the facility name, etc., is not contained in this report. "A 150 mCi therapeutic dose (capsule) of lodine-131 was prescribed for a patient, however the patient received only one of two 75-mCi capsules. The capsule was eventually retrieved after a waste container tripped a radiation monitor at a waste transfer station. Patient has been notified and the hospital is conducting clinical follow-up. The following is a summary of the incident: "The Bureau of Environmental Radiation Protection (BERP) received a request to issue a DOT exemption to allow BFI of Buffalo, NY to return a contaminated municipal solid waste in a compactor container from American Ref-Fuel to the Hospital. DOH staff went to the site to conduct a radiological survey of the trash compactor. The maximum reading at contact was 15 mR/hr (bkg = 0.02 mR/hr). Driver side reading was background. The DOT exemption was issued and the trash container was returned to the hospital. Upon return of the waste compactor it was isolated behind the utility building and the workers, plant engineering staff, were informed of the precautions - stay away. "On 11/17/04 DOH participated in a conference call with hospital staff (Radiation Safety Officer, the treating MD and the Chief Nuclear Medicine Tech). The patient was prescribed a dosage of iodine 131, which was contained in 2 capsules supplied by a radiopharmacy. The treating MD stated that he saw the patient put each of the two capsules in the mouth, one at a time followed by water. Each capsule was in a separate cup. They claim that the patient stated that she took both. "A post administration rad survey reading was taken, as per their routine procedure, and the results were within the range of what was expected, given the activity of the material. This reading apparently was measuring the exposure from the material administered as well as the capsule in the trash next to the patient. In this geometry, the measurement appeared to indicate that the patient had taken the full dose - both capsules. One of the capsules was either not taken or was spit out into the cup. This was then discarded in the normal trash. "The capsule was isolated intact on 11/12/04 by a person who works for an asbestos firm. He did not have a personal rad monitoring device and the hospital was not aware of his level of radiation safety training. This unqualified person apparently sifted through the waste in the presence of the Chief CNMT - she had the survey meter. The capsule activity on the day of treatment was 75 mCi and about 40 mCi on the date of recovery. Hospital staff were aware that a capsule was lost and that a significant misadministration occurred but they did not immediately report either event to the Department as required by 10 NYCRR 16.15 and 16.25. "On 11/22/04, DOH staff performed an onsite investigation. Hospital staff including the RSO; Performance Improvement Manager; Chief CNMT; radiation therapy physicist; Radiology Manager; and the authorized user that administered the I-131 were interviewed. The Director of Facilities was unavailable as he had an emergency surgery the day before this scheduled investigation. Hospital staff informed us that the Director of Facilities was primarily involved with this incident because he manages the hospital's waste. Hospital staff could not explain why the RSO or RSC were not more involved in this incident. They were informed of the immediate reporting requirements for lost sources and misadministrations. It was also strongly suggested that they evaluate why the RSO and RSC did not take a greater role in responding to this incident. "A consultant provided conservative dose estimates as follows: Housekeeper who emptied the waste container - 35 mrem, in-house waste handler 63 [mrem] and the asbestos contractor 101 mrem. DOH staff interviewed housekeeping staff and reconstructed the handling times for this person, and determined the handling time assumptions used by the consultant were greatly overestimated so the dose estimates were likely lower. The contractor that entered the dumpster was not available to be interviewed. "Due to the nature of the violations and manner in which the facility mishandled the event including allowing an unqualified person to retrieve the capsule and lack of RSO and RSC involvement/oversight, enforcement action was pursued and the facility was fined." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42363 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2004-09-29 | 2006-02-22 15:25 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING AN INTRAVASCULAR BRACHYTHERAPY EVENT The following information was received via facsimile: "NY-06-006 "Intravascular Brachytherapy event. (NYS DOH Internal Tracking No 278) "New York law prohibits the release of any identities in cases of medical events. Therefore the facility name, etc., is not contained in this report. "The RSO from the Hospital called on 9/30/04 to report a Novoste Beta Cath IVBT malfunction on 9/29/04. They were using 3.5 French catheter system. They had some difficulty accomplishing a 90-degree bend; at the end of the 3 min 14 seconds treatment time, their attempts to retract the source train failed and the cardiologist had to pull out the catheter manually along with the source train. They notified the FDA and NOVOSTE. They calculated that the patient's heart received a dose of 20 cGy, which the oncologist stated is within tolerance and he anticipates no adverse consequences for the patient. Since the intended dose was delivered to the treatment site, the oncologist believes this is not a medical event. An estimate of dose to the cardiologist's hand indicates an extremity exposure of no more than 3.85 rem which will be added to his annual exposure record." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42362 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2004-05-26 | 2006-02-22 15:25 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING AN INTRAVASCULAR BRACHYTHERAPY EVENT The following information was received via facsimile: "NY-06-005 "Intravascular Brachytherapy event. (NYS DOH Internal Tracking No. 223) "New York law prohibits the release of any identities in cases of medical events. Therefore the facility name, etc., is not contained in this report. "RSO of the hospital called to report that on May 26, 2004, during the introduction of Novoste Sr-90 (3.5 French catheter with the 40mm source train) it was noted, on fluoroscopy that the sources did not advance into the intended target tissue site in the right coronary artery. The licensee used a survey meter to confirm the source train was not in its intended position (rough check). The measurement served to confirm that the source train advanced partially and became stuck in the patient's abdomen. Emergency procedures were followed and all sources were removed within 30 seconds from the 63 [year old] female patient. The catheter assembly containing all sources was placed into a Lucite shield (bailout box). Confirmation of the stuck sources in the transfer case was obtained through fluoroscopy and indicated that the sources were trapped 13 cm from the distal end of the guide catheter. The patient was informed of the event and was subsequently treated with a stent. "This is reportable under 10 NYCRR 16.25(a)(3)&7 (part of the body other than intended and total dose deviation greater than 10 %). The hospital will send the catheter back to Novoste for an evaluation and will submit a written report following Novoste written analysis. "The incident reports from the facility, as well as from Novoste, were provided to DOH. Novoste provided guidance to avoid a recurrence." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42361 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2004-12-13 | 2006-02-22 15:25 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING A LOST/MISSING SOURCE The following information was received via facsimile: "NY-06-004 "Lost/missing Am-241, 250 nano-curie source, 12/13/2004 Vassar College, Poughkeepsie, NY 12604, RML # 410 "College staff called to report that they had lost a 250 nCi Am-241 source. The source is a button source, approximately 2 cm in diameter. The source was discovered missing about 3 months ago, but they failed to report to NYS DOH because they were trying to locate it. The source may have been moved from its storage space in the physics department to a location in the biology department in December 2003 when they were preparing a 10 mCi Am-241 source for shipment to NSSI for disposal at Los Alamos. They think they may have shipped this source along with the 10 mCi Am-241 source. The last time they actually saw the source was when it was leak tested in 2002. Los Alamos is preparing to go through shipments stored at NSSI for repackaging and disposal. Los Alamos will look for the missing source in the shipment. Vassar College will send a written report. "An acknowledgement of their written report was sent and it asked them to keep us apprised of the results of the search at NSSI/LANL. A Notice of Violation was issued for missing quarterly inventories, late reporting of the missing source, no record of transfer/disposal of source." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42360 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2005-11-29 | 2006-02-22 15:25 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING A BROKEN I-125 BRACHYTHERAPY SEED The following information was received via facsimile: "NY-06-003 "Broken I-125 brachytherapy seed. (NYS DOH Internal Tracking No. 421) "New York law prohibits the release of any identities in cases of medical events. Therefore the facility name, etc., is not contained in this report. "RSO reported a broken I-125 source from a prostate seed implant on 11/29/05. The cartridge/source jammed in the applicator and a source was ruptured. All fragments were recovered in the rinse of the applicator and the patient did not have any seed fragments implanted. The written report stated: 90 seeds were ordered, 74 were implanted, 16 unused seeds were recovered (15 intact, one ruptured). The Mick applicator is a model 200-TP. The seeds were GE Healthcare Medi-physics supplied by Oncura Inc. The apparent activity per seed was 0.47 mCi. The radiation oncologist who performed the procedure is experienced (500+ cases). He stated that during the procedure the applicator jammed several times and that he was required to remove seeds from the applicator. It was probably during that process that the seed was ruptured and the loose seeds fell to the table. The medical physicist, upon going to the operating room to retrieve the unused seeds identified two seeds had become loose, one of which was damaged (appeared shorter than the others). A radiological survey indicated that no contamination was present on instruments or the area used for the implant. The inner contents of the broken seed, a silver rod, were recovered. Measurements indicate that the activity remained with the rod rather than being spread around/causing contamination. Bioassay measurements, thyroid and urine, were performed on the patient, physicist and RSO, all with negative results. All unused seeds were placed into the decay in storage program. "This event did not constitute a misadministration because the number of seeds implanted was as per the treatment plan, and there is no evidence that a leaking (ruptured) seed was implanted. New applicators were ordered and placed into service." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42359 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2003-12-14 | 2006-02-22 15:25 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING A MEDICAL MISADMINISTRATION The following information was received via facsimile: "NY-06-002 "HDR Brachytherapy medical event (NYS DOH Internal Tracking; No. 13) "New York law prohibits the release of any identities in cases of medical events. Therefore the facility name, etc., is not contained in this report. "RSO reported a medical misadministration involving a female patient treated on 5/12-14/2003 with SYED(needles)/HDR (Varian unit). Apparently there was an error, with respect to the area treated (incorrect dwell positions), which was not discovered until a final chart review. The treatment plan and double check of the calculations were performed as required. A different physicist than the one who did the treatment plan and double checks discovered the error. The facility submitted a written report. According to the report, since the original catheters had been discarded, reconstructing the scenario to the best of their ability, they concluded that all catheters and connecting tubes had the same lengths as previous similar implants. The measurement of 4 catheters on the first implant day obtained a catheter length of 119.8 cm. It was not repeated for the other 7 catheters and not double-checked by measurement by another physicist. However, the number, 119.8 cm is different from what they usually get for this type of procedure. Therefore, they concluded that the error occurred at this stage of the planning: i.e., (1) the planner did not verify that numbers were similar to what they usually get. (2) physics double check prior to the procedure did not include a second measurement nor did it check if the numbers were reasonable. The measurement was incorrect. Their corrective actions, if followed strictly, should prevent this error from happening again. "Target (Tumor) Intended 2000 cGy. Delivered 150 cGy. "Normal Tissue Expected 150 cGy. Delivered 2000 cGy. "The patient was seen by her gynecological oncologist. This physician and the radiation oncologist determined that the patient should not be adversely affected because the dose was within tolerance of tissue including those of the vagina, rectum and bladder. However they were concerned that the tumor bed did not receive an adequate radiotherapy dose. The patient received additional low dose brachytherapy treatment. The LDR was given on 6/27/03, 1200 cGy to 0.5 cm from the cylinder surface. This treatment was delivered as intended." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42358 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2003-04-17 | 2006-02-22 15:25 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING A RADIOPHARMACEUTICAL MISADMINISTRATION The following information was received via facsimile: "NY-06-001 "Radiopharmaceutical Misadministration. (NYS DOH Internal Tracking No. 86) "New York law prohibits the release of any identities in cases of medical, events. Therefore the facility name, etc., is not contained in this report. "Date of occurrence 4/17/2003 "The patient was prescribed 300mCi of I-131 NaI for thyroid carcinoma but received only 233 mCi. "Licensee received two vials from the radiopharmacy as ordered, one with 200 mCi and the other with 100 mCi. The vials were, as per Licensee's protocol, left in the outer plastic sleeve during assay, and the assays were within acceptable limits. Upon completion of administration to the patient, the vials were again assayed to access the residual activity in the vials. Nothing unusual was noted for the 100 mCi vial, however about 90 mCi remained in the 200 mCi vial. Water was added to that vial and the patient was administered that liquid portion. The vial was again assayed and about 70 mCi remained. The licensee asked the pharmacy for additional I-131 but was told that the additional dosage would not be available until the next day. Consequently the patient was released with only having received 233 of the 300 mCi prescribed. The patient and referring MD were notified. "The RSO/licensee staff investigated. They noted that there was some liquid between the glass vial and its outer plastic sleeve. Upon close examination of the vial it appears that the seal between the vial and septum was flawed allowing material to 'leak' from the vial. Additional surveys of packaging and area were performed. The need for bioassays of those involved in the administration was addressed. "We received copies of reports from both the medical licensee and radiopharmacy. It appears that the seal on the vial was compromised thus allowing material to move outside the vial but remain contained within the outer plastic vial. Thus it had appeared that the vial was okay for use. Bioassay and survey measurements were performed with negative results. Actions to prevent repeat of such an event were included in both reports. "The licensee followed up in regard to the patient. The treating physician stated that the dose was within the therapeutic range by existing standards. The patient was subsequently retreated with 300 mCi of I-131 in August of 2004. This post-treatment scan was positive and he was advised to return again in 6 - 9 months for re-evaluation. He did not, citing difficulties relating to employment etc. However, some time later he agreed to come in for further follow-up." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42357 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-02-22 08:30 | 2006-02-22 16:02 | 2006-02-22 | AGREEMENT STATE REPORT INVOLVING POTENTIAL EXTREMITY OVEREXPOSURE At 0830 PST on 2/22/06 following a radiography shoot at the BP Refinery in Carson, CA, the Assistant Radiographer approached the camera without a survey meter and disconnected the guide tube. The Radiographer noticed that the pigtail was hanging out indicating that the source was not in the shielded volume. A preliminary estimate of the overexposure to the Assistant Radiographer is between 128 - 358 Rem to either hand based on a duration of 14 seconds from a 62.88 Ci Ir-192 source used in the INC-IR100 camera, S/N 6744. The Assistant Radiographer's pocket dosimeter (PD) showed off-scale high (100 mR) while the Radiographer's PD indicated 10 mR. Both employee's submitted their OSLs (Optically Stimulated Luminescent) whole body badges for readings. The Assistant Radiographer has no physical manifestations of a radiological overexposure at this time. The State of CA was notified at 1150 PST and has initiated an investigation into this incident. CA Investigation # 022206. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-02-27
42356 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2006-02-22 01:22 | 2006-02-22 04:51 | 2006-02-22 | AUTOMATIC REACTOR SCRAM DUE TO VALID MAIN TURBINE LOAD REJECT SIGNAL "At 0122 hours (CST) on February 22, 2006, the Unit 1 reactor automatically scrammed from 85% power due to a valid turbine-generator load reject signal. The maximum reactor pressure was approximately 1050 PSIG during the event. All control rods inserted to their full-in position. Reactor water level decreased to approximately -10 inches, which resulted in automatic Group 2 and 3 isolations as expected. All systems responded properly to the event. Unit 1 is in Mode 3, maintaining reactor pressure, and reactor water level in the normal level band. An investigation into the Unit 1 scram and load reject is in progress. "Unit 2 remains at 85% power. "This report is being made in accordance with 10CFR 50.72(b)(2)(iv)(B) and 10 CFR50.72(b)(3)(iv)(A)." No SRVs opened during the transient. Post shutdown electrical lineup is normal with the exception of the loss of one offsite power supply. Decay heat is being removed via the turbine bypass valves to the main condenser and feedwater being provided via main feedwater. Unit 2 is in a Tech Spec LCO for Loss of One Offsite power source. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2006-02-22
42355 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2006-02-21 20:12 | 2006-02-21 23:44 | 2006-02-22 | UNACCOUNTED FOR FIREARM AT ST. LUCIE PLANT The licensee reported a missing firearm. Compensatory actions have been taken. The licensee notified the NRC Resident Inspector. Contact Headquarters Operations Officer for additional details. * * * UPDATE FROM DAVE WILLIAMS TO JOE O'HARA AT 0453 ON 2/22/06 * * * "At 0403 hours on 2/22/06, the St. Lucie County Sheriff's Department was contacted to file a missing weapons report regarding the firearm described in Event Number 42355." Licensee also added additional reporting requirement per 10 CFR 50.72(b)(2)(xi). The licensee notified the NRC Resident Inspector. R2DO(Bonser) notified. * * * UPDATE FROM CALVIN WARD TO JEFF ROTTON AT 1046 ON 2/22/06 * * * "Additional Offsite Notifications to federal government, state, and local agencies were made this morning (2/22/06) regarding Event Number 42355. The time and agencies contacted are as follows: 07:15 Federal Bureau of Investigation, 07:58 Florida Division of Emergency Management, and 08:10 Martin and St. Lucie Counties. These calls were informational calls due to the potential media interest of this event. The media has not been contacted at this time. "The Resident Inspector has been notified." Notified R2DO (Bonser). * * * UPDATE FROM CALVIN WARD TO ARLON COSTA AT 1736 ON 2/22/06 * * * "At 1620 EST on 2/22/06 a notification to the federal agency for Alcohol, Tobacco, and Firearms (ATF) was made regarding Event Number 42355. This call was a voluntary call, not a required call, due to the type of weapon missing. This is update number 3 for this event. The Resident Inspector has been notified." Notified R2DO (Bonser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) | 50.72(b)(2)(xi) |  |  | 1 | 2006-02-22
42354 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-02-21 | 2006-02-21 17:21 | 2006-02-23 | AGREEMENT STATE - LOSS OF IRIDIUM SEED STRAND FOLLOWING MEDICAL TREATMENT The following is a summary of information provided by the State via email: The licensee's Radiation Safety Officer indicated that a gynecological implant of seeds contained in a nylon ribbon were missing at the completion of a patient treatment. The "strand" contained 10 seeds of 0.675 milliCi, each, which was part of a treatment that included 9 total strands of both Cs-137 and Ir-192 sources. The lost strand contained 10 Ir-192 seeds. A resident physician removed the strands at the end of the treatment on the evening of 2/18/06. The treatment had begun on 2/15/06. After returning the strands to the radiation oncology lab it was noted that only 8 strands were present, rather than the 9 which were initially implanted. The patient was thoroughly surveyed and eventually x-ray'd to confirm the missing strand did not remain in the patient. The operating room, the patient's room, the remaining linen and trash from the patient's room, the hallway between the patient's room and the radiation oncology source storage location, the entire nursing floor, the radiation oncology department, the hospital's linen holding facility, the biohazardous waste holding facility and loading docks were all monitored without any success of locating the strand. The patient had been essentially immobilized for the treatment and had received a Foley catheter for relieving her bladder. As such, use of the toilet facilities were not likely (although they too were monitored). Surveys were conducted with instruments that were likely to detect the radiation field associated with almost 7 mCi of Ir-192 (i.e., 4 to 5 milliRem/hr at 1 meter) by the staff. Interviews were conducted with the nursing staff to determine additional details regarding handling of trash and linen from the patient's room. Although the licensee's surveys showed no elevated levels present at the time, the licensee indicated that waste and linen from the room would be held pending potential surveys by the Division. The licensee has also monitored their contracted biohazardous waste treatment facility in Cicero, IL on 2/20/06 with negative results. They also planned to visit the linen laundering facility in Palwaukee, IL on the slim chance that the strand was carried off in soiled linens that might have been changed during the patient's stay. The resident involved, the residency staff and the residency director received additional instruction regarding established procedures, in conjunction with this event, with regards to explanation of sources and accounting procedures. Similarly, the nursing staff was interviewed and refreshed on established procedures with regards to linen and waste processing from patients' rooms. The patient was scheduled to return for a follow up visit on 2/22/06 at which time she was going to be interviewed again to determine if there was any additional information she could provide to help locate the missing strand. Illinois Report #IL060013 * * * UPDATE PROVIDED BY PERRERO TO JEFF ROTTON AT 1034 EST ON 02/23/06 * * * The missing radioactive sources reported by the Illinois Emergency Management Agency (IEMA) on February 21, 2006 at 17:21 from Northwestern Memorial Hospital have been recovered by the facility's radiation safety officer. A radiation monitor alarm was reported to IEMA by the Prairie Hills Landfill staff in Morrison, IL on 2/21/2006. IEMA personnel investigated that alarm yesterday [02/22/06] and confirmed the presence of Ir-192 by gamma spectroscopy as part of a load of trash that was traced back to the hospital's laundry service provider. Arrangements were made to have the ribbon of 10 sources picked up by hospital staff this morning and returned to the hospital for proper disposal. Notified R3DO (Hills) and NMSS EO (Morell) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-02-24
42353 | 0 | MIDSTATE MEDICAL CENTER |  |  |  |  | 2006-01-09 | 2006-02-21 17:00 | 2006-02-21 | LOSS OF GADOLINIUM-153 SOURCE The licensee reported that a gadolinium-153 source (1 Curie Amersham Source #2837LN assayed 08/21/91) cannot be accounted for. The source was installed in a bone mineral density device (LUNAR DP-3) that was retired in 1994. The licensee became aware of this issue when NRC Region 1 inquired into the status of the source during a license renewal application review. Based on the investigation to date, the licensee determined that the bone mineral density device was likely disposed of as scrap metal. The disposition of the source is uncertain. There is no indication that the source was removed from the device and placed into storage. There are also no records that it was returned to Amersham (or its predecessor company). The licensee stated that Amersham did not have source reclamation records dating to the mid-1990s. The licensee noted that the Midstate Medical Center has undergone significant management change since the 1994 including the RSO position. The licensee does not have the same name (previously Veterans Memorial Medical Center) and is not even located in the same building as it was when the source containing bone mineral density device was retired. The current strength of the source based on decay would be 0.2 microCuries. The licensee's investigation is continuing. NRC Region 1 (W. Lee and R. McKinley) have been interacting with the licensee on this event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-02-21
42352 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-02-20 10:50 | 2006-02-21 10:34 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * 24 HOUR NOTIFICATION - POSSIBLE UNANALYZED CONDITION DUE TO A FIXTURE FAILURE "At approximately 10:50 on February 20, 2006, a large [DELETED] component was being removed from a vertical cold water rinse tank using a crane. While suspended directly over the tank, the fixture failed and the component was dropped into the tank. There was no significant damage to the tank or the component. Approximately 20 gallons of water was expelled from the tank and the crane was damaged from the 'recoil' of the crane hook. "There were no injuries resulting from this event. The final configuration of the component in the tank is an analyzed situation that is currently authorized by the Integrated Safety Analysis (ISA). Under the guidance of Industrial Health and Safety and Criticality Safety, the component was removed from the water tank using a different type of fixture and a different crane. The cranes were then locked out to prevent use. BWXT has suspended all use of this type of fixture for component handling until the cause of the failure is understood. "In reviewing the ISA, BWXT concluded this event (dropping a large component due to a fixture failure) was not specifically analyzed in the ISA. However, protective clothing evaluations had been performed and documented under OSHA regulations, to ensure that the worker is protected against chemical consequences. It is clearly bounded by the criticality safety and radiological safety analysis and did not result in failure to meet the criticality or radiological performance requirements of 10 CFR 70.61. The potential chemical consequences are not as clear and BWXT is continuing to evaluate whether this type event could have resulted in failure to meet the performance requirements. Further, BWXT does not believe the potential chemical consequences of this event would fall under the definition of Hazardous Chemicals produced from licensed materials in 10 CFR 70.4, however, further discussions with NRC are required to reach consensus on this. Therefore, BWXT is reporting this event under 10 CFR 70, Appendix A(b)(1). "If it is concluded the potential chemical consequences do not fall under the 10 CFR 70.4 definition, this notification will be withdrawn." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-05-11
42351 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-02-20 07:00 | 2006-02-20 15:43 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * ALARM RESOLUTION IN URANIUM RECOVERY UNIT - 24 HOUR NOTIFICATION "In accordance with 10CFR74.57(f)(2), a report to NRC is required for the following event. On February 20, 2006 the Alarm Threshold Limit was exceeded for [DELETED] Extraction (Column Based) System. This was reported to the Measurement Control Unit Manager on February 20, 2006 at approximately 08:00 a.m. The time in which the alarm was initially reported was approximately 07:00 on February 20, 2006. The initial test difference exceeded the Alarm Threshold Limit. An internal investigation is underway. "Per E41-116 and the FNMCP, an Alarm Investigation Team was established since a process monitoring test exceeded its alarm threshold limit. NRC Ops was contacted at about 15:45 on February 20, 2006. The NPD MC&A contact at NRC (Tom Pham) was contacted via voice mail at about 15:40 on February 20, 2006. Our resident inspector was notified via voice mail at approximately 15:55 on February 20, 2006." Note similar event report #42314. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 74.57 |  |  |  | 0 | 2008-05-11
42350 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-12-31 | 2006-02-20 15:35 | 2006-02-20 | AGREEMENT STATE REPORT INVOLVING POTENTIAL OVEREXPOSURE OF THREE EMPLOYEES The State of Louisiana submitted the following report via fax: "Event Date and Time: December 2005 "Nondestructive & Visual Inspection had three overexposures at the end of 2005. [The first employee] had a dose of 8445 mRem for the year 2005. He was questioned by the RSO and Vice President of the company but could not explain the readings. He was ordered to retake the 40 hour radiation safety course and finished it on February 9, 2006. [The second employee] received a dose of 5221 mRem, for the year 2005. 2092 mRem of this exposure came in September, but the September badge report did not reach Nondestructive Inspection until the end of December because of mail problems after Hurricane Katrina. The mail problem has been addressed by sending the badges to a different location. [The third employee] received a dose of 5221 mRem for the year 2005. [The third employee's] overexposure is still under investigation. The facility is still in the process of reviewing the circumstances that caused the overexposures and are implementing procedures to stop them from re-occurring." LA Event Report ID No.: LA060002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-02-23
42349 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2006-02-19 | 2006-02-20 10:03 | 2006-02-20 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE Between Saturday February 18, 2006 and Sunday morning February 19, 2006, a Troxler (Model 3440, S/N 31113, containing two sources; i.e., 0.3GBq [8 mCi] Cs-137 and 1.48 GBq [40 mCi] Am-241:Be) moisture density gauge was stolen from the operator's residence. The residence was the normal storage location for this gauge. The gauge was stolen along with other equipment from the operator's residence. The event was reported to local law enforcement. Case Number: KS060001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2006-02-23
42348 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2006-02-20 00:23 | 2006-02-20 02:14 | 2006-02-22 | SITE AREA EMERGENCY - REACTOR SCRAM "While shutting down Unit 1 IAW LGP-2-1 with the main turbine off line the plant experienced a turbine control system (EHC) malfunction. This resulted in opening all main turbine bypass valves and subsequent reactor low pressure condition. The low pressure condition resulted in a closure of all main steam isolation valves (MSIV's) and automatic reactor scram. Three rods failed to indicate fully inserted on the scram. Plant emergency operating procedures were entered. All ECCS and plant systems operated as expected. All control rods are fully inserted and the ATWS emergency operating procedure has been exited." The main turbine had been taken off line prior to this event and shutdown was being conducted with heat removal on the bypass valves. Pressure control is currently by using the steam line drains with the Safety Relief Valves in manual. Level is being maintained using normal feedwater. The electrical grid is stable though the plant is not yet on backfeed. Diesel generators are operable. The licensee will notify the NRC Resident Inspector. The NRC entered Monitoring Mode at 0243. Notified R4DO (Graves), DHS (SWO), FEMA (J Kanupp), DOE (S. Morrone), EPA(NRC) (Nowak), USDA (Amanda), HHS (Kleiman). * * * UPDATE AT 0402 ON 2/20/2006 * * * In addition to the initial notification, La Salle is reporting a group 1 isolation in accordance with 10CFR50.72(b)(3)(iv)(a). * * * UPDATE AT 0435 ON 2/20/2006 * * * The site exited the Site Area Emergency and entered the recovery phase. * * * UPDATE AT 05:59 ON 2/20/2006 * * * "At the time of the scram @ 0023 hours rod 38-43 showed position 24 and rods 26-15 and 34-47 showed unknown. Based on more than one rod out condition, it is unanalyzed until shutdown margin can be verified." * * * UPDATE AT 0655 ON 2/20/2006 * * * NRC exited Monitoring Mode. Notified IRD (Wilson), NRR EO (J. Lyons), R3DO (Lara), R4DO (Graves), NRR (Dyer), DHS (SWO), FEMA (Eerwin), DOE (Joe Stambaugh), NRC (does not take updates), USDA (Jim Brzostek), HHS (SOC) (Lt Hrynyshen). * * * UPDATE FROM DAN COVEYOU TO JOE O'HARA AT 0700 ON 02/22/06 * * * "Post trip evaluations have confirmed that all control rods were fully inserted within four minutes of the reactor scram. A review of the post-trip data suggests that there were only control rod indication problems on the three subject rods and all control rods were fully inserted immediately at the time of the reactor scram. Follow-up evaluations also demonstrated that even if the three subject control rods remained fully withdrawn in a cold shutdown condition, the reactor would have remained adequately shutdown. Additional confirmatory evaluations are continuing." The licensee issued a press release on this event. The licensee notified the NRC Resident Inspector. R3DO(Hills) has been notified. | 0 | 0 | 0 | 6 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | UNANALYZED CONDITION | IMode1: Power Operation; FMode1: Hot Shutdown | SITE AREA EMERGENCY | 3 | IL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(ii)(B) | 0 | 2006-02-20
42347 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-02-17 | 2006-02-17 16:08 | 2006-02-17 | TEXAS AGREEMENT STATE REPORT - WELL LOGGING SOURCES STUCK DOWNHOLE "Event date and time of occurrence: - Stuck 1/12/06 @1:35 - Multiple recovery attempts from 1/12/06 to 1/26/06 - Request to Abandon Source made by telephonic contact 1/25/06 @ 12:30 CST to Texas DSHS. - Written notification to DSHS dated 1/26/06. "Date notified of event by licensee: Incident Investigation received the written notification dated 02/06/06. "Radionuclide, activity: (1) - Cs-137 @ 1.7 Ci (1) - Am241Be @ 16 Ci "Sealed source, device, etc, (make, model #, serial #): Well logging tool - sealed neutron generator tube "Leak test information, when applicable: (1) Cs -137 - 1/12/06 - 9.48E-06 microcuries (2) Am241BE - 1/12/06 - 1.52E-01 microcuries "Equipment (make, model #, serial #), and clear description of any equipment problems: (1) Cs- 137 - Amersham Corp., M# CDC.CY3, S# A5006 (2) Am241BE - Gammatron, Inc., M# NSR-F (AN-HP) S# G5044 "Cause, and contributing factors While logging down at a location 14 miles West South-West of Sonora, Texas (Sawyer Canyon Field), the logging unit had multiple failures, causing a free spool of tools & 18,000 feet of cable to enter into the hole. The hole was drilled on AIR & was never loaded with fluid. Fishing tool company attempted ~11 runs to recover tools. Hole cemented on 1/27/06 @ 18:00 "Licensee corrective actions: (1) Cs- 137 Density Source abandoned @ 8,607 feet. (2) Am241BE Neutron Source abandoned @ 8,590 feet. Abandonment plaque constructed with the relevant abandonment depth location information. Well depth: 8, 625 feet. Special instructions to not enter the well before contacting Radiation Control - DSHS. "Provide status through resolution (update record when found): Well sealed with cement & abandoned 1/27/06. Dominion E&P, Inc., Sutton County, Texas" Texas Incident No.: Texas, I-8306 Abandoned in accordance with 10CFR39.77[c]. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-02-22
42346 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2006-02-16 15:30 | 2006-02-17 12:44 | 2006-02-17 | RANDOM FITNESS FOR DUTY FAILURE A non-licensed contract employee supervisor had a confirmed positive for drugs during a random fitness-for-duty test. The employee has been terminated and plant access revoked. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2006-02-17
42345 | 0 | SOUTHEAST MISSOURI STATE UNIVERSITY |  |  |  |  | 2006-02-15 09:00 | 2006-02-16 17:00 | 2006-02-16 | AMERICIUM 241 CONTAMINATION UNDER STORAGE ROOM CABINETS A contamination survey was being performed to relocate 16 cabinets in Room 25 of Magill Hall to change the use of the approximately 500 square foot storage room. These 16 cabinets had not been moved since the basement of Magill Hall went through a decontamination remediation related to an Americium 241 spill in 2000 [See EN# 37282 and EN# 37298]. The contamination survey was conducted due to a license condition relating to the removal of equipment from the facility due to the spill in the year 2000. After the cabinets were moved, fixed Am-241 contamination was found . The contamination testing was limited to 20-25 spots of 100 square centimeters on the floor of Room 25, except for one spot on one cabinet. It is estimated that approximately 30% of the room floor has potential contamination. The highest spot had 80,000 dpm fixed contamination of Am-241 (release limit of 100 dpm). Many other spots ran in the 15,000-35,000 dpm range. The average spot was calculated at 5000 dpm of fixed contamination of Am-241. Air monitoring of the room shows only background levels. Individual counting of the air samples is in progress. There is no indication of airborne contamination at this time. The room is now controlled by a high security lock which can only be opened by the licensee RSO. The room has been posted as a Radioactive Materials Contaminated Area. A very high percentage of the contamination is fixed. One round of decontamination using wet paper towels has reduced the contamination considerably but was not eliminated. The licensee estimates that it will perform up to 3 additional decontamination rounds using gentle techniques (wet paper towels) one week apart to allow the floor to dry between rounds. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2006-02-16
42344 | 0 | ST MARYS HEALTH CARE |  |  |  |  | 2006-02-16 13:00 | 2006-02-16 13:35 | 2006-02-16 | PACKAGES RECEIVED WITH HIGH LEVELS OF EXTERNAL TECHNECIUM 99 CONTAMINATION The RSO for St Marys Health Care performed receipt inspections on two packages delivered from Cardinal Health Pharmacy in Denison, MI that contained 9 milliCuries of I-131 and 14 milliCuries of I-131. The package that contained the 9 milliCurie source had external radiation levels of 0.08 mRem/hr at 3 feet and 1.5 mRem/hr on the surface, and external removable contamination of 16,000 DPM of Tech 99 (gamma emitter). That package also had removable surface contamination on the exterior of the source container inside the packaging material of 619,000 DPM of Tech 99. The second package that contained the 14 milliCurie source had external radiation levels of 0.08 mRem/hr at 3 feet and 1.5 mRem/hr on the surface, and external removable contamination of 5,000 DPM of Tech 99. That package also had removable surface contamination on the exterior of the source container inside the packaging material of 320,000 DPM of Tech 99. The licensee immediately notified the RSO for Cardinal Health Pharmacy in Denison, MI concerning the delivery. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 20.1906(d)(2) |  |  |  | 0 | 2006-02-16
42343 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-02-15 23:45 | 2006-02-16 06:38 | 2006-04-06 | POTENTIAL UNCONTROLLED RADIOLOGICAL RELEASE "This is an 8-hour notification being made to report exceeding the design basis for reactor coolant leakage outside of containment. The normal daily RCS leakrate was completed at 2345 on 2/15/06. This leakrate indicated a step change in unidentified leakrate to .8 gpm from .09 gpm. This leakage value is within the 1 gpm allowed by Technical Specifications. Investigation is on going, and the source of the leak has not been determined at this time, however preliminary conclusion is that the leakage is outside of containment and related to the centrifugal charging pumps. The design requirement ECCS leakage outside of containment is 3840 cc/hour ( .1 gpm) to support GDC-19 limits for control room habilitability. "No safety system actuation occurred or were required. No injuries have occurred due to this event." The licensee has performed troubleshooting to identify the source of the leak and to narrow down the portion of the charging system where they believe the leak to be located. The licensee believes the leak is in a relief valve or hard pipe system to the waste tanks, and that the leak is not external to the system. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM PAUL ABBOTT TO JOE O'HARA AT 2119 ON 4/6/06 * * * "On February 16, 2006, PSEG made an 8-hour report (event number 42343) in accordance with 10CFR50.72(b)(3)(v) because of exceeding the design basis limits for ECCS leakage outside containment. The leakage was determined to be approximately 0.8 gpm with a limit of 3840 cc/hour. "Further investigation into this event determined that the leakage was not in the ECCS recirculation flow path. The cause of the elevated RCS unidentified leakrate was the failure of the automatic three-way high level divert valve (2CV35), which prevents a high level from occurring in the Volume Control Tank (VCT). This valve failed to fully isolate flow to the Chemical Volume Control (CVC) Hold-Up Tanks (HUTs) after VCT level dropped below the divert setpoint of 77% . This conclusion is based on the VCT level being at the divert setpoint a number of times during the shift, the increased use of the valve to control level, and valve performance to fully isolate flow to the CVC HUT'S. "Because this flow path is automatically isolated on a Safety Injection signal by other means (valves), the leakage through this valve is not considered part of the ECCS recirculation flow path and therefore is not included in the calculation for ECCS leakage outside containment. "The event is being withdrawn." The licensee will notify the NRC Resident Inspector. R1DO(Finney) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2006-02-16
42342 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-02-16 02:35 | 2006-02-16 03:38 | 2006-02-16 | INJURED PERSON TAKEN TO LOCAL HOSPITAL "This is a voluntary notification. 10CFR50.72 is not applicable. "At 0235 on February 16, 2006, an operator informed the Control Room that a Health Physics Technician had fallen and received a cut to the head. The site first aid team and Field Unit Supervisor were dispatched and they determined the individual needed to be transported to an off site medical facility. An ambulance arrived on site at 0300 and transported the individual to a local hospital. However, the ambulance never entered the protected area. The individual was not contaminated as determined by Health Physics. "A courtesy call was made to the Pennsylvania Emergency Management Agency due to an emergency vehicle entering the site." The licensee notified the NRC Resident Inspector. | 97 | 100 | 0 | 97 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2006-02-16
42341 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-02-13 | 2006-02-15 18:04 | 2006-02-15 | AGREEMENT STATE - LOSS OF CONTROL OF POLONIUM SOURCE The State of Texas reported that a static eliminator with 20 millicurie Polonium-210 source (based on a January 2005 assay) was inadvertently shipped to Taiwan without radioactive material controls or the knowledge of the RSO for the licensee. The RSO received a Po-210 source for renewal of the source in a static eliminator and discovered that the eliminator was missing. The licensee determined that the static eliminator with the depleted Po-210 source had been shipped to Taiwan without consideration of the Po-210 source in the eliminator. There is currently no indication that the source is lost - but it is no longer under the licensee's control. Investigation into this event is ongoing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-02-20
42340 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2006-02-15 16:30 | 2006-02-15 17:26 | 2006-02-15 | INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA "On 2/13/2006, eleven (11) security handguns were delivered to the Oconee Complex Building. The Complex Building is located in the owner Controlled Area of the Oconee Nuclear Site, however, is not located within the Oconee Site Protected Area. The handguns were packaged by the manufacturer in two boxes (8 in one box and 3 in one box). "On 2/13/2006, after the handguns were delivered, the boxes were then processed through the x-ray search equipment at the Oconee Complex by Oconee Security. Subsequently, at approximately 1600 hours on 2/13/2006, these boxes were escorted by Security to the protected area vehicle access portal and brought into the protected area along with other packages for delivery to site personnel. "The boxes containing the handguns were taken to the lobby of the Oconee Office Building (within site protected area) where they remained until approximately 1630 hours on 2/15/2006. At this time the boxes were obtained by Security and brought to the Security Admin Area (within the site protected area) where it was then discovered that the boxes contained handguns. "Initial review indicates that the eleven (11) handguns were expected to be delivered to the site. Review of shipping documentation confirms that eleven (11) handguns were delivered to the site. Upon discovery by Security on 2/15/2006, the boxes were sealed and did not reveal any obvious signs of tampering." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-02-15
42339 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-02-15 13:00 | 2006-02-15 14:04 | 2006-02-15 | OFFSITE NOTIFICATION - PRESS RELEASE CONCERNING TRITIUM INSPECTION PROGRAM "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) to let the NRC know that a press release issued by Exelon Nuclear at 1300 CST on February 15, 2006 mentions, in part, recently identified inadvertent tritium releases from Braidwood, Byron and Dresden Stations." This event was reported by Exelon Corporate also includes Byron 1 & 2 ( both units at 100%) and Dresden 2 & 3 ( Unit 2 - 97% and Unit 3 - 98%). See related Braidwood Station event - Event Number 42184. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-02-15
42338 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2006-02-14 | 2006-02-15 12:17 | 2006-02-15 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The State provided the following information via email: "Received notification on 2-14-06 from Newcomb Engineering Company that their Troxler Model 3430 moisture/density gauge [8 millicuries Cesium-137 and 40 millicuries Americium-241:Be] was run over by a bulldozer at a job site. The company RSO stated that the device was smashed in the dirt and they were not getting any abnormal survey readings. He stated that the technician was performing soil densities at the job site facing away from the bulldozer driver. The bulldozer driver was going forward and did not see the technician. The bulldozer driver hit the technician also but he was not injured. The source was not in the shielded position. By his description of the device, DRH [Mississippi Division of Radiological Health] responded to the job site that was approximately 230 miles away with a shielded container. The RSO stated that they would secure the area around the gauge until DRH arrived. "DRH responded to job site. On arrival, it was apparent that Cs-137 source rod was not shielded. Inspector performed leak tests on sources and did not detect any removable contamination. Gauge was in many pieces. Cesium-137 source rod was placed in shielded container. The base plate of the gauge, that contained the Americium-241:Be source was put in a box and placed in the inspectors toolbox. All other parts of the gauge were put in the box also. Gauge was returned to DRH office for storage until disposal could be arranged. "Highest reading was 300 mR/hr at 6" from end of source rod. 2 mR/hr at 1 meter from gauge. After putting gauge in shield, highest reading was 0.5 mR/hr at the surface of the top of the shielded container. Surveys [of the area where it was run over] were conducted after the gauge was secured . No readings above background were detected. "Newcomb Engineering was told that they would have to submit a written report to DRH describing the incident. DRH is going to store the gauge until Newcomb Engineering can arrange disposal." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2006-02-20
42337 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-02-14 16:00 | 2006-02-14 22:38 | 2006-02-14 | APPENDIX "R" RELATED UNANALYZED CONDITION "During an Appendix R analysis update effort, a circuit analysis issue was identified. This issue results in an unanalyzed condition, in that, a fire in fire area 13 could result in the loss of the ability to makeup to the PCS [primary coolant system]. The fire could cause the loss of all charging. It could also potentially start the only available HPSI pump with the suction path isolated. The suction valve closes as a result of the fire. The fire detection system in the area is operable." The licensee noted that compensatory fire patrols of the area have already been instituted. The licensee is investigating both short term procedural changes and long term equipment modifications. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-02-14
42336 | 0 | US ARMY |  |  |  |  | 2006-02-10 | 2006-02-14 18:00 | 2006-02-14 | POTENTIALLY DEFECTIVE MOISTURE DENSITY GAUGE LOCKING MECHANISM As part of the Pre-Operational Check, Operators discovered the one of their CPN Model MC-1 Moisture Density Gauges had a potentially defective locking mechanism, i.e., "the handle could be moved down through the blocking mechanism no matter which position the key was in." The CPN Model MC-1, S/N M18012172 was manufactured approximately 30 years ago and contains two sources; 10 mCi Cs-137 and 50 mCi Americium-241/Be (nominal). The unit is currently locked in its' storage container at the Sierra Army Depot in CA, awaiting return to the manufacturer for evaluation and repair. The licensee notified NRC Region 3 Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-02-14
42335 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-02-14 09:00 | 2006-02-14 15:26 | 2006-02-14 | FITNESS FOR DUTY - CONTRACT SUPERVISOR A non-licensed contract employee supervisor had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employees access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Hot Shutdown | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2006-02-14
42334 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-02-13 09:33 | 2006-02-13 17:18 | 2006-02-21 | LOSS OF SINGLE POWER SUPPLY COULD RESULT IN LOSS OF VENTILATION FOR DC SUBSYSTEMS IN BOTH UNITS "At 09:33 on February 13, 2006, a Susquehanna field operator inadvertently tripped an essential instrument AC panel breaker, while applying an energy control tag. He immediately communicated this condition to the control room, and then closed the breaker to restore power. During the subsequent investigation to determine applicable technical specifications, control room operators discovered that the tripped breaker resulted in a momentary loss of both battery room exhaust subsystems. To comply with the required actions for a loss of both battery room exhaust subsystems, Susquehanna declared all Unit 1 and Unit 2 DC subsystems inoperable, which resulted in LCO 3.0.3. "Although the entry into LCO 3.0.3 is not reportable, Susquehanna did discover an unanalyzed condition on both units that significantly degrades plant safety, which is reportable in accordance with 10CFR50.72(b)(3)(ii). The loss of a single power supply could result in the loss of ventilation and cooling for all DC subsystems on both units, leading to degradation of essential DC power sources. This condition does not meet single failure criteria for safety-related equipment." The licensee notified the NRC Resident Inspector. * * * UPDATE 1342 EST ON 2/21/06 FROM GORDY ROBINSON TO S. SANDIN * * * The licensee is retracting this report based on the following: "At 0933 hours on February 13, 2006, a Susquehanna field operator inadvertently tripped an essential instrument AC panel breaker while applying an energy control tag. The field operator immediately communicated this condition to the control room and was directed to close the breaker to restore power. The breaker trip resulted in a momentary loss of exhaust flow from the Class 1E 125 VDC and 250 VDC battery rooms. In response, operators declared all Unit 1 and Unit 2 batteries inoperable. An ENS notification (# 42334) was initiated in accordance with 10CFR50.72(b)(3)(ii)(B), Unanalyzed Condition that Significantly Affects Plant Safety, because the loss of a single power supply rendered the status of all station essential DC power sources (Batteries) indeterminate and, thus, inoperable. It was believed that this condition did not meet single failure criteria for safety-related equipment. "Subsequent analysis of this event has revealed that the battery room exhaust system acted per design. The system's design is consistent with intended logic that ensures single failure proof isolation of the system, in compliance with the single failure criterion, in response to a toxic gas release. The single failure proof design of the battery exhaust system ensures isolation, not continued operation, in the presence of a single failure. The analysis further concluded that a short term loss of battery room exhaust does not compromise a battery's ability to function. The insights obtained through this analysis provide the basis for retraction of the ENS report of February 13, 2006." The licensee informed the NRC Resident Inspector. Notified R1DO(Henderson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-02-13
42333 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-12-12 | 2006-02-13 16:20 | 2006-02-13 | AGREEMENT STATE - TROXLER GAUGE STOLEN AND RECOVERED IN TEXAS The State provided the following information via facsimile: "The gauge was unlocked in the company pickup truck. The technician was in the process of carrying the striker plate and drive rod into a below ground level test site, when he returned for the gauge it was missing. The technician reported the missing gauge to his company, Paris Texas Police Department and Paris Fire Department. The gauge was found in a parking lot the next morning by law enforcement. "The gauge was a model # 3440 (serial # 27497) containing a Cs-137 nominal 8 mCi (source # 7501281) and an Am-241/Be source with nominal 40 mCi (serial # 47-23993). "This event information was found as part of a review of all reports received from April 2005 till February 12, 2006 by this department." Texas Report No. I-8286 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-02-16
42332 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-02-12 08:00 | 2006-02-12 11:34 | 2006-02-12 | LOSS OF COMMUNICATIONS - LOSS OF SIRENS "At 07:00 am, it was determined that 21 of 34 Offsite Sirens in New Jersey and 11 of 37 Offsite Sirens in Delaware, scattered through the 10-mile EPZ surrounding the Salem-Hope Creek site were not functional due to the winter storm conditions and loss of residential power. Actions to recover sirens in New Jersey and Delaware are awaiting restoration of residential power by local utilities. Local utilities are presently working to restore power. As of 10:29, 9 Offsite Sirens in Delaware have been returned to functional status, however there is no estimate when remaining Delaware and New Jersey Offsite Sirens will be functional. An alternate method to provide 'route alerting' is available as directed by county Emergency Services Directors. "This report is being made for both Salem and Hope Creek Generating Stations. Hope Creek Generating Station is at 100% power. The 'D' Service Water (SSW) Pump is inoperable; all other safety related Structure Systems Components (SSCs) are operable. Both Salem Generating Station units are operating at 100% power with all safety-related SSCs operable." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-02-12
42331 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-02-12 04:00 | 2006-02-12 04:05 | 2006-02-12 | LOSS OF ABILITY TO COLLECT METEOROLOGICAL DATA "This 8-hour notification is being made to report that both Salem and Hope Creek sites have lost all meteorological data for wind speed and direction for greater than 8 hours. The data was recognized as not being available at 2000 hours on 02/11/06. "All three units are operating at 100% power. No actuations have taken place related to this event. The cause of this inability to predict meteorological conditions is being investigated. Procedural guidance is available to obtain the necessary data from the National Weather Service should this data be necessary." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-02-12
42330 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-02-11 15:15 | 2006-02-11 15:52 | 2006-02-11 | ALERT DECLARED DUE TO A FIRE IN A VENTILATION FAN At 1506 EST, Operators heard a loud noise and discovered that a bearing in the Motor Control Switchgear in the Miscellaneous Equipment Area Return Fan "B" had failed. The Plant Fire Brigade responded and extinguished the fire. Offsite assistance was requested and did respond. No injuries were reported and all personnel have been accounted for. A reflash watch has been posted. The licensee will remain in the Alert awaiting completion of the ventilation transfer to the "A" train. The licensee notified state/local agencies and the NRC Resident Inspector. * * * UPDATE AT 1740 EST FROM KEN MEADE TO S. SANDIN * * * At 1740 EST, the licensee terminated the Alert based on the fire being out and the plant stable. The licensee plans to issue a press release. Notified R3DO(Lanksbury), EO(Wermiel), IRD(Leach) and NRR ET(Dyer). Notified DHS SWO(Marianne), FEMA(Barden), DOE(DaSilva), HHS(Lt. Kleiman), USDA(Jimenez) and NRC-EPA(Crews). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 3 | OH | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2006-02-11
42329 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-02-10 13:45 | 2006-02-10 16:30 | 2006-02-10 | OFFSITE NOTIFICATION "At 1345, a notification was made to the Ohio EPA. This notification was based on 1) Any unanticipated bypass which exceeds any effluent limitation in the NPDES Permit and 2) Any discharge of water to the storm drains that is not covered by the following excerpt from the permit. "The event itself was the pumping of rain water that had sulfuric acid (pH approximately 2.6) in it to a storm drain. Approximately 10 gallons of this mixture was pumped to the drain. The 10 gallons pumped contained approximately 1 milliliter of sulfuric acid. Sample taken at the storm drain out fall indicated normal pH value of 8.03." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-02-10
42328 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2006-02-10 08:30 | 2006-02-10 16:13 | 2006-02-28 | FAILURE TO MEET THE FITNESS FOR DUTY TESTING REQUIREMENTS "10 CFR26.24 describes the chemical and drug testing programs for persons subject to this part. 10 CFR26.24(2) states that 'Random testing must be conducted at an annual rate equal to at least 50 percent of the workforce.' On 2/10/06 at 0830, Wolf Creek determined that the random testing rate was 49.41 percent for calendar year 2005, which is below 50 percent. 10 CFR26.73 states that notification to the NRC Operations Center must be made by telephone within 24 hours." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM L. TAYLOR TO J. KNOKE AT 16:22 ON 2/28/2006 * * * This event is being retracted. A manual verification of the 2005 data was conducted. It confirmed that the random test rate for 2005 exceeded 50%, therefore this event is not reportable per 10 CFR 26.73. The licensee notified the NRC Resident Inspector. Notified the R4DO (J. Whitten) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 26.73 |  |  |  | 0 | 2006-02-10
42327 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2006-02-10 11:00 | 2006-02-10 16:06 | 2006-02-10 | POTENTIAL FOR LOSS OF SAFE SHUTDOWN CAPABILITY "As a result of Wolf Creek's 2005 Triennial Fire Protection Inspection, a re-evaluation of concerns described in NRC Information Notice (IN 92-18), 'POTENTIAL FOR LOSS OF REMOTE SHUTDOWN CAPABILITY DURING A CONTROL ROOM FIRE' was performed. During that re-evaluation it was identified that in the event of a fire in the control room, 39 motor operated valves (MOVs) credited for post-fire safe shutdown could potentially fail in an unanalyzed condition. Of those 39 MOVs, failure of 4 of them could potentially prevent achieving and maintaining safe shutdown (SSD) conditions. "In the 39 MOV circuits identified above, an intra-cable hot short between one conductor on the hot side of the indication circuit and another conductor on the load side of the control room hand switch could bypass the torque switch and energize either the open or close coil. If this occurs, the open or close contactor will close and the motor will operate in either the open or close direction until the motor stalls, possibly resulting in damage to the valve such that it cannot be manually operated. "Present system operability is not affected as there has been no occurrence of a fire in the Control Room and compensatory actions are in place to detect and mitigate the effects of a fire in the Control Room. "Actions taken or planned: An hourly fire watch was established in the Control Room due to a previous condition identified on 11/16/2005 in accordance with AP 10-104, Breech procedure. The condition identified today will be referenced on the active Breach Request that was implemented on 11/16/2005." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2006-02-10
42326 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-02-10 06:10 | 2006-02-10 15:46 | 2006-02-14 | LOSS OF ASSESSEMENT CAPABILITY "On February 10, 2006, the Clinton Power Station lost the function of the Safety Parameter Display System (SPDS). The SPDS is unavailable for planned maintenance on an un-interruptible power supply (UPS). "This event is reportable due to the major loss of emergency assessment capability per 10CFR50.72(b)(3)(xiii) (when the SPDS has been unavailable for 8 hours or greater). "The UPS outage is expected to be 3 days in duration. "The NRC Resident Inspector has been notified." * * * UPDATE FROM LEFFEL TO HUFFMAN AT 1535 EST ON 2/14/06 * * * "Repairs to the un-interruptible power supply (UPS) were completed and the plant process computer was recovered at 1030 hours on 2/14/06. The SPDS has been fully restored." The licensee notified the NRC Resident Inspector. R3DO (Lara) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-02-10
42325 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2006-02-08 14:00 | 2006-02-09 17:51 | 2006-02-09 | AGREEMENT STATE REPORT INVOLVING A STOLEN NUCLEAR DENSITY GAUGE The following information was received via facsimile: "At approximately 6:20 PM February 8, 2006, the Agency was informed that the Licensee had lost a Nuclear Density Gauge from the back of a pickup truck, while working in the area of Southern and Cortez Roads in Apache Junction, Arizona. The missing gauge is a CPN Model MC-3 gauge, SN M37037422. The disappearance occurred between 1 PM and 2 PM on February 8, 2006. The gauge contains 8 mCi of Cesium-137 and 40 mCi Am:Be-241. "The Licensee is offering a $500.00 reward for the recovery of the sources. A press release is to be made. Please contact Alf Wold, Operations Manager for Alpha Geotechnical. "The Agency continues to investigate. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." Arizona First Notice: 05-11 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2006-02-14
42324 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2006-02-09 14:15 | 2006-02-09 15:13 | 2006-02-09 | LOSS OF CONTROL OF SNM DUE TO DISCOVERY OF FUEL PELLET IN THE EMPLOYEE PARKING LOT "Please withhold this information in accordance with 10CFR2.390 "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (less than or equal to 5.0 wt.% U-235) PWR fuel fabricator for commercial light water reactors. License: SNM-1107. "Time and Date of Event: February 09, 2006, 2:25 "Reason for Notification: On February 9, 2006, an employee found what he thought to be a single uranium pellet in the parking lot of the Columbia Plant. The employee gave the pellet to Security and notified EH&S personnel. At 2:15 PM it was determined with a high degree of certainty that this was a pellet, enriched to less than 5 % U235. As a result of the discovery of SNM outside the Controlled Access Area but on Westinghouse property, it was determined that this met the requirement for notification of the EOC within one hour as a "loss of SNM" event reportable under 10CFR74.11. "Summary of Activity: · A single pellet (approximately 4.84 grams U, 0.2 grams U235) was found in the parking lot of the Westinghouse CFFF. · The parking lot and the security station have been surveyed and found to be free of contamination. · The parking lot has been visually inspected for any additional pellets or foreign material. Nothing unusual has been found. · There is no expectation of exposure to any individual. · There has been no evidence of intentional unauthorized removal of SNM. · The pellet is currently under control of CFFF personnel and additional investigations are planned or are being conducted." The licensee will notify a NRC Region II based Inspector who is currently on-site. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN SNM | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 74.11(a) |  |  |  | 1 | 2006-02-09
42323 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-02-06 16:59 | 2006-02-09 11:02 | 2006-02-09 | SAFEGUARDS REPORT Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. Immediate compensatory measures were taken upon discovery. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-02-09
42322 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2006-02-08 16:30 | 2006-02-08 18:21 | 2006-02-08 | OFFSITE NOTIFICATION "Notification is being made that the South Texas Project is notifying the State of Texas Department of State Health Services not to use the Delta Temperature method (primary method) [used to determine atmosphere stability input to offsite dose assessment calculations] for dose assessment. South Texas Project will be using the Backup method until the Delta Temperature problems are resolved." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-02-08
42321 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-11-30 | 2006-02-08 16:22 | 2006-02-08 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR DEVICES The State provided the following information via email: "Flowserve Corporation, a General Licensee, reported to Ohio Department of Health (ODH) on 2/8/06 that they were unable to account for two ionizer bars from static eliminator devices. Each device was from an NRD model P-2001 and contained an estimated 4 mCi each of Po-210. The devices were removed from a facility being shut down over the time period June 2005 through December 2005. The devices were discovered missing when the manufacturer notified Flowserve that it was time to exchange the Po-210 sources. Flowserve determined that the devices had gone to one of three places: 1. to another Flowserve facility; 2. mistakenly placed in a roll-off container and disposed of as construction debris; or 3. mistakenly placed in a roll-off container and disposed of as scrap metal. An investigation by Flowserve has determined that the devices were not sent to another facility. Flowserve has contacted their decommissioning contractors and have determined that all construction debris was disposed of at various landfills throughout the greater Cincinnati/Dayton area, and that all scrap metals were disposed of through a broker which immediately sent the metals on for processing/recycling. Flowserve does not consider any further investigation to be beneficial at this time." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2006-02-13
42320 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-02-07 18:30 | 2006-02-08 12:05 | 2006-02-08 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE In the evening on 02/07/06, the gauge operator drove to his residence to retrieve paperwork. At 1830, when the operator returned to his truck he noticed his Troxler Model 3440 (s/n 32207 8 millicuries Cs-137 and 40 millicuries Am-241/Be) was missing. The theft was reported to local law enforcement. The gauge was locked in the bed of the truck. The company's Radiation Safety Officer is enroute to conduct an investigation. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-02-13
42319 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-01-09 | 2006-02-07 19:10 | 2006-02-07 | AGREEMENT STATE - SOURCE DISPOSAL RECORDS UNAVAILABLE The State provided the following information via email: "On 09 January 2006 Washington Office of Radiation Protection received written notification from Multicare that Multicare could not account for transfer / disposal of 12 (twelve) Gadolinium-153 radioactive sealed sources (260 microcuries, 9.6 Megabecquerels total activity on 09 January 2006). The notification was in response to an Item of Noncompliance issued to Multicare for incomplete transfer / disposal records. The licensee believes that the sources were properly disposed of around December 2003, but incomplete records cannot confirm this. Complete records for similar sources confirm proper disposal of similar sources around similar time frame. [The Washington Office of Radiation Protection] investigation continues." Washington State Report #WA-06-003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-02-10
42318 | -1 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2006-02-06 20:50 | 2006-02-07 15:49 | 2006-03-27 | UNANALYZED CONDITION - NON-CONFORMING FIRE BARRIERS "Event: Field inspections have discovered several instances of non-conformance with acceptance criteria for fire barriers. The non-conformance has been conservatively assumed to reduce the fire rating of the affected penetrations below the required three hours. "At 2050 hours on 2-6-06 the Operations Shift Manager conservatively declared the all Oconee 'NRC committed' fire barrier penetration seals 'inoperable' pending further inspection. "Initial Safety Significance: Per NUREG 1022, Section 3.2.4, loss of fire barrier separation of Appendix R trains is an unanalyzed condition. Some Oconee 'NRC committed' fire barriers provide train separation between Appendix R safe shutdown trains. At this time, no specific Appendix R train separation penetrations have been discovered to be non-conforming. The reportability determination is based on the decision to conservatively declare the penetrations inoperable. Implementation of hourly fire watches in the affected areas reduces the potential for a significant fire to develop in those areas. "Corrective Actions: Operations entered Selected Licensee Commitment 16.9.5 and established an hourly firewatch in the affected areas. Further inspections continue. Evaluation of inspection findings and repairs will follow." The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 1500 EST ON 3/27/06 FROM R.P. TODD TO S. SANDIN * * * The licensee is retracting this report based on the following: "Event: At 1549 on 2-7-06 Oconee Nuclear Station reported that field inspections had discovered instances of non-conformance with a Duke Energy installation specification for fire barrier penetrations in walls and floors. The non-conformance was conservatively assumed to reduce the fire rating of affected penetrations below the required three hours. Reportability was based on the conservative declaration that the penetrations were inoperable. "Following additional inspections and review of the as-found conditions, Oconee has determined that the as-found conditions still provided a three hour fire barrier so the fire barrier penetrations were actually operable. Oconee has concluded that the event is not reportable and hereby retracts the ENS notification. "Corrective Action(s): Fire barrier penetrations will be repaired to restore compliance with Duke Energy specifications." The licensee will inform the NRC Resident Inspector. Notified R2DO(Carolyn Evans). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-02-07
42317 | 0 | PALISADES | 1 |  |  | [1] CE | 2005-12-14 06:16 | 2006-02-07 14:46 | 2006-02-07 | INVALID SYSTEM ACTUATION OF EMERGENCY CORE COOLING SYSTEM COMPONENTS "This report is being made in accordance with 10 CFR 50.73(a)(1), which states in part, 'in the case of an invalid actuation reported under 10 CFR 50.73(a)(2)(iv), other than the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER. "On December 14, 2005, at 0616 hours EST, a failure of the left channel load sequencer resulted in an invalid actuation of components associated with the left channel design basis accident (DBA) sequencer. Components in the emergency core cooling system were among the components actuated. Therefore, this event constitutes a partial actuation of the emergency core cooling system, which is reportable under 10 CFR 50.73(a)(2)(iv)(A). All components actuated by the event functioned satisfactorily as would be expected for this equipment failure and operating status of the plant at the time of the event." The licensee notified the NRC Resident Inspector. | 85 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2006-02-07
42316 | 0 | TEXAS DEPARTMENT OF STATE HEALTH SE |  |  |  |  | 2005-12-25 | 2006-02-06 15:34 | 2006-02-06 | AGREEMENT STATE - STOLEN RADIOACTIVE SOURCES The State provided the following information via facsimile: "On December 26, 2005 morning, the licensee discovered that their facility was burglarized sometime between 12/24 and 12/25/05. The licensee immediately contacted the Houston Police Department (HPD) to process a report. After conducting a quick tour of the facility with the police, the licensee noticed that some test equipment and a combination safe were taken from the test room. The safe contained (2) Cs-137 calibration/check sources @ 200 microcuries each. The safe was locked and was posted with a 'Caution Radioactive Material' sign. The Houston police were given all required information to conduct an investigation. The licensee also contacted their consultant, Bruce Bristow of Radiation Consultants, Inc. regarding the incident and were advised to purchase (2) replacement sources from the same manufacturer with the same source strength." The Texas Incident Number is I-8296. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | MAT | [5 empty] | 0 | 2006-02-06
42315 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-02-06 14:28 | 2006-02-06 15:13 | 2006-02-06 | SAFEGUARDS SYSTEM DEGRADATION AT SALEM/HOPE CREEK SITE Safeguards system degradation related to monitoring and detection of Vital Area and PA boundary. Compensatory actions were taken. Call the Headquarters Operations Officer for details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-02-06
42314 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2006-02-06 04:00 | 2006-02-06 15:02 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * ALARM RESOLUTION IN URANIUM RECOVERY UNIT - 24 HOUR NOTIFICATION "In accordance with 10CFR74.57(f)(2), a report to NRC is required for the following event. On February 6, 2006 the Alarm Threshold Limit was exceeded for [DELETED] Extraction (Column Based) System. This was reported to the Measurement Control Unit Manager on February 6, 2006 at approximately 7:30 a.m. The time in which the alarm was initially reported was approximately 4:00 a.m. on February 6, 2006. The re-analysis that was done cleared the alarm at approximately 11:30 a.m. on February 6, 2006. The initial test difference exceeded the Alarm Threshold Limit. The final difference after re-analysis was below the Alarm Threshold Limit. "Per E41-116 and the FNMCP, an Alarm Investigation team was established since a process monitoring test exceeded its alarm threshold limit. NRC Ops was contacted at 1502 on February 6, 2006. The NPD MC&A contact at NRC (Tom Pham) was contacted at 1500 on February 6, 2006. Our resident inspector was notified via voice mail at approximately 1530 on February 6, 2006." The licensee notified Doug Collins, NRC Region 2. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 74.57 |  |  |  | 0 | 2008-05-11
42313 | 0 | MAXIM TECHNOLOGIES |  |  |  |  | 2006-02-06 07:00 | 2006-02-06 10:03 | 2006-02-06 | STOLEN MOISTURE DENSITY GAUGE The licensee (Wisconsin company doing work in Michigan) reported that a Troxler moisture density gauge (Model 3440, S/N 36172, 40 milliCuries Am-241/Be, 8 milliCuries Cs-137) was discovered stolen from a construction site in Novi, MI early Monday 02/06/06. The gauge was stored in a contractor trailer and was stolen sometime over the weekend. The lock on the trailer and the chain locking the gauge case to the trailer were both cut. The general contractor reported the theft to the local police. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-02-06
42312 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-02-05 13:36 | 2006-02-05 14:59 | 2006-02-05 | REQUIRED T.S. SHUTDOWN DUE TO EMERGENCY DIESEL GENERATOR INOPERABILITY "Unit 2 Train B emergency diesel generator D6 was removed from service at 2010 CST on 1/29/06 for planned maintenance and Technical Specification (TS) 3.8.1, 'AC Source - Operating,' Condition B, 'One DG inoperable,' was entered. TS Required Action 3.8.1.B.4 requires D6 be restored to operable status with a Completion Time of 7 days. The planned maintenance activities included replacing two sets of two pistons, rings and cylinder liners on Engine 2 of D6 (D6 is a tandem-engine diesel generator). Return-to-service testing was initiated on 2/4/06 and at approximately 0000 CST; the test was halted due to high-indicated crankcase pressure on Engine 1. The test procedure specifies shutting down the diesel generator if crankcase pressure on either engine exceeds 30mm for more than a few minutes (the setpoint for the crankcase pressure trip is 52 mm). "Investigation of the cause of the high-indicated crankcase pressure on Engine 1 started immediately. Unit 2 Train A emergency diesel generator (D5) was demonstrated operable by completing a surveillance test at 1507 CST on 2/4/06. Evaluation of the scope of work to return D6 to operable status and the schedule for completing the work indicated that repairs could not be completed within the remainder of the 7-day Completion Time. Based on this assessment an orderly shutdown of Unit 2 is being performed. "Shutdown [to mode 5] of Unit 2 commenced at 1336 CST on 2/5/06. Unit 2 shutdown will continue until D6 is restored to operable status." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-02-05
42311 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-02-05 10:25 | 2006-02-05 14:56 | 2006-02-06 | LOSS OF SPDS FOR GREATER THAN 8 HOURS "On February 5, 2006 at 0225 hours, the Clinton Power Station shutdown the Plant Process Computer in preparation for transferring Uninterruptible Power Supply (UPS) 1A to its alternate source to make preps for the upcoming DC MCC 1E outage. This caused the loss of the Safety Parameter Display System (SPDS). The computer would not restart following the power supply transfer. "This event is reportable due to the major loss of emergency assessment capability per 10CFR50.72(b)(3)(xiii) (when the SPDS has been unavailable for 8 hours or greater). The cause of the failure of the computer is not known at this time. "The NRC Resident Inspector has been notified." * * * UPDATE FROM LEFFEL TO HUFFMAN AT 1318 ON 2/6/06 * * * "Repairs to the plant process computer were completed at 0810 hours on 2/6/06. The SPDS has been fully restored." The licensee notified the NRC Resident Inspector. R3DO (Lanksbury) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-02-05
42310 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2006-02-03 18:15 | 2006-02-04 00:46 | 2006-02-04 | OFFSITE POWER NOT WITHIN SPECIFICATIONS "On February 3, 2006, at about 1646 PST the Devers-Palo Verde line relayed. This required an evaluation of grid nomograms for San Onofre. At about 1815 PST, the Grid Control Center (GCC) notified San Onofre that the grid nomograms predicted offsite power would not be within limits if San Onofre Unit 3 were to trip (San Onofre Unit 2 is currently shutdown in a refueling outage and Unit 3 is operating at about 100 percent power). Plant Operators declared offsite power inoperable at about 1815 PST. "At about 1843 PST, the GCC notified San Onofre that the grid operator added generation to the grid and that offsite power was within nomogram limits. Plant Operators declared offsite power operable at that time. Consistent with the guidance provided in NUREG-1022, Rev. 2, Southern California Edison is reporting this event in accordance with 10CFR50.72(b)(3)(v)(D). "All four San Onofre diesel generators (two per Unit) remained operable during this event. The San Onofre Senior Resident Inspector has been notified of this event and will be provided with a copy of this report." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-02-04
42309 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-02-03 21:24 | 2006-02-03 23:05 | 2006-02-03 | IDENTIFIED RCS PRESSURE BOUNDARY LEAKAGE "At 2124 hrs on 2/3/06, a containment leak inspection team reported pressure boundary leakage (RCS) at a welded connection on a 3/4" bypass line around the RHR loop suction valve 2HV8701B. Presently the unit is in Mode 3. Preparations are being made to commence cooldown to Mode 5 for repair of the leak. "Unit 2 was taken from 100% RTP to approximately 30% RTP beginning at 1200 hrs on 2/01/06 for repairs of an EHC leak on the main turbine front standard. The EHC leak was repaired and power ascension to 100 % RTP commenced at 2213 hrs on 2/01/06. Approximately 100 % RTP was reached on 2/3/06 at 0600 hrs. "Between 1900 hrs on 2/01/06 and 1600 hrs on 2/02/06, radiation monitor 2RE2562A went into Intermediate Alarm for short durations on three different occasions. Due to moving the plant, an accurate RCS leak rate could not be performed. "A containment entry was performed on the night shift 2/2/06 and again on dayshift 2/3/06. Utilizing a robot and camera, leakage was observed inside the bioshield in the area of RCS Loop #1. The source of the leak on both containment entries was inconclusive. At 1412 hrs on 2/3/06, a shutdown of Unit 2 was initiated to allow further investigation/repair of the leak inside containment. "Unit 2 was placed in Mode 3 at 1807 hrs on 2/3/06." See also EN# 42194 for a similar incident. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-02-03
42308 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2006-02-03 17:59 | 2006-02-03 22:17 | 2006-02-03 | SAFEGUARDS REPORT Discovered a vulnerability in a safeguard system that could allow access to a controlled access area. Compensatory measures have been initiated. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-02-03
42307 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2006-01-30 12:30 | 2006-02-03 19:58 | 2006-02-03 | AGREEMENT STATE REPORT - EIGHT SMOKE DETECTORS FOUND IN A LANDFILL "At 1230 on Monday, January 30, 2006, RHB received a call from the Brea Landfill that a transfer truck from the South Gate Transfer Station, 9530 Garfield Avenue, South Gate, CA 90280 (562-927-0146) set off their radiation alarm (500 kcpm with a background of 7 kcpm). Using an Inovision, CHP 450, at 1145, survey of the truck found the highest reading on the driver's side of the transfer truck 11'6" from the rear and 1'9" from the bottom. A DOT exemption was issued (CA-CA-06-08) and the truck was returned to the South Gate Transfer Station, which is in the LA County Radiation Management area (LA County will also open their own RH5010 on this incident). "Later that day, LA County went to South Gate and identified the radionuclides in the load as Ra-226 and Am-241. On January 31, 2006, LA County separated out eight old Ra-226 and Am-241 smoke detectors from the waste. Two of the detectors had identifying information on them. One was a Pyrotonics, Bridgedale Ave, Cedar Knolls, New Jersey, 07927, made in Switzerland, Model F-3 s/n 66078 with 20 microcuries of Ra-226 and the other was a Pyr-Alarm Cerberus F-3/5A, s/n 24B1965, with 80 microcuries of Am-241, distributed by Pyrotronics, manufactured in Switzerland. All of the Am-241 devices appear to have an activity of approximately 80 microcuries and the Ra-226 devices appear to have approximately 20 microcuries each. LA County took possession of all eight devices and they were placed in RHB's radioactive materials storage area." CA NMED #: XCA-854-013006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-02-08
42306 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2006-01-16 | 2006-02-03 16:25 | 2006-02-03 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The State provided the following information via facsimile: "The South Carolina Department of Health and Environmental Control was notified (telephone) on February 3, 2006, by the licensee, that a medical misadministration had occurred. A patient who was scheduled for an Iodine-131 whole body scan (~4 millicuries) was administered an Iodine-131 therapy dose of 200 millicuries instead. This event took place on January 16, 2006, but was not discovered by the Nuclear Medicine Department until February 2, 2006. The Nuc. Med. Dept. notified the Radiation Safety Office on February 3, 2006. The Radiation Safety Office then notified the Department as well on February 3, 2006 at 3:15 p.m. The referring physician has been notified and was in the process of notifying the patient. The licensee knew no additional details at this point. Additional information will be provided by the licensee in a written report within 15 days. Updates to this event will be made through the NMED system as further information is received." Event Report ID #SC060002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2006-02-08
42305 | -1 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2006-02-02 23:36 | 2006-02-03 04:59 | 2006-04-03 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE DUE TO ONE HPCI TURBINE EXHAUST VACUUM BREAKER ISOLATION VALVE FAILURE "On February 2, 2006 at 23:36 [EST], during testing of the HPCI System per OPT-09.7, HPCI System Valve Operability Test, 1-E41-F079, Turbine Exhaust Vacuum Breaker valve, was given a close signal and failed in the intermediate position. The 1-E41-F079 is one of the two HPCI Turbine Exhaust Line Vacuum Breaker isolation valves. When 1-E41-F079 failed in the intermediate position, the HPCI system was considered inoperable. HPCI is a single-train, safety function system. Approximately two minutes later, the valve was reopened and HPCI was restored to operable status (1-E41-F079 remains inoperable). "The cause of the 1-E41-F079 failing to stroke is being investigated and will be repaired." HPCI will be inoperable after 1-E41-F079 is isolated for maintenance. The licensee notified the NRC Resident Inspector. ****RETRACTION BY MARK TURKAL TO MACKINNON ON 04/03/06 AT 1516 EDT ***** "The purpose of this call is to retract the notification (Event Number 42305) made by the Brunswick Steam Electric Plant, Unit No. 1, Docket No. 50-325/License No. DPR-71. On February 3, 2006, at 0459 hours, the control room Shift Supervisor made a notification (Event Number 42305) to the NRC Operations Center in accordance with 10 CFR 50.72 (b)(3)(v)(D) (i.e., any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident). The event was reported as the HPCI system inoperable due to the HPCI inboard turbine exhaust vacuum breaker isolation valve (1-E41-F079) failure during scheduled testing. "Valve 1-E41-F079 is a motor-operated valve that is normally open when the HPCI system is in service. When the valve is closed, it prevents the HPCI turbine exhaust vacuum breakers from operating, and the HPCI system is considered to be inoperable. During the testing, performed under 0PT-09.7, "HPCI System Valve Operability Test," on February 2, 2006, operators observed a dual indication when attempting to stroke the valve 1-E41-F079 closed. An auxiliary operator observed that the thermal overloads on the breaker were not tripped and no overload annunciator was received. The valve was then reopened. During the time that 1-E41-F079 had dual indication until the valve was full open (i.e., 2336 to 2338 hours), the operators considered the HPCI system inoperable and the event to be an unplanned inoperability of the HPCI system. "Further troubleshooting and evaluation of the valve performance indicates that the valve did not close sufficiently to adversely affect the HPCI system's ability to perform its safety function. Subsequent valve disassembly identified pitting corrosion of the stem. This problem results in increased torque requirements through the first approximately 20 percent of the valve travel as the valve strokes from open to closed. When operators attempted to stroke the valve closed on February 2, 2006, the valve closed less than 20 percent of its stroke when the "closed" torque switch stopped the actuator from further closing the valve. A documented engineering evaluation established that, with valve 1-E41-F079 stroked less than 50 percent closed, enough flow is provided through the valve to allow the vacuum breakers to operate and allow the HPCI system to perform its safety function. Therefore, during the stroking of 1-E41-F079 in accordance with 0PT-09.7 on September 2, 2006, it is reasonable to expect that the performance of the valve did not result in the loss of safety function of the HPCI system. "NUREG-1022, Rev. 2, Section 3.2.7 lists types of events or conditions that are generally not reportable under 10 CFR 50.72(b)(3)(v) and 10 CFR 50.73 (a)(2)(v) criteria. The list of not-reportable conditions includes: "Removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function) "The performance of 1-E41-F079 did result in the valve being declared inoperable for its PCIV isolation function. This condition resulted in the penetration being isolated under an equipment clearance, which closed the HPCI outboard turbine exhaust vacuum breaker isolation valve (1-E41-F075). Closure of 1-E41-F075 under the equipment clearance process did result in the inoperability of the HPCI system; however, this planned inoperability of the system for maintenance is not reportable (as discussed in NUREG-1022, Rev. 2, Section 3.2.7) and no condition was discovered that could have prevented the HPCI system from performing its safety function. "Investigation of this condition and evaluation of other reportability considerations documented in the corrective action program in Action Request (AR) 183102. Carolina Power & Light Company, doing business as Progress Energy Carolina, Inc., has determined that this event does not meet the 10 CFR 50.72 or 10 CFR 50.73 reporting criteria and the notification for Event Number 42305 is retracted. The resident inspector has been notified. " NRC R2DO (Tom Decker) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-02-03
42304 | 0 | WESTERN PENNSYLVANIA HOSPITAL |  |  |  |  | 2005-11-18 | 2006-02-02 17:19 | 2006-02-02 | PROBLEM WITH A VARIAN HIGH DOSE RATE (HDR) AFTERLOADER The licensee provided the following information via facsimile: "On December 1, 2005, [an NRC Region 1 inspector] conducted an inspection of our facility. During the inspection [the inspector was told] about a problem [the hospital was] having with [its] HDR unit [Varian Model VS-200] . On November 18, 2005, during a patient treatment the unit reported a fault during source retraction which reported as a source path constriction. However, the source retracted fully and the error was cleared. The patient received the treatment as prescribed; there was no unintended radiation exposure to the patient. During the following treatment, on November 21, 2005, the error recurred and Varian was contacted to service the unit. The source again retracted fully; the patient received the treatment as prescribed. Varian arrived on November 26, 2005. The engineer repaired that fault, but after the repair, a new problem arose. During post-repair testing by Varian, the inactive wire failed to move from the shielded safe position. [The NRC inspector] requested [..] a report of the findings of the manufacturer after the repair was completed. "Varian subsequently sent a new loaner HDR to [the] West Penn [hospital], and [the] HDR unit was returned to the [Varian] factory in England for repair. [The hospital] immediately forwarded the Varian Troubleshooting Report to [the NRC inspector] upon receipt on January 31, 2006. The report from the factory indicated that the cause of the wire not moving was a signal wire that had been improperly stripped at the time of assembly. Over time, this connection oxidized causing a loss of contact for that signal, which was for the drive mechanism. This caused the inactive source wire not to drive out of the safe. "Although [the West Penn Hospital is] reporting this as requested, [it] respectfully disagree[s] with the NRC interpretation of the 10 CFR 30.50(b)(2) reporting requirement. 10 CFR 30.50(b)(2) states that a 24 hour report is required when 'An event in which equipment is disabled or fails to function as designed when: (i) The equipment is required by regulation or license condition to prevent releases exceeding regulatory limits, to prevent exposures to radiation and radioactive materials exceeding regulatory limits, or to mitigate the consequences of an accident; (ii) The equipment is required to be available and operable when it is disabled or fails to function; and (iii) No redundant equipment is available and operable to perform the required safety function.' [The West Penn Hospital] believe[s] the safety systems of the HDR unit functioned appropriately by reporting the fault. [The hospital] notified the vendor and requested repair when the fault repeated and discontinued using the HDR unit until it was repaired and tested. No regulatory limits were exceeded; the source did not stick; the safety systems did not fail. [The hospital] also do[es] not believe this to be a manufacturing defect requiring reporting under 10 CFR 21.21 but defer[s] to the manufacturer and the NRC interpretation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SAFETY EQUIPMENT FAILURE | UNSPECIFIED PARAGRAPH | [8 empty] | NON EMERGENCY | 1 | PA | HOS |  | 30.50(b)(2) | 21.21 |  |  | 0 | 2006-02-02
42303 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-01-09 | 2006-02-02 12:19 | 2006-02-02 | AGREEMENT STATE - PERSONNEL OVEREXPOSURE The following was received from the State of Louisiana, Department of Environmental Quality, via facsimile: "Event description: Owensby & Kritikos reported on January 19, 2006 that [deleted] exceeded the 5000 mrem exposure for the year 2005. [Deleted] received a yearly dose of 5117 mrem for the year 2005. [Deleted] is an industrial radiographer. As corrective action, the Radiation Safety Officer discussed the importance of ALARA concepts and the use of survey meters, dosimeters, and film badges." Louisiana Event Report ID Number: LA060001. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-02-07
42302 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-12-02 | 2006-02-02 11:21 | 2006-02-02 | AGGREEMENT STATE - ABANDONED WELL LOGGING SOURCE The following information was received from the State of Louisiana, Department of Environmental Quality, via facsimile: "Precision Energy Services abandoned two sources in Well Logging operations. The logging tool was initially stuck on December 2, 2005 and abandoned on December 7, 2005. A 20 Ci source of Americium-241 (Beryllium) and a 2 Ci source of Cs-137 were abandoned at a depth of 6197 Feet. All abandonment procedures were followed. Deflection devises and cement were filled to a depth of 5902 Feet." Louisiana Event Report ID Number: LA 050010. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 2 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Category 2" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-02-07
42301 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2006-02-01 23:00 | 2006-02-02 04:51 | 2006-02-02 | EMERGENCY FILTRATION TRAIN FAN DECLARED INOPERABLE Train "A" of the Emergency Filtration Train (EFT) Unit, which services the control room ventilation system, tripped off line due to a low flow condition. The cause was determined to be a rip in the rubber boot at the suction of the fan, thus causing an automatic trip of the EFT system from a low flow condition through the filter where flow is sensed. Both the "A" and "B" trains were declared inoperable due to the amount of leakage the "B" EFT was having through the ripped boot in the "A" EFT, and the condition found on "B" EFT rubber boot. Upon further evaluation of the "B" EFT boot condition, the "B" train was declared operable at 03:02 CST on 02/02/06. The "A" EFT will remain in a 7 day LCO until the rubber boot is replaced. The 8 hour notification was issued due to both EFT Units being declared inoperable. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-02-02
42300 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2006-02-01 19:43 | 2006-02-02 01:43 | 2006-02-02 | INOPERABLE ISOLATION CONDENSER "While performing DIS 1300-02, Unit 2 ISO COND Steam/Condensate Line High Flow Calibration, workers attempted to valve in DPIS 2-1349-8, U2 Isolation Condenser Return Line Hi Flow. While opening the low isolation valve the technician noticed a vibration in the sensing line. He proceeded to close the equalizer and open the high isolation. As he opened the high side isolation the DPIS indication started to ramp high. As the indication ramped above about 9 inches the technician closed the high side isolation valve. "The Isolation Condenser has been isolated to comply with Technical Specification entered TS 3.3.6.1 C.1 and F.1, Primary Containment Isolation Instrumentation and TS 3.5.3. A.1 & A.2, Isolation Condenser. A prompt investigation has been initiated to determine the cause. A troubleshooting plan is being developed. "Per Tech Spec Bases Section 3.5.3, Applicable Safety Analysis, credit is taken for the Isolation Condenser in the loss of Feedwater Transient Analysis. Therefore the event is reportable under 10CFR 50.72.(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-02-02
42299 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2006-02-01 18:55 | 2006-02-01 21:33 | 2006-02-02 | LOSS OF SITE EXTERNAL COMMUNICATIONS At approximately 18:55 CST, the site lost external communications. At 1937 CST, Duane Arnold declared an Unusual Event due to loss of communications to most offsite agencies. Communications with the county were operating via microwave however, other external communications were not working. The site believed that the loss was due to a "single microwave tower malfunction." The county was contacted directly and other offsite communications (including this event) were being made using a cell phone. The Headquarters Operation Officer was able to contact the Control Room using a commercial phone number. The plant is currently in day 2 of a 14 day RCIC LCO. At 22:35 EST, the site verified that they now have intermittent communications using commercial phone lines. The licensee will not exit the Unusual Event until they have restored communications and know the reason for losing communications. The NRC Resident Inspector is at the site. * * * UPDATE FROM GORDON TO KNOKE AT 02:23 EST ON 02/02/06 * * * Duane Arnold terminated the Unusual Event at 01:00 CST. The licensee restored site communications by correcting the microwave tower malfunction. At a later time the licensee called to say the ENS line became operable at 03:32 EST. The licensee notified the NRC Resident Inspector. Notified R3DO (Riemer), NRR EO (Martin), IRD MOC (Leach), FEMA (Dunker), DHS (Christenson). | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | IA | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(xiii) |  |  | 0 | 2006-02-01
42298 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2006-01-31 09:50 | 2006-02-01 19:45 | 2007-04-18 | AGREEMENT STATE - MATERIAL LOSS OF CONTROL The State provided the following information via email: "[The] RSO for Baker Hughes Oilfield Operations, Inc. (NM license number WL 241-33), reported at 9:50 a.m. on January 31, 2006 that Baker Hughes temporarily lost control of a 2 Ci Cs-137 sealed source after completion of a job two to three miles south of Eunice, NM in Lea County. Upon completion of the job, the crew from the Midland, TX facility secured the 18 Ci Am/Be source in its shipping container and departed the job site, leaving the unshielded Cesium source on the ground. On returning to Midland, the crew discovered the Cesium source was not in the vehicle and they immediately notified Baker Hughes personnel in Hobbs, NM. Hobbs personnel located, recovered, and secured the source approximately 2 hours after the Midland crew left the site. Preliminary information indicated there was no drilling going on at the job site when Hobbs personnel recovered the source and it was not known if any individuals received a dose. A follow-up telephone call to [the RSO] today indicates non-badged individuals were working in the area of the unshielded source. Initial calculations show the highest dose to any of these individuals to be less than 70 mRem. The New Mexico Radiation Control Bureau is continuing the investigation of the incident and will provide updated information as it becomes available. A visit to the licensee's Hobbs, NM office is planned." ** UPDATE FROM MEDINA VIA EMAIL TO KNOKE AT 12:45 EDT ON 4/18/07 "Here is the update on EN 42298 (NMED item# 060083/Baker Hughes) for the dose to members of the public. Initially, Baker Hughes had calculated 68 mRem as the highest dose to a member of the public, our calculation based on the information they provided was 70 mRem. Their final report indicates that after characterization of the meter from a Radium field to a Cesium field, the maximum exposure is 60 mRem. I have attached the final report from Baker Hughes regarding the Cs-137 source left behind at a jobsite in Eunice, NM. The NM Radiation Control Bureau found the response from Baker Hughes and the corrective actions to be adequate." Notified R4DO (Bywater) and FSME (Morell) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Less than Cat 3 event. Note: the value assigned by device type "Category 3" is different than the calculated value "Less than Cat 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2006-02-06
42297 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2006-01-31 16:12 | 2006-01-31 17:08 | 2006-01-31 | SAFEGUARDS EVENT INVOLVING UNAUTHORIZED ACCESS An actual entry of an unauthorized person into the Owner Protected Area. Contact the Headquarters Operations Officer for additional information. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-01-31
42296 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2006-01-30 15:00 | 2006-01-31 09:19 | 2006-01-31 | AGREEMENT STATE REPORT - LOST AND RECOVERED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "The Department received notification at 3:00 pm on 1/30/06, from the RSO at Kumar and Associates, Colorado License # 778-01, that one of their Troxler Model 3430 moisture/density gauges had been stolen from a construction site in Westminster, Colorado. Apparently the technician, who was using the gauge at the construction site, left it unattended for 5 minutes, and discovered it missing when he returned. Local police were notified and responded to the scene. The gauge was found, undamaged, in a field at the construction site a short time later. No public exposures are expected from this incident. The Department is investigating." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2006-02-03
42295 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2006-01-30 | 2006-01-30 16:00 | 2006-01-30 | AGREEMENT STATE REPORT- MISSING SOURCES FOLLOWING HURRICANE KATRINA A representative from the State of Louisiana reported that an X-Ray Fluorescence (XRF) Unit used by the Chalmette Refinery is missing following the devastation from Hurricane Katrina. The building housing the XRF Unit was under 20 feet of water from storm related flooding. The building was gutted in post Katrina restoration without first locating the XRF Unit. The licensee has searched for the unit and declared it missing on 1/30/06. It is believed that the Unit was sent to a landfill with other building wastes. The XRF Unit was a model TN-927 with a 45 mCi Fe-55 source and a 5 mCi Cd-109 source. State Report Number: Pending THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-02-02
42294 | 0 | SOLAR TESTING LABORATORY, INC. |  |  |  |  | 2006-01-28 | 2006-01-30 09:39 | 2006-02-20 | TROXLER MOISTURE DENSITY GAUGE STOLEN Sometime between Friday night (1/27/06) and early Saturday morning (1/28/06), the authorized gauge user's vehicle was stolen from a residential location in Sharpsburg, PA. The vehicle's trunk contained a locked and secured Troxler Model 3440 S/N 18315 (8 mCi Cs-137 and 40 mCi Am-241/Be). The local Sharpsburg Police Department was informed of the theft (report #060309). The licensee is evaluating whether a reward will be offered. * * * UPDATE FROM MURPHY TO HUFFMAN AT 2120 EST ON 2/20/06 * * * The Pittsburgh Police Department notified the licensee that the stolen vehicle had been recovered and placed in a police impoundment lot 1930 EST on 2/20/06. A representative for the licensee was dispatched to recover the vehicle and found the gauge still in the trunk undisturbed. Visual checkout of the gauge was normal. The licensee will perform a leak test on the source in the morning. R1DO (Trapp), R3DO (Riemer) and NMSS EO (Brach) notified. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-01-30
42293 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2006-01-29 04:40 | 2006-01-29 06:37 | 2006-01-29 | OFFSITE NOTIFICATION "The New Jersey Department of Environmental Protection was notified of the sighting of 10 dead and approximately 40 stressed Bluefish in the Oyster Creek discharge canal at 0440 January 29, 2006, following a plant shutdown." The licensee will notify the NRC Resident Inspector. *** UPDATE ON 01/29/06 AT 1649 EST BY GEORGE VOISHNIS TO MACKINNON ***** "This is a NRC ENS 24 hr notification per Oyster Creek Environmental Tech Spec Section B 1.1.1 A. "At 11:45 on 01/29/06 a total of 100 fish were spotted either dead or stressed in the discharge canal following a Reactor S/D (shutdown) that was completed at 22:22 on 01/28/06" R1DO (N. Perry) notified. The NRC Resident Inspector was notified of this event by the licensee. The state will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-01-29
42292 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2006-01-27 15:00 | 2006-01-28 09:28 | 2006-01-28 | 24 HR NRC BULLETIN 91-01 DUE TO CRITICALITY CONTROLS DEGRADATION "At approximately 1500 on January 27, 2006, operations leadership notified nuclear safety that five (5) loaded rod trays were discovered stored on a conveyor at the Automated Bundle Assembly Machine (ABAM). A physical barrier intended to limit the number of rod trays to four (4) had failed, and was not in place. This event constitutes a loss of geometry control. "The independent control on moderation remained intact, thus no unsafe condition existed. This event is reported pursuant to NRC Bulletin 91-01 within 24 hours. The rod trays were removed from the conveyor, and the geometry control re-established within 4 hours. The ABAM unit has been shutdown pending investigation and implementation of additional corrective actions." The licensee will notify NRC Region 2, and State and Local authorities. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2006-01-28
42291 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-01-27 | 2006-01-27 14:02 | 2006-01-27 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE The Texas Department of State Health Services reported an "overexposure, ( 5.581 Rem) that was discovered during badge processing. The radiographer was unavailable for an interview." The event occurred "4th quarter 05" at the "Mach Industrial Group." The Texas Incident Number is I-8293. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-02-01
42290 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-01-27 08:00 | 2006-01-27 14:15 | 2006-02-06 | UNIT 2 EMERGENCY RESPONSE DATA SYSTEM (ERDS) MODEM FAILED "`AT 0800 ON 01/27/2006 the Unit 2 ERDS modem failed its testing criteria. The modem will not transmit any of the Unit 2 ERDS data. At 1234, the determination was made that repairs will exceed 8 hours. The data points transmitted by ERDS are operable. Only the transmission of the Unit 2 data to the NRC is inoperable. Unit 1 ERDS remains operable. "A review of the ability of the Emergency organization to function without ERDS was performed. The NEP (Nuclear Emergency Planning) Duty Planner has established another data line. In response to a Unit 2 event, the affected NERO (Nuclear Emergency Response Organization) positions will verbally transmit the Unit 2 data to the NRC. All affected NERO positions have been notified. "Since the Unit 2 ERDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Offsite Communications Capability and reportable under 10 CFR 50/72(b)(3)(xiii)." The NRC Resident Inspector was notified of this event by the licensee * * * UPDATE RECEIVED BY JOE O'HARA FROM RON FRY AT 1316 ON 2/6/06 * * * "This is a followup to EN# 42290, which documented a loss of emergency response capability. The Susquehanna computer group replaced the Unit 2 ERDS modem power supply with an identical component then completed the quarterly functional check as of 10:37 on 02/06/2006. As of 10:37 on 02/06/2006, the Unit 2 ERDS modem is operable and will transmit Unit 2 data to the NRC. All affected NERO positions have been notified." The licensee notified the NRC Resident Inspector. R1DO(Gray) has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-27
42289 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-12-15 | 2006-01-27 09:59 | 2006-01-27 | AGREEMENT STATE REPORT - MISSING RADIUM SOURCE "Licensee representative reported a lost Liquid Scintillation Counter with associated Radium 226 source (removed from the location approx late December 2005). Authorized user [Deleted] surplused the LSC, LKS Model 1214, Liquid Scintillation Counter- SN 115, UNC Property Number 175899, Radium 226 source of 10 microcuries. "The licensee representative searched for the LSC/source at UNC Chapel Hill Surplus Property, NC Surplus Property, and has interviewed individuals that may have purchased or acquired LSC, to no avail. "Incident Assessment by IAT: "There is no significant radiation exposure hazard, there is no significant radiation contamination hazard, and the event has been classified as LOW - Minimal or Low Risk in regards to persons, environment, and facilities/equipment at the facility." NC Incident number: 06-05 This event was reported by the State of North Carolina voluntarily to the NRC, however, the NRC does not regulate Radium 226 at this time. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-02-01